## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
0101994001 | Dresden 1 | 05/07/1994 | 06/03/1994 | 9406220041 | <strong>50,000 Gallons of Unit 1 Contaminated Demineralized Water Released to Ground Water</strong><br /><i>Abstract:&nbsp;</i>This report is voluntarily submitted in accordance with 10CFR50.73(a)(1). On Sunday, May 8th, 1994 at approximately 0830, Operations personnel observed an excessive amount of water flowing from one of the storm sewer drains into the Unit 1 intake canal. The source of the water was traced back to the ground near the Unit 1 Radwaste Decant Building. The water was determined to be from the 1A Contaminated Condensate Storage Tank (CST), which was being pumped by the Contaminated Demin Jockey Pump into the Unit 1 Contaminated Demin header (buried schedule 80 carbon steel pipe) and out of a hole into the ground. The jockey pump wall running to perform an in service leak test to a repaired valve located in the decant building. The jockey pump was secured and isolated, stopping the spill. The change in level during the test indicated that approximately 50,000 gallons was pumped into the ground. The water was sampled and found to be only slightly contaminated; the activity was not detectable using local survey instruments, and laboratory analysis verified that the activity to be well below 10CFR20 Appendix B limits and ODCM calculation. The highest activity concentration measured was 8.87 E-7 microcuries/milliliter of Cs-137 and 2.09 E-7 microcuries/milliliter of Co-60. Radiation Protection Personnel took control of the Spill. The area surrounding the spill was roped off and the standing water was pumped into the Unit 1 Radwaste System. All areas were surveyed and ropes removed by Tuesday, May 10.
0101994002 | Dresden 1 | 09/03/1993 | 08/05/1994 | 9408110190 | <strong>Technical Specification Required Sample Performed at an Incorrect Frequency Due to Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During a review of the approved Amendment 37 to Unit 1 Technical Specifications and supporting procedures, it was determined that a surveillance was performed at an incorrect frequency during the period from September 3, 1993, until January 1, 1994. Amendment 37, dated September 3, 1993, requires in section 3.8.E that grab samples of the exhaust to the Unit 1 Chimney be taken and analyzed daily whenever the Unit 1 Chimney Effluent Radiation Monitor is out of service. Contrary to this, samples were taken weekly during the periods the Effluent Radiation Monitor was out of service. on January 1, 1994 administrative controls were corrected to sample daily when the Effluent Radiation Monitor was not in service.
1331994001 | Humboldt Bay 3 | 03/29/1994 | 04/25/1994 | 9405030338 | <strong>Thermoluminescent Dosimeter Missing From Onsite Radiation Monitoring Station Due To Unknown Reasons</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1994, while the Unit was in SAFSTOR, a technician was performing the quarterly exchange of the thermoluminescent dosimeters (TLDs) in onsite environmental radiation monitoring stations when he found that one of the stations did not contain a TLD packet. The Technical Specifications (TS) require that the dosimeters at these stations be monitored at least quarterly (TS Section V.B.6.b). A new TLD packet was installed for the second quarter monitoring period.<br /><br /> The root cause of this event is unknown, as the packet is believed to have been removed by unknown parties for unknown reasons. <br /><br /> Corrective action to help prevent recurrence included fitting this and similar monitoring stations with a tamper resistant seal to discourage opening the station. In addition, all plant personnel have been informed of the purpose and importance of the stations, and information labels have been attached to the stations.
1331994002 | Humboldt Bay 3 | 10/18/1994 | 11/16/1994 | 9411250113 | <strong>Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1994, while the Unit was in SAFSTOR, a quality assurance audit found that water samples from the Humbodlt Bay Power Plant discharge canal were not analyzed 'weekly' as required by Section V.B.6.a of the Technical Specifications (TS). The samples are collected weekly and then shipped to PG&E's Department of Technical and Ecological Services (TES) where they are analyzed in batches (approximately monthly for gamma radioactivity and approximately quarterly for tritium). <br /><br /> The root cause of this event was personnel error in interpretation of the requirements of the TS. <br /><br /> Corrective actions include: <br /><br /> 1. Continue to perform onsite analysis of the weekly samples from the discharge canal composite sampler, in addition to continuing the existing practice of sending samples to TES for analysis. <br /><br /> 2. The surveillance test procedure will be revised to include weekly onsite sample analysis.
1551994001 | Big Rock Point | 02/10/1994 | 03/31/1994 | 9404110041 | <strong>Containment Sump Isolation Valve Stroke Times Failed To Meet ASME Code Timing Criteria</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1994, three containment isolation valves failed to meet the stroke timing acceptance criteria required during the execution of a ninety day surveillance test. Two of the valves were in the enclosure dirty sump discharge line, and the other was in the enclosure clean sump discharge line. Both clean and dirty sump valves were immediately closed, and were only being operated to pump down their respective sumps. <br /><br /> The root cause has been attributed to solenoid valve resilent seats made of ethylene-propylene rubber (EPR). They were exposed by the return air from air operated control valves to a foreign, hydrocarbon material similar to oil or grease. The seat material is a distinguishing feature common to the three solenoids that failed, and is designed to operate in an 'oil free' environment. <br /><br /> In addition to the affected solenoid valves, solenoid valves in similar applications were replaced using valves engineered with Viton and/or stainless steel seats before returning the facility to power operation. The manufacturer of the solenoid valves will continue to evaluate a returned valve by attempting to re-create the failure over a long period of time.
1551994002 | Big Rock Point | 03/05/1994 | 03/14/1994 | 9403220133 | <strong>Discovery Of An Unsecured High Radiation Area Door</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 6.12.2. requires that high radiation areas greater than 1000 mr/hr accessible to personnel be provided with locked doors to prevent unauthorized entry. <br /><br /> Contrary to the above, on March 5, 1994, at 0930, an auxiliary operator discovered an unlocked high radiation area door. The actions directed by a facility procedure concerning the discovery of high radiation areas found unlocked/unguarded, was recognized and immediately performed. The facility was currently in a scheduled maintenance outage. <br /><br /> The root cause was determined to be human performance, with fatigue and the midnight shift (schedule) as secondary causal factors. <br /><br /> During the time the door was unlocked, no entries were made into the high radiation area. Corrective actions will include 'locking or closure device' postings on all high radiation area doors required to be locked.
1551994003 | Big Rock Point | 03/07/1994 | 03/28/1994 | 9404050056 | <strong>Unplanned Actuation Of An Engineered Safety Feature - Electric Fire Pump</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1994, the reactor was in the cold shutdown condition and the Steam Drum had been drained to allow reactor vent valve repairs. This configuration generates an electric and diesel fire pump engineered safety features start signal through the Reactor Depressurization System (RDS) logic, which was inhibited per procedure by hand switches in the control room. These fire pumps also function as low pressure core spray pumps. <br /><br /> Following valve repair, the steam drum water level was raised above the automatic start setpoints of the fire pumps. To return the RDS system to its normal standby condition, RDS sensor cabinets were reset; and at 1812 hours that same day the key switch for the electric fire pump was switched from the 'INHIBIT' to the 'AUTO' position. Unexpectedly, the electric fire pump started. The operator then placed the switch back to 'INHIBIT', reset the modules in the actuation cabinets, and stopped the pump. The Diesel Fire Pump was not affected. <br /><br /> Root cause has been determined to be 'failure to use procedures'. Corrective actions will include examining the level of procedure usage, training, and appropriate procedure revisions.
1551994004 | Big Rock Point | 03/08/1994 | 04/04/1994 | 9404110282 | <strong>Unplanned Actuation Of An Engineered Safety Feature - Diesel Fire Pump</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1994, the reactor was in the cold shutdown condition and steam drum instrument lines were being backfilled to equalize level instrument readings. Both the Electric and Diesel Fire Pumps (these fire pumps also function as low pressure core spray pumps) were inhibited from starting (per procedure) by handswitches in the control room. At approximately 1253, the Diesel Fire Pump started unexpectedly. <br /><br /> The root cause identified a 'loss of voltage indication' in the diesel fire pump handswitch contacts. The voltage feeds the fire pump logic module to disable the auto start feature. The loss of voltage also contributed to the malfunction of an associated optical isolator/light; however additional troubleshooting identified a problem with socket-to-pin fit. <br /><br /> The handswitch contacts were changed, and the optical isolator/light socket fit was corrected. The handswitch was declared operable at 2306 hours that same day. Additional corrective action included an investigation of other safety-related optical isolator/light socket-to-pin fits before exiting cold shutdown.
1551994005 | Big Rock Point | 03/20/1994 | 04/08/1994 | 9404130183 | <strong>Unplanned Actuation Of The Reactor Protection System - No Rod Motion</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 20, 1994, a procedure was being performed that demonstrates the core remains subcritical when the highest worth control rod and an adjacent rod at a position known to contribute greater than or equal to .003 delta K/K under the most reactive conditions, are fully withdrawn. In order to proceed with control rod withdrawal, there must be no scram signals present and rod withdrawal interlocks must be clear. In an attempt to clear an interlock (an unplugged jib winch on the refuel floor), the operators repositioned the mode switch from the REFUEL to RUN position at 1957 hours. A Reactor Protection System (RPS) scram resulted unexpectedly, and the operators immediately determined that the Main Steam Isolation Valve (MSIV) was in the closed position, causing the scram. However, there was no rod motion because all the rods were already inserted fully in the core. The mode switch was repositioned from RUN to REFUEL, the safety system reset, and the interlock cleared by plugging in the jib winch. Corrective action will include additional training for the operations personnel with regards to interlock interaction with the mode switch, and procedure enhancements to prevent recurrence.
1551994006 | Big Rock Point | 07/29/1994 | 01/12/1995 | 9501240124 | <strong>Turbine Oil Fire</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1994, a Control Room Operator (CO) was performing a routine turbine inspection required during power operation. The reactor was operating at approximately 87%. While at the front standard, he noticed an odd smell. He then walked around the east side of the turbine and opened an inspection door. The CO observed an orange, flickering light reflecting from somewhere beneath the turbine. The Shift Supervisor (SS) was immediately informed, and proceeded to a recently installed closed circuit television monitor to remotely scan the room underneath the turbine. The SS identified the source of the flickering light as a baseball sized flame on top of the High Pressure Feedwater Heater insulation, and notified the Control Room at 0553. The fire alarm was then sounded. The fire brigade assembled, entered the pipe tunnel, and extinguished the fire at 0602 using dry chemicals. <br /><br /> The source of the fire was confirmed to be turbine lube oil that overflowed a collection basin placed under the # 2 turbine bearing onto the hot High Pressure Feedwater heater; which was the likely source for ignition. After a more thorough investigation, management decided to place the plant in the shutdown condition to clean up the oil spill and replace the oil soaked feedwater heater insulation.
1551994007 | Big Rock Point | 09/30/1994 | 10/31/1994 | 9411080244 | <strong>Manual Reactor Scram During Planned Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1994, the reactor was manually scrammed at 2146 from 69% power during a planned facility shutdown for the 1994 Refueling Outage. Cooldown rate and temperature spreads between primary system equipment were maintained in accordance with Technical Specifications. <br /><br /> The turbine generator (T/G) controls were not operating smoothly, causing uncontrolled variances in reactor pressure control. (These oscillations had been experienced late in the operating cycle, and were exacerbated during the shutdown). Plant management deliberated for several hours on how to lower power with erratic T/G controls, and decided that a manual scram would be the preferred method. Following the manual scram, the plant equipment operated as expected. <br /><br /> The root cause of the erratic T/G controls was the binding of the admission valve operating piston pilot valve extension rod in its guide bushing. The extension rod and the guide bushing were cleaned and dimensional checks performed to obtain clearance information. Prior to returning to service, the system will be tested-to ensure performance.
1551994008 | Big Rock Point | 10/18/1994 | 12/22/1994 | 9412300168 | <strong>Steam Drum Water Level Switch Found Out-Of-Tolerance</strong><br /><i>Abstract:&nbsp;</i>While performing calibration and testing of the Yarway Reactor Steam Drum water level sensors during the 1994 refueling outage, one out-of-four sensors was found out-of-tolerance in the non-conservative direction. The switch is required to trip at a steam drum level of minus 8.5 inches below centerline, and the actual trip during testing occurred at minus 10.6 inches. A trip signal from these sensors anticipate a loss of water which could lead to a low reactor water level, and initiate a reactor scram. (In this case the logic, one out of two, is such that if a valid trip signal had been received, the other three switches would have initiated the reactor scram). The root cause of the discrepancy has been identified as instrument drift from as-left settings. This is the first instance of non-conservative drift exceeding its acceptance criteria associated with this switch. <br /><br /> An investigation into the issue by the Probabilistic Risk Assessment Group recommended what the future 'as left' settings should be, taking into account that the postulated affect of high range instrument drift would not have a significant impact on plant response for analyzed transients. Calibration procedures have been revised accordingly.
1551994009 | Big Rock Point | 11/03/1994 | 01/19/1995 | 9501310228 | <strong>Invalid Manual Actuation Of The Primary Containment Spray System</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1994, the fire header, which feeds the core and containment spray lines, was being filled and vented by Operations when flow through the primary containment spray nozzles occurred. Approximately 100 gallons of water was sprayed inside containment before a manual isolation valve was closed, terminating the event. Although no plant equipment was damaged, the Plant Manager ordered a stop to all outage activities that required switching and tagging support from Operations. <br /><br /> Subsequent investigation found that the Primary Containment Spray Valve, MO-7064, had been left partially open following the completion of preventive maintenance to facilitate post maintenance testing. However, this testing was not performed prior to repressurizing the fire header. <br /><br /> The root cause of this event was an inadequate switching & tagging order (S&TO) tracking system. To prevent recurrence, Operations will develop an enhanced means of tracking and displaying plant configuration.
1551994010 | Big Rock Point | 11/29/1994 | 07/03/1995 | 9507110247 | <strong>Manual Scram Due To Loss Of Feedwater</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1994, reactor power escalation following a refueling outage was in progress. In addition, the second condensate pump was being returned to service following the replacement of a mechanical seal. <br /><br /> At 1530, the reactor was manually scrammed from about 54% power due to loss of suction pressure to the only operating feedwater pump. While filling and venting the condensate pump prior to operating, air was drawn through the common vent line to the operating condensate pump and discharged to the operating feedwater pump. All of the rods inserted and the plant functioned as designed. An Administrative cooldown limit for the Steam Drum was briefly exceeded, however an evaluation confirmed that engineering design limits were well within the specified parameters. <br /><br /> The loss of feedwater was caused by a procedure that had never been validated for the rare operating condition of returning a condensate pump to service during power operation after it had been drained for maintenance. Corrective actions include procedure revision and validation for this operating condition.
2131994001 | Haddam Neck | 05/18/1993 | 01/28/1994 | 9402080258 | <strong>Containment Air Recirculation Fans Failed Flow Test</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1993, with the plant shut down in Mode 5 for the Cycle 17 Refueling Outage, three of four Containment Air Recirculation (CAR) Fans did not meet the acceptance criteria for air flow rates during surveillance testing. At that time a reportability evaluation concluded that, based on the time of discovery, this event was not reportable. On January 4, 1994 with the plant in Mode 1 at 100 percent power, a further review of the event determined that the time of discovery reporting criteria may not have been valid and that the event was reportable under 10CFR50.73 (a) (2) (i) (B). The causes of the failure were instrument calibration inaccuracy and worn backdraft dampers. The four CAR Fans were adjusted and retested prior to startup from the refueling outage in June, 1993 and all air flow rates were within the Technical Specification's required range. Corrective actions included using a different approved vendor for instrument calibration and replacement of the backdraft dampers. Also, a Technical Specification change request is being considered which will widen the acceptance criteria for the CAR Fan flow requirements.
2131994002 | Haddam Neck | 02/12/1994 | 06/03/1994 | 9406130068 | <strong>Service Water System Declared Inoperable Due to Pipe Weld Flaws</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1994, at approximately 0945 hours, with the plant in Mode 1 at 100% power, a pin hole leak developed on the Service Water System (SWS) supply piping to the 'A' Emergency Diesel Generator. The leak occurred on the first weld upstream of a manual isolation valve . This weld was undergoing light surface grinding in preparation for Ultrasonic Test (UT) inspection. This work was part of an ongoing inspection and evaluation effort related to some noted corrosion of this piping and associated welds. Following leak initiation, both SWS headers were conservatively declared inoperable since previous assumptions regarding weld thickness and structural capability were considered suspect. Plant operators entered Technical Specification 3.0.3, immediately commenced a shutdown and entered Mode 5 at 1810 hours on February 13, 1994. The root cause of this event was determined to be Microbiologically Influenced Corrosion (MIC). Initial corrective action was to initiate replacement of the SWS lines to the diesels via a plant modification. Additional corrective action included inspecting other applicable safety related locations and conducting repairs as appropriate. This supplemental report is being submitted to provide the results of the root cause evaluation and to address the additional corrective actions taken.
2131994003 | Haddam Neck | 02/10/1994 | 03/11/1994 | 9403180153 | <strong>Containment Personnel Hatch Failed Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 10, 1994, at 0912 hours, with the plant in Mode 1, at 100 percent power, the containment air lock reduced pressure test was performed by plant operators in accordance with Technical Specification 4.6.1.3(a) after a containment entry was made on February 8, 1994. The pressure decay rate calculated by plant operators met the procedural acceptance criteria but a subsequent calculation completed by Engineering to adjust for an air lock temperature increase yielded a leak rate in excess of the Technical Specification limit. The cause of the failure is attributed to a procedure deficiency. The test procedure did not provide adequate guidance to the operator in the event a temperature increase was observed during the 60 minutes hold time. A temporary procedure change was immediately generated to correct the procedure, and the airlock leak test was re-performed with a Volumetrics Leak Rate Monitor on February 17, 1994. The leak rate recorded on February 17, 1994 was within the Technical Specification limit which indicated the containment air lock was operable. This event is reportable per 10CFR50.73(a)(2)(ii) and 10CFR50.73 (a) (2) (i) (b) since operability of the containment air lock was not determined within 72 hours of the containment entry.
2131994004 | Haddam Neck | 02/16/1994 | 05/26/1994 | 9406020153 | <strong>Automatic 480 Volt Bus Transfer Failure Due to Circuit Breaker Malfunction</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1994, at 0130 hours with the plant shut down in mode 5 (cold shutdown) for Service Water piping repairs, performance of special test ST 11.7-126 'Functional Test Of MCC-5 Automatic Bus Transfer (ABT)' was unsatisfactorily completed when the 480 volt bus 6 feed to Motor Control Center (MCC) 5 circuit breaker 11C failed to close. The cause of the failure has been identified to be an out - of- position mechanical retaining device mounted on the manual operating shaft of the bus 6 11C breaker. This device being out of its normal position allowed the shaft to travel further than designed into the breaker operating mechanism causing the breaker to malfunction upon receiving a close signal. Corrective action consisted of replacing the breaker's manual operating mechanism and modifying the ABT scheme to minimize challenges to the breaker operation. The condition leading to the transfer failure had very likely existed for a time period in excess of the 72 hour Action Statement in Technical Specification 3.8.3.1.2 and,thus is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. This Supplemental Report provides the results of the root cause evaluation and the long term corrective action.
2131994005 | Haddam Neck | 02/19/1994 | 03/18/1994 | 9403250177 | <strong>Pressurizer PORVs Failed to Fully Stroke Open During Testing</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1994 at 1345 hours, with the plant in Mode 5 (Cold Shutdown) while performing a stroke test of the pressurizer Pilot-Operated Relief Valves (PORVS) it was determined that the valves would not fully open. The problem was traced to a leak in the diaphragm assembly of the PORVs (PR-AOV-568 & 570). This leak was caused by improper assembly of the diaphragm in the actuator due to incomplete communication between the manufacturer and the licensee. Both PORV diaphragms were replaced during the 1993 refueling outage with a new style. style diaphragms with the original material which had no history of this kind of failure. It is not known how long the PORVs had been inoperable prior to this surveillance, but it is believed to have been longer than the ACTION time allowed. Therefore, this event is reportable under 10CFR50.73(a)(2)(i)(B), since it resulted in a condition prohibited by the plant's Technical Specifications. It is also reportable under 10CFR50.73(a)(2)(v)(D) and 50.73(a)(2)(vii) as a common mode failure.
2131994006 | Haddam Neck | 02/23/1994 | 03/02/1995 | 9503080397 | <strong>Main Steam Safety Valves Exceeded Lift Setpoint Criteria</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1994, at 1600 hours, with the plant in Mode 5 (cold shutdown),it was determined that five active pilot valves associated with four main steam safety valves (MS-SV-14, 24, 34, and 44) exceeded the Technical Specification acceptance criteria for their lift setpoint. The cause of the event appears to be a disc and nozzle adhesion in the pilot valves. Short term corrective action was to regularly exercise the pilot valves to prevent the adhesion. off-site facility for additional setpoint testing, simulating normal operating conditions, in order to establish a baseline testing frequency . Long term corrective action was initiated to determine the type of adhesion present on the valves and the need for material changes to the pilot valve seating area. The current corrective action is to continue to follow the progress of the material change. This supplemental report is being submitted to provide the results of the corrective actions taken to date.
2131994007 | Haddam Neck | 03/08/1994 | 04/05/1994 | 9404130172 | <strong>Potential for Radiological Release During Post LOCA Sump Recirculation</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1994, at approximately 1320 hours, with the plant in Mode 5 (cold shutdown), it was determined that the potential existed to lift a relief valve in the Chemical and Volume Control System (CVCS) during the performance of the emergency response procedure to establish containment sump recirculation following a Loss of Coolant Accident (LOCA). This in turn could cause another relief valve to lift in the Radioactive Waste Gas System which discharges to the environment via the plant stack. If such an event were to occur, radiological dose consequences could be more severe than previously predicted. The cause of this condition was a failure to recognize the full potential adverse impacts of a change to an emergency response procedure during the review of the procedure change in 1990. Corrective action involved revising the affected emergency response procedure to eliminate the potential overpressure condition. Also, in October, 1991 the station procedure addressing the preparation, change, and review of emergency response procedures was revised to provide for a more rigorous technical review of new or changed procedures than had existed previously.
2131994008 | Haddam Neck | 03/24/1994 | 11/08/1995 | 9511130265 | <strong>Auxiliary Feedwater Hydraulic Control System Setpoints Found Low</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1994, at 0655 hours, with the plant in Mode 5, a surveillance was performed to verify the setpoints of the Auxiliary Feedwater control system DC hydraulic pump automatic start and low pressure trip pressure switches. The As-Found setpoint of the DC pump automatic start pressure switch setting was 25 psi below the Technical Specification allowable value. The cause of the event was investigated. The location of the switches may have been a contributing factor. Initial corrective action consisted of recalibrating the switches. Subsequent corrective action consisted of relocating and replacing the switches with a different type. Although instrument drift found during a surveillance typically is assumed to have occurred at the time of discovery, the disproportionate number of unexpectedly large setpoint deviations provided reasonable doubt that the switch was within its Technical Specification limits following refueling outage 17 and prior to the February/March maintenance outage. This event was reportable under 10CFR 50.73 (a) (2) (i) (B) as a condition prohibited by the plant's Technical Specifications. This supplemental report provides the results of the failure investigation and the corrective actions taken.
2131994009 | Haddam Neck | 03/28/1994 | 04/21/1994 | 9404260318 | <strong>Automatic Reactor Trip During Reactor Coolant Pump Bus Transfer</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1994 at 2227 hours with the plant in mode 1 and reactor power approximately 7 percent of rated thermal power, an automatic reactor trip occurred while performing Normal Operating Procedure (NOP) 2.1-6, 'Reactor Just Critical to Minimum Load.' When the operators transferred the 4160 volt electrical power supply to reactor coolant pump bus 1-1A from offsite power to the main generator, circuit breaker 3T-1A opened however 309-1A failed to close. Subsequently, indicated reactor power exceeded the P-7 permissive enable setpoint while reactor coolant pumps 1 & 2 were de-energized. Before breaker 3T-1A could be reclosed, the 2 out of 4 reactor coolant low flow trip logic was satisfied and the reactor tripped. The cause of this event was equipment failure and a procedure deficiency. Immediate corrective actions consisted of a procedure revision to NOP 2.1-6 and the repair/reinstallment of breaker 309-1A. This event is reportable under 10CFR50.73 (a) (2) (iv) since it resulted in an automatic actuation of the Reactor Protection System.
2131994010 | Haddam Neck | 04/20/1994 | 05/18/1994 | 9405250058 | <strong>Neutron Source / Detector Geometry Yields Non- Conservative Analysis</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1994, at 1445 hours, with the plant in Mode 1 at 100 percent power, an engineering evaluation determined that a non-conservative assumption was used in the reactor coolant system boron dilution analysis. The non-conservative assumption involved the use of a linear relationship between the inverse count rate ratio (1/M) and boron concentration during a dilution event. The placement of the incore neutron sources too close to the excore detector causes this relationship to become non-linear. The actual 1/M curve results in a shutdown monitor doubling alarm occurring closer to criticality than assumed in the analysis. Therefore, the time allowed for operator action to terminate an inadvertent boron dilution is less than required. The cause of this event was the failure to verify the assumed detector response to an inadvertent dilution event. The short term corrective action was to take credit for the actual alarm setpoint of 1.62 instead of the assumed doubling (2.0) and to account for the accumulated core burnup. The long term corrective action being evaluated is revising the alarm setpoint, increasing the required shutdown margin and relocating the source assemblies. This event is reportable per 10CFR50.73(a)(2)(v)(D) since it resulted in a condition that alone could have prevented the fulfillment of a safety function of a system needed to mitigate the consequences of an accident.
2131994011 | Haddam Neck | 04/23/1994 | 05/20/1994 | 9405250099 | <strong>Unplanned Loss of Spent Fuel Cooling</strong><br /><i>Abstract:&nbsp;</i>On April 23 1994, at 2150 hours, with the plant in Mode 1, at 100 percent power, plant security, during a routine round, notified the control room of smoke inside the lower level of the spent fuel building. Plant operators determined that the source of the smoke was a failed seal on the 'B' Spent Fuel Cooling pump. The 'A' Spent Fuel Cooling pump was out of service at the time for routine maintenance. Immediate action by operators was to shut down and isolate the pump and commence hourly nt fuel pool temperature and level. The 'A' Spent Fuel Cooling pump was placed back in service on April 24, 1994 at 1140 hours. During this temporary loss of spent fuel cooling the spent fuel pool temperature increased from 90 degrees F at 2200 hours to 97 degrees F at 1100 hours (0.54 degrees/hr). Forced cooling to the spent fuel pool was unavailable for approximately 13 hours. This event is not reportable under 10CFR50.73 however this LER is being submitted as a voluntary report.
2131994012 | Haddam Neck | 04/28/1994 | 05/26/1994 | 9406020114 | <strong>Potential Loss of Service Water Due to Flood Induced Strainer Fouling</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1994, at 1230 hours, with the plant in Mode 1 at 100 percent power, a previously unidentified external flooding scenario was discovered which has the potential to incapacitate the service water (SW) system at a river flood elevation less than that which was assumed in the design analysis. Under this newly discovered scenario, a flood at slightly above site grade elevation would enter the plant's intake structure and completely flood the lower level. This would prohibit personnel from entering the lower level to clean the SW pump discharge strainers. It is further postulated that river debris could clog the SW strainers to the point that the SW pumps are not capable of delivering sufficient flow. The cause of this condition was the apparent lack of recognition of the potential need to clean SW strainers during floods. Corrective action consisted of providing the operating shifts with alternatives for mitigating this event and incorporating appropriate changes into plant procedures. This event is reportable under 10CFR50.73(a)(2)(v)(D) as a condition that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
2131994013 | Haddam Neck | 05/05/1994 | 07/07/1997 | 9707140218 | <strong>HPSI Pump Discharge Relief Valve Setpoint Found Low</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1994, at 1630 hours, with the plant in Mode 1, at 100 percent power, the High Pressure Safety Injection (HPSI) common discharge header relief valve was found to be lifting during the performance of a routine surveillance procedure. The relief valve was found to be lifting when 'B' HPSI pump was operating, however it did not open when the "A" HPSI pump was operating. Lifting of the relief valve during the injection phase of a LOCA and its subsequent failure to reseat during sump recirculation would result in a discharge of contaminated sump water back to the refueling water storage tank and the potential for an unacceptable radiological release. The apparent cause of this event is setpoint drift coupled with the proximity of normal operating pressure to the relief valve setpoint. Short term corrective action consisted of removing the 'B' HPSI pump from service, increasing the allowable system header pressure along with the relief valve setpoint and returning the pump to service within 28 hours. Long term corrective action involves increasing the testing frequency of the relief valve (5 years to each refueling) and evaluating the feasibility of a further increase in allowable system pressure. <br /><br /> This supplemental report is being issued to retract originally proposed corrective actions that will no longer be implemented due to the Haddam Neck Plant being in a permanently defueled state.
2131994014 | Haddam Neck | 05/31/1994 | 06/27/1994 | 9407050135 | <strong>Test Procedure for AFW Pump Surveillance Found Inadequate</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1994, at 1504 hours, with the plant in Mode 1, at 100 percent power, Operations Department personnel, during an administrative review of surveillance procedures, determined that the monthly test procedure for the Auxiliary Feedwater DC hydraulic pump auto start actuation device did not fully meet the quarterly requirements of a 'Trip Actuating Device Operational Test' as defined in the plant's Technical Specifications. Operations surveillance procedures verify the DC hydraulic pumps start on a loss of hydraulic system pressure but do not verify that the pumps start at the proper hydraulic pressure nor provide instructions for adjusting the setpoint of the pressure switches as necessary. The cause of the event was the failure to adequately incorporate Technical Specification surveillance requirements into appropriate implementing procedures. Immediate action consisted of confirming that the setpoints of each pressure switch had been recently verified and adjusted by other testing over the previous month. revised to satisfy the requirements of the Technical Specifications and the lessons learned were sent to appropriate personnel. In addition, a review of all of these type of surveillances is being performed to ensure there are no other similar problems.
2131994015 | Haddam Neck | 06/16/1994 | 09/05/1997 | 9709160187 | <strong>Main Steam Safety Valve Pilot Valves Exceed Lift Setpoint</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1994, at 100 hours, with the plant in Mode 1 at 100 percent power, while performing setpoint verification testing on the pilot valves associated with four main steam safety valves, it was determined that four pilot valves were outside of their allowable setpoint tolerance. Both pilot valves for main steam safety valve MS-SV-24 lifted at a setpoint which was higher than permitted by Technical Specification 3.7.1.1 resulting in MS-SV-24 being declared inoperable. The cause of this event has been attributed to seat adhesion resulting from similar materials being used for both the pilot disc and nozzle. Immediate corrective action was to readjust the setpoints. Long term corrective action consisted of evaluating the replacement of the pilots with new pilots with discs constructed from alternate materials. This supplemental report is being submitted to retract originally proposed corrective actions that are no longer required due to the Haddam Neck Plant being in a permanently defueled state.
2131994016 | Haddam Neck | 07/07/1994 | 04/24/1996 | 9605030277 | <strong>Entry Into Technical Specification 3.0.3 Due to Inverter High Temperatures</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1994, at 1412 hours, with the plant in Mode 1 at 100 percent power vital inverter B transferred vital bus B to the alternate supply and shut down on over temperature. At 1445 the shift supervisor entered the switchgear room and noted that inverter A had also transferred and shut down on over temperature. The temperature in the switchgear room was 100 degrees F. Operators reduced the temperature in the room by opening doors and using temporary fans. Operators logged entry into Technical Specification 3.0.3 at 1431 hours due to loss of both inverters. At 1515 hours both inverters had cooled down and the alarms were reset. Both inverters were then restarted and both vital buses were transferred to their normal supply. The cause of the event was inadequate design of the over temperature feature of the inverters in that there can be considerable variation in the setpoint which is not adjustable. defeated using a temporary modification. Long term corrective action consists of modifying the over temperature feature to alarm only with an adjustable setpoint. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications due to entry into Technical Specification 3.0.3. This supplemental report describes changes in the corrective actions taken.
2131994017 | Haddam Neck | 07/05/1994 | 08/03/1994 | 9408100162 | <strong>Auxiliary Feedwater DC Pump Start Setpoint Found Low</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1994, at 0900 hours, with the plant in Mode 1 at 100 percent power, a monthly surveillance was performed to verify the setpoint of the 'A' train Auxiliary Feedwater control system DC hydraulic pump automatic start pressure switch. The Technical Specification minimum allowable value is greater than or equal to 934.5 psig. The as-found setpoint was 885 psig. A trend of significant setpoint deviations for these instruments was identified earlier this year (LER 94-008-00). The cause of the event is believed to be the location of the pressure switches. The pressure switch was recalibrated and the surveillance frequency was increased to weekly. Corrective action consists of replacing the switches with a more reliable type and changing their location during the current cold shutdown outage. Although instrument drift found during a surveillance typically is assumed to have occurred at the time of discovery, the disproportionate number of unexpectedly large setpoint deviations provides reasonable doubt that the switch was within its Technical Specification limits. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131994018 | Haddam Neck | 07/11/1994 | 01/24/1996 | 9601300162 | <strong>Manual Reactor Trip Due to Reactor Coolant Pump Motor Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1994, at approximately 0745 hours, with the plant in Mode 1 at 100 percent power, control room operators received a low oil level alarm for No.3 reactor coolant pump (RCP) motor accompanied by increased bearing temperatures. A load reduction was commenced at 0833 however, at 0907, at approximately 50 percent power, a manual reactor trip was initiated, with subsequent shutdown of the RCP, when bearing temperatures reached 200 degrees F. Immediately following the trip the No.1 feedwater regulating valve failed to close resulting in actuation of the steam generator overfill protection system which closed the feedwater regulating valve and its associated motor operated isolation valve. In addition, one of the main steam safety pilot valves appeared to be simmering. At 0956 a heat detector near #3 RCP alarmed. At 1004 a fire was observed on the pump's insulation. The fire brigade entered the containment and at 1010 the fire was extinguished. cracked PVC coupling on the line leading from the #3 RCP motor upper bearing oil reservoir to its lift oil pump. Corrective action consisted of redesigning the coupling and shimming the supports to eliminate stress. This supplemental report provides the results of the failure cause of the feedwater solenoid valves.
2131994019 | Haddam Neck | 07/28/1994 | 08/25/1994 | 9409060241 | <strong>RCP Oil Collection System Not in Compliance with Appendix R</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1994, at approximately 1555 hours, with the plant in Mode 5 (cold shutdown) a review of the July 11, 1994 RCP oil leak, which resulted in a plant trip and subsequent RCP lagging fire (LER 94-018-00), determined that the RCP oil collection system did not meet Appendix R design requirements in that the system was not capable of collecting oil from all potential leakage sites in the RCP lube oil systems. The cause of the event was the failure to account for RCP motor stator ventilation air flow in the design of the oil collection enclosures. The air flow prevented oil from dripping into the lower collection pan. Corrective action consisted of redesigning the oil collection system, including taking air currents into consideration. In general, this involved installation of shrouds around all potential leak sites and the addition of drain lines where appropriate. This event is reportable under 10CFR50.73(a)(2)(ii)(B) since it resulted in a condition that was outside the design basis of the plant.
2131994020 | Haddam Neck | 07/29/1994 | 08/25/1994 | 9409070001 | <strong>RCP Motor Platforms Determined to be Non-Seismic</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1994, with the plant in Mode 5 (cold shutdown), a review of the reactor coolant pump (RCP) motor oil lift system (LER 94-019-00) identified a potential unanalyzed seismic condition between the upper RCP platforms and the seismically qualified RCP motor lube oil system. On July 29, 1994, at 1434 hours, with the plant in Mode 5, an engineering review, based upon observations made during previous walkdowns, determined that the collapse of the RCP upper level platforms during a seismic event could potentially affect equipment that is required to either maintain their structural integrity or function during and following a seismic event. The cause of this condition was program failure in that the upper platforms were not reviewed for seismic interaction. Seismic interaction was not an original design basis for Haddam Neck. Corrective action consisted of removing the grating from the platforms and connecting the platforms with cable to existing RCP supports. A walkdown of miscellaneous,platforms in the containment building and other areas containing safety related equipment was conducted and no similar problems were identified. This event is reportable under 10CFR50.73 (a) (2) (ii) (A) since it resulted in an unanalyzed condition.
2131994021 | Haddam Neck | 08/15/1994 | 05/19/1997 | 9705230313 | <strong>Reactor Shutdown Due to Rod Position Indication Inaccuracies</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1994, at 1820 hours, with the plant in Mode 2 (startup); a reactor startup was terminated due to the individual rod position indication system (IRPI) for control bank B deviating from the group position indication system (group step counters) by more than 16 steps. Haddam Neck Technical Specifications 3.1.3.2 requires that the group position indication system and the bank average individual rod position indication system agree within +/- 16 steps. An attempt to adjust the affected control indication within tolerance failed and a reactor shutdown was initiated at 1835 hours in accordance with the Technical Specifications. Mode 3(hot standby) was entered at 1900 hours. The cause of the event was a combination of IRPI system inaccuracies including curve fit error at specific rod heights, indication drift due to reactor temperature effects on the secondary coil resistance and temperature related drift in the equipment drawers. Short term corrective action consisted of recalibrating all control rod indication. Long term corrective action was to replace the IRPI system during the 1996 refueling outage. Since the Haddam Neck Plant has permanently ceased power operation and all fuel assemblies have been permanently removed from the reactor, the proposed corrective action will not be implemented.
2131994022 | Haddam Neck | 08/17/1994 | 09/13/1994 | 9409200276 | <strong>Error Found in Large Break LOCA Analysis</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1994, at 2015 hours, with the plant in Mode 1 at 30 percent power (during a plant chemistry hold), an engineering analysis indicated that the peak cladding temperature during a large break loss of coolant accident (LBLOCA) could, for the analysis of record LBLOCA case (102% power, maximum allowable operating limits), exceed the 2200 degree F limit. This analysis was performed with an updated evaluation model that accounted for previously identified errors. The cause of this event can be attributed to the incorporation of previous identified error corrections and the use of tighter convergence criteria. Corrective action consisted of performing a supplemental analysis with a reduction in the allowable F Delta H from 1.60 to 1.44 and taking credit for the accrued burnup during cycle operation to effectively lower the initial stored energy. The results of the additional case yielded an acceptable peak cladding temperature < 2200 degrees F. An evaluation of past operation has shown that the plant operated with sufficient margin to the operating limits such that 2200 degrees F would not have been exceeded during a LBLOCA.
2131994023 | Haddam Neck | 08/25/1994 | 09/22/1994 | 9409280316 | <strong>Failure to Perform Reactor Coolant Sampling After Thermal Power Change</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1994, at 1024 hours, with the plant in Mode 1 at 100 percent power, technicians performing maintenance on the control rod position indication system inadvertently grounded a lead in the rod bottom relay circuit causing an automatic reactor and turbine load runback to approximately 90 percent power. Shortly thereafter the plant was stabilized at approximately 82 percent power. After returning the rod position indication system to service a load increase was commenced at 1241 hours and 100 percent power was reached at 1800 hours. Haddam Neck Technical Specifications require that an isotopic analysis for iodine be performed between 2 and 6 hours following a thermal power change exceeding 15 percent within a one hour period. On August 25, 1994, at approximately 1105 hours, with the plant in Mode 1, at 100 percent power it was determined that the iodine analysis had not been performed following the load runback. The cause of the event was inadequate communication between control room and chemistry personnel. Immediate corrective action consisted of reviewing reactor coolant system activity and gaseous effluent data obtained following the transient and no anomalies were found. Follow-up corrective action consisted of requiring compensatory reactor coolant sampling following all load runbacks.
2131994024 | Haddam Neck | 09/26/1994 | 10/21/1994 | 9411010350 | <strong>AFW DC Pump Start Setpoint Low Due To Start Switch Installation Error</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1994, at 0900 hours, with the plant in Mode 1 at 100 percent power, a surveillance was performed to verify the setpoint of the 'B' train auxiliary feedwater (AFW) control system DC hydraulic pump automatic start pressure switch. The setpoint of the automatic start of the DC powered pump on low hydraulic system pressure is listed in the plant's Technical Specifications as greater than or equal to 961 psig, with an allowable value of greater than or equal to 934.5 psig. The setpoint found during performance of the surveillance was 913.0 psig. The initial investigation identified an installation error as the cause of the setpoint deviation. When the pressure switch covers were installed, the micro switches were displaced by the force of the covers against the wires. Corrective action consisted of replacing the 'B' train pressure switch with a spare. In addition the wires to both the 'A' and 'B' train switches have been rerouted to eliminate the interference with the switch cover. The pressure switch had been installed six weeks earlier as part of a modification to improve system reliability.
2131994025 | Haddam Neck | 11/03/1994 | 11/30/1994 | 9412050248 | <strong>Core Cooling System Inoperable With RH-MOV-21 Open During Testing</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1994, at 1525 hours, with the plant in Mode 1, at 100% power, the normal opening of a motor operated valve (RH-MOV-21) during routine, monthly core cooling system surveillance testing was determined to be reportable. One issue was the possible diversion of low pressure safety injection flow (assuming check valve failure) during the injection phase of a loss of coolant accident (LOCA) coincidental with the opening of RH-MOV-21. Another issue was the valve being open during the containment sump recirculation phase. If RH-MOV-21 was left open during sump recirculation, containment pressure would eventually decrease to a point where the residual heat removal (RHR) pumps would take suction from the refueling water storage tank which could potentially cavitate/damage the RHR pumps. The cause of the event is attributed to inadequate technical review during procedural development because the procedure did not provide the necessary controls to ensure valve repositioning if an accident were to occur during testing. Short term corrective action consisted of revising the surveillance procedure to station a dedicated operator at RH-MOV-21, to manually close the valve, should a LOCA occur during testing. Long term corrective action consists of adding the check valve to the inservice testing program and determining if similar valve alignment issues exist.
2131994026 | Haddam Neck | 11/09/1994 | 04/24/1995 | 9505030296 | <strong>Technical Specification 3.0.3 Entered Due to Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1994, at 0745 hours, with the plant in Mode 1, at 100 percent power, a containment isolation valve (SS-AOV-955), which was being closed to support reactor coolant system sampling, failed to close and was declared inoperable. At 0830, following a review of the Technical Specifications, operators concluded that this failure constituted entry into Technical Specification Action Statement 3.0.3. At 0835, the valve indicated closed. At 0850, a power reduction was commenced. The valve was verified closed, deactivated, and isolated by closed manual valves upstream and downstream. Technical Specification 3.0.3 was exited at 0948 and the power reduction was stopped at approximately 82 percent power. On November 10, 1994, a temporary modification was installed which diverted the normal sampling path through another sampling penetration, thus, allowing SS-AOV-955 to remain in the closed position, fulfilling its safety function, without impeding normal plant operation. misapplication of packing and excessive packing load.
2131994027 | Haddam Neck | 12/13/1994 | 05/23/1995 | 9505310486 | <strong>Surveillance Frequency Exceeded for Verifying Offsite Power Source Operability</strong><br /><i>Abstract:&nbsp;</i>On December 13, 1994, at 2253 hours, with t e plant in Mode 1 at 100 percent power, Operations personnel discovered that the 12 hour surveillance for demonstrating the operability of the AC offsite sources had not been performed within the required timeframe. The surveillance frequency increased to once per 12 hours due to entry into Technical Specification Action Statement 3.8.1.1.b for scheduled emergency diesel generator maintenance. Upon discovery of the event, the surveillance was immediately initiated and successfully completed on December 13, 1994 at 2303 hours. The root cause of the event is attributed to a procedure deficiency (lack of detail) in that the shift turnover procedure for tracking Technical Specification action statements did not include a specific method to track and initiate event based surveillance requirements. Corrective action consisted of revising the procedure to provide a specific mechanism for identifying Technical Specification action statement required interim actions / surveillances as well as providing for recording when interim actions are actually performed. Long term corrective action includes a review of all Technical Specification event based surveillance requirements to ensure procedural mechanisms, where possible, are in place to initiate required actions.
2131994028 | Haddam Neck | 12/15/1994 | 01/12/1995 | 9501230129 | <strong>Potential Inoperability of Control Circuitry Due to Indicator Light Failure</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1994 at 1510 hours with the plant in Mode 1 at 100 percent power, the results of an engineering analysis indicated that a short circuit failure of full voltage (110 v and higher AC or DC) incandescent light bulbs in control circuits could conservatively be considered a consequential failure during a postulated seismic event. Additionally, a concurrent loss of offsite power and single failure of one Emergency Diesel Generator was postulated. This bulb failure could render control circuits in the Service Water System inoperable. This scenario could lead to insufficient service water to safety related heat loads and possible failure of the operating Emergency Diesel Generator. The cause of the event is that the original design of the Haddam Neck plant did not consider the short circuit failure of a full voltage indicating light as a credible failure for these control circuits. The initial corrective action was to remove the identified light bulbs on December 15, 1994. The control room operators were made aware of the monitoring options available to them in lieu of the indicating lights. On December 20, 1994, the removed incandescent bulbs were replaced with Light Emitting Diodes (LEDs). All identified control circuitry is no longer susceptible to the potential inoperability due to short circuit failure of incandescent light bulbs.
2131994029 | Haddam Neck | 12/28/1994 | 01/25/1995 | 9501310122 | <strong>Closure of Motor Control Center Tie Breakers Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1994 at 1015 hours with the plant in Mode 1 at 100 percent power, the results of an engineering evaluation indicated that the procedure for locating 480 VAC grounds incorrectly identified that closure of either MCC 3, 4 or 8 tie breakers would place the plant in an Action Statement per Technical Specification 3.8.3.1.1. Since no Action Statement exists in Technical Specification 3.8.3.1.1 which addresses the cross-tying of redundant busses via the MCC 3, 4 or 8 tie breakers, this condition is prohibited by the Haddam Neck Technical Specifications and is reportable under 10CFR50.73 (a) (2) (i) (B). The root cause of the event is a procedural deficiency due to an incorrect interpretation of the action statements for the Haddam Neck Plant Technical Specification 3.8.3.1. The initial corrective action was to instruct the operators to not shut the MCC 3, 4 or 8 tie breakers while attempting to locate a 480 VAC ground, to ensure that there would be no cross-tie of redundant busses. On December 29, 1994, the procedure for locating 480 VAC grounds was revised to remove the steps which had allowed operators to perform the cross tie of MCC 3, 4 or 8. The procedure biennial review process will be revised to ensure that Technical Specification Action Statements are clearly identified and applicable to the Limiting Condition for Operation. This event is being reported for historical purposes since the past practice of closing any of the three tie breakers for ground isolation was a reportable condition.
2191994001 | Oyster Creek | 01/13/1994 | 08/16/1994 | 9408250076 | <strong>Core Spray Piping Exceeding the Code Allowable Stresses Due to Original Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>During the design process for a Core Spray piping modification, it was discovered that the existing Core Spray Systems 1 and 2 minimum recirculation piping configuration did not meet the seismic and thermal expansion criteria allowables specified in the UFSAR. The root cause of this condition was inadequacy of the original design. <br /><br /> The safety significance is considered to be minimal, as the existing configuration meets the ASME Section III allowable seismic and thermal expansion criteria and satisfies the operability limits.<br /><br /> A modification presently scheduled for the upcoming 15R refueling outage will change the subject piping configuration to meet the UFSAR criteria.
2191994002 | Oyster Creek | 02/13/1994 | 03/14/1994 | 9403180030 | <strong>Alternate Diesel Fuel Supply Low level Per Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 2/13/94 at 2:00 p.m. it was observed that fuel oil level in the Main Fuel Oil Tank had dropped below the level necessary for Appendix R fire protection design requirements. Difficulty in receiving fuel shipments in a timely manner occurred due to the vendor's decision not to place trucks on dangerous roads when state officials banned trucks and vehicular traffic on most major roadways for significant periods of time due to hazardous conditions. Main Fuel Oil Tank Level dropped below 6'3' (system design minimum level for fuel oil pump suction pressure) to 6'0'. One shipment of 7590 gallons was received on 2/13/94 restoring level to above 6'3'and another shipment of 7800 gallons was received on 2/14/94. During the period of low tank level, the station blackout transformer was available to provide adequate power should a fire in the diesel generator fuel oil tank room occur with a loss of offsite power. Therefore, the safety significance of this event is considered minimal.
2191994003 | Oyster Creek | 04/05/1994 | 05/03/1994 | 9405160213 | <strong>Turbine Trip/Reactor Scram on High RPV Water Level Due to Erroneous Main Steam Flow</strong><br /><i>Abstract:&nbsp;</i>On 04/05/94 at 1550 hours a turbine trip and reactor scram occurred due to high reactor water level. Cause of the event was the failure of a proportional amplifier which provides a density correction signal to both A & B steam flow signals. This resulted in a false high steam flow signal which resulted in the feedwater control system increasing feedwater flow to the reactor which caused reactor water level to increase. When water level reached the high level turbine trip setpoint of 175', the turbine tripped and a reactor scram occurred as designed. The faulty electronic module was replaced and the feedwater flow control system was returned to operational status.
2191994004 | Oyster Creek | 04/22/1994 | 05/20/1994 | 9405260211 | <strong>Isolation Condenser Valve Closure Times Could Exceed Design Requirement</strong><br /><i>Abstract:&nbsp;</i>Calculations performed as part of the Generic Letter 89-10 Motor-Operated Valve (MOV) Program for the Isolation Condenser System (ICS) DC-powered isolation valves determined that the voltage available at the motor operator combined with the dynamic blowdown conditions existing during ICS high energy line break (HELB) isolation would produce valve closure times greater than the design condition of 60 seconds identified in the Final Safety Analysis Report, (FSAR) Section 6.3.2.5 and Table 6.2-12. The root cause of this condition was the reevaluation of the design capabilities of the motor-operated valves as a result of the Generic Letter 89-10 program recommendations. <br /><br /> The safety significance is considered to be minimal since the calculated valve stroke times for the subject valves meet the design criteria for establishing isolation times for high energy line breaks (HELB). These criteria are defined in Oyster Creek Technical Specification Section 4.5 Basis and Oyster Creek FSAR Section 6.3.2.5. <br /><br /> The 60 second isolation design time requirement in the FSAR will be revised for these valves, in conjunction with the results of the ongoing Oyster Creek Generic Letter 89-10 MOV Program.
2191994005 | Oyster Creek | 03/08/1994 | 11/30/1994 | 9412050152 | <strong>Casting Defects Discovered On Overhead Crane Flex Couplings</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1994, during an inspection it was discovered that the Turbine Building overhead 150, ton crane main hoist motor to gear box flex coupling exhibited casting defects and a through wall hole. On May 6, 1994, during an inspection it was discovered that the Reactor Building overhead 100 ton crane main hoist motor to gear box flex coupling exhibited casting defects and a crack. GPUN decided to voluntarily report these conditions. <br /><br /> The main hoist motor to gear box flex couplings have been installed on the overhead cranes since initial plant startup. Radiographic examination showed that the casting defects were shrinkage cavities. Subsequent sectioning of the defects showed the indications to be a lack of fusion defect that was part of the shrinkage cavity formed during solidification of the casting during fabrication. <br /><br /> Since the overhead crane meets NUREG-0612 requirements and no historical record of failure exists for the flex coupling, this condition is considered to have low safety significance. <br /><br /> The main hoist motor to gear box flex couplings have been replaced on both overhead cranes.
2191994006 | Oyster Creek | 05/23/1994 | 06/20/1994 | 9406300253 | <strong>Technical Specification Required Shutdown Due To Both Control Rod Drive Pumps Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>A technical specification required plant shutdown commenced on May 22, 1994 at 1110 hours when both Control Rod Drive (CRD) Pumps were found to be inoperable during surveillance testing. The plant was placed in cold shutdown at 0639 hours on May 23, 1994. The single discharge stop check valve on CRD pump 'B' would not close. This resulted in both pumps failing their operability test. <br /><br /> Valve failure was determined to be valve body erosion which allowed the disc to become lodged between a groove in the body and the valve seat. The safety significance was minimal. <br /><br /> The corrective action taken was to replace the stop check valve on CRD pump 'B' with separate check and globe valves. Performance of the new valve configuration will be evaluated during the run cycle.
2191994007 | Oyster Creek | 05/31/1994 | 06/30/1994 | 9407070274 | <strong>Reactor Scram Due To Personnel Error While Performing Switchyard Work</strong><br /><i>Abstract:&nbsp;</i>A reactor scram occurred due to modification work in the switchyard on May 31, 1994 at 1332 hours. While loosening a wire connected to an auxiliary relay of the 230 KV bus section differential relay, to install a Digital Fault Recorder, the relay actuated causing a generator and turbine trip resulting in a reactor scram. All five Recirculation Pumps tripped, two Electromatic Relief Valves opened and both Isolation Condensers initiated. All systems responded to the scram as expected and therefore, there was no safety significance to this event. The plant was placed in cold shutdown at 2210 hours on May 31. Corrective actions included placing the modification on hold pending engineering review and strengthening procedural controls over switchyard work.
2191994008 | Oyster Creek | 06/19/1994 | 07/19/1994 | 9407250247 | <strong>Electromatic Relief Valve Setpoints Exceed Technical Specification Limits Due to Drift</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1994, while performing an Electromatic Relief Valve (EMRV) Pressure Sensor surveillance, the as-found trip setpoints for the high pressure relief function on two EMRVs were above that specified in the Technical Specifications. The cause of this occurrence has been attributed to setpoint repeatability and instrument drift. The design setpoint repeatability allows the as-found value to be within 2.5 psig, of the Technical Specification limit. Previous surveillance records indicate that these instruments can drift due to changing plant and ambient conditions. <br /><br /> This occurrence is considered to have minimal safety significance as the automatic depressurization function of the EMRVs is not affected by these pressure switches, all five EMRVs would have actuated to relieve pressure, the Isolation Condenser System and turbine bypass valves were fully operable, and manual operation of the valves was not affected. Additionally, a recent Technical Specification Chance request was submitted demonstrating that an increase in the EMRV setpoints of 15 psig would have no impact on safety. The pressure switches were adjusted to actuate within the Technical Specification limit.
2191994009 | Oyster Creek | 07/01/1994 | 07/25/1994 | 9408030175 | <strong>Single Failure Potential In Diesel Generator Fast Start Logic Circuit due to Original Plant Design</strong><br /><i>Abstract:&nbsp;</i>As a result of design reviews for modifications to be implemented during the 15R refueling outage, an existing, design deficiency was identified. A postulated single failure of either of two terminal blocks, one located in each non-vital 4160 volt switchgear 1A and 1B, could render the automatic initiation of both Diesel Generator Systems inoperable. The safety significance of this postulated single failure mode is considered to be minimal based upon the very low probability of occurrence of this postulated single failure and the fact that the activation of the Appendix R Local Shutdown Panel would have isolated the single failure and allowed the operators to take manual control of Diesel Generator number 2. <br /><br /> Temporary modifications completed July 12 and 13, 1994, lifted leads associated with this logic. This eliminated the single failure concern.
2191994010 | Oyster Creek | 07/05/1994 | 08/04/1994 | 9408120015 | <strong>Reactor Shutdown Commenced Due to Loss Both Containment Spray Systems due to Biological Plugging</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1994 at approximately 1155 hours, both Containment Spray and Emergency Service Water systems were declared inoperable due to high differential pressure on the tube side of the heat exchanger due to biological plugging. A 30 hour plant shutdown was commenced per Technical Specifications. The heat exchangers were cleaned and returned to service prior to completion of the shutdown. The plant was returned to full power. The cause of this event was the release of Blue Mussel shells and other minimal biological debris into the heat exchangers.<br /><br /> Immediate corrective action was taken to clean, inspect, and return the heat exchangers to operability. Additional corrective actions are planned to inspect and clean the Emergency Service Water piping during the upcoming refueling outage and install inspection ports in the affected systems to assist in the early detection of possible future concerns.
2191994011 | Oyster Creek | 07/18/1994 | 08/17/1994 | 9408240093 | <strong>Containment Spray/Automatic Depressurization Panels Did Not Meet Seismic Criteria due to Original Design</strong><br /><i>Abstract:&nbsp;</i>During the course of a Seismic Qualification Utility Group (SQUG) walkdown, it was discovered that the control panels ER 8A and ER 8B housing the control logic for portions of the Automatic Depressurization System and Containment Spray Systems were not restrained sufficiently to ensure operability during a Safe Shutdown Earthquake. The root cause of this condition was the original design. <br /><br /> The safety significance is considered minimal as the probability of occurrence of an SSE in combination with a Loss of Coolant Accident was extremely low. which would have addressed this concern. <br /><br /> Immediate corrective action was taken to install modified supports for the panels. The SQUG walkdowns are continuing and if any additional corrective actions are identified, they will be evaluated and implemented through the SQUG program.
2191994012 | Oyster Creek | 07/24/1994 | 08/16/1994 | 9408290162 | <strong>Electromatic Relief Valve Setpoints Exceed Technical Specification Limits Due to Drift</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1994, while performing an Electromatic Relief Valve (EMRV) Pressure Sensor surveillance, the as-found trip setpoints for the high pressure relief function on two EMRVs were above that specified in the Technical Specifications. The cause of this occurrence has been attributed to setpoint repeatability and instrument drift. The design setpoint repeatability allows the as-found value to be within 2.5 psig of the Technical Specification limit. Previous surveillance records indicate that these instruments can drift due to changing plant and ambient conditions. <br /><br /> This occurrence is considered to have minimal safety significance as the automatic depressurization function of the EMRVs is not affected by these pressure switches, all five EMRVs would have actuated to relieve pressure, the Isolation Condenser System and turbine bypass valves were fully operable, and manual operation of the valves was not affected. Additionally, a recent Technical Specification Change request was submitted demonstrating that an increase in the EMRV setpoints of 15 psig would have no impact on safety. The pressure switches were adjusted to actuate within the Technical Specification limit.
2191994013 | Oyster Creek | 07/26/1994 | 08/25/1994 | 9409130486 | <strong>Technical Specification Shutdown Margin Limit Exceeded due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1994, the reactor was operating at approximately 100% power. To facilitate repairs to a nitrogen leak on HCU 06-19, the HCU was removed from service at 1930 hours with its associated control rod at the full out position. At 2220 hours, a determination was made that the shutdown margin criteria required by the Technical Specifications could not be satisfied with the rod removed from service in the full out position. <br /><br /> The cause of the event was human error. <br /><br /> The safety significance is minimal. Ample time would be available for manual actions to be performed to ensure the reactor core is shutdown following a postulated event where a face adjacent control rod failed to scram. There is a low probability of such an event occurring. <br /><br /> Immediate corrective action was taken to return HCU 06-19 to service. The Control Rod was then fully inserted to complete repairs. Additional corrective actions taken were discussing this event in detail with the personnel involved and including this event in the licensed operator training program.
2191994014 | Oyster Creek | 07/27/1994 | 08/25/1994 | 9409060084 | <strong>Reactor Triple Low Water Level Sensors Rendered Inoperable Due To Human Error</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1994 the reactor was operating at approximately 100% power. During performance of the Reactor Triple Low Water Level Test and Calibration, the equalizing valve on sensor RE18-B was inadvertently opened at approximately 1052 hours. This action coupled with sensor RE18-D being inoperable at the same time is a violation of plant technical specifications. <br /><br /> This event was caused by human error. An action was performed without using proper self-checking techniques. <br /><br /> The safety significance is minimal. A loss of redundancy not a loss of function occurred. There is a low probability of a LOCA occurring during the short time both sensors were inoperable. <br /><br /> The equalizing valve sensor on RE18-B was closed and the instrument line excess flow check valve was verified open. Additional corrective actions taken were discussing this event in detail with the personnel involved and including this event in the Instrument and Control technical training program.
2191994015 | Oyster Creek | 08/08/1994 | 09/07/1994 | 9409190161 | <strong>Reactor Shutdown Commenced due to Biological Plugging of Both Containment Spray Systems</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1994 at approximately 1100 hours, both Containment Spray and Emergency Service Water systems were declared inoperable due to lower than expected flow rates for Emergency Service Water pumps due to a release of biological material within the system that plugged the flow sensing element. A 30 hour plant shutdown was commenced per Technical Specifications. System 2 was then started, run, and declared operable after continued operation raised the indicated flow to within the operability limit. The reactor was returned to full power prior to completion of the shutdown. The cause of this event was determined to be the release of Blue Mussel shells and other biological debris into the system. <br /><br /> Immediate corrective action was taken to clean, inspect, and return the systems to operability. Additional corrective actions are planned to inspect and clean Emergency Service Water piping during the upcoming refueling outage and install inspection ports in the affected systems to assist in the early detection of possible future biological concerns.
2191994016 | Oyster Creek | 09/12/1994 | 04/06/1995 | 9504120120 | <strong>Local Leak Rate Test Results In Excess of Technical Specification Limits Due to Component Wear</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1994, Local Leak Rate Testing (LLRT) results indicated that Main Steam Isolation Valve NS04B exceeded the leak rate limit of 12.08 SCFH at 20 psig as specified in the plant Technical Specifications. The leak rate was quantified as 36.91 SCFH at 20 psig.<br /><br /> The cause of this occurrence was attributed to a combination of component installation and wear. The safety significance of this event is considered minimal as the total penetration leakage would have been limited by Main Steam Isolation Valve NS03B in the same steam header. Maintenance was performed on the valve to restore seat integrity. The as left local leak rate test, performed prior to startup, was satisfactory.
2191994017 | Oyster Creek | 09/15/1994 | 10/06/1994 | 9410120281 | <strong>Spurious Actuation Of Reactor Triple Low Water Level Sensors</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1994, the reactor was in a cold shutdown condition during a refueling outage. While water flushing a reactor water level instrument reference leg line tap inside the reactor vessel, two reactor triple low water level sensors spuriously actuated causing an automatic reactor building closed cooling water system valve to isolate flow returning from the drywell at approximately 1034 hours. <br /><br /> This event was caused by a work package inadequacy. Prerequisites to disable the function of the instruments connected to the reference leg line were not communicated to the contractor performing the work. <br /><br /> This event was not safety significant since the isolation function of this valve is not required to be operable during the present plant conditions. <br /><br /> The isolated valve was reopened and all instruments connected to the reference leg lines were isolated. Additional corrective actions will include communicating lessons learned from this event to appropriate personnel who have responsibility for work package preparation.
2191994018 | Oyster Creek | 09/24/1994 | 10/21/1994 | 9410270217 | <strong>Inadvertent Isolation of Containment Exhaust Valves Due to Improper Switch Position</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1994 the reactor was defueled during a refueling outage. During performance of the High Range Radiation Monitoring System calibration, the Channel I monitor function selector switch was inadvertently turned to the OFF position causing four automatic drywell and torus nitrogen inerting/ventilation exhaust isolation valves to close at approximately 1026 hours. <br /><br /> This event was caused by a fabrication deficiency. The monitor function selector switch knob does not have an indication on the side of the knob to show an accurate position reading. <br /><br /> This event was not safety significant since the isolation function of these valves are not required to be operable during present plant conditions.<br /><br /> The four isolated valves were reopened. Additional corrective actions include purchasing a monitor function selector switch knob with a position indicator and revising the surveillance procedure.
2191994019 | Oyster Creek | 10/19/1994 | 11/21/1994 | 9412010179 | <strong>SBO Power Source Unavailable Due To Inadequate Design Of Modification Due To Inadequate Administrative Control</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1994, a Station Blackout (SBO) power supply failed to start during a functional test. Subsequent investigation determined a control power modification made in May, 1994 without GPUN review prevented the unit from starting in a loss of power mode. Interruption of AC power to a trip circuit caused a unit trip. An uninterruptible power supply (UPS) was installed to maintain the trip circuit energized. The agreement between GPUN and the operator of the power supply (JCP&L)was revised to include review and testing of unit modifications.
2191994020 | Oyster Creek | 11/10/1994 | 12/07/1994 | 9412130247 | <strong>Inadvertent Isolation Of Containment Exhaust Valves Due To Operator Performance</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1994 the reactor was being refueled during an outage. During performance of the Containment High Range Radiation Monitoring System test, the Channel 2 monitor was inadvertently tested causing two automatic drywell ventilation exhaust isolation valves to close. <br /><br /> This event was caused by an operator performance deficiency. The operator intended to test Channel 1 and did not self-check sufficiently, inadvertently testing Channel 2. <br /><br /> This event was not safety significant since the isolation function of these valves was not required to be operable during plant conditions at the time of the event. <br /><br /> The two isolated valves were reopened. Additional corrective action include a human engineering review of the panel layout, procedural instructions and operator training.
2191994021 | Oyster Creek | 11/19/1994 | 12/15/1994 | 9412230053 | <strong>Automatic Reactor Scram Due To High Reactor Recirculation Flow Caused By Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1994, during a refueling outage, an unexpected reactor scram occurred. While performing troubleshooting and a wiring repair on the Reactor Recirculation Flow Control System computer, an inadvertent introduction of a low speed demand succeeded by a high speed demand from the digital control system (DCS) led to total recirculation flow exceeding the high flow scram setpoint. <br /><br /> The cause of this event was personnel error due to misoperation of the DCS computer. <br /><br /> There is no safety significance to this event. The high flow scram feature was believed necessary to terminate a flow increase transient during power operation. GPUN has since proved that this limiting safety system setting is not necessary and has obtained NRC approval to remove this feature from the technical specifications.<br /><br /> Interim corrective action has been taken to ensure DCS maintenance activities have technical support and supervising personnel present during such activities. Also, the conduct of maintenance activities will be proceduralized to help minimize misoperation/misapplication of the DCS diagnostic tools.
2191994022 | Oyster Creek | 12/19/1994 | 01/18/1995 | 9501300048 | <strong>Primary Containment Leak Rate in Excess of Technical Specification Requirements Due to Maintenance Procedure Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1994, while performing a reactor startup following the 15R refueling outage, Lt was noted that the amount of nitrogen being added to the primary containment was higher than normal. It was subsequently determined that leakage from the primary containment exceeded the Technical Specification limits. A reactor shutdown was initiated and an Unusual Event was declared. A subsequent evaluation determined that the Drywell vent and purge valves were leaking past their seats. The valves were declared inoperable. The reason for the seat leakage was determined to be valve actuator misadjustment.<br /><br /> Immediate corrective action was taken to readjust the valve stroke length and perform a local leak rate test required to declare the valves operable. The reactor shutdown and Unusual Event were terminated. <br /><br /> The cause of this event was determined to be failure to comply with existing maintenance administrative procedures. Long term corrective actions are planned which will raise the sensitivity and understanding of maintenance personnel to the need for procedure compliance.
2201994001 | Nine Mile Point 1 | 08/09/1992 | 02/04/1994 | 9402150199 | <strong>Violation of Technical Specification Surveillance Requirements Caused by Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1994, plant management at the Nine Mile Point Nuclear Station Unit 1 (NMP1) determined that NMP1 had previously violated Technical Specification Surveillance Requirements. Specifically, prior to reactor restart on August 9, 1992, NMP1 maintenance personnel failed to properly calibrate Intermediate Range Monitors (IRMs) as required by Technical Specification Surveillance Requirements 4.6.2.a(9) and 4.6.2.g(2). Similar errors were subsequently repeated five (5) times between September 3, 1992 and April 14, 1993. Further review of this event determined that NMP1 committed the same error for the Source Range Monitors (SRMs) at the same times, in violation of Technical Specification Surveillance Requirement 4.6.2.g.(1). <br /><br /> The root cause of this event is cognitive personnel error by the Maintenance Manager. Technical Specification Surveillance Requirements and definitions were misinterpreted and an improper procedure change to calibrate the SRMs and IRMs was approved. <br /><br /> Immediate corrective actions included restoring the previous calibration process to meet the Technical Specification Surveillance Requirement for SRM and IRM calibrations.
2201994002 | Nine Mile Point 1 | 04/05/1994 | 05/05/1994 | 9405090235 | <strong>Reactor Scram Caused by Main Generator Trip as a Result of a Failed Output Breaker Protective Relay</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1994 at 0451 hours, Nine Mile Point Unit 1 (NMP1) received an automatic scram initiation signal resulting in a full reactor scram. While preparing for maintenance on the #9 345KV line disconnect switch, breaker R925 was opened, at which time the #8 line breaker R915 tripped unexpectedly. This resulted in a main generator trip and full reactor scram. At the time of the event, the plant was operating at 100 percent of rated thermal power.<br /><br /> The apparent root cause of this event was an electrical short in the polarizing circuit within the distance directional relay 21B-1. <br /><br /> Immediate operator actions included commencing scram recovery activities and initiating a controlled plant cooldown. Additional corrective actions include: 1) replacing the faulty relay; 2) verifying the correct operation of a similar relay; and 3) training operators to identify the precursor to this event.
2201994003 | Nine Mile Point 1 | 04/06/1994 | 01/09/1996 | 9601170255 | <strong>Missed Technical Specification Surveillance Caused By Inadequate Change Management</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1994 at 1517 hours, Maintenance Department personnel at the Nine Mile Point Nuclear Station Unit 1 (NMP1) discovered a violation of Technical Specification Surveillance Requirements. Specifically, the drywell personnel air lock and the drywell emergency air lock had not been leak rate tested every six months as required by Technical Specifications. At the time of discovery, NMP1 was in cold shutdown for a forced outage and primary containment integrity was not required.<br /><br /> The root cause of this event was inadequate change management. Personnel failed to maintain the Preventive Maintenance-Surveillance Test (PMST) database (the scheduling tool for preventive maintenance and surveillance testing activities) consistent with the frequency specified in the surveillance procedure and the Technical Specification requirements. <br /><br /> Corrective actions include correcting the PMST database frequency codes, performing the appropriate leak rate tests, strengthening the process for implementing Technical Specification amendments and changing the PMST database, providing training to individuals tasked with updating and changing the PMST database and issuing a Lessons Learned Transmittal.
2201994004 | Nine Mile Point 1 | 04/11/1994 | 05/09/1994 | 9405170193 | <strong>Reactor Scram on Intermediate Range Monitor High Flux Caused by Spiking Electrical Noise</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1994, at 1920 hours, Nine Mile Point Unit 1 (NMP1) received an automatic reactor scram initiation signal resulting in a full scram. While performing a reactor startup, a spurious Intermediate Range Monitor (IRM) 'high-high' neutron flux trip occurred. At the time of the event, the plant was being started up with the mode switch in the 'STARTUP' position; a reactor heat up was in progress, and reactor pressure was 810 pounds per square inch gauge (psig). <br /><br /> The apparent cause of this event was determined to be IRM spiking caused by electrical noise generated from actuation of relays external to the neutron monitoring system.<br /><br /> Immediate operator actions included commencing scram recovery activities. Additional corrective actions included determining the cause for the IRM spiking and installing noise suppression circuits to correct the probable causes.
2201994005 | Nine Mile Point 1 | 07/11/1994 | 08/10/1994 | 9408220236 | <strong>Reactor Scram on High Neutron Flux Caused by an Electrical Pressure Regulator Malfunction</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1994 at 0001 hours, with the reactor mode switch in the 'RUN' position and reactor power at approximately 85 percent, Nine Mile Point Unit 1 (NMP1) experienced a Reactor Protection System (RPS) actuation. Specifically, a full reactor scram was caused by neutron flux exceeding the flow-biased Average Power Range Monitor (APRM) scram setpoint. Additionally, the turbine tripped and the High Pressure Coolant Injection (HPCI) System initiated on the turbine trip, as expected. <br /><br /> The immediate cause of this event was a malfunction in the Turbine Control System's Electrical Pressure Regulator (EPR). Extensive troubleshooting of the EPR failed to pinpoint the exact malfunction but has narrowed the cause of the malfunction to selected components within the EPR. A formal root cause analysis will be completed when failure analysis of these components is obtained from the EPR vendor. <br /><br /> The EPR's operational amplifier and steam line resonance compensator were replaced. Additional Data Acquisition & Analysis System (DAAS) points were added to the steam line resonance compensator for on-line monitoring. The mercoid switch for #12 Feedwater Pump suction pressure was replaced. An electrical connector for control rod position indication was repaired.
2201994006 | Nine Mile Point 1 | 10/27/1994 | 01/16/1995 | 9501250185 | <strong>Violation of Technical Specification Requirements for Reactor Building Integrity Because of Inadequate Original Design</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1994 at 10:30 hours, with the mode switch in 'RUN' and reactor power at approximately 76 percent thermal, it was discovered that Nine Mile Point Unit 1 (NMP1) was operating outside of a Technical Specification requirement for Reactor Building integrity. Specifically, it was assumed that the Technical Specification limitation on air in-leakage may have been exceeded as a result of discovering that the cover plates were missing from two (2) floor drains in the cask washdown area of the refueling floor in the Reactor Building. <br /><br /> The cause of this event was determined to be an inadequate original design in that maintaining secondary containment integrity was not identified as one of the drain system functions. A contributing cause was a personnel error which involved a modification, without adequate review, changing the cover plates to grates. <br /><br /> Corrective actions for this event include insertion of mechanical plugs in the drain lines, reinstallation of floor drain covers, review of other Reactor Building drain lines, and revision of appropriate procedures. A radiological analysis was completed subsequent to the original submittal of this report. The radiological analysis demonstrates that radiation doses resulting from an accident would remain less than the limits of 10CFR100 and General Design Criterion 19 of 10CFR50.
2201994007 | Nine Mile Point 1 | 11/02/1994 | 12/02/1994 | 9412120282 | <strong>Automatic Reactor Scram on High Neutron Flux Signal Caused by Inadequate Work Practices During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1994 at 1004 hours, Nine Mile Point Unit 1 (NMP1) received a full automatic reactor scram initiation signal. Specifically, while performing a scheduled surveillance test on the Average Power Range Monitor (APRM) Flow Converters, a high neutron flux trip signal was inadvertently initiated on Reactor Protection System (RPS) Channel 12 while a manual one-half scram signal was inserted on RPS Channel 11. Additionally, High Pressure Coolant Injection (HPCI) initiated on low reactor water level. <br /><br /> The root cause of the event is failure of the Instrument and Control (I&C) technicians to use good work practices while implementing the self-checking and peer verification processes. A contributing factor was that the flow converter panel was not labeled with the RPS channel designation. Additionally, two weaknesses were identified. First, Control Room Operations oversight of this critical activity was inadequate because Management's expectations did not require the appropriate level of oversight. Second, the sequence of steps in the surveillance procedure for inserting one-half scrams was not adequate. <br /><br /> The technicians involved were counseled. I&C technicians were retrained in the self-checking and peer verification processes. The flow converter panels have been labeled with the RPS channel identification. Operations Management will develop new expectations for control room Operations personnel with respect to oversight of critical activities. Procedures have been revised regarding inserting one-half scrams during certain surveillances. A Rod Position Indication System probe buffer card has been replaced.
2371994001 | Dresden 2 | 01/05/1994 | 02/04/1994 | 9402100240 | <strong>Process Line Primary Containment Isolation Valves Never Subjected to Type C Local Leak Rate Test due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At approximately 1100, on January 5, 1994 with Unit 2 operating at 100% power, as a result of a walkdown of primary containment penetration X-146 it was determined that a process line, which taps off an instrument line upstream of the excess flow check valve, had primary containment isolation valves which had never been given a proper 10 CFR 50, Appendix J Type C Local Leak Rate Test (LLRT). Upon identification of this problem, the instrument line was isolated at the containment penetration rendering the 2A Core Spray loop line break detection instrumentation inoperable. Subsequently, the 2A Core spray loop was declared inoperable which placed Unit 2 in a 7 day Limiting Condition for Operation (LCO). The process line, which was used to obtain Reactor Coolant Samples, had rarely been used since Unit 2 Start Up Testing. This sample line, which did not show up on a Piping and Instrumentation Diagram, was determined to be an undocumented plant modification. The safety significance of the leakage past the sample line isolation valves was minimal, since the isolation valves leaked 0 scfh when given a Type C LLRT. The leakage out of containment, as determined on a minimum pathway basis, would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded in the event of a LOCA. The sample line was subsequently cut and capped and the instrument line placed back in service.
2371994002 | Dresden 2 | 01/09/1994 | 02/03/1994 | 9402170336 | <strong>Common Supports for PT 2-1459-A do not Meet SAR Allowables Due to a Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1994, at 1500 hours, an Engineering evaluation which was being performed to remove an unauthorized modification determined that the piping supports associated with primary containment penetration X-146 did not meet design requirements stated in the UFSAR. The supports affected piping for Differential Pressure Transmitter dpt 2-1459-A, which senses Core Spray System Sparger integrity, as well as other instrumentation lines on the common supports. An operability determination was performed to assess the impact of the supports that did not meet design requirements. This evaluation found that the supports and attached piping would have remained intact during a seismic event. Therefore, the safety significance was minimal. Corrective actions will include upgrading the support configuration during the next refueling outage. \\\\\\
2371994003 | Dresden 2 | 02/17/1994 | 03/17/1994 | 9403210183 | <strong>High Pressure Coolant Injection >BJ! Minimum Flow Valve Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1994, at 1245 with Unit 2 at 99% rated core thermal power, the Unit 2 High Pressure Coolant Injection (HPCI) Motor Operated (MO) minimum flow valve 2-2301-14 breaker trip ed during performance of Special Procedure: (SP) 93-12-119, 'Generic Letter 89-10 dP Testing'. The tripped breaker resulted in the minimum flow valve being inoperable. The Unit 2 HPCI System was already Out-of-Service (OOS) for the performance of the special procedure. The breaker was replaced and the HPCI system was returned to service on February 20, 1994, at 0041 hours. The cause of the trip was determined to be failure of the terminal block due to a loose lug. The breaker was inspected and replaced. Other breakers on the bus were inspected for loose lugs and none were found.
2371994004 | Dresden 2, Dresden 3 | 01/24/1994 | 02/22/1994 | 9403040105 | <strong>High Pressure Coolant Injection System Steam Drain Line Isolation Valves Installed Backwards Due to Construction Error</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1994 at 1140 hours, with Unit 2 at 88% and Unit 3 at 74% rated core thermal power, it was determined that the HPCI steam drain line isolation valves would not open under LOCA conditions. The unit 3 valve was replaced on January 15, 1994 as a result of leakage through the valve. During this valve replacement, the original valve was discovered to be installed backwards. When the valve was replaced, it was installed in the proper direction. The installed orientation of the Unit 2 valve was verified to be incorrect on January 17, 1994 at approximately 0800 hours. An engineering evaluation determined that, since a stronger spring had been installed on May 5, 1993, the Unit 2 valve would perform its design function. Prior to these dates, the valves would not have functioned as required. The safety significance was minimal because the HPCI system was capable of initiation during an event. A nuclear work request to re-orient the unit 2 valve has been initiated. \\\\\
2371994005 | Dresden 2 | 04/30/1994 | 04/23/1997 | 9705070311 | <strong>Manual Reactor Scram Due to Loss of Instrument Air Resulting from Air Receiver Pipe Failure Caused by Improper Installation of Threaded Pipe During Initial Construction</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1994 at 2334, Unit 2 was manually scrammed from 99% power due to rapid depressurization of the Instrument Air (IA) header. All systems operated as expected. The loss of Instrument Air was due to a mechanical failure of the threaded portion of the inlet air supply piping to the 2A IA Receiver Tank. Pipe failure is attributed to pipe wall thinning from moisture induced corrosion compounded by the original construction threaded pipe installation which was contrary to the original plant (butt weld) design specification. The 2A receiver tank and inlet pipe were replaced and the compressor returned to service. The safety significance of this event was minimal. The ADS system was available for reactor pressure relief and the LPCI and Core Spray systems were available for core cooling. A previous reactor scram on loss-of-instrument-air, reported on January 16, 1993, was caused by dryer and backup air supply system failures. Corrective actions from that event would not have prevented this event. <br /><br /> This event is reportable per 10 CFR 50.73(a)(2)(iv), any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS).
2371994006 | Dresden 2 | 02/05/1994 | 11/30/1994 | 9412050207 | <strong>Unit 2 Shutdown Cooling Pump Motors did not have Relay Setting Orders Reviewed Prior to Motor Installations due to Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>At approximately 1300 hours on February 5, 1994 with Unit 2 at 99% power, it was discovered that the installed Unit 2 Shutdown Cooling Pump Motors, which were replacement motors, had different electrical characteristics than the original motors. It was determined that a review of the protective relay setpoints for these motors had not been performed.<br /><br /> Subsequent engineering analysis indicated that the relay setpoints should be reset to accommodate the installed motors. The analysis also indicated that the coordination between the motor feed breakers and the main feed breakers to ESS buses 23-1 and 24-1 had not been affected. The ESS buses were never in jeopardy of becoming unavailable due to a fault at or on any of the Shutdown Cooling Pump motors. The protective relay setpoints were reset and the pumps declared operable.
2371994007 | Dresden 2 | 03/30/1994 | 03/28/1996 | 9604020102 | <strong>Potentially Unanalyzed Control Room Habitability Condition Due to Purge Mode</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1994, at 1700 hours, with Unit 2 at 100% rated core thermal power and Unit 3 in refueling outage (D3R13), a System Engineer noticed that the Control Room heating ventilation and air conditioning (HVAC) system was operating in the outside purge mode. In the outside purge mode, the Control Room HVAC system takes greater than 2000 cfm outside make-up air. However, the Control Room habitability was analyzed based on normal outside make-up air flow rate of 2000 cfm. As a result of the Control Room habitability analysis, the existing operating procedure requires that the Control Room HVAC system be isolated within 40 minutes of receiving a high radiation signal from the Reactor Building vent duct to minimize the radiation dose received by the Control Room personnel. Therefore, upon review of the Control Room habitability study, it was determined that the Control Room HVAC system was operated in a potentially unanalyzed Control Room habitability condition. The Control Room HVAC system was immediately taken to the normal mode and was restricted from use in outside purge mode by placement of an equipment out-of-service. The safety significance of this event is minimal because the back up emergency safety related PVAC train 'B' and the air filtration unit were operable and in standby to meet the Control Room habitability requirements.
2371994008 | Dresden 2 | 04/09/1994 | 04/18/1994 | 9405090087 | <strong>Yarway Reactor Water Level Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On April 09, 1994, at 1100 hours, with Unit 2 at 99% rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 0500-03, Reactor Water Level ECCS Initiation Indicating Switch Calibration, level switch 2-263-72C contact 5-6 tripped outside of the Technical Specification (TS) limits. Level Indicating Switch (LIS) 2-263-72C is part of the High Pressure Coolant Injection (HPCI) [BJ] and Low Pressure Coolant Injection (LPCI) [BM] Loop 1, -59' RWL initiation one out of two/twice logic. The TS limit is 159.375' water column (WC), however, the switch was actuated closed at 159.81, WC. The switch was adjusted to a revised setpoint. The necessary redundant switches were available during the event allowing both systems to remain operable. Previous events involving the failure of similar Yarway configurations are documented in 'Operability Assessment' of February 17, 1994, (Chron 0124505) written in response to LER 93-031/050237 and LER 94-007/050249. Input to the Operability Assessment included two years of calibration data on the Yarway instruments.
2371994009 | Dresden 2 | 03/30/1994 | 04/22/1994 | 9404290059 | <strong>Unit 2 Isolation Condenser Manually Isolated Due To Operator Action</strong><br /><i>Abstract:&nbsp;</i>At 1355 on March 30, 1994, a report of a possible leak on the Unit 2 Isolation condenser inlet line was received in the Unit 2 Control Room. operations immediately isolated the Isolation Condenser [BL]- Further investigation revealed the Isolation Condenser was not the source of the leak and was capable of performing its design function. The removal of the Isolation Condenser from service is reportable per the 10CFR50.73(a)(2)(v) statement 'Any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat'. The Operators acted in a prudent and conservative manner during the conduct of this event and an error or malfunction of a safety system did not occur.
2371994010 | Dresden 2, Dresden 3 | 04/12/1994 | 08/14/1995 | 9508210208 | <strong>HPCI Room Cooler Fan Minimum Starting Voltage Above Second Level Undervoltage Relay Setpoint</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1994, a review of calculation 8982-19-19-2 was performed in response to an NRC unresolved item in Engineering and Technical Support Inspection 237(249) 94-003. The review revealed that the control circuit contactor (motor starter) minimum starting voltage for the High Pressure Coolant Injection (HPCI) Room Cooler Fans was above the set point for the second level degraded voltage relay settings. The cause was an inadequate design calculation and review. The existing Size 2 full voltage non-reversing contactors have been replaced with new General Electric Series 300 Size 1 contactors. By reducing the contactor size and improving the pickup of the coil, the burden on the control circuit is reduced and the contactor voltage is improved to the extent that the existing set points for the second level degraded voltage relays do not affect the operation of the HPCI Room Cooler Fans.
2371994011 | Dresden 2, Dresden 3 | 05/04/1994 | 06/03/1994 | 9406070140 | <strong>Auto-start of 2/3 Emergency Diesel Generator Due to Operator Error.</strong><br /><i>Abstract:&nbsp;</i>At 0908 on May 04, 1994, while performing 4kV breaker checks on Bus 33 per a Special Procedure (Modification Test for Bus 33 Breakers and Stationary Switch Replacement), Bus 33 and Bus 33-1 were inadvertently de-energized. The 2/3 Emergency Diesel Generator (EDG)[EK] auto-started and closed onto Bus 33-1. <br /><br /> As part of the Special Procedure, the Nuclear Station Operator (NSO) was switching the Bus 33 feed from Transformer TR-31 (Unit Aux Transformer) to TR-32 (Reserve Aux Transformer). The NSO closed in the feed breaker from TR-32, but failed to notice that the breaker immediately went to its trip-free condition. The NSO then opened the feed breaker from TR-31, de-energizing Bus 33, which caused the Unit 2/3 EDG to start on Bus 33-1 undervoltage. The Unit 2/3 EDG started normally, closed-in to Bus 33-1, and was loaded and run for approximately 20 minutes. Power to Bus 33 was then restored from TR-31, and the Unit 2/3 EDG was secured. <br /><br /> The feed breaker from TR-32 went to its trip-free position because the TR-32 undervoltage relays had not been reset from a previous test.
2371994012 | Dresden 2 | 04/18/1994 | 12/12/1995 | 9512180065 | <strong>Inadvertent Auto Start of 2A Core Spray Pump Due to Personnel Error Supplement</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1994 at 1741, with Unit 2 at 99% rated core thermal power, the 2A Core Spray Pump (CS) started inadvertently during modification work in the 2/3 Diesel Generator (DG) cubicle at Bus 23-1. This resulted in core spray flow through the minimum flow lines. <br /><br /> While transferring wires on the auxiliary switch, the worker lost control of a wire, and its lug subsequently shorted across two other energized terminals. He taped up the loose wire lug and stopped work. Operators in the control room responded to alarms, checked drywell pressure and reactor water level as proper and then opened the 2A CS Pump Circuit breaker and placed it out-of-service. After an investigation, the wiring was completed and tested, and the 2A CS Pump was returned to service at 2009 hours.
2371994013 | Dresden 2 | 05/23/1994 | 06/22/1994 | 9406290081 | <strong>Auto Initiation of Diesel Generator 2/3 During Modification Due to Design Error</strong><br /><i>Abstract:&nbsp;</i>During preparations for an operations surveillance, an inadvertent automatic start of the Unit 2/3 Diesel Generator was received when the newly installed Bus 33-1 to Bus 23-1 bus tie breaker was closed. Investigation of the event identified that the recently installed modification contained a design discrepancy that was undetected by the design checking process or installation and testing personnel. The discrepancy resulted in the control circuits for the Bus 33-1 breaker of the Bus 33-1 to Bus 23-1 Tie, the Bus 33-1 Main Feed breaker, and the Unit 3 automatic start of the Unit 2/3 Diesel Generator being superimposed. This wiring error did not prevent any system from providing its safety function. The immediate corrective actions included diagnosis of the wiring discrepancy, development of a work package to correct the discrepancy, and an additional design and field wiring review prior to successful completion of the operations surveillance. <br /><br /> Additional corrective actions include a lessons learned notification to the design organization at this and other company sites reinforcing the expectations and requirements of the design program.
2371994014 | Dresden 2 | 05/23/1994 | 07/28/1995 | 9508020218 | <strong>Tech Spec LCO Not Met Due to Inadequate Diesel Generator Maintenance</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1994, the Unit 2/3 Emergency Diesel Generator (EDG) had been made administratively inoperable due to the service water temperatures rising above 82 degre es. During the performance of a Tech Spec required operability demonstration of the Unit 2 EDG due to the Unit 2/3 EDG being administratively inoperable, the Unit 2 EDG tripped on overspeed. The Unit 2 EDG was declared inoperable and Dresden Unit 2 entered a 24 hour Limiting Condition for operation (LCO). System Engineering was requested to assist in the overspeed trip investigation. Operations monitored the service water temperature and once they were verified to have dropped below 83 degrees, the 2/3 EDG was demonstrated operable. continued on a 7 day LCO. <br /><br /> The root cause of the governor failure was attributed to the compensation valve being out of adjustment due to less then optimal preventative maintenance. The current preventative maintenance and general surveillance tracking program currently in place ensures that the governors are inspected on a 2 cycle frequency in accordance with the EDG owners group recommended maintenance program. The governor was replaced under work request 26179 and the Unit 2 EDG was successfully demonstrated operable on May 25, 1994 at 2237 hours.
2371994015 | Dresden 2 | 06/27/1994 | 07/22/1994 | 9407280102 | <strong>Yarway Reactor Water Level Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On June 27,1994, at 1000 hours, with Unit 2 at 99% rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 0500-03, Reactor Water Level ECCS Initiation Indicating Switch Calibration,level switch 2-263-72C contact 7-8 failed to trip. Level Indicating Switch (LIS) 2-263-72C contact 7-8 provides Core Spray initiations, ADS permissives, and an input to the Diesel Generator start logic on decreasing low low water level. The safety function of the instrument is to sense decreasing water level prior to or at -59' indicated which is 84' above the top of the active fuel. The switch was adjusted to an acceptable value of 153.8' WC. The necessary redundant switches were available during the event allowing these systems to remain operable. Previous events involving the failure of similar Yarway configurations are documented in 'Operability Assessment' of February 17, 1994, (Chron 0124505) written in response to LERS 93-031/050237 and 94-007/050249. Input to the Operability Assessment included two years of calibration data on the Yarway instruments. Additionally LER 94-008/050237 dated April 18, 1994 and LER 94-016/050237 dated June 16, 1994 documents similar events for the same instrument.
2371994016 | Dresden 2 | 05/30/1994 | 06/16/1994 | 9407010181 | <strong>Yarway Reactor Water Level Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1994, at 1540 hours, with Unit 2 at 90% rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 0500-03, Reactor Water Level ECCS Initiation Indicating Switch Calibration,level switch 2-263-72C contact 5-6 tripped outside of the Technical Specification (TS) limits. Level Indicating Switch (LIS) 2-263-72C is part of the High Pressure Coolant Injection (HPCI) [BJ] and Low Pressure Coolant Injection (LPCI) [BM] Loop 1, -59' Reactor Water Level initiation one out of two/twice logic. The TS limit is 159.375' water column (WC), however, the switch was actuated closed at 171.2' WC. The switch was adjusted to an acceptable value of 153.6' WC. The necessary redundant switches were available during the event allowing both systems to remain operable. Previous events involving the failure of similar Yarway configurations are documented in 'Operability Assessment' of February 17, 1994, (Chron 0124505) written in response to LERS 93-031/050237 and 94-007/050249. Input to the Operability Assessment included two years of calibration data on the Yarway instruments. Additionally LER 94-008/050237 dated April 18, 1994 documents a similar event for the same instrument.
2371994017 | Dresden 2 | 07/04/1994 | 07/27/1994 | 9408050115 | <strong>HPCI System Suction Swap due to Incorrectly Installed Jumpers</strong><br /><i>Abstract:&nbsp;</i>On July 4, 1994 at 0957 hours, with Unit 2 at 87% rated core thermal power, while draining the 2/3B Condensate Storage Tank (CST) the High Pressure Coolant Injection System swapped from the normal 2/3 CST suction path to the Suppression Pool suction path. An operator was dispatched to the CST level switch area to investigate the potential cause for the suction swap. It was determined that the jumpers installed under Out of Service 1994 0-0385, 2/3B Cst Draining, were installed on the Unit 3 side of the level switches instead of on Unit 2. Unit 3 was in refuel at the time with the HPCI system inoperable and isolated. Additional jumpers were then installed on Unit 2 and the HPCI suction was realigned to the 2/3A CST at 1300 hours. The investigation which followed concluded that the jumpers were placed on the wrong unit due to improper wiring verification. An additional contributing factor was that the internal and external labeling of the associated Terminal Boxes were inadequate. <br /><br /> The safety significance of this event is considered minimal since all other Emergency Core Cooling Systems (ECCS) required by Technical Specification (T.S.) 3.5.C.2.a were operable and a suction path for the HPCI system was available throughout this event. There have been no previous events involving the unplanned swap of the HPCI system suction path.
2371994018 | Dresden 2, Dresden 3 | 06/08/1994 | 12/29/1994 | 9501050189 | <strong>Potential Trip of Motor Control Centers Due to Improper Feed Breaker Settings</strong><br /><i>Abstract:&nbsp;</i>With Unit 3 in Refuel, while performing a 24 hour endurance run of the Unit 3 Emergency Diesel Generator, motor control center (MCC) 39-2 tripped. The trip of MCC 39-2 caused a trip of the Unit 3 Emergency Diesel Generator Cooling Water Pump and consequently a trip of the Unit 3 Emergency Diesel Generator on high temperature. Loss of MCC 39-2 also caused a loss of the 3B Reactor Protection System (RPS) MG-Set, the 'B' Standby Gas Treatment (SBGT) Train, the 125VDC Charger #3 and the 250VDC Charger #2/3. The loss of the RPS MG-Set caused a Unit 3 half scram, and the loss of the 'B' SBGT train caused a start of the 'A' SBGT train, which is considered an ESF actuation. An operability determination was made which stated that the MCC trip was due to an improperly set feed breaker. It also stated that the MCC was operable provided the compensatory action of controlling running load on the MCC was implemented. Station Operations department controlled the loading on the MCC until trip settings could be revised. A review of the MCC loading indicated that the original setting of the breaker was adequate but that load additions over time had created an overload situation. This event initiated a review of all safety related MCC feed breakers. The review indicated that MCCs 28-3 and 38-3 also had improperly set feed breakers. A separate operability assessment was performed on these two MCCS, which included immediate compensatory actions of controlling running loads to below the breakers' trip settings. The loading restrictions remained in place until the breakers could be properly set.
2371994019 | Dresden 2, Dresden 3 | 06/30/1994 | 09/26/1994 | 9410240263 | <strong>2/3 Chimney Grab Sample Not Obtained Within Required Time Frame Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>When the 2/3 Chimney Noble Gas Monitor (SPING) is inoperable, a grab sample must be pulled every 8 hours using the backup General Electric sample system. Failure to pull this sample is a violation of Tech Spec Table 3.2.5. On 6/30/94, the Chemistry Technician failed to obtain a required sample from the 2/3 Chimney. The sample was obtained and analyzed by a Chemistry Technician on the following shift. The sample results were within the specified limits for radioactivity.
2371994020 | Dresden 2, Dresden 3 | 07/15/1994 | 07/29/1994 | 9408180019 | <strong>Unit 2 HPCI Booster Pump Oil Drain Plugs Were Changed Instead of Unit 3 HPCI Booster Pump Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1994 with Unit 2 at 99% rated power and Unit 3 in a Refuel Outage, two contractor Millwrights were to perform a leak repair on the Unit 3 High Pressure Coolant Injection (HPCI) [BJ] booster pump bearing housing oil drain plugs. The Millwrights inadvertently removed the plugs and drained the oil from the Unit 2 HPCI booster pump, then reinstalled the plugs and filled the bearing housing with oil. Upon noticing they had worked on the wrong unit, they then proceeded to work on Unit 3 and when complete, turned in the work package without notifying anyone of the error. On July 18, 1994 the System Engineer was performing his walkdown and noticed some oil leaking from the Unit 2 HPCI booster pump oil drain plugs. After his investigation, he questioned the Unit 3 working department as to whether they could have been working the Unit 2 HPCI booster pump, however they were not aware of the safety significance of their actions, specifically, rendering the U2 HPCI System inoperable for twenty (20) minutes. The cognizant job supervisor and the System Engineer then notified the Unit 2 Operating Engineer and the Shift Engineer.
2371994021 | Dresden 2 | 08/04/1994 | 07/25/1997 | 9708040040 | <strong>HPCI Turbine Tripped on High Exhaust Pressure Due to a Failed Exhaust Check Valve</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1994, at 1559 hours, with Unit 2 at 099% rated core thermal power, while performing Dresden Operating Surveillance (DOS) 2300-03, High Pressure Coolant Injection (HPCI) System Monthly Operability Verification, the turbine tripped due to high exhaust pressure. Inspection and functional check of the turbine drain system was performed to verify correct operation. The exhaust line check valves were functionally tested and the rupture diaphragms were also replaced. DOS 2300-03 was reperformed on August 7, 1994 and exhaust pressure again was observed to be increasing abnormally. The turbine was manually tripped prior to exhaust pressure reaching 30 psig. Following a failed Local Leak Rate Test (LLRT) on the turbine exhaust check valves, Unit 2 was shut down. An inspection of the 2-2301-74 valve, the HPCI turbine exhaust stop check valve, revealed that the valve disc was found separated from the piston guide assembly causing a blockage in the exhaust line. Tack welds which prevent the disc from unthreading from the piston were found failed. The tack weld failures were caused by flow induced vibration that was a result of vendor test specifications that did not consider the effect on exhaust check valve design. The valve was repaired and tested satisfactorily. The safety significance of this event is considered minimal since all other Emergency Core Cooling Systems were available throughout this event. There have been no previous failures of this type.
2371994022 | Dresden 2 | 08/08/1994 | 07/21/1995 | 9507250078 | <strong>Type B and C Leakage Limit Exceeded Due to Worn Seating Surface of HPCI Check Valve</strong><br /><i>Abstract:&nbsp;</i>At approximately 0600, on August 8, 1994, with Unit 2 operating at 99% power, the performance of Dresden Technical Surveillance (DTS) 1600-01, Local Leak Rate Testing Of Primary Containment Isolation Valves, identified the High Pressure Coolant Injection (HPCI) System Turbine Exhaust to Suppression Pool Check Valve 2-2301-45 and Stop Check Valve 2-2301-74 to be leaking 234.7 standard cubic feet per hour (scfh). This value when added to the existing maximum pathway leakage rate resulted in the maximum pathway leakage rate limit for Type B and C primary containment leakage, 488.452 scfh (0.6L sub a), as listed in Technical Specification 3.7.A.2.b.(2)(a) being exceeded. The safety significance of the leakage past the 2-2301-45 was considered to be minimal since the additional leakage out of containment, on a minimum pathway basis, was 87.6 scfh from the outboard isolation Check Valve 2-2301-45 and would not cause the maximum off-site dose rates established in 10 CFR 100 to be exceeded. The cause of the excessive leakage was due to a worn seating surface which allowed leakage between the valve seat and the plate-type disks. This valve was replaced and the as-left LLRT yielded a leakage rate of 1.06 scfh. This supplement is submitted to report the corrective actions taken for this check valve failure as well as the results of an NPRDS search.
2371994023 | Dresden 2, Dresden 3 | 07/29/1994 | 08/19/1994 | 9408300052 | <strong>ASME Code Allowable Stresses Exceeded on the Control Rod Drive Flange Cap Screws Due to Lack of Engineering Review</strong><br /><i>Abstract:&nbsp;</i>At 2130 on July 29, 1994, with Unit 2 at 91% rated power and Unit 3 in a Refuel Outage, Site Engineering personnel determined that ASME code allowable stresses were exceeded on the Control Rod Drive (CRD)[AA] flange cap screws on CRD H-7 on Unit 2 and CRD A-6 on Unit 3. These CRDs were over-torqued to 550 ft-lbs per Dresden Maintenance Procedure (DMP) 300-9 'Control Rod Drive Removal and Replacement' to reduce or eliminate minor o-ring leakage at the CRD flange. This exceeded the vendor specified torque of 350 +\- 25 ft-lbs. <br /><br /> The affected bolts on the Unit 3 CRD were replaced prior to startup and the affected bolts on Unit 2 were determined to be operable and will be replaced during D2F23. The cause of this event was inadequate engineering review in 1981 when calculations were incorrectly performed by maintenance management personnel allowing the CRD cap screws to be torqued up to 550 ft-lbs. The safety significance of this event was minimal because the failure of all eight cap screws on a CRD flange is bounded by Dresden's LOCA analysis and even though code allowables were exceeded, stress values were well below yield.
2371994024 | Dresden 2 | 08/09/1994 | 09/01/1994 | 9409160318 | <strong>HPCI Outboard Containment Isolation Valve Failure to Close Due to Corroded Contacts in Local Push Button Station</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1994, Dresden Unit 2 was being shutdown as part of a forced outage. As reactor pressure dropped below the High Pressure Coolant Injection (HPCI) containment isolation set point (80 psig decreasing), the outboard containment isolation valve failed to close. When the position switch in the control room also failed to close the valve, an Operator was dispatched to manually close the valve using the actuator handwheel. <br /><br /> An investigation revealed that there was an open circuit in the 'Stop' push button of the local control Push button station. The 'Stop' button is wired such that it can prevent containment isolation logic and the remote control switch from actuating the Motor-Operated Valve (MOV). The apparent root cause of this failure is corrosion of the 'Stop' Push button contacts. <br /><br /> Immediate corrective actions included burnishing all contacts in this local control push button station, and, the contacts in the remaining 131 safety related local control push button stations. Steps will be added to an existing Environmental Qualification surveillance procedure to assure that these contacts are cleaned once every other refueling cycle.
2371994025 | Dresden 2 | 08/26/1994 | 09/20/1994 | 9409270210 | <strong>Continuous Monitoring of 2/3 Chimney Effluent Not Performed Due to SPING Inadvertently Put in Flush Mode.</strong><br /><i>Abstract:&nbsp;</i>Continuous monitoring of 2/3 main chimney effluent was not performed due to the Noble Gas Monitor (SPING) inadvertently being put in flush mode. At 1316, 8/26/94 the 2/3 main chimney SPING was inadvertently placed into the flush mode. The incorrect mode was not noticed until 2302, 8/26/94, at which time the system was switched to the G.E. backup system. Technical Specifications Table 3.2.5 states that grab samples must be obtained every 8 hours when the SPING is inoperable. The grab sample was obtained approximately 12 hours after the SPING was put into the wrong mode. Some difficulties were also encountered when switching over from the SPING to the G.E. backup system. Both units were shutdown during this event and samples before and after were at normal levels. The safety impact was minimal.
2371994026 | Dresden 2 | 09/19/1994 | 10/17/1994 | 9410240271 | <strong>Main Steam Line Drain Piping Exceeding code Allowable Stress Limits</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1994, during a Dresden Unit 2 maintenance outage, isometric drawings of the small bore, main steam drain lines were being developed as part of a design change to replace the main steam drain line containment isolation valves (2-220-1&2). This walk down identified that the four main steam drain lines inside the drywell did not contain thermal flexible loops. An analysis identified that the piping stresses exceeded allowable limits. This piping was field routed and supported in accordance with 'Blume Curve' span criteria. This discrepant piping configuration is the result of an original design\construction error. <br /><br /> The immediate corrective action was to design thermal flexible loops for the four main steam drain lines in the drywell (P12-2-94-268). This design change, which includes changes to the support configuration, will be implemented before Unit 2 start up. <br /><br /> The Unit 3 main steam drain line piping contains thermal flexible loops. The stresses on this piping system were determined to be within code allowable limits.<br /><br /> The Quad Cities Station main steam drain line were reviewed as a result of this concern. It was determined that the existing configuration of the Quad Cities main steam line drains is adequate.
2371994027 | Dresden 2 | 09/22/1994 | 10/21/1994 | 9411070426 | <strong>Both RVWLIS Loops Inadvertently Removed From Service Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1994 at 1830, with Unit 2 in cold shutdown with the Reactor Vessel flooded to the Main Steam lines, it was discovered that the instrumentation for Reactor Low Low Water Level Emergency Core Cooling System (ECCS) initiation was valved out for both trip systems. This rendered auto initiation of ECCS on Reactor Low Low Water Level inoperable for approximately eight hours. Technical Specification limits were not exceeded during this lineup due to the cold shutdown condition of the Reactor. Alternate level instrumentation was available for monitoring Reactor Vessel level, but auto initiation of ECCS was not operable. Root Cause of the event is inadequate tracking of Technical Specification requirements by Operations Personnel and lack of consideration of systems affected by Reactor Vessel Water Level Instrumentation (RVWLIS) by Operations personnel. This supplement is to address additional causal factors.
2371994028 | Dresden 2 | 11/19/1994 | 12/16/1994 | 9412230132 | <strong>Unit 2 Mark I Torus Spray Piping Outside of UFSAR Allowables Due to Incomplete Walkdowns Which Led to the Use of Inaccurate Design Basis Documentation</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1992 an operability assessment was generated to document a weight discrepancy on the Torus spray subsystem containment isolation valves. In September 1994, comment design drawings were issued for the Unit 2 piping support modifications for these valves. The extent of the support changes along with the piping acceleration values of the original Mark I analysis raised a concern about the condition of the existing piping configuration. Although stresses on this piping were determined to be within operability allowable limits, it was determined by engineering judgement that the stresses on this piping exceed code allowable limits. The weight discrepancy is attributed to incomplete walkdowns performed which led to the use of inaccurate design basis documentation. The stresses and accelerations on all other Mark I piping have been evaluated and have been found to be acceptable. Torus Spray piping support modifications for Unit 2 are scheduled for D2R14, currently scheduled for June 1995. A piping analysis will be performed on the Unit 3 Torus Spray piping by February of 1995. If support modifications are determined to be required they will be implemented during D3R14.
2371994029 | Dresden 2 | 11/26/1994 | 12/23/1994 | 9412290112 | <strong>Spurious Group V Isolation Due to Pressure Spike when Opening the Isolation Condenser Reactor Inlet Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>At 1938 hours on November 26, 1994, with Unit 2 at 2% rated power while in the startup mode, a spurious Group V Isolation Signal was received when Motor Operated Valve (MOV) 2-1301-4 was being opened per Dresden General Procedure (DGP) 1-1 Unit 2(3) Normal Unit Start-up. The procedure required the valve to be opened prior to exceeding 150 psig reactor pressure to place the Isolation Condenser system [BL] in stand-by operation. When the valve opened, a pressure transient occurred which caused a Group V isolation on high condensate flow. All the Isolation Condenser Group V isolation valves went closed as expected except for MOV 2-1301-4. The breaker for MOV 2-1301-4 valve tripped. When the breaker was reset the valve indicated closed. The isolation signal was reset and the valve was stroked successfully. The cause of the spurious isolation was attributed to a pressure transient which occurred when the MOV 2-1301-4 valve was opened. The breaker tripped because its settings were too low to handle the in-rush current that occurred when the motor operated valve was required to reverse directions mid-stroke. This portion of the event is reported under LER 94-30.
2371994030 | Dresden 2 | 12/04/1994 | 12/23/1994 | 9501060134 | <strong>Spurious Tripping of Motor Operated Valve Feed Circuit Breaker Under Valve Reversal Conditions Due to Inadequate Breaker Magnetic Setting Procedure</strong><br /><i>Abstract:&nbsp;</i>At 1938 hours on November 26, 1994, with Unit 2 at 2% rated power while in the startup mode, a Spurious Group V Isolation Signal was received when Motor Operated Valve (MOV) 2-1301-4 was being opened. All the Isolation Condenser [BL] Group V isolation valves went closed as expected except for MOV 2-1301-4. The breaker for MOV 2-1301-4 valve tripped. During special testing, on December 1, 1994, to verify the cause of the breaker trip it was determined that the breaker trip setting was not set high enough to account for higher starting currents that occur during MOV reversal conditions. A review of all safety related MOVs on Units 2 & 3 revealed that there were 2 valves on Unit 2 and 4 valves on Unit 3 that may not have breaker settings with sufficient margin to prevent breaker tripping during MOV reversal conditions. The Unit 2 breakers were reset prior to unit start-up and the Unit 3 breakers will be reset during the next short outage. The safety significance is minimal as this condition is only present during valve cycling operations (normally surveillance testing). This LER is being submitted voluntarily as the MOV reversal condition is not part of the Design Basis as identified in the UFSAR.
2371994031 | Dresden 2 | 11/22/1994 | 12/22/1994 | 9412290110 | <strong>10 CFR 50 Appendix J Type A Administrative Limit Exceeded Due to Leaking HPCI Primary Containment Isolation Check Valve 2-2301-34</strong><br /><i>Abstract:&nbsp;</i>At approximately 1400, on November 22, 1994, a local leak rate test (LLRT) on the primary containment isolation valves, 2-2301-34 and 2-2301-71, was performed per Dresden Technical Surveillance (DTS) 1600-01. This minimum pathway leakage, when added to the 10 CFR 50 Appendix J Type A leakage, caused the administrative limit for the Type A leakage (85% of 0.75 L sub a) to be exceeded. This administrative limit of the Type A leakage was in effect on October 28, 1994, requested when Dresden Station requested an one-time schedular exemption of the 18 month Type A test interval for Unit 2. The 2-2301-34 check valve was disassembled and inspected under work request (WR) D26912. The seats of the valve were lapped and the final leakage was 0.20 scfh. The cause for this event was a lack of aggressive valve corrective maintenance. The safety significance is considered minimal since the Type A leakage never exceeded the Unit 2 Technical Specification 4.7.A.2.b limit of 0.75 L sub a. In order to solve primary containment isolation valve problems, the station has developed a valve project team. Also, an inspection and repair interval of every two refuel outages has been developed for this check valve. This LER is being submitted voluntarily.
2441994001 | Ginna | 01/19/1994 | 02/17/1994 | 9403010270 | <strong>Radiation Monitor R-32 ("B" Main Steam Line) Inoperable, Due to Personnel Error, Causes a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1994, at approximately 1330 EST, with the reactor at approximately 97% steady state power, the output of the 'B' Main Steam Line Radiation Monitor R-32 was discovered to be low by one decade. R-32 was declared inoperable. <br /><br /> Investigation revealed that a calibration constant was incorrectly documented due to a transposition error, and the incorrect value was edited into the R-32 control terminal. Immediate corrective action was to edit the correct value of the calibration constant into R-32. This restored the output of R-32 to the correct range, and R-32 was declared operable. (This event is NUREG-1022 (A) cause code.) <br /><br /> Corrective action to preclude repetition is outlined in Section V (B). <br /><br /> This LER meets the requirements of a Special Report required by the Ginna Technical specifications.
2441994003 | Ginna | 02/08/1994 | 03/10/1994 | 9403170001 | <strong>Uninstalled Swagelok Tubing Plug, Due to Personnel Error, Causes a Loss of Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1994, at approximately 1020 EST, with the reactor at approximately 98% steady state power, an Instrument and Control technician observed an open instrument tube. Event reconstruction determined that this open tube had resulted in a loss of Containment integrity on November 18, 1993. <br /><br /> Immediate corrective action was to install a swagelok plug on the open tube. <br /><br /> The underlying cause of the open tube was a personnel error on the part of a plant technician. (This event is NUREG-1022 (A) cause code.) <br /><br /> Corrective action to preclude repetition is outlined in Section V (B).
2441994004 | Ginna | 02/14/1994 | 03/16/1994 | 9403230032 | <strong>Missed Surveillances, Due to Lack of Clearly Defined Interpretations of Technical Specifications Requirements, Resulted in Violations of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1994, at approximately 1000 EST, with the reactor at approximately 98% steady state power, the Plant Operations Review Committee determined that four surveillance tests had not fully complied with the requirements of Technical Specifications (TS).<br /><br /> Immediate corrective action was to confirm that four missed surveillances had been completed (or other methods used) to ensure that all TS requirements were fully complied with. Except for a test of a pushbutton for manual Containment Isolation actuation, necessary tests and/or verifications had been completed.<br /><br /> The underlying cause of the four missed surveillances was a lack of clearly defined interpretations of the TS wording for the four missed surveillances. (This event is NRC Performance Indicator Program cause code 5.8.1.) <br /><br /> Corrective action to preclude repetition is outlined in Section V (B).
2441994005 | Ginna | 02/17/1994 | 03/21/1994 | 9403290326 | <strong>Loss of Offsite Power Circuit 751, Due to Loss of Power to #2 34.5 KV Bus at Station 204, Causes Automatic Actuation of RPS System (Turbine Runback)</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1994, at approximately 1421 EST, with the reactor at approximately 98% steady state power, a turbine runback occurred when offsite power 34.5 KV Circuit 751 was lost, causing low voltage on safeguards busses 14 and 18.<br /><br /> The Control Room operators performed the appropriate actions of AP-TURB.2, 'Turbine Load Reduction', and verified that the plant was stabilized at approximately 93% power after the runback signal cleared. <br /><br /> The underlying cause of the loss of power to offsite 34.5 KV Circuit 751 was loss of power to #2 34.5 KV Bus at offsite Station 204. (This event is NUREG-1022 (C) Cause Code.) <br /><br /> Corrective action to preclude repetition is outlined in Section V (B).
2441994006 | Ginna | 03/23/1994 | 04/22/1994 | 9404280277 | <strong>Steam Generator Tube Degradation Due to IGA/SCC, Causes Quality Assurance Manual Reportable Limits to be Reached</strong><br /><i>Abstract:&nbsp;</i>During the 1994 Annual Refueling and Maintenance outage, subsequent to the eddy current examination performed on both the 'A' and 'B' Westinghouse Series 44 steam generators, 164 tubes in the 'A' steam generator and 134 tubes in the 'B' steam generator required corrective action due to tube degradation. <br /><br /> The immediate cause of the event was that the 'A' and 'B' steam generator tube degradation was in excess of the Ginna Station Quality Assurance Manual reportable limits.<br /><br /> The underlying cause of the tube degradation is a common steam generator problem of a partially rolled tube sheet crevice with recurring Intergranular Attack/Stress Corrosion Cracking (IGA/SCC) and Primary Water Stress Corrosion Cracking (PWSCC) attack on steam generator tubing. This event is NRC Performance Indicator System Cause Code 5.8.4.3 and NUREG-1022 Cause Code (B). <br /><br /> Corrective action taken was to either sleeve or plug the affected tubes with accepted industry repair methods.
2441994007 | Ginna | 04/27/1994 | 05/27/1994 | 9406030044 | <strong>Feedwater Transient, Due to Loss of Ability to Control Feedwater Regulating Valve, Causes a Lo Lo Steam Generator Level Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1994, at approximately 1407 EDST, with the reactor at approximately 45% reactor power, the ability to control the "A" main feedwater regulating valve was lost. At 1410 EDST, the reactor tripped on Lo Lo level ( operators performed the actions of procedures E-0 and ES-0.1. <br /><br /> The underlying cause was determined to be an improperly secured stroke adjust set screw for the valve positioner signal diaphragm assembly for the "A" main feedwater regulating valve. This event is NUREG-1022 Cause Code (B), "Design, Manufacturing, Construction/Installation." <br /><br /> Immediate corrective action was to install a new valve positioner of a previous design. Corrective action to preclude repetition is outlined in Section V (B).
2441994008 | Ginna | 06/13/1994 | 07/13/1994 | 9407200011 | <strong>"B" SI Pump Declared Inoperable Due to Broken Motor Rotor Bar, Causes Completion of a Plant Shutdown Required by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1994, at approximately 1349 EDST, with the plant at approximately 97% steady state power, the 'B' safety injection pump was declared inoperable during performance of the monthly surveillance test. On June 13, 1994, at approximately 1614 EDST, the reactor was placed in the hot shutdown condition to comply with Ginna Technical Specifications for safety injection pump operability requirements.<br /><br /> The underlying cause of the shutdown was inoperability of the 'B' safety injection pump, due to a broken motor rotor bar. This event is NUREG-1022 Cause Code (B), 'Design, Manufacturing, Construction/Installation.' <br /><br /> Corrective action to preclude repetition is outlined in Section V (B).
2441994009 | Ginna | 08/09/1994 | 09/08/1994 | 9409190247 | <strong>Safety Injection Pumps Declared Inoperable Due to Leak, Causes Condition Prohibited by Technical Specifications and Completion of Plant Shutdown Required by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1994, at approximately 1420 EDST, with the plant at approximately 97% steady state power, a leak developed at a socket weld in the common recirculation line for the safety injection (SI) pumps. All three (3) SI pumps were declared inoperable, which required entry into Technical Specification 3.0. To comply with Technical Specifications, the plant was shut down, and the reactor coolant system temperature was below 350 degrees F at 0130 EDST on August 10. <br /><br /> The underlying cause of the leak was a crack in the socket weld in the common recirculation line, caused by pipe displacement from air entrainment and pump misalignment. The affected weld was cut out and replaced. This event is NUREG-1022 Cause Code (D), Defective Procedure. <br /><br /> Corrective action to preclude repetition is outlined in Section V (B).
2441994010 | Ginna | 09/16/1994 | 10/17/1994 | 9410270363 | <strong>Loss of 4160 Volt Bus 12B, Due to Defective Procedure, Results in Automatic Start of "B" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1994, at approximately 1018 EDST, with the reactor at approximately 98% steady state power, the 4160 Volt circuit breaker that was supplying power to 4160 Volt bus 12B was inadvertently tripped. This resulted in deenergization of bus 12B and momentary loss of power to 'B' train 480 Volt safeguards buses 16 and 17. <br /><br /> The 'B' Emergency Diesel Generator started and reenergized buses 16 and 17, as per design.<br /><br /> The underlying cause of the inadvertent circuit breaker trip was a defective procedure. This event is NUREG-1022 Cause Code (D).<br /><br /> Corrective action to preclude repetition is outlined in Section V.B.
2441994011 | Ginna | 09/17/1994 | 10/17/1994 | 9410270370 | <strong>Short Circuit in Indication Lamp Causes Blown Fuse, Resulting in Disabling of Automatic Actuation of Engineered Safety Features Actuation System for "B" Safeguards Logic Train Components</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1994, at approximately 1224 EDST, with the reactor at approximately 98% steady state power, an indicating lamp on the 'B' train safeguards initiation cabinet failed in a manner that caused a short circuit that blew a 10 ampere fuse in the 125 VDC control power circuit. This disabled the automatic actuation of 'B' train safeguards components.<br /><br /> Immediate corrective action was to replace the burned out indicating lamp and blown fuse.<br /><br /> The underlying cause of the event was determined to be a shorting out of the low resistance leads that connect the indicating lamp base to the lamp filaments. This event is NUREG-1022 Cause Code 'B'. <br /><br /> Corrective action to preclude repetition is outlined in Section V. B.
2441994012 | Ginna | 09/21/1994 | 10/21/1994 | 9410310306 | <strong>Loss of 34.5 KV Offsite Power Circuit 751, Due to External Cause, Results in Automatic Start of "B" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1994, at approximately 1032 EDST, with the reactor at approximately 98% steady state power, power from Circuit 751 (34.5 KV offsite power source) was lost. This resulted in deenergization of 4160 Volt bus 12B, and momentary loss of power to 'B' train 480 Volt safeguards buses 16 and 17.<br /><br /> The 'B' Emergency Diesel Generator started and reenergized buses 16 and 17, as per design. <br /><br /> The underlying cause of the loss of power from Circuit 751 was that a tree was accidently knocked into the transmission wires for Circuit 751 by a private citizen operating heavy equipment. This event is NUREG-1022 Cause Code (C). <br /><br /> Corrective action to preclude repetition is outlined in Section V.B.
2451994001 | Millstone 1 | 12/30/1993 | 09/12/1995 | 9509200010 | <strong>Potential Loss of Off-Site Power During a LOCA</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1993, at 1435 hours, with the plant operating at 100% power, an evaluation concluded that a potentially reportable condition existed. Using a computer model of the Millstone Unit One electrical distribution system, various load studies were being conducted. One of the cases involved the mitigation of a postulated Loss of Coolant Accident (LOCA). with power being supplied by the Reserve Station Service Transformer (RSST), the preferred source of off-site power. With switchyard voltage assumed at the worst case minimum value of 348 KV, results of the load study indicated that LOCA mitigation loads, in combination with the normal loads which are not shed upon receipt of an accident signal, combine to produce a voltage drop across the RSST which 0 sufficient to lower the voltage available at 4160 volt emergency buses 14E and 14F. This low voltage would result in the actuation of the relays which monitor for degraded bus voltage conditions. Worst case minimum switchyard voltage is postulated to occur after the loss of Millstone Unit One generation when both Millstone Unit Two and Millstone Unit Three are off-line. In the unlikely event that this scenario occurs, the preferred source of off-site power would be automatically tripped, and LOCA mitigation would be accomplished utilizing the on -site sources of emergency power, the Diesel Generator and the Gas Turbine Generator. With either or both Millstone Unit Two and Millstone Unit Three on-line, it is postulated that electrical distribution system voltage would not decrease low enough to actuate the degraded grid voltage relays upon loss of generation at Millstone Unit One.<br /><br /> Compensatory measures were taken to limit the potential for this postulated scenario, and long term corrective actions are currently being finalized. No safety consequences resulted from this event. Supplemental information is shown with vertical change bars.
2451994002 | Millstone 1 | 12/30/1993 | 01/28/1994 | 9402070325 | <strong>Closure of Turbine Building Railroad Access Door</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1993, at 0920 hours with the plant at 100% power, a Plant Equipment Operator found the Turbine Building railroad access door in the closed position. This door is administratively controlled in the open position under the station protective tagging program. This door is required to be open during power operation to ensure operability of Switchgear equipment during a postulated Turbine Building High Energy Line Break. <br /><br /> Upon discovery, the door was immediately opened. Investigation revealed a Millstone employee assigned work in the Turbine Building railroad access area closed the door approximately 2 hours earlier due to the inclement weather and freezing temperatures. No safety consequences resulted from this event.
2451994003 | Millstone 1 | 01/03/1994 | 02/01/1994 | 9402100086 | <strong>Simultaneous Inoperability of Both Channels of Steam Tunnel Ventilation Radiation Monitoring System</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1994, at 1013 hours, with the plant operating at 94% power, during the performance of routine surveillance testing of the Steam Tunnel Ventilation Radiation Monitoring System, monitor RIS-1705-39A failed to initiate a high radiation trip within allowable limits. With no adjustments or repairs, three successive checks of the monitor then met the acceptance criteria and RIS-1705-39A was returned to service. Surveillance testing proceeded successfully on monitor RIS-1705-39B. <br /><br /> At 1420 hours, during a subsequent surveillance to reverify Channel 'A' operability. RIS-1705-39A again failed to trip within the acceptance criteria, and the monitor was declared inoperable from the time of the original failure, 1013 hours. bypassed for testing, resulting in both channels of the Steam Tunnel Ventilation Radiation Monitoring System being inoperable for a four minute period.<br /><br /> I&C personnel affected repairs and, on January 4, 1994, the monitor was declared operable and returned to service under an increased surveillance frequency. Both RIS-1705-39A and RIS-1705-39B had been previously scheduled for end of qualified life replacement during the current refueling outage, which commenced on January 15, 1994. This replacement will be completed prior to startup. <br /><br /> No safety consequences resulted from this event.
2451994004 | Millstone 1 | 01/16/1994 | 08/18/1994 | 9408250119 | <strong>LLRT Failures</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1994, at 1200 hours with the Unit at 0% power (Refueling Outage #14), while performing Local Leak Rate Testing (LLRT), Main Steam Isolation Valves (MSIV) 1-MS-IB and 1-MS-2C failed to meet the required leakage rate specified in Unit 1 Technical Specifications.<br /><br /> On January 30, 1994, the combined leakage rate for penetrations tested up to that date exceeded the Technical Specification limit of 0.60 La. Several penetrations exceeded administrative guidelines, however three major valve penetrations contributed adversely to the failed LLRT combined as-found leakage criteria. The three valve penetrations include penetration X-8, Main Steam system valves 1-MS-5 and 1-MS-6; penetration X-9A, Feedwater system valves 1-FW-9A and 1-FW-10A; and penetration X-25/X-202D, Atmospheric Control system valves 1-AC-7, 8, 9, 10, 11, and 12.<br /><br /> The two MSIVs and all other valves that exhibited significant leakage were repaired and satisfactorily retested.<br /><br /> There were no safety consequences as a result of this event.
2451994007 | Millstone 1 | 02/08/1994 | 08/25/1994 | 9409010001 | <strong>Reactor Water Cleanup Break Isolation on Reactor Low Low Water Level</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1994, at 1400 hours, with the plant shutdown for a refueling outage, a discrepancy was noted in the original Reactor Water Cleanup (RWCU) system break analysis. Specifically, it was determined that a RWCU system isolation at reactor low low water level, with offsite power available, would not occur until the feedwater makeup source from the condenser hotwell is depleted. The mass/energy release from this event could potentially result in an increase in offsite dose as described in the Millstone Unit 1 Updated Final Safety Analysis Report (UFSAR) Chapter 15, 'Accident Analyses.' In addition, the affects of the mass/energy release on the current Reactor Building temperature profile and the ensuing water release to the Reactor Building are unknown. <br /><br /> No safety consequences resulted from the event. Although the break scenario may result in dose consequences outside the UFSAR Chapter 15 analysis,and no specific analysis was performed, it is believed offsite dose consequences would remain within 10CFR100 limits. No safety equipment was required to function as a result of this event. A plant design change was installed during the 1994 refueling outage to detect line breaks in the RWCU system and isolate the system. This modification was complete prior to plant startup.
2451994009 | Millstone 1 | 02/22/1994 | 06/28/1994 | 9407080180 | <strong>Hydraulic Snubbers HSS-015 & HSS-018</strong><br /><i>Abstract:&nbsp;</i>On February 2-2,1994, with the plant in Cold Shutdown for refueling, it was determined 2 hydraulic snubbers failed to meet the acceptance criterion for functional testing. <br /><br /> Functional testing of the first 10% sample for hydraulic snubbers found one snubber (HSS-015) that failed to meet the acceptance criterion. An additional 5% were functionally tested as required by Technical Specifications with no additional failures. <br /><br /> One snubber (HSS-018) required a retest as a result of failing the previous functional test during the 1992 inspection and failed to meet the acceptance criterion. <br /><br /> Engineering evaluations were performed to determine what affects, if any, the failure or these snubbers had on the system to which the snubbers were attached. These evaluations concluded the inoperable snubbers did not have any affects on the attached system which would have impaired the operability of these systems.<br /><br /> These events are reportable pursuant to 10CFR50.73(a)(2)(i)(B).
2451994011 | Millstone 1 | 03/22/1994 | 03/07/1996 | 9603200025 | <strong>Non Conservative Reactor Vessel Low-Low Level Setpoint</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1994, while shutdown (137 Fahrenheit, 0 psig), it was identified that as a result of a 1979 plant design change which failed to specify the need for either a Technical Specification change or a setpoint change, the reactor vessel low level scram setpoint and low-low level Emergency Core Cooling System (ECCS) initiation setpoint were potentially non-conservative. The 1979 design change installed a new fuel design which had a longer active fuel length making the top of active fuel higher. Millstone Unit No. 1 Technical Specifications reference the low level reactor scram and low-low ECCS setpoints at inches above top of active fuel. Review of historical calibration data indicated that the low level scram setpoint would have met the Technical Specification requirement but the low-low setpoint was outside allowed Technical Specification values. Discussions with General Electric confirmed that the increased fuel height was accounted for in plant specific safety analyses and that there was no negative safety consequences associated with the existing level setpoints. However, Millstone Unit No. 1 has implemented a plant design change to ensure the setpoints are in compliance with existing Technical Specification requirements. <br /><br /> There were no safety consequences as a result of this event.
2451994012 | Millstone 1 | 03/29/1994 | 08/28/1996 | 9609030087 | <strong>Main Steam Safety/Relief Pilot Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1994, with the plant shut down for a planned Cycle 14 Refueling Outage (0% power, 110 degrees F, 0 psig) bench testing of the Main Steam system safety/relief pilot valves indicated that all six of the valves lifted at pressures in excess of the Technical Specification limit. Analysis indicates that the ASME Code/Safety Limit would not have been exceeded during a limiting transient when the as-found setpoints are considered. All pilot valves will be refurbished and recertified to their desired set pressures. Replacement pilot valves have already been installed.
2451994013 | Millstone 1 | 03/28/1994 | 04/28/1994 | 9405050009 | <strong>LPCI Heat Exchanger 15 psid Differential Pressure May Not Be Achievable</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1994, with the reactor in cold shutdown as part of a refueling outage, analyses conducted in support of Generic Letter 89-13 indicated that the ESW flow may be less than the values assumed in the post-LOCA Containment Cooling analysis. <br /><br /> Following a postulated loss of coolant accident (LOCA), LPCI System flow may need to be throttled to satisfy net positive suction head (NPSH) concerns. A corresponding reduction in ESW flow rate is then required to maintain a 15 psid differential. This reduction in ESW flow, which occurs only when the LPCI flow is throttled, may result in less than the credited heat removal capability from the LPCI heat exchangers and a subsequent heatup of containment above the maximum calculated temperature.
2451994014 | Millstone 1 | 04/08/1994 | 05/09/1994 | 9405170048 | <strong>Inadvertent Initiation of ECCS</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1994, at 1051 hours, with the plant in cold shutdown, inadvertent Emergency Core Cooling System (ECCS) actuations occurred during the performance of a special procedure. Lack of procedure detail resulted in bypassing the wrong relay contacts during preparations for a portion of the test. This error resulted in ECCS equipment actuation when a high drywell pressure (2 psig) was simulated. Expected system responses to the actuation signal were verified. No safety consequences resulted from this event.
2451994015 | Millstone 1 | 04/10/1994 | 08/03/1995 | 9508080053 | <strong>RPV Drain Down and Drywell Spray Event</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1994, during the performance of a Low Pressure Coolant Injection (LPCI) System logic surveillance test, an inadvertent decrease in the Millstone Unit One reactor pressure vessel (RPV) water level occurred. The water level decrease was the result of a procedural deficiency that established a flow path from the Shutdown Cooling (SDC) System to the 'A' LPCI drywell spray header through the LPCI cross- connect piping. This flow path allowed approximately 12,000 gallons of reactor coolant to spray into the drywell. <br /><br /> The RPV level decrease was recognized by the reactor operators who terminated the event by closing the LPCI drywell spray valves. The final water level remained above any automatic level setpoints (i.e. scram, isolations, or ECCS initiations). No emergency safety features actuated during this event.<br /><br /> This event resulted from a failure to recognize system interactions during the development, approval, and implementation of the LPCI System logic test procedure.
2451994016 | Millstone 1 | 04/22/1994 | 05/23/1994 | 9406010112 | <strong>Loss of Special Nuclear Material Accountability</strong><br /><i>Abstract:&nbsp;</i>On April 22,1994, with the plant shutdown for a scheduled refueling outage and the drywall under vessel area accessible, a discrepancy was noted between the number of Intermediate Range Monitors (IRMs) stored in the drywell equipment drain sump and the number indicated in the Special Nuclear Material Inventory Log. Actions were initiated to recover the four (4) IRMs that were recorded as being stored in the sump. Two (2) IRMs could not be accounted for. <br /><br /> No safety systems were required to actuate as a result of this event. <br /><br /> This event is reportable pursuant to 10CFR20.2201(a)(i)(ii), which requires reporting the theft or loss of licensed material and 10CFR70.52(a) and (b) which requires immediate notification of accidental criticality or loss of special nuclear material.
2451994017 | Millstone 1 | 04/22/1994 | 05/23/1994 | 9406010053 | <strong>Invalid Actuation of Primary Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1994 at 1636 hours, with the plant in cold shutdown, an invalid Primary Containment Isolation occurred. A technician had removed the rear cover of the newly installed steam leak annunciator panel in order to terminate wires. In the process of terminating connections in the back of the annunciator, the technician bumped the cover, causing it to make contact with an unpainted steel unistrut member and an Instrument AC fuse block. A short occurred between the fuse block line side and the grounded unistrut, however it cleared almost immediately. Primary Containment Isolation groups 2, 3, and 5 occurred due to a momentary reduction in Instrument AC voltage. Expected system responses to the isolations were verified. No safety consequences resulted from this event.
2451994018 | Millstone 1 | 04/29/1994 | 05/31/1994 | 9406080265 | <strong>Turbine Building Secondary Closed Cooling Water (TBSCCW)</strong><br /><i>Abstract:&nbsp;</i>On April 29,1994, it was determined that the TBSCCW heat exchanger tube to tubesheet joint configuration did not meet code allowable stress limits when certain worst case accident parameters were analyzed. Previous engineering evaluations assumed that the tubes were rolled and welded. The results of visual inspections determined that the tubes were rolled only.<br /><br /> This condition could have resulted in tube leakage from TBSCCW to Service Water. The fresh water inventory loss could have caused TBSCCW to become inoperable. The loss of TBSCCW could have resulted in rendering the Feedwater Cooling Injection System (FWCI) and the Diesel Generator inoperable if the loss went unattended. <br /><br /> A field implemented tube rolling procedure was performed which corrected the tube joint deficiency restoring the joint strength. <br /><br /> No safety systems were required to function as a result of this event.
2451994019 | Millstone 1 | 05/10/1994 | 01/24/1995 | 9502010229 | <strong>1-MS-5 & 6 and 1-FW-4 A & B Unable to Perform Design Function pre-RFO-14</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1994, at approximately 1500 hours with the plant in Shutdown Mode (170 degrees F and 0 PSIG), an engineering analysis determined Main Steam Line Drain Valves 1-MS-5 & 6 and Feedwater Coolant Injection Valves 1-FW-4A & B may have been unable to perform their safety function. <br /><br /> This conclusion was reached when as-found valve factors derived for valves 1-MS-5, 1-MS-6, 1-FW-4A and 1-FW-4B were found to meet their original design requirements, however EPRI and other Industry data suggest that a higher valve factor (>.4) is more appropriate to ensure operability. These derived valve factors indicate the Motor Operated Valves (MOVs) would not have had sufficient thrust margin to provide reasonable assurance 1-MS-5 & 1-MS-6 would performed their intended safety function to close, or 1-FW-4A & 1-FW-4B to open. <br /><br /> During the Cycle 14 refueling outage, modifications were performed to 1-MS-5 and 1-MS-6 to increase their closing thrust capability to ensure the valves will isolate, based upon the most current Industry data. Operating procedure changes were made to leave 1-FW-4A and 1-FW-4B in the open position at all times the Feedwater Coolant Injection System is required to be operable. <br /><br /> No safety system actuations were required and no safety consequences resulted from this event.
2451994020 | Millstone 1 | 05/27/1994 | 02/10/1997 | 9702130080 | <strong>Intake Structure Ambient Temperature</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1994, at 1432 hours, with the plant at 100% power (530 degrees F and 1030 psia), an ongoing engineering analysis concluded that the Service Water (SW) System and Emergency Service Water (ESW) System pump motors could not be demonstrated to be operable during several postulated loss of intake structure ventilation scenarios. Previous evaluations had determined that intake structure ventilation was not essential to support operability of these motors. <br /><br /> The engineering analyses performed in May 1 994 indicated that loss or degradation of intake structure ventilation could expose equipment credited for safe shutdown (SW System and ESW System pump motors) to ambient temperatures greater than their maximum continuous operating temperature limit of 140 degrees F, thereby potentially rendering them inoperable for long term, post - Design Basis Event (DBE) cooling due to accelerated motor aging if the loss or degradation of ventilation went undetected or unattended.<br /><br /> Further engineering review performed in late 1 994 indicated that components of the safety-related ESW strainer motor circuits (i.e a thermal overload relay and auxiliary relay) designed for service temperature of 104 degrees F would degrade at elevated temperatures. Possible failure of these components could render the ESW strainer motor inoperable. <br /><br /> Local temperature indication, plant procedures, and compensatory measures have been implemented to assure the intake structure ambient temperature will not increase to a level at which SW or ESW System operability could be compromised. No safety systems were required to function as a result of this event.
2451994021 | Millstone 1 | 06/03/1994 | 07/27/1995 | 9508040076 | <strong>Service Water Temperature During Mussel Cook Evolution</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1994 at 0155 hours, with the plant operating at 85% power, the Ultimate Heat Sink temperature of 75 degrees F was exceeded during a thermal heat treatment and backwashing (mussel cook) evolution of the 'A' and 'B' Intake Bays. During the service water temperature transient, the maximum operating temperatures of the Service Water, Reactor Building Closed Cooling Water (RBCCW), Turbine Building Closed Cooling Water (TBCCW) and the Turbine Building Secondary Closed Cooling Water (TBSCCW) systems were exceeded. The thermal heat treatment evolution was subsequently secured due to high turbine bearing and lube oil temperatures resulting from the increased service water supply temperatures.<br /><br /> No safety systems were required to function as a result of this event. Following the event, the Service Water, TBCCW, RBCCW and TBSCCW systems were inspected for evidence of leakage and potential thermally-induced piping and support degradation. No deficiencies were identified.
2451994022 | Millstone 1 | 06/14/1994 | 07/08/1994 | 9407140094 | <strong>Missed Surveillance on Tech. Spec. Fire Doors</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1994, with the unit at 100% power, it was determined that (4) four Fire Doors had never received a fire door inspection per requirements of Technical Specifications. <br /><br /> The (4) four doors were immediately inspected to Fire Door Inspection Procedure and were found to be acceptable with no deviations. <br /><br /> The Fire Door Inspection Procedure will be updated to include these (4) four Fire Doors. <br /><br /> There were no safety consequences as a result of this missed surveillance.
2451994023 | Millstone 1 | 06/20/1994 | 07/05/1994 | 9407130044 | <strong>High Range Stack Noble Gas Monitor Out of Service</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1994, at 0900 hours, with the plant operating at 100% power, during continuation of scheduled surveillance testing of the Stack High Range Noble Gas Radiation Monitor, the auxiliary sample pump was discovered to be disabled since the surveillance began on June 9, 1994, thereby resulting in the monitor being inoperable for that period of time. Following completion of testing and repair of an inoperable particulate-iodine channel, I&C personnel placed the auxiliary sample pump in standby readiness. <br /><br /> Subsequently, on June 22, 1994, at 1640 hours, with the plant operating at 100% power, it was determined that the acceptance criteria as specified in the calibration procedure for the Stack High Range Noble Gas Radiation Monitor had not been met since the surveillance began on June 9, 1994. An assessment of the basis for operability of the Stack High Range Noble Gas Radiation Monitor was determined to be operable even though the acceptance criteria of the surveillance procedure was not met. <br /><br /> No safety consequences resulted from this event.
2451994025 | Millstone 1 | 07/26/1994 | 04/07/1995 | 9504180254 | <strong>Isolation Condenser Containment Isolation Valve Timing Failure</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1994, at 1220 while at 100% power (530 degrees F, 1030 psi), the isolation condenser (IC) steam inlet valve did not meet the Technical Specification closing time acceptance criterion during performance of the 'Containment Isolation Valve Operability Demonstration' surveillance test. The cause of the valve exceeding the Technical Specification stroke time was an improper setting of the valve limit switches. The valve was tested to ensure no degradation had occurred and was setup in a short stroked position to meet stroke timing requirements.
2451994027 | Millstone 1 | 07/28/1994 | 08/01/1995 | 9508080178 | <strong>Non-Conservative Flow Biased Scram Setpoint</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1994, at approximately 1030 hours, with the plant operating at approximately forty percent power, it was identified by Reactor Engineering personnel that the Maximum Fraction of Limiting Power Density (MFLPD) had exceeded the Fraction of Rated Power (FRP). When MFLPD exceeds FRP the flow biased Average Power Range Monitor (APRM) scram and rod block setpoints must be adjusted if corrective action is not possible by adjusting the control rod pattern. <br /><br /> This condition had existed from July 27, 1994, at approximately 1030 hours causing the flow biased APRM scram setpoint and the rod block setpoint to be non-conservative until it was discovered the following day. Upon discovery of this condition, immediate corrective action was taken to lower MFLPD below FRP by adjusting the control rod pattern and core flow. <br /><br /> The APRM flow biased scram setpoint is not credited in transient analysis and no safety systems were required to operate as a result of this event. Therefore, there was no impact on plant safety.
2451994028 | Millstone 1 | 08/18/1994 | 09/19/1994 | 9409270299 | <strong>Control Room Habitability Concern Due to Drain Holes on Each SGT System Train</strong><br /><i>Abstract:&nbsp;</i>On August 18,1994 at 1721 hours with the plant operating at 100% power (530 degrees F, 1030 psig), four 1/4 inch round drain ports on the Standby Gas Treatment System (SGTS), two ports per train, previously thought to be plugged were discovered open to the Heating Ventilation and Air Conditioning (HVAC) room atmosphere. These drain ports in the SGTS trains could potentially release radioactivity that would result in radiation levels in the control room greater than that established by the Millstone Unit 1 Updated Final Safety Analysis Report. Specifically, in the event of a postulated design basis loss of coolant accident (LOCA)with SGTS in operation, the 1/4' drain ports upstream of the SGTS filtration system could discharge radioactivity into an area that communicates with the control room. This condition could have rendered the control room uninhabitable. <br /><br /> No safety systems were required to function as a result of this condition.
2451994029 | Millstone 1 | 09/08/1994 | 10/11/1994 | 9410170272 | <strong>MCC Circuit Breaker Not Properly Coordinated</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1994, at 1330 hours, with the plant at 100% power, it was determined that, a molded case breaker on safety related Motor Control Center (MCC) E4 does not coordinate with the MCC supply breaker. This determination was made during a review of coordination requirements for preparation of a plant design change package. An electrical fault on the load side of the breaker could have topped the MCC supply breaker, resulting in loss of power to safety related loads associated with the Feedwater Coolant Injection (FWCI) System as well as the alternate supply to the Instrument AC system. The load on the breaker is a non essential supply to the plant process computer and is not safety related. Until a permanent design change can be implemented, the breaker has been safety tagged open. No safety consequences resulted from this event.
2451994030 | Millstone 1 | 10/05/1994 | 11/03/1994 | 9411100245 | <strong>LPCI Flow Surveillance Inconsistent with Technical Specifications Requirement</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1994, at 1430 hours with the plant operating at 100% power, it was determined that the technical specification surveillance requirement to verify three Low Pressure Coolant Injection (LPCI) pumps deliver 15,000 gpm had not been performed exactly as specified in technical specifications. Instead, individual pump flow rates were obtained and verified to be greater than 5,000 gpm. Additionally, the surveillance requirement to check, calibrate and test the header AP instrumentation had not been performed since the technical specification requirement was inadvertently added in 1981. An analysis of the existing pump flow data was immediately performed which verified the LPCI system would perform adequately to meet the three pump criteria. The LPCI header DELTA P surveillance requirements could never be met since this instrumentation does not exist, nor is any such instrument required. <br /><br /> Three LPCI pumps are not credited in the LOCA analysis and the LPCI system is not designed with a spray header that would require break detection instrumentation. No safety systems were required to operate as a result of this event and there was no impact on plant safety.
2451994031 | Millstone 1 | 10/17/1994 | 01/13/1995 | 9501240198 | <strong>Gas Turbine Start Logic Seal-in</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1994, at 1300 hours, with the plant operating at 100% power, 530F and 1030 psi, a design review concluded that the signal to start the gas turbine generator due to an Engineered Safety Features (ESF) actuation, does not seal-in. The lack of a seal-in can result in the gas turbine generator not completing its emergency start sequence, if the ESF signal clears in the short time interval while the machine is in its startup sequence. Subsequent investigation also revealed that the instrument air compressor in the diesel powered train could inadvertently start if the ESF signal were to clear. These conditions are not in accordance with the provisions of Section 4.16 of Institute of Electrical and Electronics Engineers (IEEE) Criteria for Nuclear Power Plant Protection Systems, IEEE No. 279. An operability evaluation has been performed, and the gas turbine generator and the diesel generator were found to be operable. No safety consequences resulted from this event. <br /><br /> Supplemental information is shown with vertical change bars.
2451994032 | Millstone 1 | 11/15/1994 | 12/15/1994 | 9412270247 | <strong>Failure to Complete Daily Surveillances</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1994, it was discovered that during the previous refueling outage, with the plant in cold shutdown (161 degrees Fahrenheit and 0 psig), a daily Technical Specification surveillance was not performed within the required frequency. Specifically, the daily Reactor Protection System Inoperable and Control Rod Disarming surveillances, required when the reactor protection system and control rod block trip functions are bypassed with fuel in the reactor vessel, were not performed within the daily surveillance time interval requirement. These surveillance requirements had been satisfactorily performed for several weeks prior to this event and continued to be satisfactorily performed following the event. <br /><br /> In addition to the missed technical specification surveillance requirement, the reporting requirements associated with this event were not recognized. <br /><br /> No safety systems were required to function as a result of this event.
2451994033 | Millstone 1 | 11/24/1994 | 09/29/1995 | 9510110154 | <strong>Main Steam Safety/Relief Pilot Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On November 24,1994, the plant was shutdown due to main steam system safety/relief valve (SRV) pilot valve leakage. An evaluation determined that the SRV pilot valve leakage could cause one or more of the SRVs to be inoperable due to the setpoint drift induced by the leakage. <br /><br /> In addition, on November 30, 1994, with the plant still shutdown for replacement of the leaking SRVs, bench testing of the six pilot valve assemblies which had been removed indicated that all six of the valves lifted at pressures in excess of the Technical Specification limit. <br /><br /> This LER has been suplemented to provide updated information on NNECO's initiatives to improve the performance of the Target Rock Model 7567F Safety/Relief Valves in use at Millstone Unit 1. This supplemental information is included in Section IV (Corrective Action).
2471994001 | Indian Point 2 | 01/26/1994 | 02/25/1994 | ML10043088 | <strong>ESF and Emergency Diesel Generator Actuation</strong><br /><i>Abstract:&nbsp;</i>At 1440 hours on January 26, 1994, with the plant at 100% power, the inservice 138 kv feeder from Buchanan Substation to the IP2 station auxiliary transformer experienced a phase to ground fault. Protective relay/breaker operation resulted in a loss of power to 6.9 kv buses 5 and 6 and 480V buses 5A and 6A as designed. Power was therefore lost to two circulating water pumps causing a reduction in condenser vacuum and a load reduction of approximately 60 MWe. <br /><br /> All three emergency diesels automatically started as designed upon loss of 480V buses 5A and 6A. Buses 5A and 6A were then re-energized from their respective diesels, and equipment supplied by these buses was restored in accordance with Station Procedures. At 1541 hours, power was restored to 6.9 kv buses 5 and 6 from a 13.8 kv source. 480V buses 5A and 6A were reconnected to their 6.9 kv sources and the diesels were secured. At 1646 hours the station auxiliary transformer was re-energized from the alternate 138 kV feeder to provide power to 6.9 kV buses 5 and 6. <br /><br /> Upon the loss of power all fan cooler units entered the incident mode. This occurred because one train of the two trains of associated solenoid operated valves (SOV's) was being energized from 480V bus 6A. One charcoal outlet valve of one of the five fan cooler units did not open as expected with the loss of power (the valve did stroke properly when its control switch was operated). A SOV associated with this valve was subsequently replaced.
2471994002 | Indian Point 2 | 04/02/1994 | 05/02/1994 | ML10043088 | <strong>Entry into Technical Specification 3.0.1. on IVSWS</strong><br /><i>Abstract:&nbsp;</i>On Saturday, April 2, 1994, an entry into Technical Specification 3.0.1 took place. The initiating event was corrected within the one hour allowed for trouble shooting and a plant shutdown was not commenced. <br /><br /> On April 2, 1994, Indian Point 2 was operating at 90% steady state power. At approximately 0100 on April 2, 1994, a tag out was applied for purposes of making repairs to a valve in the Nitrogen System, SGN-41. The tag out isolated the Nitrogen System from the Isolation Valve Seal Water (IVSW) system. The IVSW system has its own supply of nitrogen in the form of pressurized nitrogen bottles. However, due to a procedural discrepancy, the IVSW nitrogen bottles were isolated. Therefore, the tag out for valve SGN-41 effectively isolated the nitrogen supply to the IVSW tank.<br /><br /> At 0725 an alarm was received in the Central Control Room (CCR) because the IVSW tank pressure was less than 54 psig. An operator was dispatched to investigate the problem per the Alarm Response Procedure. The IVSW tank pressure was found to be at 49 psig. The operator took immediate action to restore the IVSW tank pressure and at 0815 the pressure was greater than the Technical Specification 3.3.C.1.b pressure of 52 psig. There is no Limiting Condition for operation (LCO) action statement when the requirements of Technical Specification section 3.3.C.1.b cannot be met and therefore Technical Specification 3.0.1 was entered. Because the low pressure condition in the IVSW tank was corrected in less than one hour a plant shutdown was not commenced.
2471994003 | Indian Point 2 | 11/02/1994 | 12/02/1994 | ML10166044 | <strong>Inadvertent Start of Component Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1994, with the unit operating at 89% power, two component cooling water pumps were inadvertently started during the calibration of a flow switch. The inadvertent start occurred when a switch circuit lead was lifted by a technician in accordance with a procedure. Upon the start of the pumps, the calibration procedure was suspended, the switch circuit lead reattached and the pumps secured and returned to automatic. At no time during this event were the two component cooling water pumps needed to fulfill a safety related function, nor was the portion of the circuitry which started these pumps associated with Engineered Safety Feature (ESF) actuation logic.
2471994004 | Indian Point 2 | 11/05/1994 | 12/05/1994 | ML10043089 | <strong>Inadequate Mounting of Control Rod Drive Fan (CRDF)</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1994, with the unit operating at 89% power, house maintenance crews completed the replacement of 22 Control Rod Drive Mechanism Cooling Fan (CRDF). The fan motor had failed on November 3, and was replaced over the course of several shifts. When the fan was remounted on the reactor missile shield blocks, the lower fan support bolts which mount the fan to the support bracket and to the fan intake duct were out of alignment and could not be reinstalled. The work crew then connected the duct to the fan and support bracket with high strength cable ties to close the gap between the duct and fan, thereby minimizing air inleakage to the duct. This physical arrangement was then reported to and subsequently evaluated by engineering staff and found to be inadequate to support the fan. The fan was removed and later reinstalled in accordance with engineering guidance.
2491994001 | Dresden 3 | 02/26/1994 | 03/21/1994 | 9408170130 | <strong>Containment Atmosphere Monitor Check Valve 3-2499-28B Exceeded Technical Specification Leakage Limit of 0.6 L sub a Due to Foreign Materials on Seat</strong><br /><i>Abstract:&nbsp;</i>At approximately 1330 hours on February 26, 1994 with Unit 3 in the Run mode at 64% power. While performing the operational Local Leak Rate Test (LLRT) Special Procedure (SP 93-8-73) of the 3-2499-28B (3-B H**2 O**2 monitor return line lift check valve made by Rockwell International) leakage exceeded the capacity of the flowmeters by an undetermined amount. The Technical Specification leakage limit of 0.6 L sub a was exceeded per Dresden Technical Specification 3.7.A.2.b(2)(a). Upon internal inspection of the check valve, black debris wall found between the seating surfaces holding the seats open a sufficient amount to fail the leak rate test. The Mechanical Maintenance department cleaned the valve internals and made a final visual inspection. No physical damage to valve internals was found. The valve was closed and leak tested. Final leakage of zero was recorded. This is a reoccurring problem and redesign is being evaluated.
2491994002 | Dresden 3 | 01/05/1994 | 02/04/1994 | 9410210269 | <strong>Process Line Primary Containment Isolation Valves Never Subjected to Type C Local</strong><br /><i>Abstract:&nbsp;</i>At approximately 1750, on January 5, 1994 with Unit 3 operating at 79% power, as a result of a walkdown of primary containment penetration X- 141, it was determined that a process line, which taps off an instrument line upstream of the excess flow check valve, had primary containment isolation valves which had never been given a proper 10 CFR 50, Appendix J Type C Local Leak Rate Test (LLRT). The process line, which was used to obtain Reactor Coolant Samples, had rarely been used since Unit 3 Start Up Testing. The sample line, which was added to the Piping and Instrumentation Diagram as a result of a system walkdown in 1990, was determined to be an undocumented plant modification. The sample line, which is pressurized by 1000 psig reactor coolant, shows no evidence of leakage. The piping and valves, per the Master Equipment List, are ASME Section XI class 1 components as well as seismically qualified. Therefore, the safety significance is considered to be minimal. Upon identification of the problem, the sample line primary containment isolation valves were taken Out-of-Service in the closed position per Technical Specification 3.7.D.2. As-found Type C leak testing was performed and the valves were not leaking. The process line has been subsequently removed with the welded end cap being subjected to a Hydro and an Appendix J Type A test.
2491994003 | Dresden 3 | 01/19/1994 | 02/16/1994 | 9402240015 | <strong>Reactor Vessel level Instrumentation Found Outside of Technical Specification Limits Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1994, at 1340 hours, with Unit 3 at 74% rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 0500-03, Contact 7/8 of Emergency Core Cooling System (ECCS) Initiation Level Indicating Switch 3-263-72B failed to trip on a low Reactor Water Level signal. Level Indicating Switch (LIS) 3-263-72B Contact 7/8 is part of the Core Spray System 2 and Automatic Depressurization System (ADS) -59 inch initiation one out of two twice logic. The necessary redundant switches were available during this event allowing both systems to remain operable. The contacts were readjusted and tested satisfactorily using DIS 0500-03. The Safety Significance of this event is minimal since the redundant switches that make up the one out of two twice logic were available throughout this event. This event is not isolated. For the years 1992 and 1993, the ECCS initiation contacts of LIS 2(3)-263-72A(B)(C)(D) have been found to be out of their administrative calibration limit (in a non-conservative direction per DIS 0500-03) during their monthly surveillance tests a total of 54 times. Twenty-nine (29) of these events were outside of the Technical Specification surveillance limit.
2491994004 | Dresden 3, Dresden 2 | 02/03/1994 | 12/12/1994 | 9412150167 | <strong>Dresden Unit 3 Inability to Meet Technical Specification 3.9 Limiting Condition for Operation Due to Redundant Emergency Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1994 during performance of the High Voltage Rounds, the High Voltage Operator (HVO) discovered that the Unit 2/3 Emergency Diesel Generator (EDG) Air Start System regulator had drifted up, creating a downstream pressure of approximately 245 psig. Attempts to adjust the regulator failed to achieve a pressure setting of 175-190 psig. Upon further inspection of the air start components, it was identified that the air start motors had a nameplate rating of 200 psig. A concern was raised as to the integrity of the airstart motors and other system components downstream of the air regulator which were potentially subjected to an air pressure higher then the nominal range 175-190 psig. The redundant Unit 3 EDG had been inoperable since February 2, 1994 at 0902 hours pending an investigation into the cause of a High Crankcase Pressure trip received during the performance of the monthly operability surveillance. The Unit 2/3 EDG was declared inoperable and Unit 3 entered into a 24 hour Limiting Condition for Operation (LCO) and Unit 2 entered into a 7 day LCO. <br /><br /> The root cause of the regulator leak is attributed to improper component selection. The root cause of the High Crankcase Pressure trip is lack of preventative maintenance resulting in water intrusion of the lube oil. The existing regulators will be replaced with the vendor recommended Norgren regulators. The lube oil cooler will be inspected/replaced on a vendor recommended frequency of twelve years.
2491994005 | Dresden 3, Dresden 2 | 04/11/1994 | 05/04/1994 | 9405170247 | <strong>Non Conservative Second Level Undervoltage Protection Relay Settings Due to Defective Testing Equipment</strong><br /><i>Abstract:&nbsp;</i>During a routine calibration of second level undervoltage relays removed from 4160 Volt Bus 34-1, the as found settings were found out of tolerance in the non-conservative direction. The relays had been replaced prior to the calibration. The cause of the non-conservative settings was identified to be a defective power supply used for the bench calibration. Unit 2 second level undervoltage protection was conservatively declared inoperable at 1500 hours on April 13, 1994, and Unit 2 entered Action 1 to Technical Specification Table 3.2.2, a 24 Hours to Shutdown Limiting Condition for operating (LCO). Commonwealth Edison Company requested Enforcement Discretion with NRC Region III, and received verbal approval to delay completion of Action 1 until April 20, 1994. No power reductions were commenced. Unit 3 Bus 33-1 second level undervoltage relays were replaced, and the as found settings of the removed relays were also out of tolerance. The relays for Unit 2 4160 Volt Buses 23-1 and 24-1 were found out of tolerance and recalibrated. Unit 2 exited the LCO on April 15, 1994 at 1415 hours. Unit 3 was in a refueling outage during the event, and second level undervoltage protection was not required. This is the first reported instance of this type.
2491994006 | Dresden 3 | 03/03/1994 | 03/31/1994 | 9404080221 | <strong>Unit 3 HPCI Isolation Motor-Operated Valves Declared Inoperable Due to High Valve Factors</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1994, at 1820 hours, with Unit 3 at 63% power, Dresden Site Engineering (SEC) informed the OperationS Department of the potential inoperability of the High Pressure Coolant Injection (HPCI) Turbine Steam Supply inboard and outboard containment isolation motor-operated valves (MOVs) 3-2301-4 and 3-2301-5, respectively. This was a result of a review performed by SEC, of EPRI testing documentation in which various MOV configurations were subjected to high differential pressure (blowdown) conditions. SEC determined that the two HPCI MOVs would require greater thrust output than previously calculated to overcome valve internal frictional forces and perform their isolation Safety function. Operations entered a 7-day Tech Spec LCO by closing both HPCI valves and declaring the HPCI system inoperable. These events resulted in Unit 3 being shutdown and commencing D3R13 refuel outage at 2040 on March 9, 1994 in accordance with Technical Specification 3.5.C. The safety significance of this event was considered minimal because of the ability of the MOVs to isolate steam line leaks and the low probability of a complete steam line rupture (blowdown condition). Operability Assessments were performed for the remainder of Unit 2 and 3 Blowdown MOVs. Corrective actions for the Unit 3 Blowdown MOVs include the implementation of upgrade modifications to the existing MOV configurations during the D3R13 outage. The Unit 2 Blowdown MOVE received these modifications during the D2R13 refuel outage (Winter 1993).
2491994007 | Dresden 3 | 03/16/1994 | 04/11/1994 | 9404140183 | <strong>Yarway Reactor Water Level Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1994 at 0845 hours, with Unit 3 at 0 % rated core thermal power, while performing Dresden Instrument Surveillance (DIS) 0500-03, Reactor Water Level ECCS Initiation Indicating switch calibration , level switch 3-263-72A contact 5-6 tripped outside of the Technical Specification (TS) limits. Level Indicating Switch (LIS) 3-263-72A is part of the High Pressure Coolant Injection (HPCI) and Low Pressure Coolant Injection (LPCI) Loop 1, -59' RWL initiation one out of two/twice logic. The TS limit is 114.5' water column (WC), however, the switch was actuated closed at 114.7' WC. The switch was exercised and returned to within tolerance. No adjustments or corrective maintenance was required. The necessary redundant switches were available during the event allowing both systems to remain operable. Previous events involving the failure of similar Yarway configurations are documented in 'Operability Assessment' of February 17,1994 (Chron 0124505) written in response to LER 93-031/050237.
2491994008 | Dresden 3 | 03/11/1994 | 05/12/1995 | 9506010134 | <strong>Anticipated Transient Without Scram (ATWS) Trip Time Delay Failure Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1355 hours on March 11, 1994, with Unit 3 in the Refuel Mode, during the performance of Dresden Instrument Surveillance (DIS) 0260-06, 'Anticipated Transient Without Scram (ATWS) [JC] Transmitter and Master Trip Unit Calibration and Logic System Functional Test', time delay relay 3-0260-K101D tripped at 32.29 seconds and relay 3-0260-K101C failed to time out. 'Recirculation Pump Trip Initiation', requires that the time delay be greater than or equal to 8 seconds and less than or equal to 10 seconds. The relay failures were a result of component aging and cycling. Under Work Request D21641, both relays were removed and replaced. The root cause of this event was incomplete corrective actions from a previous event. The original relays were not replaced in a timely manner.
2491994009 | Dresden 3 | 03/12/1994 | 07/24/1995 | 9507270184 | <strong>Type B and C Leakage Limit Exceeded Due to Valve 3-1301-3 Not Fully Closed</strong><br /><i>Abstract:&nbsp;</i>At approximately 1800, on March 12, 1994, with Unit 3 in Refuel Outage D3R13, the performance of Dresden Technical Surveillance, Local Leak Rate Testing Of Primary Containment Isolation Valves, identified the Isolation Condenser System Condensate Return Throttling Valve 3-1301-3 to be leaking an undetermined amount. This value when added to the existing maximum pathway leakage rate resulted in the maximum pathway leakage rate limit for Type B and C primary containment leakage being exceeded. Trouble-shooting determined that the Motor Operated Valve had not closed completely when stroked for draining the system. After the valve was closed using primary containment isolation logic another LLRT was performed and leakage was determined to be 5.3 scfh. The safety significance of not fully closing the 3-1301-3 valve for the LLRT is considered minimal since when the valve was fully closed with primary containment isolation logic an acceptable LLRT was obtained. This supplement contains the root cause, corrective actions taken and results of an NPRDS search for all test volumes that exceeded administrative local leakage limits during Refuel Outage D3R13.
2491994010 | Dresden 3 | 03/11/1994 | 04/08/1994 | 9404130142 | <strong>Reactor Scram While Unit was Shut Down Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 2015 on March 11, 1994, a Reactor Scram wall received while Instrument Maintenance Department (IMD) was performing Dresden Instrument Surveillance procedure (DIS) 700-4, Intermediate Range Monitor (IRM) surveillance. The Nuclear Station Operator (NSO) reset the scram per Dresden General Procedure (DGP) 2-3 and in attempting to return the Control Room panels to an 'as normal' condition as soon as practicable, the NSO placed the Scram Discharge Volume (SDV) Reactor Scram bypass switch back to the 'normal', position before the volume had drained down. This resulted in a second scram signal. The first scram signal was spurious due to an IRM spiking, the second scram signal was due to personnel error. The Unit 3 reactor was in refueling outage so consequences of the event are negligible.
2491994011 | Dresden 3 | 03/25/1994 | 12/31/1997 | 9801070344 | <strong>Loss of Power to Bus 34 Resulted in Auto-Start of Unit 3 Emergency Diesel Generator Due lack of preventive maintenance on Bus Pots.</strong><br /><i>Abstract:&nbsp;</i>At 2355 on March 25, 1994, multiple alarms were received on panels 903-8, 903-5, 902-4, 923-2, 923-5, and many of the lights on the Unit 3 side of the Control Room went off. This caused a Unit 3 Half Scram, Standby Gas Treatment (SBGT) auto-start and auto-start of Unit 3 Emergency Diesel Generator (EDG) which closed onto bus 34-1. Bus 34 indicated a low voltage condition (via panel meters and white bus energized light out) with the feed breaker from Transformer (TR) 32 to Bus 34 indicating closed. The loss of power to Bus 34 was caused by corrosion buildup on the Bus Pots due to lack of preventive maintenance. A continuing program of preventive maintenance on the Bus Pots has been implemented.
2491994012 | Dresden 3 | 03/07/1994 | 04/20/1994 | 9404260338 | <strong>Engineering Review Required For Lasalle RCIC Investigation</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER. Following investigations of the RCIC [BN] Rupture Diaphragm Failure Event which occurred at LaSalle County Station on February 21, 1994, Dresden Station discovered that the vent path did not exist to Unit 3 PS 2355, HPCI [BJ] Rupture Diaphragm High Pressure Alarm. The discovery was made on March 7, 1994. This pressure switch is located between the inner and outer rupture diaphragms on the High Pressure Coolant Injection (HPCI) turbine discharge line to provide an alarm should the inner rupture diaphragm fail non-catastrophically. The purpose of the vent is to allow the inner rupture disk to flex with pressure fluctuations in the HPCI turbine discharge line without affecting the outer disk. Without the vent line, flexing of the inner diaphragm causes a pressure increase between the inner and outer diaphragms. This results in the flexing and potential work hardening of the outer diaphragm. The work hardening may result in a decrease in rupture diaphragm life. Work Request D24604 was initiated to re-establish a vent path to the pressure switch. Since the condition of the vent line only affects the outer rupture diaphragm performance, and does not affect the inner rupture diaphragm performance, the safety significance of this event is minimal.
2491994013 | Dresden 3 | 05/19/1994 | 06/18/1994 | 9406220030 | <strong>Missed Tech Spec 4..6.I.1.b Surveillance (Snubber Visual Inspection)</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1994 at 1000 hours, an unidentified snubber, subsequently labelled 3-1626-02, was found in the Torus [BT] Basement of Unit 3. This snubber was on the safety-related line, 3-1626-1', which is the lower leg of level transmitter, LT 3-1626, which starts from the Torus penetration X-305D. It was determined on May 25, 1994 that the Unit 3 Technical Specification 4.6.I.1.b was missed for this particular snubber since installation. This Technical Specification requires a visual inspection of all safety-related snubbers at most, once every eighteen months (plus or minus) 25%. Modification M12-3-88-41C included the installation of this snubber which was authorized for operation on February 2, 1990. The snubber was installed due to a seismic evaluation of Torus-attached piping. The root cause for this event is attributed to a modification process that did not identify the Technical Specification requirement. The safety significance of this event is minimal since no anomalies or apparent decline to the functionality of the snubber were found. The corrective actions will include a review of all modifications since January 1, 1980 for any snubber additions and a review of the snubbers added due to the Torus-attached piping seismic evaluation. No other occurrences of this event were found.
2491994014 | Dresden 3 | 07/14/1994 | 08/30/1994 | 9409140020 | <strong>Unit 3 Torus/Reactor Building Relief Valves Cycled due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1994, with Unit 3 in a refueling outage, the Torus Vacuum Breakers, 1601-20A and 1601-20B, cycled due to negative pressure in the suppression chamber. The cause of the event was due to closing the torus hatches with the Drywell and Torus Purge fan in operation while aligned to the torus only. The vacuum breakers began to cycle when the torus reached approximately -0.46 pounds per square inch differential (psid) between the reactor building and the torus. The Technical Specification requires the vacuum breakers operate at -0.5 psid between the reactor building and torus. The Unit 3 Nuclear Station Operator (NSO) was alerted by actuation of the 'TORUS VACUUM RELIEF VALVE NOT CLOSED' annunciator alarm, and he observed the vacuum breakers cycling. Also, the Mechanical Maintenance Department personnel, responsible for closing the last torus hatch, observed the vacuum breakers cycling and called the control room to inform the operator. The Unit 3 NSO closed the 18 inch torus purge suction valve, 1601-60, and the torus vacuum breakers stopped cycling within approximately 20 seconds.
2491994015 | Dresden 3 | 05/16/1994 | 06/15/1994 | 9406210263 | <strong>CCSW Vault Watertight Door And Penetration Seals Failed Leak Test</strong><br /><i>Abstract:&nbsp;</i>While Unit 3 was shutdown for the D3R13 Refueling Outage, Dresden Technical Surveillance (DTS) 1500-01, Containment Cooling Service Water (CCSW) [BO] Pump Vault Watertight Door Leak Test, was performed on May 23, 1994 at 1545 hours. When the test was performed, 1.1 gallons of water was collected in one hour, which is greater than the 1 gallon per hour Technical Specification limit. The source of the leakage was observed to emanate from the primary latching mechanism on the door. This leakage was due to premature degradation of the primary packing caused by procedural inadequacy. Also, Dresden Technical Surveillance (DTS) 0030-1, CCSW Pump Vault Penetration Surveillance Testing, was performed on May 16, 1994 at 1655 hours. All penetrations, less one, showed some initial leakage. This penetration leakage was quickly eliminated by tightening the seal and re-testing. Penetration MK-852 would not meet the acceptance criteria of the test and was replaced using sealant. Seal MK-852 had leakage which was due to a non-smooth surface in the sleeve where it was installed. Due to the quantity of leakage and the ample warning which would be received in the control room during a flooding event, the safety significance of this event is minimal.
2491994016 | Dresden 3 | 06/06/1994 | 07/01/1994 | 9407060135 | <strong>Unplanned Partial Group II Primary Containment Isolation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1994, with Unit 3 in refuel mode an unplanned partial Group II Primary Containment Isolation signal was received while attempting to open the Drywell and Torus Vent to Reactor Building Exhaust (3-1601-24) Valve. The partial isolation signal affected a total of fourteen Group II Primary Containment Isolation valves. Of the fourteen affected valves, four valves were observed to cycle to the isolated (closed) position. The remaining ten valves were closed and/or Out-of-Service at the time of the event. The cause of the event was determined to be a ground located on the spliced connection to the local pilot solenoid of valve 3-1601-24. The root cause of the event was attributed to personnel error while performing a maintenance activity. The safety significance of the event was considered minimal since Unit 3 was in the Refuel mode and primary containment integrity was not required. The damaged splice was repaired, Group II Primary Containment Isolation logic was reset, and valve 3-1601-24 was successfully tested.
2491994017 | Dresden 3 | 06/30/1994 | 07/24/1994 | 9408020196 | <strong>Group I Primary Containment Isolation Due to Instrument Rack Vibration</strong><br /><i>Abstract:&nbsp;</i>At 1408 on June 30, 1994 with Unit 3 in a shutdown mode for D3R13 refueling outage, a Primary Containment Isolation Group I alarm was received in the Control Room. The inboard Main Steam Isolation Valves (MSIV) and inboard Recirculation sample isolation valves closed. The associated outboard isolation valves were closed and tagged out-of service at the time, and did not move. <br /><br /> Plant parameters that could cause a Group I isolation were checked, and no abnormal conditions were observed. The alarm and isolation had occurred concurrently with a start of the of 3B Containment Cooling Service Water (CCSW) Pump, so CCSW piping was walked down to determine wheather there had been a piping pressure transient (water hammer) in the system sufficient to vibrate the Group I instrument racks. No indications of pipe or restraint movement or damage were found. <br /><br /> While the root cause of the Group I alarm and isolation could not be positively determined, it is stongly believed that the instrument rack had been inadvertently jarred by workers in the area.
2491994018 | Dresden 3 | 08/06/1994 | 09/05/1994 | 9409160342 | <strong>Unit 3 Reactor Scram on Low Level Due to Programmatic Deficiency and Human Error</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1994, at 07:40 hours, during plant startup, Unit 3 scrammed from 3W reactor power on Low Reactor Water Level. While attempting to place a third Condensate Demineralizer into service, the operating shift crew became distracted monitoring Condensate/Condensate Booster (C\CB) pump amps and demineralizer differential pressure, and failed to monitor reactor water level. In the course of manipulating the C/CB pump minimum flow bypass valve to control amps and demineralizer differential pressure, the valve was fully opened, diverting nearly all condensate flow to the Main Condenser. Reactor water level decreased to the scram setpoint. <br /><br /> The C/CB pump minimum flow valve was closed down to establish normal flow. Recovery from the Scram was completed per procedures and the reactor was cooled down to cold shutdown condition. The licensed operators involved in the event were temporarily relieved of shift duties to assess their performance and assist in the investigation of the event.
2491994019 | Dresden 3 | 10/26/1994 | 11/23/1994 | 9411300271 | <strong>Reactor Scram Due to Instrument Valving Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 0126 hours on October 26, 1994, Unit 3 was in the Refuel mode, with Dresden Instrument Surveillance (DIS) 500-01, Reactor Vessel High Pressure Scram Pressure Switch Calibration, in progress. As pressure switch 2-263-55C was being returned to service, a full RPS scram, Group II isolation and Group III isolation occurred on a reactor vessel low water level signal. All control rods were fully inserted before the scram, therefore no control rod motion occurred. All isolation valves and the Standby Gas Treatment System responded as expected. There was no measured change in reactor coolant temperature while the Shutdown Cooling System was isolated. Pressure switch 2-263-55C has a common sensing line to reactor vessel water level transmitters 2-263-57C and 2-263-57D which provide signals to the reactor protection system and primary containment isolation system. The event was caused by a pressure transient produced while valving in pressure switch 2-263-55C with a differential pressure across the isolation valve. There have been two previous events involving instrument valving.
2491994020 | Dresden 3 | 10/29/1994 | 11/16/1994 | 9411300286 | <strong>Unit 3 Unexpected Full Reactor Scram while Shutdown During Special Test</strong><br /><i>Abstract:&nbsp;</i>During the performance of Special Test Procedure SP 94-10-126, Special Procedure to Determine Root Cause of Scram While Performing Reactor Vessel High Pressure Scram Pressure Switch Calibration, an unexpected full reactor scram signal occurred while the unit was shutdown in refuel mode. The full scram occurred when the Control Systems Technician (CST) performing the valve manipulations on Instrument Rack 2203-6 inadvertently opened the bypass valve on the deadweight tester to reduce the pressure on PS 3-263-55C, Reactor Vessel High Pressure Scram Pressure Switch. Recognizing this error, the CST closed the bypass valve. The pressure transient resulting from this valve manipulation produced a momentary Reactor Protection System (RPS) Reactor Vessel Low Level Scram signal. There was no change in actual Reactor Vessel Level. All safety Systems functioned as required.
2491994021 | Dresden 3 | 11/08/1994 | 11/29/1994 | 9412080194 | <strong>Failure to SCRAM of CRD E-10 due to Spring Disengaged From the Core Assembly of a SCRAM Solenoid Pilot Valve</strong><br /><i>Abstract:&nbsp;</i>At 0445 hours on November 8, 1994 with Unit 3 at 25% rated power while performing SCRAM Testing per Dresden Technical Surveillance (DTS) 300-2, Control Rod Drive (CRD) [AA] E-10 failed to SCRAM from the control room. The CRD was inserted to Position '00' and taken out-of-service (OOS). The failure to SCRAM was attributed to failure of the V118 SCRAM Pilot Solenoid Valve (SSPV) to operate. Both SSPVs were removed from the hydraulic control unit (HCU) and sent to the manufacturer (ASCO) for autopsy. Upon disassembly of the V118 pilot head assembly, the spring was found disengaged from the core assembly. When the SSPV is de-energized, the absence of the spring force, caused by the detached spring, prevented proper retraction of the core assembly to discharge the pilot head air. Both SSPVs were replaced on HCU E-10 and the CRD was successfully SCRAM Tested and returned to service. Both Dresden and the industry have had previous similar failures. G.E. and ASCO have stated that this was an isolated incident.
2491994022 | Dresden 3 | 12/14/1994 | 01/07/1995 | 9501200067 | <strong>Control Rod Drive Insert/Withdraw Lines Outside Design Basis Due to Inadequate Seismic Supports</strong><br /><i>Abstract:&nbsp;</i>It was discovered on 12/14/94 that the insert and withdraw lines for Control Rod Drive (CRD) [AA] M-8 had branch connections installed on both lines. The branch lines were installed during initial construction in 1971 to facilitate CRD testing. The branch lines were not seismically supported. This condition caused the insert and withdraw lines to fall outside of design basis.
2501994001 | Turkey Point 3, Turkey Point 4 | 01/19/1994 | 07/26/1994 | 9408040239 | <strong>Failure of Emergency Containment Cooler Component Cooling Water Discharge Solenoid Valves</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1994, a failure of SV-4-2924 to fully change position occurred. This resulted in an unsatisfactory Technical Specification surveillance on an emergency containment cooler. SV-4-2924 is a solenoid-operated valve supplying air to operate flow control valves for the component cooling water discharge from the emergency containment coolers. The solenoids are normally energized. There are three of these valve configurations on Unit 3 and three on Unit 4. This was the third failure of this type since November 11, 1993. Two of these three failures have occurred since the frequency of exercising the solenoid valves was administratively changed to once per week after the November 11 failure. One failure occurred on each unit. <br /><br /> All three surveillance failures were caused by failure of the solenoids to change position when de-energized, but at no time were more than one ECC inoperable. <br /><br /> The valve failures were caused by degradation of the lubricant, resulting in increased friction between the disc and seat, which in turn caused incomplete shifting to the de-energized position. <br /><br /> Interim corrective action was to exercise the solenoid valves once per day. Final corrective action was to change the solenoid valves from a de-energize to actuate to energize to actuate configuration. <br /><br /> This condition was reported by the vendor as a 10CFR21 notification on July 7, 1994.
2501994002 | Turkey Point 3, Turkey Point 4 | 05/05/1994 | 05/31/1994 | 9406070088 | <strong>Inadvertent Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1994, with Turkey Point Unit 3 in Mode 5, while restoring power to the safeguards racks, a spurious actuation of the 3A safety injection signal occurred. This spurious signal resulted in the actuation of the 3A channel of engineered safeguards. The Unit 3 A train signal initiated the 3A, 4A, and 4B sequencers which started all four Emergency Diesel Generators as well as other engineered safety features which were in service at the time. The actuation occurred when a safety injection block relay failed to maintain the block signal after power application to the relay racks. The cause was an intermittent seal-in contact failure of a block relay. <br /><br /> All equipment operated as designed except the 4A safety injection pump which did not start. This failure to start has been concluded to be an intermittent failure mechanism which could not be duplicated during trouble-shooting. <br /><br /> To replace the suspect relay causing the failure of the 4A pump to start, the 4A sequencer had to be taken out of service for a short time. This short out-of-service time required the plant to comply with Technical Specification Table 3.3-2, Action 23. This action requires that the sequencer be returned to service within one hour or further action on Unit 4 be taken. The duration during which the 4A sequencer was out of service was 17 minutes. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv).
2501994003 | Turkey Point 3, Turkey Point 4 | 07/20/1994 | 08/16/1994 | 9505190285 | <strong>Nine Missed Surveillance Due To Personnel Error; Quarterly Valve Stroke Timing Required By Inservice Test Program</strong><br /><i>Abstract:&nbsp;</i>On July 20 and 21, 1994, with both units operating at about 100% power, Florida Power & Light Co. discovered that several required valve stroke time surveillances had not been performed. The missed surveillances involved a total of 9 quarterly surveillance procedures, a Total of 20 valves, and covered a period of about 16 months from January 1993 to April 1994. <br /><br /> The root cause of this event is personnel error in that the IST Coordinator did not ensure that the scheduling was adequate to ensure that the associated valve timing surveillances were performed. He is responsible for ensuring IST program changes are incorporated into plant procedures, for ensuring conformance to plant procedures pertaining to IST testing, and for reviewing the completed surveillances to trend the valve stroke times. <br /><br /> All 20 valves have had satisfactory stroke time surveillances performed in the current quarter, so there is no present operability concern. Review of maintenance history showed that none of the valves were inoperable during the quarters in which the surveillances were missed. Therefore the health and safety of the public was not, and is not now, at risk. <br /><br /> Corrective actions included review of maintenance and surveillance history for other missed stroke time surveillances, reassignment of personnel, and enhancement of procedures and surveillance tracking software.
2501994004 | Turkey Point 3 | 11/03/1994 | 11/10/1994 | 9411150397 | <strong>Unit 3 Outside The Design Basis Due To Two Of Three Required Safety Injection Pumps Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0906 EST on November 3, 1994, during performance of the Unit 4 'A' train safeguards testing required by Technical Specifications, the two Unit 3 high head safety injection pumps' control switches were incorrectly placed in a pull-to-lock position. This configuration resulted in both Unit 3 high head safety injection pumps being inoperable. The Unit 4A safety injection pump was functional but technically inoperable due to the requirements of the safeguards procedure. Additionally, the 4B pump was operable throughout this event. Recovery from this condition of the plant, assuming an accident, is covered under Turkey Point Emergency Operating Procedures. Since the current licensing basis assumes two high head safety injection pumps, the functionality or operability of the 4A and 4B pumps provide the systems required. <br /><br /> The cause of this event was human error by a licensed operator while performing the safeguards test procedure on Unit 4. The condition was discovered by Operations management in its oversight role.<br /><br /> Corrective actions have been put in place to enhance communications and revise procedures to ensure correct system alignment.
2501994005 | Turkey Point 3, Turkey Point 4 | 11/03/1994 | 07/17/1995 | 9508080294 | <strong>Design Defect In Safeguards Bus Sequencer Test Logic Places Both Units Outside The Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1994, Turkey Point Unit 3 was in Mode 1 at 100% power, and Unit 4 was in Mode 5 d uring a refueling outage. During the Unit 4 Integrated Safeguards Test, the 3A sequencer failed to respond to the Unit 4 Safety Injection signal. A defect w as found in the sequencer software logic which, for a limited period of time, c ould inhibit any or all of the four sequences from responding to specific valid signals. The defect only affects the sequences during manual or automatic tes ting. The sequences were installed in late 1991.<br /><br /> Monthly manual testing of t he sequencer has been resumed. Front panel visual examinations are being perfo rmed every 8 hours, and internal visual examinations are being performed every 24 hours. A permanent repair to the software logic is being evaluated. Indepe ndent consultants performed an assessment of the existing sequencer design, sof tware design, and the Validation and Verification process. Two other conditio ns were discovered, one involving Containment Spray (CS) pump autostart, and on e involving the 480 Volt Load Center feeder breaker autoclosure. Both were det ermined to have minimal safety significance. The CS system and the 480 Volt Loa d Centers remain operable.
2501994006 | Turkey Point 3 | 12/26/1994 | 01/20/1995 | 9501310304 | <strong>Automatic Reactor Trip\Turbine Trip Due To Main Feedwater Control Valve Failing Closed</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1994, Turkey Point Unit 3 was in Mode 1 at 100% power. At 0141, Eastern Standard Time, the 'C' main feedwater control valve failed closed. After the valve closed an automatic reactor trip/turbine trip occurred after a Steam Generator Water Level - Low Coincident With Steam/Feedwater Flow Mismatch trip signal was received. The valve closed because a screw terminal found loose on the 'C' valve electro-pneumatic transducer caused an intermittent open circuit which resulted in a closed valve position demand to the feedwater control valve. The transducer was replaced. Operation of the valve was monitored prior to the trip and subsequent to the return of the plant to full power.
2511994001 | Turkey Point 4 | 02/23/1994 | 03/21/1994 | 9403280013 | <strong>Missed Surveillance On Steam Generator Protection Channels</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1994, Florida Power and Light Company personnel discovered that Technical Specification required Analog Channel Operational Tests (ACOTs) had not been performed within the surveillance interval. The set of procedures not completed address ACOTs on three cabinets containing Steam Generator Protection Channels. This procedure set fulfills the requirements of Technical Specifications Table 4.3-1 Item 12 and Table 4.3-2, Items 1.e, 1.f, 4.d, and 6b for Channel III. <br /><br /> The last surveillances of these channels were completed on January 14, 1994. The surveillances are required to be completed each 31 days with a maximum allowable extension not to exceed 25% of the 31 days. Therefore, the surveillance was to be completed by February 22, 1994 or 38.75 days later. <br /><br /> The surveillances were in progress at the time of discovery and were completed on February 23, 1994. <br /><br /> Turkey Point has determined the root cause to be a procedural surveillance scheduling error. <br /><br /> Corrective actions made included the modification of Maintenance procedures to display the required due date for a surveillance and the allowed maximum extension allowed by Technical Specifications. Other procedure changes and administrative aids will be implemented to ensure completion of surveillances within required time frames.<br /><br /> This missed surveillance is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B).
2511994002 | Turkey Point 4 | 03/10/1994 | 04/01/1994 | 9404110261 | <strong>Plant Shutdown Required Due To Reactor Coolant System Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1994, with Unit 4 at 100% rated power, Florida Power and Light Company personnel discovered an indication of boric acid on a flux mapper guide tube. The location of the indication was just above the seal table. At approximately 0600 EST March 10, 1994, an Unusual Event was declared in accordance with EPIP 20101, due to a Technical Specification required shutdown. Required NRC and State notifications were completed. <br /><br /> The small indication found on the guide tube was due to outside diameter chloride induced transgranular stress corrosion cracking. <br /><br /> The affected section of guide tube and associated fitting adapter was removed and a new fitting adapter installed on the newly prepared guide tube end. <br /><br /> The reactor coolant system was pressure tested and Unit 4 was returned to service. <br /><br /> This Technical Specification required nuclear plant shutdown is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A).
2511994003 | Turkey Point 4 | 03/18/1994 | 04/11/1994 | 9404190005 | <strong>Four Analog Rod Position Indicators Greater Than Twelve Steps Deviation From Group Step Counters; Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1994, with Unit 4 at about 88% rated power, Analog Rod Position Indication (ARPI) for first one rod, then three more rods, all in Bank D, indicated more than twelve steps deviation from their associated group step counters. Incore flux maps verified that all Bank D rods were at 190 steps. ARPIs were adjusted to read 190 steps. The rod position indication varies with temperature, and the phenomenon has been known since 1972. The vendor has stated that the variation is inherent to the design of the system, and Technical Specifications allow a one-hour soak time after rod motion, during which most of the apparent misalignments correct themselves. Since there is no Technical Specification action statement for more than one inoperable ARPI in a bank, Unit 4 entered Technical Specification 3.0.3. <br /><br /> A task team investigating an earlier similar event (LER 251-92-001), confirmed the cause, and identified and corrected several contributing conditions. The team was not able to arrive at a cost-effective modification to completely eliminate the problem, but investigation for other contributing conditions continues. <br /><br /> The ARPIs for the four rods were adjusted to read 190 steps, and Technical Specification 3.0.3 was exited.
2511994004 | Turkey Point 4 | 09/23/1994 | 10/21/1994 | 9411010214 | <strong>AUTOMATIC REACTOR TRIP DUE TO LOSS OF POWER TO ROD CONTROL CABINET</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1994, Unit 4 tripped automatically from 100% rated power. Personnel working in the 4C 4160 VAC bus switchgear inadvertently caused a bus lockout, resulting in a loss of the backup power supply to the rod control system. The normal power supply to the 1AC rod control cabinet (already degraded), also failed, and 12 rods dropped. The resultant pressure drop and negative flux difference lowered the OT delta T setpoint below actual delta T, and the reactor tripped on OT delta T. <br /><br /> The C bus lockout was caused by the jarring of a differential relay, due to an interference between a breaker cubicle door and the wall of the switchgear room. The backup power supply failure was due to a faulty regulator transistor. <br /><br /> The reactor trip on OT delta T progressed as expected, and therefore did not impact the health and safety of the public. <br /><br /> The faulty backup power supply was replaced, and 15 similar power supplies were inspected. Maintenance history for the power supplies was reviewed. Replacement power supplies are being evaluated. The interference between the cubicle door and the wall is being removed. The differential relays, as well as others with the potential to cause a spurious bus lockout, are being relocated off the cubicle doors.
2511994005 | Turkey Point 4 | 09/24/1994 | 10/20/1994 | 9411010225 | <strong>Manual Reactor Trip Due To Partial Los Of Rod Position Indicator</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1994, Unit 4 was manually tripped because of the partial loss of rod position indication. Unit 4 was in Mode 3 in the process of a reactor startup with one shutdown bank fully withdrawn and one shutdown bank and all control banks fully inserted. An operator noted that a position indicating light bulb for one rod in the fully inserted shutdown bank was not illuminated. The operator touched the light to check if the light was burned out and noted a flash. After the flash, the indicated position on the analog rod position indicating system for the withdrawn bank dropped to about 60% full scale. After the drop in rod position indication, a manual reactor trip was initiated. All systems responded as expected to the manual reactor trip.
2511994006 | Turkey Point 4 | 11/30/1994 | 12/13/1994 | 9412210168 | <strong>Automatic Reactor Trip Due To Main Generator Ground</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1994, Unit 4 tripped automatically because of the failure of a flexible link connection between the main generator B phase bus and its associated isolated phase bus bar. The flexible link came loose and grounded against the isolated phase bus duct work causing a generator lockout, turbine trip and automatic reactor trip. At the time of the trip Unit 4 was in Mode 1 operating at approximately 100% power. All systems responded as expected to the automatic reactor trip.
2541994001 | Quad Cities 1 | 01/02/1994 | 02/18/1994 | 9403040314 | <strong>Inadvertent Insertion Of Control Rod H-1 From Position 48 to 14 During An Instrument Maintenance Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 01/24/94, Unit-1 was at 97% rated core thermal power. The Instrument Maintenance Department (IMD) was performing a quarterly surveillance when a unit 1/2 scram A channel signal was purposely inserted, and caused rod drift of Control Rod Drive (CRD)(AA) H-1 from position 48 and 14. <br /><br /> The exact cause for the rod drift of CRD H-1 could not be determined. The most probable cause is a combination of the 118 scram pilot solenoid valve (SOL) leaking instrument air, and causing 126 scram inlet valve momentarily lifting off its seat. The Causal Factor of this event was attributed to Plant/System Operation. <br /><br /> Corrective actions included inserting CRD H-1 to position 00, taking Hydraulic Control Unit (HCU) 30-03 out-of-service, rebuilding the HCU scram pilot solenoid valves, and resetting the stem stroke of HCU scram inlet/outlet valves.
2541994002 | Quad Cities 1, Quad Cities 2 | 01/04/1994 | 01/19/1998 | 9801280081 | <strong>"B" Control Room HVAC Inoperable Due to Failure of a Compressor Motor Contactor</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in the RUN mode holding load at 97% of rated core thermal power, and Unit 2 was in the SHUTDOWN mode at 0% power, at 1400 hours on 01/04/94, at which time the "A" Control Room [NA] Heating Ventilation Air Conditioning (HVAC) [VI] was out of service for maintenance, and the "B" Control Room HVAC was operating. At 1400 hours, a burning smell was noticed by Control Room personnel. The electrical breaker for the Refrigeration Condensing Unit (RCU) [RFU] for the "B" HVAC was hot. <br /><br /> The breaker for the RCU was manually opened, making the "B" Control Room HVAC inoperable. The two (2) fuses for the control power for the RCU breaker were found to be blown. <br /><br /> The cause of the event was a coil failure in the contactor which resulted from cumulative cycling of the compressor. The contactor has been replaced. The temperature sensor, which controls compressor operation, will be relocated to reduce compressor cycling. LER254\94\002R1.WPF
2541994003 | Quad Cities 1 | 01/21/1994 | 02/18/1994 | 9403110254 | <strong>Continuous Firewatch Not Established Following Impairment Of A Safe Shutdown Path.</strong><br /><i>Abstract:&nbsp;</i>Unit one was in the RUN mode at approximately 97% of rated core thermal power on 1/21/94. Unit Two was shutdown with the Reactor (Rx) Mode switch in the REFUEL position. The Unit Two Emergency Diesel Generator (EDG) [KL] was Out Of Service (OOS) which placed the Unit in a Limiting Condition for Operation (LCO), requiring hourly compensatory firewatch measures (which were in place). At 1600 on 1/21/94, it was noted that the Unit 112 Rx Recirculation System Motor Generator Set Deluge 'Water Curtain ' system [KP] had also been OOS during the time period (from 1/15/94 to 1/21/94) the EDG was OOS (12/29/94 to 1/21/94). Per QCAP 1500-2, 'Administrative Requirements For Inoperable Safe Shutdown (SSD) Equipment', the simultaneous OOSs of a SSD equipment system and a Fire Protection (FP) system in the same (SSD) path required that a continuous, rather than an hourly firewatch, be established. <br /><br /> The primary Causal Factors for this event were inadequate verbal communications and training which resulted in shift supervision misinterpreting procedural requirements. Contributing causal factors were written communications, and change management. Written communications and training have previously been identified as elements of programmatic problems with the appendix R safe shutdown program. Corrective actions to address these causal factors are planned and in the process of being implemented. <br /><br /> Proper compensatory measures were established. Designated Operations personnel will receive additional training on the Fire Protection Administrative Requirements/SSD procedures in retraining sessions during the first quarter of 1994. \\
2541994004 | Quad Cities 1, Quad Cities 2 | 02/28/1994 | 03/25/1994 | 9404070160 | <strong>Results Of Feedwater Flow Testing Found Flow Indication In The Non-conservative Direction</strong><br /><i>Abstract:&nbsp;</i>In February, 1994, Special Test 1-176, Rev. 1, was performed to determine the difference in actual versus measured Feedwater (FW) flow for both units at Quad Cities Station. The results of the tests indicated that measured FW flow could be non-conservatively low by as much as 1.40% (Unit-1) and 1.70% (Unit 2). The measurement error in FW flow indicates that past operation of the units at full power exceeded the licensed steady state power level of 2511 Megawatts thermal by 1.56% (Unit-1) and 1.78% (Unit-2). <br /><br /> The Causal Factors for this event are attributed to Design Configuration and Analysis, and Equipment Specification, Manufacturer and Construction. <br /><br /> Corrective actions taken prior to Special Test 1-176, Rev. 1, was to limit thermal power of both reactors to 97% of rated thermal power. and the Average Power Range Monitors and Rod Block Monitors setpoints were setdown by 1%. Additional corrective actions are to recalibrate the FW flow instrumentation to calculated flow coefficients, determine if further inspection and testing of the FW nozzles is needed, and to address concerns associated with GE SIL NO. 452, Revision 1. A supplemental report will be submitted to inform the NRC of actions taken to address GE SIL No. 452, Revision 1 concerns.
2541994005 | Quad Cities 1 | 03/14/1994 | 12/20/1994 | 9412290205 | <strong>Valve\Penetration Technical Specification Leakage Limits Exceeded During Local Leak Rate</strong><br /><i>Abstract:&nbsp;</i>At approximately 2330 on March 14, 1994, Quad Cities Unit-1 was shutdown for the cycle 13 refueling and maintenance outage. After Local Leak Rate Testing (LLRT) the 'A' Main Steam Isolation Valves (MSIV), it was determined that the measured leakage rate of 15.8 standard cubic feet per hour (SCFH) in the inboard MSIV AO-1-203-1A exceeded the individual MSIV Technical Specification (3.7.A.2.a.3) leakage limit of 11.5 SCFH. <br /><br /> The outboard MSIV AO-1-203-2A had a measured leakage rate of 0.35 SCFH. <br /><br /> On March 17, 1994, at 0500 hours while performing LLRT on the Unit-1 Feedwater (FW) check valve 1-220-58B, the valve failed with an undetermined leakage. <br /><br /> The unquantified leakage exceeds the 0.6 La (293.75 SCFH) combined leakage limits specified in Technical Specification 3.7.A.2.a.2. <br /><br /> The cause of the excessive leakages have been determined where possible, repairs have been completed and the valves/penetrations have been retested. This report is being submitted to comply with 10CFR50.73(a)(2)(ii)(B).
2541994006 | Quad Cities 1 | 08/08/1994 | 09/06/1994 | 9409190160 | <strong>Uncontrolled Personnel Exposure from A Sr-90 Radioactive Source</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1994 a contract laborer received an estimated radiation dose of 17 to 34 rem Shallow Dose Equivalent (SDE) to the skin from a Sr-90 check source. The source was discovered in the laborer's back pocket during routine exit monitoring through a personnel contamination monitor. The source was determined to be detached from a plexiglass instrument check source in the turbine building. The initial investigation was unable to determine how the source was detached and placed in the pocket of the laborer. An ongoing security investigation is in progress. Causes of this event include personnel error (vandalism), incomplete failure mode analysis concerning the potential for vandalism, and incomplete worker awareness of the hazard. Corrective actions include restricting access to check sources, evaluating the exposure potential of vandalism with other radiological hazards, revising a procedure, and expanding the discussion of radiological hazards in General Employee Training to include potential consequences of vandalism. This event is being reported due to the significant dose to the worker, and the associated potential for exceeding the SDE limit of 10CFR20.1201.
2541994007 | Quad Cities 1 | 04/01/1994 | 05/02/1994 | 9405180053 | <strong>During Maintenance Activities The HPCI Restricting Orifice 1-2301-63B Was Found Clogged By A Foreign Material.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1100 on 03/21/94, Unit-1 was in cycle 13 refueling outage when Mechanical Maintenance Department (MMD) personnel disassembled the High Pressure Coolant Injection system (HPCI) restricting orifice (RO) 1-2301-63B. Upon disassembly, the RO was found clogged approximately 95% closed. <br /><br /> The cause of the clogged RO is unknown. The Causal Factor associated with this event is Maintenance/Testing. <br /><br /> Immediate actions involved disassembly and inspection of steam line drain RO's and steam traps on Unit-2 HPCI and Reactor Core Isolation Cooling systems (RCIC). Unit-1 HPCI and RCIC RO's and steam traps will be inspected during cycle 13 refuel outage. Remaining corrective actions involve review of the practices associated with post maintenance and periodic flushing of the HPCI and RCIC steam line drain piping. and development of RO periodic inspection schedules.
2541994008 | Quad Cities 1 | 08/20/1994 | 09/19/1994 | 9409270190 | <strong>HPCI Flow Oscillation During Operability Run Due To Broken Instrumentation Wire</strong><br /><i>Abstract:&nbsp;</i>At approximately 1200 on 08/20/94, Unit-1 was in the start up mode at approximately 4% power. The Operations Department had satisfactorily completed the uncoupled overspeed test for the High Pressure Coolant Injection (HPCI) Periodic Pump Operability Run (QCOS 2300-1). <br /><br /> During the HPCI low pressure operability run, oscillations in flow and speed were detected in the Control Room (CR) at 1908 hours. The HPCI test was terminated, and trouble shooting activities were started. <br /><br /> At 0538 hours, on 08/21/94, the Unit-1 reactor was manually scrammed by procedure to achieve a shutdown condition required by Technical Specifications. <br /><br /> Trouble shooting activities identified a broken feedback wire on the HPCI flow convertor instrument loop Linear Variable Displacement Transducer (LVDT). Causal Factors attributed for the broken wire are Work Practices, and Maintenance/Testing.<br /><br /> The HPCI front standard instrument wiring, and general material condition, was inspected for Unit-1 and Unit-2 with special attention given to wire crimping integrity. All wires to the effected unit HPCI LVDT had the wire terminal lugs replaced with new parts, and double crimping placed on all of them. The Unit-1 HPCI FIC instrument loop was functionally checked, calibrated, and verified operational.
2541994009 | Quad Cities 1, Quad Cities 2 | 08/23/1994 | 09/15/1994 | 9409230289 | <strong>Failure To Maintain Current Source Inventory</strong><br /><i>Abstract:&nbsp;</i>During a review of the current inventory for sealed sources and records of leak testing on required sealed sources, a deviation from Technical Specification section 3.8/4.8.F was found. <br /><br /> Three Strontium-90 (Sr-90) sources that were to be disposed of as radwaste were removed from the inventory. The sources were stored in a barrel in the Radwaste High Level Bin. At a later date, it was determined that, due to the activity of the sources, they could not be disposed of. These sources were left in storage and never put back on the inventory. One of the sources was removed from storage, leak tested and put back into service, but was not verified to be on the current inventory. When the required six month leak testing was performed, this source was missed because it was not on the inventory. <br /><br /> One Cesium-137 (Cs-137) source missed the required leak testing because it had been inadvertently deleted from the inventory and subsequently missed again due to the units of activity being entered wrong on the inventory. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B).
2541994010 | Quad Cities 1, Quad Cities 2 | 08/08/1994 | 09/21/1994 | 9409290240 | <strong>Control Room Air Conditioning Unavailable Due To Plugged Service Water Strainers</strong><br /><i>Abstract:&nbsp;</i>On 8/08/94 Unit-1 was shutdown and Unit-2 was in Run at 100% power. At 1756 hours when attempting to start the B-train Control Room air conditioning (HVAC) [VI] the compressor [CMP] repeatedly tripped on high pressure. At 1931 hours, Operations declared the B-train of Control Room HVAC inoperable as of 1823 hours. A 4-hour Non-Emergency NRC notification was made in accordance with 10CFR50.72(b)(2)(iii)(D). At 2013, Operations discovered the on-line Service Water strainer [STR] upstream of both the Control Room HVAC compressors was clogged with mud. This problem was not diagnosed earlier as a flow indicator [FI] was providing a false indication of adequate flow. The cause of this event was the failed flow indicator. Corrective actions include repairing the flow indicator and modifying a procedure to ensure Operations utilizes the backup source of cooling water in a timely fashion. <br /><br /> Discussions were held with NRC R III and the due date for this LER was extended to 9/23/94.
2541994011 | Quad Cities 1 | 08/29/1994 | 10/28/1994 | 9411140013 | <strong>During Scram Timing, Control Rod Drive L-11 Failed To Scram Due To Pipe Plug Inserted Into Solenoid Valve Due to Personnel Not Adhering To Procedure</strong><br /><i>Abstract:&nbsp;</i>At 1935 on 08/29/94, Unit-1 was in the run mode when Control Rod Drive (CRD) L-11 failed to scram when given a signal. <br /><br /> The root cause of the event was due to Mechanical Maintenance Department (MMD) personnel not adhering to procedure during maintenance activities on the Hydraulic Control Unit (HCU) scram valves. The MMD personnel performed an informal work practice associated with installing a pipe plug in the HCU Scram Solenoid Pilot Valve exhaust port. <br /><br /> Contributing causes and factors for this event were maintenance procedure deficiencies, a lack of communication between the Work Planners and maintenance personnel, and a lack initial training on HCU scram valve maintenance activities. <br /><br /> Immediate corrective actions included CRD insertion to position 00, and inspections for similar obstructions. <br /><br /> Corrective actions to be completed include HCU maintenance procedure review and enhancement, reevaluation of the HCU Post Maintenance Test/Verification, and reevaluation of the MMD training on HCUs (which will include refresher training). Additional training will be developed for Temporary Alterations specific to MMD applications.
2541994012 | Quad Cities 1 | 10/11/1994 | 11/09/1994 | 9412020203 | <strong>U-1 Drywell High Pressure Switches Found Out Of Tolerance.</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1994, Unit 1 was in the Cold Shutdown mode. The Instrument Maintenance Department (IMD) was performing a quarterly surveillance and identified the setpoints of five out of eight drywell pressure switches [PS] [JE] exceeded the Technical Specification (Tech Spec) limit identified in Tech Spec Table 3.2-2. <br /><br /> The cause of this event is setpoint drift. The root cause of the setpoint drift has not been determined. However, possible causal factors are Plant/System Operation; Equipment Specification, Manufacture and Construction; and Design Configuration and Analysis.<br /><br /> Corrective actions that have been completed include revising the ca libration procedure. Corrective actions to be completed include: changing the setpoints to a more conservative value to provide added margin to the Tech Spec limit: replacement of the switches on Unit 1 prior to startup: increasing the calibration frequency of the Unit 2 switches from quarterly to monthly: and replacement of the Unit 2 switches during the next refuel outage.
2541994013 | Quad Cities 1, Quad Cities 2 | 10/12/1994 | 11/11/1994 | 9411220211 | <strong>Nonconformance with 10 CFR 50 Appendix R Safe Shutdown Analysis separation requirements.</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1994, Quad Cities Station, Units 1 and 2 were shutdown. While evaluating the applicability of an ENS Notification from Cooper Station, ComEd determined that three relays [RLY] which control the HVAC systems [VJ] for all three Emergency Diesel Generators (EDGs) [EK] could be impacted by a fire in a single fire zone. This report is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(ii), 'Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers being seriously degraded, or that resulted in the nuclear power plant being in an unanalyzed condition that significantly compromised plant safety.' Causes for this event are inadequate change management for consideration of system interactions during the Safe Shutdown Analysis and inadequate verification and validation of the Safe Shutdown Analysis. Corrective actions include installation of manual bypass switches, procedure revisions, and a review of the Safe Shutdown Analysis.
2541994014 | Quad Cities 1, Quad Cities 2 | 11/07/1994 | 12/05/1994 | 9412130293 | <strong>Twelve Instrument Maintenance Department Fire Surveillance Exceeded Critical Dates.</strong><br /><i>Abstract:&nbsp;</i>On June 9 and July 20, 1994, with Unit 1 in a Refuel outage and Unit 2 holding approximately 97% power, 12 Instrument Maintenance (IM) Department fire surveillances were deferred until after the refuel outage was completed. On November 7, 1994, with both Units in Cold Shutdown, the 12 surveillances were identified as having gone past their critical dates. <br /><br /> The apparent cause of this event has been attributed to a lack of training in the use of the stations General Surveillance (GSRV) database for the IM Department schedulers. A contributing factor was identified as there were no critical dates specified in the GSRV database for the fire surveillances. <br /><br /> Immediate corrective actions were to declare the affected fire systems inoperable, implement required compensatory measures and perform the past due surveillances on the Essential Fire Protection (EFP) systems. The GSRV database has been changed to include lead dates and critical dates for all IM Department Fire Protection system surveillances residing in the database. Corrective actions to be taken to prevent recurrence are to review the GSRV database for Mechanical Maintenance and Operating Departments' EFP system surveillances and provide training to the IM Department schedulers by the end of December 1994.
2541994015 | Quad Cities 1 | 10/02/1994 | 11/01/1994 | 9411080212 | <strong>Single Loop Operation In An Unanalyzed Condition Due To Management Systems Deficiency</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1994, Quad Cities Unit 1 entered Single Loop Operation (SLO) in order to support planned maintenance on the motor generator set [MG] for the '1A' Reactor Recirculation (RR) [AD] Pump [P]. Following shutdown of the '1A' RR Pump, core flow changes were made with the '1B' RR Pump (active loop) to acquire SLO jet pump baseline data. Upon completion of the data gathering, a final power level of 225 MWe was established (with a core flow of approximately 31% of rated) while work continued on the motor generator set. At 0915 hours, in preparation for restart of the '1A' RR Pump, the Unit 1 NSO identified a temperature difference of greater than 50 degrees F between the RR loops. As required by QCOP 202-2, 'Reactor Recirculation Start-Up', a unit shutdown was performed. Subsequent to shutdown of the unit (October 3, 1994), it was determined that the unit (RR System) had been in an unanalyzed condition. The root cause of this event was determined to be the failure to previously establish, in procedures and operator training, a minimum core flow limit during SLO in order to avoid the potential cooldown of the idle loop. Corrective actions include procedure revisions and training on the minimum core flow limit during SLO.
2541994016 | Quad Cities 1 | 11/16/1994 | 12/21/1994 | 9501060019 | <strong>Failure To Maintain Seismic Category I Qualification Of the EDGCW Pump, EPN 1/2-3903, Due To An Unloaded Piping Hanger</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1994, while troubleshooting for the cause of the alert range vibrations on the Unit 1/2 Emergency Diesel Generator Cooling Water Pump (EDGCWP) [P], several voids were identified under the pump bedplate. On November 16, while repairing the 1/2 EDGCWP bedplate, hanger [H] 1052-M-303 was noted as being unloaded. This hanger is located on the common Emergency Diesel Generator Cooling Water and Residual Heat Removal Service Water System [BI] suction header near the suction piping branch connection for the 1/2 EDGCWP. The function of hanger 1052-M-303 is to support the suction line during operation and during operation with a seismic event. The unloaded hanger could preclude the system from performing its analyzed design function. This report is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(ii)(B). The root cause for this event is unknown. Corrective actions included re-adjustment of the rod hanger, review of the Unit 1 and Unit 2 EDGCWPs, revision of applicable procedures and work instructions.
2541994017 | Quad Cities 1, Quad Cities 2 | 12/05/1994 | 01/04/1995 | 9501120257 | <strong>Banked Position Withdrawal Sequence Rules Violated Since October of 1991 Due To, Training, Procedure And Work Practice Deficiencies In The Nuclear Engineering Group.</strong><br /><i>Abstract:&nbsp;</i>On 12/5/94, the Station Reactor Engineer identified an error in the sequence for control rod movement on Unit 2. It was found that this error had been routinely copied from one sequence to another for both units since 1991.<br /><br /> The causes of this event are, inadequate Nuclear Engineering training, inadequate sequence building procedures and associated poor work practices in the Nuclear Engineering Group. <br /><br /> Immediate corrective actions include retraining, evaluation of the Rod Drop Analysis, review of proposed startup sequences, a review of rod sequence loading into the rod worth minimizer, and review of the Banked Position Withdrawal Sequence (BPWS) software program. <br /><br /> Long term corrective actions include, development of basic expectations for Quad Cities Nuclear Engineer's, review of the Qualified Nuclear Engineer training, review of Nuclear Engineer qualification board questions, sequence building procedures enhancement, and testing of the Sequence Builder software program.
2551994001 | Palisades | 01/21/1994 | 02/18/1994 | 9403080272 | <strong>Failure To Maintain Minimum Pressure In The Control Room With The HVAC System In The Emergency Mode Because The Intake Was Plugged With Ice And Snow</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1994, at 1017 hours, with the plant operating at 100% power, both trains of the control room emergency heating, ventilation, and air conditioning (HVAC) were unable to maintain the required 0.125 inches water gauge (WG) pressure, were declared inoperable and the action statement for Technical Specification 3.0.3 was entered. <br /><br /> This event was caused when the control room emergency HVAC fresh air intake bird screen became plugged with ice and snow. <br /><br /> Corrective action for this event includes modifying a surveillance procedure to record control room pressures from one reading in 10 hours to 10 hourly readings and modifying an alarm response procedure to instruct the operators to inspect the intake for blockage if control room pressure is low.
2551994002 | Palisades | 01/26/1993 | 02/25/1994 | 9403090176 | <strong>Inadvertent Containment Spray Pump (Engineered Safety Feature) Actuation During The Performance Of TS Surveillance Testing Because Of An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1994, at 1825 hours, with the Plant operating at 100% power, technical specification surveillance procedure (TSSP) QO-1, 'Safety Injection System,' was being performed to verify the proper operation of the safety injection actuation system (SIAS) logic. During the performance of one step in the TSSP, the control room operator verifies the white standby lights are illuminated for the containment spray pumps (CSPs) P-54B and P-54C, indicating that the SIAS signal is initiated for these CSPs to start. While performing self-checking to verify that the white light had illuminated, the operator inadvertently depressed the white light/pushbutton resulting in P-54B starting. P-54B was energized for approximately one second; however, since both containment spray control valves (CV-3001 and CV-3002) were closed, no borated water was sprayed in containment. <br /><br /> The cause of this event was an inadequate procedure in that the procedure did not warn the operator that depressing the white standby indicator light/pushbutton will result in a CSP start. <br /><br /> Corrective action for this event includes: modifying TSSP QO-1 to warn the operators that the CSPs will start if the white standby light/pushbutton is depressed when the light is illuminated; examining the P-54B standby light/pushbutton to determine if replacement, adjustment, or repair are appropriate due to its apparent sensitivity; investigating the purpose for the standby start design feature, and; performing operator training on this event.
2551994003 | Palisades | 02/03/1994 | 03/03/1994 | 9403150469 | <strong>Lack Of Environmental Qualification For The Position Switches For The Service Water Inlet And Outlet Valves To The Containment Air Coolers</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1994, at 1615 hours, with the plant operating at 100% power it was discovered that the position switches for the containment air cooler service water inlet and outlet valves were not environmentally qualified for submergence in accordance with the requirements of Regulatory Guide (RG) 1.97. An operability determination was performed that determined the service water inlet and outlet valves would be operable in the event of the failure of the position switches. <br /><br /> The cause of this event was that the master equipment list (MEL) did not alert the MEL user of the existence of qualification restrictions. <br /><br /> Corrective actions for this event include: (1) reviewing the environmental qualification (EQ) equipment files for any other items with restrictive qualification; (2) determining if qualification restrictions are permitted by evaluation to the requirements of 10CFR50.49 and RG 1.97; (3) revising the (MEL) to direct the user to go to the specific equipment file discussion to identify appropriate EQ restrictions; and (4) for this event, evaluating whether the position switches should remain on the MEL or whether an alternate means of informing the operators of the status of service water flow to the containment heat removal system should be provided.
2551994005 | Palisades | 01/25/1994 | 03/14/1994 | 9403210007 | <strong>Lack Of Physical Separation Between The Redundant Channels Of Safety-Related Instrumentation Circuits</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1994, at approximately 1300 hours, with the plant operating at 100% power, it was discovered through a cable tray walkdown that metal cable tray separation barriers were missing from certain vertical cable trays that contain redundant instrumentation channels of reactor protection and engineered safeguards systems. The physical separation of the instrumentation channels is required by IEEE 279, Section 4.6. <br /><br /> Initially, the affected cables were determined to be operable using procedures, engineering judgment, and previous analysis. Further investigation determined that the guidance provided in plant procedures was not applicable to the cable tray conditions described in this event. Therefore, a failure modes and effects analysis (FMEA) will be performed prior to plant heat-up from the current maintenance outage to determine if plant operability is affected by this condition. <br /><br /> The cause for this event was an inadequate field walkdown during original plant construction. <br /><br /> Corrective action for this event includes performing a FMEA to determine systems operability, revising existing plant drawings to show actual field conditions of missing barriers, developing "lessons learned" memorandum to alert plant personnel about missing separation barriers, performing additional inspections to verify that other required cable tray separation barriers have been installed, and installing metal barriers in the currently identified cable trays during the 1996 refueling outage.
2551994006 | Palisades | 02/17/1994 | 03/21/1994 | 9404010017 | <strong>Plant Shutdown In Accordance With Plant Technical Specifications Because Of A Leak On An ASME, Section Xi, Class 2 Safety-Related Check Valve</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1994, at 1538 hours, with the plant operating at 100% power, an accumulation of boric acid on the valve body of check valve CK-ES3166 was confirmed to be caused by a through wall defect. The 24-inch austenitic stainless steel check valve is located between the containment sump and the suction piping for one train of Engineered Safeguards System (ESS) pumps. component in the Section XI program. The valve was declared inoperable. A Plant shutdown was initiated at 1634, February 17, 1994 and the plant was taken to cold shutdown.<br /><br /> Inspection of the comparable check valve in the other ESS train, CK-ES3181, identified indications of a similar nature in the casting of that valve. <br /><br /> The cause of this event was a through wall defect in the body of an ASME, Class 2, check valve, CK-ES3166, due to preferential corrosion at the grain boundaries in a weld repaired region of the valve casting. The code does not allow operation of an ASME Class 2 component with a through wall leak. <br /><br /> Corrective action for this event will be the repair of both check valves, CK-ES3166 and CK-ES3181.
2551994007 | Palisades | 03/08/1994 | 07/25/1994 | 9407280164 | <strong>EDG Fuel Oil Supply Does Not Meet Licensing Basis - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1994 the plant was in cold shutdown. During an evaluation of the emergency diesel generator (EDG) fuel oil supply system it was determined that portions of the emergency diesel generator fuel oil transfer system, including the storage tank, T-10 and associated piping, is not tornado protected. It was also established that this condition did not meet the original General Design Criteria (GDC-2). and associated piping has not been maintained as safety related since plant construction and the diesel fuel oil transfer system is not fully protected from the effects of a design basis seiche as determined in the Systematic Evaluation Program (SEP). <br /><br /> The cause of the event is incomplete design basis information.<br /><br /> Corrective action for this event includes providing interim measurers to ensure a continuous diesel fuel oil supply is available to the EDGs in the event of a design basis event. Additional physical protection and procedures for a transfer of diesel fuel oil to the EDGs will be in place prior to plant startup.
2551994008 | Palisades | 03/29/1994 | 08/29/1994 | 9409130421 | <strong>LACK OF SEPARATION OR ISOLATION BETWEEN 1E AND NON-1E CIRCUITS - SUPPLEMENTAL REPORT</strong><br /><i>Abstract:&nbsp;</i>Between March 29, and May 3 1994, with the plant in cold shutdown, twelve discrepancies were identified where Class 1E and non-Class 1E equipment was not isolated or separated as required by the Palisades FSAR and IEEE 279 - 1971. These discrepancies are reportable as required by 10CFR50.73 (a)(2)(ii)(B) as conditions which were outside the plant's design basis. <br /><br /> Causes for the deviations from separation or isolation criteria include inadequate design reviews and design installation controls utilized at the time of either plant construction or subsequent modifications in the 1980's that added cabling or additional control circuits to the plant. <br /><br /> Eleven of the twelve discrepancies have been corrected. The twelfth will remain in place under an NRC approved deviation until the 1995 refueling outage. Longer term corrective actions include full utilization of the recently enhanced modification review process, providing training to design reviewers regarding specific separation or isolation modification guidelines previously developed, and developing accurate schematics for affected systems. This report addresses all of the plant's discoveries made as a result of a review of isolation and separation issues.
2551994009 | Palisades | 04/07/1994 | 05/09/1994 | 9405160140 | <strong>CONDENSATE STORAGE TANK AND PRIMARY COOLANT SYSTEM MAKEUP TANK COMBINED INVENTORY BELOW TECHNICAL SPECIFICATION LIMITS.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 7, 1994, plant personnel identified that the Technical Specification requirement for maintaining 100,000 gallons of available water in the Condensate Storage Tank (CST) and Primary Coolant System Makeup Tank (PCSMT) for auxiliary feedwater supply might not have been met at all times during past operation. On April 20, 1994, it was confirmed that the requirement had not been met on six occasions in August 1992. To maintain compliance with this requirement, the low level setpoint for the CST has been changed to make the operators aware of the available inventory and Procedures will be revised correspondinely.
2551994010 | Palisades | 03/02/1994 | 05/11/1994 | 9405170146 | <strong>Open Convection Barrier Panels Result In Bioshield Concrete Temperatures In Excess Of Technical Specification Limit.</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1994, with the plant in cold shutdown, it was verified that two of the hinged horizontal panels of insulation comprising the convection barrier around the reactor vessel were not in the closed position. Later, on April 12, 1994, with the plant still in cold shutdown, it was determined that the two open sections of the barrier allowed the concrete bioshield temperature to increase above limits established in the Technical Specifications. Although the Technical Specification design limit for the concrete of 165 degrees F was exceeded, the bioshield was effected only where the reactor vessel insulation was open. Preliminary analysis indicates that the bioshield wall remained operable. The lack of adverse impact to the bioshield was attributed to the local nature of the temperature increase, the shallowness of the through wall gradients, the relatively low magnitude of the applied loads and the distribution of those loads. Both open sections of the barrier were closed on March 13, 1994. The final analysis of the impact of the openings in the convection shield on the bioshield itself will be completed before plant startup from the current maintenance outage.
2551994011 | Palisades | 04/25/1994 | 05/25/1994 | 9405310216 | <strong>Previously Unanalyzed Combination Of Events Indicates Potential For Inability Of A Single Source To Reliably Start Diesel Generators.</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1994, with the plant in cold shutdown, plant personnel discovered that, in certain circumstances, the ability of the plant's Emergency Diesel Generator's (EDGs) to start within the prescribed time frame could be adversely impacted. When loss of a station battery was considered as a single failure mechanism along with a design basis accident and loss of offsite power the result would be a reliance on only one starting circuit for each EDG. That circuit is the 'A' air start circuit for both diesel generators. The starting time for the 'A' air start circuit for EDG 1-2 had previously exceeded the specified starting time. The single failure, a station battery, had not occurred in the past and availability of all starting circuits for both EDGs had not been impacted. However, the effect of the identified condition placed the plant outside its design basis. The slow air start motor and its regulator have been replaced and tested satisfactorily. Procedures used to control testing of both EDGs have been changed to reflect the information obtained as a result of this discovery.
2551994012 | Palisades | 04/27/1994 | 02/19/1996 | 9602270326 | <strong>Thermal Margin Monitor Internal Ground - Reactor Protective System (RPS) Design Basis - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1994, with the plant in cold shutdown, it was determined that an internal ground in the Thermal Margin Monitor (TMM) causes a non-conformance with the Reactor Protective System (RPS) design basis. The TMM is part of the RPS and the RPS is designed to operate as an ungrounded system. The ground path in the TMM was connected to the pressurizer pressure measurement loop, the Nuclear Instrumentation (NI) System and the Primary Coolant System (PCS) temperature inputs. A second ground in the pressurizer pressure loop or in the PCS temperature transmitter loop could adversely affect the RPS accuracy and reliability.<br /><br /> The cause of this event is an internal ground in the TMM design which was not identified at the time of installation and the failure to recognize that this internal ground put the RPS outside of the FSAR design basis in that the RPS is designed to be ungrounded. <br /><br /> Modifications to effectively isolate the internal ground in the TMM from the pressurizer pressure circuitry and PCS temperature circuits were completed prior to plant heat-up.
2551994013 | Palisades | 04/27/1994 | 08/16/1994 | 9408240161 | <strong>Unsupported Reactor Coolant Pump Instrument Tubing Identified As Being Outside The Plant Design Basis Due To The Lack Of Supports</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1994, with the plant in cold shutdown, a 30-foot section of 0.5-inch instrument tubing was found without supports. This tubing connects to the Delta P indicator across the Reactor Coolant Pump (RCP). Instrument tubing is required to be installed per Palisades Specification M-195 (Q). The unsupported section did not meet the stress analysis requirements outlined in the specification and was, therefore, outside the design basis. Once identified, the deficiency was corrected. Additional tubing was physically checked and further problems were found on all four of the plant's RCPs. Each was subsequently repaired or modified to meet specification requirements. The plant will develop a process to integrate all hanger and support programs including inspection and repair processes.
2551994014 | Palisades | 05/30/1994 | 05/31/1994 | 9406090194 | <strong>Potential Sump Blockage From Signs, Adhesive Labels, And Tape</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1994, with the plant in cold shutdown, signs, adhesive labels, and tape which have the potential to block the containment sump were identified. The initial operability evaluation assumed, in a worse case scenario, that if these items became loose they could obstruct the containment sump screens and cause an unacceptable flow blockage for recirculation of the containment sump water. The root causes are a lack of controls on the use of material used to attach signs and labels to walls and equipment in containment, lack of consideration of the impact the loose signs, labels, or other material could have on post accident containment sump water recirculation path and a less than adequate containment cleanliness verification process. An extensive containment cleanliness and re-labeling effort was undertaken. clogging of the containment sump by the remaining identified signs, labels, and tape is unlikely.
2551994015 | Palisades | 06/01/1994 | 06/30/1994 | ML00367330 | <strong>Discovery Of Cable Lacking Qualification In An Environmentally Qualified Application Places Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1994, with the plant in cold shutdown, an examination of an electrical cable revealed it was not environmentally qualified (EQ) for use in an application which required qualified cable. The non-EQ cable provides power to a solenoid valve which, on receipt of a safety injection (SI) signal, deenergizes and vents the control air used to open a pressure control valve. The design and safety function of the pressure control valve, located in the outlet piping to safety injection tank T-82C, is to close on the receipt of the SI signal. Analysis identified that a positive to negative short circuit in the non-qualified cable would cause the solenoid valve to vent and the pressure control valve to fail to its safety position. A fault to ground would not cause the pressure control valve to remain open unless other multiple, simultaneous, and low probability grounds also occurred. In accordance with NRC Generic Letter 91-18 guidance, a Justification for Continued Operation with the cable installed has been completed.
2551994016 | Palisades | 08/24/1994 | 09/23/1994 | 9409300118 | <strong>Inaccurate Analysis Leads To Boric Acid Storage Tank Concentration Below Technical Specification Criteria</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1994 with the plant at 100% power, plant personnel identified a situation where previous concentrated boric acid tank concentrations had been outside of the plant technical specification limits. Since present boric acid tank concentrations were identified as being within the technical specification requirements, no immediate actions were required. Reviews of previous analysis revealed that, because of sample density and temperatures, relying on a volume sample for the concentrated boric acid tank technical specification concentration verification was non-conservative by approximately 10%. Other chemistry analytical procedures were reviewed to determine if they were subject to a similar error due to sample concentration and/or temperature. No other analysis were determined to be affected.
2551994017 | Palisades | 09/02/1994 | 11/22/1994 | 9412020137 | <strong>Licensee Event Report 94-017-01 - Emergency Diesel Generator, EDG 1-1, Degraded Load Carrying Capability - Supplemental Report</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1994, while the plant was operating at 100% power, and during maintenance testing, it was discovered that the Emergency Diesel Generator 1-1 (EDG 1-1) maximum output was below the maximum required design basis load. A misadjusted engine governor output linkage and engine performance degradation limited the EDG 1-1 output. The engine problems were corrected and an electrical load test was completed on September 4, 1994 to verify design basis maximum load carrying capability. A similar load test and minor linkage adjustments were completed for the alternate EDG 1-2 on September 7, 1994. The as-found load carrying capability of the EDG 1-2 was found slightly below the maximum analyzed design basis load.<br /><br /> The causes for this event were inadequate design basis testing, failure to effectively monitor for engine performance degradation, and failure to adequately control modifications made to engine governors in the past.<br /><br /> Corrective actions for this event include periodic peak load testing for EDGs, and enhanced EDG performance monitoring, to include engine governor performance. Also, an engineering evaluation has determined that the safety consequences of the reduced load carrying capability are minor. The engine would have remained running during the peak load period, and the safety functions of the associated electrical loads would have been fulfilled.
2551994018 | Palisades | 10/26/1994 | 11/22/1994 | 9412020150 | <strong>Failure To Properly Implement Technical Specification 4.7.1.C, Emergency Diesel Generators Refueling Outage Inspections</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1994, plant personnel identified a failure to fully implement a Plant Technical Specification requirement. The requirement is to inspect each diesel generator in accordance with procedures prepared in conjunction with the manufacturer's recommendations. In 1982, the manufacturer provided a new version of inspection recommendations created solely for standby engine service. The new recommendations included major engine tear down inspections every 12 years. Plant engineering determined that this frequency was excessive, but this determination was not sufficiently documented. <br /><br /> The cause for this event was a failure to maintain an adequate Technical Specification Basis Document to provide a properly documented and approved exception to published manufacturer's recommendations. <br /><br /> Corrective actions for this event include; completing a formal evaluation of the diesel generator manufacturer's recommended inspections, continuing the present effort of evaluating and optimizing preventive maintenance practices for critical risk significant systems, structures, and components within the scope of the Maintenance Rule, and revising plant administrative procedures to clarify the process for dispositioning manufacturer's recommended inspections.
2551994019 | Palisades | 11/09/1994 | 12/07/1994 | 9412190217 | <strong>Failure To Test Redundant Equipment Per Technical Specification 3.3.2.F Prior To Removal Of Electrical Breakers From Service For Planned Preventive Maintenance</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1994, plant personnel identified a failure to implement a Plant Technical Specification requirement. The requirement states that prior to initiating repairs to certain safety injection system components that all valves and interlocks in the system, that provide the duplicate function, shall be tested to demonstrate operability. Contrary to this requirement, on two separate occasions an electrical supply breaker for a Low Pressure Safety Injection Valve was removed from service for preventive maintenance (PM) without prior testing of the three redundant valves. Subsequent testing of the appropriate redundant valves has determined they had remained operable. <br /><br /> The cause for this event was personnel error during the final processing of a revision to an electrical breaker PM. A data entry error was made in the controlling document and the second level review of the changes was not adequate. The error led to inadequate testing requirements on the associated work order controlling the breaker work. A contributor to the event was the failure by the licensed operators to identify the required testing during approval of the work order, which allowed the work to commence. Corrective actions for this event include; the development of a document to assist operators and planners in the identification of testing requirements for duplicate equipment, and a procedure upgrade to ensure final reviews occur after all changes are made to PM documents.
2551994020 | Palisades | 12/07/1994 | 01/06/1995 | 9501130265 | <strong>Inadvertent Actuation of Auxiliary Feedwater Flow (Engineered Safety Feature) During the Performance of Technical Specifications Surveillance Testing Because of a Failed Electrical Relay</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1994, at 1952 hours, with the plant operating at 100% power, a monthly Technical Specification Surveillance Test was being performed to verify the proper operation of the Auxiliary Feedwater (AFW) Pumps. During the performance of this test for AFW Pump P-8A, the control room operator placed a test switch into a position which blocks the automatic opening of the pump discharge flow control valves upon the pump start. This step allows the pump to be tested on recirculation flow. However, an undetected electrical relay failure had occurred approximately seventeen hours earlier, and had caused the normally closed flow control valves to stroke to the open position. Upon manually starting the pump, the control room operator detected the unexpected flow to the steam generators and the test was stopped. <br /><br /> The causes for this event were an undetected electrical relay failure, and the failure to recognize that the pump discharge flow control valves were full open prior to starting the pump. Corrective actions for this event include procedure enhancements to better define the control room operators shiftly review of component positions, and actions to ensure that fuse holder clips maintain adequate contact with installed fuses.
2591994001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 02/04/1994 | 03/07/1994 | 9403140291 | <strong>An ESF was actuated During an surveillance instruction due to personnel error when a jumper was installed on the wrong relay.</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1994, Emergency Equipment cooling water (EECW) pump A3 inadvertently auto started during the performance of Surveillance Instruction (SI)(0-SI-4.2.B.-67 'Residual Heat Removal Service Water Initiation Logic') after a jumper was placed on the wrong HFA relay. This event is reportable in accordance with 10 CFR 50. 73 (a)(2)(iv) due to an unplanned actuation of an Engineered Safety Feature. <br /><br /> The cause of the EECW pump A3 auto start was personnel error. Electrical Maintenance (EM) personnel did not perform an adequate self-checking verification process during a second party verification when the jumper was initially installed. Contributing factors were the inconsistencies in labeling. <br /><br /> This event will be reviewed with maintenance personnel to heighten their awareness regarding proper verification of jumper installation. TVA will evaluate a potential drawing discrepancy for identified labeling inconsistencies. Labels for the time delay relays will be removed from the front of the panel. Walkdown of 4kV shutdown boards will be performed for labeling inconsistencies. EM procedure will be revised to denote accurate GE mark numbers when a HFA relay is replaced. The EM Manager will further review the incident and decide if any additional actions are required.
2591994002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/28/1994 | 09/20/1994 | 9409290268 | <strong>Circuit Breakers Failed Trip Time Tests Because of Different Testing Equipment Used to Perform the Tests</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1994, TVA conducted an acceptance test for General Electric (GE) 250 VDC, 1600 Amp, AKR circuit breakers equipped with EC1 trip devices. Using the TVA test set, the breakers tripped at time intervals in excess of GE's published tripping times (or curves) at low-level current settings [i.e., 1.5X rated current (2400 Amp) and 2X rated current (3200 Amp)]. The breakers had been factory tested and passed the tests at GE with a much shorter trip time using the GE test set. TVA cannot make a conclusive determination as to why the curves and the breaker settings differ. However, TVA believes that the differences in breaker tripping time could be due to the different test equipment used by TVA and GE for their breaker testing. Specifically, GE's test equipment may have contained sufficient harmonic distortions to cause the breakers to trip faster at low-level settings and that these distortions could lead to the breakers actual operating characteristic being different from the curves published by GE. The above condition is not reportable per 10 CFR 50.73; however, TVA is reporting it voluntarily since this may be a potential safety concern at other nuclear plants in the industry. At TVA's request, GE lowered EC1 device oil viscosity so that the breakers will pass TVA test criteria.
2591994003 | Browns Ferry 1, Browns Ferry 3 | 07/13/1994 | 09/20/1994 | 9409290286 | <strong>A Defect was discovered in the pressure rating for the BFN Unit 1 and 3 Air Conditioning Units supplied by Ellis and Watts</strong><br /><i>Abstract:&nbsp;</i>This event concerns a defect involving four (4) 25-ton safety-related, water cooled Air Conditioning Units (ACUs) manufactured by Ellis and Watts. The ACUs are only installed in BFN Units 1 and 3 (two in each unit), but the ACUs have not yet been operated. on July 13, 1994, TVA discovered that the ACU condensers were designed to a lower pressure than their operating pressure. The condensers were designed and American Society of Mechanical Engineers Section (ASME) VIII stamped for a pressure of 150 psig. However, under post-accident conditions, the condensers could experience an operating pressure of 300 psig. The ACUs provide cooling to the Unit 1 and Unit 3 electrical board rooms. The design error in the condensers applies to all four ACUs (common mode failure) and could cause their failure when operated. However, no current safety hazard exists since BFN Units 1 and 3 are defueled and the ACUs are not required to be operational. This event does not affect the operating unit (i.e., unit 2). TVA performed a substantial safety hazard determination and, on August 23, 1994, determined that this event was reportable per 10 CFR Part 21.
2601994001 | Browns Ferry 2 | 02/14/1994 | 03/14/1994 | 9403210161 | <strong>Entry into Technical Specification 1.C.1 due to a loss of Emergency Core Cooling Systems (ECCS) Division II instrumentation resulting from a blown fuse.</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1994, at 0929 hours CST, with Unit 2 at approximately 100 percent power, control Room operators received alarms that indicated a lose of Unit 2, Division II Emergency Core Cooling Systems (ECCS) instrumentation. ECCS provides adequate cooling to the reactor core under abnormal and accident conditions utilizing various diverse and redundant cooling systems. The operators declared Division II of ECCS instrumentation inoperable, resulting in all ECCS being declared inoperable, and entered Technical Specification (TS) 1.C.1 (i.e., Standard TS 3.0.3) which requires that the unit be placed in Hot Standby within six hours and Cold Shutdown within 30 hours. <br /><br /> Operators initiated troubleshooting which found that a fuse had blown on the ECCS Division II Analog Trip Unit (ATU) Inverter. Further investigation identified the root cause of the event to be a failed ATU Inverter control card. The fuse and control card were replaced. The affected systems were returned to service. Operators exited TS 1.C.1 at 1226 hours CST before having to initiate actions to achieve Hot Standby. TVA sent the removed ATU Inverter control card to the manufacturer for further analysis. <br /><br /> This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant's TS due to the entry into TS 1.C.1. Additionally, this event is reportable in accordance with 10 CFR 50.73(a)(2)(v) and 10 CFR 50.73(a)(2)(vii).
2601994002 | Browns Ferry 2 | 04/12/1994 | 05/06/1994 | 9405180008 | <strong>Noncompliance with 10 CFR 50 Appendix R Results in Plant Being Outside Its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1994, Browns Ferry Unit 2 was operating at approximately 100% power when TVA concluded that two errors in the Unit 2 Appendix R Program involving noncompliance with 10 CFR Part 50 Appendix R requirements were reportable as conditions outside the design basis of the plant. The errors were identified by TVA on October 28, 1993, and December 29, 1993, and initially determined to be not reportable. The first error involves power supply cables to redundant reactor water cleanup system valves being located in the same fire zones. The second error involves an associated circuit concern wherein the power supply cable to a spare Unit 1 raw cooling water pump was not adequately separated electrically from a Unit 2 4160-volt shutdown board needed for safe shutdown. Both errors were identified during the development of the Unit 3 Appendix R Program. <br /><br /> The errors resulted from individual failures to correctly interpret/implement the applicable requirements of the calculations and/or design criteria used during the original development of the Unit 2 Appendix R Program. The program was developed from 1985 through Unit 2 restart in May 1991.<br /><br /> Upon discovery of these events, the appropriate fire watches were posted. Modifications have been or will be implemented to correct these deficiencies. To address the root cause, the affected engineering department personnel will review the circumstances that led to these events. <br /><br /> A previous event concerning noncompliance with Appendix R was reported in LER 259/91-008.
2601994003 | Browns Ferry 2 | 01/04/1994 | 05/10/1994 | 9405180057 | <strong>Standby Gas Treatment Trains Declared Inoperable as a Result of Inoperable Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1994, at 063 hours Central Standard Time (CST), TVA declared the Unit 1/2 'A' Emergency Diesel Generator (EDG) inoperable as a result of a fuel oil leak. At 1940 hours CST, the Unit 3 'D' EDG was declared inoperable due to a failed timing relay. With these two EDGs being simultaneously inoperable, TVA also declared the 'A, and 'C' Standby Gas Treatment (SBGT) trains inoperable per the plant's Technical Specifications (TS). The Limiting Condition for operation (LCO) of the TS required the Unit to restore one of the SBGT trains to operable status or be in hot standby within six hours. At 2025 hours, TVA restored the 3 'D' EDG and the 'A' and 'C' SBGT trains to operable status, and the six- hour LCO action was exited. Following appropriate corrective maintenance, the 1/2 'A' EDG was restored to operable status on January 6, 1994. <br /><br /> The fuel oil leak on the 1/2 'A' EDG resulted from a cracked brass nipple in the diesel engine driven fuel pump piping. The failure of the timing relay on the 3 'D' EDG was due to a bent lead on its integrated circuit chip. <br /><br /> TVA performs a monthly operability test on each EDG, which checks for any leakages and damages. No similar oil leaks were observed on the other EDGS, and no similar nipple failures have been found from maintenance history search; therefore, no further action is necessary to prevent recurrence of the problem associated with the 1/2 'A' EDG. Concerning the problem associated with the 3 'D' EDG, TVA will inspect other similar type timing relays. This event is similar in nature to LERs 259/86026 and 259/86036. on April 12, 1994, TVA concluded that this event was reportable per 10 CFR 50.73 (a)(2)(V)(D).
2601994004 | Browns Ferry 2 | 04/15/1994 | 05/13/1994 | 9405240094 | <strong>Unit 2 Scram From Full Power During Planned Maintenance Activity Due to Inappropriate Personnel Action</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1994, at 0219 hours , Unit 2 received a full scram from full power due to a RPS trip signal generated by a low Scram Pilot Air Header pressure signal. This resulted in a low reactor water level which caused isolation of various ESF and RPS system actuation. exception that high temperature alarms were received for the High Pressure Coolant Injection (HPCI) system. Affected ESF and RPS systems were returned to operable status by 0300 hours on April 15, 1994. Operators returned HPCI to service at 0535 hours after no abnormal conditions could be found. <br /><br /> The root cause of this event was inappropriate personnel action during maintenance activity on the Scram Pilot Air Header. The personnel involved deviated from the work order, but did not take the proper actions to ensure that their actions would not adversely affect plant operation. If the work order had been performed as written the scram would not have occurred. <br /><br /> During the unit scram a false high temperature alarm in the HPCI led to isolation of HPCI. This was attributed to a failed module in the temperature detection loop. <br /><br /> This event is reportable per 10 CFR 50.73(a)(2)(iv) due to the ESF and RPS actuation, and 50.73(a)(2)(v) due to the isolation of the HPCI system, which is a single train system. Corrective actions to prevent recurrence include a review of this event by appropriate personnel and tighter controls for those activities which have the potential for ESF actuation.
2601994005 | Browns Ferry 2 | 04/18/1994 | 05/16/1994 | 9405230305 | <strong>Unit 2 Reactor Automatically Scrammed When Main Steamline Isolation Valves Unexpectedly Closed</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1994, at approximately 0355 hours CDST, the Unit 2 reactor automatically scrammed from 15 percent power when the Main Steamline Isolation Valves (MSIVs) unexpectedly closed. MSIV closure was caused by low main steam pressure when six main turbine Bypass Valves (BPVs) spuriously opened to their full open position. Engineered Safety Feature (ESF) systems responded as designed. These systems included the automatic isolation or actuation of primary containment isolation system groups 2, 3, 6, and 8. This event is reported in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in the automatic actuation of any ESF, including the reactor protection system. <br /><br /> TVA determined that the most likely cause of the BPVs opening was an Electro-Hydraulic Control (EHC) system malfunction. A defective pressure regulator potentiometer was found in the EHC circuitry. <br /><br /> The defective potentiometer was replaced and satisfactorily tested before the restart of Unit 2. TVA will perform a failure investigation of the defective potentiometer and reevaluate preventive maintenance actions for other sensitive system potientiometers. While there have been a number of previous reactor trips due to EHC/turbine control problems, there were no previous similar reactor scrams caused by multiple BPVs opening unexpectedly.
2601994006 | Browns Ferry 2 | 08/31/1994 | 09/29/1994 | 9410050054 | <strong>Entry into Technical Specification 1.C.1 due to a loss of Emergency Core Cooling System Division I instrumentation from a short in the Analog Trip Unit Inverter</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1994, at 1248 hours CDT, at approximately 93 percent power, control room operators received alarms that indicated a loss of Unit 2, Division I Emergency Core Cooling Systems (ECCS) instrumentation. The operators declared Division I of ECCS instrumentation inoperable and entered Technical Specification (TS) 1.C.1 (i.e., Standard TS 3.0.3) which requires that the Unit be placed in Hot Standby within six hours and Cold Shutdown within 30 hours. Troubleshooting determined that the event was initiated from a shorted Silicon Controlled Rectifier (SCR) in the ECCS Division I, Analog Trip Unit (ATU) inverter. The short caused the inverter supply breaker to trip, which resulted in a loss of power to the inverter and loss of input logic signals from the affected systems to the control room instrumentation. TVA determined the root cause to be a random failure of the inverter. Contributing to the event is the ECCS ATU design which lends itself to the loss of an entire ECCS division from a single component failure. The ATU inverter was repaired by replacing the shorted SCR, and a search of previous similar events has not found any other incidents with the same root cause. TVA will evaluate the present design on the ECCS ATU power distribution to determine if design enhancements can be made.
2601994007 | Browns Ferry 2 | 09/29/1994 | 10/31/1994 | 9411090409 | <strong>Noncompliance With 10 CFR 50 Appendix R Results in Unit 2 being Outside Its Design Basis And In a condition Not Covered By The Plants Operating Instructions</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1994, at approximately 1300 hours TVA discovered that a condition involving noncompliance with 10 CFR Part 50 Appendix R, Criterion III.L.2.d. existed. Specifically, TVA discovered that the Unit 2 suppression pool level indication was not available due to a loss of the supporting power supply, which is fed from 480V Shutdown Board 2B. Additionally, the Appendix R Safe Shutdown Program did not require compensatory measures for Fire Area 18. This event is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the design basis of the plant, and 10 CFR 50.73(a)(2)(ii)(C) as a condition not covered by the plant's operating and emergency instructions. This event resulted from failures to correctly interpret/implement the applicable requirements of the calculations and/or design criteria used during the initial development of the Unit 2 Appendix R program. <br /><br /> TVA will revise the Safe Shutdown Program along with appropriate procedures and calculations. Finally, TVA will perform a comparative review of the Required Equipment Calculation against the Browns Ferry Unit 2 Safe Shutdown Program.
2601994008 | Browns Ferry 2 | 10/02/1994 | 02/27/1995 | 9503060060 | <strong>Containment penetration and main steam isolation valve leak rates exceeded Technical Specification limits.</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1994, local leak rate testing was being performed during the BFN Unit refueling outage. At 1240 hours, primary containment ventilation penetrations X-25 and 205 (2809.2329 SCFH) exceeded the Technical Specification (TS) limit of 655.9 SCFH. Subsequently, at 2000 hours, the outboard 'D' main steam isolation valve (MSIV) had leakage (60.5745 SCFH) which exceeded the TS limit of 11.5 SCFH. Therefore, these events are reportable in accordance with 10 CFR 50.73 (a)(2)(ii). The cause of X-25 and 205 penetration leakages resulted from a lack of adequate procedural guidance as to the proper shimming of seismic mounting brackets. The cause of the outboard 'D' MSIV leakage was abnormal rib guide wear. Corrective actions taken for the X-25 and 205 penetration leakages were to properly shim seismic mounting brackets and to successfully retest the penetrations. A maintenance instruction will be written for these and similar type of valves to address the proper shimming requirements. Corrective actions taken to address the excessive leakage for outboard 'D' MSIV were to repair and successfully retest the MSIV.
2601994009 | Browns Ferry 2 | 04/20/1994 | 11/04/1994 | 9411170027 | <strong>Missed Technical Specification (TS) Surveillance before Reactor Startup as a Result of a Misunderstanding of TS</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1994, during a review of the plant's Technical Specification (TS) surveillances, TVA determined that the Intermediate Range Monitor (IRM) instrumentation functional test was not performed before the Unit 2 startup on April 20, 1994. Further review also determined that a similar test for the Average Power Range Monitors (APRMs) was not performed. This is a condition prohibited by the plant's TS requirements and is reportable per 10 CFR 50.73(a)(2)(i)(B). BFN TS requires that they be tested before each startup and once a week for IRMs during refueling and weekly for APRMs when required to be operable. The root cause of this event was a misunderstanding of TS resulting in inadequate procedures. The General Operating Instructions (GOIs) for Unit Startup did not require the IRMs and the APRMs to be functionally tested before each startup. Additionally, the IRM functional test surveillance did not specify the correct frequency. To prevent recurrence, the GOIs have been revised to require IRM and APRM tests be performed before each startup. The surveillance for the IRMs was also revised to require IRM testing before each startup. TVA will train licensed operators on this event. As an enhancement, TVA will submit a TS change to clarify the frequency for the IRM and APRM instrumentation functional tests.
2601994010 | Browns Ferry 2 | 10/05/1994 | 09/30/1996 | 9610090110 | <strong>Loss of the Emergency Core Cooling Systems (ECCS) Division II instrumentation resulting from a blown fuse in the Analog Trip Unit (ATU) Inverter caused by a failed capacitor.</strong><br /><i>Abstract:&nbsp;</i>On October 5, 1994 at 2220 hours CDT, with Unit 2 in a refueling outage, Control Room operators received alarms that indicated a loss of Unit 2, Division II, Emergency Core Cooling Systems (ECCS) instrumentation. Operators declared Division II of ECCS instrumentation inoperable, in accordance with TS 3.2.B. However, ECCS Division I instrumentation remained operable during this event. Since the unit was already shutdown, no further operator action was required. Operators initiated troubleshooting that found a fuse had cleared on the ECCS Division II Analog Trip Unit (ATU) Inverter. The fuse cleared during a transfer of the 2A 250 Volt DC Reactor Motor Operated Valve board to its normal power source following a battery discharge test. The fuse was replaced at 0110 hours on October 6, 1994 and the Division II ECCS was declared operable. Further investigation identified the root cause of the event to be a failed capacitor in the ATU inverter capacitor bank. This event is reportable pursuant to 10 CFR 50.73(a)(2).(i)(B) as any operation or condition prohibited by the plant's TS. Additionally, this event is reportable in accordance with 10 CFR 50.73 (a) (2) (vii).
2601994011 | Browns Ferry 2 | 10/01/1994 | 03/09/1995 | 9503140140 | <strong>Failure Of a Motor With a Magnesium Alloy Rotor on a Reactor Water Recirculation System Pump Discharge Isolation Valve Placed Unit 2 In a Limiting Condition for Operation</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1994, Unit 2 commenced shutdown for the Cycle 7 refueling outage. Preparations were under way to align the Residual Heat Removal (RHR) system to the shutdown cooling mode. At approximately 1245 hours, a control room operator attempted to close Reactor Water Recirculation System pump B discharge isolation valve. However, the valve failed to close. Subsequently, TVA declared Loop I of the RHR system inoperable, and entered the appropriate Limiting Condition for Operation (LCO). At 1423 hours, the LCO was exited when the valve was manually closed. The motor was replaced prior to Unit 2 Cycle 8 operation. TVA's analysis found that upon energizing, the motor rotor partially disintegrated, particularly along the joint between the rotor bars and the end ring. This condition is not reportable per 10 CFR 50.73. However, the circumstances surrounding this event are similar to those described by IE Information Notice 86-02. Accordingly, due to the generic safety significance of this event, TVA is providing this voluntary report.
2601994012 | Browns Ferry 2 | 11/13/1994 | 12/12/1994 | 9412220129 | <strong>A Residual Heat Removal Shutdown Cooling Valve was Inadvertently closed as a Result of Personnel Failure to Follow Procedure During Performance of a Surveillance Instruction</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1994, at 1546 hours Central Standard Time (CST), the Residual Heat Removal (RHR) outboard shutdown cooling isolation valve (2-FCV-74-47) was inadvertently closed during the performance of Surveillance Instruction (SI) 0-SI-4.9.A.1.b-4, 'Diesel Generator D Emergency Load Acceptance Test.' The closed valve caused a loss of shutdown cooling and resulted in the 2A RHR pump to trip. The shutdown cooling was restored approximately one minute later when operators reopened the closed valve and restarted the 2A RHR pump. This event is reportable in accordance with 50.73(a)(2)(v)(B). The root cause of this event was failure to follow procedure. Both the operator and electrician performing the load acceptance test SI fail to carefully read the procedure. Corrective actions to prevent recurrence included the following: counselling the personnel involved in the event, incorporating the event in the incident investigation of recent operational errors, and revising the regulatory reporting requirement site standard practice to include this as example of events to be reported.
2601994013 | Browns Ferry 2 | 12/02/1994 | 01/19/1995 | 9502010030 | <strong>Unit 2 Scram From 54 Percent Power Caused By Balance Of Plant Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1994 at 0717 hours, Unit 2 received a full automatic scram from 54 percent reactor power. The scram was generated by a main generator turbine trip with the first stage turbine pressure greater than 154 psig. The turbine trip was caused by an invalid loss of main generator stator cooling water signal. The scram resulted in a low reactor water level which caused the isolation/actuation engineered safeguards (ESF) and reactor protection (RPS) systems. The affected ESF and RPS systems were returned to standby readiness by 0729 hours. The root cause of the event was mechanical degradation of the Main Generator Stator Cooling Water system temperature switch. The switch experienced setpoint drift which caused it to prematurely actuate. TVA will issue a procedure for calibration of the stator cooling water temperature switch. Additionally, TVA will evaluate balance of plant devices capable of causing turbine generator trips and ensure that the procedural guidance for calibration is adequate. Finally, TVA will evaluate other balance of plant devices to Bee if due to its age, replacement is required. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv), as any event or condition that resulted in manual or automatic actuation of any ESF including the reactor protection system.
2611994001 | Robinson 2 | 02/04/1994 | 04/15/1994 | 9404280115 | <strong>Failure To Test Instrumentation Channels Per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit 2 was in the cold shutdown condition. A 1992 internal assessment questioned the previously accepted interpretation of testing methodology for Technical Specifications (TS) Table 4.1-1, Items 8 and 31, required surveillance test. These interpretations have been effective since the issuance of the plant's full power license. Therefore, the associated tests had not been adequately implemented to address all of the pertinent features of the equipment being tested. This event had no actual,impacts on plant safety. The tests for the applicable TS Surveillance Requirement ( SRs) were revised to include the untested portion of the equipment in question and were performed with satisfactory results. Therefore, there is reasonable assurance that the equipment has always been capable of performing its intended safety function. <br /><br /> The failure to promptly disposition the findings from the 1992 internal assessment and to correctly apply NRC reporting criteria are the result of: 1) an overall focus on completing the assessment without proper plans for addressing the findings, 2) failure to adhere to the formalized corrective action process, and 3) differing and evolving conclusions regarding the technical adequacy and correctness of the internal assessment findings. <br /><br /> This condition was determined to be reportable on February 4, 1994. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS, since the SRs were not fully complied with and the associated TS actions were not taken within the allowed time interval.
2611994002 | Robinson 2 | 04/25/1994 | 03/15/1995 | 9503210201 | <strong>Plant Condition Outside Design Basis Due To MSIV Inoperability</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was in hot shutdown conditions. During Main Steam Isolation Valve (MSIV) operability testing, all three MSIVs were declared inoperable when they failed to meet the Technical Specification (TS) required closure time. Each valve was secured in its TS required closed position; however, the 'B' MSIV drifted partially open, placing the plant outside of the TS containment integrity requirements. <br /><br /> Plant staff subsequently determined that the original MSIV actuator design incorporated minimum design margin. A complicating factor was that a design enhancement related to inadequate MSIV air accumulator volume was not pursued following its initial identification. A modification was implemented on February 7, 1994, to enhance the design margin, and all three valves were subsequently declared operable. <br /><br /> This condition had minimal impact on actual plant safety. During the time that this condition was discovered, conditions did not exist that would have caused radiological release limits to be exceeded. Based on the possibility that the MSIVs may have been inoperable in the past, and the associated TS action was not taken, we concluded that this condition was reportable on April 25, 1994, pursuant to 10 CFR 50.73(a)(2)(i)(B).
2611994003 | Robinson 2 | 02/18/1994 | 11/30/1994 | 9412050246 | <strong>TS Required Shutdown Due To Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at twenty-nine percent power. During operability testing for the 'B' Emergency Diesel Generator (EDG), a locking pin for the modulating air damper in the EDG intake air system came out and was propelled through the engine's air system, inflicting damage to the scavenging air blower and turbochargers. Because repairs could not be completed within the Technical Specification (TS) Allowed Outage Time (AOT), the plant was placed in shutdown conditions. Corrective actions taken in response to an EDG air intake system malfunction on February 12, 1994, did not preclude occurrence of the February 18, 1994, damper pin failure. The air intake system was subsequently disassembled and inspected; the damaged components were replaced. Upon restoration of the EDG-B to service, operators then removed EDG-A from service for inspection of the air inlet modulating air damper. The damper pins were found to be acceptable with no discrepancies noted. This event had minimal effect on plant safety. During the time the EDG-B was inoperable, EDG-A was operable, and off-site power was available to provide sufficient power to run normal operating and required emergency core cooling equipment. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(A) as the completion of a shutdown required by TS.
2611994004 | Robinson 2 | 03/12/1994 | 04/13/1994 | 9404180025 | <strong>Auxiliary Building Outside Design Basis Due To Positive Pressure Condition</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was in cold shutdown for a forced outage. A scheduled Containment purge was in progress, and the Reactor Auxiliary Building (RAB) supply and exhaust fans were operating. Emergency Diesel Generator (EDG) testing was in progress which required the EDG Room supply and exhaust ventilation fans to be operating. This configuration created a positive pressure condition in the RAB, which is contrary to the design basis of the building. Subsequent system realignment re-established a negative pressure condition. <br /><br /> This event was caused by the ventilation system configuration during EDG testing. When the EDG room ventilation supply and exhaust fans are operated with a Containment purge in progress, the RAB exhaust flow will decrease due to back pressure in the plant stack, thereby creating a positive pressure condition. <br /><br /> This event had no actual effect on plant safety. During the time period that a positive pressure condition existed, the plant was in cold shutdown condition, and contaminated material was not released to the environment that exceeded 10 CFR 20 limits. This event is reported pursuant to 10 CFR 50.73(a)(2)(ii) as a condition outside the design basis of the plant.
2611994006 | Robinson 2 | 04/03/1994 | 05/03/1994 | 9405090073 | <strong>Manual Reactor Trip Due To Electro - Hydraulic System Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit 2 was operating at 100% power. At 2214 hours, the reactor was manually tripped during a load reduction that had been initiated at 2211 hours due to an electro-hydraulic (E-H) oil leak. The leakage, which originated from the #1 turbine governor valve (GV-1), resulted in automatic trips of the B-H oil pumps due to the low oil level in the oil reservoir. Prior to the trips of the E-H oil pumps, a manual load reduction had been initiated due to the leak. Once the pumps tripped, the governor valves started closing, which resulted in a rapid unanticipated load reduction. A manual reactor trip was initiated when the operators determined that an automatic reactor trip was imminent. The Unit was subsequently stabilized at hot shutdown. The leak was caused by a failed O-ring in the blank flange of GV-1 which had been installed during refueling outage 15 (RFO #15). An event evaluation determined the primary root cause of the O-ring failure to be incorrect installation of its associated blank flange. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(iv) as a condition that required a manual reactor trip.
2611994008 | Robinson 2 | 05/07/1994 | 11/30/1994 | 9412230215 | <strong>Condition Outside Design Basis Due To Control Room HVAC Inoperability</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100 percent power. Reactor Auxiliary Building (RAB) ventilation system flow balancing was in progress and, with the building supply fan operating, the exhaust fan was secured to support the flow balancing activities. The air pressure in the RAB subsequently increased. Following review of flow measurement data, the plant staff determined that pressure in a room adjacent to the Control Room had exceeded the Control Room pressure that would exist during the emergency pressurization mode of operation. This condition is considered outside the design basis of the plant. The building supply and exhaust fans were immediately secured, resulting in a pressure reduction in the affected areas. Plant procedures were subsequently revised to place operating restrictions on the building supply fan.<br /><br /> This event was caused by an inadequate system design and testing program. Specifically, the design and testing program did not consider all modes of system lineups and the effect of these lineups on Control Room habitability during the Emergency Pressurization mode of operation. Plant procedures have been revised to ensure the most conservative mode of plant ventilation system operation is appropriately considered during testing.
2611994009 | Robinson 2 | 05/26/1994 | 06/27/1994 | 9407060052 | <strong>Spent Fuel Cask Crane Storage Results In Condition Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100 percent power. A routine inspection identified that, contrary to the commitments stated in the Updated Final Safety Analysis Report, the spent fuel cask handling crane was stored in a position over the Spent Fuel Pit (SFP), which constituted a condition outside the design basis of the plant. This event was caused by failure of the System Engineer to adequately assess if this configuration was bounded by the plant licensing basis commitments prior to authorizing it to be moved to that location. Upon discovery of this condition, the crane was returned to its normal storage location. this condition was performed, and no condition adverse to safety of the plant or the public existed while the crane was parked over the SFP. Appropriate corrective actions were taken with regard to the human performance aspects of the event, and administrative controls were initiated to preclude recurrence. This report is submitted pursuant to 10 CFR 50.73(a)(2)(ii) as an operation in a condition outside the design basis of the plant.
2611994010 | Robinson 2 | 05/27/1994 | 06/27/1994 | 9407060074 | <strong>Missed Surveillance Test Results In Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100 percent power. A routine inspection identified that all of the spent fuel cask handling crane limit switches had not previously been adequately inspected in accordance with Technical Specifications (TS). This event was due to personnel error. During the procedure revision process, the TS required tests were inadvertently deleted. A contributing factor to this condition is that the TS requirement is ambiguous with respect to the specific limit switches that are affected, and the applicable operational mode for testing. Failure to conduct the testing within the specified interval did not result in any condition adverse to safety. Administrative controls have been placed on the crane which prohibits its use without management approval. The individuals responsible for the procedure revision and review are no longer employed by CP&L, and the procedures that they were responsible for are under review to ensure that the ability to meet the applicable TS requirement has not been jeopardized. The TS and its bases will be evaluated and the appropriate changes will be submitted to clarify the applicability of this TS surveillance requirement. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as operation in a condition prohibited by TS.
2611994011 | Robinson 2 | 05/16/1994 | 06/15/1994 | 9407070002 | <strong>Technical Specifications 3.0: Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On May 16, 17, 18, 19, and 25, 1994, and on June 7, 1994 and June 8, 1994, with the H. B. Robinson Steam Electric Plant (HBRSEP) Unit 2, operating at 100% power, the 'A' Emergency Diesel Generator (EDG) was out of service for maintenance. In accordance with Technical Specification (TS) Action 3.7.2(d), the 'B' EDG was tested daily during these periods to ensure operability. Performance of the Operations Surveillance Test (OST) results in an EDG being inoperable during portions of the testing. As a result, both EDGs were inoperable for approximately two and one half hours on each day that the test was performed, placing the plant in a condition outside of TS Limiting Condition for Operation 3.7. Therefore, TS Section 3.0 was entered for the duration of each test period. <br /><br /> The basis of this situation is that since the action required by TS 3.7.2(d) cannot be met without placing the plant into a condition for which there is not an action statement, a condition prohibited by TS results. This situation had minimal effect on plant safety. During each time that the 'B' EDG was inoperable, off-site power was available and operators were located at the EDG with the ability to manually place the 'B' EDG in service should off-site power have been lost. <br /><br /> This report is submitted pursuant to 10 CFR 50.73 (a)(2)(i)(B) as operation in condition prohibited by TS.
2611994012 | Robinson 2 | 05/23/1994 | 06/22/1994 | 9406280096 | <strong>CVCS Heat Trace Channel Inoperability Requires TS 3.0 Entry</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100 percent power. With the 'A' Emergency Diesel Generator (EDG) removed for service to perform scheduled surveillance testing, Maintenance personnel notified Control Room operators that heat trace primary circuit 25P was inoperable. Because the remaining operable channel of heat tracing was powered from the inoperable 'A' EDG, both channels of heat tracing were declared inoperable, and the action statement of TS 3.0 was entered. Repairs were expedited, and heat trace circuit 25P was declared operable at 1530 hours on May 23, 1994. The 'A' EDG was tested satisfactorily and declared operable on May 24, 1994 at 0010 hours. <br /><br /> Heat tracing Circuit 25P failed due to breakdown of its cable insulation. Because the specific piping configuration does not allow installation under optimum conditions, sufficient heat transfer from the cable to the piping did not occur, resulting in insulation degradation and subsequent cable failure.<br /><br /> The actual ability to provide negative reactivity insertion by boric acid addition was not affected. safety. This event is reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2611994014 | Robinson 2 | 06/14/1994 | 08/29/1994 | 9409090228 | <strong>Technical Specification Violation Due To Improper High Steam Flow Setpoint</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. was operating at 100 percent power. An engineering review discovered that an incorrect assumption in a 1988 calculation had been used to establish Engineered Safety Feature (ESF) high steam flow setpoints. As a result of this error, Main Steam pressure instrumentation setpoints were rescaled in 1988 to a value that did not meet the values required by Technical Specifications (TS) for high steam flow. <br /><br /> This event was caused by personnel error. The engineering evaluation that justified the setpoint was inadequate in that it did not provide a thorough design basis analysis of the high steam flow setpoint. The consequences of this condition did not have an adverse impact on plant safety. The high steam flow trip setpoint did not result in an unanalyzed condition during the time that the setpoint was in effect. <br /><br /> The setpoints were rescaled to their correct value and associated instrumentation was recalibrated on June 15, 1994. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation in a condition prohibited by TS.
2611994015 | Robinson 2 | 06/21/1994 | 10/27/1994 | 9411030185 | <strong>Technical Specification 3.0: Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>This supplement provides a compilation of information concerning 1994 Emergency Diesel Generator test program events which required entry into Technical Specification (TS) Section 3.0. On several occasions during 1994, with the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 operating at 100% power, one of the two Emergency Diesel Generators (EDGs) was removed from service for scheduled maintenance. In accordance with TS Action 3.7.2(d), the redundant EDG was tested daily during the respective maintenance period to ensure operability. Performance of portions of this test results in the tested EDG being rendered inoperable. However, the Action required by TS Section 3.7.2(d) cannot be met without placing the plant in a condition for which there is not a compensatory Action Statement. As a result, both EDGs were inoperable for approximately three hours on the days that the TS required test was performed, placing the plant in a condition outside the TS Limiting Condition for Operation 3.7. Therefore, TS Section 3.0 was entered for the duration of each testing period. During each time that both EDGs were inoperable, off-site power was available and operators were located at the EDG being tested with the ability to manually place the EDG in service should off-site power have been lost. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
2611994016 | Robinson 2 | 08/02/1994 | 11/11/1994 | 9411220263 | <strong>Manual Reactor Trip Due To Main Turbine Governor Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100% power. At 0541 hours, control room operators initiated a manual reactor trip in anticipation of an imminent automatic reactor trip due to rapidly decreasing turbine generator load. During the transient, operators received indication that a pressurizer power operated relief valve (PORV) had not completely reclosed after operating to relieve the pressure transient, and at 0554 hours, an Unusual Event was declared due to this configuration. Following the reactor trip, the plant was placed in normal hot shutdown status, with one PORV block valve shut. The Unusual Event was terminated at 0717 hours following verification that there was no leakage through the block valve. Subsequent investigation revealed that the PORV had, in fact, closed as required.<br /><br /> This event was caused by component failure. A fuse failure occurred in a control circuit that monitors the generator output breaker position, and closes the main turbine governor valves if the generator output breakers open with the unit operating at full load. Following fuse replacement and system testing, the plant was returned to 100 percent power. This report is submitted pursuant to 10 CFR 50.73 (a)(2)(vi) since this condition resulted in a manual reactor trip.
2611994017 | Robinson 2 | 08/05/1994 | 09/06/1994 | 9409150272 | <strong>Technical Specification 3.0: Safety Injection Pump Testing</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1994, with H. B. Robinson Steam Electric Plant, Unit No. 2 operating at 100%; power, the 'B' Safety Injection (SI) pump was taken out of service for corrective maintenance. In accordance with Technical Specification (TS) 3.3.1.2.b, the remaining operable SI pump (i.e., the 'A' pump) was then tested. Performance of portions of this operability test results in the pump being tested becoming inoperable. <br /><br /> TS Section 3.0 was entered when the 'A' SI pump was declared inoperable during performance of this Operations Surveillance Test since the 'B' SI pump was already inoperable. TS 3.3.1.2.b could not be met without placing the plant in a condition for which there is not an action statement (i.e., a condition prohibited by TS). The 'A' SI pump was inoperable for a period of twenty three minutes; an operator was located at the pump throughout the test and could have taken manual action should the pump have been required to perform its intended function. <br /><br /> This event is reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as operation in a condition prohibited by TS.
2611994018 | Robinson 2 | 08/09/1994 | 12/16/1994 | 9412230208 | <strong>Technical Specification 3.0: Containment Spray System</strong><br /><i>Abstract:&nbsp;</i>On August 9, 10, and September 30, 1994, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 operating at 100% power, the Containment Spray (CS) system was declared inoperable during Technical Specifications (TS) scheduled testing and Spray Additive Tank (SAT) educator line sampling. These evolutions require that the Refueling Water Storage Tank be lined-up to the SAT educator line that supplies Sodium Hydroxide to the CS pumps, thereby rendering the system incapable of performing its Iodine removal function under certain accident conditions. This configuration does not have an action required by the HBRSEP TS; therefore, TS Section 3.0 was entered. The CS system was declared inoperable between August 9, and 10, 1994, a total of six times; the CS system was declared inoperable four times on September 30, 1994. An operator was located in close proximity to the valves throughout the August 1994 testing and, although not procedurally directed, could have performed manual action should the system have been required to perform its intended function. During the September testing, procedural direction for manual action was provided to the operator. Upon completion of the testing, the system was restored to its normal configuration. These events are reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as operation in a condition prohibited by TS.
2611994019 | Robinson 2 | 08/22/1994 | 11/14/1994 | 9411220176 | <strong>Pressurizer Heatup And Cooldown Rate Limit Exceeded</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100% power. Following a review of an event at another CP&L plant, a determination was made that on February 26, 1994, with the plant in cold shutdown condition, the liquid temperature in the pressurizer exceeded the Technical Specifications (TS) limitation of 200 degrees F per hour. The accelerated cooldown rate was a result of an insurge of cooler Reactor Coolant System (RCS) fluid into the pressurizer during a period of relatively high temperature difference between the RCS coolant and the pressurizer liquid space. This event resulted from an inadequate procedure. Due to previous incorrect assumptions made by the plant staff, the procedure did not provide direction to specifically monitor and record the pressurizer cooldown rate. An analysis was performed that confirmed that this transient, as well as other similar transients during previous operations, did not adversely affect the structural integrity of the pressurizer. Procedures have been revised to require logging of pressurizer temperatures to ensure TS compliance; training is being conducted accordingly. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
2611994020 | Robinson 2 | 08/31/1994 | 12/05/1994 | 9412120150 | <strong>Technical Specification Violation Due To Mispositioned Valves</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1994, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 1000% power. Following review of a report of main steam line drain line root isolation valves being in the 'open' position, an initial determination was made that a condition existed that was outside the design basis of the plant, since these valves are considered to be containment isolation valves. Technical Specifications (TS) 1.7 and 3.6 collectively require that these valves be closed during normal operation. Subsequent reviews have shown that operating with the affected valves in the open position was within the design basis of the plant. administrative controls; however, from August 6 to August 29, 1994, the configuration of these valves were not administratively controlled. As such, the plant was operating in a condition prohibited by TS. This event was caused by personnel error. Specifically, an operator error during plant startup activities resulted in the valves not being returned to their closed position. Upon discovery of this condition, the mispositioned valves were placed in the closed position. The operator involved with the valves, misposition was counselled.<br /><br /> This report is submitted pursuant to 10 CFR 50.73 (a)(2)(i) as a condition
2611994021 | Robinson 2 | 09/01/1994 | 10/01/1994 | 9410030213 | <strong>TS Violation: Failure Of Operator To Properly Reactivate License</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1994, as a result of an evaluation to determine if inactive operator licenses were properly reactivated in accordance with 10 CFR 55.53(f)(2), a Shift Foreman holding a Senior Reactor Operator's license was determined to have performed watch duties without having properly conducted a complete plant tour as required for reactivation. This condition constitutes a condition prohibited by Technical Specifications (TS). Specifically, the TS requirements for the shift complement during hot operations were not met. This event was caused by a lack of written guidance delineating the plant tour requirements for operator license reactivation, and utilization of poor judgement on the part of the individual involved. Upon identification of this situation, the individual was restricted from his shift responsibilities pending proper reactivation, and the Acting Operations Manager issued a directive providing the necessary guidelines for conducting complete plant tours during license reactivation. A procedure is being developed to ensure license reactivation includes a thorough familiarization of equipment conditions and any plant changes that have occurred during the period the license was inactive. Although the individual licensee did not conduct a complete plant tour, there were no adverse safety consequences resulting from this situation. This report is submitted pursuant to 10 CFR 50.73 (a)(2)(i) as a condition prohibited by TS.
2611994022 | Robinson 2 | 09/07/1994 | 11/11/1994 | 9411210292 | <strong>Technical Specification 3.0: Safety Injection System</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1994, with the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 operating at 100% power, a Safety Injection (SI) accumulator and an SI pump were declared inoperable during performance of a feed and bleed evolution to increase the Boron concentration of the SI accumulator. This evolution requires that SI pump flow be lined up to the SI accumulator, thereby rendering the pump incapable of performing its injection function. The SI accumulator being fed is also out of service throughout this evolution if pressure, level, or boron concentration cannot be maintained. This configuration of SI equipment does not have a limiting condition for operation action required by Technical Specifications (TS); therefore, TS section 3.0 was entered to perform the feed and bleed evolution. Subsequently, on September 8, and October 12, 1994, an accumulator and SI pump were removed from service to perform the same evolution for that accumulator. A licensed operator was at the control board throughout both feed and bleed evolutions and could have taken procedurally directed, manual actions had the SI system been required to perform its intended function. Upon completion of the feed and bleed evolutions, the system was restored to its normal configuration. This event is reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as operation in a condition prohibited by TS.
2611994023 | Robinson 2 | 11/26/1994 | 12/26/1994 | 9412300152 | <strong>Condition Prohibited By TS Due To Degraded Reactor Trip Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1994, with the H. B. Robinson Steam Electric Plant, Unit No. 2 operating at 98.5% power, DC control power for 4kV Buses 1 and 2 was de-energized when a circuit breaker cable was inadvertently pulled out of the breaker's terminal during ground tracing activities. This rendered the undervoltage and underfrequency trips for the 'A' and 'C' reactor coolant pumps inoperable. The cause of the cable being pulled away from its termination was due to a loose electrical connection. The loose connection was repaired, and the circuit was returned to service. The action statement of Technical Specifications (TS) for underfrequency and undervoltage on the 4kV Systems states that, in the event that the minimum number of operable channels cannot be met, the reactor must be maintained in the hot shutdown condition. Since this action could not be met, TS Section 3.0 was entered. This condition did not have a safety consequence because the loss of undervoltage and underfrequency trips of the reactor coolant pumps are not credited for mitigating an accident in the Updated Final Safety Analysis Report Accident Analysis. Procedures will be implemented to provide instructions and precautions for inspection and tightening the specific electrical connections. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by TS.
2631994001 | Monticello | 03/23/1994 | 04/22/1994 | 9404260358 | <strong>Missed Surveillance Due to Procedural Error</strong><br /><i>Abstract:&nbsp;</i>A missed surveillance on the SRV Low-Low Set Logic was discovered while performing verification of the Reactor Pressure Relief System design basis document. The surveillance procedure contained incorrect prerequisites. During a reactor shutdown, the surveillance procedure was not performed as the procedural prerequisites were not met. Following discovery of the error, the surveillance was successfully completed at power using a special procedure. The surveillance procedure has been revised.
2631994002 | Monticello | 03/24/1994 | 08/02/1994 | 9408090282 | <strong>Instantaneous Trip of 480 VAC MCCBs Do Not Meet Acceptance Criteria Due to Manufacturer's Design</strong><br /><i>Abstract:&nbsp;</i>During routine plant preventative maintenance testing of a Klockner Moeller 480 VAC 3 phase molded case circuit breakers, it was discovered that the breaker tripped at a current below the lower tolerance for the instantaneous trip. Spare breakers of the same model number produced similar test results. The tests results were verified by an independent testing laboratory. The cause is believed to be the design of the breakers. In all cases, sufficient margin exists above requirements to ensure successful load operation. Motor starting, reduced voltage conditions, and fuse/breaker coordination were all considered. This report is a voluntary report as this issue caused no safety problem at Monticello. An Institute For Nuclear Power Operations - Nuclear Network item was issued on March 28, 1994 to inform the industry of this issue.
2631994003 | Monticello | 04/15/1994 | 05/16/1994 | 9405200147 | <strong>Transmission System Electrical Fault Causes Loss of Circulating Water Pumps Resulting in a Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>A transmission system electrical fault on the 345 kV system (originating at a nearby generating plant) caused protective relaying to trip plant equipment. The tripping of the Circulating Water Pumps caused the loss of the condenser vacuum, which caused a reactor scram. The electrical fault caused a decrease in voltage to approximately 55% for 2 to 3 cycles. A modification will be initiated to reduce the likelihood of similar substation transients initiating a reactor scram.
2631994004 | Monticello | 06/04/1994 | 07/05/1994 | 9407120064 | <strong>Electrical Storm Disables Plant Equipment on Two Occassions (One Led to a Reactor Scram on Low Condenser Vacuum and the Other Led to a Group 2 Isolation)</strong><br /><i>Abstract:&nbsp;</i>An electrical storm caused the loss of the Offgas Recombiner system resulting in loss of condenser vacuum causing a reactor scram. A second storm caused a false upscale trip on the Fuel Pool Monitor causing a Containment Isolation. be made to make the affected instrumentation less sensitive to electrical storms.
2631994005 | Monticello | 06/08/1994 | 07/08/1994 | 9407130291 | <strong>One Automatic Depressurization Valve Found Inoperable During a Drywell Entry</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1994, during a maintenance outage drywell entry, the instrument air line to the 'A' Safety/Relief Valve was found to be disconnected from the valve operator. This made the manual and Automatic Depressurization System features inoperable for the 'A' Safety/Relief Valve. There are 8 Safety/Relief valves installed, three of these are part of the Automatic Depressurization System. The point of disconnection for the affected Safety/Relief was downstream of the solenoid operated pneumatics supply/isolation valve. The failure of this line did not affect the operability of the other valves as each of the other valves have accumulators (which were fully charged) and check valves to prevent depressurization of the accumulator pneumatic supply. A brass fitting had broken; it was replaced and the valve was returned to service. No failure mechanism could be determined.
2631994006 | Monticello | 06/20/1994 | 07/19/1994 | 9407250149 | <strong>Licensed Operator Turns Wrong Switch During a Radiation Monitor Operability Test Causing a Group 2 Isolation</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1994, a licensed reactor operator was performing an operability test on the 'B' Fuel Pool Radiation Monitor. The operator turned the wrong switch and de-energized a different radiation monitor which caused a Group 2 isolation. The monitor was returned to service; the operability test completed and isolation was reset. The operator was disciplined and the radiation monitor switches have been modified to reduce the likelihood of an inadvertent de-energization.
2631994007 | Monticello | 06/22/1994 | 07/22/1994 | 9407250232 | <strong>Appendix R Fire Protection Program and Subsequent Surveillances Failed To Identify an Unsealed Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1994, an engineer discovered an inoperable fire barrier in the Division II Battery Room. The engineer was field verifying the Plant Control and Cable Spreading Structure Design Basis Document. Upon identification, an hourly fire watch was established. The fire watch continued until the barrier was sealed and operability was verified on June 24, 1994 at 1700. All other similar configurations were reviewed and no other problems were identified. The inoperable barrier had been overlooked by the original Appendix R review and subsequent surveillances. Training will be provided to personnel performing this surveillance in the future with respect to this event and other past similar events.
2631994008 | Monticello | 07/27/1994 | 10/31/1994 | 9411090129 | <strong>Structural Beam Connections Associated With the Cable Spreading Room Floor Found to be Different Than Design</strong><br /><i>Abstract:&nbsp;</i>While operating at 96% power on July 27, 1994, an engineer discovered a potential operability concern with the Cable Spreading Room Floor. The engineer was field verifying the Plant Control and Cable Spreading Structure Design Basis Document. The field welds for the framed beam connections did not conform with the design specified by the Architect Engineer. Initially actions were taken to ensure operability while additional structural analysis was conducted. The subsequent analysis determined that the connections are operable as installed. The field welds were made during original plant construction. This review also identified a concern with a modification that installed the Halon system in the Cable Spreading Room. A miscommunication between NSP engineers and the Architect Engineer resulted in the Halon system being installed with inadequate documentation. Improvements to the modification process have significantly reduced the probability of miscommunications similar to one discussed here.
2631994009 | Monticello | 09/07/1994 | 10/07/1994 | 9410140213 | <strong>Electrical Maintenance Personnel Error During Surveillance Test Causes Both Emergency Diesel Generators to Fast Start</strong><br /><i>Abstract:&nbsp;</i>Electrical maintenance personnel were performing the Monthly Degraded Safeguards Bus Voltage surveillance, when both Emergency Diesel Generators unexpectedly received a fast start signal and started. Electrical maintenance personnel did not perform the test in accordance with the procedure. An incorrect relay was manually actuated, causing the Emergency Diesel Generators to start. The person responsible was disciplined. The procedure will be modified.
2631994010 | Monticello | 09/19/1994 | 10/19/1994 | 9410260320 | <strong>Containment Isolation Valves Exceed Local Leak Rate Limits</strong><br /><i>Abstract:&nbsp;</i>The Local Leak Rate testing of the Containment Isolation Valves conducted during a refueling outage determined that the Technical Specification leakage limit was exceeded and one valve was not leak tested in the 'as found' condition. The measured leakage from 7 of the 8 Main Steam Isolation Valves exceeded the Technical Specification limit. The causes of the high leakage included changes in test methodology, wear and seat pitting. All failed inboard valves were repaired as needed. All the outboard valves are being replaced with valves of a different design. All valves not meeting the acceptance criteria were re-tested with satisfactory results. The cause of the one valve not being tested in the 'as found' condition is personnel error. The person was disciplined.
2631994011 | Monticello | 09/29/1994 | 06/07/1995 | 9506190329 | <strong>Inoperable Safety/Relief Valves Resulting in Violation of Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1994, during a refueling outage, it was discovered that potentially two Safety/Relief Valves were inoperable at the same time during the previous cycle. Technical Specification 3.6.E.1.a and 2.4.B require 7 of the 8 Safety/Relief Valves to be operable whenever reactor coolant pressure is greater than 110 psig and temperature is greater than 345 degrees F. <br /><br /> On January 19, 1994, during normal plant operation, a bellows leaking alarm was received on the 'H' Safety/Relief Valve (SRV) resulting in its self-actuation function being declared inoperable. On September 29, 1994 during the next refueling outage, ASME Section XI testing of the 'D' Safety/Relief Valve determined its self-actuation pressure setpoint to be out of acceptance range. Thus, the self-actuation function of 'D' Safety/Relief Valve was also inoperable for an undetermined portion of the previous operating cycle. Failure mechanism for 'H' Safety/Relief Valve was determined to be a leaking bellows O-ring. The high lift pressures of 'D' Safety/Relief Valve were attributed to an increase in the abutment gap between pilot stem and pilot disc. Both Safety/Relief Valves were replaced with spare units.
2631994012 | Monticello | 09/30/1994 | 10/31/1994 | 9411090148 | <strong>Fire Door Latch Found with Insufficient Throw Due to Original Construction Error</strong><br /><i>Abstract:&nbsp;</i>During the Triennial Fire Protection Plan Inspection, the latch on a double Fire Door was discovered to not meet the requirements of National Fire Protection Association 80, Standard for Fire Doors and Fire Windows. The latch was required to have a 3/4' throw and was found to have a 5/8' throw. The wrong latch was installed during original plant construction. The latch was replaced with a latch with a 3/4' throw. All Fire Doors in fire area barriers have been inspected to ensure that the correct latches are installed.
2631994013 | Monticello | 10/13/1994 | 11/10/1994 | 9411220128 | <strong>Spurious 480 VAC Breaker Trip De-energizes 120 VAC Instrument Bus Resulting in a Partial Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>While operations' personnel were switching power supplies for the Division II instrument busses, the breaker supplying the busses opened causing a partial containment isolation. No cause for the breaker opening could be found.
2631994014 | Monticello | 10/13/1994 | 11/14/1994 | 9411220168 | <strong>Missed Procedural Step While Switching the Power Supply to the Reactor Protection System to the Alternate Source</strong><br /><i>Abstract:&nbsp;</i>While switching power supplies for the Division II Reactor Protection System bus, a procedural step was missed causing the partial containment isolation. The plant was in a refueling outage at the time. The operator was disciplined.
2631994015 | Monticello | 10/15/1994 | 11/09/1994 | 9411220117 | <strong>Failed Component in the Uninterruptible Power Supply Inverter Causes a Partial Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>While performing a functional test of the Division II Uninterruptible Power Supply, a partial containment isolation occurred during a refueling outage. A logic card in the Uninterruptible Power Supply had failed and was replaced. The test procedure was changed so that testing is done when the instrument busses are being supplied by the alternate power supply. With the revised procedure, a failure identified during testing will not cause the instrument busses to be de-energized.
2631994016 | Monticello | 10/17/1994 | 11/15/1994 | 9411220234 | <strong>False High Reactor Pressure During Testing Causes a Partial Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>While flushing instrument lines with demineralized water, a partial containment isolation occurred during a refueling outage. The pressure in one of the instrument lines increased to the setpoint for the high pressure isolation of the Shutdown Cooling valves. these valves prior to performance of the test.
2631994017 | Monticello | 10/23/1994 | 11/22/1994 | 9411300273 | <strong>HPCI Isolates on High Steam Flow During Test at Lower than Normal Pressure</strong><br /><i>Abstract:&nbsp;</i>During a surveillance test of the High Pressure Coolant Injection System, the system steam supply valves closed on an automatic isolation signal of 150,000 lbm/hr steam flow for 45 seconds. The combination of performing the test at a reduced steam supply pressure and an indicated turbine speed error caused the steam flow to produce a differential pressure across the venturi that was greater than the isolation setpoint. As a procedure enhancement, the preventative maintenance procedure for the High Pressure Coolant Injection system will be modified to narrow the calibration tolerance for the turbine speed control system at the turbine speed of concern. The surveillance procedure for demonstrating High Pressure Coolant Injection pump operability will be modified to perform this test near 1000 psig.
2631994018 | Monticello | 10/26/1994 | 11/22/1994 | 9411300276 | <strong>Automatic transfer of HPCI Suction from the Condensate Storage Tanks to the Torus on High Torus Level During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>During a surveillance test of the High Pressure Coolant Injection System, the Suppression Chamber (Torus) water level rose to the setpoint for transferring the pump suction from the Condensate Storage Tank to the Torus. The cause of this event was the lack of an appropriate procedure action point to allow time for the operator to pump water from the Torus prior to the level reaching the transfer setpoint. An operator guideline will be established for the High Pressure Coolant Injection test identifying the level at which the Torus level should be reduced.
2651994001 | Quad Cities 2 | 01/26/1994 | 02/21/1994 | 9403040309 | <strong>RCIC Failed To Meet The Technical Specification Flow And Pressure Requirements</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in the STARTUP mode at 8% of rated core thermal power at 0430 hours on 01/26/94, at which time the quarterly Reactor Core Isolation Cooling (RCIC) [BN] pump [P] operability test was being performed in accordance with procedures QCOS 1300-5 in order to satisfy the 920 psig Reactor pressure operability requirement during startup. The Technical Specification of 400 gpm flowrate for the RCIC pump could not be obtained. <br /><br /> The Unit 2 RCIC system was declared inoperable. Additional testing was performed and the rotating element in the RCIC pump was replaced.<br /><br /> The cause of the event was increased clearances between the pump shaft throttle sleeve and throttle bushing, and the wear rings which reduced the margin of the pump's performance.
2651994002 | Quad Cities 2 | 01/27/1994 | 02/28/1994 | 9403090227 | <strong>Voluntary LER On The Unit Two Rod Mispositioning Event</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was between 20-25% thermal power and holding load. Unit 1 was holding load at less than 97% thermal power. On 1/27/94 on Unit 2, during the performance of QTS 130-4. 'Control Rod Scram Timing In The Hot Condition', control rod [rod] M-8 was withdrawn from position 00 to position 48 per the approved testing sequence. The rod was scrammed and the rod 'full in' position indicated (--), rather than the expected (00). The Nuclear Station Operator (NSO) incorrectly assumed rod M-8 needed to be re-tested and withdrew rod M-8 and left it at position 48 (without a control rod special maneuver written). Rod M-8 was not retested. The next in sequence rod, M-6, was withdrawn from 00 to 48. At this time it was noted that power had increased to a higher than expected level. It was then realized that rod M-8 had been mispositioned.<br /><br /> The Causal Factors related to this event were: inappropriate WORK PRACTICES, MANAGEMENT/SUPERVISORY METHODS, and VERBAL COMMUNICATIONS: ineffective CHANGE MANAGEMENT, WORK ORGANIZATION/PLANNING and TRAINING/QUALIFICATION also contributed.<br /><br /> Rod M-8 was returned to position 00 in accordance with QCOA 300-4. 'Mispositioned Control Rod'. Rod M-6 was also returned to position 00 and rod testing/movements were suspended. This is a voluntary Licensee Event Report.
2651994003 | Quad Cities 2 | 01/30/1994 | 02/28/1994 | 9403090075 | <strong>Unit Two HPCI Room Cooler Declared Inoperable Due To A Buildup Of Silt</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was in the RUN mode at 97% of rated core thermal power at 1200 hours on 01/30/94, at which time the 'ECCS Room and DGCWP Cubicle Cooler Differential Pressure Monthly Surveillance' procedure (QCOS 5750-9) was being performed. This surveillance procedure tests the cooling flow to area coolers in certain rooms that contain safety related equipment. <br /><br /> On 01/31/94 at 1630 hours, the Unit 2 High Pressure Coolant Injection (HPCI) [BJ] Room Cooler [CLR] was declared inoperable between 1200 hours and 2100 hours on 01/30/94, because of low cooling water flow. Flow was increased to an acceptable value and the surveillance frequency has been accelerated to every two (2) weeks. <br /><br /> The cause of the event was silt buildup in the cooling water system. The Mississippi River is the source of cooling water.
2651994004 | Quad Cities 2 | 01/31/1994 | 03/09/1994 | 9403150248 | <strong>Control Rod Coupling Integrity - Neutron Instrumentation Response Test Untimely Completion.</strong><br /><i>Abstract:&nbsp;</i>On 5/26/93 Unit 2 was taken critical. Technical Specifications section 4.3.B.1 states that nuclear instrumentation [IG] response shall be noted the first time a control rod [ROD] is withdrawn subsequent to each refueling outage, or upon subsequent exercising of these rods if no response is discernible due to low reactor [RCT] power. The procedure which implements this requirement QCOS 300-4 'CONTROL ROD COUPLING INTEGRITY - NEUTRON INSTRUMENTATION RESPONSE' was completed on 1/31/94. <br /><br /> The technical specification does not specify a time requirement for completing the test therefore the requirement was satisfied since the test was completed. The station is voluntarily reporting this occurrence due to it's untimely completion. <br /><br /> The cause of the event was the failure to prioritize and track the completion of QCOS 300-4, which is a WORK ORGANIZATION/PLANNING factor issue. <br /><br /> A revision will be added to QCTP 920-4, 'BEGINNING OF CYCLE STARTUP TEST PROGRAM', requiring, unless waiver authorization is received from the Operations and Station Managers, that QCOS 300-4 be completed prior to exceeding 75% power. This is a voluntary Licensee Event Report.
2651994005 | Quad Cities 2 | 06/21/1994 | 07/11/1994 | 9407190166 | <strong>Unit Two Electro Hydraulic Control (ECH) Fluid Leak and Subsequent Manual Scram.</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1994, Unit 2 was in the RUN mode at approximately 95% power. An Equipment Operator reported that the Electro Hydraulic Control (EHC) fluid reservoir level was rapidly decreasing. At 1405 the Reactor was manually scrammed and the main turbine was manually tripped due to anticipation of low EHC control oil pressure. <br /><br /> The source of the EHC fluid leak was discovered on a one inch EHC line to turbine control valve #2. It appears that the EHC line failure was due to high cycle fatigue crack propagation at the radius of the tube flare. The exact source of the cycle stresses responsible for the fatigue crack initiation and propagation could not be determined. A likely cause is that the stresses were induced by vibration on the EHC line caused by oscillations of the #2 turbine control valve. <br /><br /> The Causal Factors (C/F) for this event are attributed to Equipment Specification, Manufacture, Construction and Plant/System Operation. <br /><br /> Corrective actions that have been completed include: replacement of the EHC lines to the #2 control valve, liquid penetrant examination of the EHC lines to the #1, 3 & 4 control valves, replacement of the #2 control valve servo valve and circuit boards and recalibration of the #2 control valve controller loop. <br /><br /> Corrective actions to be completed include: analysis of the cracked tubing, evaluating the replacement of the flared fittings, and liquid penetrant examination of the EHC lines to the Unit 1 control valves.
2651994006 | Quad Cities 2 | 08/23/1994 | 09/19/1994 | 9409280252 | <strong>Unit Two Main Steamline (MSL) High Flow Group I Isolation From Rack Vibration By Contractor Personnel</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1994, Unit 2 was in the RUN mode at approximately 99% power. Contractor Instrument Maintenance (IM) personnel had received permission to calibrate the 2B Reactor Recirculation pump seal pressure transmitter located on an instrument rack immediately adjacent to one of the two Main Steamline (MSL) high flow instrument racks. At 0827 a Group I primary containment isolation (PCI) was received from a main steamline high flow signal. A Reactor Scram followed from Main Steam Isolation Valves not being full open while in the Run mode. <br /><br /> The root cause of this event was inadvertent vibrational disturbance to the MSL high flow instruments by contractor IM personnel working at the rack. This vibration resulted in the trip of the MSL high flow switches. A full Group I PCI and Reactor Scram then occurred. The Causal Factors for this event are attributed to Lack of awareness of the need for concern and Design configuration. Corrective actions that have been completed include: installation of vibration dampening pads, construction of an additional temporary barrier and placement of 'CAUTION Sensitive Equipment' signs around the instrument racks. <br /><br /> Corrective actions to be completed include: review current training requirements and consider additional training for all work groups at the station reiterating the sensitivity of the MSL high flow instrument racks and other racks identified as vibration sensitive, improving the permanent rack barriers and investigating a method to reduce the vibrational sensitivity of the MSL high flow actuation switches.
2651994008 | Quad Cities 2 | 04/17/1994 | 05/16/1994 | 9405240016 | <strong>Inboard And Outboard Reactor Recirculation Sample Isolation Valve AO-22-220-44 And 45 Failure To Close During Quarterly Surveillance.</strong><br /><i>Abstract:&nbsp;</i>At 0850 on 04/17/94, Unit-2 was in the Run mode at approximately 95% rated core thermal power. During performance of quarterly Reactor Recirculation System Air Operated Valve Testing (QCOS 202-12), the inboard and outboard Reactor Recirculation (RR) sample isolation valves AO 2-220-44 and 45 failed to close. Additional attempts to close both valves were successful. <br /><br /> The valves were declared inoperable due to failure to meet inservice inspection testing (IST) requirements.<br /><br /> The valves AO 2-220-44 and 45 were verified closed and taken out of service at 1000, on 4/17/94. <br /><br /> At 1140 the station made a 1 hour ENS phone call under 10CFR50.72(b)(1)(ii), degraded condition while operating. <br /><br /> The cause of the event and recommended corrective actions will be determined based on continuing testing and investigation. Further information will be provided as a supplement to this report.
2651994009 | Quad Cities 2 | 05/22/1994 | 09/15/1995 | 9509250373 | <strong>Primary Containment Interlock Doors Defeated To Release Personnel Trapped Inside Due To Malfunction Of Interlock Door Linkage.</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1994 Unit 2 had dropped to approximately 25% of rated core thermal power for a drywell entry. While inside the interlock, trouble-shooting a problem with the drywell interlock doors [BD], the entry team was unable to open the outer door [DR] and initiated emergency procedures to exit the drywell. <br /><br /> At approximately 0520 personnel outside the interlock removed the local leak rate test tap caps to provide air flow into the interlock. This started the 60 minute Limiting Condition for Operation (LCO) clock for opening an operable air lock door to repair an inoperable door or remove personnel.<br /><br /> Inside the interlock, emergency disassembly of the interlock linkage coupling was required to defeat the interlocks, and at 0529 the outer door was opened. At 0601 the outer door was secured. stopping the 60 minute LCO clock at 41 minutes. <br /><br /> The doors were locked closed and taken out of service to maintain primary containment. At 0642 a voluntary ENS notification was made to the NRC.<br /><br /> A voluntary LER is being submitted to report this event. The cause of the event and recommended corrective actions will be determined based on inspection and repair by the vendor during the next outage of sufficient duration. Further information will be provided as a supplement to this report.
2651994010 | Quad Cities 2 | 08/29/1994 | 09/28/1994 | 9410040134 | <strong>Control Rod D-11 Unplanned Scram From Position 48 to 00 During Instrument Maintenance Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 08-29-94, Unit 2 was in the run mode at 98% rated core thermal power. The Instrument Maintenance Department (IMD) was performing a monthly surveillance when a channel B 1/2 scram signal was intentionally inserted, and caused an unplanned scram of Control Rod Drive (CRD) [AA] D-11 from position 48 to 00. <br /><br /> The unplanned scram of CRD D-11 was due to instrument air leakage past the exhaust port diaphragm of the 117 scram solenoid pilot valve (SSPV) (SOL). This caused the 127 scram outlet valve to open when the channel B 1/2 scram signal was inserted. <br /><br /> Corrective actions included taking Hydraulic Control Unit (HCU) D-11 out-of-service, rebuilding the HCU SSPVs, and rebuilding the 127 scram outlet valve.
2651994011 | Quad Cities 2 | 10/06/1994 | 11/07/1994 | 9411150323 | <strong>Thirty Day Limited Condition Of Operation Exceeded For The 2B Residual Heat Removal Service Water Pump Due To Inadequate Work Planning And Scheduling.</strong><br /><i>Abstract:&nbsp;</i>At about 2320 hours on 09/06/94, Unit-2 was in the Run mode at 95% power, and the 2B Residual Heat Removal Service Water (RHRSW) pump was taken out of service for scheduled maintenance. A voluntary, 30 day Limited Condition of Operation (LCO) was entered.<br /><br /> At 2320 hours, on 10/06/94, the 2B RHRSW pump train exceeded the LCO. The cause of the pump train exceeding the LCO was due to inadequate work planning, and scheduling, and poor communication. <br /><br /> At the time the LCO was exceeded, both Quad Cities units were shutdown by station management due to declining station performance with respect to this job and other events. A Work Control Task Force to improve the station's work control process was started, and a root cause investigation was initiated in response to events leading up to the decision to shutdown Quad Cities Unit-2. A meeting was held with all individuals associated with this event to identify lessons learned, develop an action plan, and develop corrective actions needed to prevent recurrence. <br /><br /> Corrective actions to be completed are, evaluating inventory of major RHRSW pump parts, improved communication with respect to pipe movement, and issuance of engineering requests prior to entering an RHRSW LCO. The RHRSW system design will be reviewed to validate as-built condition, and preliminary solutions to engineering issues from past RHRSW maintenance activities, shall be addressed prior to voluntarily entering an RHRSW LCO.
2661994001 | Point Beach 1, Point Beach 2 | 02/08/1994 | 03/08/1994 | 9403150413 | <strong>Failure To Perform a Fire Watch at the Technical Specification Frequency</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1994 at 0743, with both units operating at full power, the automatic actuation feature of the Halon fire suppression system for the auxiliary feedwater pump room and the vital switchgear room was disabled to support modification work being performed in the area. As a result of disabling this portion of the Halon system, hourly fire rounds were required to be performed by the Technical Specifications. However, fire rounds were only performed twice during the 8-hour day shift. At 1515, during the swing shift crew briefing, it was determined that the fire rounds were not being performed at the required frequency. The Duty and Call Superintendent was notified and hourly fire rounds were commenced at 1530. These hourly fire rounds continued until the Halon system was restored to service at 1622 on February 8, 1994.
2661994002 | Point Beach 1, Point Beach 2 | 02/08/1994 | 03/09/1994 | 9403160301 | <strong>Inoperability Of Both Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>At 0339 hours, on February 7, 1994, with both units operating at full power, Emergency Diesel Generator (EDG) G02, the Train B EDG, was voluntarily removed from service for annual maintenance. This required placing both PBNP units into the LCO defined in Specification 15.3.7.B.1.g which states that an emergency diesel generator can be inoperable for up to 7 days provided the other emergency diesel generator (in this case the Train A EDG G01) is tested daily to ensure operability. On February 8, 1994, at 2204 hours, EDG G01 was declared inoperable due to abnormal voltage regulator indications. The declaration of EDG G01 as inoperable placed both units in a condition, which by Technical Specification 15.3.0.A, required both units be placed in hot shutdown within 3 hours (by 0104 hours on February 9, 1994). A Notice of Enforcement Discretion (NOED) was requested from the NRC, to allow additional time in the LCO to return at least one EDG to service. The NOED was granted at 2320 hours on February 8, 1994. At 0244 hours, EDG G01 was returned to an operable status, Technical Specification LCO 15.3.0.A was exited and the 7-day LCO required when one EDG is inoperable (EDG G02) was continued.
2661994003 | Point Beach 1, Point Beach 2 | 02/17/1994 | 03/21/1994 | 9403250225 | <strong>Reactor Coolant Sample System Containment Isolation Valve Testing</strong><br /><i>Abstract:&nbsp;</i>A comprehensive review of containment mechanical penetrations and our 10 CFR 50, Appendix J testing program was performed to verify that the appropriate testing was being conducted and to ensure that the Point Beach Nuclear Plant design and licensing basis for containment isolation is being appropriately maintained. Penetration P-28a in both units, reactor coolant system hot leg sample lines, was identified as potentially not meeting redundant barrier design criteria for containment penetrations in its tested configuration. The tested isolation valve inside containment is located inside the missile shield which is in conflict with FSAR requirements. A subsequent evaluation was performed, based on leak before break analyses and the probability of failure of the sample line following a design basis event, that justified returning the sample line to service for an interim period until final corrective action can be taken.
2661994004 | Point Beach 1 | 04/27/1994 | 05/25/1994 | 9405310223 | <strong>Unexpected Automatic Reactor Trip During Hot Control Rod Drop Testing</strong><br /><i>Abstract:&nbsp;</i>At 1214 hours CDT on April 27, 1994, while Point Beach Nuclear Plant (PBNP) Unit 1 was shut down during its annual refueling outage, an unexpected reactor trip occurred during hot control rod drop testing. Reactor protection analog testing was being performed concurrently with hot control rod drop testing. Due to a degraded steam flow transmitter, the Duty Shift Superintendent (DSS) and Instrumentation and Control (I&C) technician expected to receive a Unit 1 reactor trip signal from low steam generator level concurrent with feed flow/steam flow mismatch when the low steam generator level switch was placed in trip. However, they did not expect the reactor trip breakers to be shut or any control rods to be withdrawn at that time. The trip signal caused shutdown control rod bank A to drop from 20 steps. All other rods were fully inserted in the core. The event was caused by inadequate coordination of activities in the control room. A 4-hour ENS notification was made in accordance with 10 CFR 50.72(b)(2)(ii). The NRC Resident Inspector was also notified.
2661994005 | Point Beach 1 | 05/09/1994 | 06/08/1994 | 9406140101 | <strong>Unit 1 Reactor Cavity Cooling Fans in a Condition Outside of Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1994, during Unresolved Safety Issue A-46, 'Seismic Qualification of Equipment in operating Plants,' seismic verification walkdowns being performed at Point Beach Nuclear Plant on the Unit 1 containment reactor cavity cooling fan assemblies, it was discovered that their installed configuration differed from the installation detail contained on an original drawing. A follow-up inspection conducted on April 12, 1994, revealed that the plenums for each fan were not anchored to the containment structure, as required. Upon determination of this situation, a modification request was initiated. This modification was completed on April 22, 1994, ensuring that the Unit 1 containment reactor cavity cooling fan assemblies were properly anchored to the containment structure. Subsequent to the completion of the modification, an evaluation was completed that determined that Unit 1 had been in a condition potentially outside its design basis.
2661994006 | Point Beach 1, Point Beach 2 | 06/18/1994 | 07/18/1994 | 9407220154 | <strong>Incorrect Operability Determination Following Spurious Halon Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1994 at 1233, with both units operating at full power, the Halon fire suppression system spuriously actuated and released Halon into the cable spreading room. As a result of this actuation, the Halon system was declared inoperable and hourly fire rounds were commenced in the cable spreading room, vital switchgear room, and auxiliary feedwater pump room, as required by the Technical Specifications. Fire Protection and Safety Coordinator, the Duty Shift Superintendent declared one bank of the Halon system operable and available to provide fire suppression to the vital switchgear room and the auxiliary feedwater pump room. He then suspended the hourly fire rounds for these two rooms. On June 20, 1994, at 0200, a different Duty Shift Superintendent declared the Halon system inoperable and recommenced hourly fire rounds in all three rooms pending further evaluation. At 0600, the plant's Fire Protection and Safety Coordinator determined that the Halon system was inoperable and that hourly fire rounds were required.
2661994007 | Point Beach 1, Point Beach 2 | 07/13/1994 | 08/12/1994 | 9408170197 | <strong>Containment Integrity Requirements Not Satisfied During Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1994, it was discovered that, during inservice stroke testing of the low head safety injection (SI) suction valves, 1(2)SI-850A and 1(2)SI-850B, a drain and vent path between the Unit 1 or Unit 2 SI-850 and SI-851 valves is opened to the Plant Auxiliary Building (PAB). When the SI-850 valves are stroked open, a direct path exists between the containment atmosphere and the PAB. As such, during the stroke test of 1(2)SI-850A or 1(2)SI-850B, containment integrity is not maintained as required by Point Beach Nuclear Plant's Technical Specifications (TS). Test procedures are being modified to station a dedicated operator at the drain valve during testing to shut the valve if an event occurs requiring containment isolation.
2661994008 | Point Beach 1 | 08/12/1994 | 09/12/1994 | 9409210263 | <strong>Containment Integrity Requirements Not Satisfied During Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1994, it was discovered that, during inservice stroke testing of the low head safety injection (SI) suction valve, 1SI-850A and 1SI-850B, a drain and vent path between the Unit 1 SI-850 and SI-851 valves was opened to the Plant Auxiliary Building (PAB). A dedicated operator was not stationed at the drain valve to shut the valve in the event of a accident which requires containment isolation. As such, containment integrity was not maintained as required by Point Beach Nuclear Plant's Technical Specifications (TS). When the SI-850 valves are stroked open, a direct path exists between the containment atmosphere and the PAB. Test procedures have been modified to station a dedicated operator at the drain valve during testing to shut the valve if an event occurs requiring containment isolation.
2661994009 | Point Beach 1, Point Beach 2 | 09/09/1994 | 10/06/1994 | 9410130065 | <strong>Inadvertent Emergency Diesel Start And Loss Of A Station Battery Charger</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1994 at about 1114 hours, with both units at full power, a fuse in the Unit 2, B train, 4160V emergency bus 2A-06 metering and relaying circuit blew during modifications to Control Board C-02 for the installation of additional emergency diesel generators. The blown fuse caused a 2A-06 undervoltage signal to be generated. The undervoltage signal caused the normal power supply breaker for 2A-06 to open and deenergize the bus. Emergency Diesel Generator G-02 immediately started and reenergized the 2A-06 bus. One of the four station battery chargers (D-08) tripped off, as expected, during the momentary loss of power to the Unit 2, B train. D-08 was restored at 1129 hours. The DC buses for PBNP are shared by both units; therefore, this event affected both units. The normal configuration of the other equipment that was affected was re- established. The blown fuse was replaced at about 1400 hours and the normal configuration of the electrical distribution system was re- established at 1429 hours. The blown fuse was the result of an inadequate procedure because the procedure did not contain the proper equipment isolation for the work being performed.
2661994010 | Point Beach 1, Point Beach 2 | 09/27/1994 | 10/25/1994 | 9411030127 | <strong>Inadvertent Emergency Diesel Generators Start, Loss Of Two Station Battery Chargers, And Unit 2 Loss Of Decay Heat Removal</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1994, Unit 1 was operating at full power and Unit 2 was in cold shutdown. The gas turbine was to be used as the sole power source for the Unit 2 4160 volt supply buses (A03 and A04) for a short period of time, to establish cross-ties to the Unit 1 4160 volt supply buses, A03 and A04. The control operator, operating the gas turbine, incorrectly manipulated the controls by lowering speed and voltage of the gas turbine when speed should have been raised. Voltage on the Unit 2 4160 volt system was reduced and reached the degraded voltage relay setpoint. At 0223 hours, the degraded voltage condition caused actuation of the degraded voltage relays for Unit 2, which initiated opening of the normal safeguards buses supply breakers for Unit 2. The emergency diesel generators automatically started and provided power to the Unit 2 safeguards buses. restoration of the two station battery chargers, decay heat removal for Unit 2, and off-site power to Unit 2 via the 4160 volt supply buses cross-ties from Unit 1. The electrical distribution system was restored and other equipment that tripped-off during the loss of power was recovered. All the required equipment operated properly. Unit 1 continued to operate at full power and Unit 2 remained in cold shutdown during this event.
2661994011 | Point Beach 1, Point Beach 2 | 10/04/1994 | 11/03/1994 | 9411070376 | <strong>Redundant Decay Heat Removal Requirements Not Met During Refueling Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1994, we discovered that on April 9, 1994, during the Point Beach Nuclear Plant Unit 1, annual maintenance and refueling outage, both residual heat removal pumps were secured when reactor coolant system temperature was <140 degrees F with fuel in the core, a condition prohibited by Point Beach Technical Specifications. The cause of this event is inadequate communication to the operators concerning the interpretation of Technical Specification 15.3.1.A.3.b. Inadequacies in the temporary procedure change process are contributing factors. Both residual heat removal pumps were secured for less than two minutes and residual heat removal suction and discharge temperatures remained steady at approximately 74 degrees F and 54 degrees F, respectively. The health and safety of plant personnel and the public were not impacted by this event.
2691994001 | Oconee 1, Oconee 2, Oconee 3 | 02/21/1994 | 03/23/1994 | 9403290009 | <strong>Seismic/Loop Event May Result In The Loss Of Post Accident Cooling Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1993, during a walkdown of the Condenser Circulating Water (CCW) System, a System Engineer discovered that four CCW valves on each unit were not shown on the CCW flow diagrams and the valves were adjacent to buoyancy restraints. On February 17, 1994, with Oconee Units 1 and 2 at 100% Full Power and Unit 3 in a refueling outage, an operability evaluation was completed by Oconee Engineering. The evaluation revealed that the Emergency CCW System and the Low Pressure Service Water System had been inoperable during various periods from July 1991 to January 1994, due to a potential for interaction between the valves and restraints, during a seismic event. Deficiency: Unanticipated Interaction of Components, (Design oversight). Corrective actions include a review of all engineering documents and associated training will be conducted and revised/implemented as appropriate. Immediate corrective action was a modification which increased the distance between the restraints and instrument lines.
2691994002 | Oconee 1 | 02/26/1994 | 03/28/1994 | 9404060015 | <strong>Inappropriate Action Results In False High Steam Generator Level Causing Loss Of Main Feedwater And Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1994, at 0657 hours, Oconee Unit 1 tripped on loss of both Main Feedwater (MFDW) pumps, while operating at 100% Full Power. An Instrument and Electrical Supervisor (IES) was removing power from an Integrated Control System power supply that had failed and was smoking. The IES removed a neutral wire that is daisy chained with other devices. When the neutral (daisy chained) terminal was loosened, the 1B Steam Generator high level circuits were de-energized. This condition resulted in a trip of the Main Turbine/Reactor, of both MFDW pumps, and the initiation of the Emergency Feedwater system. The Unit was stabilized at Hot Shutdown conditions. The root cause of the Unit trip was Inappropriate action; Improper action (Response chosen was proper but proper execution failed because; a human factors deficiency existed). A contributing cause is Equipment Failure. Corrective actions included replacing the defective power supply and removing the daisy chain associated with this circuit.
2691994004 | Oconee 1, Oconee 2, Oconee 3 | 07/26/1994 | 03/30/1995 | 9504070171 | <strong>Post Accident Core Cooling Technically Inoperable Due To A Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1994, during the planning process for maintenance on the High Pressure Service Water System (HPSW), System Engineering (SE) was asked to determine the applicable Limiting Conditions for Operations. SE determined that the HPSW was required for Emergency Condenser Circulating Water (ECCW) siphon flow when lake level is low, and this could render the Low Pressure Service Water (LPSW) System inoperable. As a result, SE performed an operability evaluation. On July 26, 1994, with all three Oconee Units at 100 % Full Power, SE completed the evaluation which revealed that the ECCW System could not maintain siphon flow as required following a Loss of offsite Power event if lake level is less than 798.13 feet and the Elevated Water Storage Tank is unavailable. The evaluation also determined that the LPSW System had been inoperable for short durations in the past due to this condition. Further evaluation completed by SE on February 15, 1995 revealed that the LPSW System had been past inoperable on other occasions due to the Unit 1 MFB being out of service greater than 72 hours. The root cause of this event is a Design Deficiency, Unanticipated Interaction of components, (Design Oversight). Planned corrective actions included reviewing and revising design basis documents.
2691994005 | Oconee 1 | 10/05/1994 | 11/03/1994 | 9411100253 | <strong>Containment Isolation Valve Technically Inoperable Due to Change Management</strong><br /><i>Abstract:&nbsp;</i>At 1745 hours on October 5, 1994, with Unit 1 at 100 % power, it was discovered that Post Maintenance Testing (PMT) had not been performed following maintenance on containment isolation valve 1RC-7, rendering the valve technically inoperable. Upon discovery, all compensatory actions required by the Technical Specifications were completed. The Work Order's cover sheet indicated that a stroke test and a leak rate test were required to be performed; however, another sheet, titled the PMT Plan, listed the required tests and they were marked Not Applicable (N/A) in the 'completion/verified by' column. During the planning process the N/A's were entered to indicate that no signatures were required in the column. Maintenance personnel however, interpreted the N/As to mean that the tests were not required. As a result, the appropriate personnel were not notified to perform the PMT. The root cause of this event is Change Management (Risks and consequences associated with change not adequately assessed). Corrective actions included taking the appropriate compensatory actions per the Technical Specifications, changing the method of N/Aing, revising all previously planned work orders which contained similar misleading information, and communicating to all maintenance personnel that N/A's should be questioned.
2691994006 | Oconee 1, Oconee 3 | 12/15/1994 | 01/12/1995 | 9501240194 | <strong>Technical Specification Limit Exceeded Due To Vendor Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1994, Unit 1, and 3 were at 100% full power. Unit 2 was at Hot Shutdown conditions following a unit trip. Instrument and Electrical technicians were performing routine calibration of Unit 1 Reactor Protective System loss of Feedwater pressure switches. Switch setpoint drift was identified during the calibration. On December 12, 1994, the setpoint drift for some switches was determined by engineering evaluation, to be excessive. The vendor is testing and evaluating the pressure switch to determine the cause of the excessive setpoint drift. The root cause of the event is Vendor Design Configuration and Analysis; Design Analysis; Component functional design deficiency. Corrective actions include increasing calibration frequencies and replacing or repairing the pressure switches.
2701994001 | Oconee 2 | 02/08/1994 | 03/10/1994 | 9403160207 | <strong>Technical Specification Limit Exceeded Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1993, at 2100 hours, Operations personnel discovered water leaking from the 2A Motor Driven Emergency Feedwater Pump automatic initiation pressure switch (2PS0386). On December 30, 1993, the switch was replaced, an investigation was initiated, and an engineering evaluation into the past operability was requested. on February 8, 1994, with Unit 2 at 100% full power, the engineering evaluation determined that the 2A Motor Driven Emergency Feedwater Pump would not have automatically initiated on low Main Feedwater (MFDW) discharge pressure while the switch contacts were shorted by the water intrusion. A DC ground alarm had been received on December 14, 1993 but had not been located until the pressure switch was replaced on December 30, 1993. Problems with this model switch have been identified previously and replacements of a different design were in the process of being scheduled. The root cause of this event is equipment failure. <br /><br /> Corrective actions include replacing the defective pressure switch and to replace other switches of this model, used for sensing MFDW discharge pressure, on all three Oconee Units.
2701994002 | Oconee 2 | 04/06/1994 | 05/04/1994 | 9405160126 | <strong>Reactor Trip On Loss of Both Main Feedwater Pumps Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1994, Unit 2 was operating at 100% Full Power (FP) when the 2B Main Feedwater Pump (MFDWP) tripped on low oil pressure at 1047 hours. The Integrated-Control System (ICS) automatically ran back reactor power to approximately 54% FP as designed. Automatic control of the 2A MFDWP was erratic, resulting in feedwater oscillations. As operators were taking ICS stations to manual to control the feedwater swings, the 2A MFDWP tripped on high discharge pressure. This resulted in an Anticipatory Reactor Trip at 1108 hours, due to the loss of both MFDWPs. The response of operators and .automatic systems brought the unit to stable hot shutdown conditions. An investigation into the cause of the 2A and 2B MFDWP trips revealed a set screw on the 2A MFDWP's Motor Gear Unit was loose and the Main Shaft Oil Pump gear's on 2B MFDWP had failed. The root cause was Equipment Failure with a contributing cause of Defective Procedure (technical deficiency). Corrective actions included revising the MFDWP's preventive maintenance procedure, replacing the set screw, and the repair of 2B MFDWP.
2701994003 | Oconee 2 | 07/28/1994 | 08/25/1994 | 9409060114 | <strong>Unplanned Reactor Protective System Actuation While Sub- Critical Due To Deficient Work Practices</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1994, Oconee Unit 2 was in the process of shutting down to repair a steam generator tube leak with the unit sub-critical and all control rods fully inserted, an unanticipated Reactor Protective System (RPS) trip occurred at 0115 hours. Per procedure, the operators had placed the RPS in bypass at a Reactor Coolant System (RCS) pressure of approximately 1700 psig and decreasing, which shifted the high pressure trip setpoint to 1710 psig. At about the same time, a make-up valve had opened automatically to maintain the Pressurizer level at setpoint. This increased RCS pressure also. The control operator noted that RCS pressure was at 1690 psig, but failed to recognize that pressure had started increasing rather than decreasing. While the operator was reading procedure limits and precautions for the next step, the RCS pressure reached the trip setpoint. The primary root cause is Deficient Work Practices (Error Detection Practice: self-checking not applied to ensure expected response) with a secondary root cause of Supervisory Methods (job performance and self-checking standards not properly communicated). Corrective actions include personnel counselling, a procedure change, and clarification of management expectations.
2701994004 | Oconee 2 | 10/21/1994 | 11/17/1994 | 9411250092 | <strong>Inadequate Work Practices Results In Advertent Engineered Safeguards Actuation While Defueled</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1994, Unit 2 was in a refueling outage with no fuel in the core. Instrument and Control Maintenance technicians were performing Engineered Safeguards (ES) System Analog Channel B Reactor Coolant Pressure Channel Calibration. At 1320 hours, an invalid actuation of ES occurred due to the technicians manipulating channel A instead of B while performing this calibration. When this actuation occurred, ES channels 1 through 4 started the ES related equipment that was in service. The other ES channel 1-4 related equipment was out of service due to the outage. Operators verified the actuation was invalid and secured the systems/components that had started. The root cause of the ES actuation is Work Practices; Error detection practices; Self-checking not applied to ensure correct train. documents; Omission of relevant information. Corrective actions include training personnel, revising procedures, and adding labels.
2701994005 | Oconee 2 | 12/08/1994 | 01/05/1995 | 9501190229 | <strong>Equipment Failure of Breaker Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1994, at 1425 hours, Unit 2 Reactor tripped from 100% full power. The Reactor tripped when a breaker that supplies 'auto' power to the Integrated Control System (ICS) tripped. The loss of 'auto' power caused a relay to deenergize (by design) that introduced a false high Steam Generator (S/G) level that tripped the Main Feedwater Pumps and the Main Turbine. The trip of the Main Feedwater Pumps and Main Turbine resulted in an anticipatory trip of the Reactor Protective System. Emergency Feedwater automatically actuated with all three pumps starting and feeding the S/Gs as expected. The Unit was then stabilized at Hot Shutdown condition with decay heat removal via the S/Gs. No major problems were noted as a result of the trip. Investigation revealed a loose lug on the load side of the breaker that generated sufficient heat to trip the breaker on thermal overload. The root cause of the event is equipment failure possibly due to thermal cycling. Corrective actions included the changeout of the power supply breaker and review of breaker preventive maintenance program.
2711994001 | Vermont Yankee | 01/06/1994 | 02/03/1994 | 9403140246 | <strong>Non-Conservative Technical Specification Setpoint Range Applied to Calibration Procedure for Rod Block Monitor Auto-Bypass Feature Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 1/6/94 at 1250 hours, with the reactor operating at 100% steady state power, it was identified that the setpoint for the Rod Block Monitor (RBM) Auto Bypass Logic was potentially set at a value which was slightly non-conservative relative to the specific value contained in Technical Specifications (TS). Following a review of the condition by plant personnel, it was confirmed that an error existed in the calibration procedure, that the setpoint was non-conservatively set, and a 1-hour NRC notification was made at 1524 hours on 1/7/94. Technical Specifications (TS) allow the RBM to be bypassed when reactor power is /= 30% power. Corrective actions presently being implemented as a result of other recently identified TS non-compliance issues were reviewed and are considered appropriate to prevent recurrence of this event.
2711994002 | Vermont Yankee | 02/09/1994 | 06/30/1994 | 9407060236 | <strong>Alternate Cooling System Water Temperature Greater Than Design Basis During Warm Weather Circ Water System Operation Due to Inadequate Analysis of the Alternate Cooling System</strong><br /><i>Abstract:&nbsp;</i>During a Self Assessment of the Service Water System and as a result of evaluations conducted to respond to issues identified by this assessment, several design conditions were identified which may have precluded the Alternate Cooling System from performing its intended design basis functions <br /><br /> The root cause of this event has been determined to be an inadequate analysis of the Alternate Cooling System to ensure that it could achieve its design basis function to remove sensible and decay heat from the reactor under all postulated design basis events <br /><br /> Corrective actions included procedure changes, the documentation of a Basis for Maintaining Operability (BMO) and an update to the FSAR under 10CFR50.59 to ensure that the FSAR accurately describes required parameters
2711994004 | Vermont Yankee | 04/10/1994 | 06/05/1995 | 9506140134 | <strong>Reactor Scram from High Moisture Separator Level due Inadequate Maintenance on the "C" Moisture Separator Normal Drain Valve Level Transmitter</strong><br /><i>Abstract:&nbsp;</i>On 4/10/94, at 0122 hours with the reactor at 98.5 % power, a reactor scram occurred from a Turbine Control Valve (TCV) Fast Closure scram signal due to a high level in the 'C' Moisture Separator (MS). The event was initiated during turbine testing when the level transmitter for the Normal Level Control valve failed to sense an increasing level in the MS Drain Tank due to a shift in calibration of the transmitter. This allowed the level in the MS Drain Tank to increase to the Emergency Dump Valve opening setpoint. The Emergency Dump Valve Level Transmitter sent an open signal to the Emergency Dump Valve Level Controller but the controller failed to bleed the air off the Emergency Dump Valve diaphragm which allows the valve to open. Consequently, the high MS level trip point was reached and tripped the turbine which resulted in the TCV Fast Closure scram. <br /><br /> During this event, a subsequent reactor scram and corresponding Primary Containment Isolation signals for Groups 2,3 and 5 were received due to low reactor water level. The reactor was stabilized in Hot Standby, the Primary Containment Isolations were reset, Reactor Water Cleanup was restarted and normal water level was re-established using the 10% Feedwater Regulator valve. <br /><br /> The apparent cause of this event is inadequate preventive maintenance of the Emergency Dump Valve level controller. The failure mode of the controller could not be determined as the controller was checked and recalibrated, in an effort to correct the problem, prior to being sent to the manufacturer for analysis. A contributing cause of this event is a calibration shift of the normal water level transmitter. Corrective Actions include replacement and calibration of the level instruments and controllers in the MS drain system.
2711994005 | Vermont Yankee | 03/30/1994 | 04/29/1994 | 9405090014 | <strong>Service Water System Configuration Outside Of Design Bases</strong><br /><i>Abstract:&nbsp;</i>On 2/9/94, the Fire Suppression Water Supply System was declared inoperable. Utilizing plant procedures, operators cross-connected the Station Service Water System with the Fire Suppression Water Supply System by opening valve SW-8. This put the plant outside of its design basis, as it has been determined that it may not have been possible to maintain adequate cooling flow to essential equipment following a design basis Loss of Coolant Accident concurrent with a Safe Shutdown Earthquake, failure of one diesel generator and the assumed failure of the non-seismic fire system. <br /><br /> The root cause of this event is inadequate design of the cross-connection portion of the Service Water System. Inadequate procedures were generated due to the inadequate design. <br /><br /> Valve SW-8 has been tagged shut to prevent re-opening. Procedural changes will be made to prevent recurrence of this event. Additional evaluations will be performed to determine if similar potential configurations exist elsewhere in the Service Water System.
2711994006 | Vermont Yankee | 04/12/1994 | 11/09/1994 | 9411170097 | <strong>Missed Reactor Coolant Conductivity Samples due to a Misinterpretation of the Test Method Used to Meet Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 4/12/94, during a chemistry training class, it was discovered that, contrary to Technical Specifications (T.S.) 4.6.B.3.a, a reactor coolant conductivity sample had not been taken on a 'once every 96 hour' basis since 6/19/92. A new highly accurate laboratory quality conductivity monitor had been installed that continuously measures conductivity and this was assumed to exceed the intent of the T.S. due to the increased accuracy, the continuous monitoring mode of the monitor, and by recording the conductivity on a daily basis. This replaced the once every 96 hour sampling that was accomplished with a portable conductivity meter used to verify the accuracy of the old installed conductivity monitor. <br /><br /> The root cause of this event is a misinterpretation of a test method used to meet the T.S. requirement. A contributing cause is a lack of consistent application of the requirements in the T.S. Bases for Chemistry. <br /><br /> The immediate corrective actions were to revise the sampling procedure to require the resumption of the 96 hour conductivity sample; training of the Chemistry Supervisory Staff on the importance of the T.S. Bases in determining surveillance requirements; and a review of Chemistry T.S. Surveillances to determine if any other frequency or performance discrepancies existed. Long term corrective actions include a Chemistry Department six month self-assessment of the effectiveness of the review of T.S. related procedure changes.
2711994007 | Vermont Yankee | 04/20/1994 | 05/20/1994 | 9405260104 | <strong>Inadvertent Primary Containment Isolation System Actuation Due To A Spurious Spike On A Refuel Floor Radiation Monitor.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1521 hours on 04/20/94, with the reactor operating at approximately 100% power, a Standby Gas Treatment System (SBGTS) initiation and Reactor Building Ventilation isolation occurred concurrent with a Primary Containment Isolation System (PCIS) Group III isolation. These isolations and the initiation of SBGTS were caused by a spike on the 'B' Refuel Floor Radiation Monitor. <br /><br /> The cause of the event was dirty/oxidized contacts on the function switch for the radiation monitor. <br /><br /> Corrective actions consisted of cleaning the function switch contacts on the subject monitor and the other three radiation monitors that initiate a PCIS Group III isolation.
2711994008 | Vermont Yankee | 10/03/1994 | 08/29/1995 | 9509050149 | <strong>HPCI/RCIC System Inoperable Due To Low Spiking Of Level Transmitter LT-2-3-728 Instrument Loop</strong><br /><i>Abstract:&nbsp;</i>On 10/03/94 at 1520 hours, with the reactor operating at 100% steady state power and the plant preparing for a scheduled maintenance shutdown, several low spikes occurred in Reactor Water Level Instrument Loop LT-2-3-72B resulting in a momentary loss of high water level trip capability for High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. Both systems were declared inoperable as a result of the event. The plant entered a Technical Specifications (TS) imposed 24 how plant shutdown which was later exited at 2030 hours following completion of equipment troubleshooting by Instrumentation and Control personnel. <br /><br /> The root cause of this event is unknown. Actions and equipment surveillance completed to date have been unable to pinpoint the cause of the downspiking. Based on a review of similar events which have occurred elsewhere coupled with manufacturer discussions to date, it is believed that a Rosemount Model 710DU Master Trip unit PC board (K1) calibration relay may have malfunctioned after the performance of monthly surveillance earlier in the day, during which, the relay was cycled. On 11/07/94, the plant reentered the Tech Spec 24 hour shutdown action statement to replace the suspect trip unit, which was subsequently returned to the vendor for failure analysis. Vendor testing and inspections performed on the returned trip unit did not identify any operational deficiency or other direct evidence supporting the reported failure condition. There has been no reoccurrence of spurious spiking in the LT-2-372B instrument loop subsequent to replacement of the Master Trip Unit.
2711994009 | Vermont Yankee | 07/20/1994 | 07/20/1995 | 9507250054 | <strong>INADVERTENT PRIMARY CONTAINMENT ISOLATION SYSTEM ACTUATION DUE TO AN UNEXPECTED TRANSFER OF THE 120/240VAC VITAL BUS TO ITS ALTERNATE POWER SOURCE DURING A LIGHTNING STORM</strong><br /><i>Abstract:&nbsp;</i>On 07/20/94, at 1832 hours, with the Reactor at approximately 100% power, a lightning strike resulted in a transfer of the 120/240V Vital AC Bus from the 'normal' motor-generator power source to the 'alternate' source. This momentary interruption of Vital Bus power resulted in Primary Containment Isolation System (PCIS) partial isolations, the initiation of the 'A' Standby Gas Treatment System (SBGTS), a partial Reactor Building Ventilation isolation, the shutdown of the Electronic Pressure Regulator (EPR), and lockups of the Feedwater Regulation Valves and Recirculation Pump Motor-Generator Set Scoop Tubes. Operators immediately reset the Feedwater Regulation Valve lockups to regain control of reactor water level, and the Mechanical Pressure Regulator (MPR) automatically assumed control of reactor pressure. These actions maintained the monitored parameters of the Reactor Protection System (RPS) within the required ranges, thus averting a Reactor Scram. In addition to the Vital AC transfer, several Technical Specification Limiting Conditions for Operation (LCOs) were entered due to other equipment inoperabilities. <br /><br /> The root cause of the event was a lightning strike to the plant site which resulted in an unexpected transfer of the Vital AC Bus to its alternate power source and the inoperability of various pieces of plant equipment. The installation of additional surge/lightning suppression devices on the affected equipment is currently being implemented.
2711994010 | Vermont Yankee | 08/11/1994 | 09/09/1994 | 9409150131 | <strong>NNS Components Acting as a Primary Containment Boundary</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1994, as a result of an engineering review performed by the Yankee Atomic Electric Company (YAEC), it was determined that a condition existed with two primary containment penetrations (X-52E and X- 52F) which did not meet the required safety class design. The Vermont Yankee Safety Classification Manual in section 2.2.3.2.d, specifies that the classification of systems, components and structures, which are required to provide or maintain primary containment integrity be built to Safety Class 2 standards. The identified Non-Nuclear Safety (NNS) portions of these penetrations were isolated on August 11, 1994 and a reportability determination was completed on August 25, 1994. This event was reported to the USNRC as a non-emergency notification within one hour pursuant to 10CFR50.72 (b)(1)(ii).
2711994011 | Vermont Yankee | 10/05/1994 | 11/03/1994 | 9411070303 | <strong>FAILURE TO PROPERLY IDENTIFY ALL AREAS REQUIRING EMERGENCY LIGHTING UNITS IN ACCORDANCE WITH 10 CFR 50 APPENDIX R, SECTION III.J</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1994 Vermont Yankee identified that emergency lighting units were not provided in all areas needed for operation of safe shutdown equipment and in all access and egress routes thereto. The condition was discovered during an investigation resulting from a Plant Operating Review Committee (PORC) follow item which was generated during a review of the Alternate Cooling System operating procedure. The plant was in hot shutdown at the time, and compensatory actions were instituted prior to start-up of the plant. The cause of the event was failure to properly identify all areas required to be provided with Appendix R safe shutdown lighting. The focus of the evaluation of Appendix R lighting requirements had been on only those areas required to support alternate and dedicated shutdown capability (10 CFR 50 Appendix R, Section III.L). Vermont Yankee did not evaluate the Appendix R lighting requirements for all possible fire scenarios where remote manual actions were required to support shutdown from the control room.
2711994012 | Vermont Yankee | 10/10/1994 | 11/17/1994 | 9411250095 | <strong>Exceeded Core Thermal License Limit by 0.75 MWTH due to the Isolation of the Feedwater Pressure Transmitter that Supplies a Signal to the Computer Program that Calculates Core Thermal Power</strong><br /><i>Abstract:&nbsp;</i>On 10/24/94, it was discovered that during the period 10/10/94 through 10/21/94 Core Thermal Power (CTP) as calculated by the process computer was non-conservatively low by 1.5 Megawatts Thermal (MWTH). This calculation, used to determine reactor power, allowed Vermont Yankee to unknowingly exceed its license limit by a maximum of 0.75 MWTH. A feedwater pressure transmitter, whose signal is used as an input to the computer CTP calculation, was isolated according to procedure due to a leak in its sensing line. However, the operator did not realize that the transmitter provided data to the CTP calculation. The root cause of this event is inadequate administrative controls. No source of information was available to the operators to allow them to assess the impact on the process computer calculations of CTP induced by a loss of an input signal. <br /><br /> A contributing cause was a lack of communications between the Operations and the Computer Engineering Group (CEG), on this issue, as no attempt was made to contact the CEG to determine the impact of the loss of the signal input due to isolation of the transmitter. <br /><br /> Immediate corrective action was to manually substitute a fixed value for the feedwater pressure signal. The CTP calculation then reported a correct value with a special status that the CTP was using a substituted value. Long term corrective actions will include evaluations: to improve the fault tolerance of the heat balance calculation; for additional training of the operators to improve their knowledge of the process computer and to create a document that provides information on each critical computer point.
2711994013 | Vermont Yankee | 10/13/1994 | 03/09/1995 | 9503160125 | <strong>Initiation of Technical Specification Required Shutdown Due to Unisolable Service Water Leak Resulting in Inoperability of Both Service Water Subsystems and the Alternate Cooling Subsystem.</strong><br /><i>Abstract:&nbsp;</i>On 10/13/94, at 1635, operators observed a leak from the bottom of the 'B' Reactor Building Closed Cooling Water Heat Exchanger due to flow induced vibration fatigue on a drain line. Closing the Service Water inlet valve stopped the leak, but outlet valve V70-92C could not be closed due to an obstruction in the seat area. At 2345 both Service Water Subsystems were declared inoperable due to the unisolable leak and a 7 day LCO was entered. After further analysis, the Alternate Cooling Subsystem was also declared inoperable due to the leak and a 24 hour LCO was entered at 1512 on 10/14/94. A shutdown was initiated at 1935 on 10/14. Installation of blind flanges in place of the failed V70-92C valve completely isolated the leak and the Service Water Subsystems and the Alternate Cooling Subsystem were declared operable at 0815 on 10/15. Implementation of a permanent fix for the cracked drain connection was completed on 1/31/95.
2711994014 | Vermont Yankee | 10/30/1994 | 11/29/1994 | 9412070090 | <strong>Fire Suppression System Sprinkler Head Obstructed Due to Inadequate Evaluation of Scaffold Installation.</strong><br /><i>Abstract:&nbsp;</i>On 10/30/94, with the plant operating at 100% power, the sprinkler system protecting the diesel fire pump engine was declared inoperable due to a scaffold installation that obstructed a sprinkler head spray pattern. Technical Specification 3.13.F.2 requires that a fire watch be established within one hour to inspect the diesel fire pump engine room on an hourly basis when this sprinkler system is inoperable. Contrary to this requirement, an hourly fire watch was not established within one hour from the time the scaffold was erected on 10/21/94. Therefore, this event is considered reportable.<br /><br /> The root cause of this event was determined to be human error in the failure to adequately evaluate the scaffold installation in accordance with the procedure governing review and evaluation of temporary structures and materials in the plant. <br /><br /> Immediate corrective actions included establishing an hourly fire watch in accordance with Technical Specification 3.13.F.2. The scaffolding was removed Less than three hours later and the sprinkler system was declared operable. <br /><br /> No similar events involving the obstruction of sprinkler heads by scaffolding have been reported to the Commission with the last five years. <br /><br /> Appendix A, AP 0010 Rev. 25, page 1 of 3
2711994015 | Vermont Yankee | 12/05/1994 | 01/04/1995 | 9501100265 | <strong>HPCI System Declared Inoperable As A Result Of The Identification Of A Blown Fuse In The Turbine Trip Circuit During Quarterly Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 12/05/94 at 0850 hours, with the Reactor operating at 100% steady state power, the High Pressure Coolant Injection System (HPCI) Stop and Governor Valves failed to close when the turbine remote trip pushbutton was depressed during quarterly valve surveillance testing. Control Room personnel declared the HPCI system inoperable and contacted Instrument and Control (I&C) technicians to initiate troubleshooting. In accordance with Technical Specification requirements, the Emergency Core Cooling Systems that provide a backup to HPCI were verified operable, and a 7-Day Limiting Condition for Operation (LCO) was entered.<br /><br /> I&C troubleshooting found an open circuit Buss FNA indicating fuse in the 125VDC control circuit which actuates the HPCI turbine trip solenoid and closes the subject valves. However, further testing did not identify any problems with the equipment downstream of the fuse. On 12/05/94 at 1418, after fuse replacement and circuit functional testing, the HPCI system was declared operable. On 12/06/94 and 12/07/94, the proper operation of this circuit was again verified when the HPCI quarterly valve stroking and full flow surveillances were performed respectively.<br /><br /> Based on the manufacturer's failure analysis of the subject fuse on 12/21/94, the cause of the event is attributed to an intermittent overload/short circuit condition in the HPCI turbine trip solenoid circuit. Corrective actions for this event include, the replacement of the subject solenoid and additional troubleshooting of the circuit during the Spring 1995 Refueling Outage. In the interim, a visual inspection of the installed trip circuit fuses will be performed to verify the fuses have not blown after the completion of each HPCI system surveillance.
2711994016 | Vermont Yankee | 11/30/1994 | 08/04/1995 | 9508080006 | <strong>Unisolable Service Water Piping Leaks Resulting In Inoperability Of The SW Subsystems And The Alternate Cooling Subsystem</strong><br /><i>Abstract:&nbsp;</i>On 11/30/94 at 2055, operators observed minor leakage from the Service Water (SW) discharge piping connected to the 'A' Reactor Building Closed Cooling Water heat exchanger. As this piping is not isolable from the main SW return header, both SW Subsystems were declared inoperable at 2055 on 11/30/94. The Alternate Cooling Subsystem had previously been declared inoperable due to maintenance activities. As a result of both the SW and Alternate Cooling Systems being inoperable, a 24 hour LCO was entered. While performing inspections of the leak area, another leak was identified in a different weld in the area. After incorporating inspection data into appropriate analyses, it was determined that the piping structural integrity was not impacted. Per Generic Letter 90-05, the SW Subsystems were declared operable at 1200 on 12/1/94. The Alternate Cooling Subsystem was declared operable at 1620 on 12/2/94 after completion of additional evaluations. ASME Code replacement of the piping was completed during the 1995 Outage. The root cause of one of the leaks was Microbiological Induced Corrosion (MIC) which initiated at a crevice due to fit-up problems. The root cause of the other leak was lack of fusion of the root of the weld which led to severe MIC attack.
2711994017 | Vermont Yankee | 12/27/1994 | 01/26/1995 | 9501310330 | <strong>Control Room Heating, Ventilating And Air Conditioning (HVAC) System Configuration Outside Of Design Basis Due To A Failure Of The Inlet Damper To Close Due To Wear And Corrosion.</strong><br /><i>Abstract:&nbsp;</i>On 12/10/94 and 1/17/95, the inlet isolation damper for the Control Room Heating, Ventilating and Air Conditioning (HVAC) system failed to fully close when the Control Room HVAC Recirculation Mode Select Switch was placed in the Emergency position. On the first event operators were performing a quarterly Control Room Isolation Surveillance Test intended to ensure that dampers would isolate when required to ensure control room habitability. The second event occurred while performing maintenance inspections. in-leakage of outside air into the control room, potentially exceeding the 20 scfm design basis in-leakage required to ensure control room habitability. Therefore, the failure of the damper to close resulted in a system condition assumed to be outside of the design basis. <br /><br /> The root causes of these events was wear and corrosion in the damper operating mechanism for the control room HVAC system which caused misalignment of the mechanism, resulting in random binding. Contributing causes relating to programmatic failures allowed the degraded condition to go undetected. <br /><br /> A maintenance Work Order Request was initiated to repair the damper operator. The repair was completed on 12/12/94 and the surveillance was repeated successfully. A follow-up work order was generated to check the other dampers and recheck the repaired damper. This check identified continuing problems and the damper was replaced on 1/19/95.
2711994018 | Vermont Yankee | 12/16/1994 | 06/07/1995 | 9506140431 | <strong>Two Vital Fire Barriers Inoperable Due To Degraded Fire Penetration Seals; Supplement 1</strong><br /><i>Abstract:&nbsp;</i>On 12/16/94 and 12/20/94, with the plant at 100% power, personnel performing the operating cycle surveillance of vital fire barriers identified two penetration seals, required by Technical Specification (TS) section 4.13.E.1, that did not satisfy the applicable acceptance criteria for operable seals. The associated fire barriers were subsequently declared inoperable and appropriate fire watches established. The barriers and seals are required to be operable at all times per plant Technical Specification 3.13.E.1. <br /><br /> The apparent cause for both events is human error in the failure to (1) recognize that an unrelated maintenance or modification activity damaged one seal, and (2) adequately repair one seal during the previous operating cycle surveillance. Immediate corrective actions included establishing a continuous fire watch within one hour on one side of each barrier and promptly repairing both seals with approved materials and procedures. Vermont Yankee performs a 100% inspection each operating cycle so that all penetrations and barriers are inspected for similar conditions. Similar events regarding inoperable fire barriers and seals were reported within the last five years as LER 93-001, 95-004 and 95-010.
2721994001 | Salem 1, Salem 2 | 01/05/1994 | 02/03/1994 | 9402180173 | <strong>TS 3.0.3 Entries; More Than One Inoperable ARPI Per Bank.</strong><br /><i>Abstract:&nbsp;</i>Intentional Technical Specification (TS) 3.0.3 entries were made: for Unit 2 on 1/5/94, from 1637 to 1642 hours, and on 1/16/94, from 0037 to 0045 hours, and for Unit 1 on 1/24/94, from 2215 to 2245 hours. This was done to permit calibrating the respective Analog Rod Position Indicator (ARPI) Control Board dual indicator modules for Unit 2 control rods 2B4 and 1D2 and for Unit 1 control rods 2A1 and 2B2. Calibrating the indicators required removing the dual indicator modules, which rendered ARPI for subject rods and for the rods sharing the same module inoperable: 2B3 and 1D1 (Unit 2) and 2A2 and 2B1 (Unit 1). In each case, actual rod positions (per group demand) were correct. The root cause of these events is design of ARPI position indicators requiring entering TS 3.0.3 whenever ARPI calibrations are performed. The subject position indicators were calibrated and TS 3.0.3 was exited. A Night Order Book (NOB) entry was made, on 1/27/94, to provide guidance/restrictions for ARPI Dixon indicator calibrations and TS 3.0.3 entries. An Information Directive will be issued to formalize the 1/27/94 NOB entry.
2721994002 | Salem 1 | 01/21/1994 | 02/16/1994 | 9402230294 | <strong>Manual RPS Actuation Due To Less Than Required Operable Control Rod Demand Pos. Indicators.</strong><br /><i>Abstract:&nbsp;</i>On 1/21/94, at 1017 hours, the Reactor was manually tripped, (reactor trip system breakers opened) in accordance with Technical Specifications. During rod drop testing, the step counter readings of the Control Rod Shutdown Bank B group demand position indicators for Groups 1 and 2 did not agree: Group 1 demand indicated 188 steps for rod SB1 while Group 2 indicated 174 steps for rod SB2. Testing was stopped, position was verified at 188 steps, and the Group 2 indicator was declared inoperable. The cause of this event is improper assembly, by the supplier, of the indicator step counter liquid crystal display (LCD) module to the counter back plane. The counter was replaced with a spare, which was satisfactorily tested and placed into service. The indicator supplier, science Application International Corporation (SAIC), has been requested to provide the results of full inline inspection and failure analyses of the failed counter. The Unit 2 design change package for installing these counters will be revised to provide for visual verification/testing to confirm that the indicator LCD module is properly installed. The PSE&G vendor manual will be revised to ensure proper operation of SAIC GRID counters prior to installation or replacement. This event will be reviewed by operations personnel and by the Training Department for incorporation into the Operations lesson plan.
2721994003 | Salem 1 | 01/27/1994 | 02/25/1994 | 9403080275 | <strong>Reactor Trip During Startup, On 14 Steam Generator Low- Low Level.</strong><br /><i>Abstract:&nbsp;</i>On 1/2 94, at 2034 hours, during startup following the eleventh refueling outage, a Reactor trip on No. 14 Steam Generator (S/G) low-low level occurred from 9% power. When placed in automatic, the 14BF19/40 level demand signal periodically failed to zero. To compensate, the Nuclear Control Operator (NCO) controlled S/G level by returning the controller to manual and allowing demand signal to return to the program value. During one attempt, the NCO anticipating automatic control circuit recovery of S/G level, delayed transferring control to manual. The automatic control circuit did not recover level and when the NCO transferred to manual, S/G feedwater flow increased causing a level shrink to the 16% low-low setpoint. Emergency Operating Procedure- TRIP-1, 'Reactor Trip Or Safety Injection' was entered and the Unit stabilized and placed in Mode 3. The primary root cause of this event is equipment failure of three circuit cards in 14BF19/40 controller. A contributing factor was buildup of sediment in the sensing line to the 14 S/G feedwater flow transmitter. The failed controller circuit cards were replaced and the controller returned to service. Satisfactory channel calibrations were performed on the S/G level control circuits. The sensing lines to the S/G feedwater flow transmitters were blown down and vented to remove sediment and air. A root cause evaluation of the failed components will be performed.
2721994004 | Salem 1 | 01/31/1994 | 03/02/1994 | 9403090246 | <strong>T/S 3.0.3 Entry: Planned Inop. Of ARPI System To Support Maintenance Troubleshooting.</strong><br /><i>Abstract:&nbsp;</i>An intentional Technical Specification (TS) 3.0.3 entry was made on 1/31/94 (from 0422 to 0443 hours) due to deenergizing the Analog Rod Position Indication (ARPI) System for all control rods. The 115-volt alternating current (AC) power supply fuses to the ARPI System primary and auxiliary 13-volt direct current power supplies were conservatively removed to support correction of ARPI indication drift affecting rod 2SA4. Rod positions were verified prior to fuse removal and after reinstallation. The root cause of this event is ARPI System design that necessitated the TS 3.0.3 entry to avoid possible equipment damage during correction of the 2SA4 indication drift. The 2SA4 signal conditioning module was adjusted, a channel check demonstrated ARPI operability, and TS 3.0.3 was exited. PSE&G will continue participation in the industry Rod Control User's Group and will utilize User's Group and vendor recommendations regarding ARPI System drift.
2721994005 | Salem 1 | 02/10/1994 | 03/11/1994 | 9403180072 | <strong>Turbine Trip Due To Loss of Direct Current Control Power To Electro-Hydraulic Control Syst.</strong><br /><i>Abstract:&nbsp;</i>On 2/10/94, hours, at 1258 hours, a control power failure of the turbine Electro-Hydraulic Control (EHC) System occurred causing a turbine/reactor trip. The Unit was stabilized in Mode 3, at approximately 1315 hours (same day). Insufficient margin between the EHC overvoltage protection setpoints and normal EHC power supply voltage allowed a variation in voltage to actuate the overvoltage protection circuitry. The margin resulted from design/installation of the EHC power supplies and use of a 17.3VDC setpoint. A contributor was EHC procedures that did not record power supply voltages in a manner that would reveal a reduced margin to trip. No component failures were identified as contributors to this event. EHC power supplies were monitored and no problems or transients/pulses were recorded. The overvoltage protection circuits were replaced and the circuits, setpoints were reset to 17.9 +/-.1 VDC, and the EHC +15 VDC bus wiring was reworked. Procedure changes have been implemented to ensure adequate margin below the overvoltage protection setpoint. The A +15VDC power supply was replaced and additional testing will be conducted to evaluate transient effects. During the next Unit 2 outage, voltage readings of the Unit 2 EHC 15VDC power supply will be taken to verify adequacy of the overvoltage protection margin to trip setpoint.
2721994006 | Salem 1 | 02/21/1994 | 03/16/1994 | 9404010021 | <strong>TS 3.0.3 Entry: Planned Inoperability Of ARPI Systems To Support Maint. Troubleshooting.</strong><br /><i>Abstract:&nbsp;</i>Intentional Technical Specification (TS) 3.0.3 entries were made on 2/21/94 (from 1819 to 1827 hours) and 2/22/94 (from 1042 to 1052 hours) due to deenergizing the Analog Rod Position Indication (ARPI) System for all control rods. The 115-volt alternating current (AC) power supply fuses to the ARPI System primary and auxiliary 13-volt direct current power supplies were conservatively removed to support correction of ARPI indication drift affecting rods 2C4 and 2SA2. In each case, rod positions were verified prior to fuse removal and after reinstallation. The root cause of these events is ARPI System design that necessitated the TS 3.0.3 entries to avoid possible equipment damage during correction of the 2C4 and 2SA2 indication drift. The 2C4 and 2SA2 signal conditioning modules were adjusted, channel checks demonstrated ARPI operability, and TS 3.0.3 was exited. These modules will be replaced, as required, should recurring indication drift be identified. PSE&G will continue participation in the industry Rod Control User's Group and will utilize User's Group and vendor recommendations regarding ARPI System drift.
2721994007 | Salem 1 | 04/07/1994 | 05/10/1994 | 9405160182 | <strong>Reactor Trip From 25% Power/Two Safety Injections, Manually Initiated Main Steam Isolation, And Discretionary Declaration Of ALERT</strong><br /><i>Abstract:&nbsp;</i>At 1050 hours on 4/7/94, an automatic Reactor trip occurred, was immediately followed by an Emergency Core Cooling System (ECCS) Safety Injection (SI) and, at 1100 hours an Unusual Event was declared. At 1105 hours, the SI signal was reset and ECCS flow reduction began. Reactor Coolant System temperature increased, Pressurizer level increased to >100%, steam generator pressure increased and main steam safety valves lifted, and at 1128 hours, a second automatic SI occurred. At 1316 hours, a precautionary ALERT was declared. HOT SHUTDOWN was achieved at 0106 hours on 4/8/94, and at 1124 hours (same day), COLD SHUTDOWN was achieved. The trip resulted from assigning inappropriate priority of actions and improperly monitoring reactor power while withdrawing rods. The first SI resulted from inadequate control of primary loop temperature, concurrent with a false high steam flow signal. The second SI resulted from low Pressurizer pressure due to lifting a steam generator safety valve. Involved personnel will complete remedial training and evaluation. Operating procedures have been revised, as appropriate. Component testing, repairs, and modifications have been made, as required.
2721994008 | Salem 1, Salem 2 | 08/28/1990 | 06/22/1994 | 9406280309 | <strong>Quarterly Channel Functional Testing Of Position Indication For Power Operated Relief Valves Missed On Both Units.</strong><br /><i>Abstract:&nbsp;</i>From 8/90 through 4/94, quarterly channel functional testing of position indication for both Units' power operated relief valves (PORVs), 1(2)PR1 and 1(2)PR2, was performed late on four occasions on Unit 1 and six on Unit 2. The testing is specified by Technical Specification (TS) Table 4.3-11, Item 12. This event is attributed to personnel error, which resulted from inattention to detail: during review/implementation of Generic Letter (GL) 90-06 it was not recognized that revising TS Table 4.3-11 was necessary, and a surveillance procedure revision eliminated the mechanism by which TS Table 4.3-11, Item 12 was met. The procedure has been revised to ensure TS compliance and the requirement has been reaffirmed with licensed Operations personnel. A license change request (LCR) is being submitted to revise TS Table 4.3-11, Item 12 to meet the intent of the GL. A verification audit of TS Table 4.3-11 will be performed to ensure all requirements are being procedurally met. The importance of adequate procedure reviews to ensure compliance with TS will be stressed with appropriate personnel. This report will be reviewed by appropriate personnel to ensure their awareness of the importance of attention to detail when reviewing procedure requirements involving LCRs.
2721994009 | Salem 1 | 06/10/1994 | 06/29/1994 | 9407070005 | <strong>Turbine/Reactor Trip Due To Main Generator Ground Fault Protection Actuation With Reactor Power More Than/= 50%</strong><br /><i>Abstract:&nbsp;</i>On 6/10/94, at 1434 hours, a turbine/reactor trip turbine trip signal while above the P-9 reactor power interlock setpoint of >/= 50% reactor power. The turbine trip was initiated by a main generator ground fault protection relay, CV-8, actuation. Emergency operating procedures were entered and Main Steam was isolated to limit cooldown of the Reactor Coolant System (RCS). The Unit was stabilized in Mode 3. This event occurred due to an internal ground fault on the primary high voltage winding of the phase 1 potential transformer feeding the main generator voltage regulator and relay circuits, which caused CV-8 to actuate. The PT and a blown PT primary fuse were replaced. Electrical tests were performed, which verified integrity of all main generator PTs and PT fuses. The PT insulators and cubicles were cleaned, as a preventive measure. Additional investigation will be conducted to determine the failure mechanism of the phase 1 PT failure and appropriate action will be taken. Engineering is continuing to investigate RCS cooldown following trips and potential corrective actions are being assessed.
2721994010 | Salem 1 | 06/25/1994 | 07/13/1994 | 9407210131 | <strong>Technical Specification 3.0.3. Entry; More Than One Inoperable Analog Rod Position Indicator Per Bank</strong><br /><i>Abstract:&nbsp;</i>On 6/25/94, at 0238 hours, Technical Specification (TS) 3.0.3 was entered when the Analog Rod Position Indication (ARPI) for rods 2SA1, and 2SA4 indicated > a +/- 12 step deviation from their group demand counters. At 0335 hours, reactor shutdown was initiated in accordance with TS 3.0.3. This event resulted from output drift of the ARPI coil stacks. The most probable causes of the drift are changes in mutual inductance between the rods and/or temperature changes at the ARPI coil stacks resulting from significant changes in reactor power. Ambient temperatures had changed as the result of reduction in power to Mode 2. Secondary AC voltage values to the 2SA4 signal conditioning module were redeveloped, the module was adjusted, and at 0341 hours, the shutdown was terminated and TS 3.0.3 was exited. At 0341 hours, TS 3.1.3.2.1 Action 'a' was entered for 2SA1. The signal conditioning module of 2SA1 was adjusted in a similar manner and at 0539 hours, TS 3.1.3.2.1 Action 'a' was exited. PSE&G will continue participation in industry Rod Control User's Group efforts to resolve ARPI System drift problems.
2721994011 | Salem 1 | 07/14/1994 | 08/11/1994 | 9408180036 | <strong>Manual Reactor Trip From 100% Power Following Automatic Tripping Of All Circulating Water Pumps Due To Lightning Strike.</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1994, at 2132 hours, during full power operation, a Unit 1 manual reactor trip was initiated due to loss of all CW pumps caused by the undervoltage (UV) tripping of the Circulating Water (CW) System 4KV bus infeed/load breakers. The UV condition resulted from a lightning- induced voltage drop of the 500KV Hope Creek - New Freedom line that transferred to Salem's switchyard via the Salem - Hope Creek tie line. Emergency Operating Procedures were entered and at 2139 hours Main Steam was isolated to limit cooldown of the Reactor Coolant System. The root cause of the event is attributed to Design, Manufacturing, Construction/ Installation. The Unit 1 circulating water bus UV protection, installed as part of a switchyard upgrade design change in 1993, included new switchgear containing instantaneous relays. A time delay, which would have precluded UV relay actuation, was not used. Time delay relays with a 700 millisecond setting have now been installed. The protective relaying technical standard will be revised to provide overall guidance on the selection of UV protective relaying schemes. In addition, specific reference to the CW 4KV bus system will be provided. The Unit 2 switchyard upgrade DCP (which includes CW bus UV protection) will be reviewed and a suitable UV time delay scheme will be incorporated.
2721994012 | Salem 1 | 07/18/1994 | 08/03/1994 | 9408110258 | <strong>Intentional Technical Specification (TS) 3.0.3 Entries To Support Correction Of Analog Rod Position Indication (ARPI) System Drift Affecting Rod 2C4.</strong><br /><i>Abstract:&nbsp;</i>Two intentional Technical Specification (TS) 3.0.3 entries occurred on 7/18/94 due to deenergizing the Analog Rod Position Indication (ARPI) System for all control rods to support correction of ARPI indicator drift for rod 2C4. Rod positions, as compared to the rod group demand indicator, were correct prior to and following the TS 3.0.3 entries. Design of the ARPI System necessitated the TS 3.0.3 entries to avoid possible equipment damage during the 2C4 repair. Internal adjustments were made to the 2C4 signal conditioning module and the module span, a channel check demonstrated ARPI operability, and TS 3.0.3 was exited. PSE&G will continue participation in the industry Rod Control User's Group and will utilize User's Group and vendor recommendations regarding ARPI System drift. A license change request will be submitted to more closely align with the recommendations of NUREG-1341, Vol. 1, by providing a time frame within the TS Action Statement to restore operability when more than one ARPI indicator per bank is inoperable.
2721994013 | Salem 1 | 07/25/1994 | 08/24/1994 | 9408310127 | <strong>Containment Pressure Relief Performed Without Capability for Automatic Isolation</strong><br /><i>Abstract:&nbsp;</i>At 0300 hours on 7/25/94, a containment pressure relief was performed without the automatic isolation capability, provided by Radiation Monitoring System Noble Gas, Activity Monitor, 1R12A or redundant monitor 1R41C. Prior to the event, an electrical jumper was installed to block erroneous output spiking from 1R12A. At the time,, troubleshooting had not determined the cause of overhead alarm (OHA) C24, 'CBV (containment building ventilation) Isolation with Signal Present'. This event resulted from a design change package (DCP) that removed internal jumper J2A thereby eliminating the source of temporary power to a field test jack at terminal TB E-1 to block the 1R12A output signal. A contributor to this was incomplete review of procedures affected by the DCP. 1R12A was blocked and 1R41C was returned to operable. 1R12A was repaired and returned to service on 7/26/94. A walkdown did not identify other similar problems with the subject DCP. Appropriate training will be conducted to emphasize expectations regarding the DCP review process, as related to this event. The OHA response procedure for C24 will be appropriately revised.
2721994014 | Salem 1 | 08/25/1994 | 09/14/1994 | 9409270334 | <strong>Planned Technical Specification 3.0.3 Entries to Support Correcting Analog Rod Position Indication System Drift Affecting Rods 2D1, 2D3, and 2SA4.</strong><br /><i>Abstract:&nbsp;</i>On 8/25/94, five planned Technical Specification (TS) 3.0.3 entries were made: from 1307 to 1308 hours, from 1316 to 1317 hours, from 1628 to 1631 hours, from 1646 to 1648 hours, and from 2056 to 2107 hours. These events occurred when the Analog Rod Position Indication (ARPI) System for all control rods was conservatively deenergized to support correcting ARPI indication drift affecting rods 2D1 (twice), 2D3 (twice), and 2SA4 (once). Rod positions, as compared to the rod group demand indicator, were correct prior to and following each TS 3.0.3 entry. These events are attributed to design of the ARPI System, which necessitated the TS 3.0.3 entries to avoid possible equipment damage during correction of the indication drift affecting the subject rods. Internal adjustments were made to the rods' signal conditioning modules and the modules' span, a channel check demonstrated ARPI operability, and TS 3.0.3 was exited. PSE&G will continue participation in the industry Rod Control User's Group and utilize User's Group and vendor recommendations regarding ARPI System drift. On 8/19/94, a license change request was submitted to more closely align with the recommendations of NUREG-1341, Vol. 1, by providing a one hour time frame within the TS Action Statement to restore Operability when more than one ARPI indicator per bank is inoperable.
2721994015 | Salem 1 | 10/18/1994 | 07/24/1996 | 9608010265 | <strong>Refueling Water Storage Tank Volume Less Than Required</strong><br /><i>Abstract:&nbsp;</i>Following calibration of the Refueling Water Storage Tank (RWST) level transmitters, 1LT921 and 1LT920, on September 29, 1994 and October 1, 1994, a review determined that since January 20, 1994, the RWST minimum required water volume of 364,500 gallons was potentially not met at various times, due to an indication error equivalent to 8,900 gallons. 1LT921 and 1LT920 were found with indication errors of +13 inches (+2.4%) and +11 inches (+1.9%) at the high end. A low end level indication error of +6 inches (+1%) was common to both transmitters. Vendor testing and investigation by the Public Service Electric & Gas Maintenance Department have not been able to identify the cause of this event.<br /><br /> The transmitters were properly adjusted and RWST level was returned within specification. In addition instrument calibration procedures were revised to provide additional guidance on draining and returning the transmitter to service. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
2721994016 | Salem 1 | 11/16/1994 | 11/04/1997 | 9711170069 | <strong>Non-compliance with Control Room Area Senior Reactor Operator (SRO) Technical Specification staffing requirements</strong><br /><i>Abstract:&nbsp;</i>This supplemental Licensee Event Report (LER) is being submitted as a corrective action from a follow-up investigation performed as a result of a letter issued by the NRC on April 16, 1996, expressing concerns with the completeness and accuracy of the initial investigation.<br /><br /> As a result of Hope Creek LER 354/94-13-00 on Control Room Staffing, the Nuclear Safety Assessment Group (NSAG) performed an independent review to determine if instances of inadequate Control Room staffing had occurred at Salem. That review involved interviews with Salem licensed personnel, who recalled four separate instances of not having met the requirements of Technical Specification 6.2.2.b. The review concluded that the individuals were knowledgeable of the "on-duty" Senior Reactor Operator (SRO) responsibilities, but did not recognize the need for an Incident Report or the possible reportability until after the Hope Creek LER. These incidents were attributed to personnel error as a result of inadequate communication and operators allowing themselves to become distracted by other activities. LER 272/94-016-00 was included in operator continuing training, and Licensed Operator lesson plans for Shift Turnover, Conduct of Operations, Corrective Action Program, and Technical Specifications have been revised to more clearly address the administrative section of the Technical Specifications. Also, the Corrective Action Program has been extensively revised with a reduced threshold for problem identification.
2721994017 | Salem 1, Salem 2 | 11/17/1994 | 08/25/1995 | 9509050165 | <strong>Inadequate Margin For Pressurizer Overpressure Protection During Low Temperature Conditions</strong><br /><i>Abstract:&nbsp;</i>On 11/17/94, a 10CFR50.72(b)(1)(ii) notification was made when it was determined that based on realistic assumptions for various system availability and alignments, Salem Generating Station Unit 1 was outside the design/licensing basis for Pressurizer Overpressure Protection System (POPS) should an inadvertent safety injection (SI) signal occur in Mode 5 below 200 degrees F. Under these conditions, an SI signal could result in a peak RCS pressure of 474 psig which exceeded the then current design basis pressure limit of 450 psig. This concern was not considered applicable to Unit 2 at that time. Subsequent review of an engineering evaluation has determined that both Units 1 and 2 were outside their design/licensing basis for the POPS analysis and should have been reported on December 30, 1993. This conclusion is based on the differential pressure from the operating RCPs that was not considered in the original POPS analysis for the mass addition transient. The transient analysis code and inappropriate use of ASME Code Case N-514 led to the misreporting. Code Case N-514 has since been approved by the NRC for use at Salem.
2721994018 | Salem 1 | 12/09/1994 | 01/04/1995 | 9501130115 | <strong>Design Basis Concern Due to Inoperability of 1A Safeguards Equipment Cabinet (SEC - Emergency Load Sequencer) and Subsequent TS 3.0.3 Entry Due to Inoperability of 1A and 1B SECs</strong><br /><i>Abstract:&nbsp;</i>At 0914 hours on 12/9/94, 1A Safeguards Equipment Cabinet (SEC) was declared inoperable due to a sequencing problem and Technical Specification (TS) required action was entered. While troubleshooting the 1A SEC problem, 1B SEC was inadvertently rendered inoperable, TS 3.0.3 was entered and, at 1328 hours, reactor power reduction was begun. At 1530 hours, 1B SEC was restored to operable and TS 3.0.3 was exited. At 1700 hours, 1A SEC was restored to operable, TS required action was exited, and return to full power was begun. 1B SEC inoperability is attributed to personnel error when the 1B SEC test panel was removed for installation in the 1A SEC cabinet and the panel output relay test switch pushbutton A9 was inadvertently pushed and stuck in the depressed condition. 1A SEC inoperability is attributed to sticking of pushbutton C7 during surveillance testing on 11/23/94. Pushbuttons A9 and C7 were exercised and returned to service and will be replaced during the upcoming Unit refueling outage. A root cause analysis will be performed to determine, if possible, the involved pushbutton failure mechanisms) and appropriate action will be taken on both Units. Procedure revisions will be implemented to require verification that SEC output test relay pushbuttons are not stuck following operation of the SEC output test relay pushbuttons. These procedure revisions will also include a requirement to run the Automatic Test Insertion (ATI) circuit through one complete test cycle prior to aligning the ATI in its final configuration and closing the SEC cabinet door. This report is also intended to satisfy reporting requirements applicable to a potential 10CFR21 concern.
2751994001 | Diablo Canyon 1, Diablo Canyon 2 | 01/28/1994 | 02/26/1999 | 9903080377 | <strong>Inadequate Fire Barrier Penetration Seals Resulting From a Lack of Damming Boards Due to a Programmatic Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1994, at 1730 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 1 00 percent power, PG&E determined that certain fire barrier penetration seals did not meet the required fire rating because damming boards were not installed on the ends of the seals. Fire watches were verified to be in place as compensatory measures. A one-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> Subsequent inspections have identified additional deficiencies in penetration seals and gaps in fire rated walls.<br /><br /> The design process did not adequately incorporate fire protection requirements (design input) to assure proper design, construction, inspection, and maintenance of fire barrier seals and gaps.<br /><br /> Corrective actions include: performing walkdowns; qualifying penetration seals and gaps; reviewing design documents and procedures that control penetration seals and gaps to ensure the requirement for installing and/or restoring seals and gaps is clear; and clarifying organizational responsibilities.
2751994002 | Diablo Canyon 1 | 03/15/1994 | 03/31/1994 | 9404130022 | <strong>Loss Of Temporary Control Room Annunciator Due To Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On March 15, 1994, at 1311 PST, with Unit 1 stable in Mode 6 (Refueling), a loss of the temporary control room annunciator system capability was identified by control room operators. Plant operators immediately implemented preplanned compensatory measures to manually monitor plant systems and equipment by stationing additional operators. The temporary control room annunciator was returned to service within approximately 31 minutes. On March 26, 1994, at 1416 PST, with Unit 1 in Mode 6, defueled, a loss of the temporary control room annunciator occurred due to a maintenance console input error. The system was restored within three minutes. <br /><br /> The root cause of these events was personnel error. <br /><br /> Corrective actions for these events include verification of all connectors, extension of the controlled work area, assignment of additional supervisory personnel, issuance of an operations standing order regarding compensatory actions and incorporation of the 'lessons learned' into next scheduled quarterly I&C training session.
2751994003 | Diablo Canyon 1, Diablo Canyon 2 | 02/08/1994 | 11/07/1994 | 9411150078 | <strong>Technical Specification 3.7.1.1 Not Met During Main Steam Safety Valve Surveillance Testing Due To Setup Drift</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1994, for Unit 1, and on March 5, 1994, for Unit 2, with each unit in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.7.1.1 was not met when 13 Unit 1 main steam safety valves (MSSVs) and 15 Unit 2 MSSVs did not meet TS tolerances. Following additional testing and/or adjustment, all of these valves lifted within the TS tolerances. <br /><br /> The root cause of these events was setpoint drift of the MSSVs. <br /><br /> A new test (lift-assist) device has been purchased and correlation tested to live steam. A License Amendment Request will be initiated requesting relaxation of the TS for MSSV setpoint tolerance.
2751994004 | Diablo Canyon 1, Diablo Canyon 2 | 03/12/1994 | 04/12/1994 | 9404180355 | <strong>Main Steam Safety Valves Outside TS Resulted In Auxiliary Feedwater System Outside Design Basis Due To A Vendor- Identified Deficiency In Setpoint Testing Methodology</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1994, at 1800 PDT, with Unit 1 in Mode 5 (Cold Shutdown) and Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that all 20 of the main steam safety valves (MSSVs) for each unit had setpoints outside the values required by Technical Specification (TS) 3.7.1.1, Table 3.7-1, which resulted in the auxiliary feedwater (AFW) system not meeting its design basis. As a compensatory measure, a conditional surveillance was implemented to verify the temperature of the condensate storage tank (CST) to be less than or equal to 100 degrees Fahrenheit every 12 hours or whenever a rejection from the condenser hot well is in progress. At 1900 PST, the NRC verbally exercised its discretion not to enforce compliance with TS 3.7.1.1 Action Statement a. for Unit 2. <br /><br /> A one-hour, non-emergency report was made for Unit 2 in accordance with 10 CFR 50.72(b)(1)(ii)(B) on March 12, 1994, at 1931 PST. TS 3.0.3 for Unit 2 was entered. Unit 1 should have been included in this one-hour, non-emergency report since this condition also applied to Unit 1. <br /><br /> The root cause has been determined to be a vendor-identified deficiency in the MSSV testing methodology. <br /><br /> The Unit 2 MSSV setpoints were reset to the required tolerance using the revised mean seat area (MSA) value supplied by the Trevitest vendor. On March 14, 1994, at 1609 PST, the MSSVs were declared operable. The MSSVs for Unit 1 will be reset prior to returning to power operation.
2751994005 | Diablo Canyon 1 | 03/14/1994 | 03/31/1994 | 9404130031 | <strong>Failure To Control Reactor Vessel Inventory During Draindown Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On March 14, 1994, at approximately 1032 PST plant operators became aware that the reactor coolant system (RCS) inventory had increased approximately 6 feet unexpectedly. The RCS inventory draindown initiated earlier in the day had been secured at an indicated 111-foot 6-inch elevation as indicated on the wide range reactor vessel refueling level instrumentation system. There were no RCS inventory increases or decreases prior to or subsequent to this plant evolution. <br /><br /> The root cause of this event was personnel error (cognitive) in that licensed plant operators misinterpreted a procedural step which allowed the RCS to be drained below 121 feet without establishing a common vapor (nitrogen) reference (vent) between the pressurizer and the reactor vessel. <br /><br /> Corrective actions include revision of Operating Procedure (OP) A-2:II, 'Reactor Vessel - Draining The RCS To The Vessel Flange - With Fuel In The Vessel,' to clarify instructions regarding RCS draindown, issuance of an operations incident summary, additional procedural review of operating procedures that involve major evolutions and a new administrative procedure will be written to provide guidance for pre-job tailboards.
2751994006 | Diablo Canyon 1, Diablo Canyon 2 | 06/24/1994 | 06/15/1995 | 9506290226 | <strong>Centrifugal Charging Pump Outside Design Basis Due to Throttling of Component Cooling Water to Subcomponents</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1994, at 1700 PDT, with both Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the throttled component cooling water (CCW) flow rate to the centrifugal charging pump (CCP) skids may not have been high enough to adequately cool the CCP skid subcomponent heat exchangers and, therefore, maintain post-accident CCP operability. As a result, a 1-hour, non-emergency notification was made to the NRC on June 24, 1994, at 1739 PDT in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> The CCP skid throttle valves were opened to the full-open position. A test was developed and performed to determine actual CCW flow rates to the CCP skid subcomponents under throttled conditions. CCP skid flow balancing was performed to determine optimum flow conditions. Following testing, the valves were returned to the full-open position pending determination of the final valve throttling position. <br /><br /> The cause of throttling of CCW flow to the CCPs was human error, inadequate understanding of design basis. Corrective actions include calculation revisions and establishment of a method to control flow to the CCP skid such that each subcomponent heat exchanger receives sufficient flow to perform its design basis function.
2751994007 | Diablo Canyon 1 | 03/29/1994 | 04/27/1994 | 9405040006 | <strong>Unplanned Diesel Generator Start (ESF Actuation) When A Potential Transformer Sensing Circuit Shorted-To-Ground Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1994, at 0054 PST, with Unit 1 defueled, Diesel Generator (DG) 1-1 automatically started and loaded onto its associated vital bus from second level undervoltage (U/V) when the 'C-phase' potential transformer sensing circuit shorted-to-ground during installation of a new circuit in a circuit breaker cubicle. This event constitutes an Engineered Safety Features (ESF) actuation. The control room operators verified that auxiliary power was available and returned all actuated equipment to normal status. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on March 29, 1994, at 0312 PST.<br /><br /> The cause of this event was personnel error (cognitive), in that craft personnel did not take the appropriate safety measure of taping the ends of the new wire that was being routed through the cubicle. This error, combined with the design of the second level (U/V) sensing scheme in that both second level U/V relays actuate on a single failure of a potential circuit, resulted in an inadvertent automatic start and loading of the associated DG. <br /><br /> A description of the event and lessons learned will be published in an Electrical Maintenance Bulletin and distributed to all personnel involved in electrical maintenance and construction activities. The work package preparation/revision process will be evaluated and changes implemented, if necessary, to ensure that proper review is conducted and the appropriate precautions included if work will be performed in or near energized equipment. LER 1-94-011 discusses corrective actions related to the potential wiring design deficiency.
2751994008 | Diablo Canyon 1, Diablo Canyon 2 | 04/06/1994 | 05/06/1994 | 9405180078 | <strong>Technical Specification 3.4.6.2. Not Met As A Result Of Inadequate Test Procedure Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1988, with Unit 1 in Mode 4 (Hot Shutdown), and on November 27, 1988, with Unit 2 in Mode 4, the Limiting Condition for Operation for Technical Specification (TS) 3.4.6.2. was not met when TS 4.4.6.2.2.a requirements for residual heat removal (RHR) valve 8702 were inadequately verified. <br /><br /> On April 6, 1994, during performance of Surveillance Test Procedure (STP) V-7C, 'Leak Test of RHR Suction Valves 8701 and 8702,' PG&E system engineers identified that the June 13, 1988, and subsequent revisions of STP V-7C were inadequate to verify the requirements of TS 4.4.6.2.2.a. The test method did not adequately verify the reactor coolant system (RCS) leakage integrity of RHR valve 8702 because no vent path for leakage past the downstream seat was provided. All testing performed on both units subsequent to the June 13, 1988, revision of STP V-7C did not meet the TS 4.4.6.2.2.a requirements. <br /><br /> The root cause of this event was personnel error (cognitive), inadequate review of a procedure change. <br /><br /> Corrective actions included revising STP V-7C, retesting RHR valve 8702 for Units 1 and 2, and review of all RCS boundary valve test procedures to assure adequate vent paths are utilized.
2751994009 | Diablo Canyon 1 | 03/28/1994 | 10/30/1995 | 9511200165 | <strong>Technical Specification 3.4.2.1 And 3.4.2.2 Not Met During Pressurizer Code Safety Valve Surveillance Testing Due to Random Setpoint Spread</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1994, with Unit 1 in Mode 6 (Refueling), Technical Specifications (TS) 3.4.2.1 and 3.4.2.2 were not met when three Unit 1 pressurizer code safety valve (PSV) setpoints were found outside 2485 psig, plus or minus 1 percent during testing conducted at the Westinghouse Service Center (WSC) test facility in Beaumont, California. <br /><br /> The Unit 1 PSVs were reset at the WSC test facility to the required tolerance using Surveillance Test Procedure M-77, 'Safety and Relief Valve Testing.' <br /><br /> The root cause of the PSV setpoints being outside the TS tolerance is random setpoint spread. PG&E has participated in industry and independent PSV setpoint investigations. These investigations confirm the adequacy of the present test methodology and that adequate margin exists to accommodate the identified random setpoint spread characteristics of the valves. <br /><br /> PG&E is investigating a design change to the PSV upper spring washer that has preliminarily been shown to reduce the magnitude of the random setpoint spread by approximately 50 percent. PG&E will not implement this design change until an acceptable testing method and facility can be found.
2751994010 | Diablo Canyon 1 | 05/10/1994 | 02/28/1997 | 9703100013 | <strong>Unit 1 shutdown in Accordance with Technical Specification 3.8.1.1 Action b Due to a Degraded Condition on the C Phase 500 kV Transformer</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1994, at 2245 PDT, Unit 1 completed a shutdown to Mode 5 (Cold Shutdown) as required by Technical Specification (TS) 3.8.1.1 Action b. The Unit 1 shutdown was due to a loss of an offsite power source when the Unit 1 main transformer bank was declared inoperable after acetylene was detected in the Unit 1 C phase 500 kV transformer oil. An Unusual Event was declared at 1145 PDT on May 10, 1994, and an immediate, emergency report was made to the NRC in accordance with the requirements of 10 CFR 50.72(a)(1)(i). At 2245 PDT, Unit 1 entered Mode 5 and the Unusual Event was terminated. <br /><br /> The root causes of this event were determined to be manufacturer design problems and substandard manufacturing workmanship. <br /><br /> The transformer was initially replaced with a spare. In October and November 1995, during the Unit 1 seventh refueling outage, all three phases of the main bank transformer were replaced with transformers designed and manufactured by another vendor.
2751994011 | Diablo Canyon 1 | 04/11/1994 | 05/10/1994 | 9405170246 | <strong>Unplanned Diesel Generator Start (ESF Actuation) When A Potential Transformer Sensing Circuit Shorted-To-Ground- Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1994, at 1332 PDT, with Unit 1 defueled, Diesel Generator (DG) 1-3 automatically started and loaded onto its associated vital bus from second level undervoltage (U/V) when the 'C-phase' potential transformer sensing circuit protective fuse opened, due to a short-to-ground, during post-modification test (PMT) activities. This event constitutes an engineered safety feature (ESF) actuation. The control room operators verified that auxiliary power was available and returned all actuated equipment to normal status. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on April 11, 1994, at 1636 PDT.<br /><br /> The most probable cause of this event is personnel error (cognitive), in that during a PMT being performed in the AFW 1-3 4160-volt circuit breaker cubicle, the ac potential circuit was inadvertently and momentarily cross-tied to a grounded dc control circuit (normally ungrounded) during or following the installation of the voltmeter across the coil of a timing relay. This event combined with the design (wiring) of the second level U/V sensing scheme, in that both second level U/V relays actuate on a single failure of a potential circuit fuse, resulting in an inadvertent automatic start and loading of the associated DG. <br /><br /> A description of the event and lessons learned will be published in an Electrical Maintenance Bulletin and distributed to all personnel involved in electrical maintenance and construction activities. The second level U/V sensing scheme will be evaluated and a design change implemented, if necessary, to preclude a single failure from causing an inadvertent DG start and loading onto the associated vital bus, and to ensure that the potential circuitry is designed to provide optimum DG reliability.
2751994012 | Diablo Canyon 1, Diablo Canyon 2 | 04/08/1994 | 07/11/1994 | 9407190331 | <strong>Containment Airlock Electrical Circuit Backup Over-Current Protection Outside Design Basis Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1994, at 1830 PDT, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 1 (Power Operation), PG&E determined that backup over-current protection devices were not provided for non-Class 1E 120 Vac circuits that feed into the containment personnel airlock or the emergency personnel airlock, presenting a condition that was outside the design basis of the plant. On April 8, 1994, at 1849 PDT, a one-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B) for Unit 2, and at 1856 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(C) for Unit 1. <br /><br /> The root cause was personnel error, cognitive, due to a preconceived idea, tunnel vision, unawareness, and wrong assumptions. <br /><br /> Corrective actions included opening the breakers for the circuits affected (Unit 2 only; Unit 1 was in a refueling outage), and installing backup over-current protective devices for the affected circuits for both units. In addition, the FSAR Update and affected Design Criteria Memoranda will be revised to identify the special applications of containment personnel airlock circuits. <br /><br /> A review of other applications where non-conventional electrical penetrations may have been used determined that no other containment penetrations lacked backup over-current protection, where required. Thus, PG&E concluded that this event constitutes an isolated case.
2751994013 | Diablo Canyon 1 | 04/17/1994 | 05/16/1994 | 9405230298 | <strong>Unplanned Diesel Generator Start (ESF Actuation) When The Startup Feeder 4160-Volt Bus F Undervoltage Relay Was Actuated Due To An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1994, at 0137 PDT, with Unit 1 in Mode 6 (Refueling), Diesel Generator (DG) 1-3 automatically started due to startup feeder 4160-volt Bus F undervoltage (U/V) relay actuation when an operator closed the relay cut-out knife switch during removal of a clearance. This event constitutes an engineered safety feature (ESF) actuation. The control room operators verified that auxiliary power was available and returned all actuated equipment to normal status. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on April 17, 1994, at 0252 PDT.<br /><br /> The cause of this event was Operating Procedure OP J-5:I, '12 kV System - Make Available and Energize,' did not account for all likely plant conditions under which the procedure might be used. There were no precautions regarding closing the relay cut-out knife switches prior to energizing the startup system power up to the vital 4160-volt buses, which resulted in an inadvertent automatic start of the associated DG.<br /><br /> A description of the event and lessons learned will be presented in an Operations Incident Summary. The OP J-5 series of operating procedures for the 12 Kv startup system will be revised to ensure they account for all likely plant conditions.
2751994014 | Diablo Canyon 1 | 04/26/1994 | 05/24/1994 | 9406010063 | <strong>Unplanned Diesel Generator Start (ESF Actuation) When Two Indicating Light Sockets Shorted Together Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1994, at 1332 PDT, with Unit 1 in Mode 5 (Cold Shutdown), Diesel Generator (DG) 1-2 automatically started from an apparent loss of the startup power source when the "C-phase" and "B-phase" potential transformer sensing circuits were inadvertently shorted together while an operator was replacing an indicating light bulb. This event constitutes an engineered safety feature (ESF) actuation. The control room operators verified that auxiliary power was available and returned all actuated equipment to normal status. A four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii) on April 26, 1994, at 1136 PDT. <br /><br /> The root cause of this event is personnel error (noncognitive), due to a lack of knowledge concerning the task at hand, in that the operator was not aware that the ac potential circuits could be inadvertently shorted together while attempting to replace an indicating light bulb. This inadvertent short between the C-phase and the adjacent B-phase socket resulted in the C-phase secondary potential fuse opening. This caused the DG 1-2 circuitry to sense startup bus undervoltage (U/V), resulting in an inadvertent automatic start of the DG. The DG did not load onto the bus since auxiliary power to the vital 4160-volt bus was not interrupted and, therefore, no 4160-volt U/V was sensed. <br /><br /> A description of the event and lessons learned will be published in an Operations Incident Summary and distributed to personnel involved in minor maintenance activities, such as replacement of an indicating bulb.
2751994015 | Diablo Canyon 1, Diablo Canyon 2 | 06/29/1994 | 02/14/1995 | 9502220111 | <strong>Failure to Implement Residual Heat Removal System Overpressure Protection Requirements Due to Insufficient Design Basis Information</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1994, with Units 1 and 2 in Mode 1 (Power Operation), PG&E determined that operation of the residual heat removal (RHR) system with flow less than 3000 gpm in Mode 4 (Hot Shutdown) and 5 (Cold Shutdown - with loops filled) may not meet ASME Code design basis overpressure protection requirements for the RHR heat exchangers during postulated pressure transients. At 1236 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(B). <br /><br /> On October 14, 1994, PG&E personnel determined that the design pressure of the RHR pumps could also be exceeded. <br /><br /> The root cause of this condition was insufficient information provided in design basis documentation, combined with inattention to detail regarding the design pressure of the RHR system heat exchangers and pumps. <br /><br /> An engineering review of the design and operation of the RHR system has been performed to ensure ASME Code overpressure protection requirements are met. A design change will be issued to increase the design pressure rating of the RHR system components to ensure that they comply with requirements for maximum anticipated pressure in the RHR system for normal and overpressure transient events. No physical modifications of the RHR system will be required. PG&E has also requested the NSSS vendor to clarify the overpressure design basis requirements.
2751994016 | Diablo Canyon 1, Diablo Canyon 2 | 08/15/1994 | 09/12/1994 | 9409210231 | <strong>Diesel Generators Started as Designed Upon De-Energization of Startup Bus Due to Offsite Wildfire</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1994, at 1704 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, all six diesel generators (DGs) auto-started, as required, when the Diablo Canyon Power Plant (DCPP) startup bus de-energized following the loss of 230kV transmission lines due to an offsite wildfire. On August 15, 1994, at 1828 PDT, a one-hour, non-emergency report was made to the NRC in accordance with 10CFR 50.72(b)(1)(v), 'loss of offsite response capability,' to report that many of the early warning sirens were inoperable due to the wildfire. This report was updated on August 16, 1994, at 1100 PDT to report that the de-enegerization of the 230kV transmission line for the DCPP startup bus had resulted in the auto-start of all six DGs. <br /><br /> The DGs performed as required by design, therefore no corrective action was determined to be necessary. The reportability guidance procedure was revised to include anticipatory DG starts due to loss of the startup bus as an engineered safety feature actuation.
2751994017 | Diablo Canyon 1, Diablo Canyon 2 | 08/25/1994 | 12/19/1994 | 9412290307 | <strong>Diesel Generator Ventilation System Air Flow Potentially Outside Design Basis Due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1994, at 1505 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the emergency diesel generator (DG) ventilation system may not have provided sufficient cooling air flow to meet licensing functional requirements. The licensing basis for the DG radiator inlet ambient air temperature is based on the ASHRAE standard of 0.1 percent probability of occurrence (historically established as 78 degrees F). A one-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> The August 25, 1994, determination was based on initial air flow tests. Further air flow measurements were obtained on September 7 and 8, 1994. Calculational results using these air flow measurements indicate that the DG ventilation system is, and has been, capable of meeting its licensing functional requirements. Therefore, in accordance with NUREG-1022, PG&E is submitting this revision to Licensee Event Report 1-94-017 as 'voluntary.' <br /><br /> Modifications will be made to the DG ventilation system to reduce the overall system air flow resistance, thus increasing cooling air flow, such that the DGs have more margin for opererating continuously with their associated east roll-up fire doors closed.
2751994018 | Diablo Canyon 1, Diablo Canyon 2 | 08/31/1994 | 09/30/1994 | 9410050018 | <strong>Battery Charger Degraded Due to Manufacturing Error and Inadequate Commercial Grade Dedication of Replacement Printed Circuit Boards</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1994, at 1420 PDT, PG&E conservatively determined that defects existed in battery charger printed circuit boards that could potentially prevent the fulfillment of the safety function to maintain battery voltage following a seismic event. On August 31, 1994, at 1745 PDT, a 4-hour non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(A). <br /><br /> The circuit board defects were deficient hand-soldered connections. The root cause of this event is manufacturing error. A contributory cause is inadequate pre-installation dedication criteria for the battery charger commercial grade circuit boards.<br /><br /> Corrective action to prevent recurrence includes implementing specific receipt inspection of soldered connections for all in-stock and future procurement of battery charger printed circuit boards.
2751994019 | Diablo Canyon 1, Diablo Canyon 2 | 09/01/1994 | 12/28/1994 | 9501050067 | <strong>Inadequate Containment Penetration Over-Current Protection Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1994, at 1730 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that inadequate movable incore detector system (MIDS) dehumidifier containment penetration over-current protection devices resulted in the plant being in a condition that alone could prevent the fulfillment of a safety function. On September 1, 1994, at 2117 PDT, a 4-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iii)(C). After further consideration, PG&E determined that this notification should have been made in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> A review of all power, control, and instrumentation circuits penetrating containment identified the following additional circuits with inadequate containment penetration over-current protection: (1) loose parts monitoring instrumentation test circuits, (2) MIDS control circuits, and (3) seismic monitoring system (for micro-earthquake monitoring) sensor circuits that exist only in Unit 1. <br /><br /> The root cause of this condition was personnel error, cognitive, by PG&E design personnel. <br /><br /> All affected circuits were de-energized by opening the appropriate breakers and switches. Design changes will be implemented to provide adequate over-current protection.
2751994020 | Diablo Canyon 1, Diablo Canyon 2 | 12/14/1994 | 01/13/1995 | 9501190176 | <strong>Reactor Trip Due to Reactor Coolant Pump Bus Undervoltage that Resulted from an Electrical System Disturbance External to the PG&E System</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1994, at 0026 PST, with Unit 1 and Unit 2 in Mode 1 (Power Operation) at 100 percent power, both units experienced reactor trips. Both units were stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A four-hour, non-emergency report was made at 0131 PST in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The reactor trips were due to an undervoltage on the auxiliary power bus that provides power to the reactor coolant pumps. The undervoltage condition was due to a system disturbance external to the PG&E system. <br /><br /> Due to the circumstances of the event, no corrective actions were deemed necessary. However, the Western System Coordinating Council, a utility coordination group composed of the eleven western states and British Columbia that are interconnected through the 500 kV Pacific Intertie, will study the transient and a formal report should be available in several months. If PG&E determines that any corrective actions are necessary as a result of this final report, a supplement to this LER will be issued.
2751994021 | Diablo Canyon 1 | 04/03/1994 | 12/02/1994 | 9412160169 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1994, during the Unit 1 sixth refueling outage (1R6), eddy current inspections were completed on all four Unit 1 steam generators. Thirty-five tubes in steam generator (SG) 1-2 were identified as defective and were plugged. The number of tubes plugged in each steam generator was reported to the NRC in a 15-day Special Report (PG&E Letter DCL-94-078) dated April 14, 1994, pursuant to TS 4.4.4.5a.<br /><br /> Following discussions with the NRC and review of related industry reportable events, PG&E determined that the 1R6 SG 1-2 tube plugging results should have been reported to the NRC under 10 CFR 50.72 prior to resumption of plant operation On November 3, 1994, at 1607 PST, PG&E made a 4-hour non-emergency report to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(C) to report that more than 1 percent of the tubes inspected in SG 1-2 during 1R6 were defective. <br /><br /> The cause of the majority of the tube defects is attributed to primary water stress corrosion cracking (PWSCC). PG&E has a comprehensive program to minimize steam generator tube degradation. No other corrective actions are deemed necessary. <br /><br /> The root cause of the late 10 CFR 50.72 report is personnel error. A contributory cause is inadequate procedural details. Responsible personnel are now fully aware of steam generator reporting requirements. Procedures which govern steam generator tube inspections will be enhanced to specify reportability requirements.
2751994022 | Diablo Canyon 1 | 10/27/1994 | 12/02/1994 | 9412160175 | <strong>Technical Specification 3.8.4.2 Not Met When a Containment Penetration With Inadequate Overcurrent Protection was Re-Energized Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1994, at 1645 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the Limiting Condition for Operation for Technical Specification (TS) 3.8.4.2 was exceeded, when the movable incore detection system (MIDS) dehumidifier circuits were re-energized prior to completion of design changes (DCNs) to provide adequate containment penetration overcurrent protection. <br /><br /> LER 1-94-019 identified inadequate containment penetration overcurrent protection on several circuits. In accordance with the action requirement of TS 3.8.4.2, these circuits were de-energized and administrative controls were established to keep them de-energized until adequate overcurrent protection was provided. On November 3, 1994, during a review of a surveillance test procedure, an engineer questioned the energized condition of the MIDS dehumidifier. In accordance with the requirements of TS 3.8.4.2, the MIDS dehumidifier circuit was immediately de-energized.<br /><br /> The root cause was determined to be personnel error (cognitive), inadequate communication. <br /><br /> Operations Procedure OP1.DC17, 'Control of Equipment Required by TS,' will be revised to require that the DCN sponsor be consulted prior to declaring equipment operable when equipment problems have been resolved by a design modification. In addition, an Operations Incident Summary will be issued for this event, stressing the need to perform an adequate assessment of work performed prior to declaring equipment operable.
2751994023 | Diablo Canyon 1 | 05/04/1994 | 03/28/1996 | 9604020265 | <strong>Technical Specification 3.04 Not Met Due to Equipment Degradation</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1994, Technical Specification (TS) 3.0.4 was not met when Unit 1 entered Mode 3 (Hot Standby) with centrifugal charging pump (CCP) 1-1 inoperable. TS 3.5.2 was not met because the calculated CCP 1-1 flow was greater than the TS 4.5.2h.1)d) limit.<br /><br /> A calculation completed on February 27, 1996, using data from flow tests performed during Unit 1's sixth and seventh refueling outages (1R6 and 1R7) showed that CCP 1-1 exceeded the maximum flow limits of TS 4.5.2h. 1)d) from the last performance of the flow test during 1R6 until flow balancing was performed during 1R7. Calculation results showed that the TS limits are currently being met for both units. <br /><br /> The excessive CCP 1-1 flow was caused by the erosion of the CCP miniflow recirculation orifices and leakage through flow control bypass valves 8387 B and C. The erosion was caused by extended use of the CCPs for normal charging. <br /><br /> The positive displacement pumps are now used as the primary supply for normal charging. The Unit 1 CCP miniflow recirculation orifices are scheduled to be replaced and flow measurement equipment installed during the upcoming Unit 1 and Unit 2 eighth refueling outages. Tests are being performed to accurately measure the current recirculation flow. This is being done to confirm the calculation results to verify operability of the CCPs on both units.
2771994001 | Peach Bottom 2, Peach Bottom 3 | 01/19/1994 | 02/18/1994 | 9402280220 | <strong>Technical Specification Violation due to a missed firewatch</strong><br /><i>Abstract:&nbsp;</i>On 01/19/94, a fire supervisory alarm annunciated in the Control Room. The Shift Engineer identified that the alarm was from the alarm loop serving the four Diesel Generator Bays and the Cardox Room. The Shift Supervisor (SSV) determined that an hourly firewatch would be appropriate for the four Diesel Generator Bays and the one Cardox Room. Security was contacted to establish a firewatch in these areas. At approximately 0900 hours, Fire Protection personnel identified that a breaker must have opened or had been opened which made the Cardox Room fire detection inoperable. Technical Specification (Tech Spec) 3.14.C.2 requires that an hourly firewatch be performed when fire detection instrumentation becomes inoperable for a given area. In addition, it was discovered by Fire Protection personnel that the firewatch was not in place for the Cardox Room from 0500 to 0900 hours. Therefore, since no firewatch was established, a Tech Spec violation occurred. The breaker was then closed and the instrumentation was restored to an operable condition. The cause of the event was having the fire detection system breaker open with no hourly firewatch in the Diesel Generator Cardox Room. The firewatch was not established due to miscommunication between the SSV and the Security Individual. The cause of the open breaker could not be determined. The event has been discussed with the involved individuals and pertinent information will be provided to the appropriate personnel. No previous similar events have been identified.
2771994002 | Peach Bottom 2, Peach Bottom 3 | 04/21/1994 | 07/07/1994 | 9407130130 | <strong>Failure to have the circulating water composite sampling systems operable</strong><br /><i>Abstract:&nbsp;</i>On 4/26/94, a review by Chemistry Personnel confirmed that the Circulating Water Composite Sampler systems were not operated in a manner to obtain representative composite samples of the Circulating Water intake and discharge. The cause of the event has been determined to be that the sample lines on the systems became plugged due to the build up of silt from the river water. This condition caused a decrease in the sample flow rate over time. Therefore, representative composite samples were not obtained every two hours and this resulted in a Technical Specification (Tech Spec) violation. In addition, the Chemistry Technicians, on a regular basis, adjusted the sample flow rates in an attempt to compensate for silt blockage. If the sample flow rate was found low and the sample tank was not completely filled, the flow rate was increased to fill the sample tank. This overcompensation resulted in the dilution of the composite sample. The permanent systems were declared inoperable and daily grab samples were initiated. Portable composite sampling systems have been installed on the Circulating Water Intake and Discharge in lieu of the permanent systems. In addition, the procedures used to operate the new portable systems includes guidance to the Technicians to address low sample flow conditions. The information from this event will be provided to the appropriate members of the Station staff. No previous similar events have been identified.
2771994003 | Peach Bottom 2 | 05/15/1994 | 06/13/1994 | 9406170083 | <strong>Unit 2 Scram on High Neutron Flux Condition</strong><br /><i>Abstract:&nbsp;</i>On 5/15/94, the '2A' Reactor Recirculating (RECIRC) Pump experienced an unexpected speed increase. This caused a reactor power spike which reached the Average Power Range Monitor (APRM) High Neutron Flux Scram Setpoint. It was determined that the '2A' RECIRC Pump speed increase was due to a mismatch between the Blind Controller and the Linear Variable Differential Transformer (LVDT) output signals. Troubleshooting concluded that the decrease in the LVDT output signal was caused by a spurious problem with either the LVDT or its demodulator. A spare LVDT and demodulator was installed and calibrated to control the '2A' RECIRC Scoop Tube Positioner over the full range of motion. The inputs to the strip chart recorder installed on this pump to monitor RECIRC M/G set control system performance have been modified to include a channel to monitor the status of the electrical power supply to the Scoop Tube Positioner. An evaluation will be performed to identify what actions can be taken to mitigate the effects of a future similar failure. The RECIRC M/G Sets are scheduled to be replaced with improved Adjustable Speed Drive units during the next Refueling Outages. The components which malfunctioned will be eliminated as part of this modification. No previous similar events have been identified.
2771994004 | Peach Bottom 2 | 07/18/1994 | 08/15/1994 | 9408230092 | <strong>HPCI Inoperable due to Failed Signal Isolator</strong><br /><i>Abstract:&nbsp;</i>On 07/18/94, during the performance of a normally scheduled Surveillance Test (ST), the High Pressure Coolant Injection (HPCI) system was declared inoperable when turbine speed could not be raised greater than 1000 rpm. An investigation revealed that the HPCI Flow Controller Signal Isolating Device (XS-2-23-144) failed thus preventing the HPCI turbine from achieving its design turbine speed. XS-2-23-144 was removed and replaced with a new device. The required calibration testing was performed on the HPCI control system. In addition, ST-O-23-400-2 was successfully performed and the system was restored to its normal condition. The cause of this event has been determined to be a problem with the HPCI Signal Isolator. The device was sent to the PECO Energy Laboratory which determined that the isolator's voltage regulator failed. A review of similar devices at PECO Energy Nuclear facilities found no other instances of failure. There are thirty six devices in service at various locations. The failure mode of this device is being evaluated to determine what corrective actions are required to ensure continued operability of these type devices. Corrective actions will be implemented as needed. No actual safety consequences occurred as a result of this event. No previous similar events have been identified.
2771994005 | Peach Bottom 2, Peach Bottom 3 | 07/22/1994 | 08/22/1994 | 9408290098 | <strong>Torus Water Level Instrumentation Calibration Concern</strong><br /><i>Abstract:&nbsp;</i>On 07/22/94, it was determined that the Torus Water Level Narrow Range Instrumentation was indicating up to 1' high on Unit 3 and 3.30' high on Unit 2. This means that the actual Torus level was less than that indicated on the narrow range instrumentation. Therefore, since actual Torus water level was, at some points, maintained below the 122,900 cubic feet Technical Specification (Tech Spec) limit, a Tech Spec violation occurred. Following discovery of the condition, actions were taken to maintain Torus levels between the Tech Spec limits and the appropriate Surveillance Instructions were performed to make actual Torus level match indicated Torus level. The cause of this event was that the initial reference markings used to support calibration activities were not correct. Subsequently, in 1990, placards were installed on each instrument to replace the original reference markings. In addition, it was noted that these placards were secured using tie wraps instead of a more rigid fastener. New placards were mounted on both units to reflect new transit survey points and the placards have been more rigidly secured. An evaluation concluded that this was the only situation where a placard is used as a calibration reference point which requires critical survey data from another location. The pertinent information from the event will be provided to the appropriate Station personnel. There were no actual safety consequences as a result of this event. No previous similar events have been identified.
2771994006 | Peach Bottom 2, Peach Bottom 3 | 08/04/1994 | 09/06/1994 | 9409150099 | <strong>Technical Specification Violation due to a Missed Firewatch</strong><br /><i>Abstract:&nbsp;</i>On 08/04/94 at 1630 hours, fire watches which were posted in both HPCI Rooms and the Cable Spreading Room were prematurely relieved from their watch prior to the return of the carbon dioxide fire suppression system to an operable status. Since no firewatches were in these areas during a 50 minute period when the carbon dioxide fire suppression system was inoperable, a violation of Tech Spec section 3.14-B-4 occurred. The cause of the event was that a firewatch was not maintained in these areas due to inadequate communication between the Work Control Station Coordinator and the Fire Protection Individual (FPI). Since the FPI believed that the clearance had been removed, the fire watches associated with both HPCI and the Cable Spreading Room were prematurely removed. An evaluation will be performed on the Firewatch Process to identify if additional corrective actions are needed to minimize future firewatch violations. The involved individual has been counselled regarding this event and Managements expectations that all communication is clear and understood by all individuals. The pertinent information from the event will be provided to the appropriate Operations and Fire Protection personnel. There were no actual safety consequences as a result of this event. No previous similar events have been identified.
2771994007 | Peach Bottom 2 | 08/10/1994 | 09/08/1994 | 9409160348 | <strong>Secondary Containment Breached to Fight Fire</strong><br /><i>Abstract:&nbsp;</i>On 8/10/94, a fire occurred inside the Unit 2 vent stack protective siding during modification activities. Hangers were being welded within the vent stack walls. The welding cloth was removed and smoke started coming from the opening. The fire brigade leader in conjunction with Shift Supervision directed that the hatch on the Reactor Building (R/B) roof be opened to allow a fire hose to be run through it. Once the fire hose arrived at the vent stack, water was sprayed into the opening until the steam/smoke mixture stopped. The Secondary Containment hatch was closed. The cause of this event was that a Secondary Containment hatch was opened on the R/B roof to allow a fire hose to be run through it. The cause of the fire has been determined to be that the work area was not properly staged. The Welder did not properly install the welding cloth in a manner which would prevent sparks from dropping between the inner and outer walls of the vent stack. In addition, the Work Supervisor had not properly inspected the welding area in accordance with the Hot Work Permit (HWP). An evaluation will be performed on the A-12 'IGNITION SOURCE CONTROL' and HWP Processes to identify if additional corrective actions are needed to prevent future events. The event has been discussed with the Welding Crew and the Supervisor has been coached regarding this event. No previous similar events have been identified.
2771994008 | Peach Bottom 2, Peach Bottom 3 | 08/03/1994 | 10/07/1994 | 9410170093 | <strong>Condition Prohibited by Technical Specification when MO- 0498 was Closed and Left Unattended</strong><br /><i>Abstract:&nbsp;</i>On 09/09/94, it was discovered that the Emergency Core Cooling Systems (ECCS) and the Emergency Diesel Generators (EDG) may have been Technical Specification (Tech Spec) inoperable on 08/03/94. This occurred when an Emergency Service Water (ESW) Outlet Valve (MO-0498) was closed and left unattended for approximately 47 minutes during Valve Operation Test and Evaluation System (VOTES) testing. Having MO-0498 in the incorrect position jeopardized the operability of the ECCS and EDGs due to reduced cooling water flow rates while in this mode. This condition is considered a condition prohibited by the Tech Specs since this would have placed the plant into Tech Spec 3.0.C. The cause of the event was that MO-0498 was closed and left unattended because less than adequate controls were established to ensure that MO-0498 was continuously manned during VOTES testing. The event has been discussed with the involved Operations and Maintenance personnel. The pertinent information from the event has been provided to the appropriate Operations and Maintenance personnel and it will be provided to other members of the station staff. In addition, VOTES testing procedures will be revised as appropriate to ensure that future events will be prevented. An evaluation will be performed to ensure that adequate administrative controls are established to maintain system operability whenever testing or maintenance must be done on an operable system. No previous similar events have been identified.
2771994009 | Peach Bottom 2 | 09/21/1994 | 10/21/1994 | 9410260366 | <strong>Shutdown Cooling Isolation During Relay Replacement</strong><br /><i>Abstract:&nbsp;</i>On 9/21/94, during the performance of a maintenance activity to replace a relay, six valves associated with the Primary Containment Isolation System Group II Isolation logic closed when a common neutral lead to the relay was removed. Lifting the common neutral lead caused the 16A-K30 relay to de-energize thus closing a Shutdown Cooling valve. In addition, lifting the lead interrupted electrical power to several other relays which caused the closure of five other valves. The logic was reset and the affected systems were restored. The valve closures were caused by lifting a common neutral lead on relay 16A-K63 as part of a Preventive Maintenance activity. This was due to a less than adequate clearance preparation and technical review to support relay replacement. The clearance preparer and reviewer did not identify the effects of removing the common neutral lead on this relay which was connected with other relays. Outage clearances involving relay replacements or clearances reviewed by individuals not specifically trained as Technical Reviewers, have been re-reviewed. In the interim, technical reviews are to be performed by a limited number of individuals specifically trained in technical reviews. Procedural guidance will be generated to provide more specific guidance and examples on the performance of a technical review. Training will be provided to preparers and the reviewers on common neutrals. Two previous similar events have been identified.
2771994010 | Peach Bottom 2 | 10/24/1994 | 11/22/1994 | 9411280306 | <strong>Main Steam Relief And Safety Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On 10/24/94, following the completion of the tenth Unit 2 Refueling Outage, Peach Bottom Atomic Power Station personnel reviewed ST-M-01G-450-2 'Main Steam Safety and Relief Valve Replacement'. This test documents the as found setpoint of these valves at the completion of the operating cycle in compliance with ASME Code Testing requirements and the Technical Specifications (Tech Spec). Test data indicated that three of the eleven MSRVs and two of the two SVs did not lift within the Tech Spec +/- 1 % tolerance specified in Tech Spec Section 2.2.1. Band 2.2.1.C. The three MSRVs that were beyond their 1 % tolerances lifted within the range of -1.5 % to + 2.0 % of their nameplate setpoints. The two SVs lifted within the range of -2.52 % to -4.47 % below their nameplate setpoint. The ability of the MSRVs and the SVs to successfully maintain a 1 % tolerance is an industry wide concern. The event was caused by a small drift in the setpoint of the valves which is inherent in the valve's design. Refurbished valves have been properly setup at the test facility and were installed for these MSRVs and SVs. In addition, a Technical Specification change request is being evaluated by the PECO Energy Company to address MSRV and SV setpoint tolerance relaxation. No actual safety consequences occurred as a result of this event. Previous similar events have been experienced.
2781994001 | Peach Bottom 3 | 01/24/1994 | 02/03/1994 | 9402170141 | <strong>High Pressure Coolant Injection System being inoperable due to a hydraulic oil line problem</strong><br /><i>Abstract:&nbsp;</i>On 01 /24/94, the High Pressure Coolant Injection (HPCI) system was declared inoperable during the performance of a quarterly Surveillance Test (ST). The HPCI system did not properly respond to flow controller changes during ST performance. Therefore, the applicable Technical Specification Limiting Condition for Operation (LCO) was entered. The HPCI system did start within its specified time limit and did control system flow greater than the Tech Spec 5000 gpm limit, however, system flow could not be reduced to a lower value. The cause of this event has been determined to be a leak on the HPCI system hydraulic control line. An investigation was performed which identified that a HPCI system hydraulic control line pulled out of its fitting at the system hydraulic governor. This condition prevented oil from getting to the system Servo thus not allowing the HPCI system flow rate to be reduced to a value other than its maximum. Following hydraulic control line repairs, the HPCI system was tested satisfactorily and the associated Tech Spec LCO was exited. Other hydraulic control line fittings associated with HPCI system were inspected and determined to be properly secured. An evaluation is currently in progress to determine what corrective actions are necessary to prevent future recurrences. No previous similar events have been identified.
2781994002 | Peach Bottom 3 | 02/03/1994 | 02/28/1994 | 9403080367 | <strong>Unit 3 Manual Scram Due to a Main Generator Problem</strong><br /><i>Abstract:&nbsp;</i>On 2/03/94, a Main Generator Ground Fault alarm was received in the Control Room. A Nuclear Plant Operator (NPO) discovered that the Main Generator Ground Relay status light was out, which is indicative of a field ground, but the relay flag was not up. While troubleshooting the Main Generator ground condition, the Outside Shift Supervisor (SSV) discovered a problem in the Main Generator Exciter cabinet. The Alterex Field Collapsing Circuit resistor was overheating. A rapid reactor shutdown was commenced to enable the Main Generator to be removed from service without having to scram the reactor. The NPO and SSV returned to the Main Generator cabinet and found control wiring melted and wiring insulation discolored above the resistor. Shift Management made the decision to scram the reactor. At 1914 hours, at approximately 45% power, the unit was manually scrammed. An investigation has revealed that an internal 'rack out' tab was not installed on the Alterex Field Breaker during recent maintenance activities. The Maintenance procedures used to overhaul-this breaker did not provide guidance to ensure that the rack out tab was properly installed. The damaged components were repaired and the breaker was replaced with a spare. The procedure used to overhaul the Alterex Field Breaker has been temporarily changed and will be permanently revised. No previous similar events have been identified.
2781994003 | Peach Bottom 3 | 08/11/1994 | 09/12/1994 | 9409190185 | <strong>HPCI Inoperable During Maintenance Activities</strong><br /><i>Abstract:&nbsp;</i>On 08/11/94, the High Pressure Coolant Injection (HPCI) system was considered inoperable and was placed in the secured condition by the Reactor Operator. This was done due to a spurious annunciation of the 'Auxiliary Oil Pump Running' (AOP) alarm and lighting of the red status light associated with AOP. The cause of this event has been determined to be that Maintenance Technicians working in a electrical panel in the HPCI Room inadvertently worked on a relay associated with the AOP circuit. Following identification of the cause of the event, the HPCI system was restored to its normal condition and the associated Technical Specification LCO was exited. The involved individuals have been coached regarding this event. The pertinent information from this event will be provided to the appropriate Maintenance personnel. In addition, labels will be provided for these relays to minimize future concerns. An evaluation will be performed to determine if additional labelling is required for relays with similar type component configurations. <br /><br /> Corrective actions will be implemented as appropriate pending the results of the evaluation. No previous similar events have been identified.
2781994004 | Peach Bottom 3 | 09/24/1994 | 10/07/1994 | 9410170224 | <strong>High Pressure Injection System being Inoperable when Steam Supply Valve was Closed to Isolate a Leak</strong><br /><i>Abstract:&nbsp;</i>On 09/24/94, it was identified that Drywell (DW) pressure and temperature were increasing. It was expected that a valve inside the DW had developed a packing leak. A systematic approach of closing DW valves to locate the leak was utilized. The High Pressure Coolant Injection (HPCI) system Steam Supply Valve (MO-3-23-15) was closed and both DW pressure and temperature started to decrease. The electrical power was removed from this valve to prevent it from automatically opening on a HPCI initiation signal. seat to isolate the leak. This method of back seating a valve was performed to prevent damaging the valve in any way. Verification that the valve was coasted into its back seat was ensured using Valve Operation Test and Evaluation System (VOTES) data. DW parameters were monitored to ensure that the valve was sufficiently back seated to stop the leak. This returned the HPCI system to an operable status. In addition, the valve was stroked from the back seated condition to ensure that the valve was operable for isolation purposes. The cause of this event is believed to be a packing leak on MO-3-23-15. The exact cause of the packing failure can not be determined until the unit is shutdown and an inspection is performed. MO-3-23-15 will be repaired as necessary at a future shutdown. Corrective actions will be implemented as appropriated following identification of what caused the leak. One previous similar event has been identified.
2781994005 | Peach Bottom 3 | 10/11/1994 | 11/04/1994 | 9411080230 | <strong>Unit 3 Scram Due to a Static Inverter Failure</strong><br /><i>Abstract:&nbsp;</i>On 10/11/94, the 'A' & 'C' Reactor Feed Pumps (RFP) locked up and both Recirculating (Recirc) Pumps ran back. The lockup of the two RFPs in conjunction with the Recirc Pump run back caused the reactor water level to increase to the high water level Main Turbine trip setpoint. At 1121 hours, the Main Turbine trip caused a closure of the Turbine Stop Valves which is an input to the Reactor Protection System (RPS) scram logic. Immediately following the scram, Primary Containment Isolation System (PCIS) Group II/III isolations also occurred when the Reactor water level decreased below 0'. Troubleshooting revealed that a failed Static Inverter caused a momentary loss of electrical power to the 30Y050 panel which in turn caused the two RFPs to lockup and both Recirc Pumps to runback. After the scram occurred, the appropriate PCIS and RPS scram logics were reset. The failed transformer was replaced and infrared thermography was performed on the Unit 2 and 3 Static Inverters to identify elevated component temperatures. No questionable indications were identified on either unit. An evaluation will be performed to establish a frequency for performance of infrared thermography on Static Inverters and to identify what additional transformer testing can be performed. In addition, PM activities for the replacement transformers will be initiated. No previous similar events have been identified.
2781994006 | Peach Bottom 3 | 11/10/1994 | 12/23/1994 | 9412300079 | <strong>Average Power Range Moniotr Flow Biased Setpoints on Rod Block Being Non Conservative</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 11/10/94, a Shift Engineer identified that the flow input signals to the Average Power Range Monitors (APRM) were reading higher than actual core flow conditions. This condition affected the conservatism associated with the Scram and Rod Block flow biased setpoints. It is possible that the flow biased APRM Rod Block setpoint may have exceeded the Technical Specification limit. The flow biased APRM Scram setpoints remained in compliance. This event was caused by a change in plant operating strategy that impacted the initial drive flow to core flow correlation established at rated power and flow conditions. The change in operating philosophy allowed entrance into the MELLLA region of the power flow map. The vendor did not advise the station of the nonconservative impact on APRM flow biased setpoints while in the MELLLA region. No information was provided that indicated a need to re-establish a drive flow to core flow correlation when the MELLLA region was initially entered. The modification team failed to identify this issue due to the subtle nature of this phenomenon. Following discovery of this condition, all APRMs were adjusted to ensure that the normal APRM flow biased setpoints were re-established. An evaluation was performed which verified that this condition does not exist on Unit 2. Additional controls will be created to ensure that these limits can not be exceeded. One previous similar event has been identified.
2801994001 | Surry 1 | 02/03/1994 | 03/04/1994 | 9403150078 | <strong>Welding on Pressurizer Piping Results in Hydrogen Burn in Pressurizer</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was at cold shutdown in a refueling outage on February 3, 1994. The Reactor Coolant system (RCS) loops had been drained, the reactor head de-tensioned, and the reactor vessel head and pressurizer were vented to the containment. Contract welders were implementing a modification that installed a drain line on a section of RCS four inch piping that runs from the pressurizer to the pressurizer power operated relief valves. The weld area was purged with argon gas. As a tack weld was being performed, water squirted from the opening in the RCS piping and a rumbling noise was heard by the welding personnel. At 0243 hours, the Ventilation Vent system radiation monitors alarmed in the control room. Abnormal Procedure 0-AP-5.20 was initiated. The Operations Shift Supervisor ordered an evacuation of the containment until plant conditions could be evaluated. A task team investigation of the event concluded that hydrogen gas in the pressurizer had been ignited by the welding arc. To prevent recurrence, procedures and work processes have been revised to heighten personnel awareness of systems that may have the potential for explosive gas mixtures. This event is being reported voluntarily due to its potential safety significance and general interest to other licensees.
2801994002 | Surry 1 | 02/04/1994 | 02/28/1994 | 9606190156 | <strong>MAIN STEAM SAFETY VALVES OUT OF TOLERANCE DUE TO MINOR SETPOINT DRIFT</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 4, 5, and 7, 1994, with Unit I at cold shutdown and Unit 2 at 100% power, setpoint testing on fifteen Unit 1 Main Steam Code Safety Valves r evealed that the lift settings of three valves (I-MS-SV-IO5B, 102B and 104A) were outside the q 3% 'As Found' range that is allowed b y the Technical Specifications (TS). The three valves exhibited li ft settings ranging from 3.3% to 4.7% above their nominal value. The affected valves were inspected and overhauled by the manufacturer. They were adjusted to within q 1% of the required 'As Left' setpoints. The valves were tested to verify that three consecutive lifts were with in tolerance without setpoint adjustment. An engineering evaluatio n of the accident analysis was performed which verified that the safeties would have performed their safety function. Therefore, the health and sa fety of the public were not affected. This event is reportable pur suart to IOCFRSO.73(a)(2)(i)(8) for conditons prohibited by TS 3.6. A. 3.6.8.3 and 3.6.D.
2801994003 | Surry 1 | 02/04/1994 | 03/04/1994 | 9403140238 | <strong>Hole in Recirculating Spray Heat Exchanger Service Water Outlet Piping</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1994, with Unit 1 at Cold Shutdown for the Cycle 12 refueling outage, a Service Water (SW) flow test was performed on one train of the Recirculation Spray System heat exchangers (RSHXs). During subsequent inspections of the 24 inch SW piping for the RSHXs, a small hole was discovered in an elbow on the SW outlet piping of RSHX B. This piping is in containment and provides a membrane barrier between the outside and containment atmospheres. A second barrier exists at the closed SW inlet and outlet motor operated isolation valves located outside containment. Since the unit was at cold shutdown, the recirculation spray system and containment integrity were not required. A Deviation Report was submitted and an evaluation of the potential leakage path from containment was performed. The evaluation determined that leakage through the hole would have been in excess of the 10CFR50 Appendix J limits. On February 4, 1994, it was determined that this condition was reportable pursuant to 10CFR50.72(b)(2)(i). A four hour non emergency report was made at 1748 hours. <br /><br /> Inspection of the Unit 1 SW outlet piping for each RSHX has been completed. No other areas of piping below code allowable wall thickness were found. RSHX B SW outlet piping elbow will be replaced prior to unit startup. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(ii).
2801994004 | Surry 1 | 03/01/1994 | 03/23/1994 | 9403280370 | <strong>Loop Isolation Valve Not Open Within Tech. Spec. Limit Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1994, Unit 1 was at refueling shutdown in the 38th day of a scheduled refueling outage. The Reactor Coolant System (RCS) loops had been drained and isolated. The reactor core was partially loaded with 32 fuel assemblies. Operating Procedure 1-OP-RC-002 was initiated to fill RCS Loop 'B' from the active RCS. At 0840 hours, the loop was determined to be full. At 1050 hours, the hot and cold leg isolation valves were fully opened. Technical Specification 3.17.5.c requires that the hot and cold leg isolation valves be fully opened within two hours after an isolated loop is filled. During this event, the hot leg isolation valve was not fully opened within the two hour time limit. This event was caused by a cognitive personnel error. To prevent recurrence, the Operations Department personnel involved were counseled. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2801994005 | Surry 1 | 03/30/1994 | 04/27/1994 | 9405020236 | <strong>Steady State Reactor Power Exceeded Operating License Limit</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 001%. On March 30, 1994, Unit 1 completed power ascension following a refueling outage. When the unit reached 100% power, control room operators noted that the main generator gross output indication was high, up to 835 megawatts-electrical (MWe). Station management reviewed the condition and directed Operations personnel to reduce power to 820 MWe until plant parameters could be evaluated by the Engineering Department. At 2054 hours, unit power was reduced to approximately 98%. Engineering personnel investigated the discrepancy and determined that the Prodac 250 computer system FLOWCALC program, which computes main steam and feedwater flows, had not been updated to incorporate the most recent revision of the main steam flow transmitter differential pressure span values. Output from the FLOWCALC program is used by the CALCALC program which provides an indication of reactor power. Further investigation indicated that the unit had operated at a shift average of approximately 100.5% power, 2453 megawatts-thermal. This event was caused by an inadequate instrumentation change control process. To prevent recurrence, the instrumentation change control process will be modified to ensure changes to station instrumentation are effectively controlled. The event is being reported voluntarily as a violation of the facility operating license.
2801994006 | Surry 1 | 05/11/1994 | 06/09/1994 | 9406160107 | <strong>Unit 1 Manual Reactor Trip During Safeguards Actuation Logic Testing</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1994, with Unit 1 initially at 100% power, the reactor was manually tripped at 2109 hours. The trip was initiated when one of the two sources of main feedwater was isolated and Operators were unable to recover steam generator levels. The cause of partial feedwater isolation was inadvertent actuation of a relay in the safety injection actuation circuitry during logic testing. Actuation of this relay caused the tripping of the power supply to one of the Main Feedwater (MFW) pump motors and the closure of the MFW pump's discharge isolation valve. The Reactor Protection System functioned as designed, and post-trip response was satisfactory. The reactor was placed in a safe, hot shutdown condition. The health and safety of the public were not affected. This report is being made pursuant to 10CFR50.73(a)(2)(iv).
2801994007 | Surry 1 | 06/14/1994 | 07/12/1994 | 9407180131 | <strong>Process Vent High Range Accident Monitor Inoperable Greater Than Seven Days</strong><br /><i>Abstract:&nbsp;</i>The Kaman Process Vent Radiation Monitors were declared inoperable on June 14, 1994, at 1425 hours when the Equipment Failure light began to come on intermittently and Annunciator RM-A-C-4, Effluent Rad Mon Trbl, locked in. This failure occurred on the Normal Range Radiation Monitor (1-GW-RM-130-1) and also rendered the Mid and High Range Radiation Monitor Channels (1-GW-RM-130-2) inoperable. The inoperability of 1-GW-RM-130-2 is contrary to Technical Specification (TS) Table 3.7-6, item 11, which requires both channels of the 1-GW-RM-130-2 to be operable. As required by the TS Limiting Condition of Operation (LCO), the alternate monitoring method was placed in service. An investigation into the problem with the 1-GW-RM-130-1 indicates the problem is moisture entrapment in the charcoal cartridge. A seven day LCO was started on 1-GW-RM-130-2. This LCO expired on June 21, 1994, at 1,425 hours. Therefore, this Special Report is being submitted, pursuant to TS Table 3.7-6 and Section 6.2, since 1-GW-RM-130-2 was inoperable for a period in excess of seven days.<br /><br /> During accident conditions, the sampling flow path in 1-GW-RM-130-1 is rerouted around the low range iodine filter and gaseous monitor. The current moisture problems being encountered will have insignificant impact on 1-GW-RM-130-2 during the sampling periods designed, for the system in case of an accident. Therefore, the health and safety of the public are not affected.
2801994008 | Surry 1, Surry 2 | 08/04/1994 | 02/24/1995 | 9503030023 | <strong>Entry Into Technical Specification 4.0.3 for Failure to Test New Charcoal in Accordance With Technical Specification 4.12.B.7(b) and a Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1994, at 0243 hours, with Unit 1 at 100% power and Unit 2 shut down for a Steam Generator Chemical Cleaning (SGCC) outage, the auxiliary ventilation system was placed in service to purge Unit 2 containment through the redundant safety related charcoal filter beds. The auxiliary ventilation system is a common system used to filter potential airborne iodides from the affected spaces during design basis accidents. Containment purge was secured on June 21, 1994, at 1845 hours to reestablish containment integrity following completion of the SGCC outage. Based on sampling results after the SGCC outage, both filter beds experienced similar abnormal losses in efficiency for removal of methyl iodide. This event is being reported pursuant to 10 CFR 50.73 (a) (2) (vii) (c) due to a possible single cause resulting in both filters being rendered inoperable. As part of the corrective action for this Licensee Event Report (LER), other Technical Specification requirements for event driven surveillances were evaluated. On September 29, 1994, it was determined that an inconsistency had existed for the testing methodology for new charcoal. The evaluation also determined that certain sensitized stainless steel piping flushes performed in the past per Technical Specification 4.1.3.A/B did not include a visual inspection of the affected piping per Technical Specification 4.2. These are reportable pursuant to 10 CFR 50.73 (a) (2) (i) (B). Design basis requirements were met during these events. Therefore, the health and safety of the public were not affected.
2801994010 | Surry 1, Surry 2 | 09/27/1994 | 10/27/1994 | 9411030260 | <strong>Missed Emergency Diesel Generator Battery Surveillance Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1994, with Unit 1 and Unit 2 at 100% power, Engineering identified that procedure 0-EPT-0109-03, Weekly Emergency Diesel Generator Battery Pilot Cell and Bus Voltage Checks, due by September 27, 1994, had not been performed. <br /><br /> The Emergency Diesel Generator (EDG) batteries are the DC supply power for two EDG Start Circuit Controls, for Annunciator power, and for DC Control. Procedure 0-EPT-0109-03 tests the EDG batteries for pilot cell electrolyte level, specific gravity, temperature, voltage and battery bus voltage. <br /><br /> The weekly requirements of Technical Specifications (TS) 3.16.A.7 and 4.6.D.1.a are met by the performance of procedure 0-EPT-0109-03. Upon learning of the missed surveillance, a 24 hour action statement was entered in accordance with TS 4.0.3. The action statement was entered on September 29, 1994, at 1100 hours and was exited at 1257 hours upon successful completion of 0-EPT-0109-03. Since the EDG Battery Pilot Cell and Bus Voltage Checks tested satisfactory, the health and safety of the public were not affected. <br /><br /> This event is being reported pursuant to10CFR50.73(a)(2)(i)(B).
2811994001 | Surry 2 | 01/24/1994 | 02/16/1994 | 9402230289 | <strong>Both Auxiliary Ventilation Exhaust Filter Trains Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1537 hours on January 24, 1994, with Unit 1 in Cold Shutdown and Unit 2 at 100% power, the 'A' Filtered Exhaust Fan, 1-VS-F-58A, tripped and was declared inoperable. Because of the testing configuration of the power supply to the redundant 'B' auxiliary ventilation exhaust filter train, both trains were inoperable, a condition not permitted by Technical Specification (TS) 3.0.2. TS 3.0.2 specifies that if the normal or emergency power supply to a system, subsystem, train, component or device is inoperable, all of its redundant system(s), subsystem(s), train(s), component(s) and device(s) must be operable. Otherwise, the unit must be placed in at least hot shutdown within six hours and in at least cold shutdown within the following thirty hours. Accordingly, a six-hour action statement to hot shutdown for Unit 2 was entered. During the time that 1-VS-F-58A was inoperable, a source of power was available to the 'B' ventilation filter exhaust train. Therefore, the health and safety of the public were not affected. 10CFR50.73(a)(2)(i)(B).
2811994002 | Surry 2 | 03/07/1994 | 03/30/1994 | 9404070199 | <strong>Both Trains of Auxiliary Ventilation Exhaust Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1994, Unit 1 was in refueling shutdown and Unit 2 was operating at 97.5% power. At 0939 hours, the 'B' filtered exhaust fan (1-VS-F-58B) tripped, rendering auxiliary ventilation filtered exhaust train 'B' inoperable. At the time, the emergency power supply to the redundant filtered exhaust train, Emergency Diesel Generator #1, was in EXERCISE for testing purposes. The absence of its emergency power source, coupled with the inoperability of the redundant train, rendered auxiliary ventilation filtered exhaust train 'A' inoperable as well. Operation in this condition is prohibited by Technical Specification 3.0.2. Accordingly, a six hour action statement to hot shutdown was entered for Unit 2. During the time that auxiliary ventilation filtered exhaust train 'A' was technically inoperable, its normal off-site power supply was available. Therefore, the health and safety of the public were not affected. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B).
2811994003 | Surry 2 | 06/17/1994 | 07/14/1994 | 9407220125 | <strong>Failure to Isolate Primary Grade Water to Blender</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1994, Unit 2 was at cold shutdown in the 14th day of a 23 day Steam Generator Chemical Cleaning Mid-Cycle Outage. The reactor core was fully loaded. The Reactor Coolant System (RCS) B loop was drained and isolated. The Residual Heat Removal System was operating. At approximately 1100, the primary grade water supply manual isolation valve, 2-CH-212, was opened to prepare for makeup to the Chemical and Volume System. A license trainee and the Reactor Operators (ROs) performed the makeup activity. Technical Specification 3.2.F requires that during refueling or cold shutdown conditions, 2-CH-212 will be in a closed position within 15 minutes following a planned dilution or makeup. The valve was found in the open position at 1622 by the relief shift RO. The event was caused by personnel error. There was no safety consequence since no dilution occurred. To prevent recurrence, appropriate procedural controls will be implemented and the briefing given to trainees and ROs, prior to the trainee in-plant period, will be enhanced. <br /><br /> This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2811994004 | Surry 2 | 10/07/1994 | 12/02/1994 | 9412070192 | <strong>Station Battery 2A Inoperable Longer Than Allowed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1994, with Unit 1 at 97.5% and Unit 2 at 100% power, Maintenance personnel noted during a review of the actions taken to correct the degraded condition of Station Battery 2A that the measured voltage of Cell 52 had been within the 'Inoperable' range prior to October 27 (when the battery had been declared inoperable). Upon further review, it was determined that the measured voltage of Cell 52 had been within the 'Inoperable' range on October 7, 17, 22, and 26. Since the measured voltages were not recognized as being in the 'Inoperable' range, the appropriate Limiting Condition for Operation was not initiated and Station Battery 2A remained inoperable for a period in excess of that allowed by TS 3.16.8.3. This event was caused by inadequate post- maintenance testing and a cognitive personnel error by a utility engineer. To prevent recurrence, the process by which station battery electrical corrective maintenance is performed was changed to require the performance of post-maintenance testing that is independent of the electrical corrective maintenance procedures. The post-maintenance testing specifies acceptance criteria to ensure the recognition of inoperable conditions. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2821994001 | Prairie Island 1, Prairie Island 2 | 03/01/1994 | 03/31/1994 | 9404040127 | <strong>Auto-start of No. 121 Cooling Water Pump on Low Header Pressure While Aligned for Safeguards Operation</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1994, both units were at 100% power. No. 11 Motor-driven Cooling Water Pump was running and supplying all cooling water loads. See Figure One. Technical Specifications allow a diesel cooling water pump to be removed from service with no Limiting Condition for operation entry, provided that No. 121 Cooling Water Pump is aligned to supply the affected header. No. 121 Cooling Water Pump had been aligned for safeguards operation (valves C and D closed) in accordance with Technical Specification 3.3.D.1.a., in order to isolate No. 12 Diesel Cooling Water Pump for repair of a leaking lube oil fitting. After the repair was made, No. 12 pump was started locally to verify the leak had been fixed. The discharge valve for No. 11 pump was then slowly closed to allow No. 12 pump to gradually assume the header load, and No. 11 pump to be unloaded and shut down. After No. 12 pump had been run for 1 hour, No. 11 pump was restarted to assume the header load and No. 12 pump was shut down. When No. 12 pump was shut down locally, No. 11 pump did not pick up the header loads quickly enough, and the resultant decrease in header pressure was sufficient to cause No. 121 pump to start automatically at 1408 hours. This was a nonsafeguards actuation of an ESF component.
2821994002 | Prairie Island 1, Prairie Island 2 | 03/03/1994 | 05/04/1994 | 9405100075 | <strong>Inoperability of Radwaste Building Ventilation System Radiation Monitor R-35 Went Undetected Because of Component Failure</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1994, radiation monitor R-35, RadWaste Building Ventilation System Monitor, was removed from service for modification of its sampling system. The modification was completed and the monitor was returned to service on February 11. On March 3, the noble gas monitor in R-35 did not respond when source-checked during the routine radiation monitor surveillance. The RadWaste Building Ventilation System was secured OFF until the monitor could again be made operable. During investigation of the failure on March 4, a broken detector signal lead was discovered. Further investigation led to the conclusion that the lead had probably been broken during the modification done in February, and that the monitor had been inoperable since that time. The monitor was repaired, source-checked and returned to service on March 9. Based on weekly grab samples and historical monitoring data, it was shown that no releases via the RadWaste Building Ventilation System took place during the event.
2821994003 | Prairie Island 1, Prairie Island 2 | 04/29/1994 | 05/31/1994 | 9406070329 | <strong>Missed Surface Examinations of the Reactor Coolant Pump Flywheels</strong><br /><i>Abstract:&nbsp;</i>During a 1993 internal audit of the inservice inspection activities at Prairie Island, the Nuclear Quality Department compared the Prairie Island Technical Specifications requirements for NDE examinations of the reactor coolant pump flywheels with the examinations which had been performed.<br /><br /> From this review and subsequent investigation it has been determined that the ten year interval surface examinations for both Units 1 and 2 have not been completed as required (at approximately 10-year intervals). A final determination of this was made on April 29, 1994 during a conference call with the NRC. <br /><br /> Since the determination that the examinations may not have been performed as frequently as required, all flywheels have been examined.
2821994004 | Prairie Island 1, Prairie Island 2 | 05/08/1994 | 06/07/1994 | 9406150252 | <strong>Two Main Steam Safety Valves Found to Lift Outside of Their Technical Specification Tolerance of +/-1%</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1994, Unit 1 was being shut down for a scheduled refueling outage. The Reactor Coolant System had been borated to the Cold Shutdown boron concentration and the secondary steam system was being maintained at 915 psig in order to test the main steam safety valves. The 5 safety valves on 1 of the 2 main steam lines are tested each refueling outage. The test involves stabilizing the valve body temperature, then using a hydraulic lift assist device to simulate the higher streamline pressure needed to lift the safety valve. The valves are tested one at a time to determine the actual lift setpoint via a correlation with the hydraulic oil pressure in the test equipment. The as-found lift setpoint for valve RS-21-1 was determined to be 1098 psig, 2% above the nominal setpoint of 1077 psig. The as-found lift setpoint for valve RS-21-5 was determined to be 1111 psig, 1.8% below the nominal lift setpoint of 1131 psig. The as-found lift setpoints of the other 3 valves were within the +/- 1% Technical Specification acceptance criteria. Valves RS-21-1 and RS-21-5 were adjusted so that their as-left lift setpoints were within +/- 1% of their nominal setpoints.
2821994005 | Prairie Island 1, Prairie Island 2 | 07/19/1994 | 08/18/1994 | 9408250102 | <strong>Inadvertent Closure of a Steam Generator Blowdown Containment Isolation Valve Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1994, Unit 1 was at 100% power. At 1543 Control Room operators noticed computer and control board indications that steam generator blowdown containment isolation valve, MV-32044, had gone closed and then about 15 minutes later noted the opposite indication and alarm when the valve reopened. During this time operators checked on personnel status and activities that might have caused the closure. <br /><br /> Modifications associated with the electrical safeguards upgrade project had been recently completed, during the Unit 1 refueling outage, with the exception of the wire code tag changes. At 15:43 hours, while changing the wire codes, an electrician shorted across the 111J-13CL and 111J-13CL1 terminals with a tool, causing the valve to close. Approximately 16 minutes later a short across the 111J-130 and 111J-1301 terminals caused the valve to open. <br /><br /> Corrective actions have been implemented to reduce the potential for inadvertently shorting across the terminals and to minimize the impact if inadvertent contact were to occur.
2821994006 | Prairie Island 1 | 09/07/1994 | 10/06/1994 | 9410130058 | <strong>Unplanned Closure of a Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1994, Unit 1 was operating at 100% power. At 2059, control room operators observed receipt of the annunciator '12 Charging Pump Overload Trip'. Within seconds several other alarms were received (Letdown Orifice Isolation Valve - CLOSED, Low RCP Seal Injection Flow, Low RCP Labyrinth Seal DP) as a result of the trip of No. 12 Charging Pump. Since the pump was the only charging pump operating at the time, trip of the pump caused letdown isolation; the open letdown orifice isolation valve closed. Letdown orifice isolation valves also function as containment isolation valves. This unplanned closure of the letdown orifice isolation valve was a non-ESF actuation of dual-function equipment. The operators started No. 13 charging Pump, restoring charging flow and reactor coolant pump seal injection flow, and within 1 minute they restored letdown. The outplant operator investigated the cause of the trip and found that the breaker for No. 12 Charging Pump had tripped. Since No. 11 and 13 Charging Pumps were available, no LCO was entered. <br /><br /> The breaker for No. 12 Charging Pump had tripped due to an overheated C phase loadside connection at the MCCB, a connection made at the breaker.
2821994007 | Prairie Island 1, Prairie Island 2 | 09/20/1994 | 10/19/1994 | 9410260249 | <strong>Determination that electrical load shedding functions were not being fully tested During routine surveillance</strong><br /><i>Abstract:&nbsp;</i>Review of electrical system testing was being done in response to a report of inadequate testing at another facility. During review of SP 1083, Unit 1 Integrated Safety Injection Test, in June 1994, a reviewer questioned whether the test satisfies Technical Specification 4.6.A.3.b.1, which requires, among other things, that load shedding (proper tripping of motor feeder breakers) be demonstrated at 18-month intervals. An extensive review of load shedding and load restoration testing functions was undertaken. The conclusion of the review was that load restoration testing was adequate, but that load shedding was not properly demonstrated.<br /><br /> Since Unit 1 was in a refueling outage, SP1083 was reviewed first. Findings were that load shedding was not being properly demonstrated during the test. The test was revised to fully test load shed functions. The test was successfully performed during the Summer 1994 refueling outage. <br /><br /> SP2083, Unit 2 Integrated SI Test, was reviewed, and the same inadequacies were found. Since Unit 2 was at full power, the integrated test could not be performed, but individual component testing was done to insure proper load shedding capabilities. SP2083 will be revised and performed at the next scheduled refueling.
2821994008 | Prairie Island 1, Prairie Island 2 | 09/26/1994 | 10/26/1994 | 9411020097 | <strong>Inoperability of Continuous Aur Monitor When Power Supply Was Tripped Without Control Room Knowledge</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1994, both units were at 100% power. A Nuclear Plant Services Attendant (NPSA) was buffing the floor near Continuous Air Monitor No. 5 (CAM-5). At about 1315 hours, the buffer went dead so the NPSA tried plugging the buffer into other receptacles in the area until he found one that worked, and continued buffing the floor. At 0724 on September 27, the Auxiliary Building Operator on normal rounds noticed that CAM-5 was not operating and notified the Control Room. The Control Room Operator secured Spent Fuel Pit normal ventilation while the Auxiliary Building Operator and the Duty Chemist worked to repower CAM-5. At 0745 the Duty Chemist repowered CAM-5 from an alternate source, and the Control Room Operator restarted SFP normal ventilation. At 0807 the Auxiliary Building Operator found that the normal supply for CAM-5 was tripped and reset it. The Duty Chemist then connected CAM-5 to its normal source of power.
2821994009 | Prairie Island 1, Prairie Island 2 | 10/29/1994 | 04/06/1995 | 9504110297 | <strong>Design Basis Reconstitution Effort Uncovered Design Deficiency in Containment Isolation Function</strong><br /><i>Abstract:&nbsp;</i>Design basis reconstitution of the containment integrity and containment isolation functions uncovered a design deficiency. <br /><br /> The chemical and volume control system letdown line from the reactor coolant system has redundant containment isolation valves; inboard, the 3 letdown orifice isolation valves, and outboard, the letdown isolation valve. The RHR to letdown line, which is used for shutdown purification and overpressure protection of the RHR piping, ties in to the letdown line between the redundant containment isolation valves. <br /><br /> Failure of the outboard letdown line containment isolation valve in the open position would allow the RHR system to pump contaminated water to the letdown system outside of containment. Assuming no operator action, there is a potential to exceed the USAR offsite dose calculation values.<br /><br /> Additionally, with contaminated water in the auxiliary building in locations other than those evaluated, it may not be possible to fully implement all the emergency procedures within the assumed radiation dose.
2821994010 | Prairie Island 1, Prairie Island 2 | 10/27/1994 | 11/23/1994 | 9411300284 | <strong>Determination That Scaling for Overtemperature Delta T Reactor Trips Was Inadequate</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1994, the NRC resident inspector informed plant staff that a similar plant was investigating a concern with their reactor trip functions, specifically with the overtemperature delta temperature (OTDT) trips. Plant Instruments and Controls Engineering contacted the other plant and our own Nuclear Analysis Department to determine if a similar concern existed at Prairie Island. On October 27, it was determined that, although the T sub hot temperature channels are calibrated for the range 520F to 620F, the maximum temperature requiring protection by the OTDT trip corresponds to a T sub hot of 635F. <br /><br /> On October 28, testing of spare modules verified that they could operate reliably in the extended range of 520F to 651F. In-service modules in both Units 1 and 2 were verified to operate in the range 520F to 645F, and a Safety Evaluation was written justifying the extended range. The Safety Evaluation addressed all the required testing of the modules to validate acceptable performance in the extended range. on October 29, the Operations Committee reviewed the Safety Evaluation and determined that the event was reportable.
2821994011 | Prairie Island 1, Prairie Island 2 | 11/18/1994 | 12/19/1994 | 9412290160 | <strong>Discovery That No. 121 Cooling Water Pump Was Inoperable for Safeguards Operation</strong><br /><i>Abstract:&nbsp;</i>No. 121 Cooling Water Pump was recently upgraded to a safeguards pump during the station blackout/electrical system upgrade project, which provided a safeguards power supply to the pump motor. Engineering design basis reconstitution efforts have uncovered two scenarios in which a single failure could threaten operability of No. 121 Cooling Water Pump. The scenarios relate only to No. 121 Cooling Water Pump and its support ventilation when the pump is credited for safeguards operation per Technical Specification 3.3.D.1.a. Cause of the event was inadequate review of electrical supply and control circuitry to assure full qualification of No. 121 Cooling Water Pump as a safeguards pump. <br /><br /> Controls have been established to prevent taking credit for No. 121 CLP as a safeguards pump. It is anticipated that a modification will be necessary to repower the screenhouse safeguards exhaust fan start circuitry relating to No. 121 CLP before it can be declared a safeguards pump.
2821994012 | Prairie Island 1, Prairie Island 2 | 12/02/1994 | 12/22/1994 | 9412290287 | <strong>Unplanned Closure of a Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1994, Unit 1 was operating at 100% power. At 0021, No. 12 charging Pump tripped. Since the pump was the only charging pump operating at the time, trip of the pump caused letdown isolation; the open letdown orifice isolation valve closed. Letdown orifice isolation valves also function as containment isolation valves. This unplanned closure of the letdown orifice isolation valve was a non-ESF actuation of dual-function equipment. The valves are designed for thousands of such operations; this one unplanned operation had no deleterious effect on the equipment. The letdown orifice isolation valves were, at all times, available for their ESF function. The operators started No. 13 Charging Pump, restoring charging flow and reactor coolant pump seal injection flow, and within 2 minutes they restored letdown. The outplant operator investigated the cause of the trip and found that the breaker for No. 12 Charging Pump had tripped. Since No. 11 and 13 Charging Pumps were available, no Limiting Condition for Operation was entered. <br /><br /> The breaker for No. 12 Charging Pump had tripped because the breaker did not adequately compensate for an increase in ambient temperature that resulted from routine ventilation system testing.
2851994001 | Fort Calhoun | 02/11/1994 | 03/14/1994 | 9403210228 | <strong>Safeguards Actuation and Subsequent Reactor Trip Due to Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1994 at 0340, an invalid Containment Pressure High Signal (CPHS) occurred. The CPHS initiated Engineered Safeguards actuations including safety injection actuation containment isolation actuation, steam generator isolation, and starting of emergency diesel generators. Steam generator isolation also resulted in a turbine/reactor trip. The cause of the event was a coil-shorting failure of a supervisory relay, resulting in actuation of the CPHS lockout relay. <br /><br /> Post-event investigation determined that if a coil-shorting failure of certain other supervisory relays were to occur coincident with certain design basis accidents, the result could involve premature actuation of lockout relays associated with the Recirculation Actuation Signal (RAS). It was concluded that these concerns represented conditions outside the design basis of the plant. The cause of the design basis concerns was determined to be failure of the original plant design to anticipate a potential failure mode. <br /><br /> The failed CPHS supervisory relay was replaced, and will be sent off-site for investigation of the failure mechanism. An engineering analysis was performed with respect to engineered safeguards supervisory relays. Eight supervisory relays have been disconnected to address the design basis concerns identified by the engineering analysis.
2851994002 | Fort Calhoun | 03/08/1994 | 04/07/1994 | 9404110218 | <strong>Inoperability of Boric Acid Pump Due to Inappropriate Feeder Breaker</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1994, it was discovered that an inappropriate model of feeder breaker was installed for boric acid pump CH-4B. The range of adjustment for the instantaneous trip setting of the installed breaker was lower than the recommended setting for the pump motor. As a result, CH-4B was declared inoperable due to the inability to ensure reliable starting of the CH-4B motor. <br /><br /> The root cause of this event was determined to be improperly specified hardware. The inappropriate model of breaker has been installed since at least October 1991, and may have been installed as part of the original plant configuration.<br /><br /> The breaker was replaced with an appropriate model of breaker, and the breaker for the other boric acid pump (CH-4A) was verified to be appropriate. Subsequently, an initial review of the safety-related Motor Control Centers was conducted to confirm breaker sizing adequacy. This review determined that the existing breakers are adequately sized and properly set. Engineering Assistance Request 94-044 has been initiated to further evaluate Motor Control Center starter units and document the results.
2851994003 | Fort Calhoun | 03/04/1994 | 04/04/1994 | 9404060008 | <strong>Inoperability of Raw Water Pumps Due to Excessive Sand Accumulation</strong><br /><i>Abstract:&nbsp;</i>At 1624 on March 1, 1994, an attempt was made to start Raw Water (RW) Pump AC-10B for routine pump rotation. The Operator noted that pump motor amps appeared to stay high for a longer period of time than normal. Normally, amp meter indication will go high initially when the pump is started, but will come down after the associated pump, discharge isolation valve is fully open. The Operator immediately secured the pump, AC-10B was declared inoperable and action was taken to restore the pump to operable status within Technical Specification time limits. <br /><br /> At 0407 on March 4, 1994, a similar incident occurred involving RW Pump AC-10C.<br /><br /> The primary cause of these events was determined to be elevated sand content in the river, resulting in excessive sand accumulation around the suction area of the pumps. <br /><br /> The normal frequency for rotation of RW pumps has been increased on an interim basis in order to minimize the possibility of excessive sand accumulation. Sparge lines will be installed at the inlets of RW pumps AC-10B and AC-10C, and an evaluation will be performed to assess whether diversion baffles should be placed on the river bed in front of the Intake Structure.
2851994004 | Fort Calhoun | 04/13/1994 | 05/13/1994 | 9405180241 | <strong>Inoperability of Halon Gas Fire Suppression System due to Inoperable Fire Damper</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1994 with the plant operating at 100% power, a fire damper designed to retain Halon in the cable spread room in the event of a fire was found improperly latched open. This rendered the cable spread room Halon gas system inoperable and, since a continuous fire watch was not established until the condition was discovered, Technical Specification 2.19(8) was violated. This Technical Specification violation is being reported pursuant to 10 CFR 50.73(a)(2)(B).<br /><br /> The primary cause of this event was inappropriate action by unknown personnel. Corrective actions include communicating to applicable personnel a summary of this event and its consequences, emphasizing that (a) only authorized and qualified personnel are to operate plant equipment, and (b) the control room or Shift Supervisor should be notified of any unexpected plant or system condition.
2851994005 | Fort Calhoun | 04/27/1994 | 05/27/1994 | 9406010259 | <strong>Failure to Appropriately Address Out-of-Tolerance Test Results for Snubbers</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1994, during a programmatic review of snubber history in preparation for the 1995 Refueling Outage, it was found that three snubbers tested during the 1990 Refueling Outage and two tested during the 1992 Refueling Outage were accepted as passing the as-found functional test although they did not meet the surveillance test acceptance criteria for bleed rate. This resulted in the failure to retest the snubbers during the 1992 and 1993 Refueling Outages, and the failure to sample an additional 22 snubbers during the 1990 Refueling Outage, as required by Technical Specification 3.14. <br /><br /> The primary cause of the event was determined to be procedural inadequacy. Contributing causes to the event were determined to be failure of the Snubber Test Operator to self-check during the initial evaluation of the test results and failure of subsequent reviewers to compare the raw data to the test results of every snubber tested. <br /><br /> For corrective actions, the snubber surveillance test procedure will be revised and the five snubbers in question will be functionally tested during the 1995 Refueling Outage.
2851994006 | Fort Calhoun | 05/14/1994 | 06/13/1994 | 9406230223 | <strong>Failure to Place Charcoal Filter in Service Prior to Moving Irradiated Fuel</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1994, spent fuel movement was in progress to support the Spent Fuel Pool (SPF) Rerack modification. At 1457, fuel movement was temporarily halted for shift turnover and VA-66, the SFP charcoal filter, was taken out of the filtered mode. At 1516 the operator for the new shift started fuel movement. VA-66 was not placed into the filtered mode of operation until 1547. When fuel is moved in the SPF Technical Specification (TS) 2.8(7) requires VA-66 to be in the filtered mode of operation. <br /><br /> The root cause of this event was determined to be poor communications. <br /><br /> Corrective actions include requiring on-coming operators to participate in the shift turnover and improvements to the fuel handling procedure.
2851994007 | Fort Calhoun | 10/07/1994 | 11/07/1994 | 9411150272 | <strong>Raw Water Pump Seal Water Supply Outside of Design Basis</strong><br /><i>Abstract:&nbsp;</i>The Potable Water (PW) storage tank provides the normal source of seal water for lubrication and cooling of Raw Water (RW) pump shaft bearings and packing. A backup source of seal water is available from the discharge of the RW pumps, and can be aligned to supply seal water via local manual valves. The RW pumps are classified as Critical Quality Element (CQE) equipment and the PW supply is classified as non-CQE equipment. <br /><br /> On October 7, 1994, the results of an evaluation, regarding whether RW pump seal water supply piping performs a safety related function, were presented to the Fort Calhoun Station Plant Review Committee (PRC). Based on this presentation, the PRC concluded that a reportable condition existed involving reliance of the RW pumps on a non-CQE seal water supply. <br /><br /> The root cause of this event was determined to be that the design process prior to initial plant start-up (in 1973) failed to adequately address the importance of seal water availability to RW pump operability.<br /><br /> Corrective action was taken to make the backup seal water supply available without operator action. The seal water supply configuration to the RW pumps will be modified, prior to the 1995 Refueling Outage, to resolve this issue.
2851994008 | Fort Calhoun | 11/08/1994 | 12/07/1994 | 9412130307 | <strong>Potential for Raw Water Pump Room Flooding Following a Heavy Load Drop</strong><br /><i>Abstract:&nbsp;</i>Fort Calhoun Station (FCS) Updated Safety Analysis Report (USAR) Section 14.24, 'Heavy Load Incident,' in part, discusses the hazards associated with postulated load drops involving the Intake Structure Crane, HE-5. This discussion addresses the potential effect on the Raw Water (RW) System of several scenarios involving a postulated drop of a 24,000 lb. Circulating Water pump motor from HE-5. Questions were raised regarding the existing Hazard Elimination Statements in that they did not appear to adequately address the possibility of flooding in the RW pump room as a result of a heavy load drop. Subsequent evaluation concluded that a heavy load drop in the Intake Structure could result in flooding of the RW pump room, with the potential to render the RW System inoperable. <br /><br /> The root cause of this event was determined to be a lack of depth in evaluation/review associated with the original load drop analysis. <br /><br /> A Danger Tag was placed to restrict the use of HE-5. Additional corrective actions will include completion of an Engineering Assistance Request to address the deficiency in the original heavy loads analysis for the Intake Structure and establishment of procedural guidance to appropriately control the use of HE-5.
2851994009 | Fort Calhoun | 11/08/1994 | 12/08/1994 | 9412140053 | <strong>Inappropriate Use of Auxiliary Building Crane Over Irradiated Fuel</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1994, Maintenance Work Order (MWO) 943168 was performed to repair Spent Fuel Pool (SFP) Filter/Vacuum AC-20. During the course of the job, the Auxiliary Building Crane (HE-2) was used to lift AC-20 from the SFP and subsequently to return it to the SFP. Following completion of the job, an individual familiar with the location of AC-20 and the location of irradiated fuel in the SFP, recognized that the use of HE-2 to lift AC-20 at this location violated Technical Specification 2.11(2). <br /><br /> The event was determined to have resulted from a combination of an inadequate pre-job briefing and inadequate training for Crane Supervisors. A contributing cause was inadequate procedural requirements on determining the location of irradiated fuel in the SFP. <br /><br /> Corrective actions include conveying management expectations regarding conduct of pre-job briefings, providing training to qualified Crane Supervisors and revising procedures associated with the use of HE-2.
2851994010 | Fort Calhoun | 11/14/1994 | 06/30/1995 | 9507060074 | <strong>Potential Accident Scenario Involving Loss of Control Room Air Conditioners</strong><br /><i>Abstract:&nbsp;</i>Potential accident scenarios were identified that could have resulted in inoperability of both Control Room Air Conditioning (CR/AC) units. The scenarios involved either a Large Break Loss of Coolant Accident (LBLOCA) or a Main Steam Line Break inside Potential accident scenarios were identified that could have resulted in inoperability of both Control Room Air Conditioning (CR/AC) units. The scenarios involved either a Large Break Loss of Coolant Accident (LBLOCA) or a Main Steam Line Break inside Containment (MSLB/IC). Evaluation indicated that under certain conditions, post-accident Component Cooling Water (CCW) temperature could have risen to a point at which the CR/AC unit Freon compressors would have shutdown, possibly followed by failure of rupture discs and release of the Freon from the units. Rising Control Room temperature could have subsequently hindered Operations personnel and possibly resulted in design temperatures being exceeded for safety-related electrical equipment in the Control Room cabinets. <br /><br /> Two root causes were identified. The first involved failure to specify a post-accident CCW temperature on the CR/AC unit procurement specification. The second involved reliance on an inappropriate methodology to establish a maximum post-accident CCW temperature.<br /><br /> A modification to the CR/AC units has been installed to address the potential impact of postulated post-accident CCW temperatures on the CR/AC units. In addition, administrative controls have been implemented to ensure that CCW temperatures will be maintained within acceptable limits in the event of a postulated accident.
2851994011 | Fort Calhoun | 12/28/1994 | 01/27/1995 | 9502010308 | <strong>Failure to Satisfy Surveillance Requirement for Steam Generator Level Check</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1994 at approximately 0800, a Control Room Operator failed to record steam generator level readings on the data sheet for Surveillance Test OP-ST-SHIFT-0001, 'Operations Technical Specification Required Shift Surveillance'. This resulted in a violation of Technical Specification 3.1, Table 3-1, Item 6.a, which requires that steam generator level instrumentation be checked on a frequency of once per shift, and that a comparison of indications from redundant channels be made.<br /><br /> The root cause of this event was determined to be inadequate review. Following an interruption in the performance of the surveillance, the operator failed to ensure that the surveillance was resumed where it had been interrupted. <br /><br /> Corrective actions will include training operations department personnel on this event, stressing the importance of attention to detail during the performance of routine activities.
2861994001 | Indian Point 3 | 01/28/1994 | 04/29/1994 | ML10049068 | <strong>Pressurizer Liquid Sampling Line Support Discrepancies Place the Plant Outside its Design Basis Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1994, with the plant in cold shutdown, a Maintenance Engineer identified valve and tubing support discrepancies at the sampling system line for sampling pressurizer liquid space. This event, which occurred prior to November 14, 1992, is a result of poor work practices and attitudes that previously existed. Stress analysis indicates that, in this condition, tubing stresses could have exceeded code requirements but would have maintained operability for the sampling system in a seismic event. Therefore, this event places Indian Point 3 outside its design basis. This event was caused by personnel error (inadequate work practices) during maintenance activities. The Authority used this event to further emphasize to station personnel the expectations regarding supervisory oversight, procedure adherence and proper work practices. Corrective action has been and continues to be taken to address the procedural adherence issue. The support discrepancies will be corrected and a walkdown will be conducted to determine the extent of condition.
2861994002 | Indian Point 3 | 02/15/1994 | 03/16/1994 | ML10049067 | <strong>Failure of RCS Overpressurization Trip Alarm To Annunciate, Due To Personnel Error, Places The Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1994, with the plant in a cold shutdown condition, Instrumentation and Control technicians issued Deviation Event Report 94-174 which identified the failure of the Reactor Coolant System Overpressurization Trip Train A alarm to annunciate during the performance of a surveillance test. The alarm can was determined to be miswired since the installation of modification MOD 85-3-033 ED in August 1987. The cause of the event was personnel error; inattention to detail when installing the modification. A contributing cause to the duration of the event was that the modification retest and the surveillance test were inadequate. Corrective actions include a review of surveillance tests required by Technical Specifications; and the review of each control room instrumentation rack, supervisory panel, and flight panel to ensure all terminations within these areas are in accordance with electrical termination specifications and regulations. Further review involving the details of the inadequate surveillance test is continuing and the results will be submitted in a separate LER.
2861994003 | Indian Point 3 | 02/18/1994 | 03/18/1994 | ML10049067 | <strong>Inadequate Surveillance Test, Due To Personnel Error, Places The Plant In A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1994, with the plant in a cold shutdown condition, Instrumentation and Control (I&C) department personnel determined that the surveillance test for the Overpressurization System (OPS) did not fulfill the channel calibration requirements of the technical specifications. As a result, the OPS alarm and logic trip functions were not tested as required. The cause of the event was personnel error - inattention to detail when writing the initial surveillance test and when preparing subsequent revisions. Corrective actions include revising and performing procedures, counseling personnel writing and revising I&C procedures, and ensuring surveillance tests are current and demonstrate operability.
2861994004 | Indian Point 3 | 03/09/1994 | 04/05/1994 | ML10049067 | <strong>Failure To Fulfill Channel Calibration Requirements, Due To Personnel Error, Places The Plant In A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1994, with the plant in a cold shutdown condition, Instrumentation and Controls Department personnel determined that surveillance tests for several systems did not fulfill the channel calibration requirements of the Technical Specifications. As a result, certain alarm functions were not tested as required. The cause of the event was personnel error, misjudgment due to inadequate work practices when writing the initial surveillance tests and subsequent revisions. In addition, approximately 55 procedures that meet Technical Specifications testing requirements in the body of their procedures, failed to include certain alarm functional checks in the equipment operability section of the surveillance tests. Corrective actions include: training, revising the additional surveillance tests to include alarm functional checks in the equipment operability criteria and revising surveillance tests to include steps required for testing alarm functions.
2861994005 | Indian Point 3 | 06/01/1994 | 07/29/1994 | ML10049069 | <strong>Central Control Room Heating, Ventilation and Air Conditioning System Outside Design Basis Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1994, at approximately 1130 hours with the reactor in cold shutdown, Nuclear Engineering and Design concluded that there was a Central Control Room (CCR) Heating, Ventilating and Air Conditioning (HVAC) system design deficiency. After loss of offsite power, the compressors for the CCR HVAC system air conditioning would not automatically restart upon restoration of power. This is outside the CCR HVAC design basis. This event was caused by a personnel error in the original design of the control circuit. Corrective action will be taken to modify the compressor control circuits to provide automatic restart capability. The extent of condition will be determined by a review of the CCR HVAC circuits for similar problems and an unavailability analysis of the CCR HVAC system.
2861994006 | Indian Point 3 | 06/07/1994 | 09/30/1994 | ML10049069 | <strong>The Central Control Room Ventilation System Is Outside of Design Basis Following A Single Electrical Failure Due To Personnel Error in Design</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1994, at approximately 0830 hours with the plant in a cold shutdown condition, a Nuclear Engineering and Design engineer determined that a single electrical failure would cause the Central Control Room outside air intake damper to the filters to fail closed, a condition subsequently determined not to be outside the plant design basis. During the evaluation of this event, a single electrical failure was determined to cause dampers to the filter booster fans and air conditioning units to close, a condition outside the design basis caused by personnel error of an indeterminate origin. The current Modification Control Manual and Design Control Manual provide assurance that this type of error will not occur again. An analysis was performed to determine the extent of condition and identified vulnerabilities are being evaluated. Corrective action to modify control circuits is underway.
2861994007 | Indian Point 3 | 04/26/1994 | 07/12/1994 | ML10049068 | <strong>Improper Stem Setting of Pressurizer PORV Degraded Operator Action Time to Mitigate a Low Temperature Over-Pressure Event Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1994, with the reactor in the cold shutdown condition, a Maintenance department engineer discovered an improper adjustment to the valve stems of Pressurizer Power Operated Relief Valves (PORVs), RC-PCV-455C and RC-PCV-456. This improper adjustment could have caused a condition outside of the design basis for the Overpressurization Protection System (OPS) and PORV nitrogen supply system. The event was caused by a failure to incorporate the required stem adjustment into the generic procedure used to service the PORVs. The stem adjustment was corrected on May 7, 1994. Planned corrective actions include development of a PORV specific maintenance procedure, review of generic maintenance procedures to determine which ones require component-specific instructions, and determination of the extent of condition with respect to other air operated valve dedicated gas supplies. In addition, the OPS component design bases and operating limits shall be re-evaluated and then updated if necessary.
2861994008 | Indian Point 3 | 07/28/1994 | 12/05/1994 | ML10049070 | <strong>31 Boric Acid Storage Tank Recirculation Valve Mis- adjusted Resulting In Potential Inability to Maintain a Technical Specification Required Boric Acid Inservice Flow Path</strong><br /><i>Abstract:&nbsp;</i>During the 31 Boric Acid Transfer Pump (BATP) performance evaluation test on May 4, 1994, a Performance engineer noted that throttling of the 31 Boric Acid Storage Tank (BAST) recirculation valve, CH-HCV-105, did not cause reduction of flow to the BAST. Further investigation revealed that the subject valve was approximately full open while the valve position indicator indicated the valve to be closed. This condition was attributed to an improper adjustment of the CH-HCV-105 valve stem. Improper adjustment of the BAST recirculation valve caused a degradation of the boration capability of the 31 BATP train contrary to Technical Specification section 3.2.B.4 which requires a boration path from the boric acid storage system. Corrective actions include re-adjustment of the subject valve, installation of new flow instrumentation, completion of a heat trace modification and an extent of condition review. Additionally, maintenance specific training improvements will be made. The associated surveillance test for 31 and 32 BATPs was revised to provide for flow trending.
2861994009 | Indian Point 3 | 08/28/1994 | 09/26/1994 | ML10049069 | <strong>The Central Control Room Ventilation System Is Outside Of Design Basis Because Of Inoperable Seismic Supports Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1994, at approximately 1330 hours with the reactor in cold shutdown at atmospheric pressure, Technical Services concluded that the seismic supports of the Central Control Room air conditioning units were inoperable, and made a four hour report because the Central Control Room (CCR) Heating Ventilating and Air Conditioning (HVAC) system (air conditioners) was outside design basis. The event was caused by personnel error, misjudgment by management by not properly assessing, over a number of years, the significance and priority of the material condition of the CCR HVAC system. Immediate action was taken to provide temporary supports. Corrective action will restore the seismic supports to their design basis condition, return the air conditioning system to a material condition that ensures reliable performance and implement an enhanced preventive maintenance program to maintain the material condition.
2861994010 | Indian Point 3 | 10/07/1994 | 11/07/1994 | 9411220180 | <strong>A Surveillance Test of the CO sub 2 Fire Protection System Resulted in a Condition Prohibited by Technical Specifications due to a Procedural Deficiency and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1994, at approximately 1500 hours, with the plant in cold shutdown, Technical Services concluded that at least two Emergency Diesel Generators were inoperable during a June 1992 surveillance test. During this event and seven prior surveillance tests, IP3 was in violation of Technical Specification 3.7.F.4. This event was caused by a procedural deficiency and personnel error. Corrective actions include correction of the surveillance test, a revision of the writers guide to require consideration and identification of system inoperability induced by surveillance test and counseling of plant personnel. These actions correct the deficiency and prevent recurrence. The extent of condition and corrective action that may be required are under evaluation. The effects on public health and safety were negligible.
2861994011 | Indian Point 3 | 10/19/1994 | 12/15/1994 | ML10049070 | <strong>A Failure to Maintain the Required Equivalent Vented Opening of 2.00 Square Inches in the Reactor Coolant System Placed the Plant in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1994, between 1305 hours and 2127 hours, and on October 22, 1994 between 1030 hours and 1140 hours, with the plant in the cold shutdown condition and the reactor coolant system (RCS) depressurized, the available RCS equivalent vented opening was less than 2.00 square inches. This condition was in violation of Technical Specification 3.1.A.8.b(1). This event was due to a failure to fully block open one Power Operated Relief Valve (PORV), RC-PCV-455C or RC-PCV-456, while the other PORV was being stroked opened and closed during testing. The initial Licensee Event Report (LER) 94-011-00 reported that PORV RC-PCV-456 was not fully blocked open, and subsequently it was concluded that both PORVs were not blocked fully open. The cause of this event was that the critical technical information regarding the necessity to block each PORV fully open was not included in the plant operating procedures. Corrective actions include installation of blocking devices to fully block open the PORVs, procedural revisions to provide guidance for maintaining an RCS equivalent opening of at least 2.00 square inches and to provide technical review of valve blocking devices, and completion of the Restart Action Plan to improve interdepartmental communication.
2861994012 | Indian Point 3 | 12/28/1994 | 01/18/1995 | ML10049070 | <strong>The Design And Evaluation Of Central Control Room Emergency Lighting Did Not Meet The Intent Of 10 CFR 50, Appendix R, Section III.J</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1994, with the plant in cold shutdown, a Fire Protection Engineer identified a condition at Indian Point 3 that could have resulted in a loss of normal and emergency lighting in the Central Control Room due to a fire in the Lower Cable Tunnel. The event was identified while addressing a design document open item tracked as part of the design basis consolidation (reconstitution) program. The cause was determined to be design criteria that did not adequately address the consequences of fire on the Central Control Room emergency lighting functions. than this event, has eliminated this concern for the Central Control Room. Corrective actions that have been or will be performed to prevent recurrence of this event include: upgrading the Fire Protection/Appendix R compliance procedure, preparing the Fire Protection Design Bases Document, evaluating other battery powered lights, training of design engineers on Appendix R compliance, and further assessment of the extent of condition. This event did not affect the health and safety of the public.
2871994001 | Oconee 3 | 03/01/1994 | 03/31/1994 | 9404110318 | <strong>Reactor Trip On False High Level Indication Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>At 1014:30 hours, March 1, 1994, Unit 3 tripped from 100% Full Power. All systems responded as expected. The response of Operators and automatic systems brought the unit to stable hot shutdown conditions. The initiating signal was an Anticipatory Reactor Trip on Turbine Trip due to a false emergency high level in a Moisture Separator/Reheater (MSR), even though there were no other high level indications or alarms. Troubleshooting personnel identified a defective mercury contact switch assembly in one of four MSR high level instruments. Root cause was Equipment Failure. The defective contact assembly was replaced prior to restart of the unit.
2871994002 | Oconee 3 | 08/10/1994 | 09/08/1994 | 9409150161 | <strong>Reactor Trip From Blown Control System Fuse Due To An Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1994, at 0426 hours, while operating at 100% full power, Unit 3 tripped as a result of a momentary loss of power to the Integrated Control System inverter, 3KI. Operators observed an overcooling of the Reactor Coolant System and also noted a diverging pressure trend between 3A and 3B Steam Generators (S/G) and suspected a leak or rupture of the 3B main Steam header. They isolated the 3B S/G, then noted that the Turbine Bypass Control valves (TBVs) were partially open and closed them. The open TBVs had caused the overcooling and depressurization of the S/Gs. The Unit was then stabilized at Hot Shutdown condition with decay heat removal via 3A S/G. The event was terminated when the 3B S/G was unisolated, refilled, and pressurized. The cause of the event was determined to be blown fuses on 3KI inverter, but the root cause of the blown fuses is unknown. Corrective actions included the continuation of troubleshooting the problems with the inverter and modification to the TBVs controls.
2871994003 | Oconee 3 | 08/12/1994 | 09/12/1994 | 9409200388 | <strong>Reactor Trip On Loss Of Main Feedwater Due To Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1994, Unit 3 was at approximately 42% full power and returning to full power operation at 3% per hour following a Unit trip. The 3B Main Feedwater (MFDWP) was supplying feedwater and the 3A MFDWP was being warmed in preparation for placing it in service. At 0447 hours, an anticipatory Reactor trip occurred due to the loss of the MFDWP that was in service. The response of the operators and automatic systems brought the unit to stable hot shutdown conditions. An investigation into the cause of the Unit 3 Reactor trip revealed that a gasket connection on the 3B MFDWP Turbine, between the relay valve and the emergency governor lockout valve, had failed resulting in low hydraulic oil pressure. This coincident with low discharge pressure on the 3A MFDWP resulted in the Reactor trip. The root cause is a component failure due to aging. Corrective actions include replacing the valve gasket, revising the maintenance procedure, and contacting the vendor for other operating experience associated with this type equipment.
2891994001 | Three Mile Island 1 | 03/07/1994 | 08/18/1994 | 9409060180 | <strong>Boric Acid Degradation Of Pressurizer Spray Valve (RC-V1) Fasteners</strong><br /><i>Abstract:&nbsp;</i>BORIC ACID DEGRADATION OF PRESSURIZER SPRAY VALVE (RC-V1) FASTENERS DUE TO FAILURE TO CONSIDER PRE-LOAD WHEN INCREASING MOTOR OPERATOR TORQUE <br /><br /> On March 7, 1994, TMI-1 was operating at reduced power having located and isolated a body-to-bonnet leak from the pressurizer spray valve (RC-V1). RC-V1 was declared inoperable. Because of boric acid degradation exhibited by RC-V1 fasteners, this event was found to be reportable in accordance with 10CFR50.72(b)(1)(ii) and 10CFR50.73(a)(2)(ii). With RC-V1 isolated, operation was permitted while preparations were made to shut down and repair RC-V1. The plant was shut down on March 17, 1994 and the valve repaired. The root cause was failure to consider the effects on fastener pre-load when the motor operator torque settings were increased. There were no safety consequences. RC-V1 was repaired and other bolted connections were inspected. Corrective actions include an evaluation of corrosion resistant fastener materials, programmatic improvements, and training.
2891994002 | Three Mile Island 1 | 03/17/1994 | 04/18/1994 | 9404250001 | <strong>Control Rod Drop Times Exceed TS Section 4.7.1.1 Limits</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1994 while TMI-1 was in a hot shutdown condition for the purpose of repairing the pressurizer spray valve, control rod drop time testing was performed in accordance with Surveillance Procedure 1303-11.1. Twelve control rods [AB/AA] exceeded the trip insertion time limit, of 1.66 seconds from fully withdrawn to 3/4 insertion, designated by the TMI-1 Technical Specifications. The control rod drop time data was evaluated with BW Nuclear Technologies and it was concluded that the longer drop times were caused by blockage of the thermal barrier check valves in combination with reduced clearance in the thermal guide bushing caused by crud deposition resulting from the low pH conditions in the reactor coolant system.<br /><br /> Past experience had shown that this blockage could be reduced by subsequent control rod drops. The control rods were dropped until the drop times improved and were within the specified limit. In addition, the lithium concentration in the reactor coolant system was increased to raise pH to reduce the rate of corrosion. <br /><br /> The event was reported per 10CFR50.72(b)(2)(i).
2891994003 | Three Mile Island 1 | 05/23/1994 | 06/20/1994 | 9406270349 | <strong>Inadvertant Level Reduction Of The NaOH Tank Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>TMI-1 was operating at 100% power. On May 23, 1994 during the performance of prerequisites for Technical Specification (TS) Surveillance Procedure 1303-5.1, an Auxiliary Operator failed to follow established operator work practices and incorrectly reduced the level of the Sodium Hydroxide Tank (NaOH) so that the Borated Water Storage Tank (BWST)/NaOH tank differential levels were beyond the required TS limit for approximately 2 hours. The root cause of this event was personnel error. TS 3.3.1.3.b requires that the NAOH tank be maintained at 8 ft. +/- 6 inches lower than the BWST as measured by the BWST/NaOH tank differential pressure indicator. This condition is reportable under 50.73.a.2.i.B. Having the NaOH tank outside of the required specification for approximately 2 hours had low safety significance since iodine removal enhancement was only marginally reduced in this condition and the probability of having a design basis accident during this short time period was very low. Management will review work practice requirements with all operators and ensure training programs contain proper emphasis. The applicable administrative requirements and computer alarms will be reviewed to determine need for changes.
2891994004 | Three Mile Island 1 | 06/01/1994 | 06/24/1994 | 9406300088 | <strong>Three Control Rod Drop Times Exceed TS Section 4.7.1.1 Limits</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1994 while in a hot shutdown condition control rod drop time testing was performed in accordance with Surveillance Procedure 1303-11.1. Three control rods [AB/AA] exceeded the trip insertion time limit of 1.66 seconds from fully withdrawn to 3/4 insertion as specified in the TMI-I Technical Specifications. The reactor was placed in cold shutdown and four CRDMs and their thermal barriers were removed. Inspection showed deposits in the area of the thermal barrier ball check valves that restricted movement of the balls and in the lead screw guide bushing. These results confirm the previously postulated deposits (LER 94-002) as the cause of the slow drop times.<br /><br /> The four thermal barriers were replaced with new thermal barriers which have larger clearances in the ball check valves and the drop times for these rods were verified to be restored to less than 1.66 seconds.<br /><br /> The event was reported per 10 CFR 50.72(b)(2)(i).
2891994005 | Three Mile Island 1 | 06/09/1994 | 07/08/1994 | 9407180007 | <strong>Control Rod Overlap Between Groups 6 And 7 Does Not Meet TS 3.5.2.5.A Limit</strong><br /><i>Abstract:&nbsp;</i>On June 9, 1994 the plant was in power operations conditions at low power (<20% full power) and was commencing a power escalation in accordance with Operating Procedure 1102-2 'Plant Startup'. <br /><br /> At approximately 1745, the Primary Control Room Operator (CRO) noted an irregularity in the overlap between the average positions of control rod [AA/ROD] groups 6 and 7. This was later verified by evaluation of data. After reviewing the event, the cause was attributed to an intermitent failure of a control rod drive system programmer motor [AA/MO]. The failure resulted in Group 7 rods lagging Group 6 rods in excess of the value permitted by TS 3.5.2.5.a (25% q5%). The event ended at 1807 when the overlap was restored to greater than 20%.<br /><br /> Corrective actions will include replacement of the entire Group 7 programmer assembly of which the faulty programmer motor is a part.
2891994006 | Three Mile Island 1 | 10/02/1994 | 10/30/1994 | 9411070203 | <strong>Inadvertent Actuation Of EG-Y-1B Due To Personnel Error During Preventive Maintenance</strong><br /><i>Abstract:&nbsp;</i>At 1637 on October 2, 1994, the plant was operating at 100% power and preventive maintenance was being performed on the 1E 4160 volt bus metering accordance with Procedure E-55, 'Switchgear and Main Generator/Transducer Calibration.' <br /><br /> While lifting a current transformer lead within the bus breaker 1SB-E2 cubicle to configure the 'A' phase ammeter for calibration, the Electricians unknowingly opened the common ground for protective circuitry. closed feeder breaker and the subsequent undervoltage condition on the 1E 4160 volt bus automatically started the emergency diesel generator (EG-Y-1B). The EG-Y-1B breaker could not close on the 1E 4160 volt bus to restore power because the overcurrent relay was tripped and locked out. <br /><br /> At 1640, the lead was replaced, the 86B/E relay was reset and the EG-Y-1B breaker was automatically closed to re-power the 1E bus. Plant emergency and abnormal condition procedures were implemented to restart required plant equipment. After the 1E bus was transferred back to the normal power supply, the diesel was secured.<br /><br /> The automatic start of EG-Y-1B is reportable under 10 CFR 50.73(a)(2)(iv).
2931994001 | Pilgrim | 01/04/1994 | 02/03/1994 | 9402100028 | <strong>High Pressure Coolant Injection System Inoperable Due to Unplanned Isolation During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1994, at 1834 hours, the High Pressure Coolant Injection (HPCI) System became inoperable and a seven day Technical Specification (3.5.C.2) Limiting Condition for Operation (LCO) was entered. The HPCI System became inoperable because the HPCI turbine steam supply isolation valves closed during a scheduled calibration test of related Analog Trip System (ATS) units. The HPCI System was declared operable and returned to normal standby service at 0326 hours on January 5, 1994. Applicable systems were verified operable during the period the HPCI System was inoperable. <br /><br /> The cause was a false low Reactor Vessel pressure signal. The cause of the signal was investigated but could not be determined with certainty. The investigation concluded the most probable cause was human performance. Corrective action taken included feedback to Instrumentation & Control (I&C) technicians and supervisors regarding this event. Corrective action planned includes procedure improvement and I&C technician training. <br /><br /> The event occurred while at 100 percent reactor power. position. The Reactor Vessel (RV) pressure was 1029 psig with the RV water temperature at 545 degrees Fahrenheit. The event posed no threat to the public health and safety.
2931994002 | Pilgrim | 03/09/1994 | 04/08/1994 | 9404140193 | <strong>High Pressure Coolant Injection System Inoperable Due to Inoperable Motor Operated Valve</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1994, at 1035 hours, Operations personnel declared the High Pressure Coolant Injection (HPCI) System inoperable based on the inoperability of a HPCI motor operated valve that could not be opened after being closed for a surveillance test. <br /><br /> Operations discovered the problem during the performance of a monthly surveillance procedure. The operators closed the valve remotely from the main control room and received a valve operator motor electrical overload alarm. Upon investigation the valve operator motor was found hot to the touch, the valve's breaker was found tripped open, and there was a burnt smell in the vicinity. The motor operator torque switch drive pinion gear roll pin had failed due to the pin design. Suspected causes contributing to the roll pin failure include hardened grease in the motor operator spring pack and the magnitude of the forces on the valve starting and stopping transients . Either cause could result in higher force on the roll pin. The valve is currently maintained open with a temporary modification to allow the HPCI System to be made operable. The HPCI System was tested satisfactorily and declared operable on March 10, 1994. Corrective action planned includes installation of a torque switch with an improved design and a new spring pack resistant to grease buildup into the valve. Other valves potentially susceptible to torque switch drive pinion gear roll pin failure have been identified and evaluated for operability with satisfactory results. <br /><br /> The event was discovered with reactor power at 100 percent and the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1030 psig with the reactor vessel temperature at approximately 550 degrees Fahrenheit.
2931994003 | Pilgrim | 04/27/1994 | 05/26/1994 | 9406080138 | <strong>False Low Reactor Vessel Water Level Signal While Shut Down During Control Rod Drive System Venting</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1994, at 1410 hours, a false low reactor vessel water level signal occurred while shut down. The trip signal resulted in designed automatic responses that included a full scram signal, closing of applicable Primary Containment System isolation valves that were open, closing of the Secondary Containment System ventilation dampers and start of the Standby Gas Treatment System. The affected systems were returned to normal service by 1427 hours on April 27, 1994. The event occurred while venting a portion of the Reference Leg Backfill System as part of returning the Control Rod Drive System to service following scram solenoid pilot valve diaphragm replacements.<br /><br /> The cause of the false low water level signal was a deficiency in a procedure being used for venting and filling the Control Rod Drive System charging water header. Corrective action taken included filling, venting and repressurizing the CRD System charging water header. Corrective action planned includes revisions to the related vent and fill procedures. <br /><br /> The event occurred while shut down with the reactor mode switch in the REFUEL position for prestartup testing. The Reactor Vessel (RV) pressure was zero psig with the RV water temperature at approximately 135 degrees Fahrenheit. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv). The event posed no threat to the public health and safety.
2931994004 | Pilgrim | 08/03/1994 | 12/29/1994 | 9501040103 | <strong>Automatic Closing of the Reactor Core Isolation Cooling System Turbine Steam Supply Isolation Valves Due to High Steam Flow Signal During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On August 3, 1994, at 1122 hours, an automatic Primary Containment Isolation Control System (PCIS) group 5 actuation occurred during performance of the Reactor Core Isolation Cooling (RCIC) System quarterly surveillance test. turbine steam supply isolation valves. This caused the RCIC system to become inoperable. The isolation resulted from a high steam flow isolation signal. Investigation revealed the direct cause for the isolation signal was the governor control valve failed to respond to the control system demand due to valve binding. Further investigation into the cause of the control valve binding determined the fulcrum dowel pins were not properly aligned. Subsequent investigation determined the maintenance procedure did not provide sufficient guidance regarding alignment of the dowel pins. Utilizing guidance provided in the vendor technical manual, the valve was rebuilt and properly aligned. The maintenance procedure will be revised to included adequate guidance for dowel pin alignment. During post work testing on August 5, 1994, the turbine had been running for approximately fifteen (15) minutes when the turbine speed began to oscillate. governor end bearing cover, oil level on the coupling end bearing housing dropped below the sight glass level and oil was observed on the skid. The turbine was manually tripped at this time to investigate the cause of these problems. The cause for the oil level change was determined to be due to air becoming entrained in the oil. Vents were added to the oil sump and system oil pressure was reduced to correct the problem. This event occurred during plant operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The Reactor Vessel (RV) pressure was approximately 1030 psig with RV temperature at saturation. The RCIC System was returned to operable status on August 12, 1994. The High Pressure Coolant Injection System was operable during the period the RCIC was inoperable.
2931994005 | Pilgrim | 08/29/1994 | 09/11/1996 | 9609250125 | <strong>Automatic Scram Resulting from load Rejection at 100 Percent Power</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1994, at 0732 hours, an automatic scram occurred while at 100 percent reactor power. The scram was the result of a load rejection that was automatically initiated by a Main Generator faulted condition. Responses included automatic transfer of the plant's auxiliary power system and the brief, automatic opening of three of the Main Steam relief valves for pressure relief. The Reactor Core Isolation Cooling System was operated manually for Reactor Vessel level control for approximately three minutes. Two in-series secondary containment dampers did not fully close (i.e., approximately 90-95 percent closed) as designed but the secondary containment design basis was evaluated as being met with the dampers in the as-found position. <br /><br /> The cause of the main generator fault was the partial blockage of cooling water through one of the generator stator bars that was caused by foreign material, i.e, pieces of gasket, inadvertently introduced into the main generator stator cooling water system oulet header. Corrective action taken included completely rewinding the generator stator, completely rewinding the generator rotor, and inspecting and flushing the generator stator cooling water system. The cause of the two dampers not fully closing was an accumulation of damper lubricant and dirt along the dampers' side seals and a buildup of degraded lubrication in the dampers' actuators. Corrective action taken included cleaning the dampers, modifying the preventive maintenance program to inspect the secondary containment dampers more frequently, and to periodically rebuild the dampers' actuators. The event posed no threat to public health and safety.
2931994006 | Pilgrim | 09/17/1994 | 10/21/1994 | 9411010236 | <strong>Unplanned Actuation of a Portion of Core Cooling Systems Logic Circuitry During Preventive Maintenance while Shut Down</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1994, at 0624 hours, an unplanned actuation of a portion of the Channel 'B' Core Standby Cooling Systems logic circuitry occurred during a first-time preventive maintenance activity while shut down in a mid-cycle outage. The activity included the re-energizing of one solid state Analog Trip System cabinet while one of its two power supplies was removed for testing. The event included an automatic initiation of the Residual Heat Removal System for the Low Pressure Coolant Injection mode, automatic start of an emergency diesel generator, and initiation of a portion of diesel generator load shedding logic circuitry. The event resulted in a brief interruption of the RHR System that was operating in the shutdown cooling mode (non-safety related) at the time of the event. Subsequent action taken included returning the RHR System to the shutdown cooling mode of operation. The RV water temperature increase that occurred was negligible. The redundant cabinet was not affected. <br /><br /> The root cause was inadequate plant impact reviews for the activity being performed. The plant impact reviews performed used elementary wiring diagrams instead of more detailed internal wiring diagrams.<br /><br /> Significant corrective action planned includes training, procedure changes to require engineering review prior to the performance of a first-time preventive maintenance activity and a possible change to the cabinets' negative ground bus design. <br /><br /> The event posed no threat to the health and safety of the public.
2931994007 | Pilgrim | 12/28/1994 | 01/27/1995 | 9502070145 | <strong>Primary Containment Pressure Boundary Degraded due to Uninstalled Instrument Plug</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1994, at approximately 1040 hours, a plug for the Drywell-to-Torus atmosphere differential pressure transmitter that is part of the Torus atmosphere portion of the Primary Containment System pressure boundary was discovered to be not installed during a calibration of the transmitter while at 100 percent power. Immediate action taken included the installation of a plug for the transmitter and the senior utility shift Licensed Operator was notified of the discovery. A 24 hour limiting condition for operation was entered and later terminated at 1646 hours on December 28, 1994. Preliminary engineering evaluation concluded potential PCS leakage due to the uninstalled plug at the PCS integrated leak rate test pressure of 45 psi could have exceeded 1 (one) percent. The NRC Operations Center was notified of the condition at 1756 hours on December 28, 1994. <br /><br /> The root cause was utility non-licensed I&C Technician and Supervisor error during the previous calibration of the transmitter on November 22, 1994. Contributing factors included deficiencies in the calibration procedure, physical location of the plug, and transmitter design and installation (lack of calibration valves). Corrective action taken included Maintenance Manager direction to Maintenance personnel regarding procedure signoffs and verification, Senior Management briefings to Maintenance personnel regarding the uninstalled plug and management expectations, strengthening the calibration procedure and tagging of all instruments that are part of the Primary Containment pressure boundary. Corrective action planned includes the installation of isolation valves to selected instruments. <br /><br /> Evaluation of the potential radiological consequences of the uninstalled plug concluded 10 CFR Part 100 and 10 CFR 50 Appendix A (GDC 19) exposure guidelines would not have been exceeded if a design basis accident had occurred while the plug was not installed.
2951994001 | Zion 1 | 02/19/1994 | 03/21/1994 | 9403250193 | <strong>Insufficient Charging Flow Through Cold Leg Injection Due to Mispositioned Throttle Valves.</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1994, during the performance of Technical Staff Surveillance (TSS) 15.6.84, 'Charging and Safety Injection Check Valve Verification Test'. it was discovered that the flow through the cold leg injection piping did not meet the requirements of Technical Specification 4.8.4.B. Investigation into this event revealed that throttle valves 1SIB810A, 1SI8810B, 1SI8810C and 1SI8810D [BQ] had changed position after being set during flow balance testing on June 21, 1992. Flow balancing was being performed as required by Technical Specifications as a result of a modification to the Chemical and Volume Control System [CB].The cause of this low flow condition was procedural deficiency.<br /><br /> An evaluation was performed by the Nuclear Fuel Services Department to determine if the decrease in flow would have an adverse effect on the LOCA analysis. The results of this calculation showed that there was no increase in the significance of a LOCA to the health and safety of the public. <br /><br /> Corrective actions include rebalancing injection line flows and amending TSS 15.6.84 to include verification of injection flow subsequent to the installation of the Mechanical Restraints.
2951994002 | Zion 1, Zion 2 | 03/10/1994 | 04/08/1994 | 9404120089 | <strong>Auxiliary Building Ventilation Panel OLP17 Found to be Insufficiently Seismically Mounted.</strong><br /><i>Abstract:&nbsp;</i>On 03/10/94, a seismic evaluation was performed on auxiliary building ventilation panel OLP17, that indicated that OLP17 was not sufficiently seismically mounted. This calculation was performed as a result of information gathered during a walkdown of that panel. This walkdown was conducted while investigating the seismic qualification of an instrument mounted in OLP17. <br /><br /> The cause of this event is the lack of implementation of original design criteria. This event had minimal safety significance. <br /><br /> Corrective actions include implementing a design change on 03/13/94 to seismically mount OLP17, initiating design changes on three other panels to bring them into compliance with the original design criteria, ensuring all other HVAC panels are adequately supported, and implementing the Seismic Qualification Utility Group (SQUG) Program to address the mounting of designated equipment throughout the plant.
2951994003 | Zion 1, Zion 2 | 03/23/1994 | 04/22/1994 | 9404260376 | <strong>Containment Pressure Sensing Lines Were Inadvertently Capped During Containment Close Out</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1994 at 1754, the Operating Department was attempting to vent containment. Pressure indications were not lowering, so a Shift Foreman was dispatched to investigate. He found that the sensing lines on all of the safety related containment pressure transmitters were capped off inside containment. <br /><br /> The cause of this event was management/QA deficiency. Containment Penetrations inside containment are not labeled. <br /><br /> As a result of the inoperability of these instruments, there was not an accurate indication of containment pressure in the control room and the following automatic actuation functions of Engineered Safeguard Features, (ESF) were also inoperable: Safety Injection on a Containment High Pressure Signal at 4.5 psig. Containment Spray Initiation (CS), Phase B Containment Isolation and Main Steam Isolation Valve (MSIV) Isolation on a containment high high pressure signal at 23 psig. Updated Final Safety Analysis Report (UFSAR) transients which generate a containment pressure increase were evaluated to identify the safety significance of this event. Specifically, the Main Steam Line Break (MSLB) and Loss of Coolant Accident (LOCA) were reviewed and determined not to have been adversely affected. <br /><br /> Immediate corrective actions included removing the pipe caps that were found and verifying that lines required to be open to containment pressure for both units were open. Additional corrective actions will include labeling penetrations inside containment for both units, changing GOP-0, Checklist G, 'Containment Closeout,' to verify penetrations are open before plant heatup, and incorporating lessons learned from this event.
2951994004 | Zion 1, Zion 2 | 03/26/1994 | 06/24/1994 | 9407010064 | <strong>Defeated Safeguards Actuation Signal Due to Lifted Lead on Two Motor Operated Valves</strong><br /><i>Abstract:&nbsp;</i>On 03/26/94, at 1245 during the performance of Technical Staff Surveillance (TSS) 15.6.35. 'Manual Actuation of the Safety Injection and Safe Shutdown Systems and Diesel Generator Loading Test', on Train A, 1MOV-VC112D, 'Refueling Water Storage Tank (RWST) to Charging [CB] Pump Suction Isolation Valve' filed to open. Troubleshooting subsequently determined that 1MOV-VC112D had two lifted leads. Further investigation revealed that 1MOV-VC112E also had two lifted leads. This removed the ability for the Charging Pumps to take automatic suction from the RWST.<br /><br /> The cause of the 1MOV-VC112D event was personnel error, and the cause of the 1MOV-VC112E event was management deficiency. Nuclear Fuel Services determined that the safety significance of this event was minimal.<br /><br /> Corrective actions include verifying the operability of the other MOVs with safeguards actuation signals, counselling the individuals involved, changing EM procedures with jumper/lifted lead logsheets, and establishing standards for package documentation.
2951994005 | Zion 1, Zion 2 | 04/03/1994 | 01/16/1998 | 9801210070 | <strong>Unit 1 Main Reactor Trip and Subsequent Start of 1A Auxiliary Feedwater Pump Following a Generator Fire and Isophase Bus Duct Fault</strong><br /><i>Abstract:&nbsp;</i>On 04/03/94, at 0430, Unit 1 was synchronized to the electrical distribution system following refueling outage Z1R13. At 0618, a loud noise was heard in the control room, and a subsequent generator trip and reactor trip occurred. At 0619, operating personnel reported that a fire was emanating from the main generator lead box. The Generating Site Emergency Plan (GSEP) was activated and the appropriate notifications were made. At 0905, the fire was extinguished and the GSEP was terminated. At 1456, during isolation of the main generator, incorrect fuses were pulled creating a two of four reactor coolant pump bus undervoltage signal and the 1A turbine driven auxiliary feedwater (AFW) pump autostarted. The fuses were reinstalled and the 1A AFW pump was secured. <br /><br /> The cause of the main generator fire was the inner ceramic surface inside the main generator C phase bushing had been contaminated with an oily substance during initial manufacturing. The cause of the 1A AFW pump autostart was an inadequate out of service. All reactor protection, engineered safeguards, and auxiliary power systems functioned normally throughout this event. <br /><br /> Corrective actions were replacing the Unit 1 west main transformer, inspecting and repairing the Unit 1 main generator and inspecting the Unit 2 main generator. <br /><br /> This supplementary report provides generator failure information as committed to in the original report.
2951994006 | Zion 1, Zion 2 | 05/19/1994 | 06/16/1994 | 9406210361 | <strong>Missed Surveillance on Containment Pressure High High Circuitry Because of an Overlap Deficiency in Safeguards Testing.</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1994, System Engineering became aware that a overlap testing deficiency existed for Containment Pressure High High (CPHH) [JE] circuitry. The section of untested circuitry consisted of wiring and fuses between the Eagle 21 output and the Safeguards relay for CPHH. This problem was found to be isolated to the CPHH channels, and did not exist prior to the Eagle 21 modification.<br /><br /> The cause of this event is attributed to inadequate modification design review. The safety significance of this event is minimal, since existing emergency procedures provide direction for manual containment spray in the event that the automatic actuation fails. The immediate corrective action for this event was to test the circuitry by manually tripping the channel from Eagle 21, and verifying that the CPHH relay energizes.
2951994007 | Zion 1, Zion 2 | 06/08/1994 | 01/09/1995 | 9501190211 | <strong>Failure to Perform Type C Leak Rate Testing on 1(2)MOV- CC685 per Technical Specification 3.9</strong><br /><i>Abstract:&nbsp;</i>In June 1994, during a review of the requirement of Technical Specification 3.9 for containment isolation valves 1(2)MOV-CC685, the system engineer questioned the adequacy of the testing of these valves. Further review and discussion with the Assistant System Engineering Supervisor determined that Zion Station was not in compliance with the testing requirements for 1(2)MOV-CC685.<br /><br /> The cause of this event was Management Deficiency. Several deficiencies in the implementation of the modification process resulted in the improper implementation of testing requirements for 1(2)MOV-CC685. The safety significance of this event was minimal. <br /><br /> Corrective actions include documenting modification approval, counselling the System Engineering individuals involved in the review and approval of the initial modification test, formalizing turnovers to new system engineers, reviewing this event with Engineering personnel, and ensuring that testing of 1(2)MOV-CC685 is completed following the installation of the modification resolving Generic Letter 89-10 concerns.
2951994008 | Zion 1 | 06/10/1994 | 07/08/1994 | 9407150140 | <strong>Failure of the 1A Auxiliary Feedwater Pump Discharge Check Valve 1FW0031 Due to Corrosion Causing Both 1B and 1C Motor-Driven Auxiliary Feedwater Pumps to Become Inoperable.</strong><br /><i>Abstract:&nbsp;</i>On Friday, June 10, 1994, at 0755 hours, during restoration of Periodic Test PT-7A-ST, 'Auxiliary Feedwater Pump A System Checks and Tests, ' the Operating Department discovered the 1A Auxiliary Feedwater [BA] Pump was spinning backwards with one of the motor driven pumps operating. The operator determined the 1A Pump discharge check valve, 1FW0031, had failed in the open position allowing backflow through the pump. The check valve was disassembled, inspected, and repaired with new internal parts. The 1A AFW pump and check valve 1FW0031 were tested and returned to service on Sunday, June 12, 1994. The cause of the event was component failure. The valve failed in the open position due to corrosion material trapped in the space between the valve body and valve plug. The failure was within the design basis of the unit and safety was not adversely affected. Corrective actions include repairing the 1FW0031 check valve, verifying all Auxiliary Feedwater Pumps and associated check valves function properly, and further investigation of the source of the corrosion material.
2951994009 | Zion 1, Zion 2 | 06/22/1994 | 07/19/1994 | 9407250140 | <strong>Missed Technical Specification Action Statement on the Control Room SPING Radiation Monitor 0RIA-PR29</strong><br /><i>Abstract:&nbsp;</i>At approximately 1930 on 06-22-94 during the performance of Periodic Test (PT) 0 Appendix X, 'Auxiliary Building Operator Rounds', an equipment attendant noticed the blue alert beacon flashing on top of the control room system particulate-iodine-noble gas (SPING) radiation monitor (0RIA-PR29) field unit. It was determined that 0RIA-PR29 had been in the external fail mode from 1356 to 1945 due to the blower for the radiation monitor being de-energized. Technical Specification 3.14 requires that within 2 hours of an inoperable monitor channel on 0RIA-PR29 the control room ventilation be placed in the recirculation mode. This surveillance requirement was not met as the monitor remained in a failed condition for approximately 6 hours undetected. <br /><br /> The cause of the blower being de-energized is unknown. The cause of the 'external fail' alarm not being immediately recognized by the unit operator is an equipment design deficiency. The safety significance of this event was minimal. <br /><br /> Corrective actions include investigating the possibility of modifying the SPING alarms to facilitate acknowledgement by the unit operator.
2951994010 | Zion 1, Zion 2 | 07/02/1994 | 09/18/1997 | 9709240313 | <strong>Unit 1 Reactor Trip Due to a Generator/Bus Duct Fire</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1994, at approximately 1144 hours, a firewatch contacted the control room and reported smoke on the Unit 1 turbine deck between the generator and the exciter. The Shift Engineer confirmed that all three bus duct phases were on fire and the Station fire alarm was initiated. A unit shutdown of 5% per minute was initiated. At approximately 1152 hours the fire brigade had completed discharging portable CO sub 2 units on the fire and was in the process of discharging the first dry chemical unit on the fire when the Unit 1 Reactor tripped. The control room entered Emergency Operating Procedure E-0, "Reactor Trip or Safety Injection". All systems functioned as designed and no abnormalities were noted in responding to the reactor trip other than control rod M-8 did not indicate fully inserted. <br /><br /> The cause of the reactor trip most likely was due to ionization of the dry chemical from fire fighting efforts resulting in a main generator neutral ground trip. The cause of the bus duct fire was most likely inadequate design and vendor recommendations which did not ensure a sufficient connection during operation. The bus duct jumper cable connections, as designed, use threaded stainless steel inserts into the aluminum bus duct. Some of these connections loosened, apparently from the vibration and temperature changes of unit operation despite being tightened to vendor recommendations. The conductivity of the loosened cables decreased increasing the current flow in the other cables, causing cable insulation to overheat and ignite. Corrective actions include developing guidelines for improved installation with a revised design. <br /><br /> This supplemental report provides additional information concerning the root cause and corrective actions for the event.
2951994011 | Zion 1, Zion 2 | 07/14/1994 | 08/12/1994 | 9408170208 | <strong>Violation of the 10CFR50 Appendix R Analysis Separation Criteria in Fire Zone 18.6.A-1</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1994 while preparing Exempt Change (EC), No. E22-0-93-255 (Work Request Z32800) to replace Thermo-Lag fire wrap with an approved material for a conduit in Fire Zone 18.6.A-1, it was discovered that an adjacent conduit, which is not fire wrapped, or part of the EC scope, created a discrepancy in the 10CFR50, Appendix R analysis currently on record. This discovery indicates that a failure scenario exists that could render the 0 Emergency Diesel Generator (EDG) inoperable for both units, and disable both the 1A and 1B centrifugal charging pumps. This means that the necessary equipment for reaching hot shutdown would not be available in the event of a fire in Zone 18.6.A-1, concurrent with a loss of offsite power. <br /><br /> The cause of this event is management deficiency. The engineering review that was performed for the original 10CFR50, Appendix R analysis did not realize that the 1B Cent. Charging Pump could be affected by a Unit 2 cable. <br /><br /> The corrective actions include verifying that the existing continuous fire watch was still in place, and ensuring that no other 10CFR50, Appendix R discrepancies on common unit cables for the 0 EDG existed.
2951994012 | Zion 1, Zion 2 | 07/26/1994 | 08/22/1994 | 9408290142 | <strong>Missed Action Statement on ORT-PR07, Component Cooling Heat Exchanger Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1994 with Unit 1 in Mode 5, Cold Shutdown, the 'O' Component Cooling (CC) [CC] Heat Exchanger was taken Out-of-Service (OOS) for System Engineering to investigate for leaks. When Operations isolated the CC heat exchanger, the process flow to ORT-PR07. Component Cooling Heat Exchanger Radiation Monitor, was isolated. Technical Specification (Tech Spec) Table 3.14-1 requires a shiftly grab sample to be obtained if the monitor is inoperable. When the ORT-PR07 went into instrument fail, no action was taken. At approximately 2045 hours, Control Room personnel discovered that ORT-PR07 was in instrument fail, and that the first Tech Spec required grab sample was missed at 1540 hours. The Licensed Shift Supervisor initiated the appropriate paperwork to begin the grab sample surveillances. <br /><br /> The cause of this event was personnel error. Licensed Operators failed to recognize that ORT-PR07 would be rendered inoperable, and failed to take action when ORT-PR07 went into instrument fail. Contributing to this event was a incomplete procedure. Corrective actions include determining the appropriate actions for the personnel involved, and revising the appropriate procedures. ler
2951994013 | Zion 1 | 07/21/1994 | 08/22/1994 | 9408290115 | <strong>Missed Action Statement on 1RT-PR07B, Class I Pipe Tunnel Iodine Radiation Monitor.</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1994 the Instrument Maintenance (IM) Department Technicians performed a channel calibration on 1RT-PR07B, 'Class I Pipe Tunnel Iodine Monitor', which renders 1RT-PR07B inoperable. Technical Specification (Tech Spec) 3.14.1.A requires the Class I Pipe Tunnel and Fuel Building Exhaust ventilation systems to be diverted through the Charcoal Filters whenever 1(2)RT-PR07A or 1(2)RT-PR07B are inoperable. During the calibration, the ventilation did not remain diverted as required by the Tech Specs. <br /><br /> The cause of the event was Management Deficiency. The safety significance of this event was minimal. Corrective Actions include changing procedures to ensure that the ventilation system remains diverted through the charcoal filters during the time that the radiation monitor is inoperable.
2951994014 | Zion 1, Zion 2 | 09/07/1994 | 10/07/1994 | 9410130337 | <strong>Failure to Perform an Off-Site Review of a 10CFR50.59 Safety Evaluation</strong><br /><i>Abstract:&nbsp;</i>On 09/07/94 it was determined that a 10CFR50.59 safety evaluation approved on 01/21/94 to place the Containment Spray (CS) diesel oil storage tank out of service was not transmitted to the corporate off- site Safety Review Group for an independent review. This is in violation of Zion Station Technical Specification 6.1.7.A.1.a. <br /><br /> This event was caused by a management deficiency. Administrative controls existed to ensure that all 10CFR50.59 safety evaluations were reviewed by the corporate off-site Safety Review Group, however, the administrative controls were not implemented properly. <br /><br /> Safety evaluation 50.59/0010/94 was reviewed by the off-site Safety Review Group and it was determined that no unreviewed safety condition existed. Therefore, this event has no safety significance. <br /><br /> Corrective actions include submitting the safety evaluation to off-site review, correctly implementing the established administrative controls, ensuring that the completion of all safety evaluations are adequately tracked and performing a periodic review to ensure that off-site reviews are performed in compliance with the Technical Specifications.
2951994015 | Zion 1, Zion 2 | 09/26/1994 | 10/26/1994 | 9411010174 | <strong>Engineered Safeguards Feature Actuation of the OC Component Water Pump</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1994, at approximately 1100, the Operating Department was performing Periodic Test (PT) 10-3, 'Containment Isolation Phase B Testing'. During the performance of the test restoration section, the OC Component Cooling Water (CC)[CC] Pump autostarted. Unit 1 was placed on a 6 hour troubleshooting/repair Limiting Condition for Operation (LCO) clock. An investigation identified a nut that was shorting contact #8 of the Train A. Division 19 Safeguards safety injection sequence timer. Contact #8 of the sequence timer is a part of the OC CC Pump safety injection autostart circuitry. <br /><br /> The cause of this event was component failure. One of two nuts for the lower contact assembly of the Division 19. Train A Safeguards safety injection sequence timer became dislodged. The nut was found across the upper contact spring and lower contact spring of the contact finger assembly effectively shorting out the contacts. The safety significance of this event was minimal. <br /><br /> Corrective actions include verifying the thread engagement for contact assemblies on all other safeguards sequence timers on Unit 1 and Unit 2, successfully testing the timer to verify proper operation and timing of the contact, and initiating an engineering request to evaluate and recommend the use of a thread securing substance. ler
2951994016 | Zion 1 | 10/25/1994 | 11/23/1994 | 9411300272 | <strong>Missed Technical Specification Action Statement on 1AOV-RV0004</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1994, Operating removed 1AOV-RV0004, 'Containment Purge Outlet Isolation Valve,' [BD] from service for Mechanical Maintenance to rebuild the air operator in support of voluntary LCO related maintenance. 1AOV-RV0003, 'Containment Purge Outlet,' was taken Out-Of-Service (OOS) closed on the same OOS to comply with the Containment Isolation Valve Technical Specification (T.S.) 3.9.3.A. On October 19, 1994, maintenance completed the work on 1AOV-RV0004 and released the OOS for 'Full Clear.' On October 20, 1994, Operating cleared the OOS on 1AOV-RV0004 for Post Maintenance Verification (PMV). The operators also cleared the OOS card on the control air valve for 1AOV-RV0003, even though it was still required to meet T.S.3.9.3.A. On October 25, 1994, it was discovered that T.S. 3.9.3.A had been exceeded on October 20, 1994, at 1918 hours. <br /><br /> The cause of this event was management deficiency. Management systems failed to control equipment status and configuration during voluntary Limiting Condition for Operation (LCO) maintenance. Corrective actions include using administrative OOS(s) to maintain the required configuration until the work packages can be properly completed to allow the equipment to be tested and declared operable. ler
2951994017 | Zion 1, Zion 2 | 11/02/1994 | 12/02/1994 | 9412120283 | <strong>Channel Checks Missed on RPS Instrumentation Prior to Entering Mode 2</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1994, Site Quality Verification (SQV) (Quality Assurance) conducted a field monitoring activity and discovered that channel checks were not being performed on the following instrumentation prior to entering Mode 2: 1) Overtemperature delta T, 2) Overpower delta T, 3) Pressurizer Level, 4) Primary Coolant Loop Flow, and 5) Feed Water Flows. Technical Specification 4.1.2, 'Reactor Protection Instrumentation and Logic Surveillance Specification,' requires the surveillances of Table 4.1-1 to be performed prior to exceeding Mode 3, one of which is a channel check for the above instrumentation. <br /><br /> This event was caused by procedure deficiencies. Operations initiated a permanent procedure change to ensure the required surveillances are completed prior to exceeding Mode 3.
2961994001 | Browns Ferry 3 | 10/18/1994 | 11/17/1994 | 9411300291 | <strong>Unexpected Auto-Start of Unit 3 Diesel Generators During the Performance of a SI due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1994, at 16 hours CDT, during the performance of the surveillance instruction (SI) for the Core Spray (CS) System Logic Functional Test Loop II, an unplanned Engineered Safeguard Feature (ESF) actuation occurred when Unit 3 Emergency Diesel Generators 3A, 3C, and 3D automatically fast started from a fast start signal and accelerated to full speed and rated voltage. The fast start signal resulted from an inadvertent actuation of the CS Pre-Accident Signal C logic relay. TVA initiated an incident investigation (II) and reported this event in accordance with 10 CFR 50.73(a)(2)(iv), as an event or condition that resulted in manual or automatic actuation of an ESF. The II has initially determined that the apparent root cause was personnel error due to inadequate self-checking. A human performance evaluation determined that contributing causes were cramped conditions associated with the tested component and inadequate assessment of the risk associated with a procedure change. TVA will complete awareness training for appropriate electrical personnel and emphasize the Stop, Think, Act, Review program and the 'good practice,' on circuit continuity measurement. TVA will also evaluate safety system SIs and the 4kV shutdown board compartments to minimize the potential of future ESF actuations.
2961994002 | Browns Ferry 3 | 10/31/1994 | 02/07/1995 | 9502160290 | <strong>A Deficiency Regarding Raychem Tubing Used For Environmental Qualification Applications</strong><br /><i>Abstract:&nbsp;</i>A deficiency regarding Raychem material was discovered on October 31, 1994, during the usage of the Raychem tubing for Environmental Qualification (EQ) applications. The Raychem tubing, type WCSF-070-N (Lot #N15057), used to insulate the splice connection of Conax ECSA conductors to their field cable conductors, could not be installed in a manner meeting the installation acceptance criteria. No immediate safety hazard exists since the equipment affected by the Raychem tubing is not required with Units 1 and 3 defueled and its failure does not impact the operating Unit 2. TVA shipped the Lot #N15057 tubing to the manufacturer for evaluation. The Unit 2 EQ applications are not affected by this problem since the tubing has not been used in any required Unit 2 EQ splices. TVA is evaluating the Unit 3 work issues to determine if the referenced Raychem material, Lot number, and contract were used on EQ components. The above condition is not reportable per 10 CFR 50.72, 50.73, or 10 CFR Part 21. However, TVA is submitting a voluntary report on this deficiency because other utilities may also have this particular type of tubing.
2981994001 | Cooper Station | 01/19/1994 | 02/18/1994 | 9403020028 | <strong>Unexpected Opening of the High Pressure Coolant Injection Pump Minimum Flow Valve, an ESF Component, During Surveillance Testing Due to Actuation of the Pump Discharge pressure Switch</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1994, at approximately 2:15 am, with the plant in full power operation, HPCI-MOV-MO25, the High Pressure Coolant Injection (HPCI) pump minimum flow bypass valve, unexpectedly opened during surveillance testing while the pump discharge valve was being opened. An initial assessment indicated that the cause of the actuation was due to pressure fluctuations caused by the pressure maintenance system. HPCI-MOV-MO25 was closed, system parameters were verified to be normal, and the surveillance test was continued without any further problems. <br /><br /> An engineering evaluation concluded that operation of the valve could occur when HPCI-MOV-MO20, the pump discharge valve is re-opened. Discussions with Control Room Operators revealed that occasionally, the valve had automatically opened during past valve operability tests. Such actuation(s) had not been reported due to lack of understanding of the extent of ESF component level reporting requirements. However, due to increased emphasis on a questioning attitude and attention to detail, this actuation was documented as a discrepancy and subsequently determined to be reportable. The root cause of the problem is design, since unnecessary actuations of the minimum flow valve should not occur. <br /><br /> A procedure change was made to the HPCI valve operability surveillance test to ensure operator awareness that automatic operation of the minimum flow valve could occur when HPCI-MOV-MO20 is re-opened. A similar change has been made to the RCIC surveillance test. An evaluation of the HPCI and RCIC Pump Discharge Pressure switch configurations and setpoints will be made and changes implemented, if practical, to eliminate the unnecessary cycling of the minimum flow valves. To ensure operator awareness of reporting requirements, licensed Operators will be apprised of ESF component level reporting requirements.
2981994002 | Cooper Station | 02/01/1994 | 09/02/1994 | 9409140105 | <strong>Unexpected Cycling of CS Pump Minimum Flow Valves During MOV and System Operability Testing Potentially Resulting in Pump Degradation & Loss of System Redundancy</strong><br /><i>Abstract:&nbsp;</i>During performance of the Core Spray (CS) Motor operated Valve (MOV) operability surveillance test on February 1, 1994, the B loop minimum flow isolation valve, CS-MOV-MO5B, unexpectedly closed and immediately re-opened when the subsystem test line isolation valve, CS-MOV-MO26B, was opened. During CS MOV testing in March, no unexpected valve actuations were observed. However, on April 27, 1994, during CS MOV testing, a recurrence of this event was experienced. These events occurred when the plant was in operation at full power. July 23, during the CS pump operability test that was being performed as part of the continuing investigation into the unexpected closures of CS-MOV-MO5B during MOV testing, the A loop minimum flow isolation valve closed approximately 10 seconds after the A pump started, before flow was established through the test line return path. An evaluation concluded that the A subsystem minimum flow valve would have been subjected to frequent cycling which, over a prolonged period of time at minimum flow conditions, could have resulted in burnout of the MOV motor and possible loss of minimum flow protection. This latter event was discovered when the plant was in a Cold Shutdown condition. <br /><br /> The causes of these unexpected valve operations have been attributed to design related factors associated with piping configuration, compounded by narrowly focused problem resolutions and insufficient surveillance testing at pump minimum flow. <br /><br /> A temporary design change was implemented, adding an eight (8) second time delay for closure of the minimum flow valve upon sensing a high flow signal to prevent spurious flow signals from closing the Core Spray minimum flow isolation valves CS-MOV-MO5A/B. A corrective action p an has been established to address the causes of inadequate problem resolution and surveillance testing.
2981994003 | Cooper Station | 02/15/1994 | 03/17/1994 | 9403230173 | <strong>Technical Specification Violation for Inoperable Radiation Monitors Caused By Improperly Assembled Particulate/Iodine Filter Assemblies</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1994, RMV-RM-30B, the Radwaste Building High Range Gaseous Effluent Radiation Monitor, was declared inoperable at 1:48 pm upon discovering a missing O-ring in the lower portion of the sample assembly that could have resulted in an inaccurate sample if the monitor was required to operate. Continued investigation determined that an additional O-ring was missing in the upper portion of the sample assembly. Following O-ring installation and leak testing, the monitor was declared operable at 2:39 pm on February 18. On February 22 at 5:35 pm, two similar monitors, RMV-RM-20B, Turbine Building High Range Gaseous Effluent Radiation Monitor, and RMP-RM-3B, Elevated Release Point High Range Gaseous Effluent Radiation Monitor, were declared inoperable upon determining that O-rings were also missing in the upper portion of the sample assemblies. Following O-ring installation and leak testing, these monitors were returned to service on February 25 at 4:45 pm. <br /><br /> The lower O-ring was not installed during previous surveillance testing or maintenance. The upper O-rings were removed to allow use of an alternate sample cartridge, and were not replaced when the original configuration was restored. Personnel have been made aware of the situation and procedures will be revised to provide additional guidance on the replacement and testing of the sample assembly.
2981994004 | Cooper Station | 03/02/1994 | 03/31/1994 | 9404080052 | <strong>Unexpected Automatic Reactor Scram Due to High Neutron Flux Caused By Partial Closure of Turbine Governor Valves Resulting From Turbine Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 097%. On March 2, 1994, at 5:45 pm, a reactor scram from 97 percent power occurred as a result of Average Power Range Monitor (APRM) high neutron flux trip. The cause of the event was partial closure of turbine governor valves caused by a turbine digital electro-hydraulic (DEH) control system malfunction resulting in a momentary reactor pressure increase. This pressure increase caused a reduction in reactor core void fraction, resulting in reactor power reaching the APRM high flux scram setpoint. Immediately following the reactor scram, vessel inventory shrink due to void collapse resulted in reactor water level reaching the nominal Level 3 trip setting of >/= +4.5 inches with Instrument 0 being approximately 165 inches above the top of active fuel. Reactor water level was restored by the reactor feed system in combination with short term operation of both the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. The plant was stabilized in a safe condition following the transient and later placed in cold shutdown. <br /><br /> Through extensive failure analysis, the most likely component failure was determined to be a transistor relay on the DEH Valve Transfer Control Card. The card was replaced. During the plant startup, conducted March 12, erratic bypass valve operation occurred resulting in a small pressure spike and associated power increase. The DEH System 24 volt power supplies were determined to be the cause of the problem. Both power supplies were replaced.
2981994005 | Cooper Station | 03/17/1994 | 04/15/1994 | 9404210019 | <strong>Actuation of Shutdown Cooling Isolation Valves Due to a Pressure Perturbation Caused By Void Collapse in the RHR System</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1994, at 9:26 a.m., with the Reactor at approximately atmospheric pressure and a temperature of 175 degrees Fahrenheit in the Reactor Recirculation system, the Shutdown Cooling Supply Isolation Valves (Group 2 components) automatically closed. The Residual Heat Removal system was in operation in the Shutdown Cooling mode at the start of a planned maintenance outage. Both Shutdown Cooling isolation valves closed as a result of the spurious actuation of the Shutdown Cooling high suction pressure interlock. Shutdown Cooling was restored in 13 minutes and the Reactor cooled to 110 degrees without further difficulties. <br /><br /> The most probable cause of this event was steam void formation and collapse in the RHR system piping. The NSSS Vendor indicated that void formation is not unexpected at this temperature. Equipment which could potentially have caused this event was inspected or tested to verify an equipment problem was not the cause. Piping and equipment were inspected to verify no damage had occurred. Procedures and practices will be reviewed, including a review of the practices of other similar vintage BWRs, and enhancements implemented as appropriate.
2981994006 | Cooper Station | 04/11/1994 | 10/19/1994 | 9410250297 | <strong>Inoperable Control Room Emergency Filter System</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1994, the Control Room Emergency Filter System failed post maintenance testing for planned maintenance of a door comprising part of the Control Room pressurization boundary. During the following 7 days, door seals were adjusted or replaced and smoke tests performed to identify leaks in the Control Room envelope, and repairs implemented. Although system performance was improved, acceptance criteria still could not be met. Enforcement discretion was granted by the NRC providing a 14 day extension to restore the Control Room Emergency Filter System operability. A significant number of additional leaks in conduits and cable trays were repaired. Post maintenance testing was completed satisfactorily and the Control Room Emergency Filter System was declared operable on April 30, 1994 at 2:52 pm. <br /><br /> The direct cause of this event was inadequate design of the system, resulting in a system with marginal capacity. The original system design criteria was inadequately defined, and subsequent opportunities to correct the condition were missed. Surveillance procedures have been revised to provide more conservative acceptance criteria, and a modification will be implemented to increase ventilation flow and pressurization margin.
2981994007 | Cooper Station | 04/13/1994 | 05/13/1994 | 9405190135 | <strong>Inoperability of the High Pressure Coolant Injection System Due to a Pressure Control Valve Controller Deficiency Caused by Lack of Preventive Maintenance</strong><br /><i>Abstract:&nbsp;</i>On April 13, at 1:57 pm, the High Pressure Coolant Injection (HPCI) System was declared inoperable when lube oil cooler pressure control valve, HPCI-AOV-PCV50, failed to re-open after the HPCI turbine had been tripped. The HPCI System had been in operation in accordance with surveillance procedure (SP) 6.3.3.1.1, HPCI IST and Quarterly Test Mode Surveillance Operation. Approximately three minutes after trip of the turbine, the valve should have opened as the downstream cooling water pressure decreased. However, due to a controller malfunction, control air was still applied to the valve, causing it to remain closed. At the time of this event, the plant was in operation at full power. <br /><br /> An inspection of the valve air controller revealed a disconnected elastomeric tube. Upon its reconnection, the controller output signal decreased to 0 psig and the valve opened. During the surveillance test, operation of HPCI-AOV-PCV50 had been checked and found to be satisfactory. A review of lube oil temperature during operation of the turbine was conducted and determined to be typical of past turbine operation. <br /><br /> Repairs to the controller were completed, post maintenance testing was satisfactorily conducted and the HPCI System was declared operable. To prevent recurrence, replacement ,of the tubing and clamps installed in this and similar controllers will be accomplished at periodic intervals.
2981994008 | Cooper Station | 04/19/1994 | 10/21/1997 | 9710270268 | <strong>Inoperable Appendix A Fire Barrier Penetration Seal Resulting From Inadequate Initial Installation</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1994, at approximately 1300, an inadequate fire barrier penetration seal in an Appendix A (to Branch Technical Position 9.5-1) fire barrier was discovered while penetration seals associated with the Control Room pressurization envelope boundary were being inspected. The barrier was declared inoperable and a Fire Watch posted in accordance with Technical Specification requirements. The opening was subsequently sealed, and the fire barrier declared operable at 1936 on April 21. Subsequent reviews and inspections revealed additional inadequate fire barriers seals and missed surveillances. <br /><br /> These deficiencies were considered to be symptomatic of a lack of fire protection program oversight. Inadequate resources were dedicated to implementation of the Appendix A program, resulting in insufficient authority and technical knowledge to adequately implement an effective program, inadequate coordination of program activities, and a lack of sensitivity to changing requirements, with the net result that the program did not ensure full compliance with regulatory requirements.<br /><br /> The deficient fire barriers penetration seals were restored and the fire barriers subsequently declared operable. Fire barrier inspection procedures were reviewed and revised to ensure appropriate inspection criteria and methods are defined. The surveillance procedure for fire dampers has been revised to incorporate the required fire dampers. Appendix A fire barriers have been "as-built" and associated station drawings and calculations for the Appendix A fire barriers have been updated. A Fire Protection Program owner has been established with the responsibility to define and coordinate all aspects of the fire protection program.
2981994009 | Cooper Station | 05/25/1994 | 01/26/1995 | 9502020111 | <strong>Inadequate load shed and logic system surveillance testing resulting in inoperability of safety systems</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1994, a tie wrap was discovered on the undervoltage trip device for the 480 VAC feeder breaker for MCC-N. This breaker is designed to trip during a loss of offsite power, which the tie wrap prevented. On May 23, additional investigation determined that the load shedding of other MCCs was not verified during surveillance testing. On May 25 it was determined that there were additional 480 VAC loads which were not procedurally verified to load shed (the Station Air Compressors and Control Rod Drive pumps). At 1:14 pm, both DGs were declared inoperable due to inadequate surveillance testing and a Notification of Unusual Event was declared. The continuing investigation into this condition also revealed that contacts in the 4160 VAC load shedding circuits of the Service Water Booster Pumps were not tested. A plant shutdown was subsequently commenced. Subsequent investigations determined that there were contacts in additional systems which were not tested in accordance with Technical Specification requirements for Logic System Functional Testing. <br /><br /> This revision is being submitted to provide the cause of this condition and the corrective actions taken and planned. <br /><br /> The cause of these conditions is attributable to a Management/Quality Assurance Deficiency (NUREG-1022, Cause code E) due to inadequate management expectations for configuration control, inadequate management commitment to the operating experience review program, and inadequate organization and programmatic controls.<br /><br /> Corrective actions include revising surveillance procedures, completion of required testing, modifying load shed trip devices, and organizational and programmatic changes.
2981994010 | Cooper Station | 05/26/1994 | 11/14/1994 | 9411220236 | <strong>Closure of Shutdown Cooling Suction Isolation Valves While Warming the Residual Heat Removal System Due to Leakage Through the Minimum Flow Valve</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1994, at 09:44 am, and again at 11:57 am and 12:06 pm, Residual Heat Removal (RHR) shutdown cooling isolation valves RHR-MOV-M017 and RHR-MOV-M018 closed as a result of actuation of one or both of the shutdown cooling suction high pressure switches RHR-PS-128A and RHR-PS-128B. These isolations occurred during heatup and flushing of RHR subsystem B loop piping which was being conducted in order to place the subsystem in the Shutdown Cooling mode of operation. At the time when these isolations occurred, reactor pressure and temperature was approximately 40 psig and 280 degrees F, respectively. The turbine bypass valves were controlling RPV pressure, rejecting decay heat to the main condenser. <br /><br /> Subsequent to these isolations, leakage was audibly detected through RHR-MOV-M016B (RHR pump B minimum flow valve) to the suppression pool (torus). At 12:30 pm, RHR-MOV-M016B was closed manually with less than one hand wheel turn of the motor operator. Leakage through the valve was determined to have caused the rapid depressurization of the shutdown cooling suction line, creating steam voids in that section of piping, which led to hydraulic instability (pressure spiking) upon admittance of fluid to the suction piping. Per NUREG-1022, the root cause of this event is 'Other,' attributed to the lack of a Foreign Material Exclusion (FME) program at CNS.
2981994011 | Cooper Station | 06/02/1994 | 11/15/1994 | 9411250124 | <strong>Primary Containment Penetration Design and Testing Deficiencies Discovered During Design Basis Reconstitution Activities</strong><br /><i>Abstract:&nbsp;</i>On June 2, Primary Containment penetration X-218 was inspected and determined to not be in compliance with design requirements and not being leak rate tested (LLRT) as required by 10CFR50 Appendix J. A similar deficiency was found with penetrations X-209A thru D on June 6. These discrepancies were discovered during a walkdown of all Primary Containment penetrations performed during the design basis reconstitution of the Primary Containment System. Due to their discovery, Primary Containment was declared inoperable on June 7. Further investigation revealed concerns with approximately 100 penetrations, including drawing deficiencies, penetration barrier deficiencies, piping stem weld classification and NDE record deficiencies and additional LLRT deficiencies. When these deficiencies were discovered, the plant was in Cold Shutdown and Primary Containment Integrity was not required. <br /><br /> The root causes for the failure to identify and promptly resolve the numerous containment penetration design discrepancies were determined to be due to organizational and programmatic deficiencies associated with a compliance based engineering assessment approach and lack of an aggressive Appendix J program management function. <br /><br /> Corrective actions to resolve the containment penetration discrepancies have been taken and completed. Further corrective actions are being taken to address and resolve the root causes of the organizational and programmatic deficiencies that resulted in the failure to identify and promptly resolve the numerous containment penetration discrepancies that were found.
2981994012 | Cooper Station | 07/08/1994 | 01/12/1995 | 9501200124 | <strong>Technical Specification non-compliance for the HPCI System due to a setpoint discrepancy associated with the low steam line isolation pressure switches.</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1994, while investigating surveillance test requirements for the High Pressure Coolant injection (HPCI) system, it was determined that the setpoint for the low steam line isolation pressure switches was above the HPCI system operability requirement of greater than 113 psig. New switches were installed that have trip setpoints less than 113 psig, but after further review it was determined that the reset pressure for the new switches was, and had been with the old switches, greater than the 113 psig operability requirement in the Technical Specifications.<br /><br /> The cause of these conditions was due a Management\Quality Assurance Deficiency (NUREG-1022, Cause Code E) since this was a breakdown in program controls. The breakdown resulted in an oversight of the Technical Specification requirements. This oversight was influenced by conflicting statements between and within the Technical Specifications and the USAR. <br /><br /> Corrective actions taken include a Technical Specification change request submitted to the NRC to establish the operability limit for HPCI at greater than 150 psig. In addition, administrative changes will be implemented to increase assurance of properly considering requirements in station modifications. A similar situation for the Reactor Core Isolation Cooling system was reviewed and determined to satisfy Technical Specification requirements.
2981994013 | Cooper Station | 07/12/1994 | 08/11/1994 | 9408180185 | <strong>Reactor Scram and Group Isolations Due to Spurious trip of Reactor Vessel Level Instruments Caused by Leaking Solenoid Valve in the Reference Leg Injection System</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1994, at 2:45 am, a Reactor Scram and Group 2 (Shutdown Cooling), 3 (Reactor Water Cleanup), and 6 (Reactor Building Ventilation) Isolations occurred and Standby Gas Treatment started as a result of a spurious decrease in the indicated Reactor vessel water level on the 'B' channel level instruments. Actual vessel level was at 50 inches. All control rods were at the full in position, thus no rod motion occurred. The Scram was reset at approximately 2:49 am, and Shutdown Cooling returned to operation at 3:04 am. Reactor coolant temperature increased from approximately 110 to 113 degrees Fahrenheit while Shutdown Cooling was isolated. <br /><br /> The cause of the spurious actuation was leakage through a solenoid valve due to wear. This solenoid valve provides injection of Core Spray to backfill the 'B', channel reference leg of the Reactor vessel water level indication system. The wear was due to pressure transients from valve surveillance testing in the Core Spray system, which was not anticipated during installation. The valve was replaced and, along with the comparable solenoid valve for the 'A' reference leg, was checked satisfactorily for leakage. The system line-up will be changed to isolate the solenoid valves from the Core Spray system during normal operation, and Core Spray system testing will be revised to minimize the potential for pressure transients.
2981994014 | Cooper Station | 07/23/1994 | 08/22/1994 | 9409020313 | <strong>Inoperable Control Room Emergency Filter System due to Unanticipated Balancing Damper Movement</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1994, at 12:08 am, the Control Room Emergency Filter System failed to meet the acceptance criteria specified in Surveillance Procedure 6.3.17.18, Control Room Envelope Pressurization Test, Revision 5. Although the system maintained a positive pressure, it did not satisfy the acceptance criteria which had been recently revised. Performance of the system to meet the new criteria had last been acceptably demonstrated on July 12, 1994. Troubleshooting identified that small changes in the position of the Cable Spreading Room Exhaust damper caused significant changes in the pressure of the Control Room and Cable Spreading Room. Attempts to re-create the damper position changes due to postulated operational conditions were unsuccessful. <br /><br /> Previous experience indicated that proper pressurization of the Control Room envelope (Control Room/Cable Spreading Room) was sensitive to the position of this damper. The existing damper could not satisfy current expectations for system performance, and personnel responsible for system performance did not initiate appropriate actions to ensure damper movement was prevented. The damper was modified to function as a fixed orifice, and subsequent testing demonstrated satisfactory system performance. Additionally, actions are planned to lessen the sensitivity of the system to air flow balance.
2981994015 | Cooper Station | 08/04/1994 | 01/31/1995 | 9502090069 | <strong>Excessive Heatup/Cooldown During RPV Stratification Events</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1994, during a diagnostic self assessment, Nebraska Public Power District (NPPD) discovered that the average rate of reactor coolant temperature change exceeded the Technical Specification LCO 3.6.A.1 requirement of 100 degrees F/hour when averaged over a one hour period during plant trips on December 14, 1993, and March 2, 1994. During the December 14, 1993 plant trip, both reactor recirculation pumps tripped resulting in a loss of forced circulation. resulting in a temperature drop of more than 100 degrees F/hour. Also, during cooldown when the rate of depressurization was increased, enhanced core boiling increased coolant circulation and resulted in the bottom head metal and coolant temperatures exceeding a 100 degrees F/hour heatup rate. The same event occurred during the March 2, 1994, plant trip. LER 94-015 described these events. The above events did not exceed Thermal and Pressurization limits as defined in Technical Specification Figures 3.6.1.a, 3.6.1.b, and 3.6.2. <br /><br /> On September 10, 1994, other related events were discovered to have occurred on November 20, 1979, December 19, 1993, and March 12, 1994, during plant startups. Also, events since initial plant startup were reviewed and were found to be bounded by the analyses performed on RPV components. This revises LER 94-015-01.<br /><br /> Per NUREG-1022, the cause of these events is attributed to Other, specifically a Technical Specification, Section 3.6.A.1, Application Error.
2981994016 | Cooper Station | 08/04/1994 | 11/17/1994 | 9411250051 | <strong>Noncompliance With 10CFR50 Appendix R, Inadequate Isolation of Diesel Generator Control Circuits</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1994, it was determined that Diesel Generator (DG) 2 was not in compliance with Alternate Shutdown requirements. A single fuse and circuit breaker was located in a control power circuit for DG 2, the dedicated Alternate Shutdown DG. A fire affecting Control Room indication circuits could have resulted in a fuse failure or breaker trip rendering the DC unable to start. Additionally, a fire affecting cables associated with the diesel generator speed regulator control could have resulted in the control being mis-positioned prior to being disabled by a fire, resulting in the diesel generator being unable to perform its intended Alternate Shutdown function. At the time this condition was discovered, the plant was in cold shutdown and Alternate Shutdown was not required to be operable. <br /><br /> The cause of this condition was a narrow interpretation of the isolation requirements for the diesel generator during the implementation of Appendix R requirements, and inadequate review of subsequent regulatory guidance issued after the design was complete. A design change was implemented to provide isolation fusing of the circuit, and procedure changes are being implemented to address the potential disabling of the speed regulator. An independent verification of the Appendix R Safe Shutdown Analysis will be performed.
2981994017 | Cooper Station | 08/09/1994 | 09/08/1994 | 9409150018 | <strong>Potential Breach of Primary Containment Through the Reactor Equipment Cooling System Due to Rupture of System Piping Inside the Drywell Caused by a HELB</strong><br /><i>Abstract:&nbsp;</i>A re-assessment of the condition described in IN 89-55 and the ensuing engineering evaluation performed in 1989 raised concerns that the evaluation may not have been responsive to the intent or the potential ramifications of the condition addressed by the IN. IN 89-55 is directly applicable to the Reactor Equipment Cooling (REC) System in that it is the only closed system utilizing the specific isolation scheme described. The scenario described in the IN is of concern because a vent path from containment through the REC Drywell return line and out the REC Surge Tank 4' vent into the Reactor Building (Secondary Containment) could develop. <br /><br /> The original assessment of the condition described in IN 89-55 concluded that the concern was not applicable since the probability of a Reactor Recirculation System line break causing an REC System line break inside containment together with a subsequent failure of an REC Containment Isolation Valve was very remote. <br /><br /> An evaluation of the re-assessment is ongoing. Prior to plant startup, this concern will be resolved and a supplement to this LER will be submitted.
2981994018 | Cooper Station | 08/20/1994 | 07/31/1995 | 9508030311 | <strong>Reactor Core Isolation Cooling System Trip and Throttle Valve Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1994, while reviewing surveillance test requirements associated with the Reactor Core Isolation Cooling (RCIC) System, the reset function for RCIC-MOV-MO14, the RCIC Turbine Trip Throttle Valve, was determined to be powered by an AC, not a DC motor. However, the design basis of the RCIC System states that it shall be independent of AC power and shall depend only on DC power for short term operation. <br /><br /> In the event of a Station Blackout (SBO) in which all offsite and onsite AC power is lost for a period of up to 4 hours, RCIC is required to function to provide residual heat removal. However, due to the reset motor being powered by AC, neither automatic nor remote manual reset of the valve would have been possible although local manual reset could be performed. <br /><br /> To prevent recurrence of such an event, the AC motor operator on the RCIC-MOV-MO14 valve was replaced with a DC motor operator on December 22, 1994.
2981994019 | Cooper Station | 04/11/1994 | 01/12/1995 | 9501200017 | <strong>Maximum authorized power level exceeded due to feedwater flow transmitter calibration error.</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1994, while the plant was operating at full power, it was determined that the feedwater flow transmitters had been improperly calibrated since installation in 1980. This resulted in a non-conservative error in the total feedwater flow signal of about 1 percent. The error was due to not incorporating a static pressure span correction factor in the calibration of the Rosemount 1151DP Alphaline differential pressure transmitters. The underestimation of feedwater flow resulted in the core power being about 20 MW thermal greater than the Maximum Power Level authorized by the facility license and core flow about 0.5 percent above rated flow. In addition, in a past attempt to correct an assumed instrument loop accuracy problem, a design change was incorporated that inappropriately eliminated a feedwater temperature compensation function. This report is being submitted voluntarily as a potential generic concern for other facilities.<br /><br /> The cause of this condition was personnel error (NUREG-1022, Cause code: A) on the part of the engineers involved in the installation and modification of the Rosemount 1151DP transmitters. The personnel error includes weak reviews in response to NRC Information Notice 85-100 and GE SIL 452 that might have led to the earlier discovery of this calibration error.<br /><br /> Corrective actions include restoring the instrument loops to their original configuration and correctly calibrating Rosemount 1151DP transmitters affected by the static pressure effect.
2981994020 | Cooper Station | 09/01/1994 | 10/03/1994 | 9410130333 | <strong>Installation of Non-Essential Elapsed Time Meters in Essential Control Room HVAC and Standby Gas Treatment Systems</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1994, during the Design Criteria Document development, a review of open items associated with the Control Room Ventilation System revealed that an Elapsed Time Meter (ETM) which had been purchased non- essential had been installed in 1976 in the essential control circuits for the Control Room Emergency Supply Fan, HV-MOT-(VF-C-1A) with a design change. A review of the design change further revealed that identical ETMs were installed in an identical fashion in the logic circuits for Standby Gas Treatment System exhaust fans SGT-MOT-(EF-R-1E and SGT-MOT- (EF-R-1F). The ETMs were wired in parallel with the fan motor, and should they fail, the control power fuse for the fan could blow, preventing fan start or causing fan trip. <br /><br /> On September 3, 1994, the Nuclear Engineering Department determined that the installed ETMs could not be qualified. At 4:30 pm, the Control Room Emergency Bypass Filter System and the Standby Gas Treatment System were declared inoperable. <br /><br /> Per NUREG-1022, the cause of this event is attributed to defective procedures at the time of installation.
2981994021 | Cooper Station | 10/07/1994 | 11/07/1994 | 9411150536 | <strong>Design error that allows spurious DG Room HVAC isolation During a fire or seismic event</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1994, a design flaw was discovered that could cause both Diesel Generators (DGs) to be rendered inoperable during a fire in the Turbine Building or a design basis earthquake. During either of these events the High Pressure Carbon Dioxide Extinguishing System (HPCDES), which protects the DG Rooms from fire, may erroneously isolate HVAC to both DG Rooms, thereby threatening DG operability. <br /><br /> The root cause of both design vulnerabilities is an inadequate HPCDES design change which relocated two essential components to the same fire area within a non-seismic structure [CAUSE CODE B].<br /><br /> Corrective actions include disabling the HPCDES input to the DG Room HVAC auto-isolation logic and stationing fire watches until a design change can be implemented that addresses the seismic and Appendix R concerns. This LER also fulfills the Technical Specification 3.17.C requirement for a Special Report following HPCDES inoperability that exceeds 14 days.
2981994022 | Cooper Station | 09/19/1994 | 10/19/1994 | 9410250305 | <strong>Failure to properly perform Technical Specification surveillance requirements due to procedure inadequacy</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1994, it was determined that the Technical Specification (TS) maximum flow limitation for the Low Pressure Coolant Injection (LPCI) system was not adequately proven by the existing surveillance procedure, SP 6.3.5.1. The maximum flow specified in TS 4.5.A.3.d is 8400 gpm for single pump operation with system head equivalent to a reactor pressure of 20 psid above drywell pressure with water level below the jet pumps. SP 6.3.5.1 adjusts flow using RHR-MO-34A(B) and verifies pump performance is above that required to inject 7700 gpm (and 15,000 gpm for two pumps running) into the vessel at 20 psid. The testing did not verify pump performance would exceed that required to limit the one pump flow to less than 8400 gpm. When found, the plant was in Cold Shutdown with the Residual Heat Removal (RHR) System in the Shutdown Cooling mode of operation. <br /><br /> The root cause for non-compliance with the Technical Specification requirement was due to misunderstanding the TS flow limitations and assuming the design of the system, with orifice plates in the pump discharge lines, would limit maximum flow. (NUREG-1022, cause code E, 'Management/Quality Assurance Deficiency.') <br /><br /> Corrective actions will include a surveillance procedure change to incorporate the proper test configuration for testing the LPCI flow under the TS surveillance restrictions. Additionally, a surveillance testing validation program is in progress to study and review Technical Specification surveillance requirements.
2981994023 | Cooper Station | 10/03/1994 | 11/02/1994 | 9411100235 | <strong>Technical Specification Violation of Failure to Re- demonstrate Diesel Generator After Other Diesel Generator was Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1993, following a successful four hour operability run on diesel generator (DG) DG-1, DG-2 failed its four hour operability test and was declared inoperable. However, due to the satisfactory operability run of DG-1 earlier the same day, the re-demonstration of DG-1 operability was not performed. This is a violation of Technical Specifications (TS) 4.5.F.1. This event was identified during Quality Assurance (QA) Audit 94-01, however was not determined to be a TS violation until October 3, 1994. <br /><br /> Per NUREG-1022, the cause of this event is attributed to a Inadequate Training, NUREG-1022 code X, Other, specifically misapplication of TS 4.5.F.1.<br /><br /> The corrective action includes providing a TS clarification to ensure the proper interpretation of the TS and providing training on the TS clarification.
2981994024 | Cooper Station | 10/02/1994 | 10/31/1994 | 9411070306 | <strong>Inoperable Condition of the Halon System in Service Water Pump Room</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1994, at 9:30 am while performing an inspection of the Service Water Pump Room, it was discovered that Service Water Pump 'B' casing was not seated to the floor due to ongoing maintenance. If the Halon System is activated in the room in case of a fire, Halon would be discharged and escape to the area below the Service Water Pump Room, thereby diluting the extinguishing agent. <br /><br /> At 9:30 am per Technical Specification 3.17.B, the Service Water Pump Room Halon System was declared inoperable and a fire watch was stationed within one hour. <br /><br /> Per NUREG-1022, the root cause of this event is inadequate procedures to address sufficient details for declaring the Halon System operable.
2981994025 | Cooper Station | 09/30/1994 | 11/04/1994 | 9411150608 | <strong>Improper installation and calibration of Kaman normal and high range gaseous activity detectors due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>Information obtained at a Kaman Users Group meeting indicated that the positioning of the gaseous activity detectors affects their accuracy. Plant staff subsequently determined that these detectors have been improperly installed in monitors in various process system sample flow paths. Preliminary information from the current equipment vendor indicates that the as-found detection error ranges up to approximately 55 percent. As a result of further discussions with the current equipment vendor it was also determined that an improper method has been used for calibration of most Kaman detectors. The source used in the calibration device has been used with its storage planchet, whereas, the manufacturer's procedure uses the source without the planchet. The vendor has indicated that this discrepancy may result in approximately a 5 to 9 percent non-conservative calibration error. This report is being made for potential generic implications. <br /><br /> The root cause of these deficiencies is personnel error in not fully understanding system configuration needs and not properly translating vendor requirements into station procedures. (NUREG-1022, Cause Code A, 'Personnel Error') <br /><br /> Corrective action planned includes proper installation and calibration of these detectors (including appropriate procedure changes) and a review of other Kaman detector installation and calibration procedures for proper implementation of vendor requirements. Additionally, generic implications for other systems will be investigated.
2981994026 | Cooper Station | 10/09/1994 | 11/09/1994 | 9411150631 | <strong>Standby Liquid Control System not maintained at proper temperature due to design deficiency and lack of appropriate monitoring.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On October 9, 1994, it was determined that the temperature of the solution in the Standby Liquid Control (SLC) System was not being monitored in accordance with Technical Specification requirements for maintaining the temperature for the concentration of sodium pentaborate solution in the system. Specifically, the suction piping has not been monitored and verified above the required temperature. In addition, the pump head is not properly heat traced and insulated. Assuming worst case wintertime room temperatures, a portion of the SLC system could have sodium pentaborate precipitate out and deposit in a film in the bottom of the pump head. However, the pumps are expected to operate when needed and pump out any precipitate present.<br /><br /> The root cause of this event is a Management/Quality Assurance Deficiency (NUREG-1022, Cause Code E) in not identifying the requirement to monitor the SLC system suction piping to satisfy Technical Specifications and not identifying the need to properly heat trace and insulate the pump head and suction piping.<br /><br /> Corrective actions include design changes to improve heat tracing and monitoring capabilities of the SLC system and procedure changes to include required monitoring in the Technical Specification surveillance program. In addition, a Design Basis Reconstitution Program is underway to review design, USAR, and Technical Specification requirements. Also, a surveillance testing verification program is in progress to review surveillances with Technical Specification criteria and verify that component/system testing is satisfactory.
2981994027 | Cooper Station | 11/16/1994 | 12/23/1994 | 9412290341 | <strong>Installation of an Unqualified Relay in a Potential Harsh Environment</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1994, a non-environmentally qualified relay, MS-REL-52XCP was discovered. <br /><br /> Failure of the relay coil due to a High Energy Line Break (HELB) in the Reactor Building could open Fuse 10A-F13A which would deenergize essential equipment that shares the fuse. It would result in failure of Service Water (SW) and Reactor Heat Removal (RHR) instruments as well as Nuclear Boiler Indicators (NBIs) for Reactor Shroud Level indication and Reactor Level Nozzle Range indication. The coil failure also impacts the control circuit of the Motor Operated Valves (MOVs), RHR-MO-920MV (Steam Supply to AOG Upstream Shutoff) and RHR-MO-921MV (Steam Supply to AOG Downstream Shutoff). <br /><br /> Per NUREG-1022, the root cause of this event is attributed to defective procedures at the time of the installation of the relay.
2981994028 | Cooper Station | 11/01/1994 | 12/01/1994 | 9412050270 | <strong>Design error that places the Ultimate Heat Sink in an unanalyzed condition During design low river level conditions.</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1994, it was recognized that during low river level conditions, the Intake Structure weir wall configuration would create a relatively narrow water channel between the Missouri River and the Intake Structure bays, and that this channel had previously contained a significant riprap and silt deposit. Assuming design basis low level conditions, the existing analysis was inadequate to conclusively demonstrate that sufficient service Water could be supplied to achieve and maintain safe shutdown. <br /><br /> The root cause of this condition is a modification made at the end of plant construction that created an Intake Structure weir wall, but did not adequately assess the impact on design bases assumptions concerning river level [NUREG-1022 CAUSE CODE B]. <br /><br /> Corrective actions include dredging the channel and implementing a design change to the weir wall that will reestablish the original analysis bounding assumptions.
2981994030 | Cooper Station | 10/10/1994 | 12/12/1994 | 9412210016 | <strong>Failure to properly satisfy Technical Specification requirement for fire barrier inspection due to inspection by an uncertain inspector</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1994, the ceiling plugs in the Service Water (SW) pump room were reinstalled as part of maintenance activities. Technical Specifications require a visual inspection to verify fire barriers are functional following maintenance. A utility person signed the inspection procedure which subsequently led to securing the fire watch in the room (established because the Halon system is inoperable with the ceiling plugs removed). About twelve hours later it was determined that the inspection was invalid since the person was not QC certified for this inspection. The ceiling plugs were inspected by a QC certified inspector and signed-off as functional. No additional work on the ceiling plugs was performed during that twelve hour period. Because the barrier was subsequently shown to be functional this event was not originally determined to be reportable. Upon review of this event on November 11, 1994, it was determined to be reportable due to the non-QC certified inspection not satisfying Technical Specification requirements. <br /><br /> The cause of this event was personnel error (NUREG-1022, Cause Code A) due to inadequate interface between the Control Room and maintenance supervision in identifying the QC certification of the person doing the original inspection.<br /><br /> Corrective action consisted of the Maintenance Manager issuing instructions to assure maintenance personnel are aware of their QC certifications and to assure the Control Room notifies maintenance shop supervision when support for non-emergency work is required. In addition, monthly QC certification reports will be provided to maintenance shops until a computerized tracking system provides real time certification information.
2981994031 | Cooper Station | 11/15/1994 | 12/15/1994 | 9412230077 | <strong>Calibration Frequency Error on Steam Leak Detection System Temperature Switches</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1994, it was recognized that the Steam Leak Detection System (SLDS) temperature switches were not being calibrated within the surveillance interval intended by the Technical Specifications. Specifically, the requirement 'Once/Operating Cycle' had been interpreted to mean 'Once during the Operating Cycle', rather than 'Once at a periodicity not to exceed an Operating Cycle'. <br /><br /> The root cause of this condition is personnel error, in that an interpretation had been made of the Technical Specification requirements for 'Once/Operating Cycle' instrument calibrations that was not adequately conservative [NUREG-1022, CAUSE CODE A]. <br /><br /> Corrective actions include updating the calibration schedule of the switches, revising the governing surveillance procedures, and briefing applicable I&C personnel on the issue.
2981994032 | Cooper Station | 12/21/1994 | 01/26/1995 | 9502020165 | <strong>Weakness in ASME Section XI IST program due to discrepancies in component boundary selection criteria</strong><br /><i>Abstract:&nbsp;</i>A review of the Cooper Nuclear Station (CNS) ASME Section XI Inservice Testing (IST) program identified several weaknesses in the program scope and in the test methods. These weaknesses were found by applying the guidance of (Draft) NUREG-1482. The cause was partly due to changes in the boundary classifications and partly due to inadequate program maintenance. Approximately 900 components were identified for potential reclassification and about 200 potential testing program weaknesses were identified for further investigation.<br /><br /> All components identified for reclassification were found to be qualifiable for pressure boundary; one component was found not to be qualified seismically. <br /><br /> Of the approximately 200 potential IST Program weaknesses, 22 require testing prior to startup. <br /><br /> This report is being made as a voluntary submittal to inform the NRC of IST program issues. <br /><br /> The cause of this condition is a Management/Quality Assurance Deficiency (NUREG-1022, Cause code E) due to past inadequacies in administrative and technical control of the IST program. <br /><br /> Corrective action includes a complete review using updated boundary selection criteria and updating of the ISI and IST programs as necessary.
2981994033 | Cooper Station | 12/20/1994 | 01/19/1995 | 9501260086 | <strong>Safety Relief Valve Setpoint Variance Not Within Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>While the plant was shutdown during the current outage, eight Safety Relief Valves (SRVs) were removed and sent to the Westinghouse testing facility in Banning, California for testing in accordance with the Technical Specifications. Four of the SRV lift pressures were higher than their required setpoint tolerance of +1%. One was lower than its required setpoint tolerance of -1%. This has been an industry-wide problem for a number of years. The eight installed SRVs were tested in 1993 and seven of the eight were higher than their required tolerance of +1%. Similar failures have been noted in the past. <br /><br /> Additionally, one valve had a part of the disc spring break during testing/refurbishment and two valves were found with springs approximately two inches shorter than a new spring.<br /><br /> Although CNS is still in Cycle 16, it has been approximately eighteen months since the last test and it was considered prudent to test the installed SRVs at this time.<br /><br /> Per NUREG-1022, the cause of this event is attributed to Design, Manufacturing, Construction/Installation, NUREG-1022 code B, specifically corrosion bonding of the pilot disc to the pilot seat.<br /><br /> The corrective actions include having General Electric review the results of the testing and confirm the conclusions that the as-found setpoints would not adversely affect plant safety. Also, CNS will replace 1/2 of the valve discs with a platinum catalyst alloy.
2981994034 | Cooper Station | 11/12/1994 | 02/08/1995 | 9502150340 | <strong>Emergency Lighting System cannot be assured of meeting 8 hour operation requirement due to design and maintenance deficiencies.</strong><br /><i>Abstract:&nbsp;</i>On November 12, 1994, after an investigation into the maintenance of 10CFR50, Appendix R Emergency Lighting, the Nebraska Public Power District (District) determined that the Emergency Lighting, as designed and maintained, would not fully satisfy design requirements. Specifically, the investigation revealed potential problems with lamps due to the existing maintenance program not addressing their rated life time, batteries due to inadequate analysis of temperature effects on battery performance and life, and battery chargers due to the use of non, or improperly, temperature-compensated control boards that would adversely affect battery life. <br /><br /> The cause of this event is attributable to a Management\Quality Assurance Deficiency (NUREG-1022, Cause Code E) due to past inadequacies in administrative controls on design practices and preventive maintenance practices. <br /><br /> Corrective action consists of replacement of Emergency Lighting batteries, lamps, and battery charger circuit boards where required and initiating appropriate preventive maintenance for Emergency Lighting. In addition, the design basis of the Emergency Lighting system will be reconstituted and testing will be verified to provide reasonable assurance of system operability.<br /><br /> This supplement is being submitted to provide additional information about inadequate lighting found during corrective actions taken as described in Revision 0.
2981994035 | Cooper Station | 12/29/1994 | 01/26/1995 | 9502020116 | <strong>Inoperable Standby Gas Treatment (SGT) System Due to a Potential Backflow of Water from the Z Sump Under Design Basis Accident Condition</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1994, while investigating the safety classification of a system with respect to a proposed modification to prevent freezing of the Elevated Release Point Drain Sump (Z sump) pump discharge lines, the Engineering Support Department discovered the following condition:<br /><br /> Under design basis accident conditions with a coincident loss of offsite power, the Z sump pumps and high level alarm would lose power and the condensation from Standby Gas Treatment (SGT) effluent cooling in the underground piping and the Elevated Release Point (ERP) tower would accumulate in the sump filling the 10' SGT discharge lines through the open 2' drain line. As a result, the SGT system operability could not be assured and, therefore, secondary containment could not be maintained. <br /><br /> Per NUREG-1022, the cause of this event is attributed to a design error at the time of plant construction (Cause code B).
2981994036 | Cooper Station | 12/07/1994 | 12/13/1994 | 9412200077 | <strong>Fire Suppression Water System Did Not Meet the Minimum Requirements For Operability</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1994, an electrical transient on the 12.5 KV System resulted in loss of power to the Cooper Nuclear Station (CNS) primary electric-driven fire pump and fire water jockey pump. The diesel-driven fire pump control switch was placed in pull-to-lock to prevent pump damage from erroneous pump starts due to system header pressure decay. Collectively, these conditions resulted in Fire Suppression Water System inoperability due to having less than two operable fire pumps. Power was restored and the Fire Suppression Water System was returned to operability later that day. <br /><br /> Additionally, on December 11, 1994, a planned power outage occurred to implement permanent repairs to the 12.5 KV System stemming from the December 7 event. This resulted in again placing the Fire Suppression Water System in the same inoperable configuration. Power was restored within 4 hours and the Fire Suppression Water System was returned to operability at that time. <br /><br /> Per CNS Technical Specifications, whenever the Fire Suppression Water System is inoperable a written report is required within one working day following the event. This LER fulfills this reporting requirement.
3011994001 | Point Beach 2 | 03/23/1994 | 07/29/1994 | 9408020156 | <strong>Potential Feedwater Flow Measurement Inaccuracies</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1994, with both units operating at full power, we identified conditions which indicate that feedwater flow in Unit 2 may have been underestimated by approximately 2% since the beginning of the current operating cycle. Attempts to verify this indication have not been completed due to equipment problems. The cause of this potential underestimation of feedwater flow is believed to be due to a degradation in the signals from the Leading Edge Flow Meter transducers. As a conservative measure, an updated Reactor Thermal Output calorimetric calculation was performed based on the potential 2% underestimation of feedwater flow. The results of this calculation indicate that reactor power may have been 2% higher than indicated and one channel of Overtemperature Delta T and Overpower Delta T protection may have been inoperable. Power range nuclear instrument gains, and Overtemperature Delta T and Overpower Delta T setpoints were adjusted accordingly. We will continue our evaluation of the potential underestimation of feedwater flow and report the results in a supplemental Licensee Event Report.
3011994002 | Point Beach 2 | 07/13/1994 | 10/07/1994 | 9410250134 | <strong>Quarterly Technical Specification Test or PORV Block Valve Not Performed</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1994, after preparing a temporary change to Inservice Test Procedure IT-25, 'Reactor Coolant Valves (quarterly), Unit 2, ' Revision 11, Operations personnel discovered that a quarterly test of power- operated relief valve (PORV) Block Valve 2RC-516 was not performed during the first quarter 1994. This is contrary to Point Beach Technical specifications Table 15.4.1-2 which requires quarterly stroke tests of PORV block valves. After further review, it was determined that inservice test Procedure IT-25, 'Reactor Coolant Valves (Quarterly), Unit 2, ' Revision 10, had been temporarily changed on March 10, 1994, to omit the testing of PORV Block Valve 2RC-516 due to slight leakage through its associated PORV. Valve 2RC-516 was successfully tested on June 10, 1994, during its second scheduled quarterly test. A new temporary change to IT-25, Revision 11, was modified and approved on July 7, 1994, to re-instate Valve 2RC-516 test requirements. This event was caused by an improper temporary change to Inservice Test Procedure IT-25, 'Reactor Coolant Valves (Quarterly), Unit 2, ' and subsequent inadequate review of the test results and testing requirements.
3011994003 | Point Beach 2 | 10/10/1994 | 10/26/1994 | 9411020185 | <strong>Steam Generator Tube Degradation</strong><br /><i>Abstract:&nbsp;</i>Point Beach Nuclear Plant (PBNP) Unit 2 was shut down for Refueling 20 (U2R20) on September 24, 1994. Leak testing and eddy current examination of the steam generator tubes began on October 5, 1994, and was completed on October 12, 1994. Eddy current testing of the 'A' steam generator revealed 4 tubes degraded >/= 40% of the wall thickness, 8 tubes with axial indications in the tube-end area, and 155 sleeved tubes with parent tube circumferential indications. All of these tubes (167 total) were plugged.<br /><br /> In the 'B' steam generator, eddy current testing revealed 1 tube degraded >/= 40% of the wall thickness, 10 tubes with axial indications in the tube-end area, and 67 sleeved tubes with parent tube circumferential indications. All of these tubes (78 total) were plugged. <br /><br /> The 800 psid secondary-to-primary leak test revealed 6 sleeves and 2 open tubes with dampness in the 'A' steam generator and 13 open tubes with dampness in the 'B' steam generator. These tubes remain in service. The 800 psid leak test also revealed 2 wet mechanical plugs in the 'A' steam generator and 30 wet mechanical plugs in the 'B' steam generator. All of these plugs (32 total) were replaced with new mechanical plugs.
3011994004 | Point Beach 2 | 10/06/1994 | 10/27/1994 | 9411010262 | <strong>Late Reactor Coolant System Chloride Sample</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1994, Point Beach Nuclear Plant Unit 2 was in a defueled condition, residual heat removal secured, and the reactor coolant system in reduced inventory. A Unit 2 reactor coolant sample was drawn at 1248 CST to perform a required chloride analysis. Point Beach Nuclear Plant Technical Specifications require a chloride sample three times per week but not to exceed 72 hours between samples when a unit is in refueling shutdown. Due to incomplete communications between chemistry and operations personnel, the reactor coolant system sample was drawn approximately 76.5 hours after the initial sample. Sample results were normal.
3011994005 | Point Beach 2 | 11/02/1994 | 12/02/1994 | 9412080131 | <strong>TS Violation - Overtemperature DELTA T Minimum Degree of Redundancy Not Achieved</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1994, while performing flux mapping during Point Beach Nuclear Plant (PBNP) Unit 2 start-up following the Unit 2 Cycle 20 refueling outage, plant personnel noted that the delta flux indication for power range Channel N42 was not consistent with the other three power range channels. The N42 delta flux indication was the opposite of the N41, N43, and N44 delta flux indications. After flux mapping was completed, plant personnel confirmed via rod motion that the signals from the upper and lower N42 detectors were reversed. Technicians switched the N42 signal cables at the input to the electronics to provide the proper indication. Although the N42 flux trips and interlocks remained operable, the overtemperature delta T function for the N42 channel was inoperable due to the inaccurate delta flux input and would have resulted in nonconservative trip setpoints for some conditions of axial flux mismatch. However, these conditions did not exist while the N42 channel overtemperature delta T was inoperable. This placed the overtemperature delta T circuitry in a condition with three operable channels with two channels to actuate to trip the reactor, or a minimum degree of redundancy of 1. This condition violated Technical specifications Table 15.3.5-2, Item 5, which requires a minimum degree of redundancy of 2 for the overtemperature delta T reactor protection function.
3021994001 | Crystal River 3 | 03/15/1994 | 04/12/1994 | 9404190217 | <strong>Performance of Procedure to Return Makeup Pump 1C to Operability Results in Entry into LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION), operating at 100% reactor power and generating 871 megawatts. Makeup pump (MUP)-1C was out of service. Operations personnel were in the process of performing a test procedure which would both complete post maintenance testing to return MUP-1C to operable status and satisfy a scheduled surveillance requirement. The procedure, written for normal surveillance testing, assumes all MUPs are operable and directs the operators to close a discharge crosstie valve (MUV-3) as part of the procedure which tests associated valves. At 2205, the control room operators closed MUV-3, thereby isolating the flow path to two high pressure injection (HPI) lines from an operable HPI pump. The shift supervisor identified that the plant was in a condition outside the safety analysis and immediately entered Technical Specification Limiting Condition for Operation (LCO) 3.0.3. At 2225, following the performance of the procedure section, LCO 3.0.3 was exited. Between 2205 and 2225, the makeup system would not have provided the HPI flow paths required by the Safety Analysis without operator actions. The cause of this event was lack of immediate self-checking by the shift supervisor. Several corrective actions were established, including additional training to reinforce timely self checking.
3021994002 | Crystal River 3 | 04/04/1994 | 05/03/1994 | 9405100057 | <strong>Performance of Surveillance to Check Power Distribution Breaker Alignment and Power Availability Verification Results in Entry into LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1994, Florida Power Corporation's Crystal River Unit 3 was in MODE 1 (POWER OPERATION), operating at 76% reactor power. During performance of a power availability verification surveillance, at 2145, the voltage on Engineered Safeguards (ES) 4160 Volt Alternating Current (VAC) bus A and ES 4160 VAC bus B was observed to be 4350 VAC. This value exceeded the surveillance procedure limit of 4300 VAC. The shift supervisor entered Improved Technical Specification Limiting Condition for Operation (LCO) 3.0.3. The System Dispatcher was requested to reduce the grid voltage affecting the 230 Kilovolt (KV) switchyard, which feeds the 4160 VAC ES busses via the Offsite Power and the Back-Up ES transformers. <br /><br /> By 2210, the ES 4160 VAC A and B bus voltages were observed to be less than 4300 VAC. No reactor shutdown was initiated since the elevated voltage condition existed for less than one hour. During this event, no loss of function occurred and no measurable damage or degradation was experienced by any associated system or component. The cause of this event was the overly conservative upper voltage limits specified in the surveillance procedure. Corrective actions include the performance of no-load voltage drop calculations, revision of applicable procedures to reflect the allowable bus voltage limits, and an evaluation of an upper bus voltage alarm installation.
3021994003 | Crystal River 3 | 06/15/1993 | 07/22/1994 | 9407260331 | <strong>Personnel Error Leads to Entry into a High Radiation Area without Proper Dosimetry Equipment and Violation of Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1993, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION), operating at 100% reactor power and generating 862 megawatts. A contract employee entered the Auxiliary Building Triangle Room, posted as a 'High Radiation Area', without a dose rate meter or an alarming dosimeter, contrary to the requirements of Technical Specification 6.12.1. The individual had properly logged onto the appropriate Radiation Work Permit (RWP).<br /><br /> After realizing that he was in a High Radiation Area without the proper dosimetry equipment he exited the area and Health Physics (HP) personnel were notified of the event. A subsequent survey performed by HP technicians determined that the highest dose rate in the area traversed by the individual was 7 millirem/hour. Personal dosimeter data indicated that the individual received a dose less than the lower limit of detection. The root cause of this event was an isolated personnel error. Corrective actions include counseling the individual and a review of this event by engineering personnel. This report is submitted in accordance with 10CFR50.73(a)(2)(i)(B). <br /><br /> The delay in reporting this event is attributed to a series of two separate administrative errors. Corrective actions have been implemented to prevent recurrence of these delay problems.
3021994004 | Crystal River 3 | 07/01/1994 | 08/17/1994 | 9408240084 | <strong>Failure to Revise Procedure Causes Non-Conservative Setpoint Adjustment Resulting in Degraded Operation of ATWS-AMSAC System</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1994, Crystal River Unit-3 was at 100% power, preparing to reduce reactor power to perform maintenance. Instrument and Control technicians had recently performed an ATWS-AMSAC (Anticipated Transient Without Scram-Mitigation System Actuation Circuitry) surveillance. The procedure they used was not revised after the installation of a modification, and setpoints were nonconservatively adjusted. <br /><br /> As power descent was progressing, operators noticed the ATWS 'TURB AMSAC LOW FLUX BYPASS' annunciator began to alarm every few seconds. The plant was at approximately 89% reactor power. Plant operators realized the trip capability of ATWS-AMSAC was bypassed; plant conditions were substantially above the ATWS-AMSAC arming setpoint of 45% reactor power; and the discrepancies were probably caused by the recently completed surveillance. On July 5, 1994, the plant was returned to greater than 89% reactor power, arming ATWS-AMSAC. <br /><br /> On July 7, 1994, the appropriate ATWS-AMSAC setpoints were reset to correct values and a revised procedure performed to assure proper operation of all system modules. The cause of this event was personnel error in failing to assure revision of a procedure following a modification, compounded by further technical problems. This event did not compromise the health and safety of the general public. This report is submitted in accordance with 10CFR50.73(a)(2)(ii)(B)
3021994005 | Crystal River 3 | 09/28/1994 | 10/28/1994 | 9411040297 | <strong>Personnel Error Leads to Failure to Perform Reactor Coolant Pump Motor Flywheel Surveillance Resulting in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 878 megawatts. Discussions were being conducted by FPC personnel addressing the ISI examinations and requirements relative to the upcoming Refuel 10 outage. At that time, it was determined that CR-3 had violated the Technical Specifications (TS) relative to Inservice Inspection (ISI) requirements, due to failure to perform reactor coolant pump motor flywheel surface examinations during the first ISI ten year interval expiring in 1987.<br /><br /> The cause of this event was cognitive personnel error for failure to perform the required examination, to establish and document an alternative examination, or to secure relief from the requirement. <br /><br /> Corrective action includes counselling, a regulatory review to determine future actions, and appropriate flywheel surface examinations. Following a review of ISI data and industry experience, FPC has concluded that this event has not created a safety concern. This report is submitted in accordance with 10CFR50.73(a)(2)(i)(B).
3021994006 | Crystal River 3 | 10/06/1994 | 03/26/1996 | 9704010008 | <strong>Deficiency in understanding of Technical Requirements Leads to Nonconservative Safety Systems Setpoint and Violations of Improved Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% power. <br /><br /> It was determined that the potential existed for CR-3 to have operated outside plant Improved Technical Specifications (ITS) relative to the Reactor Protection System (RPS) setpoints. FPC personnel were reviewing a revised calculation when it was discovered that RPS setpoints may not be conservative relative to ITS. A further review of RPS setpoints determined that the Variable Low Pressure Trip (VLPT) setpoint was set at the ITS limit without provision for instrument error. The Shutdown Bypass trip setpoint was also found to be set at its ITS limit. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The remainder of the RPS trip setpoints were determined to be in compliance with ITS requirements. Subsequent evaluations determined that one Emergency Feedwater Initiation and Control System (EFIC) setpoint, two Engineered Safeguards Actuation System Bypass bistable setpoints, and instruments used to monitor Reactor Coolant System (RCS) total flow were also potentially non-conservative relative to ITS. The cause of these events was personnel error. Corrective actions include: implementation of a setpoint action plan encompassing recalibration, procedure changes, and assuring adequate setpoints for other actuation systems.
3021994007 | Crystal River 3 | 10/12/1994 | 11/10/1994 | 9411180255 | <strong>Personnel Error Leads to Failure to Perform Surveillance Resulting in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 878 megawatts. While performing a general review of containment penetration data, FPC personnel identified two Reactor Building (RB) containment penetrations and their associated test taps which were not being properly surveilled. Failure to surveil these RB penetrations constitutes a violation of Technical Specifications (TS) and is reportable under 10CFR50.73(a)(2)(i). <br /><br /> A recent modification had installed flanges on both ends of the RB containment penetrations. Additionally, leak rate valves were installed on the ends of the penetrations located outside containment. Immediately after identifying the error, a verification was conducted that determined the RB containment penetrations had blind flanges installed and valves were closed and capped in compliance with TS. Additional corrective action to prevent recurrence has been implemented.
3021994008 | Crystal River 3 | 10/11/1994 | 01/18/1995 | 9501250205 | <strong>Inattention to Detail Leads to Failure to Complete Surveillance Test Within Designated Time Period Resulting in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 was in MODE 1 (MODE ONE), operating at 100% reactor power and generating 877 megawatts. FPC personnel incorrectly concluded that a procedural note permitted a 4 hour vice 1 hour time period to verify the required circuit status from the time the diesel generator (EGDG) was declared inoperable during performance of a functional test. Several hours after the applicable conditions of the Technical Specification (TS) Limiting Conditions for Operation (LCO) were entered, operators were notified the functional test procedure was complete. The EGDG was started and the TS LCOs were exited. Since completion of the functional test procedure occurred within 4 hours, operators did not perform the Power Distribution Breaker Alignment And Power Availability Verification Surveillance procedure (SP-321). <br /><br /> On October 12, 1994 the on-coming shift questioned the previous shift logs, and recognized they had not met the TS requirement to perform SP-321. Failure to complete this verification constitutes a TS violation and is reportable under 10CFR50.73. The cause was inattention to detail coupled with poor communication and teamwork between licensed operators. Corrective actions for this event include actions to improve communications and teamwork, and applicable procedure revisions.
3021994009 | Crystal River 3 | 11/16/1994 | 11/20/1996 | 9611270176 | <strong>Unauthorized Tests Involving Makeup Tank Level and Pressure Result in Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (Power Operation), operating at 100% reactor power and generating 880 megawatts. FPC determined insufficient margin existed in the Makeup Tank (MUT) pressure/level operating curve, causing CR-3 to periodically exceed design basis (DB) conditions. On September 5, 1994, data was collected by control room operators conducting an evolution in which MUT pressure was set at high level limits and MUT level was decreased from high to low level limits. Approximately 10 months later, it was discovered that a similar unauthorized test had been performed the previous day on September 4, 1994. Additional issues associated with this event include issuance of a revision to the above plant operating curve differing from the Emergency Operating Procedure (EOP) requirements and potential vortexing in the Borated Water Storage Tank (BWST). <br /><br /> Several causes for this event include insufficient management oversight; misunderstanding by operations and engineering personnel of the importance of the MUT pressure limit curve, insufficient questioning attitude as to an alarm condition by an operating crew; poor communication between engineering and operations; and insufficient documentation of design basis information. Curves have been corrected, disciplinary actions have been taken, an action plan was established for MUT, BWST, and RB Sump inter-related issues, and safety and conservative decision making have been emphasized.
3021994010 | Crystal River 3 | 11/14/1994 | 12/23/1994 | 9412300099 | <strong>Personnel Error Leads to Breach of Control Complex Habitability Envelope Resulting in Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 880 megawatts. During a routine plant tour, a shift manager discovered that a door between the control complex and the building roof had been blocked open for roofing work. Electrical extension cords were running through the doorway. No compensatory measures were in effect and no breach permits were issued. On November 23, 1994, FPC personnel determined that this event was reportable since a breach of this magnitude places CR-3 outside the design basis and is reportable under 10CFR50.73.a.2.ii.B. The primary cause of this event was personnel error for failure to recognize the requirement to maintain the integrity of the control complex habitability envelope. A secondary cause was the failure of the corrective action for a similar event involving the text of warning signs. Corrective actions include replacement of signs and additional training for applicable personnel.
3021994011 | Crystal River 3 | 11/15/1994 | 12/15/1994 | 9412230243 | <strong>Personnel Error Leads to Missed Surveillance Resulting in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 880 megawatts. Technical Specification (TS) Surveillance Requirement 3.6.6.1 requires that each unsecured reactor building spray valve in the flow path and the first normally closed valve in each branch line be verified in its correct position every 31 days. The procedure (SP-347) used the Main Control Board position indication lights to verify BSV-11 and BSV-12. CR-3 personnel had previously completed a modification to permanently close, remove power from, and electrically disconnect valves BSV-11 and BSV-12. When completed all control room indication was also eliminated, however the surveillance requirement was not revised. Subsequently, whenever SP-347 was performed, a notation was written in the procedure records that stated the valve indications had been removed. <br /><br /> On November 2, 1994 a Temporary Procedure Change (TPC) was written to remove BSV-11 and BSV-12 from SP-347. Subsequent review of the TPC change request determined that TS 3.6.6.1 had been violated for failure to perform a required surveillance within the specified frequency. The primary cause of this event was personnel error. Corrective actions include advising operations personnel on lessons learned, and revising the applicable procedure and TS Bases.
3021994012 | Crystal River 3 | 11/28/1994 | 12/28/1994 | 9501050130 | <strong>Personnel Error Leads to Incomplete Surveillance Resulting in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 880 megawatts. At 0900, FPC personnel determined that CR-3 had violated Technical Specification (TS) Surveillance Requirement 3.3.8.1 for failure to perform a required surveillance. The TS Bases for surveillance requirement 3.3.8.1 states that a CHANNEL FUNCTIONAL TEST is performed on each Emergency Diesel Generator (EGDG) Loss Of Power Start (LOPS) channel to ensure the entire channel will perform its intended function. <br /><br /> The original CR-3 TS did not contain surveillance requirements for the First Level Undervoltage Relays (FLUR). The Improved TS added the EGDG LOPS section which includes FLUR relay Channel FUNCTIONAL test with a 31 day surveillance requirement. The cause of this event was personnel error in that FPC engineering personnel failed to recognize that the channel test included a monthly check of all three FLUR input relays. Corrective actions included counselling and procedure revision.
3021994013 | Crystal River 3 | 09/13/1994 | 01/20/1995 | 9501300243 | <strong>Marine Organism Biofouling Causes Heat Exchanger Partial Blocking and Potential for Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE (POWER OPERATION), operating at 100% reactor power and generating 872 megawatts. FPC personnel determined that they were unable to conclusively assure continuous operation within the design basis (DB) as a result of previous occurrences of raw water heat exchanger partial plugging and fouling. FPC cannot conclusively prove that CR-3 had, at all times, remained within the DB. <br /><br /> The cause of the heat exchanger fouling is due to marine organism growth. A series of corrective actions are being implemented to minimize the impact of heat exchanger performance due to marine organism biofouling. <br /><br /> On December 20, 1994 as a result of an evaluation of this issue, FPC management determined that this issue should be reported as a voluntary Licensee Event Report (LER) under 10CFR50.73.
3021994014 | Crystal River 3 | 10/31/1994 | 01/20/1995 | 9501250278 | <strong>Reactor Building Fan/Cooler Operation Develops Cooling System Flow Imbalance and Heat loading Having the Potential for Operation Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1994, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE ONE operating at 100% reactor power and generating 879 megawatts. FPC personnel determined that an inconsistency existed between the design and operation of the plant relative to Nuclear Service Closed Cycle Cooling (SW) system reactor building (RB) fan/cooler heat loads during a postulated design basis Loss of Coolant Accident (LOCA). Certain three RB fan/cooler operating scenarios establish a condition which may cause reduced component flows and the allowable SW supply temperature to be exceeded for a short period of time post LOCA. <br /><br /> The cause of the potential challenge to the SW system performance resulting from three RB fan/cooler operation is personnel error by the FPC design organization. A series of corrective actions are being implemented which include both procedural and administrative changes and an evaluation of potential plant modifications. <br /><br /> On December 20, 1994 as a result of an evaluation of this issue, FPC management determined that this issue should be reported as a voluntary Licensee Event Report (LER) under 10CFR50.73.
3041994001 | Zion 2, Zion 1 | 03/02/1994 | 03/31/1994 | 9404070168 | <strong>Actuation of Unit 2 Station Blackout Loads During Restoration of Buses 147/247 to Offsite Power.</strong><br /><i>Abstract:&nbsp;</i>On 03/02/94, Technical Staff Special Procedure (TSSP) 44-93, was being performed on the 0 Emergency Diesel Generator (EDG) [EK] following a modification that had been installed on the 0 EDG to allow it to supply power to Essential Service (ESS) Buses 147 and 247 (Attachment 1). The purpose of this testing was to verify that 0 EDG could maintain its' frequency and voltage requirements while supplying power for the Station Blackout loads for both ESS buses 147 and 247. <br /><br /> During the performance of TSSP 44-93, both of the 0 EDG output breakers tripped open during reverse power. Due to the installation of a jumper for the test, the Unit 2 blackout loads automatically sequenced onto 0 EDG. <br /><br /> The cause of this event was a procedural deficiency. TSSP 44-93 did not take into consideration that the control room megawatt indication for the 0 EDG was not accurate enough for the evolution that was required. <br /><br /> This event had minimal safety significance. Corrective actions include determining that TSSP 44-93 will not be performed again, and reviewing other procedures to ensure this condition could not recur. ler
3041994002 | Zion 2, Zion 1 | 03/07/1994 | 07/25/1994 | 9509290009 | <strong>Exceeded Limiting Condition for Operation 3.7.2. Action e for Placing Unit in Mode 4 with a Turbine-Driven and Motor-Driven AFW Pump Inoperable.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 7, 1994. during Technical Staff Surveillance (TSS) 15.6.43, 'Endurance Testing of Diesel Generators During Refueling', the 2A Auxiliary Feedwater Pump (AFW) [BA] tripped on overspeed. At 0533 hours, the 2A AFW pump was declared inoperable and a Periodic Test (PT)-14, 'Technical Specification Relate Inoperable Equipment Test Sheet,' was initiated. At 0618 hours, the 2B Diesel Generator (DG)[EK] began experiencing frequency swings and was manually tripped. The 2B DG was also declared inoperable and a PT-14 was initiated. On March 8, 1994. it was determined that Technical Specification (Tech Spec) LCO 3.7.2 Action e should have been entered at 0618 hours on March 7, 1994 due to Tech Spec 3.0.5 applicability for the redundant motor driven AFW pump inoperability. The cause of exceeding LCO 3.7.2 Action e is personnel error. The operators failed to recognize that the inoperability of the 2B DG in conjunction with the inoperable 2A AFW pump resulted in the 2C AFW pump being inoperable. Corrective Actions include tailgating this event with all operating shifts, revising PT-14 to require review of Technical Specification 3.0.5 and the ZODM for applicability, and training on the change. \ler
3041994004 | Zion 2 | 04/07/1994 | 05/09/1994 | 9405130205 | <strong>Entry into Technical Specification 3.0.3 Twice within Two Hours Due to Problems with Two Auxiliary Feedwater System Motor Operated Valves.</strong><br /><i>Abstract:&nbsp;</i>On 04/01/94, the 2A Auxiliary Feedwater Pump (AFW)[BA] pump was declared inoperable after it tripped on overspeed. This placed the Unit 2 on a 7 day Limiting Condition for Operation (LCO) per Technical Specification 3.7.2.d. On 04/07/94, while testing the 2B AFW pump, 2MOV-FW0050 failed to close electrically. Since 2MOV-FW0050 is a containment isolation valve as defined by Technical Specification 3.9.3A, Unit 2 was placed on a 4 hour LCO clock requiring the valve be manually closed and deenergized. At 1541, the valve was manually closed, deenergized and the LCO clock for containment isolation was terminated. The combination of the inoperable 2A AFW pump and the inoperable 2MOV-FW0050 placed Unit 2 in Technical Specification 3.7.2.e requiring the unit to be in hot shutdown within 20 hours and also Technical Specification 3.0.3 requiring the unit to be in cold shutdown in 48 hours. At 1622 hours, 2MOV-FW0053, '2C S/G Isolation Valve for the 2C AFW pump system', could not be throttled open to indicate 115-120 gpm per the requirements. It was reasoned that the problem was with the valve internals and the decision was made to take Unit 2 to cold shutdown. <br /><br /> The cause of the failure of 2MOV-FW0050 to close was attributed to component failure with sticky auxiliary contacts. The cause of the 2MOV-FW0053 valve failing to indicate 115 gpm flow rate was component failure with a square root extractor in the flow indication. Corrective actions include revising a maintenance procedure, reviewing the event with the electricians, and replacing the square root extractor. ler
3041994005 | Zion 2 | 07/25/1994 | 08/24/1994 | 9409060104 | <strong>Violation of Technical Specification 4.0.5. Due to an Incorrect Procedure Change to Include Acceptance Criteria.</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1994, during a routine Inservice Testing (IST) package review by System Engineering, it was discovered that 2AOV-SS9356B should have been declared inoperable on June 8, 1994 because its stroke time had exceeded the Acceptance Criteria identified in Periodic Test (PT)-300, 'Containment Isolation Valves Stroke Time Verification' . However, no action was required at the time of discovery because the maintenance had already been completed on July 8, 1994 and the stroke time was verified to be acceptable. <br /><br /> The cause of this event was procedure deficiency. 'PT-300' did not specify the correct Action Limit range on June 8, 1994 when 2AOV-SS9356B was tested. The safety significance of this event was well within the bounds assumed in the UFSAR.<br /><br /> Corrective Actions included changing PT-300 to reflect the correct calculated values, and reviewing the PTs associated with valves that had stroke time acceptance criteria adjustments to ensure the correct values were in the PTs. ler
3041994006 | Zion 2, Zion 1 | 08/23/1994 | 09/22/1994 | 9409280098 | <strong>Safety Related 480V Motor Control Center Feed Breaker Overcurrent Setting was Below the Maximum Loading Value</strong><br /><i>Abstract:&nbsp;</i>As a result of the Lessons Learned Initial Notification 94-059 from Dresden Station regarding the inadvertent tripping of a safety-related Motor Control Center (MCC) during testing, a review of safety-related 480 VAC MCC [ED] supply breaker long-time overcurrent settings at Zion Station was initiated. This review was completed on 8/23/94 and showed that the feed breaker overcurrent relay setting feeding 480 Volt Motor Control Center (MCC) 2371 was lower than the maximum load shown in the Electrical Load Monitoring System (ELMS) program for Zion Station. <br /><br /> The cause of the event was personnel error. In 1981, the overcurrent relay setting on the feed breaker to MCC 2371 was determined based on the existing coincidental load on the MCC instead of the maximum allowable MCC load. <br /><br /> The safety significance of this event was minimal, as redundant equipment fed from other safety-related supplies exist that could have operated during an accident, and the health and safety of the public were not affected. <br /><br /> Corrective actions include securing the Prime Computer Room Air Conditioning unit (00V063), a non-safety load fed off of MCC 2371 to bring the maximum load value below the breaker setting, resetting the overcurrent relay setting during the 1995 Z2R13 outage, and determining that the other essential MCC's feed breaker overcurrent relay settings were set above the maximum coincidental load value.
3041994007 | Zion 2 | 09/02/1994 | 10/03/1994 | 9410070167 | <strong>Exceeding Technical Specification 3.15.2.C for the 2A Diesel Generator Because the Allowed Interval for IST testing was Exceeded.</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1994, during the In-Service Testing (IST) review of Periodic Test (PT) 11B-2A, '2A Emergency Diesel Generator (EDG) [EK] Fuel il Transfer Oil Pump Performance Test', the IST engineer discovered that vibration readings taken on the 2A EDG east and west fuel oil transfer pumps were low relative to the previous quarterly test, The Vibration Coordinator performed a spectral analysis and determined that the readings were inconclusive. Since the critical date for performing the surveillance was August 25, 1994, the 2A diesel fuel oil transfer pumps were declared inoperable for exceeding the critical test due date. The 2A EDG was declared inoperable due to its support equipment being inoperable. <br /><br /> The cause of this event was management deficiency. The vibration data is not required to be verified by the Vibration Coordinator before the PT is declared acceptable. <br /><br /> Corrective actions include retaking vibration readings on the 2A EDG fuel oil transfer pumps, verifying their acceptability, reviewing assignment of data acquisition, and revising the vibration program administrative procedure to require Vibration Coordinator review. ler
3041994008 | Zion 2, Zion 1 | 08/03/1994 | 09/02/1994 | 9410180113 | <strong>Entry into Technical Specification 3.0.3 Due to Two Emergency Diesel Generators Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 3, 1994, Periodic Test (PT)-11-DG2A, 'Diesel Generator 2A Loading Test' was being performed on the 2A Emergency Diesel Generator (EDG)[EK]. The 2A EDG magnetic pickup target gear shaft failed during PT-11-DG2A and the 2A EDG was declared inoperable. This was the second failure of the 2A EDG magnetic pickup target gear shaft. An earlier engineering analysis providing reasonable assurance that the 0 EDG was operable and did not have this shaft problem was changed and the 0 EDG also was declared inoperable. With two EDGs inoperable, Technical Specification 3.0.3 was entered on Unit 2. Permission to operate Unit 2 for an additional 20 hours was requested from the NRC and granted. On August 4, 1994, a new magnetic pickup target gear shaft was inspected and installed on the 2A EDG and the 2A EDG was declared operable. Technical Specifications 3.0.3 was exited. <br /><br /> The cause of the failure of the magnetic pickup target gear shaft was component failure. A manufacturers defect of the magnetic pickup target gear shaft in the 2A EDG caused the shaft to fail. The safety significance of this event was minimal.<br /><br /> Corrective actions included inspecting and installing new shafts of known quality and original design in the 2A and 0 EDGs. This type of magnetic pickup target gear shaft was only installed on the 1A, 2A, and 0 EDGs. Further corrective action included initiating an exempt change to replace the smaller two piece shaft design in 1A, 2A, and 0 EDGs with a larger one piece shaft design to add margin to the shaft design. ler
3041994009 | Zion 2, Zion 1 | 09/15/1994 | 10/14/1994 | 9410200113 | <strong>Failure to Submit Special Report within 30 Days per Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1994, while reviewing the monthly Operating Report, the Regulatory Assurance Supervisor or noted that, contrary to the requirements of Zion Technical Specification 4.15.1.B.5, a report of the failure of the 2A Emergency Diesel Generator (EDG) [EK] which occurred on August 3, 1994 was being submitted to the NRC more than 30 days after the event. <br /><br /> A subsequent review of past monthly Operating Report submittals revealed that EDG failure reports have been issued late on 17 other previous occasions. The latest any individual failure report was issued was identified as 13 days (43 days after the failure). <br /><br /> The cause of this event is management deficiency. The process by which EDG failure reports was submitted did not ensure that EDG failures would be reported within 30 days of the date on which the failure occurred. <br /><br /> There is no safety significance to this event since submittal of the 30 day EDG failure report is an administrative requirement of the Technical Specifications. <br /><br /> Corrective actions include reviewing other Technical Specification special reporting requirements to ensure no other late submittals could be identified and revising ZAP 700-08, 'Root Cause Analysis Program', to identify EDG failures requiring 30 day reports. \ler
3041994010 | Zion 2 | 10/02/1994 | 11/01/1994 | 9411090280 | <strong>Voluntary Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1994, Unit 2 was in Mode 1, Maintenance was planned for replacing the Instrument Air (IA) [LD] isolation valve for 0AOV-SW0021, 'U2 Auxiliary Building Room Coolers Service Water (SW)[BI] Inlet Stop Valve.' The out-of-service isolated the makeup capability to the Isolation Valve Seal Water (IVSW) tank. This action caused Unit 2 to voluntarily enter Technical Specification (T.S.) 3.0.3. <br /><br /> The cause of this event was Management Deficiency. No guidance exists regarding voluntary entry into T.S. 3.0.3. A contributing cause of this event was Training/Qualification. It was not apparent to licensed personnel on and off shift that any T.S. 3.0.3 entry required an LER. <br /><br /> Corrective Actions include developing and implementing guidance regarding voluntary entry into T.S. 3.0.3, and reviewing this guidance and its associated reportability requirements with all licensed personnel. ler
3041994011 | Zion 2, Zion 1 | 10/29/1994 | 05/09/1995 | 9505150119 | <strong>Retraction of Licensee Event Report 2-94-011</strong><br /><i>Abstract:&nbsp;</i>Further review of this event has determined that it is not reportable per 10CFR50.73. LER 2-94-011 was submitted based on the assumption that the licensing basis for Zion's Electrical Systems is a dual unit loss of off-site power coincident with a Loss Of Coolant Accident (LOCA). However, additional discussion and review has determined that the licensing basis for Zion's Electrical Systems is a single unit loss of off-site power coincident with a LOCA. If Unit 1 had experienced a loss of offsite power coincident with a LOCA, the 0 Diesel Generator (DG)[EK] would have closed into Bus 147, and the 0 DG event fan would have been energized. If Unit 2 had experienced a loss of offsite power coincident with a LOCA, 0 DG would have closed into Bus 247, and the 0 DG vent fan could have been powered through Bus 147 from offsite power. <br /><br /> Since the 0 DG vent fan was always able to be energized, the 0 DG was never inoperable, Zion Station's Technical Specifications were never violated, and Zion Station was never outside its license basis. <br /><br /> Based on this information, Licensee Event Report 2-94-011 dated 12/08/94 is being retracted.
3041994012 | Zion 2 | 07/28/1994 | 12/12/1994 | 9412190083 | <strong>Operators Miss Valve Stroke Time Oustside of the IST Acceptable Range Low</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1994, Unit 2 was in Mode 1 at 100% power. Operations was performing PT-300, 'Containment Isolation Valves Stroke Time Verification.' During the performance of section 5.12, 'Stroke Timing Requiring Operations From the Waste Gas Control Panel,' the NSO stroked timed LCV-DT1003, 'Reactor Coolant System (RCS)[AB] Drain Pump Discharge Valve,' at approximately 9.36 seconds on the first stroke. The acceptable range for LCV-DT1003 was 12.0 - 20.1 seconds and the action limit was greater than 24.1 seconds. During the performance of the test and at the completion, it was not recognized that LCV-DT1003 was outside of the acceptable range low. Since the valve was not immediately stroked a second time, while in the alert range, the valve was inoperable on this date. On November 11, 1994, Site Quality Verification (Quality Assurance) reviewed the test completed on July 28, 1994 and discovered the deficiency. <br /><br /> The event was caused by personnel error and management deficiencies. The NSO and LSS failed to recognize that LCV-DT1003 was in the alert range. Corrective actions include, in part, the following: 1) Counselling for the personnel and: 2) Procedure changes to verify valve stroke times are within acceptable ranges and to document the action prior to proceeding to the next section of the Periodic Test.
3051994001 | Kewaunee | 01/07/1994 | 02/07/1994 | ML11188046 | <strong>Failure of Radiation Detector Results in Actuation of Steam Generator Blowdown Isolation</strong><br /><i>Abstract:&nbsp;</i>The following event is reportable as an actuation of steam generator blowdown isolation valves which are engineered safety features. On January 7, 1994 at 0100 hours, the condenser air ejector radiation monitor, R-15, suddenly increased from its normal reading of 60 counts per minute (CPM) to 1.0E5 CPM which activated its high alarm.<br /><br /> The high alarm from the monitor caused the steam generator blowdown isolation valves and the steam generator blowdown sample isolation valves to close as designed. The plant was in cold shutdown when the actuations occurred. The high alarm signal from R-15 and the subsequent associated engineered safety feature actuations were caused by the failure of the monitor's Geiger Mueller tube. The tube was replaced during the monitor repair process. Two additional electrical components in R-15's circuitry were conservatively replaced because they had apparently experienced mild degradation. <br /><br /> The radiation monitor was returned to service on January 13, 1994 at 1700 hours.
3051994002 | Kewaunee | 01/10/1994 | 02/09/1994 | ML11188045 | <strong>Personnel Error and Weakness in Implementation of Post Maintenance Testing Results in Missed Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1994, the plant was in intermediate shutdown and in the process of heating-up. Plant personnel realized that two containment isolation valves may not have been tested in accordance with Kewaunee Nuclear Power Plant's (KNPP's) Technical Specifications. KNPP Technical Specification 4.4.b has been interpreted to require a Type C local leak rate test be performed on containment isolation valves after making torque switch adjustments followed by motor operated valve (MOV) diagnostic testing. Although Wisconsin Public Service Corporation (WPSC) does not agree with this interpretation, this event is being reported as a violation of KNPP's Technical Specifications. However, WPSC management conservatively decided to stop the plant heat up and return the plant to a cold shutdown condition to perform a local leak rate test on the valves. The appropriate leak rate testing was successfully completed in accordance with surveillance procedure SP 56A-090, Containment Local Leak Rate Type B & C Test. Plant heat up was resumed the same day. <br /><br /> Corrective actions include: Revising MOV test procedures to incorporate the requirement to consult the Appendix J Leak Rate Test Coordinator prior to performing diagnostic testing of containment isolation valves, presenting training to the maintenance groups on containment integrity regulations, performing local leak rate testing of containment isolation valves following torque switch adjustments, and reviewing the implementation of the post maintenance test program.
3051994003 | Kewaunee | 04/07/1994 | 05/09/1994 | ML11188046 | <strong>Local Leak Rate "As Found" Leakage Exceeds Technical Specification Requirements Due To Improperly Seated Check Valves.</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1994, with the plant in refueling shutdown, two local leak rate test volumes associated with the reactor coolant pump A and B seal injection lines could not be pressurized to the required 46 psig. The test volumes did not pressurize due to check valves CVC-206A and CVC-205B not seating properly. As a result, Kewaunee's total 'as found' maximum pathway leakage exceeded 0.60 La. For Kewaunee, 0.60 La is equal to a leakage of 322,800 standard cubic centimeters per minute (sccm). The redundant seal injection line check valves indicated acceptable leakages of 227 sccm and 12.2 sccm. The seal injection lines are 2-inch lines that supply water to the seals on each reactor coolant pump. On April 20, 1994, a 2-inch check valve in the charging line also failed to seat properly preventing the associated test volume from pressurizing to 46 psig. The redundant valves indicated an acceptable combined leakage of 58.4 sccm.<br /><br /> There are no safety implications associated with this event since in each instance that a valve had a high leak rate, the redundant valve had an acceptable leak rate as shown by the total 'as found' minimum pathway leakage of 3,561.1 sccm. As of May 4, 1994, Kewaunee's total 'as left' maximum pathway leakage was 7,496.8 sccm. Kewaunee has initiated an engineering support request which will further investigate the failures of these valves and determine if acceptable replacement options are available.
3051994004 | Kewaunee | 04/22/1994 | 05/23/1994 | ML11188047 | <strong>Intergranular Attack And Intergranular Stress Corrosion Cracking Result In Defective Steam Generator Tubes</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1994, with the plant in refueling shutdown, the in-service inspection and resultant plugging of Steam Generator (SG) tubes was completed for the 1994 refueling outage. The in-service inspection found 77 tubes in SG A and 28 tubes in SG B which were considered defective. In accordance with the Kewaunee Nuclear Power Plant (KNPP) technical specifications (TSs), SG A was categorized as C-3, since more than 1% of the inspected tubes were considered defective in the sleeve upper expansion joint region. As required by KNPP's TS, this Licensee Event Report provides the required 30 day written report to the Nuclear Regulatory Commission. <br /><br /> The predominant SG tube degradation mode at KNPP is outside diameter intergranular attack and outside diameter intergranular stress corrosion cracking (IGA/IGSCC). In accordance with KNPP's TS, all defective tubes were plugged. This increased the overall equivalent plugging percentage from 10.37 percent to 11.87 percent for the 1994-1995 operating cycle. <br /><br /> The secondary side boric acid and Morpholine (or alternative amine) addition programs will continue during the 1994-1995 operating cycle to reduce the caustic environment and corrosion/erosion on the secondary side.
3051994005 | Kewaunee | 05/09/1994 | 06/06/1994 | ML11188047 | <strong>Radiation Monitor Alarm Resulted In An Engineered Safeguard Feature Actuation Of Steam Generator Blowdown Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>The following is a description of an actuation of steam generator blowdown isolation valves which are engineered safety features. At 1318 hours on May 9, 1994, the condenser air ejector radiation monitor, R-15, suddenly increased to 1.0E6 CPM which activated its high alarm. The monitor's high alarm caused the steam generator blowdown isolation valves and the steam generator blowdown sample isolation valves to close as designed. Sampling determined that the high alarm on R-15 was not caused by primary to secondary leakage. The plant was at 35 percent power when the actuations occurred. <br /><br /> The cause of the high alarm signal from R-15 could not be conclusively determined. However, corrective actions were taken to isolate the pre- amplifier from its ground to decrease the interference on the detector channel. It appears that this action has decreased the interference on the channel. <br /><br /> The radiation monitor was returned to service on May 13, 1994, at 0904 hours.
3061994001 | Prairie Island 2, Prairie Island 1 | 04/12/1994 | 05/12/1994 | 9405180357 | <strong>Inoperability of One Train of Post-Accident Containment Hydrogen Monitoring</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1994 an I&C Technician was performing a routine surveillance test of the Unit 2 containment hydrogen monitors. When taking as-found readings, the technician noticed that the containment pressure reading on Train B was significantly out of specification. The calibration constants were read, and it was then discovered that the Total Pressure Offset constant was in error. The technician entered the correct value, as directed by the procedure, and notified the system engineer. At the conclusion of the test, the technician and the system engineer reviewed e procedure and calibration card data. Based on review of previous surveillance data and discussions with several technicians, it was determined that the Train B hydrogen monitor had probably been inoperable since March 15, when the monthly test had last been performed. The technician that performed the March 15 test apparently had made an erroneous keystroke while displaying containment data. After the Total Pressure Offset was read, the technician should have pushed the ENTER key to move on to the next calibration constant. Instead, it appears the technician pushed the NEW CONSTANT key inadvertently, and then when the ENTER key was pushed, the incorrect calibration constant was entered. Procedures will be revised to prevent recurrence.
3061994002 | Prairie Island 2, Prairie Island 1 | 07/21/1994 | 08/12/1994 | 9408240229 | <strong>Unit 2 Turbine-Generator Trip/Reactor Trip Caused by Failure of a West Pipe Sprinkler Head</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1994, Unit 2 was at 100% power. A wet pipe sprinkler system had been recently installed at the turbine-generator to provide protection against lube oil fires. On the morning of July 21, a hydrostatic test of the fire protection piping was begun. After the system had been at test pressure for about 1 3/4 hours, a sprinkler head activating device failed and water was sprayed on the main generator bushings, establishing a current path from B phase bushing to ground. The generator ground relay actuated the 86 generator lockout relay, which caused a reactor trip at 1019 hours. The unit responded as expected to the automatic trip, including automatic start of the auxiliary feedwater pumps on low steam generator level. Leaking feedwater isolation valves contributed to an RCS cooldown, and the resulting low pressurizer level caused letdown isolation. Cause of the trip was determined; the bushing enclosure, neutral connection, isophase bus, and vertical link box were disassembled, inspected, cleaned, and tested; and the determination was made that there was no electrical damage. The unit was returned to service at 0703 on July 22. The turbine-generator wet pipe sprinkler system on both Units 1 and 2 has been isolated until further system evaluation can be completed.
3061994003 | Prairie Island 2, Prairie Island 1 | 10/25/1994 | 11/22/1994 | 9411300298 | <strong>Auto-Start of One Train of ABSVS on High Radiation During Restoration of a Unit 2 Seal Water Return Filter</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1994, both units were at 100% power. No. 22 reactor coolant pump seal water return filter had been removed from service for preventive maintenance. The filter was isolated and drained, and the filter element inspected. When the filter housing was being refilled and vented, at 1211 the control room received indications of high gas activity on radiation monitor 2R-30 and an auto-start of No. 122 Auxiliary Building Special Ventilation Fan. Control room operators evaluated the situation and manually started No. 121 Auxiliary Building Special Ventilation Fan to help clean up the Auxiliary Building atmosphere. Discharge of the Special Ventilation Fans is through particulate/absolute/charcoal filters to the outside atmosphere. Access to the Auxiliary Building was restricted while the Auxiliary Building atmosphere was being cleaned up. The 2 maintenance workers working on the filter and 10 other workers in the Auxiliary Building were contaminated with radioactive noble gases and particulate daughters. Decontamination of the workers was easily accomplished; individual exposures were less than 1 mRem. About 2.5 Curies of noble gases were released during the event. Calculated dose at the site boundary was about 0.002 mRem, which is about 0.01% of the annual dose limit.
3061994004 | Prairie Island 2, Prairie Island 1 | 12/20/1994 | 01/18/1995 | 9501250370 | <strong>Discovery That One Cooling Water System Snubber Is Not Being Tested As Required</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1994, both units were at 100% power. A 10-year InService Inspection of pipe hangers had been performed. The inspection identified a hydraulic snubber on cooling water piping to No. 23 Fan-Coil Unit, in location 2-CWH-621, which appeared to have a slight fluid leak. The snubber was declared inoperable, removed for testing, and a replacement snubber was installed; those activities used about 6 hours of the 72-hour Limiting Condition for Operation of Technical Specification 3.12. The removed snubber passed its functional test. Though the snubber appeared to be leaking a small amount of fluid, the fluid level in the reservoir was adequate. While researching the maintenance history of the snubber, it was determined that the snubber had been installed during a modification in 1983, and that the visual inspections required by Technical Specification 4.13 have not been performed. The visual inspections are scheduled for each refueling, though the required inspection interval is dependent upon prior inspection results and can be as long as 48 months. The previous visual inspection of this snubber was done in 1984 during the previous 10-year InService Inspection.
3091994001 | Maine Yankee | 01/05/1994 | 02/04/1994 | 9402180188 | <strong>Control Room Ventilation System inoperable During preventative maintenance</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1992, and on February 12, 1992, with the plant in the power operating condition, both trains of control room ventilation were made inoperable when panels were opened for fan maintenance. Opening the panels prevents effective isolation of both trains of control room ventilation by allowing a path for atmospheric air to enter. <br /><br /> Plant Technical Specification 3.25.B requires two trains of control room ventilation to be operable when the reactor is critical. Therefore the plant was in a condition prohibited by Technical Specifications. <br /><br /> The cause for this event appears to have been a failure to recognize how opening the panels affected the ventilation system and not having the activity classified as a cold shutdown activity.<br /><br /> Planned maintenance activities requiring the removal of these panels have been scheduled for times when the plant is in cold shutdown.
3091994002 | Maine Yankee | 02/07/1994 | 07/01/1994 | 9407060085 | <strong>Inadequate Configuration Control in Design and Operation of SG Blowdown System</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted to supply information related to inadequate configuration control in the design and operation of Maine Yankee's Steam Generator Blowdown System which resulted in operation of the plant in an unanalyzed condition. <br /><br /> On December 3, 1993, Maine Yankee recognized that station design and administrative controls did not prevent operation of the Steam Generator Blowdown System outside the bounds of Maine Yankee's transient analysis. Immediately following identification of this discrepancy, administrative controls were established to ensure conservative operation of the Blowdown System. At that time, Maine Yankee had determined that the blowdown system was operated in an unanalyzed condition, but that this condition did not significantly compromise plant safety.<br /><br /> Further analysis of the situation revealed that the fluid conditions post trip may change such that more mass would be transported from the steam generators than was originally considered. Thus, on February 7, 1994, Maine Yankee determined that the Steam Generator Blowdown system had been operated in an unanalyzed condition which may have significantly affected plant safety. Stricter administrative controls were immediately set to limit full power blowdown flow rates. <br /><br /> A thorough analysis of the safety consequences of this event has been completed. The analysis has concluded that the plant did not operate in an unsafe condition.
3091994003 | Maine Yankee | 02/22/1994 | 07/01/1994 | 9407060035 | <strong>Service Water Flow Potentially Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>The Maine Yankee Service Water system provides cooling to the Component Cooling system which cool Emergency Core Cooling equipment. Maine Yankee's response to GL 89-13 included installing flow measuring devices in the Service Water system and a review of Service Water Operational Performance Inspections at other plants. Through this review, heat exchanger flow imbalance was identified as an issue. Further analysis of flow data collected at Maine Yankee revealed that the Service Water system is susceptible to flow imbalances due to heat exchanger inlet strainer differential pressures and design differences. The inlet strainer differential pressures lead to flow imbalances which require an penalty in the system's safety analysis. As a result, on February 22, 1994, Maine Yankee concluded that, in the past, Service Water flow may not have met design basis requirements with warm river water temperatures. During the winter months the river water temperatures are low enough to provide sufficient cooling to the Component Cooling water heat exchangers. However, in the summer, the river water temperatures rise above that required to sufficiently cool the Component Cooling Water heat exchangers under all design conditions. Thus, Maine Yankee may have operated the Service Water system outside its current design basis. Maine Yankee is investigating several options to assure the Service Water system meets design requirements during summer months including: improving the screening of the service water pump intake water, improving service water pump performance, improving the flow measuring instrumentation, reviewing the design basis calculations, and establishing heat exchanger differential pressure limits.
3091994004 | Maine Yankee | 03/07/1994 | 04/06/1994 | 9404110222 | <strong>Control Room Ventilation Inoperable due to Preventive Maintenance</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1994, both trains of control room ventilation were declared inoperable for a brief period of time in order to perform preventive maintenance. <br /><br /> Entering the 'B' train air handler, AC-1B, to replace a filter, created a pathway for atmospheric air to enter the recirculation flowpath making both trains of control room ventilation inoperable. Technical Specification 3.0.A.2 was entered.<br /><br /> The consequences of this event , which occurs semi-annually for planned maintenance, were minimal since the loss of both trains was of short duration. Both trains were inoperable for a total of 16 minutes. Technical Specification 3.0.A.2 requires a reactor shutdown be commenced within one hour, however, due to the short duration of the planned inoperability, a shutdown was not commenced. <br /><br /> To eliminate the need to report this event for planned maintenance, a change to Technical Specification 3.25 'Installed Ventilation and Filter Systems' has been prepared for submission. The change would add an exception allowing a reasonable amount of time for preventive maintenance.
3091994005 | Maine Yankee | 03/17/1994 | 06/30/1994 | 9407060168 | <strong>Reg Guide 1.97 Containment Hydrogen Monitoring Instrumentation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1994 while operating at 100% power, Maine Yankee concluded that Containment Hydrogen Monitoring Instrumentation (HMI) required by Reg Guide 1.97 was outside design basis due to a cable separation problem. In the as found condition, a single fault could affect both channels of HMI. <br /><br /> During cable verification conducted in preparation for planned facilities upgrades, cables for post accident containment pressure monitoring instrumentation were found cross routed in A and C cable trays. The only redundant plant function affected by the cable separation problem was HMI. A fault in either tray would not result in loss of all HMI, however both channels of Main Control Room remote indication could be lost. The safety consequences of either case are minimal since both HMI analyzers are located in plant locations which are accessible during accident conditions. Maine Yankee reconfigured the affected cables to their correct trays on April 5, 1994. <br /><br /> Maine Yankee has determined that the HMI cable separation problem was caused by the craft crew's and field engineers' poor work practices. Their workload during the 1981 refueling outage contributed to this. The engineers were responsible for 25 design packages. Maine Yankee reviewed all 25 packages and field verified five. Two more wiring discrepancies were found. Neither discrepancy affected their system's operability or design basis. Both wiring discrepancies support the original causal analysis results. No further work packages will be reviewed.
3091994006 | Maine Yankee | 03/24/1994 | 05/16/1994 | 9405230129 | <strong>General Electric 4.1KV Magne-Blast Breaker Failures</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER describes problems experienced with General Electric 4.1KV Magne-Blast circuit breakers. On March 23, 1994, circuit breaker 3-17 for charging pump P-14B failed to close. The charging pump had not been operated since March 21, 1994, when it was shutdown and placed in auto. The failure of the charging pump circuit breaker was the fourth instance of a safety class 4.1 KV Magne-Blast circuit breaker failure since September 26, 1993. Prior circuit breaker failures were Emergency Diesel Generator, DG-1A, circuit breaker 3-12; Primary Component Cooling Pump, P-9A, circuit breaker 6-53; and Emergency Feedwater Pump, P-25C, circuit breaker 4-34. Each failure resulted from a different failure mechanism.<br /><br /> After each safety class circuit breaker failure, Maine Yankee determined a failure mechanism, except for P-25C circuit breaker, 4-34. Maine Yankee then identified the safety class 4.1 KV circuit breakers that needed to be inspected and implemented a campaign to check those circuit breakers to determine susceptibility to the failure mechanism and to correct deficiencies that were found. <br /><br /> All breakers had been overhauled by General Electric, at an on site portable refurbishment facility, during the 1993 refueling outage. Except for circuit breaker 4-34, the causes of the 4.1 KV Magne-Blast circuit breaker malfunctions appear to be related to workmanship and quality control practices during the circuit breaker overhaul. To ensure the safety class 4.1 KV Magne-Blast circuit breakers are reliable, Maine Yankee and General Electric have developed a comprehensive plan to inspect critical components of the circuit breakers that were overhauled.
3091994007 | Maine Yankee | 05/17/1994 | 06/16/1994 | 9406220406 | <strong>Emergency Core Cooling (ECCS) Subsystem Valve Not Locked</strong><br /><i>Abstract:&nbsp;</i>The Nuclear Safety Audit and Review Committee (NSARC) and the Operations Department Manager requested Maine Yankee Quality Programs Department (MYQPD) to perform an audit of the completed Emergency Core Cooling System (ECCS) locked valve program. During the assessment MYQPD discovered that a one inch globe valve of an ECCS subsystem was not locked. <br /><br /> The valve (SCC-18) was not in its proper ECCS position. An inline valve (SCC-19) serving the same function and administratively controlled by a class 'A' procedure was shut but not locked. Subsequently, SCC-19 was locked in lieu of SCC-18. <br /><br /> The function of the valves were to isolate Secondary Component Cooling (SCC) water to the chemical addition tank in the SCC system. <br /><br /> Maine Yankee Technical Specifications (Tech. Specs.) requires manual ECCS valves (and subsystem valves) to be aligned and locked in the position required for safeguards operation. SCC-19 was immediately locked.
3091994008 | Maine Yankee | 05/18/1994 | 08/22/1995 | 9508290016 | <strong>PLANT TRIP DURING MAIN TURBINE LOAD REDUCTION</strong><br /><i>Abstract:&nbsp;</i>On May 18,1994, the reactor tripped from 100% power on loss of load due to a main turbine trip. The main turbine tripped due to a trip of the turbine-driven feedwater pump (TDFP). The TDFP tripped on overspeed when high pressure (HP) steam was manually aligned to the TDFP. <br /><br /> Earlier, an air leak on a 345 KV switchyard breaker required decreasing power to 600 MWE (70% rated power) to allow breaker isolation. Reactor power was maintained at 100% while the main turbine load was being reduced. At 80% rated output, the main turbine extraction steam did not have sufficient pressure to run the TDFP and therefore HP steam had to be aligned. The control room recognized that the HP governor valve was cycling and dispatched an operator to open the HP isolation valve. Since the HP governor valve already had a high open demand signal, the pump tripped on overspeed. <br /><br /> The root cause of the plant trip was inadequate procedural guidance. Changes have been made to the procedure to prevent recurrence.
3091994009 | Maine Yankee | 07/03/1994 | 08/02/1994 | 9408110294 | <strong>Alternating ECCS Sub-Components Causes Inoperable ECCS Subsystem</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1994, a review of the procedure, that alternates Spray Building Exhaust Ventilation Fans, indicated that both fans are off for a brief period of time during this evolution.<br /><br /> Technical Specification (TS) 3.6 C.2 requires two operable and redundant ECCS trains during power operation. There are no specific TS associated with the fans. However, a Maine Yankee TS Interpretation concludes that Spray Building Exhaust Ventilation must be operable in order for LPSI and CS to be operable. Since both trains are affected by this action, entry into TS 3.0 A.2 is required. The time required to alternate the fans is so short that no shutdown is commenced. <br /><br /> A similar event, both fans placed in the off position, has been reported by LER #93-010. Recent NRC interpretations concluded that entry into TS 3.0 A.2 is reportable under 10 CFR 50.73. <br /><br /> The cause of this event was an inappropriate procedure for alternating fans. A new section has been added to the procedure to change the sequencing so as to avoid this problem.
3091994010 | Maine Yankee | 07/11/1994 | 08/22/1995 | 9508290028 | <strong>Degraded Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>At 1250 on July 11, 1994, an Auxiliary Operator, while performing his normal rounds, noticed wires protruding from a conduit elbow in the Main Steam Valve House. Upon closer examination, he found that there was no fire barrier sealant material inside the conduit where it penetrated the wall into the adjacent Reactor MCC Room. He then noticed a second conduit with no fire barrier sealant material within it. Both conduits were part of a new installation for upgrading Non-Nuclear Safety wiring systems in the plant. The Auxiliary Operator called the Control Room and was directed to remain at the penetrations as a fire watch. The penetrations were then properly sealed with fire barrier sealant material. All penetrations which were part of that conduit installation were inspected to ensure that they were properly sealed. No further discrepancies were found.
3091994011 | Maine Yankee | 07/16/1994 | 08/15/1994 | 9408220260 | <strong>Manual Reactor Trip Due To High Reactor Coolant Pump Vibration Indication During A Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>At 0207 on July 16, 1994, during a plant shutdown, with the plant in Hot Standby (Condition 6), operators manually actuated the Reactor Protective System (RPS) to trip the reactor in accordance with plant procedures, after receiving a high vibration alarm and observing abnormal vibration indications for the #2 Reactor Coolant Pump (RCP). The #2 RCP was shut down at 0210 pending an engineering evaluation of the indicated vibration amplitudes. <br /><br /> Subsequent investigation determined the cause of the increased vibration indication to be a faulty vibration monitoring instrument.
3091994012 | Maine Yankee | 07/27/1994 | 12/14/1994 | 9412190211 | <strong>Steam Generator Tube Inspection</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1994, the plant was shutdown when primary to secondary leakage approached 50 gallons per day (GPD). The Technical Specification limit for leakage from any single steam generator is 216 GPD. <br /><br /> On July 27, 1994, leak testing of steam generator (SG) 2 indicated 4 leaking tubes with eddy current data evaluation indicating cracking in the hot leg expansion transition region near the top of the tube sheet. The cause of the degradation was considered to be primary water stress corrosion cracking(PWSCC). Maine Yankee considered this condition to be a potential serious degradation of a principal safety barrier.<br /><br /> Maine Yankee inspected 100% of the active hot leg tube expansion transition regions in all three steam generators. Using improved evaluation techniques 303 tubes (125 in SG 1, 26 in SG 2 and 152 in SG 3) were identified as having circumferential cracking and were staked and plugged. <br /><br /> On November 14, 1994 a copy of the Maine Yankee 1994 Steam Generator Inspection Report was sent to the NRC as an enclosure to Maine Yankee letter MN-94-104. This report concludes that the plant was operating safely prior to the July/August 1994 steam generator outage and that the plant can be operated safely with a steam generator tube inspection each refueling outage.
3091994013 | Maine Yankee | 07/07/1994 | 08/22/1995 | 9508290012 | <strong>FIRE SUPPRESSION WATER PUMPS INOPERABLE</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted voluntarily for informational purposes. <br /><br /> On July 7, 1994 the facility was operating at 100% power while in the remedial action for Technical Specification 3.23.B.1 due to the motor driven fire pump (P-4) being out of service for repairs. At 0951, during the conduct of surveillance testing for the fire suppression system, the diesel driven fire pump (P-5) failed to respond to a manual start. A second attempt to start was successful and P-5 was maintained running until a pumper truck from the local fire department was connected to the plant fire suppression system. At 1547, P-5 was shutdown and a subsequent start test was conducted. The pump failed to start and was declared inoperable. With both fire pumps inoperable, the facility entered the remedial action of Technical Specification 3.23.B.2. Additionally, an Unusual Event was declared due to a loss of all fire protection pumps. Investigation of the start failure revealed that the starter motor for P-5, which had recently been replaced, was wired incorrectly. This resulted in intermittent starter operation due to improper grounding of the battery charger and starter motor start solenoids. At 1650, on July 8, 1994, wiring modifications were performed. The diesel driven fire pump was then satisfactorily tested, declared operable, and the unusual event was terminated.
3091994014 | Maine Yankee | 07/27/1994 | 08/26/1994 | 9409010206 | <strong>Missed Tech. Spec. Surveillance: Non Tech. Spec. Related Smoke Detector In Containment.</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1994, a fire protection surveillance was performed at Maine Yankee (MY) during a shutdown. MY discovered a Smoke Detector that had not been tested for an indeterminate period of time. <br /><br /> Technical Specification (Tech. Spec.) 4.12 requires each 'PYR-A-LARM' Smoke Detector in the plant to be tested on a periodic basis. Thirteen of the detectors are mentioned in surveillance procedure 3-19-3 SMOKE AND HEAT DETECTOR TESTING and are documented as being tested satisfactorily on a shutdown basis. During a surveillance field verification of CTMT Smoke Detectors MY discovered a Detector not mentioned in the surveillance procedure. <br /><br /> A Work Order was generated and the Detector was tested satisfactorily on 08/01/94. <br /><br /> The Smoke Detector Surveillance procedure has been modified to include the 14th Detector. The cause of this event was inadequate field verification when the Smoke Detector Surveillance procedure was written. <br /><br /> A similar event was reported by LER on 10/09/92 when a surveillance was missed due to lack of procedural guidance.
3091994015 | Maine Yankee | 07/24/1994 | 08/23/1994 | 9409060162 | <strong>Secondary Component Cooling System Outside Design Basis Due To An Inoperable Non-Safeguards Isolation Trip Valve</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1994, with the plant in a Cold Shutdown Condition, operators were performing a surveillance on the Secondary Component Cooling (SCC) System Non-Safeguards Isolation Trip Valves. During the surveillance, it was discovered that one of the valves had failed open due to an apparent fault in the 2-out-of-2 trip logic circuitry to the solenoid operated valves (SOV) controlling the actuating air to the isolation trip valve actuator.<br /><br /> The purpose of these trip valves is to isolate non-safeguards, SCC cooling loads in the event of a postulated seismic event. At the time the valve failed open, the SCC subsystem was required to be operable to provide cooling for Residual Heat Removal (RHR) Train B. Investigation determined that the proximate root cause of this event was a faulty, redundant contact in the 3-position control switch for one train of the trip logic circuit; which in turn caused one SOV to de-energize and vent the actuating air required to hold the trip valve shut. <br /><br /> The immediate corrective action taken to restore the operability of the trip logic circuit was to perform a temporary plant modification which installed a jumper around the faulty contact in the 3-position switch. The planned, long term corrective action is to replace the faulty, 3-position switch at the first opportunity.
3091994016 | Maine Yankee | 08/04/1994 | 10/28/1994 | 9411040218 | <strong>Emergency Feedwater Isolation Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>At 1220, on August 4, 1994 with the reactor in a cold shutdown condition, plant operators determined that the Emergency Feedwater isolation and regulating valves for #1 Steam Generator were leaking by. Subsequently it was determined that under accident conditions which require isolation of Emergency Feedwater, valve leakage could exceed Safety Analysis assumptions. Maintenance activities were performed to reduce Emergency Feedwater valve leakage to within acceptable limits. In addition, administrative controls were implemented to ensure Emergency Feedwater leakage is maintained within the bounds of Safety Analysis assumptions during accident conditions. <br /><br /> A root cause investigation identified inadequate maintenance procedures, and inadequate post maintenance testing as the main causal factors for this event. <br /><br /> The safety significance of this event was not initially known, therefore this event was originally reported under the provisions of 10CFR 50.73(a)(2)(ii)(A), an unanalyzed condition that significantly compromised plant safety. However, recently completed analyses show that plant safety was not significantly compromised by this event. Therefore, this event is now being reported for information only.
3091994017 | Maine Yankee | 10/04/1994 | 11/03/1994 | 9411150243 | <strong>Dual Function, Emergency Core Cooling System Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary report submitted for information only.<br /><br /> While performing quarterly stroke testing of containment isolation valves, with the plant at 100% power, one of two Containment Safeguards Sump Suction Isolation valves failed to fully re-shut. This valve is a dual function Emergency Core Cooling System (ECCS) valve. It is normally closed to provide the single Containment Integrity (CI) barrier between the safeguards sump and the suction piping for one train of safeguards pumps. During a Loss of Coolant Accident, this valve opens automatically upon receipt of a Recirculation Actuation Signal to provide the suction head to the safeguards pumps. <br /><br /> The valve was declared inoperable and the applicable Remedial Actions of Technical Specifications (TS) were implemented. The root cause of the failure (misalignment of the valve operating reach rod) was identified and corrected. allowable remedial action timeframes. <br /><br /> A Management review of this event resulted in a reassessment of Management's existing guidance to operators when a single containment barrier valve becomes inoperable. New, more conservative guidance, specific to the unique application of the Containment Safeguards Sump Suction Isolation Valves, will require operators to restore the CI function of an inoperable sump isolation valve within one hour; vice the four hours allowed by the TS.
3091994018 | Maine Yankee | 12/04/1994 | 08/22/1995 | 9508290050 | <strong>Secondary Component Cooling Water Inoperable due to Valve Mispositioning</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1994, while flushing the Component Cooling Water (CCW) Heat Exchangers, a non-licensed operator misaligned valves resulting in the inboard SCCW heat exchanger having Service Water aligned to it with no SCCW flow, and the outboard SCCW heat exchanger with SCCW aligned to it with no Service Water flow. Thus the SCCW system was made inoperable. Service Water was aligned to both PCCW heat exchangers with PCCW aligned to the inboard PCCW heat exchanger. The operator realized his error and immediately aligned the valves to their proper positions. With two Service Water Pumps in operation (normal configuration) and Service Water flow aligned to three heat exchangers, it was determined that the ability of the PCCW system to provide adequate cooling is affected during the recirculation mode following a Loss of Coolant Accident (LOCA). Initial corrective actions include: directing that a Human Performance Evaluation be completed, counseling the operator on the proper use of procedures, issuing a memorandum to all Operations Department personnel stressing the importance of procedure use and adherence, directing Plant Shift Superintendents to discuss the memorandum with all members of their crews, and conducting an audit of normal plant evolutions to verify there are no additional improper practices where procedure usage may not be adequate. Additional corrective actions may be determined from the root causes developed from the Human Performance Evaluation.
3111994001 | Salem 2 | 01/15/1994 | 02/10/1994 | 9403030068 | <strong>TS 3.0.3 Entry: Inoperability of ARPI System to Support Maintenance Troubleshooting.</strong><br /><i>Abstract:&nbsp;</i>Two intentional Technical Specification (TS) 3.0.3 entries occurred on 1/15/94 (from 0045 to 0047 hours, and from 0056 to 0059 hours) due to deenergizing the Analog Rod Position Indication (ARPI) System for all control rods. These events occurred due to removing the 115-volt alternating current (AC) power supply fuses to the ARPI System primary and auxiliary 13-volt direct current negative and positive power supplies. This was done to support correction of ARPI indicator drift for rod 2SB4. Rod positions, as compared to the rod group demand indicator, were correct prior to fuse removal and following fuse reinstallation. The root cause of these events is ARPI System design that resulted in the conservative approach requiring the TS 3.0.3 entries to avoid possible equipment damage during repair of the 2SB4 indication drift. Adjustments were made to the 2SB4 signal conditioning module and the module span, based on redeveloped secondary AC voltage value to the module. A channel check demonstrated ARPI operability, and TS 3.0.3 was exited. PSE&G will continue participation in the industry Rod Control User's Group and will utilize User's Group and vendor recommendations regarding ARPI System drift.
3111994002 | Salem 2, Salem 1 | 01/19/1994 | 02/02/1996 | 9602120246 | <strong>Reactor Power Higher Than Indicated and Subsequent Failure to Enter Technical Specification 3.0.3 Due to Inoperable Nuclear Instrumentation.</strong><br /><i>Abstract:&nbsp;</i>A 1/19/94 review of Unit 2 Fuel Cycle 8 calorimetric and Reactor Coolant System flow calculations indicated the unit may have operated > 3411 megawatts. Power was reduced by 3% to compensate for an estimated 2.5% error in indicated power. On 1/19/94, Technical Specification 3.0.3 was not entered when Nuclear Instrumentation (NI) Power range was inoperable. The NI was readjusted on 1/21/94. Engineering evaluation determined the Unit operated 1.4% > rated thermal power during Cycle 7 and 2.58% > rated thermal power during Cycle 8. The power indication error resulted from perimeter bypass flow of the FW flow nozzles. As a result of this event the Unit 1 feedwater flow nozzles were inspected. visual inspection showed some degradation of the nozzles. An engineering evaluation of the Unit 1 nozzles indicated a potential for having operated 0.75% greater than allowed. The unit 1 and 2 feedwater nozzles have been replaced.
3111994003 | Salem 2 | 02/04/1994 | 03/02/1994 | 9403140103 | <strong>T/S 3.0.3 Entry: More Than One Inoperable ARPI Per Bank</strong><br /><i>Abstract:&nbsp;</i>On 2/4/94, at 0800 hours, Technical Specification (TS) 3.0.3 was entered when the Analog Rod Position Indication (ARPI) for rods 2C1, 2C3, and 2C4 indicated greater than a +/- 12 step deviation from their group demand counters. At 0858 hours, reactor shutdown was initiated in accordance with TS 3.0.3. This event resulted from output drift of the ARPI coil stacks. The most probable causes of the drift are changes in mutual inductance between rods and/or temperature changes at the ARPI coil stacks, which can result from significant changes in reactor power. At approximately 0100 hours (same day) reactor power had been reduced from 93% to Mode 2. signal conditioning modules were redeveloped, the modules were adjusted, and at 0915 hours, the shutdown was terminated and TS 3.0.3 was exited. The signal conditioning module of 2C3 was adjusted in a similar manner and at 1113 hours, the involved TS action statement exited. PSE&G will continue participation in industry Rod Control User's Group efforts to resolve ARPI System drift problems.
3111994004 | Salem 2 | 03/03/1994 | 03/30/1994 | 9404040102 | <strong>Late Performance Of Offsite Power Avail. Surv. Due To Untimely Determination Of 2A D/G</strong><br /><i>Abstract:&nbsp;</i>At 0500 hours on 3/3/94, required Action 'a.' of Technical Specification (TS) 3.8.1.1. should have been performed due to clearing and tagging of A air receiver of 2A Diesel Generator (DG). TS 3.8.1.1.a requires demonstrating operability of the remaining independent alternating current circuit within one hour by performing TS 4.8.1.1.1.a and at least once per eight hours thereafter. This event was recognized at 0900 hours (same day) and TS 4.8.1.1.1.a was satisfactorily completed at 0912 hours. This event is attributed to management deficiency due to inadequate communication when operations personnel incorrectly interpreted that an administrative requirement, to declare a DG inoperable when one of its starting air trains are removed from service, no longer applied. Historically, similar clearing and tagging evolutions were performed without declaring the involved DG inoperable. The basis for this practice is outlined in PSE&G's response to NRC's Notice of Violation contained in Inspection Report 50-272/93-23; 50-311/93-23, which concluded such practice does not involve a TS violation. Expectations regarding unavailability of a DG starting air train have been reinforced with all Licensed Operations personnel and the station planning department. These expectations will remain in effect pending final disposition of PSE&G's response to the subject NRC Notice Of Violation.
3111994005 | Salem 2 | 04/03/1994 | 05/02/1994 | 9405060263 | <strong>Late Surveillance Testing Of Reactor Trip System Power Range Instrument Channel 2N41 Due To Inadequate Communication.</strong><br /><i>Abstract:&nbsp;</i>On 4/3/94, failure to meet Technical Specification,(TS) 4.0.2 occurred when the surveillance interval for channel functional testing of Reactor Trip System Power Range Instrument Channel 2N41 was exceeded. During this event, the TS specified minimum operable channels were maintained. The surveillance was completed on 4/5/94. This event resulted from inadequate communication between the Senior Maintenance Controls Supervisor (SMCS) and Station Controls Scheduler (SCS). A contributor was failure of the station TS Administrator (TSA) to apprise the SMCS (Controls TS Coordinator) that the surveillance would be overdue after 4/2/94. The importance of adequate communication has been stressed with Maintenance Department supervisors. The TS Surveillance program administrative procedure has been reviewed to ensure full understanding of responsibilities. The SMCS, SCS, and the TSA were coached/counseled. The SMCS has been directed to establish and maintain a sign-off log to ensure daily review of reports listing upcoming overdue TS surveillances. The TSA has been directed to inform TS surveillance coordinators, within a specified time interval, of upcoming surveillances at risk of violating TS 4.0.2.
3111994006 | Salem 2 | 03/25/1994 | 05/11/1994 | 9405190069 | <strong>Failure To Declare Pressurizer Relief Valves 2PR1 And 2PR2 Inoperable After Closure Of Pressurizer Block Valves 2PR6 and 2PR7</strong><br /><i>Abstract:&nbsp;</i>Action 'a.' of Technical Specification (TS) 3.4.5 should have been entered, at 0332 hours on March 25, 1994, when 2PR6 and 2PR7 (respective block valves for the power operated relief valves, 2PR1 and 2PR2) were closed per procedure. TS were not met until the block valves were reopened, at 1045 hours on 3/25/94. While the block valves were closed, a Nuclear Control operator was stationed to open them, if required. This event occurred because the procedure did not clarify the effect of block valve closure on PORV operability. Night Order Book entries were made on 3/25/94 and 3/31/94 to inform licensed operators of the requirement to enter TS 3.4.5 when the PORV block valve(s) are closed for leak determination. This event was reviewed with licensed operations personnel. Procedures will be appropriately revised to require reference to TS, whenever PORV block valve(s) are closed. This event will be included in Licensed Operator re-qualification and initial License training. Appropriate TS interpretation(s) will be reviewed and revised, as necessary.
3111994007 | Salem 2 | 04/11/1994 | 05/10/1994 | 9405170200 | <strong>ESF Actuation: Blackout Signal Loading of 2A, 2B, & 2C 4 Kilo-Volt (4KV) Vital Buses Due To Personnel Error During Emergency Safeguards Actuation Instrumentation Funct. Test</strong><br /><i>Abstract:&nbsp;</i>On 4/11/94, at 1035 hours, the infeed breakers to the Unit 4 kilo volt Vital Buses tripped on an undervoltage signal resulting in an engineered safety feature automatic starting and 'blackout signal loading' of the buses' respective Diesel Generators (DGs). This occurred during performance of procedure S2.MD-FT.4KV-0001, 'Emergency Safeguards Actuation System (ESFAS) Instrumentation Monthly', when the technician opened an incorrect switch. At 1211 hours (same day) the Nuclear Regulatory Commission (NRC) was notified of this event, in accordance with 10CFR50.72(b)(2)(ii). At approximately 1700 hours (same day), infeed power to the vital buses was restored and the DGs were secured and returned to standby. This event resulted from a perceptual mental processing error. The involved technician has been counseled, reemphasizing the importance of properly identifying components for manipulation and use of the (Stop, Think, Act, and Review) technique. Appropriate Maintenance Department supervisors and technicians have reviewed this event. The subject procedure will be revised to require concurrent verification of the location (prior to manipulation) of all test-manipulated switches in the SEC cabinets.
3111994008 | Salem 2 | 06/29/1994 | 07/27/1994 | 9408030162 | <strong>Reactor Trip Due To 23 Steam Generator Lo-Lo Level During Return To On-Line Power Operation</strong><br /><i>Abstract:&nbsp;</i>At 0439 hours on 6/29/94, an automatic Reactor Protection System trip from 14% power occurred due to 23 Steam Generator (SG) lo-lo level, resulting from the tripping of 21 SG Feed Pump (SGFP), caused by 22 SG hi-hi level. Emergency operating procedures were entered and the Unit was stabilized in Mode 3. This event is attributed to the design of the feedwater control system, which exhibits sensitivity at low power levels, that was strongly affected by normal closing of the 21 SGFP recirculation valve, 21BF32. When 21BF32 closed, a greater level increase occurred in 22 SG than in the other SGs. Operability checks and troubleshooting verified proper SG level control response. To eliminate the effect of BF32 closure upon SG level control during Startup, procedure revisions on both Units have been implemented which ensure the valves remain open during Startup. To provide additional margin of SG level control to better cope with feedwater control system transients during Startup and at low power, a license change request will be submitted in order to lower the current SG lo-lo setpoint of 16% to less than 10%. Design changes, currently scheduled for installation on Unit 1 during 1R12 and on Unit 2 during 2R9, utilize digital equipment technology that will reduce the exhibited sensitivity of the feedwater control system at low power levels.
3111994009 | Salem 2 | 07/15/1994 | 08/03/1994 | 9408110265 | <strong>Intentional Technical Specification (TS) 3.0.3 Entries To Support Correction Of Analog Rod Position Indication (ARPI) System Drift Affecting Rod 2SB2.</strong><br /><i>Abstract:&nbsp;</i>Two intentional Technical specification (TS) 3.0.3 entries occurred on 7/15/94 due to deenergizing the Analog Rod Position Indication (ARPI) System for all control rods to support correction of ARPI indicator drift for rod 2SB2. Rod positions, as compared to the rod group demand indicator, were correct prior to and following the TS 3.0.3 entries. Design of the ARPI System necessitated the TS 3.0.3 entries to avoid possible equipment damage during the 2SB2 repair. Internal adjustments were made to the 2SB2 signal conditioning module and the module span, a channel check demonstrated ARPI operability, and TS 3.0.3 was exited. PSE&G will continue participation in the industry Rod Control User's Group and will utilize user's Group and vendor recommendations regarding ARPI System drift. A license change request will be submitted to more closely align with the recommendations of NUREG-1341, Vol. 1, by providing a time frame within the TS Action Statement to restore Operability when more than one ARPI indicator per bank is inoperable.
3111994010 | Salem 2 | 09/22/1994 | 02/15/1995 | 9502220025 | <strong>Controlled Reactor Shutdown Due to 21 Centrifugal Charging Pump Inoperable Greater Than 72 Hours</strong><br /><i>Abstract:&nbsp;</i>At 0108 hours, on 9/19/94, 21 Centrifugal Charging Pump (CCP) was removed from service for scheduled preventive maintenance (PM) and subsequent post-maintenance testing results satisfied ASME operability criteria. Increased vibration was measured in the pump speed increaser however, the vibration was felt not to impact operability and the pump was returned to service, at 1800 hours on 9/21/94. Following unstable and increasing speed increaser vibration, 21CCP was declared inoperable, at approximately 0100 hours on 9/22/94 (effective from prior removal from service on 9/19/94). At 0108 hours (9/22/94) the Technical Specification (TS) action time expired and at 1222 hours (same day) the Unit was placed in MODE 4 (HOT SHUTDOWN). The speed increaser was replaced, the pump was satisfactorily tested; and, at 2241 hours on 9/25/94, the TS action was exited. The vibration in the speed increaser, Nuttal Gear Corp., Model No. SU-1023-8X, resulted from corrosion of the speed increaser gear tooth surfaces possibly aggravated by changing the motor to speed coupling gap. <br /><br /> The corrosion resulted from moisture intrusion of the speed increaser gear case, and the incorrect coupling gap resulted from an error in the technical manual. Procedures have been revised to ensure the coupling gap is set correctly. The oil sampling and PM programs and design will be reviewed and appropriate action will be taken.
3111994011 | Salem 2 | 09/29/1994 | 10/19/1994 | 9411020250 | <strong>Manually - Initiated Reactor Trip Signal Following Unplanned Closure of Main Steam Isolation Valves 21 and 22 MS167</strong><br /><i>Abstract:&nbsp;</i>The Nuclear Control Operator (NCO) with balance of plant (BOP) responsibilities mistakenly-closed main steam line isolation valves 21 and 22MS167. The other operating crew NCOs recognized this mistake however, they had insufficient time to intervene in order to avoid an automatic protective response. The BOP NCO, realizing the mistake, immediately initiated a manual reactor trip signal, at 0232 hours on 9/29/94. Expected plant response occurred and Emergency Operating Procedures were entered. Main steam was isolated to limit Reactor Coolant System cooldown and the Unit was stabilized in HOT STANDBY at 0317 hours (same day). This event is attributed to personnel error by the BOP NCO, as a result of inadequate self-checking and inattention to detail. A Human Performance Enhancement System evaluation of this event has been conducted. Appropriate personnel corrective actions have been taken. Observations of operations personnel are ongoing to ensure adequacy of self verification techniques. During the trip recovery, an incorrect attempt was made to reset the Safeguards Equipment Controllers (SECs) and Technical Specification (TS) 3.0.3 was entered. Two SECs were reset and TS 3.0.3 was exited. Subsequent review showed the TS 3.0.3 entry was invalid and the involved overhead alarm (OHA) response procedure was inadequate. Appropriate procedure changes will be made regarding the attempt to reset the SECs.
3111994012 | Salem 2, Salem 1 | 10/13/1994 | 11/14/1994 | 9411210395 | <strong>Calorimetric (Heat Balance) Calculations Not Performed Within the Specified Surveillance Interval On Both Units</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 10/13/94, required daily calibration of power range instrumentation was not performed. Investigation revealed that during 1994 on 1/8, 7/5, 7/8, and 9/12 (Unit 2), and 2/26, 3/5, and 9/2 (Unit 1), the calibration was performed beyond the allowable extension per Technical Specification (TS) 4.0.2. These events are attributed to personnel error due to failure to follow procedure. Contributors to the 10/13 event were focus upon ongoing activities and common mis-perception (applicable to all the events) that the surveillance could be completed within the confines of a calendar day. Licensed personnel from the 10/13 event were counseled concerning their actions and Management expectations. Operations Night Order Book entries were made to explain the surveillance requirement and a procedure revision to enhance/clarify the surveillance interval. All Licensed personnel and select Technical Department personnel, will review these events to ensure their understanding of the surveillance interval.<br /><br /> During the present re-qualification cycle, all licensed personnel will receive training specific to these events. By 2/28/95, additional procedure enhancement will be made to provide more focus on TS requirements and address human factors tied to procedure performance and review.
3111994013 | Salem 2 | 10/23/1994 | 12/07/1994 | 9412220097 | <strong>Core Alterations and Fuel Movement Without Containment Building Penetration Closure During Refueling Outage 2R8</strong><br /><i>Abstract:&nbsp;</i>On 10/18/94, while in Mode 5, direct access from the Containment atmosphere to the Auxiliary Building was established when Service Water piping vent and drain valves were tagged open. On 10/23/94 - 10/25/94 reactor head removal, core alterations, and movement of 5 irradiated fuel assemblies were performed without meeting the Containment closure requirements. Upon discovery, fuel movement was immediately suspended and containment closure reestablished. These events are attributed to cognitive personnel error, by the Nuclear Shift Supervisor (NSS), due to inadequate review of the components off-normal and tagged list. A procedure revision has been made to better define the depth and scope of review of the lists. An Information Directive has been distributed to all Operations personnel discussing the significance of this event. The NSS has been coached regarding this event.
3111994014 | Salem 2 | 11/18/1994 | 12/14/1994 | 9412230051 | <strong>Engineered Safety Feature Actuation: Blackout Signal Loading of 2B and 2C 4 Kilovolt (4KV) Vital Buses</strong><br /><i>Abstract:&nbsp;</i>At 0103 hours on 11/18/94, with the reactor core off-loaded and a single off-site power source aligned to Unit 2, No. 4 Station Power Transformer (SPT) tripped resulting in 'blackout signal' loading of 2B and 2C 4KV vital buses' Diesel Generators (DGs). Expected loss and transfer of electrical loads occurred. The vital buses were maintained powered from their DGs until 0458 and 0537 hours (respectively) on 11/19/94. The most probable root cause of this event is intermittent component failure of either the SPT 4T60 switcher 28 VDC manual trip coil open relay, 3X, or the switcher 125 VDC supervisory relay, 89OX and both were replaced. A strip chart recorder has been installed to continually monitor 6 points within the trip circuit, and the 28 VDC and 125 VDC buses. To-date, this device has not shown signals capable of tripping the 4T60 switcher. The recorder will be maintained until the subsequent restart and return of the Unit to service. This is intended to ensure that most likely combinations of plant operating evolutions, ambient conditions, and work activity evolutions are monitored to obtain further information, regarding this event.
3111994015 | Salem 2 | 12/20/1994 | 01/18/1995 | 9501240192 | <strong>The Waste Gas Holdup System (WE) was not sampled IAW Technical Specification (TS) 3.3.3.9.</strong><br /><i>Abstract:&nbsp;</i>On 9/27/94, during activities to support testing of the 22 Waste Gas Decay Tank (WGDT), the 'Shift Sup-Admin' tag on the 22WG106, Gas Analyzer Sample Isolation Valve for 22 WGDT, was temporarily released and the valve was placed in the closed 'off-normal' position. On 9/27/94 and 10/1/94, 22 WGDT was placed in service for approximately 24 hours on each occasion to support system requirements. When 22 WGDT was placed in service with 22WG106 closed, the flow path to the Gas Analyzer was not aligned for sampling and TS required grab sampling was not performed. On 10/5/94, an Nuclear Equipment Operator (NEO) discovered the 22WG106 closed while investigating the cause of low gas analyzer readings, the valve was opened and samples requested. These events are attributed to cognitive personnel error# by operations department personnel, due to inadequate review of the components off-normal and tagged list. An Information Directive has been distributed to all Operations personnel discussing the significance of this type of event. Additional followup is in progress to identify involved personnel and appropriate accountability will be provided.
3111994016 | Salem 2 | 12/26/1994 | 01/25/1995 | 9501270226 | <strong>Unplanned TS 3.0.3 entry due to inoperability of high steam flow/low Tavg Safety injection above 545 degrees fahrenheit reactor coolant temperature and failure to take action required due to inoperability of 24 loop Rx coolant resistance temperature device</strong><br /><i>Abstract:&nbsp;</i>During the reactor coolant system (RCS) resistance temperature device (RTD) cross calibration, an unplanned Technical Specification (TS) 3.0.3 entry, from approximately 0900 until 0915 hours on 12/26/94, occurred due to the high steam flow/low - low Tavg safety injection (SI) Engineered Safety Feature protection being blocked above the allowed 545 degrees Fahrenheit (F) P-12 value. The SI protection was immediately reenabled and TS 3.0.3 was exited. At approximately 0923 hours (same day) a planned evolution reduced RCS temperature below P-12. At 1425 hours on 12/26/94, the 24 loop RTD bistables were returned to normal. From approximately 2121 hours on 12/27/94, until 1942 hours on 1/10/95, RCS temperature was above P-12 and the TS required action, due to inoperability of 24 loop RTD channel, was not taken. The primary cause of both events is attributed to personnel error, due to failure to adequately follow procedure. 24 loop RTD channel inoperability resulted from an inadequate loop calibration subsequent to changing to an installed spare RTD during the 12/26/94 cross calibration. Positive discipline is being taken concerning both events. The TS 3.0.3 entry will be covered in Licensed Operator Requalification Retraining and an Operations directive will be distributed. Appropriate procedure enhancements will be made and lessons learned will be reviewed.
3131994001 | Arkansas 1 | 01/31/1994 | 02/25/1994 | 9403070293 | <strong>Emergency Feedwater System Flowpath Inoperable Longer Than Allowed by Technical Specifications as a Result of Failure to Identify Inoperable Instrumentation Due to Human Error and Subsequent Technical Specifications Required Shutdown.</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1994, the low range level indication (LI-2622)for the 'A' Once-Through Steam Generator was noted to be greater than the maximum normal channel difference during a routine channel check. A job request was written and a log notation was made as required by procedure. On January 28, 1994, the level indication exceeded the operability difference; however, this was not recognized until 2150 on January 31, 1994. The Emergency Feedwater (EFW) flowpath associated with the level control feature of the level transmitter (LT)-2622, was declared inoperable and the plant was shutdown as required by Technical Specifications. LT-2622 was replaced while the plant was in hot shutdown and was declared operable at 2204 on February 1, 1994 along with its associated EFW flowpath. The reactor was returned to power on February 2, 1994. The cause of the transmitter failure could not be determined on site; therefore, it was shipped to the manufacturer for failure testing. The root cause of the delay in identifying LT-2622 inoperability was operator inattention to detail while taking and reviewing logs. Corrective actions include Operations shift management and crew meetings to discuss lessons learned from the event and management expectations, enhancements to operator logs, and meetings with other ANO departments to discuss generic implications.
3131994002 | Arkansas 1 | 04/11/1994 | 05/10/1994 | 9405180147 | <strong>Reactor Trip on High Reactor Coolant System Pressure Resulting from a Lightning-Induced Closure of the Main Steam Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1994, at approximately 2040, lightning struck in the vicinity of the ANO-1 Reactor Building causing a partial loss of power within channels 'B' and 'D' of t Emergency Feedwater Initiation and Control (EFIC) system. The power loss caused spurious trip of 'A' train of EFIC which initiated actuation of the Emergency Feedwater (EFW) system and automatic closure of Main Steam Isolation Valves (MSIVs). The Reactor Protection System initiated a reactor trip due to high Reactor Coolant System pressure s a consequence of the closure of the MSIVs at power. During the post-trip response, a slight overcooling condition occurred. This resulted from the power loss to channel 'B' EFIC which supplies the automatic control signal to train 'A' EFW flow control valves a 'B' steam generator atmospheric dump control valve. This caused the 'A' EFW flow control valves to remain fully open after the reactor trip, and the 'B' ADV control valve to fully upon loss of power, as designed. The operators terminated the overcooling event and returned the plant to normal post-trip parameters within eight minutes of the event. EFIC system power supplies were reset, other affected equipment was repaired, and various systems were demonstrated operable by surveillance. ANO-1 was returned to criticality at 0223 on April 15, 1994, and escalation to 100 percent power commenced.
3131994003 | Arkansas 1, Arkansas 2 | 10/08/1994 | 01/16/1995 | 9501250133 | <strong>Surveillance Testing of Some Engineered Safeguards Components Did Not Verify Operability as Required by Technical Specifications Due to Procedural Deficiencies Resulting from Inadequate Definition of Testing Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1994, during a review of Engineered Safeguards Actuation System testing methodology which was initiated as a result of concerns identified regarding ANO-2 engineered safety features surveillance procedures, ANO-1 personnel identified two concerns with the testing of High Pressure Injection (HPI) pumps actuation circuitry. It was identified that the Engineered Safeguards (ES) Integrated Test, which is performed every 18 months during a refueling outage, did not include complete functional verification of the circuit breaker position interlocks used in the BPI pump auto-start circuitry. It was also identified that the Integrated ES Test does not verify that the swing HPI pump would start utilizing the logic path containing the normal feeder circuit breaker contact. The direct cause of this condition was inadequate procedural guidance. The root cause was determined to be inadequate definition of testing requirements for control circuitry in ES systems. The feeder breakers for P36-B were racked down and removed from the switchgear rooms, ensuring that the P-36A and C circuitry remained in a previously tested configuration. Functional testing of the previously untested BPI pump circuitry was completed and P-36B was returned to an operable status at 1622 on October 9, 1994. A task force established rules and guidelines for determining ES testing requirements which were used to evaluate the existing test program and identify any necessary ES testing procedure changes. One additional instance, the autostart function of the B:PI Auxiliary Lube Oil Pumps, required additional testing to fully meet Technical Specification surveillance requirements. Necessary procedure changes will be implemented by March 16, 1995.
3131994004 | Arkansas 1 | 08/04/1994 | 11/09/1994 | 9412020212 | <strong>Voluntary Report Concerning a Personnel Oversight During the Design Change Process Which Resulted in the Potential for a Blocked Hydrogen Analyzer Outlet Flowpath Being Undetectable During Functional Testing.</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1994, at approximately 1110 CDT, it was determined by ANO Systems Engineering personnel that the functional test procedure for the Reactor Building hydrogen analyzers was not adequate to alert plant personnel of the presence of a blocked analyzer outlet flowpath and therefore, was not adequate to assure system operability. If the analyzer flowpath were to become blocked due to foreign material buildup, failure of the analyzer outlet check valve to open, or a manual isolation valve being closed, a recirculation flowpath would be established through the analyzer, the compressor, and the bypass line. The functional test, which is not a Technical Specifications required test, would not identify this condition since the system flow switch, which is in-line with the compressor, would not alarm to alert the operators that a sample was not being drawn from the Reactor Building. The bypass Line and an additional compressor were added to the system in 1986 to improve sample transport time. The analyzers were conservatively declared inoperable at 1110 on August 4 and the provisions of Technical Specification 4.0.3 were implemented, allowing twenty-four hours to complete a valid functional test. The Hydrogen Analyzer test procedure was revised and a successful functional test was completed. The hydrogen analyzers were declared operable at 1751 on August 4. The cause of this condition was determined to be personnel oversight during the design change process. A memorandum regarding this event was issued to appropriate Engineering personnel for 'Lessons Learned' purposes. Design change procedures in place at the present time are considered adequate to prevent occurrence of similar conditions. It was determined that this condition is not applicable to ANO-2. This is a voluntary report.
3151994001 | Cook 1, Cook 2 | 02/05/1994 | 05/27/1994 | 9406010230 | <strong>Failure Of The Unit One Main Steam Safety Valves To Meet Technical Specification Lift Setpoint Requirements</strong><br /><i>Abstract:&nbsp;</i>This supplemental report is being submitted to provide additional information regarding the Main Steam Safety Valve Lift Setpoint testing initially reported on March 7, 1994. On February 3, 4, and 5, 1994, with the Unit 1 Reactor in Mode 1 (power operation) at 62 percent Thermal Power, thirteen of the twenty Main Steam Safety Valves' (MSSVs) lift settings were found out of tolerance as established in Technical Specifications during Surveillance testing. Due to the results of the Unit 1 MSSV testing, the MSSVs in Unit 2 were also tested. Nine Unit 2 MSSVs were found out of specification. Based on the Safety Evaluation conducted for this event, the MSSV as-found setpoints did not exceed the design pressure rating of the steam generators in either Unit 1 or Unit 2. The most likely cause of this event is attributed to mild galling between the disk and nozzle components along with 'mechanical keying' and/or chemical reaction of the mixed oxides on the disk with the chromium oxide on the nozzle. It is believed these combined affects, over time, caused the elevated lift setpoint on the MSSV's initial lifts. Corrective actions are being pursued which will include approval for the following: 1) Exercising the MSSVs mid-cycle to improve valve setpoint performance; 2) Develop in-house test capabilities; 3) obtain spare MSSVS; 4) work with vendor and another utility to develop a long term solution to the disc/nozzle binding problem.
3151994002 | Cook 1, Cook 2 | 03/09/1994 | 04/08/1994 | 9405020319 | <strong>High Neutron Flux Setpoints for Operation at Reduced Power Levels with Inoperable MSSVs Not Low Enough to Preclude Secondary Side Overpressurization</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1994 it was determined that the potential safety issue identified in Nuclear Safety Advisory Letter (NSAL) 94-001, operation at Reduced Power Levels with Inoperable Main Steam Safety Valves (MSSVs), was reportable. NSAL 94-001 identified that the original methodology for calculating power range high neutron setpoints with inoperable MSSVs issued generically by Westinghouse was found to be in error. <br /><br /> Appropriate administrative controls were immediately established on confirmation of tho NSAL applicability. Corrective action will include either revising the technical specifications to incorporate the revised setpoints or performing a more sophisticated analysis to show that the current technical specification limits are acceptable. <br /><br /> Due to mitigating factors which provide assurance that there is no loss of safety function this issue did not represent a significant reduction in plant safety.
3151994003 | Cook 1, Cook 2 | 03/11/1994 | 04/11/1994 | 9405020311 | <strong>Main Steam Safety Valve Test Inaccuracy Due To Miscalculation Of Valve Seat Area By Vendor</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1994, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 3 (Hot Standby) a letter was received by the Cook Plant from Furmanite America, Inc., which reported that an inaccuracy existed in the mean seat area constant (24.626 square inches) used to calculate the Main Steam Safety Valve (MSSV) lift setpoints in the vendor's Trevitest Program. The Trevitest calculation error resulted in MSSV lift setpoints being between 1 and 3 percent higher than previously determined. Consequently, all twenty MSSVs in each unit had lift setpoints outside the Technical Specification Limit of +/- 1 percent. An Engineering Evaluation of data comparing Trevitest results with data from a Full Pressure Steam Test has determined that the effective MSSV seat area is 23.047 square inches. This event, taken together with the high initial lift pressures reported in LER 50-315/94-001, revealed that despite the further increase in set pressure resulting from this event, the high lift setpoints would not have resulted in exceeding the design pressure of the steam generators in either unit. <br /><br /> Both Units 1 and 2 MSSVs will be reset to within their required set tolerance after entering Mode 3 (Hot Standby). Both Units 1 and 2 will Enter Mode 3 via the use of three Reactor Coolant Pumps with the Reactor Trip Breakers open.
3151994004 | Cook 1 | 04/06/1994 | 05/10/1994 | 9405190369 | <strong>Failure Of Three Pressurizer Safety Valves To Meet Technical Specification Required Surveillance Test Criteria</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1994 with Unit 1 in Mode 5 (Cold Shutdown) it was determined that all three of the pressurizer safety valves, which were sent to an off site test laboratory for testing, were found with lift settings outside of the Technical Specification acceptance criteria. Acceptable settings are between 2461 psig and 2509 psig. Valve 1-SV-45A was found to have a lift setpoint of 2536 psig, valve 1-SV-45B had a lift setpoint of 2535 psig and 1-SV-45C had a lift setpoint of 2538 psig.<br /><br /> There was no safety-significance since the worst case (1-SV-45C lift setpoint of 2538 psig) would result in a maximum transient pressure of 2615 psig (2538 psig plus 3 percent accumulation to attain its full rated lift). This is below the Technical Specification safety limit of 2735 Psig. <br /><br /> All three valves were partially disassembled (retaining spring compression) and inspected. No problems were noted. The nozzle and disc seating surfaces were lapped and polished. The valves were reassembled and tested satisfactorily. The safety valve conditions experienced at the D.C. Cook Plant are similar to current industry trends/concerns. Since a specific Root Cause could not be determined, no preventive action is planned at this time. However, we will be evaluating the test methods and industry activities pertaining to the pressurizer safety valves.
3151994005 | Cook 1 | 12/28/1993 | 06/09/1994 | 9406160028 | <strong>Failure of Fire Watch Personnel to Perform Assigned Duties Resulting in Missed TS Required Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 6/1/92, the fire protection for multiple areas of the Plant was declared inoperable due to the uncertainties regarding the fire proofing material used to protect components and cabling within those areas. Compensatory actions required by the Technical Specifications (TS) were established. On 2/11/94, a routine review of completed Fire Watch (FW) patrol records identified three (3) discrepancies in which an hourly FW patrol on the Essential Service Water (ESW) pump room was not conducted for a period of 1 hour 29 minutes on 12/28/93, 1 hour 38 minutes on 12/30/93 and 1 hour 29 minutes on 12/31/93. Additional reviews were conducted and identified one (1) additional discrepancy in which an hourly FW patrol was not conducted on the U-1 CD Emergency Diesel Generator (EDG) room for 1 hour 22 minutes on 2/24/94.<br /><br /> A random monitoring program has been developed to review FW tours. These events, lessons learned from these events, and management expectations were conveyed to Plant Protection personnel. FW patrol training and implementing procedures are being revised to incorporate the lessons learned from these events.
3151994006 | Cook 1, Cook 2 | 04/04/1994 | 03/06/1995 | 9503130162 | <strong>Cancellation of LER 94-006-00</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1994, with Unit 1 in Mode 6, a seismic gap filled with untreated styrofoam was discovered in the Unit 1 East Main Steam Valve enclosure. The gap was covered with a fireproof silicone sheeting, which had degraded, exposing the styrofoam underneath. Two adjacent gap seals were examined, and were also found to contain untreated styrofoam. All three seals were declared inoperable, and compensatory actions per Technical Specification 3.7.10 were initiated. <br /><br /> An interim LER was submitted on June 10, 1994, under 10CFR50.73(a)(2)(i)(B). LER 94-006-00 stated that an inspection program had been undertaken to determine the total number of gaps filled with the unqualified material. When the entire population of gap seals was inspected, a revision to LER 94-006-00 would be submitted. <br /><br /> The inspections were completed in July 1994. The results of the inspections were evaluated and it was determined that this event was not reportable. This submittal outlines the evaluation performed to reach and support the conclusion of "Not Reportable", and serves to cancel LER 94-006-00.
3151994007 | Cook 1 | 06/07/1994 | 07/06/1994 | 9407130309 | <strong>Exceeded Technical Specification Action Statement Due to Unnoticed Inacurracy in Calculation Used to Determine Rod Position</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1994, at 0843 hours with Unit 1 in Mode 1 (Power operation) it was determined that the Rod Position Indication (RPI) for Rod B-6 was indicating greater than 12 steps from the Demand Position Indication. At 0906 hours coil stack voltage measurements and calculations were completed, with rod position determined to be within the 12 steps required by Technical Specifications. The procedure was repeated for Rod B-6 at 1408 and 2000 hours, with the same results. <br /><br /> The data sheet for 2000 hours was later reviewed by the afternoon supervisor, who discovered that the calculations had been completed incorrectly each time they were performed since the Rod Position Indicator (RPI) had been declared inoperable. When the calculations were corrected it was found that the coil stack voltages indicated the rod's position to be greater than 12 steps from demand. <br /><br /> Reactor Engineering was called in to perform the required flux map, which determined that Rod B-6 was within the required 12 steps of demand. The flux map was performed at 2307 hours, exceeding the 8 hour LCO requirement of Technical Specification 3.1.3.2 by more than 6 hours.
3151994008 | Cook 1 | 01/29/1994 | 07/18/1994 | 9407250057 | <strong>Spent Fuel Pool Exhaust Ventilation System Inoperable Due To Unacceptable Leakage Around The Charcoal Adsorber</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1994, a routine engineering review of post-surveillance as-found Halide Detector calibration data brought into question the operability of the SFP Exhaust filter system. The Halide Detector had been used for surveillance testing of filter system efficiency performed on January 29, 1994 and was used as the basis for considering the system operable. On May 12, 1994, retesting of the filter system efficiency with a calibrated instrument determined that the filter system was inoperable. With the system inoperable, Technical Specification 3.9.12 prohibits all operations involving movement of fuel within the storage pool or crane operation with loads over the storage pool. No such operations were in progress at the time of the retest. A June 17, 1994 Engineering Review concluded that the SFP Exhaust Filter System had been inoperable from January 29, 1994 until May 12, 1994. Fuel movement in the SFP did occur on February 23-26, 1994 and April 4-6, 1994 in violation of Technical Specification 3.9.12. The cause of the filter efficiency test failure was related to debris on the fan unit bypass damper sealing area. This problem was corrected and, on May 17, 1994 following retesting, the system was declared operable. No cause has been determined for the out-of-calibration as-found condition of the Halide Detector. This event is reportable as an operation or condition prohibited by the Plant's Technical Specifications. This event did not adversely impact the health and safety of the public.
3151994009 | Cook 1 | 07/12/1994 | 08/05/1994 | 9408170039 | <strong>Required Continuous Fire Watch Post Not Established Due To Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1994 at 0000 hours, with Unit 1 in Mode 1 at 100% power, the Unit 1 Turbine Building Fire Protection header between 1-FP-183 and 1-FP-196 was found to have been isolated. <br /><br /> Two clearances supporting maintenance evolutions for fire protection header system component repairs were placed into effect concurrently without appropriate compensatory actions being initiated. Fire Zone #105, the Contractor Access Control area which gives access to the Auxiliary Building, is required to be under a continuous fire watch patrol when the fire suppression system for this area is inoperable. Contrary to Technical Specification 3.7.9.2.b, a continuous fire watch patrol was not established. <br /><br /> When discovered, a continuous fire watch post was established in accordance with Technical Specifications, and remained in effect until the clearances had been lifted and the system restored. <br /><br /> This event was determined not to have safety significance and did not represent a hazard to the safety and health of the public.
3151994010 | Cook 1 | 05/02/1994 | 08/09/1994 | 9408170033 | <strong>Missed Containment Personnel Access Door Surveillance Due to Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>Plant technical specifications on Divider Barrier Personnel Access Doors and Equipment Hatches requires that the personnel access doors and equipment hatches between the containment's upper and lower compartments shall be determined operable by visual inspection prior to final closure of the penetration each time it has been opened. As a result of inadequate administrative controls to ensure and document compliance with this specification it could not be determined if the surveillance had been met for two Unit 1 personnel access doors on May 2, 1994 when a mode change was made from mode 5 to mode 4. Due to the inability to demonstrate compliance with the surveillance and knowledge that the doors had been opened it was concluded that the surveillance requirement was missed. <br /><br /> The two suspect personnel access doors were inspected prior to mode ascension on May 24, 1994 and found to be operable. Administrative controls will be enhanced to ensure compliance and documentation of the subject surveillance requirement.
3151994011 | Cook 1, Cook 2 | 10/28/1994 | 12/12/1994 | 9412210135 | <strong>Missed Liquid Effluent Batch Release Sample Compositing Analysis Surveillance Due to Lack of Adequate Counting Room Program Oversight</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1994, it was discovered that three of six liquid effluent batch release samples from the month of October could not be located. Technical Specification 4.11.1.1.1 requires that liquid effluent batch release samples be composited on a monthly and quarterly basis. When the samples could not be located, it was assumed that they had been disposed of, and the three available samples were composited and analyzed. <br /><br /> On November 18, 1994, it was determined that the event was reportable under 10CFR50.73(a)(2)(i)(B). <br /><br /> This event resulted from a lack of oversight of the counting room program which resulted in the need to use multiple procedures to complete a single task. <br /><br /> The procedures will be revised to ensure proper retention of the samples for monthly and quarterly compositing. <br /><br /> During the month of October no abnormal operation occurred that would have caused a shift in the normal radionuclide composition of effluents. At no time was the health and safety of the public affected by this event as each liquid effluent batch was sampled and analyzed prior to release and showed no abnormal results.
3151994012 | Cook 1 | 11/30/1994 | 12/30/1994 | 9501060210 | <strong>Effluent Vent Stack Sample Not Analyzed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1994 during a review of Unit One gaseous radiological effluent data, it was noted that the vent stack particulate filter gamma spectrum results for November 30, 1994 were not available. Technical Specification 3/4.11.2, Table 4.11-2 requires these samples to be collected weekly and analyzed within 48 hours from sampling. The vent stack sample had been obtained in accordance with the required frequency, but destroyed prior to the required gamma analysis. The particulate filter from the backup monitor was analyzed at 120 hours after sampling. No particulate activity was detected in the backup sample. The iodine and gas samples analyzed for that time period showed no unusual radionuclide concentrations. <br /><br /> On December 12, 1994 it was determined that the event was reportable under 10 CFR 50.73(a)(2)(i)(B). <br /><br /> This event was due to personnel error. The Nuclear Test Schedule (NTS), a computer generated list of surveillances to be performed, was initialed indicating that the analysis had been completed. NTS is used as an administrative aid with surveillances being initialed or checked off as they are performed. <br /><br /> During the week of November 30, 1994 no abnormal operational activities occurred that would have cause an alteration in the normal radionuclide composition of the Unit One vent stack effluent, as was confirmed by the analysis of the backup sample. This event was determined not to be safety significant and did not represent a hazard to the health or safety of the public.
3151994013 | Cook 1, Cook 2 | 12/16/1994 | 01/16/1995 | 9501250142 | <strong>Fire Protection in Zone 29G Found Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>This is a follow-up report pursuant to the one-hour telephone notification made in accordance with 10CFR50.72(b)(ii)(b) on December 21, 1994. Certain cables associated with the Unit 1 and Unit 2 Essential Service Water (ESW) systems were found to not be enclosed in a 1 hour rated fire barrier in Fire Zone (FZ) 29G. An Unsealed penetration was also discovered between zones 29g and 29a. This is contrary to the configuration submitted in an exemption request to 10CFR50 Appendix R, Section III.G.2, which was subsequently granted in the loss of both Unit 1 ESF pumps and the loss of the nonoperating Unit 2 ESW pump. <br /><br /> Upon discovery, fire watches were immediately established in Fire Zone 29G in accordance with Technical Specification 3.7.10. <br /><br /> This condition was determined to have little safety significance due to the availability of fire detection systems in the area, the low combustible loading in the zones affected and the minimal effect on the calculated Core Damage Frequency (CDF). At no time was the health or safety of the public in jeopardy due to this event.
3151994014 | Cook 1, Cook 2 | 12/25/1994 | 01/24/1995 | 9502020100 | <strong>Weekly Gaseous Grab Sample Not Taken Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1995 it was discovered that Technical Specification surveillance 4.11.2.1.2 for Units One and Two Gland Seal Exhaust weekly gaseous effluent grab sample was not completed for the period of December 17 through December 25, 1994. As the sampling requirement was not met, this event is reportable under 10CFR50.73 (a)(2)(i)(B), as a condition prohibited by Technical Specifications. <br /><br /> Technical Specification 4.11.2.1.2 requires a monthly surveillance on the Gland Seal Exhaust for particulate, iodine and tritium in addition to the weekly gaseous grab sample. The individual involved mistakenly marked the line item for the gaseous sample as 'Not Applicable' (N/A) on the Nuclear Test Schedule system, believing the item was the monthly surveillance for particulate, iodine and tritium which had been completed the previous week. <br /><br /> This event is attributable to personnel error. Weaknesses in the Nuclear Test Schedule system schedule form and its use were identified during the investigation. These weakness have been addressed. <br /><br /> During the month of December 1994, no abnormal operational activities occurred that would have caused an alteration in the normal nuclide composition of either units' Gland Seal Exhaust effluent. A review of the gaseous samples obtained before and after this event indicated no unusual nuclides present. It was concluded that the missed surveillance created no safety hazard, nor was the health and safety of the public jeopardized at any time.
3161994001 | Cook 2 | 02/21/1994 | 03/23/1994 | 9404190127 | <strong>Unit 2 Reactor Trip On Low-Low Level In Steam Generator #4 As A Result Of Inadequate Valve Actuator/Stroke Adjustment Procedure</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1994 at 1413 hours with Unit 2 in Mode 1 at 60 percent Rated Thermal Power, Unit 2 received a reactor trip signal from a Steam Generator No. 24 low-low level condition. At the time of the trip, the Control Room crew was restoring Main Steam Stop Valve 2-MRV-240 to operable status. The valve had been declared inoperable earlier in the day (1043 hours) to repair Beat leakage on 2-MRV-241, one of the two associated dump valves. The repair work required voluntary entry into Technical Specification 3.7.1.5, which allowed continued power operation provided the inoperable valve was restored to operable status within four hours. When the dump valve was placed in service following repairs, it failed to remain closed. This caused the stop valve to begin to quickly close, which in turn, lead to a reactor trip on low-low steam generator level. <br /><br /> The root cause of this event is attributed to the valve actuator recoupling procedure. The procedure for inspection and adjustment of pneumatic/spring actuators, associated positioners, and limit switches was revised to improve the direction for coupling actuators to valves to better ensure the correct stroke length and set pressures are accurately obtained when coupling the valve to the actuator.<br /><br /> All safety systems operated normally in response to the trip signal. The event had no actual or potential adverse impact on the health and safety of the public.
3161994002 | Cook 2 | 04/30/1994 | 05/31/1994 | 9406100001 | <strong>Fire Watch Tour Omitted Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 01-21-94 at 1015, Fire Door 2-DR-AUX344 for the 609' elevation (elev.) of the Turbine (Tur.) Building (Bldg.) was declared inoperable (which rendered the CO sub 2 suppression system for Fire Zones 46A, 46B 46C and 46D inoperable) Technical Specifications (TS) 3.7.9.3 and 3.7.10 required Action items were established. On 04-29-94 at 2308 an hourly FW toured the above described area. A shift turnover occurred at 2315 in which the tour point was omitted from the newly created tour sheet. The TS (3.7.9.3 and 3.7.10) required tour did not occur again until recognized and questioned by FW personnel to the FW Supervisor on 04-30-94 at 0030. The FW Supervisor recognized that the TS 3.7.9.3 and 3.7.10 action statements were not being met and contacted FW personnel and had the tour point added to the tour. A tour of the area was conducted on 04-30-94 at 0037. The U-2 4Kv CO sub 2 system for Fire Zones (FZ) 46A, 46B, 46C and 46D, and Fire Door 2-DR-AUX344 were inoperable without a hourly FW for 1 hour 26 minutes.<br /><br /> The policy for implementing fire watch tour sheets has been revised to require a review and then an independent review prior to use. This event was discussed and reviewed with the personnel involved.
3161994003 | Cook 2 | 04/23/1994 | 07/01/1994 | 9407070328 | <strong>Compensatory Samples Invalid Due to Equipment Configuration</strong><br /><i>Abstract:&nbsp;</i>At 0845 on April 21, 1994, during the startup of Unit Two, the continuous Radiation Monitor (IL) SRA 2905 for the Steam Jet Air Ejector (SJAE) vent was declared inoperable due to condensation buildup in the sample process lines. To facilitate its dry out, the sample plugs were removed from the SRA 2900 sample wells. installed, three compensatory samples were taken at the SPING unit. The system is configured with the sample point upstream of both the sample wells and the sample pump, therefore the technician was sampling the system at a point where no flow existed. It was determined on June 1, 1994, that Technical Specification 3.3.3.10, Table 3.3-13 requirements for compensatory sampling were not met due to the configuration of the system at the time the samples were taken. <br /><br /> The root cause of the event was ineffective administrative controls concerning the status of the SPING sampling capabilities during compensatory sampling. Contributing factors included lack of procedural guidance for the RP instrument group regarding activities that cause the SPING to be unavailable for grab sampling and a lack of training for the chemistry technicians and the RP Tech Spec technicians that removing the plugs would result in non-representative grab samples.<br /><br /> Corrective actions included reinstallation of the sample plugs prior to pulling subsequent samples. Radiation Protection will revise their SPING system procedure to ensure system integrity whenever compensatory sampling is in effect. Chemistry and RP will evaluate the training received by technicians on the SPING system. A minor modification to the SPING system is scheduled to be completed during the Unit Two 1994 refueling outage, which will alleviate the moisture problem. A similar modification has already been installed on Unit 1.
3161994004 | Cook 2 | 05/30/1994 | 06/29/1994 | 9407080179 | <strong>Use of Notice of Enforcement Discretion to Extend B&C Leak Rate Testing Interval</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1994 letter AEP:NRC:1204 was submitted requesting a schedular exemption to 10CFR50, Appendix J for Type B and C leak rate testing. The request was to allow Unit 2 to operate beyond the surveillance due date until the scheduled refueling outage in September 1994, thus avoiding a forced outage to perform the surveillances. <br /><br /> Due to the unexpected Federal Holiday on April 27, 1994, the Federal Register was published a day later than scheduled. This moved the expiration of the 30-day public comment period to Saturday, May 28 instead of Friday, May 27. In combination with the Memorial Day holiday, the proposed Technical Specification amendment could not be issued until May 31, 1994, after the expiration of the surveillance period. Prompt action was taken to avoid the forced shutdown of Unit 2 in the form of a request for Notice of Enforcement Discretion (NOED). <br /><br /> After review by NRR and Region III, the NOED was granted on May 26, 1994, to be effective for a maximum period of three days, from May 30 to June 1, 1994. This bridged the time period from the end of the surveillance period to the issuance of the amendment.
3161994005 | Cook 2 | 08/15/1994 | 09/14/1994 | 9409260261 | <strong>Unit 2 Reactor Trip on Low Feedwater Flow to Steam Generator #23 Coincident with Low SG Level as a Result of a Loss of Both Main Feedwater Pumps Due to Loss of Vacuum</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1994 at 2350 hours with Unit 2 in Mode 1 at 60 percent Rated Thermal Power, Unit 2 received a reactor trip signal from a Steam Generator Number 23 Low Feedwater Flow Coincident with Low SG Level. At the time of the trip, the Control Room crew was in the process of removing the Number 21 Circulating Water (CW) Pump from service to troubleshoot a spurious low voltage alarm on the 4 KV bus. The closing of a CW pump discharge valve and stopping of the pump caused debris in the CW system to be stirred up and entrained in the cooling flow. The entrained debris then entered the Main feedpump turbine (FPT) condenser waterbox supply lines. The flow restriction in the FPT condenser waterboxes caused a rapid loss of vacuum and the West Main feedpump tripped on low vacuum. The reactor subsequently tripped on low feed flow coincident with low level on Loop 3. <br /><br /> The root cause of this event is attributed to zebra mussels within the Circulating Water system which temporarily blocked cooling flow through the main feedpump condenser water box tubes and caused a main feedpump trip on low vacuum. <br /><br /> After the reactor trip all safety systems operated normally and the reactor stabilized in Mode 3. The main feedpump condenser water boxes were cleaned and inspected and the reactor was returned to critical on August 16, 1994 at 2233 hours.
3161994006 | Cook 2 | 09/06/1994 | 10/03/1994 | 9410110049 | <strong>Failure Of The Unit Two Main Steam Safety Valves To Meet Technical Specification Lift Setpoint Requirements</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1994, with the Unit 2 Reactor in Mode 3 (hot standby), routine surveillance testing found the initial lift pressures for six of twenty Main Steam Safety Valves (MSSVs) outside the +/- one percent setpoint tolerance established by Plant Technical Specifications. Five of the valves lifted above the allowable setpoint range; one lifted below the allowable range. However, all six initial lifts were within +/- three percent of their nominal lift setpoint. Three of the MSSVs had acceptable subsequent lifts and did not require adjustment. Based on previous events, the high initial lift is believed to be caused by mild galling between the valve disk and nozzle, along with mechanical 'keying' and/or chemical bonding of the mixed oxides on the disk with the chromium oxide on the nozzle. The other three valves did require adjustment to restore them to within tolerances. These were partially attributed to setpoint drift. <br /><br /> On September 9, 1994, D. C. Cook was granted a Technical Specification amendment which increased the MSSV setpoint tolerances to +/- three percent, The as-found condition reported here under the more stringent Technical Specifications in effect previously, has already been analyzed as part of the licensing submittal and determined not to have an adverse impact on the health and safety of the public.
3161994007 | Cook 2 | 09/09/1994 | 12/22/1994 | 9501060211 | <strong>Containment Type B and C Leakage Exceeds LCO Value Due To Leakage of Post Accident Sample Line Check Valve</strong><br /><i>Abstract:&nbsp;</i>This supplemental report provides additional information regarding the Type B and C Leakrate Testing results reported on September 9, 1994. On September 9, 1994, with Unit 2 in mode 6 (Refueling) the accumulated leakage for the Type B and C Leakrate Tests on Containment penetrations and isolation valves exceeded the Technical Specification L.C.O. value of 0.60 La. At 1525 hours a four hour phone report was made to the NRC, as required by 10CFR50.72(b)(2). The total as-found Type B and C leakrate was 15.96 La. (The calculated leakrate of 2-NS-357 was determined to be 15.49 La, while the measured leakrate for all other penetrations was only 0.476La.) 2-NS-357 is a 0.5 inch diameter bonnet hung swing type check valve which serves as the Post Accident RCS Sampling Station Sample Waste Return Line Isolation Valve. During troubleshooting, the valve leakrate could be reduced by tapping the valve body. Upon disassembly and inspection, no conditions were found which would account for this inconsistent behavior. The valve was replaced and re-oriented to position the valve in a vertical line. Subsequent testing was unacceptable. Therefore, the original swing check valve was replaced with a spring loaded piston check valve. It was determined that the original valve may not be well suited for this specific application. The as-left Type B and C leakrate was 0.143 La. The leakage of valve 2-NS-357 would not have put the Plant in an unsafe condition, as the sample line is designed with redundant isolation valves. This event did not have a significant impact on public health and safety.
3161994008 | Cook 2 | 12/11/1994 | 01/10/1995 | 9502020108 | <strong>Rx Trip Caused by a Turbine Trip on High Moisture Separator Reheater Level</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1994, at 1705 hours with Unit 2 in Mode 1 at 19 percent Rated Thermal Power, Unit 2 received a turbine trip/reactor trip signal from a Main Turbine Moisture Separator High Level. At the time, of the trip, the Control Room crew was attempting to transfer the Right Moisture Separator Reheater (MSR) drain from the Main Condenser to the 4B Feedwater Heater via the Right Moisture Separator Drain Tank (MSDT). Level alarms which normally precede the MSR high level trip signal did not actuate. The turbine trip signal caused the reactor trip. <br /><br /> Despite the efforts of a troubleshooting team assigned to determine the root cause of this event, the cause of the MSR high level trip signal could not be conclusively determined. Other than the failure of the Right MSDT level alarms to actuate, no system, control or procedural abnormalities were noted. An extreme high level was observed prior to the trip in the 4B heater, but is not unusual during startup and could not be established as the cause of the event. <br /><br /> After the reactor trip, all safety systems operated normally and the reactor stabilized in Mode 3. The Right MSDT high water level alarms were inspected, repaired, and tested. The reactor was returned to critical on December 12, 1994 at 2033 hours.
3161994009 | Cook 2 | 04/02/1994 | 10/10/1995 | 9510170247 | <strong>Plant Conditions Outside the Design Basis Due to Personnel Error in Aligning Engineered Safety Feature Fans for Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1994, while performing a post high efficiency particulate air (HEPA) filter replacement surveillance test on one of the Unit 2 Engineered Safety Feature- Exhaust Filter Train the redundant Unit 2 Exhaust Filter Train Unit was taken to off resulting in entry into Technical Specification (TS) 3.0.3. The plant's TSs provide action for a single inoperable Exhaust Filter Train; however, upon inoperability of both trains, TS 3.0.3 is entered. This alignment existed for six minutes prior to being recognized. Once recognized the Exhaust Filter Train which had been taken to off was immediately restarted. <br /><br /> Based on the available information, this event was originally determined to not be reportable under 10CFR50.72 or 10CFR50.73. However, the event was later reevaluated and determined to be reportable under 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications and 10CFR50.73(a)(2)(ii), as a condition that was outside the design basis of the plant. The original reportability review had assumed credit for the exhaust filter train under test, which was subsequently confirmed operable through surveillance testing; therefore, during the six minutes of misalignment only one Exhaust Filter Train was considered inoperable and TS 3.0.3 need not have been entered. The design basis criteria was not considered applicable as the event response was being directed by the technical specifications. <br /><br /> This event has minimal safety significance as the Exhaust Filter Train under test was capable of performing it's intended safety function, the misalignment was of short duration and proper operation of the system is confirmed as part of the emergency operating procedures when the system is required. At no time was the health or safety of the public in jeopardy.
3161994010 | Cook 2 | 10/12/1994 | 09/18/1995 | 9509220041 | <strong>Unexpected isolation of containment purge valves During surveillance due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1994, in preparation for performance of Engineered Safety Features (ESF) Time Response Testing, containment purge isolation valves were closed. When delays occurred in restoring plant conditions from a previous surveillance test the same purge isolation valves were opened and the containment purge exhaust fans started to provide containment cooling. When conditions again existed to continue with the ESF time response testing the test coordinator incorrectly assumed that the purge valves had remained closed. During actual ESF time response testing the opened containment purge isolation valves automatically closed per design. This was unexpected by the test coordinator as he had assumed the valves were closed. <br /><br /> Based on the available information at the time of the event, this event was originally determined to not be reportable under 10CFR50.72 and 10CFR50.73. However, the event was later reevaluated and determined to be reportable under 10CFR50.72(b)(2)(ii), as any event or condition that results in manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System and under 10CFR50.73(a)(2)(iv) as any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature, including the Reactor Protection System as the closure of the valves was an unexpected response to an ESF signal. <br /><br /> This event has minimal safety significance as the system performed as designed and the reactor core had been unloaded into the spent fuel pool at the time of testing.
3171994001 | Calvert Cliffs 1 | 01/24/1994 | 02/18/1994 | 9405130195 | <strong>Unit 1 Reactor Trip and ESFAS Actuation Due to 12 120 VAC Inverter</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1994, at 0926, Calvert Cliffs Unit 1 experienced a reactor trip and partial actuation of system ZB of the Engineered Safety Features Actuation System (ESFAS). The reactor trip and ESFAS actuation occurred due to fluctuations in the output voltage from 12 120 VAC Vital Bus Inverter. The inverter output voltage fluctuated due to a defective voltage regulator board within the inverter. At the time of the event, Unit 1 was at 100 percent power with normal operating temperature and pressure. <br /><br /> Troubleshooting after the event identified the defective regulator board. The board appeared to be defective either due to a loose fuse in the voltage feedback circuit or due to a screw found wedged between the boards of the card. Additional inspections identified a loose capacitor and defective oscillator board. <br /><br /> Corrective actions include the inspection of the other inverters on Unit 1 and 2, replacement of the inverter with upgraded models, and an evaluation to determine if debris intrusion controls for the inverters are adequate.
3171994002 | Calvert Cliffs 1, Calvert Cliffs 2 | 02/24/1994 | 03/24/1994 | 9403290319 | <strong>Missed Surveillance on Diesel Generators Due to Misunderstood Applicability</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1994, it was discovered that the emergency diesel generator (EDG) load sequencer timer had not consistently been tested in Modes 5 and 6 as required by the Technical Specifications. This led to periods during the 1992 and 1993 refueling outages when the EDC dedicated to the shutdown unit was technically inoperable. The missed surveillance was caused by a misunderstanding about whether the test was required in these modes. There were no safety consequences associated with this event. The automatic EDG start function supported by the load sequencer is not required in Modes 5 and 6. Corrective action included measures by supervision to stress good communications and submittal of a Technical Specification amendment to delete the unnecessary test. This amendment had been submitted prior to discovery of this event.
3171994003 | Calvert Cliffs 1 | 03/21/1994 | 04/20/1994 | 9404250248 | <strong>Pressurizer Heater Sleeve Cracking</strong><br /><i>Abstract:&nbsp;</i>At 1800 hours on February 16, 1994, during removal of insulation from the Unit 1 Reactor Coolant System (RCS) pressurizer (PZR) heater sleeve area, boron deposits were noticed on PZR heater sleeve B-3 indicating leakage from the RCS. At 1700 hours on February 23, 1994, upon completing insulation removal, boron deposits were also identified on PZR heater sleeve FF-1. After discovering the leaks, boroscopic and eddy current testing were performed and heater sleeve FF-1 was examined in the laboratory. The examination revealed a circumferential bulge approximately 0.5 inches long and 0.019 inches high (diametrical) in the area of the boric acid leaks. The most probable cracking mechanism is Primary Water Stress Corrosion Cracking. The bulge area and the axial scoring showed evidence of surface metal smearing and cold work. A search of fabrication records for the PZR turned up evidence that sleeve FF-1 had to be reworked due to the presence of a stuck reamer. The source of stress for the cracking was the bulging and axial scratches associated with the removal of the stuck reamer. Corrective Actions included plugging FF-1 with an Alloy 690 plug welded to the outer diameter of the PZR lower head and examining the remaining Unit 1 PZR heater sleeves.
3171994004 | Calvert Cliffs 1 | 02/21/1994 | 07/29/1994 | 9408040213 | <strong>Excessive Corrosion of Incore Instrumentation Flange Components</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1994, we discovered higher than anticipated corrosion of three nuts on one of the Incore Instrumentation flanges on the Unit 1 reactor vessel head. A subsequent inspection discovered an additional flange with similar degradation. The flanges were known to be leaking slightly since 1993, but we deferred repairs until 1994 because the expected corrosion rate was very low. The excessive corrosion rate was apparently due to the presence of wet boric acid on some of the flange components where we expected only dry boric acid. There were no actual safety consequences, although the potential existed for a significant leak. Corrective action to repair the leaking flanges is complete.
3171994005 | Calvert Cliffs 1, Calvert Cliffs 2 | 04/24/1994 | 05/24/1994 | 9406010221 | <strong>Partial Loss of Offsite Power Caused by a 13.8 kV Voltage Regulator Fault</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1994 Calvert Cliffs experienced a partial loss of offsite power during testing activities associated with new 13.8 kV voltage regulators (VR). A turn to turn fault in VR 1102 caused an actuation of the ground fault protective circuits associated with VR 1101, VR 1102, and VR 1103. This resulted in deenergizing Bus 11 13.8 kV feeder breakers for Unit 1 non-safety Busses 15 and 16 and Unit 2 safety Bus 21. Emergency Diesel Generator 12 started. <br /><br /> The immediate cause of the event was a turn to turn fault inside VR 1102 due to foreign material between the turns. The cause of the ground fault protection circuits actuating was most likely a result of their sensitivity to rapid electrical pulses resulting from arcing inside VR 1102. <br /><br /> Voltage regulator 1102 has been replaced. We are currently investigating methods to decrease the ground fault circuits sensitivity to rapid electrical pulses. We have improved our VR testing methodology to facilitate early identification of faults in other VRs.
3171994006 | Calvert Cliffs 1 | 06/16/1994 | 09/30/1994 | 9410060086 | <strong>Unit Trip Due to Inadvertent Closure of Main Turbine Stop Valves</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1994, Calvert Cliffs Unit 1 tripped from 100 percent power due to an automatic actuation of the Reactor Protection System (RPS). The RPS signal was the result of low steam generator water levels due to feedwater shrink after all four main turbine stop valves (MTSVs) unexpectedly closed during performance of a weekly MTSV test. After the trip, steam generator levels trended downward with Steam Generator 12 level decreasing more rapidly than Steam Generator 11 level. About eight minutes after the trip, the auxiliary feedwater system actuated, restoring positive level trends in both steam generators. <br /><br /> Troubleshooting efforts did not positively identify the specific hardware cause of the MTSVs closing. Subsequent to this event, another trip of the Unit occurred on July 19, 1994, due to MTSV closure with no testing in progress. The root cause analysis of these two events have been combined. The results will be provided in the supplement to LER 317-94-007 concerning the July 19 event.
3171994007 | Calvert Cliffs 1 | 07/19/1994 | 06/16/1995 | 9506230052 | <strong>Reactor Trip Caused by Closure of Turbine Stop Valves</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1994 at 1824 Calvert Cliffs Unit 1 tripped from 100 percent power due to a Reactor Protection System (RPS) actuation. The RPS actuation was the result of low steam generator water levels due to level shrink after all four main turbine stop valves (MTSV) unexpectedly closed. During the resulting transient both Reactor Coolant System (RCS) power-operated relief valves opened and one code safety relief valve (RV) opened, closed, and then began leaking by its seat at approximately 25 gpm.<br /><br /> The event did not result in any significant potential or actual nuclear or personnel safety consequences.<br /><br /> Short-term corrective actions to support a safe Unit restart were completed. The RV manufacturer has initiated process improvements to prevent recurrence of inadequate staking of a disc holder to bellows assembly inside the RV. The root cause of the MTSV closure has been incorporated into an ongoing turbine EHC Systems improvement effort.
3171994008 | Calvert Cliffs 1 | 09/15/1994 | 10/14/1994 | 9410270366 | <strong>Technical Specification Violation Due to Two RPS Channels Out-of- Service During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1994, while performing Engineered Safety Features Actuation System (ESFAS) surveillance testing at Calvert Cliffs Unit 1, an Instrument Maintenance (IM) technician installed test equipment and opened slide links for the wrong instrument channel. As a result, for about 15 seconds, two channels of the Reactor Protective System (RPS) were not available. This was a condition prohibited by Technical Specifications. At the time of the event, the Unit was at 100 percent power. <br /><br /> The causes of the event were: 1) established self-checking practices were not adequately applied to ensure intended actions were correct; and, 2) the technicians performing the procedure completed two steps in reverse order. <br /><br /> Appropriate personnel actions have been taken; we will be reviewing this event with appropriate plant personnel to reemphasize the self- verification process and procedural adherence. Actions have been initiated to determine and correct the reasons why the self-verification process was not successful in preventing this event.
3181994001 | Calvert Cliffs 2, Calvert Cliffs 1 | 01/12/1994 | 03/16/1994 | 9403230057 | <strong>Reactor Trip Due to Opening of 13.8 Kilovolt Feeder Breaker</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1994 at 0552, Calvert Cliffs Unit 2 tripped when an electrical protective relay actuated in the 13.8 kv voltage regulator (2H2103) for Unit Service Transformer (UST) U-4000-22. This actuation caused the loss of 4 kv Busses 22, 23, and Safety Bus 24. Both control element drive mechanism motor generator sets lost power, causing a reactor trip from loss of power to the control element drive assemblies and a main turbine trip. <br /><br /> The cause of the 13.8 kv feeder breakers opening was the actuation of the sudden pressure trip circuit for the 13.8 kv voltage regulators due to intermittent grounds on their associated 125 VDC bus.<br /><br /> A Significant Incident Finding Team was appointed by the Plant General Manager to investigate the event. The results of this investigation and associated corrective actions are included in this supplemental report.
3181994002 | Calvert Cliffs 2 | 03/05/1994 | 04/04/1994 | 9404110020 | <strong>Inadvertent ESFAS Actuation Due to Less Than Adequate Self Verification</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1994 Calvert Cliffs Unit 2 experienced an inadvertent engineered safety feature actuation during a Technical Specification required monthly logic test. The actuation occurred when an incorrect logic module was manually actuated during the test. The Unit was at 100 percent power at the time of the event. <br /><br /> The causes of the event have been identified as less than adequate use of our established self verification process and poor human factors configuration of the engineered safety features actuation system logic modules. No nuclear safety consequences resulted from this event. <br /><br /> Corrective actions include re-emphasizing expectations to restart the self-verification process if interrupted and evaluation of the need for human factors enhancements to the labeling and demarcation of the logic cabinets. This event has also been discussed with Operation Shift Crews to re-emphasize expectations and responsibilities of those performing important evolutions.
3181994003 | Calvert Cliffs 2 | 07/11/1994 | 08/10/1994 | 9408170095 | <strong>Reactor Shutdown for Leak from Fatigue Crack in Safety Injection Tank Line</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, July 11, 1994 at about 1115 hours, a non-isolable Reactor Coolant System pressure boundary leak was discovered at Calvert Cliffs Unit 2. The leak was found to be caused by a 150 degree circumferential crack in a weld in the 22A Safety Injection Tank discharge test connection. In accordance with Technical Specification 3.4.6.2, 'Reactor Coolant System Leakage,' Action A, the Unit commenced a shutdown to HOT SHUTDOWN (MODE 4). <br /><br /> The line had been removed and replaced in the spring of 1993. It is suspected that minor changes made at this time resulted in harmonic oscillation causing high cycle fatigue failure. <br /><br /> The support for this line was redesigned and similar lines were examined to verify that similar conditions do not exist. The circumstances of this event will be reviewed with Design Engineering personnel. We will evaluate whether additional generic measures to prevent high frequency fatigue failure are appropriate.
3181994004 | Calvert Cliffs 2 | 08/10/1994 | 09/08/1994 | 9409160127 | <strong>Unit 2 Reactor Trip Due to Main Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1994 at 2154, Calvert Cliffs Unit 2 experienced a reactor trip due to a main generator trip. The generator tripped when the exciter field breaker and generator output breakers tripped opened due to a loss of field. At the time of the event, Unit 2 was operating at 100 percent power with normal operating temperature and pressure. <br /><br /> The cause of the event was a drop in main generator excitation leading to the actuation of the loss of field relay. Excitation was low after the operators transferred the voltage regulator from the ON to OFF position. <br /><br /> Corrective actions included testing of the excitation system prior to restart; replacement of failed components; refresher training for operators; and monitoring of the system.
3181994005 | Calvert Cliffs 2 | 09/24/1994 | 10/20/1994 | 9410270275 | <strong>Unit 2 Trip Due to Main Turbine Governor Valve Opening</strong><br /><i>Abstract:&nbsp;</i>On September 24, 1994, at 2016, Calvert Cliffs Unit 2 experienced a reactor trip at 16 percent power due to low Steam Generator (SG) pressure. The low pressure was sensed after a rapid increase in steam demand was experienced due to an unexpected opening of No. 21 main turbine governor valve. <br /><br /> Troubleshooting after this event identified a loose wire on No. 21 governor valve's Linear Voltage Differential Transformer (LVDT). This loose wire essentially removed the LVDT feedback from the valve's positioning circuit. Thus, No. 21 governor valve started to open and continued to open due to the lack of feedback from the LVDT. The sudden increase in steam flow that occurred after No. 21 governor valve ramped open caused SG pressure to drop low enough to cause the reactor trip. <br /><br /> In response to this event the wire on No. 21 governor valve LVDT was tightened and the wiring on all of the other Unit 2 main turbine throttle and governor valves was checked as well. Additional system monitoring and evaluation is being performed as well.
3181994006 | Calvert Cliffs 2 | 10/27/1994 | 11/23/1994 | 9412010251 | <strong>Reactor Shutdown Due to Turbine Trip Caused by Improperly Installed Link</strong><br /><i>Abstract:&nbsp;</i>On Thursday, October 27, 1994 at about 2353 hours, Calvert Cliffs Unit 2 tripped on receipt of a Reactor Protective System Loss of Load signal. Investigators found that a ground had been caused by the 'A' phase Main Generator transition links, which were damaged by overheating after having been installed incorrectly.<br /><br /> The root cause of this event was failure to adequately address the potential risks of work newly assumed by the Electrical Maintenance group. <br /><br /> New links were correctly installed and the Unit was brought back on line. Since the time the links were installed, improvements have been made to our Maintenance processes. These existing practices will be reviewed in light of the circumstances of this event to verify their adequacy.
3211994001 | Hatch 1 | 03/14/1994 | 04/12/1994 | 9404180253 | <strong>Slight Movement in Cable Lug Connection Results in Unplanned Actuations of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 3/14/94 at 0931 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, non-licensed electricians were attempting to identify a cable in a panel containing circuitry for the Reactor Protection System (RPS) in preparation for maintenance. To identify a cable, an electrician lightly pulled on the label tag to re-position it. This action apparently moved a connection that wasn't tight, momentarily interrupting power to one breaker supplied by the RPS power supply system. Since RPS powered systems are designed to actuate on a loss of power or control signal, several Engineered Safety Features actuated, including the outboard Group 5 Primary Containment Isolation System (PCIS) valve, several outboard Group 2 PCIS valves, and the Main Control Room Environmental Control System. Licensed personnel verified the actuations occurred as expected. When no valid cause for the signal was confirmed to exist, the signal was reset and affected valves and systems were returned to their normal lineups. The cause of this event was an electrical connection in an RPS panel that wasn't tight. When an electrician moved a wire label, the connection apparently moved, momentarily interrupting power to one breaker supplied by the RPS power supply system, producing the actuations described above. The connection will be tightened when the reactor is defueled during the Unit 1 Fall 1994 Refueling Outage. An external connection drawing will be updated after the connection is tightened, and this will be completed by 01/15/95. In the interim, a caution tag has been placed on the panel and monthly inspections of the panel will be performed using infared thermography.
3211994002 | Hatch 1 | 03/25/1994 | 04/19/1994 | 9404260306 | <strong>Personnel Error Results in Engineered Safety Features Actuations</strong><br /><i>Abstract:&nbsp;</i>On 3/25/94, at 2058 EST, Unit 1 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, the following annunciators alarmed: 'Low Reactor Water Level,' 'ADS Low Water Level Actuation Timer Initiated,' 'Auto Blowdown CS or RHR Press Permissive,' and 'Auto Blowdown Relays Energized.' Additionally, the following system actuations occurred: Emergency Diesel Generators (EDG) 1A, 1B, and 1C automatically started; Core Spray System (CS) pumps 1E21-C001A and B automatically started- the Main Control Room Environmental Control System (MCRECS) transferred to the pressurization mode; and the Plant Service Water (PSW) System Turbine Building isolation valves 1P41-F310A, B, C, and D automatically closed. Licensed personnel verified that no plant conditions existed that would have resulted in the actuations received. Nonlicensed Instrument & Controls (I&C) personnel performing a surveillance on engineered safety feature actuation instrumentation were directed to terminate the surveillance. Reactor power was reduced and actions were being taken to effect a fast reactor shutdown due to the loss of Turbine Building cooling water flow. However, valves 1P41-F310A, B, C, and D were opened prior to the shutdown being initiated. The EDGs and CS system were subsequently secured. The cause of the event was personnel error in that an I&C technician placed a volt-ohm meter on an incorrect terminal during performance of a surveillance. This resulted in simulating a LOCA signal in the engineered safety features actuation logic. Corrective actions include counseling personnel, training personnel, and repairing an EDG control circuit wire.
3211994003 | Hatch 1 | 03/29/1994 | 04/25/1994 | 9405020227 | <strong>Arcing in Main Generator Exciter Results in Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 3/29/94 at 0101 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time a full Reactor Protection System (RPS) actuation and an automatic reactor shutdown occurred due to a trip of the Main Turbine. When the Main Turbine tripped, reactor pressure increased as expected to a maximum of 1085 psig and was relieved by the automatic opening of the Main Turbine Bypass Valves and seven safety relief valves (SRVs) per design. The SRVs closed as required and reactor pressure was then controlled by the Main Turbine Bypass Valves. Reactor water level decreased to a minimum of 14 inches above instrument zero (172 inches above the top of active fuel), resulting in closure of the inboard Group 2 Primary Containment Isolation System valves. Normal reactor water level was restored with the Feedwater System. The cause of this event was a loss of Main Generator field excitation leading to a trip of the Main Turbine and an automatic reactor shutdown. Field excitation was lost when arcing occurred between the Main Generator Exciter (MGE) brush rigging and one of the collector rings on the MGE rotor. Engineering personnel believe the primary factor in the arcing was sticking of a brush in the brush rigging. <br /><br /> Corrective actions for this event included replacing the damaged MGE rotor with a rotor from the Unit 2 MGE, sending the Unit 1 MGE rotor off site for repair, and increasing the frequency of MGE brush inspections to daily.
3211994004 | Hatch 1 | 04/16/1994 | 05/09/1994 | 9405170222 | <strong>Incorrect Surveillance Schedule Results in Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 4/16/94, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, a non licensed individual performing surveillance procedure 34SV-SUV-008-1S, 'Primary Containment Isolation Valve Operability,' discovered that the surveillance frequency was not correct for seven primary containment vent and purge valves. The surveillance was brought up to date that same day. should they have been, because they fully satisfied their closure time requirements as set forth in the Unit 1 Technical Specifications.<br /><br /> When this surveillance was performed in November 1993, the test results indicated the frequency should have been changed from quarterly to monthly. However, a licensed Shift Supervisor erroneously requested that the frequency be doubled (which is typical for In-Service Testing results), or changed to once per six weeks. Subsequent reviews and verifications also failed to detect the error. During the period in which the surveillance frequency was not correct, the surveillance was performed four times and should have been performed five times. <br /><br /> The surveillance was brought up to date on the day the condition was discovered, and the surveillance frequency has been corrected to once per month for the affected valves. In addition, the individuals involved in this event have been made aware of their error and the importance of strict procedure compliance has been reemphasized to them. These actions are complete.
3211994005 | Hatch 1, Hatch 2 | 05/01/1994 | 05/25/1994 | 9406010003 | <strong>Loose Connections in Power Distribution Panel Cause Unplanned ESF System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 5/1/94 at 2102 EDT, Unit 1 was in the Run mode at 100% of rated thermal power. At that time, the output breaker for the 'B' Reactor Protection System (RPS) motor-generator (MG) set opened. This caused a loss of power to the 'B' channels of the RPS, Offgas Radiation Monitoring System, Process Radiation Monitors, Neutron Monitoring System, and Primary Containment Isolation System (PCIS). These systems actuated on loss of power resulting in an automatic reactor shutdown signal in RPS logic system 'B,' closure of various PCIS valves, actuation of the pressurization mode of the Main Control Room Environmental Control System, and the 'B' trains of the Unit 1 and Unit 2 Standby Gas Treatment Systems. After three loose connections in RPS bus power distribution panel 1C71-P001 were tightened, power was restored to the bus from the RPS MG set, its normal power supply. All affected equipment was then returned to its normal configuration. <br /><br /> The cause of this event was loose connections in panel 1C71-P001. The connections apparently loosened, causing bus voltage and/or frequency limits to be exceeded, protection relay actuation, and bus de-energization. No activities were in progress that would have caused the connections to come loose; therefore, it cannot be determined why the connections were loose.<br /><br /> The connections on the 'B' RPS bus were checked and tightened; the connections on the 'A' bus and the Unit 2 RPS busses will be checked during the next refueling outage for each unit.
3211994006 | Hatch 1 | 05/15/1994 | 06/13/1994 | 9406200342 | <strong>High Pressure Coolant Injection System Taken Out of Service for Repair</strong><br /><i>Abstract:&nbsp;</i>On 5/15/94 at 1640 EDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, the High Pressure Coolant Injection (HPCI) system was removed from service to repair flow controller 1E41-R612. During checks on 5/14/94, Operations personnel had discovered that the output signal from the controller was not upscale as expected. The controller output was adjusted on 5/15/94 and monitored for several hours to ensure it remained stable. Citing a recent instance of setpoint drift in the controller, Operations personnel declared the HPCI system inoperable on 5/15/94 at 1640 EDT to permit removal and examination of the controller. The controller was removed from service and failed components were identified and replaced. Surveillance testing was then performed successfully. At 1206 EDT on 5/17/94, the HPCI system was declared operable. On 5/20/94, questions arose as to the qualification of the replacement components installed on 5/17/94. HPCI was again declared inoperable and further testing was performed. By 5/22/94, an additional capacitor had been replaced and HPCI was returned to operable status at 1830 EDT. <br /><br /> The cause of this event was component failure. Two transistors and one capacitor within the flow control circuitry for the HPCI system failed, resulting in a slowly decreasing controller output signal. <br /><br /> The failed parts were replaced and the flow controller was satisfactorily tested in all modes.
3211994007 | Hatch 1, Hatch 2 | 06/13/1994 | 07/08/1994 | 9407190322 | <strong>Main Control Room Environmental Control System Carbon Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On 6/13/94, at approximately 1300 EDT, Unit 1 and Unit 2 were both in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, it was determined that a plant procedure contained an acceptance criterion for carbon efficiency for the Main Control Room Environmental Control System (MCRECS) that was nonconservative with respect to the requirements of the Unit 2 Technical Specifications. In investigating the discrepancy, two instances were identified in the past five years in which the carbon efficiency was less than that required by the Unit 2 Technical Specifications. In each case, only the 'B' train of MCRECS was affected. The Unit 2 Technical Specifications require that with the efficiency less than 99 percent the carbon should be replaced within seven days or the unit brought to Hot and then Cold Shutdown within the following 12 and 24 hours, respectively. However, plant personnel were not aware of the conditions at the time of occurrence; therefore, the actions were not taken. The carbon had already been replaced at the time the events were discovered. Also, discussions with the Architect Engineer revealed that even though the procedural limits were in compliance with the Unit 1 Technical Specifications, 10 CFR 50, App. A, GDC 19 limits could have been exceeded in the unlikely event of an accident if the carbon efficiency for both filter trains was at the procedural limit. The investigation into the causes of the event was inconclusive but the causes appear to involve less than adequate procedural controls, less than adequate Technical Specifications, and personnel error. Corrective actions include revising procedures and revising the Technical Specifications.
3211994008 | Hatch 1, Hatch 2 | 07/14/1994 | 08/08/1994 | 9408150325 | <strong>Loss Of The "B" RPS Bus Power Supply Causes Unplanned ESF System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 7/14/94 at 2111 EDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, the output breakers for the "B" Reactor Protection System (RPS) motor-generator (MG) set opened. This caused a loss of power to the "B" channels of the RPS, Offgas Radiation Monitoring System, Process Radiation Monitors, Neutron Monitoring System, and Primary Containment Isolation System (PCIS). These systems actuated on loss of power according to their design resulting in an automatic reactor shutdown signal in RPS logic system "B," closure of various PCIS valves, and actuation of the pressurization mode of the Main Control Room Environmental Control System and the "B" trains of the Unit 1 and Unit 2 Standby Gas Treatment Systems. Power was restored to the bus from an alternate power supply and all affected equipment was returned to its normal configuration by 2307 EDT. <br /><br /> The cause of this event appears to have been component failure. A set of relay contacts in the generator voltage regulation circuit was found to be pitted, burned, and misaligned. As part of event investigation activities, this relay was slightly bumped, causing the contacts to open. This resulted in a loss of field excitation to the generator and a subsequent loss of output voltage from the generator. The output breakers then opened on loss of voltage to their trip coils per design. It appears therefore that the state of this set of contacts made it susceptible to opening spuriously. The relay was replaced and the MG set was returned to service at 1420 EDT on 7/21/94.
3211994009 | Hatch 1 | 07/28/1994 | 09/22/1994 | 9409270313 | <strong>Main Steam Line High Flow Isolation Setpoint Not Within Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On 7/28/94 at 1130 EDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100% rated thermal power). At that time, it was determined that the high flow isolation setpoint for the main steam line flow instruments was not in compliance with the requirements of the Unit 1 Technical Specifications. Technical Specifications Table 3.2-1 requires the setpoint for the high flow isolation to be flow (101 psid). However, the actual isolation setpoint was based on 138% design steam line flow (110 psid). Consequently, the actual setpoint for the flow instruments was in excess of the limit. The flow instruments were declared inoperable and Limiting Condition for Operation (LCO) 1-94-254 was entered at 1210 EDT. The setpoint was adjusted to within limits and LCO 1-94-254 was closed at 1905 EDT on 7/28/94. <br /><br /> The cause of this event was personnel error. Nuclear Steam Supply System (NSSS) personnel developing the original main steam line high flow isolation setpoint mistakenly used design steam line flow instead of the required rated flow in the calculations. <br /><br /> The setpoint was recalculated based on rated flow and the setpoint for the flow instruments was adjusted to this new value.
3211994010 | Hatch 1 | 08/08/1994 | 09/06/1994 | 9409160093 | <strong>Work in Control Room Panel with Limited Access Leads to Actuation of Engineered Safety Feature</strong><br /><i>Abstract:&nbsp;</i>On 8/8/94 at 2345 EDT, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, the Reactor Water Cleanup (RWCU) system isolated spuriously. Electricians were subsequently requested to troubleshoot the logic system, which required them to enter Control Room panel 1H11-P623. While they were working in this panel at 0540 EDT on 8/9/94, valve 1E51-F105 isolated. This valve is a Primary Containment Isolation System (PCIS) valve in the Reactor Core Isolation Cooling (RCIC) system. No valid isolation signal for this valve was present. Since the isolation logic for this valve is installed in the panel where troubleshooting activities were underway, licensed personnel concluded that the isolation had occurred as a result of troubleshooting activities. Therefore, they immediately reopened the valve. No further actuations occurred. The isolation of the RWCU system is believed to have been spurious. The cause of the isolation of 1E51- F105 was limited working conditions in Control Room panel 1H11-P623. The clearance between relay 1E51-K48 and the side of the panel is too small to pass through without contacting the relay. When the relay was bumped, the valve received an isolation signal and responded by closing, per design. As stated previously, the affected valve, 1E51-F105, was reopened immediately after it closed. GPC is investigating the possibility of relocating the relay.
3211994011 | Hatch 1 | 09/30/1994 | 10/18/1994 | 9410250144 | <strong>Personnel Error Results in Unplanned Automatic Start of Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On 9/30/94 at 0727 EDT, Unit 1 was in a refueling outage with all fuel removed from the reactor vessel. At that time, an electrician replacing a relay in the start logic for Unit 1 Emergency Diesel Generator (EDG) 'A' inadvertently shorted two relay terminals with a pair of pliers. This sent a closure signal to the 4160-volt breaker for the alternate supply to emergency electrical bus 1E. As the alternate supply breaker closed, it sent a trip signal to the normal supply breaker, resulting in a transient low voltage condition on the emergency bus. This low voltage was sensed by the EDG start logic, and the EDG started and ran. The EDG did not tie to the bus because the alternate supply breaker completed its closure and energized the emergency bus. Licensed operations personnel secured the EDG by 0735 EDT and returned it to its normal, standby condition. <br /><br /> The cause of this event was a personnel error on the part of an electrician. He was attempting to tighten a nut on a terminal post when he inadvertently created a short to an adjacent terminal using an uninsulated tool. This produced the closure signal to the alternate supply breaker to the 4160-volt 1E bus, resulting in the actuations described above.<br /><br /> The electrician has been made aware of his error and the consequences of it. In addition, this event has been discussed with the foremen and supervisors in the electrical maintenance section.
3211994012 | Hatch 1 | 10/25/1994 | 11/14/1994 | 9411220338 | <strong>Incorrect Component Assembly Results in Engineered Safety Features Actuation</strong><br /><i>Abstract:&nbsp;</i>On 10/25/94 at 1327 EDT, Unit 1 was in the Refuel mode with the core fully loaded, the reactor pressure vessel head removed, and water level above the reactor vessel flange. At that time, contract personnel were performing planned maintenance on the Main Turbine Electro-Hydraulic Control (EHC) system. During assembly of a portion of the hydraulics hardware, a bias spring was mistakenly installed on the wrong end of a hydraulic control spool piece. When the EHC pump was later turned on for a system flush, EHC fluid was misdirected by the control spool into the hydraulic actuators for the Main Turbine Stop Valves (TSVs). This caused three of four TSVs to drift full open as the EHC fluid pressure increased. When the TSVs opened with no condenser vacuum present, a partial Group 1 Primary Containment Isolation System (PCIS) trip was initiated per design. At the time of the event, only one small-bore Group 1 valve was open and in service. It closed per design. There was no other plant response to the signal nor should there have been. The cause of this event was incorrect assembly of an EHC control spool bias spring by a maintenance contractor. With the bias spring installed on the incorrect end of the control spool, the EHC system was set up to direct the working fluid to the TSVs, which opened as pressure increased. Corrective action for this event included correcting the installation of the spool bias spring. In addition, the involved personnel have been made aware of the consequences of the incorrect assembly of the control spool bias spring. These actions have been completed.
3211994013 | Hatch 1 | 11/03/1994 | 12/01/1994 | 9412060217 | <strong>False Low Turbine Speed Signal Results In Inoperable High Pressure Coolant Injection System</strong><br /><i>Abstract:&nbsp;</i>On 11/3/94 at 1803 EST, Unit 1 was in the Startup mode with the reactor critical at a power level of 49 CMWT and reactor pressure at 160 psig. At that time, Operations personnel manually tripped the Unit 1 High Pressure Coolant Injection (HPCI) turbine during the performance of procedure 34SV-E41-005-1S, 'HPCI Pump Operability 165 PSIG Test.' The turbine was tripped because HPCI system flow rate indicated upscale (greater than 5000 gpm whereas 4250 gpm was expected) and turbine speed indicated less than 1000 rpm (approximately 2600 rpm was expected). <br /><br /> The cause of this event was failure and/or misadjustment of the HPCI turbine magnetic speed pickup. This resulted in a false low speed signal to the EG-M control box which prevented the control system from maintaining HPCI flow rate at the required value of 4250 gpm. The magnetic speed pickup was replaced and adjusted, and HPCI was functionally tested satisfactorily.
3211994014 | Hatch 1 | 11/19/1994 | 12/16/1994 | 9412230211 | <strong>Main Turbine Shutdown Results in Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 11/19/94 at 0005 EST, Unit 1 was in the Run mode at a power level of 1437 CMWT (59 percent rated thermal power). Load had been reduced from about 99 percent rated thermal power 24 minutes earlier in response to a complete loss of feedwater heating. At 0005 EST, the reactor automatically shut down per design on Turbine Stop Valve closure. The Turbine Stop Valves closed when the turbine shut down on Moisture/ Separator Reheater (MSR) A/B high water level. Reactor vessel water level decreased from its normal value of 36 inches to a minimum of seven inches (151 inches above the top of the active fuel). The Group 2 Primary Containment Isolation System valves automatically closed on low reactor vessel water level per design. The Reactor Feedwater Pumps restored and maintained water level. No Emergency Core Cooling Systems were required to actuate. Reactor pressure was adequately controlled by the Turbine Bypass valves. <br /><br /> The cause of the loss of feedwater heating was a damaged wire in a drain pot level switch combined with out-of-adjustment heater controls. This switch was repaired on 11-19-94. A more restrictive thermal limit was temporarily imposed on the core to insure a similar loss of feedwater heating event will not result in exceeding fuel design limits.<br /><br /> Investigation did not reveal any equipment problems that would have led to a high water level condition in the MSR.
3211994015 | Hatch 1 | 11/27/1994 | 12/19/1994 | 9412280420 | <strong>Cognitive Personnel Error Results in Missed Surveillances on Instruments which Monitor Drywell Leakage</strong><br /><i>Abstract:&nbsp;</i>On 11/28/94 at 0830 EST, Unit 1 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, the surveillance coordinator for the Instrument and Controls (I&C) section reported that two surveillances had been missed. These two surveillances address the drywell equipment drain and floor drain flow instruments and are required by Unit 1 Technical Specifications Table 4.2-10, items 1 and 2. Since the last performance of the surveillances had been on 10/19/94, the latest allowable date for the next performance was 11/27/94. The surveillances were performed on the day the oversight was discovered (11/28/94). <br /><br /> The cause of this event was cognitive personnel error. were missed when computerized surveillance scheduling reports were used incorrectly. <br /><br /> Corrective actions for this event included the following: The surveillances have been satisfactorily completed; the I&C surveillance coordinator has been made aware of the error, and the Outages and Planning Department has made a change in the way surveillance scheduling information is presented to responsible departments. In addition, a letter has been posted in the I&C section surveillance book clarifying scheduling information.
3221994001 | Shoreham | 01/21/1994 | 02/14/1994 | 9402250137 | <strong>Failure to Approve Temporary Procedure Change Within Technical Specification Time Limit</strong><br /><i>Abstract:&nbsp;</i>On 1/21/94, it was determined that a violation of Technical Specification 6.7.3.c occurred when a Temporary Procedure Change (TPC) was not reviewed by the Site Review Committee and not approved by the Resident Manager within 14 days. The TPC was made to Security Plan implementing procedure SP 91X004.01, Shift Operations - Security, on 12/22/93. Use of this procedure, which was not properly approved, is a condition prohibited by technical specifications and is reportable per 10 CFR 50.73 (a) (2) (i) (B). The cause of this event was a failure to follow the administrative procedure on control of station procedures. Corrective actions included approval of the TPC and issuance of the new revision of SP 91X004.01 on an expedited basis, retraining of the appropriate personnel, and initiation of a weekly review of the TPC Log to ensure TPCs are being handled properly. Also, the procedure which controls the handling of TPCs was clarified to specifically highlight that TPCs for security procedures are also meant to be reviewed by the Site Review Committee and approved by the Resident Manager within 14 days under this procedure.
3231994001 | Diablo Canyon 2 | 03/28/1994 | 04/27/1994 | 9405030360 | <strong>Unit Shutdown Due To An Unisolable Reactor Coolant System Leak</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1994, at 0405 PST, with Unit 2 in Mode 3 (Hot Standby) Unit 2 commenced cooling down to cold shutdown as required by Technical Specification (TS) 3.4.6.2 when PG&E identified a unisolatable pressure boundary leak on a 3/4 inch diameter vent line socket weld off an accumulator line connected to the reactor coolant system (RCS) loop 3 cold leg. The TS 3.4.6.2 limiting condition for operation (LCO) was not met. An Unusual Event was declared and an immediate, emergency report was made to the NRC in accordance with the requirements of 10 CFR 50.72(a)(2)(i). At 2341 PST, Unit 2 entered Mode 5 (Cold Shutdown). At 2346 PST, after Unit 2 entered Mode 5 the Unusual Event was terminated. <br /><br /> On March 31, 1994 the cracked socket weld was removed for analysis. A preliminary metallurgical analysis determined that the root cause of the cracked socket weld was most likely a combination of conditions. There was inadequate weld penetration in the weld. Also, there was a lack of fusion. Fatigue appears to have been the primary failure mechanism. The vent line was removed and capped. <br /><br /> If the final metallurgical analysis is significantly different, a supplement to this LER will be submitted to report any differences.
3231994002 | Diablo Canyon 2 | 04/06/1994 | 07/25/1994 | 9408020229 | <strong>Technical Specification 3.0.4 Not Met Following Inadequate Inservice Testing Of RHR Heat Exchanger Check Valves Due to a Programmatic Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1994, Technical Specification (TS) 3.0.4 was not met when Unit 2 entered Mode 4 (Hot Shutdown) without performing a full stroke of residual heat removal (RHR) heat exchanger (HX) discharge check valves 8730A, 8730B, 8742A, and 8742B as required by TS 4.0.5, ASME Section XI, and as defined in Generic Letter (GL) 89-04. <br /><br /> On June 23, 1994, at 1700 PDT, PG&E determined that Section XI testing performed on the check valves noted above did not meet ASME Section XI requirements.<br /><br /> The causes of this event are a deficiency in the comprehensive review of GL 89-04 requirements against the surveillance test procedures (STPs) implementing the Inservice Testing (IST) Program Plan, and personnel error (inattention to detail), by personnel incorporating valves 8742A&B into the program not identifying the potential for bypass flow to invalidate the test results.<br /><br /> Applicable procedures will be revised to ensure that ASME Section XI required flow testing for the RHR HX check valves (8742 and 8730) is adequately performed. As part of the required 10-year update, the IST Program Plan will be rewritten based on the 1987 ASME OM-Code and associated 1988 Addendum to ensure that all applicable requirements are met. As part of this update, the implementing STPs will be evaluated, and revised as necessary, to ensure that IST performance meets the requirements of the ASME OM-Code.
3231994003 | Diablo Canyon 2 | 07/07/1994 | 02/08/1995 | 9502150318 | <strong>Auxiliary Building Ventilation System Outside Design Basis Due to Previous Nonconservative ASTM Testing</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1994, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, based on confirmatory results of a sample taken from the Unit 2 auxiliary building ventilation system (ABVS) charcoal adsorber bank prior to the bank being replaced on June 24, 1994, PG&E determined that the bank would not meet its design basis. The sample analysis was performed in accordance with ASTM D-3803-1989, 'Standard Test Method for Nuclear Grade Activated Carbon.' Another sample, taken from the same Unit 2 ABVS adsorber bank was tested in accordance with ASTM D-3803-1979 and met the Technical Specifications (TS) limits. On July 7, 1994, at 1245 PDT, a one-hour, non-emergency report was made for Unit 2 in accordance with 10 CFR 50.72(b)(1)(ii)(B) because Unit 2 had operated with its adsorber bank incapable of performing its required design function. <br /><br /> PG&E reviewed all of the TS-related charcoal adsorber banks and determined that the only bank not tested to the 1989 standard was the bank for the Unit 2 fuel handling building exhaust Fan E-5. Fan E-5 was declared inoperable pending results of an analysis of a charcoal sample.<br /><br /> The root cause for this event is that the previous testing performed in accordance with ASTM D-3803-1979 was determined to be nonconservative for charcoal banks that have been in service for a substantial period of time. <br /><br /> Since PG&E has adopted and tested to the more conservative 1989 standard, no additional corrective actions are deemed necessary.
3231994004 | Diablo Canyon 2 | 07/26/1994 | 08/19/1994 | 9408250014 | <strong>Partial Phase A Containment Isolations Due to Safeguards Output Driver Card Failure</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1994, at 1411 PDT, 1419 PDT, and 1431 PDT, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, Train B of the solid state protection system (SSPS) for Unit 2 actuated partial Phase A containment isolations. (ESF) actuations. On July 26, 1994, at 1701 PDT, a four-hour, nonemergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The partial containment isolations were caused by the failure of the XA516 safeguards output driver card in Train B of the Unit 2 SSPS. The safeguards output driver card failure was due to the failure of the Z7 integrated circuit chip. <br /><br /> Licensed operators reset the spurious partial Phase A containment isolations. <br /><br /> The XA516 safeguards output driver card in Train B of the Unit 2 SSPS was replaced with a new safeguards output driver card. A review of Diablo Canyon Power Plant maintenance history and industry-wide reports indicated that no similar failure with this type of card has been reported or observed; therefore, PG&E determined this failure to be a random event. Thus, no additional corrective actions were deemed necessary
3231994005 | Diablo Canyon 2 | 08/18/1994 | 09/08/1994 | 9409190156 | <strong>Fuel Handling Building Ventilation System Outside Design Basis Due To Previous Nonconservative ASTM Testing</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1994, at 1140 PDT, with Unit 2 in mode 1 (Power Operation) at 100 percent power, based on results of a sample taken from the Unit 2 fuel handling building (FHB) exhaust fan E-5 adsorber bank, PG&E determined that the bank would not have met its design basis. The sample analysis was performed in accordance with American Society for Testing and Materials (ASTM) D-3803-1989, 'Standard Test Method for Nuclear Grade Activated Carbon.' Another sample, tested in accordance with ASTM D-3803-1979, met the Technical Specifications (TS) limits. On August 18, 1994, at 1220 PDT, a one-hour, non-emergency report was made for Unit 2 in accordance with 10 CFR 50.72(b)(1)(ii)(B) because Unit 2 had operated with its FHB exhaust fan E-5 adsorber bank incapable of performing its required design function. In addition, between June 23 and June 28, 1994, PG&E moved fuel in the Unit 2 FHB which was later determined not to meet TS 3.9.12. <br /><br /> The root cause for this event is that previous testing performed in accordance with ASTM D-3803-1979 was determined to be nonconservative for charcoal banks that have been in service for a substantial period of time. PG&E replaced the Unit 2 FHB exhaust fan E-5 adsorber bank with new charcoal. Since <br /><br /> PG&E has adopted and satisfactorily tested all safety-related charcoal filter beds to the more conservative ASTM D-3803-1989 standard, no additional corrective actions are deemed necessary.
3231994006 | Diablo Canyon 2, Diablo Canyon 1 | 10/01/1994 | 01/20/1995 | 9501310208 | <strong>Steam Generator Feedwater Ring Degradation Due to Flow Accelerated Corrosion</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1994, with Unit 2 in Mode 6 (Refueling), PG&E discovered steam generator feedwater ring degradation in the form of erosion and through-wall holes in the plugs, welds, and base metal at the location of the original feedwater bottom outlet nozzles in steam generator 2-4. <br /><br /> The cause of the holes appears to be flow accelerated corrosion. All of the holes are located downstream of the hot leg reducer in the area of highest velocity, swirl, and turbulent flow characteristics. All of the holes are on the downstream side of the adjacent bottom nozzle plug. <br /><br /> As a corrective action, the through-wall holes discovered near the feedwater ring bottom nozzle plugs of steam generator 2-4 were weld repaired. The feedwater rings for Unit 1 steam generators will be inspected during the next refueling outage. The change in secondary plant chemistry to a higher PH using ethanolamine instead of ammonia should reduce the flow accelerated corrosion rate.
3231994007 | Diablo Canyon 2 | 10/08/1994 | 12/28/1994 | 9501050091 | <strong>Technical Specification 3.7.1.1 Not Met During Main Steam Safety Valve Surveillance Testing Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1994, with Unit 2 in Mode 6 (Refueling) and the core offloaded, Technical Specification (TS) 3.7.1.1 was not met when 12 main steam safety valves (MSSVs) did not meet TS tolerances. All 20 MSSVs were reset using live steam at an offsite facility during the Unit 2 sixth refueling outage and verified to lift within setpoint tolerance.<br /><br /> The root cause of this event is setpoint drift of the MSSVs. <br /><br /> Corrective actions to prevent recurrence include purchase of a new test (lift-assist) device and continued utility participation in the industry investigative efforts. Additionally, a License Amendment Request (LAR) will be initiated to relax the TS setpoint tolerance for the MSSVs.
3231994008 | Diablo Canyon 2 | 10/18/1994 | 11/16/1994 | 9411230237 | <strong>Momentary Loss of Residual Heat Removal Flow Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1994, at 2335 PDT, with Unit 2 in Mode 5 (Cold Shutdown), residual heat removal (RHR) flow was momentarily lost when the only RHR pump shut down while performing diesel generator load shed testing. At 2342 PDT, the Reactor Operator (RO) discovered that RHR pump 2-2 was inadvertently shut down and he immediately returned it to service. Reactor coolant system (RCS) temperature had increased from 960 Fahrenheit (F) to 102 degrees F. On October 19, 1994, at 0140 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(B). <br /><br /> The root causes of this event were determined to be personnel error, cognitive, when a licensed operator verified the wrong RHR pump was running and personnel error, cognitive, when a RO failed to recognize an improper line-up during the prerequisite check of required loads. <br /><br /> Operations personnel were counseled and the department issued new directives for the conduct of Operations personnel during surveillance testing. <br /><br /> The applicable administrative procedure is being revised to require that, during refueling outages where significant outage activities are in progress, a dedicated licensed operator be in the control room with no assigned duties other than monitoring overall plant conditions and that specific component numbers to be added to surveillance procedures prior to use.
3231994009 | Diablo Canyon 2 | 10/20/1994 | 11/18/1994 | 9411250129 | <strong>Unplanned Diesel Generator Start (ESF Actuation) During a Transfer from Auxiliary Power to Standby Power Due to Slow Bus Voltage Decay During a Scheduled Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1994, at 0903 PDT, with Unit 2 in Mode 5 (Cold Shutdown), Diesel Generator (DG) 2-2 started automatically during a scheduled surveillance test due to the first level undervoltage (UV) relay sensing loss of voltage and timing out prior to the successful completion of the transfer from auxiliary power to startup power. The 4160-volt bus was lightly loaded resulting in a slow voltage decay rate that permitted the DG start signal to occur prior to completing the bus transfer and electrically resetting the UV relay. The DG is not expected to start on a successful transfer to startup power. This event constitutes an engineered safety feature actuation. <br /><br /> On October 20, 1994, at 1000 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The root cause of this event is plant design; with a lightly loaded bus, there is the potential for the bus voltage to decay at a slow enough rate such that the first level UV relay will sense a degraded bus voltage, time out, and actuate prior to the successful bus transfer electrically resetting the UV relay. <br /><br /> Surveillance test procedures (STPs) will be revised to include sufficient information to alert operators that an automatic DG start may occur during successful transfers to startup power under lightly loaded bus conditions, or the STP alignment will be modified to prevent an inadvertent DG start.
3231994010 | Diablo Canyon 2 | 10/24/1994 | 11/28/1994 | 9412050109 | <strong>Technical Specification 3.0.4 Not Met When Three of Four Accumulators Were Inoperable Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1994, 1443 PDT, Unit 2 entered Mode 3 (Hot Standby) with reactor coolant system pressure greater than 1000 psig with three of four accumulators inoperable contrary to the requirements of Technical Specification (TS) 3.0.4. On October 28, 1994, at 1604 PDT, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iii)(D).<br /><br /> During the Unit 2 sixth refueling outage, between September 25 and October 1, 1994, a plant clearance was placed in effect to isolate the electrical power (output) from alarm modules to the plant annunciator system in order to install a new annunciator system. However, the clearance removed the power to the alarm module input (power input) such that the effective input impedance at the alarm test connection was decreased. Therefore, six of the eight pressure channels were calibrated with approximately a four percent error. <br /><br /> The root cause of this event was personnel error by utility personnel. Corrective actions to prevent recurrence include provision of an incident summary of the event for review by operating personnel, inclusion of this event in the next instrumentation and controls quarterly training seminar, and revision of the alarm module training session to include lessons learned from this event.
3231994011 | Diablo Canyon 2 | 11/01/1994 | 11/23/1994 | 9412050385 | <strong>Technical Specification 3.3.1 Violation During a Nuclear Instrument Calibration Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1994, at 1233 PST, with Unit 2 in Mode 1 (Power Operation) at 74 percent power, the Limiting Condition for Operation for Technical Specification (TS) 3.3.1, Action 6, was exceeded. During the calibration of power range Nuclear Instrument N-43 per Surveillance Test Procedure I-2D, 'Nuclear Range Incore/Excore Calibration,' overtemperature delta temperature (OTDT) comparators were bypassed. TS 3.3.1, Action 6, requires that an inoperable OTDT channel be placed in the tripped condition within six hours. The channel comparators were placed in the tripped condition two minutes after the six hours allowed by TS 3.3.1, Action 6. <br /><br /> The root cause was determined to be personnel error (cognitive); there was inadequate communication between licensed operators and the Instrument and Controls (I&C) shift control technician.<br /><br /> To prevent future recurrences, an operations incident summary and an I&C maintenance bulletin will be issued stressing responsibility for maintaining awareness of short TS action times. In addition, an Operations and I&C Policy will be issued that establishes a five-hour administrative time limit on use of the Eagle 21 channel bypass features.
3231994012 | Diablo Canyon 2 | 12/19/1994 | 01/18/1995 | 9501250067 | <strong>Manual Reactor Trip Due to Circulating Water Pump Cavitation as a Result of Intake Screen Fouling</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1994, at 1014 PST, with Unit 2 in Mode 1 (Power Operation) at approximately 35 percent power, a manual Unit 2 trip was initiated due to circulating water pump cavitation due to intake screen fouling. The unit was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. On December 19, 1994, at 1202 PST, a four-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(ii). <br /><br /> The event was due to the fouling of the intake circulating water screens during a period of high ocean swells that dislodged ocean plant life from the bottom. <br /><br /> An audible alarm was installed at the intake that activates if a traveling screen drive fails. Possible design and maintenance practice enhancements will be investigated. An annunciator will be installed in the control room to alarm on high condenser differential pressure. Operation Procedure AP-7, 'Partial Loss of Condenser Vacuum and Condenser Fouling,' was revised to include guidance on condenser fouling. The operator rounds sheets were revised to provide guidance on monitoring performance of the intake screen wash system. A computer program was installed that enables control room operators to monitor and trend condenser differential pressures.
3231994013 | Diablo Canyon 2 | 12/09/1994 | 05/08/1995 | 9505250035 | <strong>Containment Spray Pump 4 kV Circuit Breaker Closing Spring Failed to Charge Following Misalignment of Charging Solenoid Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted for information purposes only as described in Item 19 of Supplement 1 to NUREG-1022. <br /><br /> On December 9, 1994, during the performance of Surveillance Test Procedure (STP) M-16HB, 'Operation of SSPS Train B Slave Relays K644 and K645 (Containment Spray Pump 1),' the containment spray pump 2-1 4 kV Magne-Blast circuit breaker closing spring failed to charge. Operators discovered this condition due to the loss of the white potential light indicator at the control room switch and activation of annunciator PK 17-18 (4 kV Bus G DC Control UV/Trouble). <br /><br /> The closing spring failed to charge on demand due to misalignment of the charging solenoid. The root cause of this event was personnel error, non-cognitive; during past maintenance, the charging solenoid was assembled by plant personnel without adequate shims to help maintain plunger alignment within the solenoid. <br /><br /> Maintenance Procedure (MP) E-63.1C, 'Overhaul of 4 kV and 12 kV Magne-Blast Circuit Breakers,' was revised to incorporate the vendor recommendations for shimming prior to discovery of this event. Upon discovery of this event, the revised procedure was used to inspect and adjust/shim as necessary the remaining vital 4 kV breakers that had not been inspected with the revised procedure.
3241994001 | Brunswick 2 | 01/31/1994 | 03/01/1994 | 9403110189 | <strong>Hardened Wetwell Vent Line Isolation Valve Logic Had Not Been Functionally Tested to Ensure Operability.</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1994, Unit 2 was operating at 100% power. Unit 1 was in Operational Condition 4, Cold Shutdown, preparing to enter Operational Condition 2, Startup. The Shift Technical Advisor (STA) observed that the Hardened Wetwell Vent Isolation Valve, Containment Atmospheric Control (CAC) V216, did not have a Primary Containment Isolation System (PCIS) Group 6 Isolation label. The Hardened Wetwell Vent Modification had been completed on both units adding the CAC-V216. Research revealed that the CAC-V216 was not included in the required Technical Specification (TS) surveillance tests. It was also determined that the plant modification acceptance test was not adequate to provide a logic system functional test. <br /><br /> A temporary change was made to Periodic Test (PT) 4.1.1, Reactor Ventilation Exhaust Monitoring System Functional Test, to satisfy the required TS surveillance and was satisfactorily performed on Unit 1 and Unit 2. of TS surveillance requirements for Group 6 isolation valves. The review failed to include an adequate functional test in the plant modification acceptance test. There was also a failure to revise the appropriate Maintenance Surveillance Test (MST) to include the CAC-V216. Corrective actions include adding the CAC-V216 in the appropriate procedures and performing training on functional test requirements when developing plant modifications. The safety significance was minimal. The temporary revision to PT 4.1.1 was performed on both units satisfactorily. The valves operated as designed. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is personnel error.
3241994002 | Brunswick 2 | 01/17/1994 | 02/04/1994 | 9402140216 | <strong>Spurious Isolation of the Reactor Core Isolation Cooling System</strong><br /><i>Abstract:&nbsp;</i>At 2051 on January 17, 1994, Unit 2 was at 100% power. A spurious Division 1 Reactor Core Isolation Cooling (RCIC) isolation signal was received, which closed the inboard steamline isolation valve, 2-E51-F007. No Riley steam leak detection modules were found in alarm, and inspections found no evidence of a steam leak that would have resulted in the isolation signal. The investigation into the source of the inadvertent isolation signal included inspection and calibration of the Riley Scam Module (2-E51-TDS-N601A), but no specific cause has been identified for the isolation signal. The RCIC system was returned to service at 1120 on January 18, 1994. Due to the history of spurious isolations associated with the steam leak detection system the Unit 2 system is scheduled to be replaced during the upcoming refueling outage (B211R1) with digital NUMAC equipment. The Unit 1 system has already been replaced. <br /><br /> This event is of minimal safety significance as the system responded as designed. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is Other (Unknown).
3241994003 | Brunswick 2 | 02/21/1994 | 03/17/1994 | 9403240048 | <strong>Personnel Contamination Monitor Panel Cover Fell Against Relay Causing a Primary Containment Isolation System (PCIS) Group 10 Isolation</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1994 , Unit 2 was operating at approximately 100% power. A maintenance evolution was in progress on a personnel contamination monitor located in the Unit 2 Control Room backpanel area. Maintenance and Health Physics personnel were investigating a possible electrical malfunction in the monitor. In order to access the electronic equipment, a cover was removed and placed against the monitor. During the investigation, the Health Physics technician bumped the cover causing it to fall against a relay on the Division II Core Spray logic panel. The technician notified the Operations Shift Supervisor who was responding to the noise. Inspection of the panel revealed that the relay window was cracked but the relay remained in it's normal state (de-energized). Operations was not aware that the relay had been jarred enough to open two normally closed contacts causing a PCIS Group 10 isolation (Pneumatic Nitrogen System). Approximately 15 minutes later, the isolation of the Pneumatic Nitrogen System resulted in a low seal staging flow alarm on the 2B Reactor Recirculating pump. It was determined that the seal staging valves had closed due to a loss of the Pneumatic Nitrogen System. The isolation was reset and the system was returned to service. Corrective actions included putting hinges on the personnel contamination monitor equipment cabinet cover and reviewing the event with appropriate personnel. The safety significance was minimal. Closure of the normally open contacts in the logic resulted in the Group 10 isolation per design.<br /><br /> The cause classification for this event per the criteria of NUREG-1022 is personnel error.
3241994004 | Brunswick 2 | 03/29/1994 | 06/23/1994 | 9407050069 | <strong>Penetration Leakage In Excess Of Technical Specification Allowable Limit During Local Leak Rate Testing</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1994, the Unit 2 reactor was shutdown in day 4 of refueling outage B211R1. Local leak rate testing (LLRT) of the main steam isolation valves (MSIVs) had been performed. The results of the LLRT indicated that the leakage on main steam line (MSL) A inboard and outboard isolation valves was approximately 135 and 38.6 standard cubic feet per hour (scfh) respectively, exceeding the technical specification limit of 11.5 scfh. The cause of the LLRT failures is attributed to indications identified on the valve seats and discs which resulted from foreign material intrusion. Additionally, a contributing factor to the leakage of the inboard isolation valve is attributed to actuator-to-valve misalignment. The valves' seat and disc surfaces have been repaired to ensure proper sealing surfaces and modified junk rings installed to prevent misalignment problems. The inboard valve actuator guide tube assembly was disassembled and remachined to improve actuator alignment.<br /><br /> Following valve maintenance the valves successfully passed LLRTs. The safety significance of this event is considered minimal. Previous events involving MSIVs not meeting technical specification leakage requirements have been reported in LERs 1-88-025, 2-91-019, and 2-92-10.
3241994005 | Brunswick 2 | 04/04/1994 | 04/28/1994 | 9405030236 | <strong>Isolation of the Primary Containment Isolation System Containment Atmospheric Monitoring Valves While Hanging an Equipment Clearance.</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1994, Unit 2 was in Refuel. At 0522 hours, a clearance was placed on the Containment Atmospheric Monitoring (CAM) valve isolation logic in preparation for a scheduled modification. At 0600 hours, the Shift Supervisor noticed that two Primary Containment Isolation System (PCIS) Group 6 Reactor Instrument Penetration (RIP) valves had dual open/closed (red/green) indications. These valves typically display dual valve position when an isolation signal has been received. A detailed Reactor Turbine Gauge Board (RTGB) walkdown revealed that the CAM valves on RTGB Panel XU-51 had closed (the valve switches were still in the open position). A review of the recent evolutions determined that the clearance evolution at 0522 had caused the Group 6 CAM valves to reposition. The cause of the event was personnel error. The Senior Reactor Operator (SRO) preparing the clearance improperly diagnosed the logic and failed to recognize that the associated PCIS relay operation would cause both division I and II CAM valves to isolate. Corrective actions include counseling the involved SRO and reviewing the event with shift Operations. isolation logic operated as designed. The CAM system was previously removed from service for the outage. The cause classification for this event per the criteria of NUREG-1022 is personnel error.
3241994006 | Brunswick 2 | 04/21/1994 | 05/23/1994 | 9405260229 | <strong>Penetration Leakage In Excess Of Technical Specification Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1994, during the Unit 2 B211R1 refuel outage, local leak rate testing (LLRT) of the Reactor Water Cleanup (RWCU) system suction line inboard and outboard isolation valves had been performed. Although the initial LLRT of the valves obtained acceptable results, subsequent testing indicated that the valves would not pressurize. Consequently, the overall test was considered a failure in that the limits established in the Technical Specification for allowable primary containment leakage were exceeded. <br /><br /> The RWCU suction line isolation valves are double-disc gate valves manufactured by Anchor Darling. The failure of the valves to minimize leakage within the allowable limits is attributed to non-uniform contact of the valve upper and lower wedges. This failure mechanism was previously documented in LER 1-92-023. The valve wedges were replaced and two post maintenance leakage tests performed. Both post maintenance leakage tests on each valve verified that leakage rates were well within the allowable limits. <br /><br /> The failure of both of the RWCU suction line isolation valves represents a potential loss of the primary containment isolation capability for that penetration had a design basis accident occurred. Previous similar events were reported in LERs 1-91-016 and 1-92-023. <br /><br /> The cause classification of this event per the criteria of NUREG-1022 is B, failures reasonably attributed to the manufacture of a component.
3241994007 | Brunswick 2 | 03/18/1994 | 06/02/1994 | 9406090235 | <strong>Evaluation of Snubber Operability Not Performed Within Technical Specification Required Time Limit</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1994, while Unit 2 was operating at rated power, craft personnel involved with the removal of a grout pad located under the baseplate of an Residual Heat Removal system snubber support identified that the snubber support anchor bolts were degraded and required repair. The involved personnel failed to take the necessary actions for ensuring an operability review of the degraded condition was performed in a timely manner. Consequently, the repair and evaluation of the inoperable snubber did not occur within the time constraints established by the Technical Specification. The failure to take prompt and effective actions is attributed to a lack of understanding of the significance of the degraded condition and planner training inadequacies. Training of craft and work planning personnel are being performed to prevent recurrence. An evaluation of RHR system operability determined that, although the degraded anchor bolts rendered the snubber inoperable, the affected RHR line remained operable. Consequently, this event has minimal safety significance. No similar events as reported in previous LERs were identified. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is A, personnel error.
3241994008 | Brunswick 2, Brunswick 1 | 05/21/1994 | 06/09/1994 | 9406270283 | <strong>Dispatcher Switching Evolution Results in Loss of Offsite Power to Unit 2</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1994, Unit 2 was in a Refuel Outage. The Unit 2 Startup Auxiliary Transformer (SAT) was being supplied from Switchyard Bus 2B. At 1442 hours, the system dispatcher notified the Brunswick Control Room that maintenance had been completed on the Whiteville 230 kV line and that the circuit breakers would be restored to service. Testing of the Whiteville breakers would involve opening one breaker on Switchyard bus 2B and two breakers on Switchyard Bus 2A. At 1509 hours, the dispatcher opened the one breaker on Bus 2B. He then opened the remaining two breakers feeding bus 2B (the two breakers feeding Bus 2A should have been opened). Opening the remaining two breakers to Bus 2B caused a Loss of Offsite Power to Unit 2. All four Diesel Generators (DGs) started and DG 3 and 4 auto loaded to their respective Emergency Buses. required. The Reactor Building Ventilation inboard dampers failed to automatically isolate due to a failed relay. The dampers were manually closed from the Control Room. All other systems operated as designed. The cause of the event was personnel error. Corrective actions include requiring dual verification for switching evolutions at nuclear power plants and reviewing the event with appropriate operations personnel. The safety significance was minimal. All DGs auto started and DGs 3 and 4 loaded to their respective Emergency Buses. The cause classification for this event per the criteria of NUREG-1022 is personnel error.
3241994009 | Brunswick 2 | 06/19/1994 | 07/07/1994 | 9407140188 | <strong>Engineered Safety Feature Actuation During Unauthorized Post Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1994, Unit 2 was in Cold Shutdown with Reactor Leak Testing in progress. Maintenance activities were in progress to replace a Unit Two Reactor Core Isolation Cooling (RCIC) temperature element. Maintenance personnel erroneously proceeded with post maintenance testing, applying heat to the new temperature element. However, the temperature monitor had been taken out of bypass prior to the element being heated. This resulted in a Primary Containment Isolation System Group 5 Isolation and the closure of the RCIC Inboard Steam Isolation valve, 2-E51-F007. The isolation signal was verified to be invalid and the valve was left closed to support plant conditions. The cause of the event is personnel error. Corrective actions include disciplinary action of the involved maintenance personnel and reviewing the event with appropriate maintenance personnel. <br /><br /> The safety significance was minimal. All safety systems functioned as designed.<br /><br /> The cause classification for this event per the criteria of NUREG-1022 is personnel error.
3251994001 | Brunswick 1 | 01/11/1994 | 02/07/1994 | 9402180167 | <strong>Group 8 Isolation During Restoration from Maintenance Surveillance Test (MST)</strong><br /><i>Abstract:&nbsp;</i>Unit 1 was in Refuel with approximately 421 out of 560 fuel bundles loaded into the core. The Residual Heat Removal (RHR) System 'A' Loop was in Shutdown Cooling. On January 11, 1994, Maintenance surveillance Test (MST) 1MST-RHR27M, RHR Shutdown Cooling Reactor Pressure Instrument Channel Calibration, was scheduled to be performed. The MST allowed the Inboard and Outboard Shutdown Cooling Isolation Valves (E11-F008 & E11-F009) to be placed under clearance open during the test to prevent a Group 8 Primary Containment Isolation System Isolation and the loss of shutdown cooling. The MST was completed satisfactorily and Operations proceeded to remove the clearances from the E11-F008 and F009. When the breaker for the E11-F009 was closed, the Group 8 isolation was received, the valve closed, and the 1A RHR Pump tripped. The Reactor Operator (RO) and the Senior Reactor Operator (SRO) observed the E11-F009 stroking closed. After verifying vessel level an unsuccessful attempt was made to reopen the E11-F009 using the control switch. The RO then depressed the group isolation reset push buttons and successfully opened the E11-F009. Shutdown cooling was re-established in approximately 8 minutes. The cause of the event was an inadequate technical review when revising the MST. Through revision 7 of the MST jumpers were installed to bypass the trip logic. Revision 8 removed the jumpers and did not address the need for an end of test reset to prevent the Group 8 isolation. Corrective actions include revising the MST to include steps to reset the isolation logic and review other MST's that test isolation circuitry to verify procedure adequacy. The safety significance was minimal. unit i had been shutdown since April 21, 1992 and there was no increase in coolant temperature during the event. Shutdown cooling was re-established in approximately 8 minutes. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is defective procedure.
3251994002 | Brunswick 1, Brunswick 2 | 01/17/1994 | 02/11/1994 | 9402170135 | <strong>Control Building Emergency Air Filtration trains rendered inoperable by frozen/plugged instrument air dryer line.</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1994, Unit 1 was in a refueling outage and Unit 2 was at 100% power. At 0312, the common Control Building Heating Ventilation and Air Conditioning (CBHVAC) air conditioners tripped, followed by the CBHVAC Fans at 0330. By 0350, it was determined that the refrigerated instrument air dryer for the Control Building ventilation instrument air system was blocked. In this condition, successful operation of the CBHVAC system could not be assured under all conditions and the Control Building Emergency Air Filtration trains were inoperable. <br /><br /> Checks of air filters downstream of the refrigerated instrument air dryer found no contamination with foreign material, but the refrigerant charge pressure of the air dryer was low. The result of the low refrigerant pressure was internal dryer temperatures low enough to freeze the moisture being condensed in the instrument air line, thereby plugging the line. At 0430, the air dryer was bypassed and the Control Building ventilation system restarted. <br /><br /> A Preventive Maintenance route to check/maintain refrigerant pressure of the CBHVAC Instrument Air Dryer within the vendor recommended pressure range will be established. <br /><br /> The safety significance of this event is minimal as the passive failure did not occur during a challenge to Control Building Habitability. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is Management/Quality Assurance Deficiency.
3251994003 | Brunswick 1, Brunswick 2 | 06/03/1994 | 06/16/1994 | 9406210220 | <strong>Unplanned ESF Actuation Resulting From De-Energizing The Main Stack Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1994, Unit 1 was operating at 100% power and Unit 2 was defueled. Repair activities on the Main Stack Wide Range Gas Monitor (WRGM) sample pump inadvertently de-energized the monitor. The loss of power resulted in unplanned actuations with Unit 1 receiving an isolation of the Containment Atmospheric Control (CAC) and Secondary Containment Isolation systems including a Standby Gas Treatment System (SBGTS) initiation. The impact on Unit 2 was limited to a Secondary Containment isolation as the SBGTS had been removed from service and the CAC valves were being maintained closed. The actuations were verified to be invalid and the affected systems were realigned to support plant conditions. Personnel error is the primary cause of the Main Stack WRGM loss of power with the following areas identified as weaknesses: (1) attention to the work control process by maintenance personnel, (2) communications between maintenance and operations personnel, and (3) operation of plant equipment by maintenance personnel without a clear understanding of the resulting impact. Secondary causes of the event include a deficiency in the detail of the work planning, inadequate turnover of information between maintenance crews, and the lack of consistent site standards governing the manipulation of plant components. <br /><br /> This event has minimal safety significance in that the affected systems functioned as required on the invalid signal from the Main Stack WRGM. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is personnel error.
3251994004 | Brunswick 1 | 01/26/1994 | 02/21/1994 | 9403040311 | <strong>Loss of RPS Bus A Power and Associated ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>At 1142 on January 26, 1994, with Unit 1 in Mode 4 (COLD SHUTDOWN), an operator error caused loss of power to Reactor Protection System (RPS) Bus A and associated Engineered Safety Feature (ESF) actuations. During performance of 1MST-DG11R1, 'DG-1 Loading Test,' 4160v Emergency Bus 1 was being powered from Diesel Generator #1 (DG-1). Preparations were being made to parallel Bus E1 with offsite power to restore the normal electrical lineup in accordance with 0-OP-50.1, 'Diesel Generator Emergency Power System Operating Procedure.' While adjusting DG-1 speed, the operator erroneously lowered DG-1 frequency rather than raising the frequency causing Electrical Protection Assembly (EPA) breaker #2 to trip on under-frequency and a loss of RPS Bus A power. The loss of power resulted in the following ESF actuations:<br /><br /> 1. Closure of 1-B21-F016, Main Steam Line Drain Inboard Isolation Valve. <br /> 2. Closure of 1-G31-F001, Reactor Water Cleanup Inboard Isolation Valve.<br /> 3. Isolation of Reactor Building HVAC. <br /><br /> The event is of minimal safety significance. Plant systems responded as designed. RPS A Bus power was restored at 1208. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is Personnel Error.
3251994005 | Brunswick 1, Brunswick 2 | 02/17/1994 | 09/15/1994 | 9409290145 | <strong>Potential Use of Less-Conservative Pressure-Temperature Limits Curves</strong><br /><i>Abstract:&nbsp;</i>The original report was issued to provide the NRC staff with information relative to apparently switched Technical Specification Pressure- Temperature Limits (PTL) Curves for Brunswick Units 1 and 2 (Technical Specification Figures 3.4.G.1-1, 3.4.6.1-2, and 3.4.6.1-3b), resulting in the potential use of less-conservative curves on Unit 1 during past heat-up/cooldown evolutions. The issue was raised following removal of a surveillance capsule from the Unit 1 reactor vessel during the recently completed Unit 1 refuel outage. Supplement 1 to this report updates the switched PTL curve issue and provides a 30-day report on one event discovered where Unit 1 was operated outside of the Technical Specifications for the PTL curves (Technical Specification 3.4.6.1). This 1992 Unit 1 event is reportable under 10 CFR 50.73(a)(2)(i). inadequate procedural guidance provided to the control room operators with respect to the proper parameters to be monitored for PTL curve compliance. Allowable stress values, fatigue, and fracture toughness margins required by 10 CFR 50 Appendix G were evaluated as acceptable for the 1992 Unit 1 event; therefore, continued operation of the unit is justified. The NUREG-1022 cause code for this event is defective procedures. Information in the original LER is not being revised. Supplemental information updating the switched PTL curve issue and the 30-day report where Unit 1 operated outside of the Technical Specifications for the PTL curves is presented under the Supplement 1 Information section. Supplement 2 provides information regarding a corrective action committed in Supplement 1.
3251994006 | Brunswick 1, Brunswick 2 | 04/12/1994 | 05/05/1994 | 9405120047 | <strong>Reactor Manual Control System Design Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1994, Unit 1 was operating at 100% power. During a previous training session on the Reactor Manual Control System (RMCS) a discrepancy had been noted on the inputs for the Average Power Range Monitors (APRMs) and the Intermediate Range Monitors (IRMs). The schematic diagrams associated with the RMCS Continuous Rod Withdrawal Block did not agree with the conventions used in other portions of the system or with the Reactor Protection System (RPS) inputs. A procedure change request was submitted to the operations support staff requesting further investigation. Subsequent investigations revealed that the schematic drawing was correct and the design described in the Final Safety Analysis Report and the Design Base Documents was not consistent with actual plant configuration. The discrepancy exists in the original design of the system and is applicable to both Units. Due to the discrepancy, APRMs have been bypassed such that on at least three previous occasions Technical Specification Table 3.3.4-1 requirements for minimum operability of APRM channel inputs to the RMCS Continuous Rod Withdrawal Block were not met. The cause of the event was the failure to follow standard conventions for the RMCS APRM and IRM groupings. Corrective actions include issuing a Standing Instruction informing operations of the discrepancy and modifying the applicable inputs to ensure consistency between RMCS and RPS groupings. not considered to be a safety system. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is design, manufacturing, construction/installation.
3251994007 | Brunswick 1 | 04/18/1994 | 05/13/1994 | 9405170162 | <strong>Reactor Core Isolation Cooling System Isolations Occur During Surveillances Test Equipment Connection</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1994, Unit 1 was at 100% power and a series of Reactor Core Isolation Cooling (RCIC) System surveillances were being performed. <br /><br /> At 1111, during RCIC Turbine Exhaust High Pressure Instrument Channel Calibration, a meter lead inadvertently touched an adjacent terminal resulting in the RCIC Inboard Steam Supply Isolation Valve closure. It should be noted that the meter leads had already been correctly landed, but were intentionally lifted from the terminal as a common practice which called for the meter to be disconnected prior to changing the meter function (to Ohms). Provisions allowing the common practice had not been incorporated into the surveillance and therefore its use was not consistent with the verbatim procedural compliance required for surveillances. The RCIC System was returned to standby at 1258. <br /><br /> At 1718, the RCIC Steam Line Low Pressure Instrument Channel Calibration, resulted in the inadvertent closure of the RCIC Outboard Steam Supply Isolation Valve. A technician became entangled in the meter leads and inadvertently pulled the leads loose at the meter. He mistakenly assumed the panel lead end had come loose and went on to connect the loose end in the panel per the next step of the procedure. This configuration provided a circuit which activated the isolation logic. The investigation linked this event to a procedural compliance concern as the surveillance required using two meters. The RCIC system was returned to standby at 2151. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is Personal Error.
3251994008 | Brunswick 1 | 04/22/1994 | 05/19/1994 | 9405240065 | <strong>Unplanned Engineered Safety Feature (ESF) Actuation During Valve Manipulation</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1994, Unit 1 was operating at 100% power. The Reactor Building Ventilation and Reactor Water Cleanup systems were in service. A revision had been made to Operating Procedure (OP-01), Nuclear Boiler operating Procedure which included administrative changes to the valve line-up section. During the revision, the rack isolation valve for spare line B21-702 was moved to page 46 of the new revision. The Unit Senior Reactor Operator (SRO) interpreted this change as a new addition because the valve did not appear on page 46 of the previous revision. The SRO dispatched an Auxiliary Operator (AO) to Instrument Rack H21-P004-001 to verify the valve position (closed). While the AO was verifying the valve position a pressure perturbation occurred resulting in a sensed Reactor Low Level II condition (118 inches sensed at B21-LT-N024A-1 and B-1). A Division I Reactor Water Cleanup isolation, a secondary containment isolation, and an initiation of the Standby Gas Train occurred. Operations verified that the conditions for the isolations did not exist, reset the isolations, and returned the affected systems to normal lineup. The cause of the event was the pressure equalization across the valve when the operator attempted to verify the position, causing the perturbation. Corrective actions include developing a process to provide recommendations to on-shift operators concerning revised valve lineups. The safety significance was minimal, all systems operated as designed. The cause classification for this event per the criteria of NUREG-1022 is Other. (Process Problem)
3251994009 | Brunswick 1 | 05/13/1994 | 03/09/1995 | 9503160277 | <strong>High Pressure Coolant Injection System Cooling Water Valve Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 1994, unit 1 was operating at 100 percent power. Following completion of a partial performance of the HPCI System Operability Test, an Auxiliary Operator noted that the position indication light for valve 1-E41-F059, 'HPCI cooling water supply valve' was not illuminated. Expecting a blown bulb, the operator proceeded with replacing the bulb. Upon removal of the green lamp lens, but prior to removal of the bulb, the glass portion of the bulb blew out of the socket while the metal portion remained in the socket. This resulted in two blown control power fuses, rendering 'HPCI cooling water supply valve' 1-E41-F059 inoperable. A loss of the cooling water valve removes the ability to cool the HPCI System lubrication oil, thus rendering the HPCI System inoperable. The bulb, bulb socket, and fuses were replaced, valve 1-E41-F059 was tested, and the system was returned to service. The system was out of service for 2 hours, 39 minutes, which is within the allowable out-of-service time of 14 days permitted by Technical Specification 3.5.1. During this time, the Automatic Depressurization System (ADS), Reactor Core Isolation Cooling (RCIC) System, Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) System, and the Core Spray (CS) System were operable. As such, the safety significance of this event was minimal. To prevent the recurrence of this event the incandescent lights installed on selected motor control center compartments have been replaced to the extent possible, with light-emitting diodes. The cause classification for this event per the criteria of NUREG-1022 is 'Other'.
3251994010 | Brunswick 1, Brunswick 2 | 06/20/1994 | 07/07/1994 | ML09152053 | <strong>Inadvertent Loss of Power To The Main Stack Radiation Monitor Results In Dual Unit Unplanned ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1994, at approximately 0830 hours, while Unit 1 was operating at 100% power and Unit 2 was in cold shutdown, both units received an isolation of the Containment Atmospheric Control system, isolation of Secondary Containment, and initiation of the Standby Gas Treatment system. The Main Stack Radiation Monitor, which is common to both units, was the source of the actuation signals. Personnel painting in the area of the radiation monitor power supply disconnect switch inadvertently tripped the disconnect switch and consequently de-energized the power supply to the monitor. The cause of this event is attributed to personnel error. Appropriate personnel will receive training on the lessons learned from this event. <br /><br /> This event is of minimal safety significance in that the affected systems functioned as designed and abnormal changes to radiological effluents did not occur during the event. Similar events involving loss of power to the Main Stack Radiation monitor have been previously reported in LERs 1- 92-028 and 1-94-03. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is personnel error.
3251994011 | Brunswick 1 | 08/20/1994 | 09/09/1994 | 9409190240 | <strong>Primary Containment Isolation System Control Logic Relay Failure Results In Unplanned ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1994, at approximately 0008 hours, while Unit 1 was operating at 100% power, an unplanned isolation of the Containment Atmospheric Control system and Drywell Floor and Equipment Drain system isolation valves occurred. At 0047 hours, after verifying that the isolation was due to an invalid isolation signal and the appropriate isolation valves had closed, the isolation signals were reset and the affected systems were restored to service to support plant operation. Further investigation into the cause of the event determined that a primary containment isolation system logic control relay had experienced an intermittent and indeterminate failure. The relay is a normally energized, General Electric model CR120A, 115 vac relay. The suspected relay has been replaced. This event is of minimal safety significance in that the involved systems failed to the condition required to fulfill their safety function. Previous CR-120 relay failures which resulted in the unplanned isolation of Engineered Safety Feature systems have been reported in LERs 2-89-020, 1-90-023, 1-90-029, and 1-91-028.<br /><br /> The cause classification for this event per the criteria of NUREG-1022 is Other.
3251994012 | Brunswick 1 | 09/22/1994 | 11/17/1994 | 9411220254 | <strong>HPCI Declared Inoperable Due to Failure of the Lube Oil Cooling Water Supply Valve Control Power Fuse</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1994, at approximately 0855 hours, while Units 1 and 2 were operating at rated power, the Unit 1 High Pressure Coolant Injection (HPCI) system lube oil cooling water supply valve, 1-E41-F059, control power fuse failed. Prior to this event, workers moving a material transport cart inadvertently struck the 1-E41-F059 Motor Control Center (MCC) cubicle. At 0905 hours HPCI was declared inoperable due to the loss of power to the 1-E41-F059. At the time of the event the 1B RHR pump was inoperable due to planned maintenance. Consequently, the requirements of Technical Specification 3.5.1, High Pressure Coolant Injection System Limiting Condition For Operation could not be satisfied and the requirements of Technical Specification 3.0.3 were invoked. <br /><br /> The cause of this event is attributed to inadequate self-checking and job scope walkdown. The involved personnel have been counselled and the appropriate plant personnel have been briefed on the lessons learned from this event. Similar events have been previously reported in LERs 1-94-009 and 2-94-003. This event is of minimal safety significance in that the Automatic Depressurization System, the Core Spray System, and Low Pressure Coolant Injection (LPCI) System with the exception of the 1B RHR pump were operable during the time the HPCI System was declared inoperable. Although the 1B RHR pump had been removed from service, the pump was prepared for return to service if necessary. <br /><br /> The cause classification for this event per the criteria of NUREG-1022 is A, personnel error. Supplement 01 to this LER corrects terms used to identify the components involved in the event.
3251994013 | Brunswick 1, Brunswick 2 | 10/23/1994 | 11/18/1994 | 9411300400 | <strong>Control Building Emergency Air Filtration Isolation Due to Chlorine Gas Release Following Chlorinator Isolation Due to Evaporator Low Water Level</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1994, Units 1 and 2 were operating at 100% power. Chlorination had been placed in service to the Unit 1 Circulating Water system at 0610 hours. At 0715 hours, the CHLORINE BLDG HI CHLORINE annunciator sounded in the Main Control Room, and an operator was dispatched to the Chlorine Building to investigate. Investigation revealed that a chlorinator isolation had occurred as a result of a low water level condition in the associated chlorine evaporator tank. At 0724 hours, the Control Building Emergency Air Filtration System isolated due to high chlorine levels at the Chlorine Loading Area. The plant declared an Unusual Event at 0740 hours. After surveying the area and determining the hazard no longer existed, the unusual Event was terminated at 0926 hours. The control building ventilation system was returned to normal operation by 0931 hours. This event resulted from inadequate verification of chlorine evaporator water level while placing the chlorination system in service at 0610 hours. Insufficient chlorine evaporator water level resulted in an evaporator low water temperature condition which caused an automatic isolation of the associated chlorinator as designed. Pressure in the isolated chlorinator increased due to evaporation at ambient temperatures until the installed pressure relief assembly actuated, resulting in the release of chlorine gas. This event is of minimal safety significance in that all systems and components operated as designed. Corrective actions included procedure revisions to clarify water level checks, training on the system operating characteristics that resulted in the release, and coaching the involved operator who placed the system in service. The causes of this event per the criteria of NUREG-1022 are personnel error and procedure inadequacy.
3251994014 | Brunswick 1 | 11/01/1994 | 12/09/1994 | 9412150063 | <strong>Unit 1 Reactor Building Radioactive Effluent Sample Analysis Not Performed Within Technical Specification Time Constraints</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1994, Units 1 and 2 were operating at 100% power. At approximately 0530 hours, Environmental and Chemistry (E&C) technicians completed the replacement and analysis of the Unit 1 Reactor Building effluent radioactive gas sample filters which had been in service from October 25, 1994 through November 1, 1994. During a routine review of the gaseous effluent report for the week of October 25, 1994, the Unit 1 Reactor Building effluent sample was determined to be atypical in that a less than detectable sample activity for the week was indicated. A subsequent investigation on November 9, 1994, revealed that the samples collected on November 1, 1994, had been misplaced and not analyzed within the 48 hours following removal of the filters as required by Technical Specification 4.11.2.1.2 (Table 4.11.2-1.B, footnote f). The misplaced samples were located and analyzed on November 9, 1994. The event resulted from an isolated case of personnel error. involved personnel, briefing of appropriate E&C personnel on the lessons learned from the event, installation of additional filter apparatus labels, correction of the effluent data and related dose assessment, and enhancement to the sampling data review and assessment process. The safety significance of this event is considered minimal in that an assessment of the ensuing analysis data indicates that site effluents were well within the dose limits prescribed by the Technical Specification during the period of October 25 through November 1, 1994. Previous similar events involving missed Radiological Effluent Technical Specification surveillance requirements due to personnel error were reported in LERs 1-92-007 and 2-93-001. The cause of this event per the criteria of NUREG-1022 is personnel error.
3251994015 | Brunswick 1 | 12/15/1994 | 01/12/1995 | 9501260045 | <strong>Unplanned Engineered Safety Feature Actuation During Performance of a Maintenance Surveillance Test.</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1994, Unit 1 was operating at 100% power. A Maintenance Surveillance Test (MST), 1MST-RHR21M, High Drywell Pressure calibration and Channel Functional Test, was in progress. At 1015 hours, the High Pressure Coolant Injection System (HPCI) received an auto initiation signal. The initiation sequence started as expected. The HPCI Injection Valve, E41-F006, did not receive an open signal and there was no injection into the reactor vessel. The Reactor Operator observed the HPCI start and secured the system after verifying there was no valid initiation signal. Investigation revealed that the meter leads were correctly placed per the test procedure but the DC circuit polarity resulted in a downscale reading. This required changing the meter polarity switch to the other DC position (+ or -). This meter model has a 'tone' position on the same switch to aid in resistance functions and it is believed that the technician inadvertently went to the 'tone' position, causing the meter to act as a jumper, completing the HPCI initiation logic. After the initial investigation, the HPCI system was returned to operable and placed in standby at 1158. Corrective actions include limiting the use of Model 260 meters and specifying a Digital Multimeter (Fluke Model 45) to he used for relay contact checks in MSTs. The safety significance was minimal. The HPCI system functioned properly and although declared inoperable, remained available throughout the event. The cause classification for this event per the criteria of NUREG-1022 is Personnel Error.
3271994001 | Sequoyah 1 | 12/21/1993 | 04/13/1994 | 9404180316 | <strong>Formation of Gas in the Reactor Head and the Steam Generator (S/G) Tubes</strong><br /><i>Abstract:&nbsp;</i>This event is being reported as a voluntary LER to inform the NRC staff of a condition involving the accumulation of gas in the reactor head and the S/G tubes during low reactor coolant system (RCS) pressure operation. On December 21, 1993, with Unit 1 in Mode 5 in a refueling outage, Operations personnel wrote a problem evaluation report concerning the potential that gas may have formed in the reactor head and the S/G tubes. Operations based this hypothesis on the amount of water that had to be added and then subsequently let down from the RCS while performing the containment integrated leak-rate test. Technical Support personnel have evaluated this condition and concluded that at low RCS pressure (the RCS was at atmospheric pressure), nitrogen is coming out of solution in the reactor head and the S/G tubes. Nitrogen is used as a cover gas on the volume control tank (VCT). The nitrogen pressure in the VCT was approximately 20 pounds per square inch gauge. Therefore, gas was being transported from the VCT to the RCS via the charging system. An additional evaluation has determined that, as the result of the gas accumulation, reactor vessel water level was reduced to the top of the RCS hot legs. The pressurizer level during this event remained steady at approximately 60 percent. The root cause of this event was insufficient knowledge and the lack of a questioning attitude concerning management's evaluation of off-normal plant conditions and the solubility of nitrogen in the RCS. SQN management will review the lessons learned from this event with appropriate site personnel.
3271994002 | Sequoyah 1 | 02/23/1994 | 03/25/1994 | 9403290253 | <strong>Engineered Safety Feature Actuation Resulting From a Loss of Nonessential Air Supply</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1994, at 0415 Eastern standard time, the Unit 1 nonessential control-air header was inadvertently isolated, causing several containment isolation valves to shut, which resulted in an engineered safety feature actuation. The event occurred during the restoration portion of the performance of a surveillance instruction. Testing personnel were realigning the system valves to their normal position. However, the sequence in which this was conducted isolated the nonessential control-air header. Operations personnel quickly determined the cause of the event and restored the system air pressure. The root cause of this event was inadequate guidance on how to sequentially perform the required operations on components contained within a table in an instruction or procedure. A training letter/standing order will be issued describing the proper sequence for manipulating the valves contained within a table in the performance section of an instruction or procedure.
3271994003 | Sequoyah 1, Sequoyah 2 | 03/10/1994 | 08/15/1994 | 9408190096 | <strong>Two Inadequate Surveillance Instructions Resulted in a Failure to Comply With Technical Specifications (TSs)</strong><br /><i>Abstract:&nbsp;</i>On March 10 and 14, 1994, with Unit 1 in Mode 5 at approximately 120 degrees Fahrenheit and 50 pounds per square inch gauge and Unit 2 in Mode 1 at approximately 100 percent thermal power, errors were identified in two separate surveillance instructions (SIs). The errors resulted in the failure to comply with two TS surveillance requirements. Both of the errors were associated with the Operations department SIs. The cause of the errors were inadequate procedure-revision reviews. The corrective action for these conditions included a 100 percent review of the 105 Operations department SIs to ensure that each technical specification surveillance was properly referenced in instructions. The review indicated that the technical specification surveillance requirements were being implemented by procedures.
3271994004 | Sequoyah 1 | 03/14/1994 | 04/12/1994 | 9404190001 | <strong>Inadvertent Feedwater Isolation While Steam Generators Were in Wet Lay-up</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1994, at 1813 Eastern standard time with Unit 1 in cold shutdown (Mode 5), an inadvertent feedwater isolation (FWI) occurred because of an indicated high-high Loop 1 steam generator (S/G) level. The FWI occurred during the drain-down of the S/G for the removal of water containing lay-up chemicals. The FWI was initiated as a result of two out of three transmitters indicating a S/G level above the high-high setpoint. The actual S/G level was below the FWI setpoint. The Loop 1 S/G was drained, and the FWI signal was reset. The cause of the FWI was an inadequate procedure for wet lay-up of the S/G. Applicable procedures will be revised to provide operators with S/G level channel-operability guidance during wet lay-up conditions.
3271994005 | Sequoyah 1 | 04/03/1994 | 05/03/1994 | 9405100139 | <strong>Inadvertent Feedwater Isolations (FWIs) During Preparation for Unit Start-Up</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1994, at 1024 and 1840 Eastern daylight time (EDT) and on April 9, 1994, at 0239 EDT with Unit 1 in hot standby (Mode 3), inadvertent FWIs occurred. The first event occurred during troubleshooting activities with the reactor trip breaker (RTB) auxiliary contacts as a result of personnel's failure to follow the work instruction. The involved individuals were counseled on the requirements to follow work document instruction steps. The second event occurred upon closure of the RTBs in the preparation for rod-drop testing. The subsequent testing and inspection of the breaker did not confirm the root cause of the spurious FWI. Test instrumentation data indicated that the signal may have been created by voltage spikes during movement of the auxiliary switch rotary contacts as the breaker traveled to the closed position. The third event occurred during observation of the RTB after one of the two RTBs failed to close. While explaining an observed difference between two breaker-locking levers, an individual inadvertently moved the locking lever on the closed breaker. This resulted in the breaker traveling to the open position and the initiation of an FWI. The cause of the event was personnel error. The appropriate disciplinary action was taken with the involved individual. Both RTBs were replaced. The replacement breakers were inspected, tested, and placed in service.
3271994006 | Sequoyah 1, Sequoyah 2 | 04/15/1994 | 05/10/1994 | 9405180165 | <strong>Control Room Emergency Ventilation System Inoperable Because of Closure of Tornado Dampers</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1994, at 1240 Eastern daylight time (EDT), with Unit 1 in Mode 2 and Unit 2 at 100 percent power, and on April 27, 1994, at 1500 EDT, with Unit 1 at 48 percent power and Unit 2 at 100 percent power, Limiting Conditions for Operation (LCOs) 3.0.3 and 3.7.7 were entered. Both trains of the control room emergency ventilation system (CREVs) were declared inoperable following closure of the tornado dampers that isolate the fresh air intake, for pressurization of the main control room, to the CREVs. The dampers were closed in accordance with plant procedures as a result of each of the tornado warnings and sightings of a tornado in Hamilton County near SQN. After the tornado warnings were downgraded, both trains of the CREVs were subsequently returned to operable status.
3271994007 | Sequoyah 1 | 04/22/1994 | 05/20/1994 | 9405270179 | <strong>Missed Surveillance Associated With the Monitoring of the Reactor Head Flange Leakoff System</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1994, at 0043 Eastern daylight time, with Unit 1 in Mode 1 at approximately 30 percent rated thermal power, Operations personnel determined that Technical Specification (TS) Surveillance Requirement (SR) 4.4.6.2.1.e had not been met. This SR requires the reactor head flange leakoff system to be monitored at least once every 24 hours. On April 18, the reactor flange leakoff temperature indicator had drifted high. A main control room annunciator alarmed, alerting the operators of the high temperature condition. Operations personnel read the annunciator response procedure, verified that the indicated temperature increase was erroneous, and initiated a work request to repair the indicator. The annunciator response procedure also indicated that an evaluation of plant TS 3.4.6.2 and SR 4.4.6.2.1.e should be performed. The assistant shift operations supervisor inadvertently reviewed the wrong TS section and determined that the inoperable reactor flange leakoff temperature indicator had no impact on TSs. The cause of this event was personnel error. The Operations crew that declared the reactor head flange leakoff temperature indicator inoperable failed to perform an adequate review to determine the applicability of TSs. Personnel actions will be developed for the appropriate individuals involved in this event.
3271994008 | Sequoyah 1 | 05/01/1994 | 05/25/1994 | 9406030079 | <strong>Turbine Trip Followed by a Reactor Trip as a Result of a Loss of a Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1994, at 0140 Eastern daylight time, with Unit 1 in power operation at approximately 50 percent power, the turbine tripped followed by a reactor trip as a result of the loss of the 1A main feedwater pump (MFP). Prior to the event, the 1B MFP was out of service for maintenance. During clearance tagging in support of the maintenance work on the 1B MFP oil pump, an assistant unit operator inadvertently deenergized the running oil pump on the in-service 1A MFP. The loss of the oil pump and the subsequent drop in the oil pressure resulted in a trip of the operating MFP. With both MFPs in a tripped condition, a turbine trip and the subsequent reactor trip was initiated. The cause of the event was personnel error. Appropriate disciplinary action was taken with the involved individual.
3271994009 | Sequoyah 1, Sequoyah 2 | 06/02/1994 | 07/01/1994 | 9407070296 | <strong>Missed Surveillance Associated With the Monitoring of Postaccident Monitoring Instrumentation on the Neutron Flux and Auxiliary Feedwater Systems</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1994, at 1330 Eastern daylight time, with Units 1 and 2 in power operation at approximately 100 percent, it was determined that Technical Specification (TS) Surveillance Requirement (SR) 3.3.3.7 had not been met for the source and intermediate range neutron flux accident-monitoring instruments because nonqualified indicators were being used in the surveillances for both Units 1 and 2. On June 21, 1994, during review of the condition, it was determined that the same TS SR had also not been met for auxiliary feedwater valve position indication. The SR requires accident monitoring instrumentation to be demonstrated operable by performance of a channel check at least every 31 days. The first failure to meet the SR was identified during resolution of a work document associated with instrument labeling. The cause of the events was an inadequate procedure. The procedure revision issued in December 1990 incorrectly incorporated a design change associated with postaccident monitoring instruments. Upon identification of the condition, Operations personnel verified equipment operability by using the qualified accident-monitoring indicators and found them to be operable. The procedure errors were corrected. Additional procedure reviews will be performed toensure that the procedures performing channel checks associated with accident-monitoring instrumentation SRs implemented by the previous design change contain correct technical details.
3271994010 | Sequoyah 1, Sequoyah 2 | 07/03/1994 | 08/01/1994 | 9408090391 | <strong>Inadvertent Failure to Staff the Shift Technical Advisor (STA) Position for 30 Minutes During Power Operation</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1994, at 0700 Eastern daylight time, with Unit 1 in power operation (Mode 1) at approximately 100 percent and Unit 2 in power operation (Mode 1) at approximately 77 percent, it was determined that Technical Specification (TS) Administrative Control 6.2.2 had not been met for the STA position. TS 6.2.2 requires a minimum of one STA on shift during operations in Modes 1 through 4. An individual filling the floor assistant shift operations supervisor (ASOS) and STA positions provided a shift turnover to the oncoming floor ASOS and left the site without providing a turnover to or being relieved by the oncoming STA. Consequently, the STA position was not staffed for 30 minutes. The condition was a result of personnel error. The individual with duty STA responsibilities did not remember that he was also filling the STA position after being relieved of the floor ASOS duties. The appropriate disciplinary action was taken with the involved individual.
3271994011 | Sequoyah 1 | 07/15/1994 | 08/12/1994 | 9408190115 | <strong>Manual Reactor Trip and Subsequent Inadvertent Feedwater Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1994, at 1352 Eastern daylight time (EDT), with Unit 1 at approximately 25 percent power and with the turbine offline, a manual reactor trip was initiated. As designed, the reactor trip initiated a feedwater isolation (FWI). Subsequent to the trip, at 1558 EDT, a second FWI occurred. The trip was initiated in accordance with procedures as a result of the loss of a reactor coolant pump (RCP). During implementation of a dispatch switching order (clearance tagging) for main generator voltage regulator repair, an individual inadvertently removed bus-side fuses instead of line-side fuses to the 1D 6.9-kilovolt unit board. The bus fuses provide power to the board's loss-of-voltage relays. When the fuses were removed, a loss of voltage was sensed, resulting in the tripping of motor breakers supplied by the board, including the Loop 4 RCP motor breaker. The condition was caused by personnel error. The individual performing the clearance did not realize that the wrong fuse compartment was accessed until after the fuses were removed. The appropriate disciplinary action was taken with the involved individual. The second FWI appears to have been caused by erratic operation of the Loop 4 steam generator power-operated atmospheric relief valve. Troubleshooting identified a problem with the valve controller. The controller was repaired and returned to service.
3271994012 | Sequoyah 1, Sequoyah 2 | 07/15/1994 | 08/15/1994 | 9408190129 | <strong>Missed Surveillance as a Result of Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1994, it was discovered that the containment building penetration surveillance was not implemented in instructions as required by Technical Specification Surveillance Requirement 4.9.4. The procedure implementing the required surveillance was incorrect in that it did not specify that all containment penetrations were required to be verified once every seven days during core alterations or during the movement of irradiated fuel in containment. Subsequently, it was determined that the surveillance had not been implemented during the Unit 1 Cycle 6 refueling outage as required by technical specifications. In September 1991, the procedure implementing the surveillance requirement was revised, separating the procedure into two separate procedures, one for each unit. This condition had existed since that time. The cause of this event was inadequate procedure revision and inadequate review by involved personnel. The surveillance instructions have been revised to properly implement technical specification requirements.
3271994013 | Sequoyah 1, Sequoyah 2 | 08/23/1994 | 09/21/1994 | 9409290051 | <strong>Missed Surveillance as a Result of Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1994, it was discovered that Surveillance Requirement (SR) 4.7.4.b.2, which verifies that each essential raw cooling water (ERCW) pump starts automatically on a safety injection (SI) test signal, was not being performed as required by technical specifications (TSs). The procedure implementing the required surveillance was incorrect. The procedure requires verifying that each ERCW pump starts automatically on a blackout (BO)/SI test signal. The BO/SI test signal will not ensure that the ERCW pumps start on an SI signal since the BO circuity starts the pumps first. It was subsequently determined that the SR had not been performed correctly since the procedures implementing the SR were revised on October 3, 1991, for Unit 1 and February 28, 1992, for Unit 2. This condition has existed since that time. The cause of this event was an inadequate procedure revision and an inadequate review by the involved personnel. The Unit 1 procedure has been revised and was successfully performed to comply with TS requirements. The Unit 2 procedure will be revised and performed before entry into Mode 4.
3271994014 | Sequoyah 1, Sequoyah 2 | 11/29/1994 | 12/22/1994 | 9412290214 | <strong>Turbine and Reactor Trips Caused by Loss of the Turbine Electrohydraulic Control System Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1994, at 0713 Eastern standard time, with Unit 1 in power operation at approximately 100 percent power, the turbine tripped followed by a reactor trip as a result of the loss of both of the turbine 48-volt electrohydraulic control (EHC) power supplies. The cause of the loss of both 48-volt turbine EHC power supplies was attributed to an electrical spike on the power supply output. The power supply output overvoltage protection limiter setting for both power supplies had previously been reduced. The root cause of this event was inadequate technical review in changing the EHC overvoltage trip point. The trip point was changed based upon verbal communication from an onsite vendor representative. A contributing factor to this event was an increase in radio frequency interference resulting in the overvoltage trip point being exceeded, causing the loss of the EHC power supply. The overvoltage trip point was reset to the 10 percent preferred margin before returning the system to operation. The appropriate plant procedures will be revised to require vendor information, including verbal information, to be evaluated in accordance with the vendor manual program before the information can be utilized.
3271994015 | Sequoyah 1, Sequoyah 2 | 12/08/1994 | 01/30/1995 | 9502070153 | <strong>Failure to Perform an Hourly Fire Watch as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>This supplement provides root causes determined as a result of the investigation. On December 8, 1994, with Unit 1 in Mode 1 at 60 percent power and Unit 2 in Mode 1 at 100 percent power a person conducting a fire watch reached the doors that were normally used for access between the control building and Elevation 734 of the auxiliary building. These doors were found to be chained and locked. The fire watch then attempted to access the area from the auxiliary building but found that access was blocked by a radiological control rope and signs which indicated that changes to radiological conditions could occur. While the fire watch was attempting to locate a Radiological Control technician, the fire watch foreman arrived. Because of the time which had elapsed, the decision was made for the fire watch to continue on the prescribed route to avoid missing additional fire watches in the auxiliary building. the refuel floor were chained and locked by Security personnel. <br /><br /> The additional investigation revealed inadequate management attention as a root cause of this event.
3271994016 | Sequoyah 1, Sequoyah 2 | 12/14/1994 | 01/12/1995 | 9501200024 | <strong>Three Events that were Granted Enforcement Discretion: Problems Encountered During a Modification to the 2A-A Diesel Generator Speed Controller, Problems with Unit 1 Vital Inverter 2-I, Oil System Problems with the Unit 2 Turbine-Driven Auxiliary Feedwat</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1994, with Units 1 and 2 in power operation (Mode 1) at approximately 100 percent, it was determined that TVA should provide NRC notification for three events in accordance with 10 CFR 50.73. These events were previously granted enforcement discretion by NRC; therefore, they were not previously considered 10 CFR 50.73 reportable by TVA. The events are being reported as conditions that resulted in operations prohibited by technical specifications (TSs). The first event occurred on July 8, 1994. In this event, the TS allowable outage time (AOT) was exceeded as a result of problems encountered during modification of the 2A-A diesel generator speed controller. The second event occurred on October 2, 1994, when the TS AOT was exceeded for Unit 1 Vital Inverter 2-I. The inverter was out-of-service because of problems encountered during the performance of maintenance activities. The third event occurred on November 7, 1994, when the TS AOT was exceeded for the Unit 2 turbine-driven auxiliary feedwater (TDAFW) pump. The TDAFW pump was out-of-service because of problems with its oil system. In each event, the specific problems were resolved, and the equipment was tested, found acceptable, and returned to service.
3271994017 | Sequoyah 1, Sequoyah 2 | 12/22/1994 | 01/23/1995 | 9502020171 | <strong>Auxiliary Building Isolation (ABI) as a Result of High Radiation in the Spent Fuel Area</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1994, at 1410 Eastern standard time, a B-train ABI and start of the B-train auxiliary building gas treatment system (ABGTS) occurred. The initiation was the result of high radiation in the spent fuel pool area. During modification activities associated with the spent fuel pool storage rack replacement, a vacuum hose was being removed from the spent fuel pool. During the removal of the hose, an air pocket developed in the hose. During attempts to remove the air pocket, the hose came into close proximity of the radiation monitor. The hose was within sufficient proximity of the radiation monitor and dose rate of sufficient magnitude for the monitor to actuate. The high radiation signal cleared after placing the hose back in the spent fuel pool. After verifying the cause of the high radiation signal, Operations returned the auxiliary building ventilation system to normal. The cause of the event was the failure to take adequate precautions to ensure that the activities associated with the spent fuel pool would not result in an ABI.
3281994001 | Sequoyah 2 | 01/08/1994 | 02/04/1994 | 9402150103 | <strong>Two Inoperable Main Steam Isolation Valves (MSIVs) Caused Entry Into Technical Specification (TS) Limiting Condition for Operation 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1994, with Unit 2 in Mode 3 with the reactor coolant system at 547 degrees Fahrenheit (F) and 2,235 pounds per square inch gauge, a shutdown of Unit 2 was being performed as the result of a problem with the 2B-B charging pump. As the result of generic concerns from an incident that had occurred approximately two weeks previously at the McGuire Nuclear Station, a decision was made that the MSIVs would be tested. The SQN testing of the MSIVs was performed at 547 degrees F. As the result of the testing, two of the four MSIVs failed the TS surveillance test. Once the unit was in Mode 4, all of the MSIVs were inspected, and the necessary adjustments were performed. The valves were retested at 547 degrees F, and all four MSIVs had stroke times within TS requirements. The root cause of this condition was a lack of guidance from the MSIV manufacturer on the required clearance adjustments necessary to compensate for thermal expansion. Testing of the MSIVs will be performed at approximately 547 degrees F until an adjustment method that is not temperature dependent can be developed.
3281994002 | Sequoyah 2 | 01/08/1994 | 02/07/1994 | 9402150253 | <strong>Technical Specification Required Shutdown Because of the Failure of the 2B-B Centrifugal Charging Pump (CCP)</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1994, at 1610 Eastern standard time (EST), with Unit 2 in Mode 1, the 2B-B CCP motor tripped on timed overcurrent. The failed pump was declared inoperable and was removed from service. During disassembly of the pump, it was determined that the pump shaft broke at the balance drum lock nut. before the failure. In accordance with technical specifications, Unit 2 was placed in Mode 4 (hot shutdown) at 2305 EST on January 8, 1994. The shaft break was determined to be the result of material fatigue. The probable cause of the fatigue failure was a gas entrainment event that occurred on August 20, 1990. It is suspected that the gas entrainment event resulted in shaft stresses that, over time, lead to material fatigue. The 2B-B CCP was repaired, tested, and returned to service.
3281994003 | Sequoyah 2 | 01/10/1994 | 02/08/1994 | 9402180060 | <strong>The Opening of a Cold Leg Accumulator (CLA) Isolation Valve Results in Injection Into Reactor Coolant System</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1994, Unit 2 was preparing to start up from a forced outage. The Unit 2 senior reactor operator (SRO) directed a unit operator and an assistant shift operations supervisor trainee to lift a clearance on the CLA isolation valves. Once power was restored, the valve immediately started opening. The operators quickly opened the breaker to the power supply and contacted the main control room SRO. The SRO instructed the operators to place power back on the valve so that the main control room operators could close the valve. Approximately 90 gallons of inventory from the No. 1 CLA injected into the reactor coolant system. The cause of this event was that personnel did not fully evaluate the cause and effect of placing power on the CLA isolation valves at that point in the start-up process. The operators involved with this event will be counseled by the Operations superintendent with regard to attention to detail and the Stop-Think-Act-Review (STAR) process.
3281994004 | Sequoyah 2 | 06/18/1993 | 05/09/1994 | 9405170203 | <strong>Pressurizer Cooldown Rate Exceeded</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1994, during a review of historical data on the pressurizer, it was determined that the technical specification pressurizer cooldown limit had been exceeded on June 18, 1993, and was not restored within the required timeframe. The performance of a surveillance instruction associated with safety injection system check valve testing requires the starting of a safety injection pump. This surveillance instruction injects water into the reactor coolant system (RCS). When the water is injected into the RCS, the water in the RCS is forced into the bottom of the pressurizer, displacing the water at the bottom of the pressurizer. The RCS was at a lower temperature than the water in the pressurizer, resulting in the lowering of the water temperature in the pressurizer. The temperature in the bottom of the pressurizer went from approximately 368 degrees Fahrenheit (F) to approximately 150 degrees F in about 22 minutes. The surveillance instruction alerted Operations personnel to monitor the pressurizer level and pressure but did not include any precaution about the pressurizer temperature. The cause of the event was an unanticipated condition. The corrective actions included revising the surveillance instruction to include lessons learned and evaluating other system interaction for potential adverse conditions.
3281994005 | Sequoyah 2 | 04/19/1994 | 05/19/1994 | 9405250251 | <strong>Loss of Containment Integrity as a Result of a Relief Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1994, at 1440 Eastern daylight time, it was determined that the technical specification for containment leak rate limits was exceeded as a result of a failed relief valve bellows and a check valve leaking through its seat. Prompted by an inability to maintain pressurizer relief tank (PRT) pressure, relief valves outside of containment that discharge to a line that is connected to the PRT inside containment were inspected. One relief valve was found to be leaking gas through the bonnet vent hole. Testing of the relief valve quantified the leakage. Leakage from the relief valve in combination with containment integrated leakage resulted in a leakage greater than allowable limits. Limiting Condition for Operation (LCO) 3.6.1 was entered. The relief valve was replaced and the LCO was exited. Upon disassembly of the failed relief valve, the bellows was found to have a 30 percent circumferential crack. The cause of the bellows failure was undetermined.
3281994006 | Sequoyah 2 | 08/25/1994 | 09/23/1994 | 9409290141 | <strong>Engineered Safety Feature Actuation Resulting From a Loss of Nonessential Air Supply</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1994, at 1711 Eastern daylight time, with Unit 2 in Mode 6 and defueled, the nonessential control air header to containment was inadvertently isolated, causing an engineered safety feature actuation. The event occurred during the performance of the restoration portion of a preventive maintenance activity. Operations personnel were realigning the system valves to their normal position. However, the sequence in which this was conducted isolated the nonessential control air header. Operations personnel quickly determined the cause of the event and restored the system air pressure. The root cause of this event was personnel error in that the unit operator did not follow procedures. An information letter has been developed for distribution to Operations personnel with lessons-learned and information concerning the correct process for performing briefings before and during the performance of activities.
3281994007 | Sequoyah 2 | 09/23/1994 | 10/24/1994 | 9411010364 | <strong>Centrifugal Charging Pump (CCP) Total Flow Rate Exceeded the Technical Specification (TS) Upper Limit Resulting in the Pump Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1994, it was determined that the 2B-B CCP total flow rate exceeded the TS limit of 555 gallons per minute (GPM). During the performance of a surveillance instruction (SI), total flow was measured at approximately 566.5 GPM. A subsequent review determined that the condition existed since January 10, 1994, resulting in the 2B-B CCP being technically inoperable for approximately six months (January 10 through July 5, 1994). During this period of time, the 2A-A CCP was out of service for short periods of time on six occasions, resulting in Unit 2 being outside the design basis. On January 5, 1994, the 2B-B CCP motor tripped on timed motor over-current. Component inspection determined that the pump shaft broke and that the rotating element required replacement. An evaluation performed on a spare rotating element determined that the spare rotating element was suitable for replacement. The spare rotating element was installed, and the CCP was tested under miniflow conditions and was placed in service. However, with the replacement rotating element, the total flow delivered was greater than the TS upper limit. The condition was caused by an incorrect evaluation of the performance of the spare rotating element in that the actual pump performance was higher than estimated in the evaluation. The SI was completed, and both CCPs were left within TS limits.
3281994008 | Sequoyah 2 | 10/21/1994 | 11/18/1994 | 9411250077 | <strong>Manual Actuation of the Reactor Trip Breakers as a Result of a Malfunction of a Rod Control Demand Step Counter</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On October 21, 1994, at 2230 Eastern daylight time (EDT) with Unit 2 in Mode 5 (cold shutdown), the reactor trip breakers were opened as a result of rod control demand step counter malfunctions in Control Bank 'A'. The Technical Specification (TS) 3.1.3.3 action statement requires opening the reactor trip breakers when the group demand counter is inoperable or is not capable of determining demand position within plus or minus two steps during Mode 5. During the manipulation of Control Bank 'A', the step counter for Group 2 did not move when Operations personnel were attempting to move the control rods. This resulted in a deviation between Group 1 and Group 2 step counters by more than the plus or minus two steps required by TSs. An investigation of the event determined that the reset mechanism for the Control Bank 'A' Group 2 step counter was mechanically bound. The subsequent operation of the counter did not reveal any problems as a result of binding.
3311994001 | Duane Arnold | 01/07/1994 | 02/04/1994 | 9402180125 | <strong>Inadequate Test of the APRM High Flux Scram Trip Setpoint</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1994 while the plant was operating at 100% power, it was determined that the test of the average power range monitor (APRM) high flux scram trip setpoint was inadequate. The test has not been performed at a recirculation flow greater than 100% to assure that the scram setpoint does not exceed 120% rated power, as required by the Technical Specifications. <br /><br /> The APRMs were considered to be inoperable and a 6 hour to Startup mode limiting condition for operation (LCO) was entered. The test was revised and performed with satisfactory results and the LCO was exited. This condition was caused by a lack of awareness of the requirement to test the 'clamping' function on the scram trip setpoint. The test results verified that the 'clamping' function had been and is set properly. There was no effect on safe operation of the plant.
3311994002 | Duane Arnold | 01/12/1994 | 07/29/1994 | 9408110077 | <strong>RCIC Low Steam Supply Pressure Isolation Loss of Function Due to Instrument Drift</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1994, during the performance of a routine surveillance test procedure (STP) for the Reactor Core Isolation Cooling (RCIC) system low steam supply pressure isolation function, three of the four pressure switches provided to perform this function were found low (non-conservative) outside their calculated allowed values. These four switches comprise a two-out-of-two-once logic that generates isolation signals to the RCIC inboard and outboard steam supply isolation valves MO2400 and MO2401 which are designated as Primary Containment Isolation System (PCIS) Group 6A valves. <br /><br /> The plant was operating at 100% power at the time of the surveillance with no existing limiting conditions for operation (LCOs) in effect. All three pressure switches were recalibrated and returned to service within the confines of the STP and allowed outage time. The cause of this event was instrument drift of the Barksdale model B2T-M12SS pressure switches.<br /><br /> Corrective actions include increased surveillance frequencies, procedure revisions, Instrument Trending Program enhancements, and Engineering evaluations of Barksdale pressure switches. There was no effect on plant safety, personnel safety or plant availability as result of this event.
3311994003 | Duane Arnold | 01/19/1994 | 02/15/1994 | 9403030053 | <strong>Failure to Establish Secondary Containment During Routine Maintenance</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1994, while the plant was operating at 100% power, it was determined that Technical Specification Table 3.2-A action statement for the Off Gas vent radiation monitors (RM4116A/B) had not been complied with during routine maintenance on January 19, 1994. The routine maintenance performed on January 19, 1994 had removed these monitors from service without establishing Secondary Containment integrity with the Standby Gas Treatment System operating within one hour. <br /><br /> The Off Gas vent radiation monitors were removed from service on January 19, 1994 at 0235 hour and returned to service on January 19, 1994 at 1414 hours. The Kaman effluent radiation monitors (RM-4176/RM-4175) for the Off Gas stack were operable during the subject maintenance with no abnormal trends indicated. The containment vent and purge valves were closed. All other Primary Containment Isolation System (PCIS) group III instrument isolation functions were operable. There was no effect on the safe operation of the plant.
3311994004 | Duane Arnold | 02/14/1994 | 03/14/1994 | 9403230201 | <strong>Standby Filter Units Inoperability Due to Inappropriate Electric Heater Design Setpoints</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1994, during a routine surveillance test performed during unusually cold weather conditions, a hot water heating coil for the 'B' Control Building Standby Filter Unit (SFU) froze, ruptured, and eventually released hot water and steam into the downstream filter train. The plant was operating at 100% power with no existing Limiting Conditions for Operation (LCO's) in effect.<br /><br /> The root cause of the event was the safety related electric heater sheath temperature trip setpoint being too low. Engineering review and evaluation determined that a potential common mode failure existed. The 'A' SFU was declared inoperable resulting in both SFU's being inoperable at the same time. <br /><br /> Both SFU's electric heater trip setpoints were raised to higher, analyzed values. The hot water coil in the 'B' SFU was removed and left out when the unit was repaired. Engineering evaluation, equipment calibrations, and procedure development will be performed to complete corrective actions. <br /><br /> There was no effect on plant or personnel safety as a result of this event.
3311994005 | Duane Arnold | 04/19/1994 | 05/12/1994 | 9405230306 | <strong>Missed Surveillances of Rod Worth Minimizer Due to Misinterpretation of Technical Specification Requirement</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1994, while the plant was operating at 100% power, the periodic review of a Surveillance test procedure (STP) concluded that one of four Rod Worth Minimizer (RWM) operability checks required by the Technical Specifications, had not been performed during shutdowns between 1989 and 1993. The cause was a misinterpretation of the Technical Specification requirements. <br /><br /> The RWM is a backup to procedural controls for control rod selection and movement. All of the RWM operability checks were performed at all startups. There was no effect on plant safety and there are no restrictions on current operation. <br /><br /> The Technical Specifications have been revised to remove misleading wording and the STP has been revised to assure complete testing during the next shutdown. The periodic procedure reviews are continuous and ongoing and are intended to detect and correct such deficiencies.
3311994006 | Duane Arnold | 04/26/1994 | 07/19/1994 | 9407250224 | <strong>Reactor Water Cleanup Isolation Due to Incomplete Valve Closure Caused by Position Indicator Obstruction</strong><br /><i>Abstract:&nbsp;</i>At 0400 hours on April 26, 1994, with the plant operating at 100% power, a Group V Primary Containment Isolation System (PCIS) signal was received and the appropriate valves closed as a result of a Reactor Water Cleanup (RWCU) high differential flow signal. The flow differential occurred while an operator was performing a system tagout during which the 'A' RWCU pump discharge valve was required to be fully closed but was not. Subsequent system draining resulted in flow back through the partially open discharge valve resulting in the high differential flow condition. The plant was in day 2 of a 7 day Limiting Condition for Operation (LCO) for the 'A' Core Spray subsystem. <br /><br /> The cause of this event was that the position indicator on the discharge valve reached the full closed position, stopping valve movement, prior to the valve being full closed. Contributing factors were improper set up of the indicator nut during previous work and the unavailability of communications in the RWCU pump room. <br /><br /> Corrective actions include removal of the position indicators and indicating plates, revising the tagout procedure, providing interim guidance to operators, and installing a plant page speaker in the RWCU pump room. There was no effect on plant safety, personnel safety or plant availability as a result of this event.
3311994007 | Duane Arnold | 05/29/1994 | 06/28/1994 | 9407080005 | <strong>Residual Heat Removal System (RHRS) Shutdown Cooling Partial Isolation</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1994, while proceeding to cold shutdown to repair a leak in the Electro-Hydraulic Control (EHC) system, a partial Primary Containment Isolation System (PCIS) Group IV actuation isolated the Residual Heat Removal (RHR) system suction piping. The RHR Shutdown Cooling (SDC) outboard isolation valve auto-closed when the RHR SDC inboard isolation valve was opened. This evolution was required in order to flush and warm the RHR piping and heat exchanger prior to initiating SDC. When the RHR SDC inboard isolation valve was opened, a pressure surge was sensed at one of the three pressure switches which resulted in a partial PCIS Group IV isolation. There was no adverse effect on the RHR system or plant. Corrective actions will include a review of the RHR SDC isolation valve control and isolation logic and procedure changes.
3311994008 | Duane Arnold | 05/17/1994 | 06/13/1994 | 9406200338 | <strong>Missed Sensor Response Time Testing of Reactor Protection System Pressure Switches</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1994, the plant was operating at 100% power. During scheduling of Reactor Protection System (RPS) sensor response time testing it was determined that this testing had not been performed at the required surveillance frequency for one reactor high pressure scram pressure switch. The cause was inadequate tracking and scheduling of surveillance testing. <br /><br /> On May 19, 1994, while the plant was operating at 100% power, additional research determined that the four RPS reactor high pressure scram pressure switches had been replaced in 1987 and between 1991 and 1992 without response time testing being performed. The cause was inadequate procurement and maintenance process controls. <br /><br /> The untested switches were declared inoperable until they were satisfactorily tested. All four RPS pressure switches were found to perform properly when tested. The scheduling of surveillance testing for these and other switches has been formalized. A corrective action team has been formed to recommend actions to prevent recurrence.
3311994009 | Duane Arnold | 06/09/1994 | 07/06/1994 | 9407140004 | <strong>Control Rod Drive Differential Pressure Transmitter Leak Into The Reactor Building</strong><br /><i>Abstract:&nbsp;</i>At 0109 hours on June 9, 1994 with the plant operating at 100% power, an Excess Flow Check Valves System B Hi Flow alarm was received on control room panel 1C03 due to a failed differential pressure transmitter (PDT). The respective excess flow check valve immediately isolated, thereby preventing the release of reactor coolant to the reactor building. This event was considered an Emergency Safety Features (ESF) actuation. <br /><br /> The cause of this event was a packing leak that dripped condensate water on to the PDT housing. Over time, two bolts that coupled the PDT housing components failed, causing subsequent failure of the PDT and the resultant leak. <br /><br /> Corrective actions include replacement of the PDT with a model that is not conducive to the entrapment of water in its housing, procedure revision, and performance of a detailed walkdown of like components to ensure there are no similar concerns. There was no effect on plant safety, personnel safety, or plant availability as a result of this event.
3311994010 | Duane Arnold | 07/10/1994 | 08/04/1994 | 9408160016 | <strong>Manual Scram Due to Loss of Electro-Hydraulic Control (EHC) Oil</strong><br /><i>Abstract:&nbsp;</i>On Sunday, July 10, 1994, at 2201 hours, with the plant operating at 68% power, a manual scram was inserted in response to an impending loss of Electro-Hydraulic Control (EHC) reservoir level. The loss of EHC reservoir level was caused by a 210 degree crack in the 1' EHC tubing supplying the number 3 main turbine control valve (CV-3). <br /><br /> All control rods fully inserted and vessel level dropped below the low level setpoint causing groups 2-5 primary containment isolations. Vessel level was restored and returned to normal. Reactor pressure was controlled by the turbine bypass valves and main steam line drains. There were no emergency core cooling system actuations and no safety relief valve openings. <br /><br /> Corrective actions include repair of the ruptured tubing and installation of accumulators on the CVs to prevent reoccurrence of this event. The reactor was restarted on July 16, 1994.
3311994011 | Duane Arnold | 07/18/1994 | 08/12/1994 | 9408250059 | <strong>Missed Surveillance of The 'A' Channel Rod Block Monitor Due to a Failure to Recognize The Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1994, at 0530 hours, during plant startup with reactor power at 63.9%, it was recognized that a surveillance test requirement to demonstrate the operability of the 'A' channel Rod Block Monitor (RBM) had not been performed as required by the Technical Specifications. Section 4.3.C.3 requires that when one RBM channel is inoperable and a Limiting Control Rod Pattern (LCRP) exists, an instrument functional test of the operable RBM channel shall be performed within 24 hours prior to rod withdrawal. The cause of this event is personnel error due to a failure to recognize the surveillance test requirement. The required surveillance test was performed and completed satisfactorily when the error was discovered. A written communication was sent to the control room to inform the Operations personnel of this event and criteria for thorough review of the limiting conditions for operation (LCOs) and surveillance requirements.
3311994012 | Duane Arnold | 10/04/1994 | 11/02/1994 | 9411080256 | <strong>Essential Bus Degraded Voltage Relay Calibration Errors Due to Harmonics</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1994, With the plant operating at 100% power, during the performance of an increased frequency surveillance test, 4 out of 8 Essential Bus Degraded Voltage relays were found high outside Technical Specification (TS) voltage limits and a fifth high outside the time delay limit. The relays were re-calibrated and returned to service. Analysis of the relay failures led to re-performance of the test using an improved calibration technique. On October 17, 1994 all 8 relays were found low outside the TS voltage limits using the improved calibration method. <br /><br /> The root cause of the event was a failure to use a line corrector on the AC power source during calibration. Corrective actions include procedure revisions, re-calibrating the relays, increased surveillance and trending, and engineering reviews for generic implications. <br /><br /> The effect on plant safety was a reduced margin in the protection against essential motor control center (MCC) trips that can occur at reduced voltage. There were no other systems, components, or structures inoperable at the time that had an effect on the event.
3311994013 | Duane Arnold | 11/11/1994 | 12/09/1994 | 9412130254 | <strong>Reactor Water Cleanup System Isolation Due to Failed Head Gasket</strong><br /><i>Abstract:&nbsp;</i>At 0149 on November 11, 1994, with the plant at 100% power, a Reactor Water Cleanup (RWCU) Hi Differential Flow alarm was received on control room panel 1C04, and subsequently, per design, a Primary Containment Isolation System (PCIS) Group 5 RWCU Isolation occurred. After confirming that the isolation was complete, a non-licensed operator was dispatched to inspect for leakage and/or system malfunctions. developed in the area of RWCU filter demineralizer 1T203A. This event was considered an Engineered Safety Features (ESF) actuation. <br /><br /> The cause of the event was the failure of the head gasket on filter demineralizer 1T203A. Corrective actions include replacement of the respective tank head gasket, rechecking the torque of the 'B' RWCU filter demineralizer closure head bolts, and periodic verification of torque values on RWCU filter demineralizer closure head bolts. There was no effect on plant safety, personnel safety, or plant availability as a result of this event.
3331994001 | FitzPatrick | 02/24/1994 | 04/06/1994 | 9404120247 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to Turbine Shaft Seal Leakage</strong><br /><i>Abstract:&nbsp;</i>The plant was operating at 100 percent power on 2/24/94 with the reactor mode switch in Run. The High Pressure Coolant Injection (HPCI) system had been declared inoperable in order to perform scheduled surveillance testing. During initial roll of the turbine, operators observed an approximate 3 to 4 foot plume of steam from the inboard shaft seal which did not diminish as the turbine came up to speed. The turbine was tripped and the limiting condition for operation for HPCI system inoperability continued. <br /><br /> The shaft seal was replaced and the HPCI system declared operable on 2/26/94. The steam seal leakage was caused by minor corrosion on gland seal surfaces and shaft sealing surfaces due to moisture within the turbine casing. Increased monitoring for leakage past the HPCI steam supply valve during standby conditions and corrective maintenance on the gland seal casings will improve turbine steam seal performance.<br /><br /> LER-89-014 describes a similar event where the HPCI system was declared inoperable due to moisture intrusion in the lubricating oil system.
3331994002 | FitzPatrick | 02/22/1994 | 03/10/1994 | 9403230081 | <strong>Reactor Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>During the Fall, 1993, maintenance outage, the pilot assemblies for two safety relief valves were removed for testing and recertification. On 2/22/94 and 2/23/94 the Authority received notification from the test facility that the test results exceeded the 1 percent tolerance allowed by Technical Specifications for valve actuation. Setpoint drift was a maximum of 1.8 percent on one valve and 2.5 percent on the second valve. A plant specific analysis performed previously envelopes the as-found setpoints. This analysis determined that setpoint drift greater than that found would have no significant safety impact on vessel overpressure margin, thermal limits, or Emergency Core Cooling system performance. Corrective action included replacing the SRV pilot assemblies with recertified assemblies and continued participation in the BWR Owners Group addressing setpoint drift. <br /><br /> LER numbers 92-016, 90-018, 89-026, 88-010, 88-004, 87-004, 85-013 and 85009 are similar events involving SRV setpoint drift.
3331994003 | FitzPatrick | 05/18/1994 | 06/15/1994 | 9406240159 | <strong>Incomplete Periodic Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>The plant was operating at 100 percent power with the reactor mode switch in Run. procedure for the west diesel fire pump starting battery, it was identified that a Technical Specification requirement to visually inspect battery cell plates had been removed from the procedure. On 10/10/91, a procedure change deleted cell plate visual inspection because the opacity of the cell jars limited the ability to do the inspection. Personnel involved in implementing the procedure change failed to adequately review the Technical Specification, Cause Code A. <br /><br /> Administrative controls for review and revision of test procedures were upgraded in 1993 as a part of the surveillance test program improvement plan. The controls for procedure changes were also improved. This error was discovered using the new controls. There is no safety significance associated with this event because other quantitative testing has assured battery capacity and reliability. Cell plate inspection was restored to the test procedure and a Technical Specification Interpretation written which describes both the scope of inspection and periodic battery replacement if the battery is not supplied with clear cell jars. LER numbers 92-032 and 93-027 describe similar test procedure weaknesses.
3331994004 | FitzPatrick | 06/09/1994 | 07/09/1994 | 9407190151 | <strong>Deviation from FSAR Single Failure Criteria for H sub 2/ O sub 2 Analyzer & CAM Valves</strong><br /><i>Abstract:&nbsp;</i>On 6/9/94, the plant was operating at 100 percent power in a steady state condition. While performing a review of the Technical Specifications for an amendment submittal, engineering determined that a single failure of a reactor vessel low level or high drywell pressure isolation control logic relay could prevent isolation of the Primary Containment Atmosphere Monitoring and the Hydrogen and Oxygen Analyzer systems. This condition was considered outside of the design basis as described in two sections of the Updated Final Safety Analysis Report. The sampling systems and their associated isolation valves were declared inoperable. Subsequent reviews found that the valve isolation control logics and power supplies were revised in 1981 to ensure post-accident sampling capability in accordance with NUREG-0578. On 6/22/94, a Nuclear Safety Evaluation was written and approved that documented the adequacy of the existing design and allowed the sampling systems and their associated isolation valves to be declared operable. The sample lines are considered 'instrument lines' which meet the primary containment isolation criteria in General Design Criteria 56 and AEC Safety Guide 11. However, the description of the containment isolation provisions for these sample lines needs to be changed in the UFSAR to reflect this distinction.
3331994005 | FitzPatrick | 06/23/1994 | 07/11/1994 | 9407190116 | <strong>Reactor Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>During the spring, 1994, maintenance outage, the pilot assemblies for two safety relief valves were removed for testing and recertification. On 6/23/94 the Authority received notification from the test facility that the test results exceeded the 1 percent tolerance allowed by Technical Specifications for valve actuation. Setpoint drift was a maximum of plus 1.2 percent on one valve and minus 2.2 percent on the second valve. There is a plant specific analysis which envelopes the as-found setpoints. This analysis determined that setpoint drift greater than that found would have no significant safety impact on vessel overpressure margin, thermal limits, or Emergency Core Cooling system performance. Corrective action included replacing the SRV pilot assemblies with recertified assemblies and continued participation in the BWR Owners Group addressing setpoint drift. <br /><br /> LER numbers 94-002, 92-016, 90-018, 89-026, 88-010, 88-004, 87-004, 85- 013 and 85-009 are similar events involving SRV setpoint drift.
3331994006 | FitzPatrick | 09/16/1994 | 10/17/1994 | 9410270364 | <strong>EQ Concerns Possibly Affecting Safety Related Electrical Switchgear in the</strong><br /><i>Abstract:&nbsp;</i>On 09/16/94, the plant was operating at 75 percent power in a steady state condition. Engineering discovered two incorrect assumptions in two EQ Program analyses performed in 1981. one assumption was that two safety-related electrical switchgear rooms located within the Turbine Building were 'sealed'. A recent walkdown revealed ventilation openings which could provide a path for steam to enter the two rooms during a high energy line break (HELB) in the Turbine Building or a Main Steam Line Break (MSLB) in the Steam Tunnel. The second assumption was that no safety-related components required to mitigate a HELB or MSLB were located in the Turbine Building (except for those located within the 'sealed' rooms). One ventilation control panel in the Turbine Building contains controls for safety-related unit cooler fans in one of the two switchgear rooms. Plant operators closed three fire dampers, essentially 'sealing' the two rooms while not degrading room cooling or fire protection. Cooling equipment for the switchgear room associated with the exposed control panel was declared inoperable for a short while, resulting in a seven day shutdown LCO. Control circuits were isolated from the exposed control panel early the next day (09/17/94), allowing an exit from the LCO. An action plan was developed to determine and implement short term and long term resolutions. The cause was determined to be personnel error.
3331994007 | FitzPatrick | 10/30/1994 | 11/29/1994 | 9412060349 | <strong>Reactor Core Isolation Cooling System Isolated on High Exhaust Diaphragm</strong><br /><i>Abstract:&nbsp;</i>On 10/30/94, at 0224 hours, while operations Department personnel were performing surveillance testing of the Reactor Core Isolation Cooling System (RCIC), an unanticipated RCIC Outboard Steam Isolation Valve isolation signal (Primary containment Isolation System) was received. Closure of the isolation valve resulted in the automatic shutdown of the RCIC turbine. At the time of the event, the plant was operating at approximately 70 percent power with the mode switch in the RUN position and the High Pressure Coolant Injection System (HPCI) operable. <br /><br /> A leaking RCIC Exhaust Diaphragm coupled with a plugged RCIC Steam Exhaust Inter-Disc Vent Line caused increased steam pressure to trip High Turbine Exhaust Pressure Logic. The leaking of the diaphragm was attributed to installation of incorrect type diaphragm during equipment replacement. The root cause was determined to be a management/quality assurance deficiency (Cause Code E). The cause for the plugged vent pipe was attributed to poor work practices. Corrective actions included replacing RCIC Exhaust Diaphragms and removal and cleaning of the vent piping. The surveillance test was satisfactorily completed and RCIC returned to an operable status at 1221 hours on 11/1/94.
3331994008 | FitzPatrick | 11/03/1994 | 12/05/1994 | 9412150102 | <strong>Relay Room Vent System Isolation Valve Cable and Design Document Concerns</strong><br /><i>Abstract:&nbsp;</i>This is a Voluntary Report. On 11/03/94, the plant was operating at 69 percent power in a steady state condition. During a review of documentation and equipment configuration for the Relay Room Ventilation System, engineering noted a potential cable separation concern with power and control cables for the intake and exhaust isolation valves. As a precautionary measure, the Relay Room Ventilation System was placed in the 'isolate' mode, with the isolation valves closed. During the reportability screening, engineering and licensing personnel questioned the adequacy of design and operating documents. Subsequent reviews determined the separation criteria was not applicable to the Relay Room Ventilation isolation valves. An action plan was developed which included: updating an operating procedure to provide better guidance; establishing a more formal definition of the design and licensing basis; reviewing Relay Room habitability under various conditions; reviewing component classifications and cable designations; and un-isolating the system. The cause for the initial 10CFR50.72 notification was incomplete documentation of the design basis. Licensing and engineering personnel subsequently determined that the condition is not reportable. However, a voluntary report is being submitted to clarify the conditions found and their evaluation.
3331994009 | FitzPatrick | 11/29/1994 | 12/29/1994 | 9501040250 | <strong>Partial Invalid Primary Containment Isolation as a Result of a Personnel Error During Electrical Bus Power Source Transfer</strong><br /><i>Abstract:&nbsp;</i>On 11/29/94 at 1701 hours while at 34 percent rated power in the Run mode and conducting a normal shutdown for refueling power to two 4160 volt electrical distribution buses was interrupted momentarily during the transfer of power from the normal source to reserve (offsite) 115kV sources. The power interruption of approximately one second resulted in a partial primary containment isolation, isolation of the Reactor Building (secondary containment), and the loss of several other safety related and non-safety related functions. Each of the isolation valve closures or system losses were due to the momentary power loss rather than the generation of a valid isolation signal. The momentary power loss was caused by a personnel error. The operator performing the evolution opened the normal supply circuit breaker prior to closure of the reserve supply. The procedure in use may have contributed to the error. Systems were restored per plant procedures. Corrective action includes evaluation of procedure changes and evaluation of the installation of automatic power source transfer equipment.
3331994010 | FitzPatrick | 12/02/1994 | 12/21/1994 | 9412290232 | <strong>Shutdown Cooling Isolation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 2035 hours on December 2, 1994, with the plant in the shutdown condition for a refuel outage and the Residual Heat Removal System (RHR) in the Shutdown Cooling mode maintaining reactor coolant temperature, an incorrect electrical breaker was opened during an equipment tag out evolution. This equipment de-energization caused partial loss of power to the Reactor Protection System (RPS) which resulted in a half scram signal and a half Primary Containment Isolation System (PCIS) isolation signal. The PCIS signal isolated the suction path for RHR and resulted in the loss of Shutdown Cooling.<br /><br /> The cause for opening the wrong breaker was personnel error. <br /><br /> Immediate corrective actions included: restoring power to vital loads; resetting systems half isolation signals; reset RPS half scram signal; restoring RHR Shutdown Cooling; and suspending all equipment tag out work so Operations could conduct event briefings with department personnel.
3341994001 | Beaver Valley 1 | 01/09/1994 | 02/08/1994 | 9402180181 | <strong>Required Plant Shutdown Due to An Inoperable Train of Recirculation Spray Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>A Technical Specification (TS) required shutdown was commenced on 1/9/94 at 1100 hours, in response to a low flow condition through the A Train of the Recirculation Spray Heat Exchangers (RSHX). During testing of the A Train River Water Pump, WR-P-1A, total river water flow through the system was 6100 gpm. TS 3.6.2.2 requires a minimum flowrate of 8000 gpm per train. condition was due to fouling of the heat exchangers and that cleaning of the heat exchangers was necessary. The plant cooldown was initiated and an Unusual Event was declared in accordance with the Emergency Preparedness Plan at 1118 hours due to the required plant shutdown. The Unusual Event was terminated when the Unit reached Operational Mode 5 (Cold Shutdown) at 1317 hours on 1/10/94. Following heat exchanger cleaning, total flowrate through the A Train RSHXs was 9700 gpm. The heat exchangers were declared operable on 1/15/94. The majority of the debris in the heat exchangers consisted of approximately 30% clam shells and 70% ferrous corrosion products and turbucles. All of the clams were dead due to a recent Clamicide treatment of the Unit 1 river water system. The source of the corrosion products is the mild steel river water system piping. The B Train RSHXs and river water pump remained operable throughout this event.
3341994002 | Beaver Valley 1 | 03/18/1994 | 04/18/1994 | 9404210129 | <strong>Inoperable Diesel Generator Due to Inadequate Electrical Separation in Control Circuit</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1994, during review of a Duquesne Light Company Engineering Memorandum, a deficiency involving inadequate electrical separation in the No. 1 Emergency Diesel Generator governor and engine control circuit was identified. The deficiency involved the use of a non-safety related relay in a safety related system. A Westinghouse Model KLF Relay, used to provide diesel generator protection in the event of a loss of field, was found to be powered from the safety related 125 volt DC (VDC) system which supplies power to the No. 1 Emergency Diesel Generator governor and engine control circuit. A failure of the KLF Relay is postulated to cause a loss of the safety related 125 VDC system powering the governor and engine control circuit, and a loss of the field flash contactor. This condition has existed since original plant construction. The knife switch which provides the circuit connections to the KLF relay has been opened under administrative control. Administrative procedural controls will reinstate the KLF Relay protection during diesel generator surveillance testing, and re-isolate the relay when testing is completed. There were minimal safety implications as a result of this event. A KLF Relay failure capable of generating enough short circuit current (20 amperes) to disable the start circuit by tripping its supply breaker is improbable due to the physical design of the relay.
3341994003 | Beaver Valley 1 | 04/04/1994 | 05/17/1994 | 9405250155 | <strong>Improperly Installed Flow Orifice</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1994 at 1330 hrs, two flow orifices used to verify compliance with the Reactor Coolant pump controlled leakage Technical Specification limits were found to be improperly installed. Because these orifices are sensitive to flow orientation, the actual flow could be as much as 20 % greater than indicated. <br /><br /> At 1729 hrs, a controlled leakage calculation was performed using this 20 % correction factor for the 'B' and 'C' reactor coolant pumps. Results showed that the controlled leakage was greater than the Technical Specification limit. Flows were adjusted within limits. <br /><br /> A review of the past year's controlled leakage calculations was performed correcting for these orifices being installed backwards. It showed that the controlled leakage technical specification limit had previously been exceeded. <br /><br /> Therefore, this event is being reported in accordance with 10CFR50.73a.2.i.B as a condition prohibited by Technical Specifications. <br /><br /> The safety implications of this event were minimal. The basis for the controlled leakage limit is to ensure that safety injection flow will not be less than that assumed in the accident analysis. Engineering analysis shows that minimum required safety injection flow required by the accident analysis would have been available.
3341994004 | Beaver Valley 1 | 05/06/1994 | 06/03/1994 | 9406130082 | <strong>Technical Specification Required Shutdown Due to Inoperable River Water Header</strong><br /><i>Abstract:&nbsp;</i>On 5/6/94, at 2120 hours, with the Unit operating at 100 percent power, a decision was made to shutdown due to an inoperable Reactor Plant River Water Header. The 'A' River Water Header had been declared inoperable on 5/4/94, at 1340 hours, and Technical Specification (TS) 3.7.4.1 entered. Water had been discovered leaking at a pipe penetration during a routine inspection and was later confirmed to be River Water. The Shutdown was initiated on 5/6/94 when it was determined that the River Water Header would not be returned to operable status within the 72 hour time frame allowed by TS 3.7.4.1. The Nuclear Regulatory Commission was notified in accordance with 10CFR50.72(b)(1)(i)(A), via the Emergency Notification System, at 2152 hours on 5/6/94. The plant entered Mode 5 at 1122 hours on 5/8/94. At 1230 hours the leak was located on the Emergency Diesel Generator 'A' Train River Watersupply line. While the unit was shutdown, non-destructive examinations were performed at various points on the associated piping. Following Code repairs and engineering analysis, it was determined that the remaining River Water piping structural integrity would be maintained until the next Refueling Outage. Plant heat-up was then initiated and the plant was returned to service and synchronized to the system grid on 5/20/94, at 1452 hours.
3341994005 | Beaver Valley 1, Beaver Valley 2 | 06/01/1994 | 07/01/1994 | 9407060112 | <strong>Main Transformer Bushing Failure Results in Electric Grid Disturbance and Dual Unit Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On 6/01/94 at 1455 hours, an insulating bushing failure on the Unit 1 Main Unit Transformer initiated an immediate generator/turbine trip followed by a subsequent reactor trip. The transformer fault initiated a voltage disturbance on the electrical grid which caused an inadvertent protective relay actuation on a circuit monitoring the 138 kilovolt (KV) AC line supplying the Unit 2 System Station Service Transformer (SSST)2A. Unit 2 4KV AC busses were being supplied by the offsite electrical grid. The loss of the 2A SSST resulted in the actuation of two reactor coolant pump underfrequency protective relays on two of the 4KV AC busses. This initiated a Unit 2 reactor trip. Both Units were stabilized in Hot Standby. The cause for this event was a single-phase insulating bushing failure on the Unit 1 Main Unit Transformer, which initiated a voltage disturbance on the electrical grid which affected Unit 2. Corrective actions have been initiated at both Units to address identified concerns. There were no safety implications as a result of this event. The reactor protection systems at both Units actuated as designed to place the reactors in safe shutdown conditions (Hot Standby). Engineered Safety Features systems actuated as required upon receipt of the initiation signals.
3341994006 | Beaver Valley 1 | 06/23/1994 | 07/22/1994 | 9407250253 | <strong>Operational Mode Change With an Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 6/23/94, it was identified that a containment isolation valve had exceeded its limiting stroke time on 5/13/94, resulting in a violation of a Technical Specification (TS). The inside isolation valve for cooling water to the control rod drive mechanism coolers,TV-1CC-111D1,is an American Society of Mechanical Engineers (ASME) Class 2 valve. TS 4.0.5 requires that testing of ASME Class 1, 2, and 3 valves shall be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code. On 5/13/94, during Cold Shutdown conditions (Operational Mode 5), the valve was timed at 12.40 sec., and should have been declared inoperable and repaired before the unit entered Hot Shutdown (Operational Mode 4). The excessive stroke time was not identified during the procedure performance or review. Unit 1 entered Mode 4 on 5/18/94, and eventually attained full power. Unit 1 returned to Mode 5 on 6/3/94, and the valve was later tested with a closure time of 12.06 sec. During the procedure review on 6/23/94, it was identified that the valve exceeded the limiting stroke time and required repair before Mode 4 could be entered. It was also identified at this time that the limiting stroke time was exceeded on 5/13/94, and the unit had entered Mode 4 on 5/18/94 with an inoperable containment isolation valve.
3341994007 | Beaver Valley 1 | 06/28/1994 | 07/28/1994 | 9408020182 | <strong>Engineered Safety Feature Actuation - Automatic Start of WR-P-1B</strong><br /><i>Abstract:&nbsp;</i>On 6/28/94, the Reactor Plant River Water pump WR-P-1B automatically started due to low River Water header pressure. This was an unplanned Engineered Safety Feature actuation. Unit 1 was in Mode 5, Cold Shutdown, with the Reactor Plant River Water pump WR-P-1C running. Work was scheduled to be performed on MOV-RW-103A and 103B, the 'A' River Water header to Recirculation Spray Heat Exchanger Isolation valves. When MOV-RW-103B was opened, the piping downstream of it began to fill. The piping had been drained previously for other valve work and not refilled. This resulted in a low River Water header pressure. WR-P-1B was the standby Reactor Plant River Water pump and automatically started, as designed, to correct the low pressure condition. There were no safety implications as a result of this event. <br /><br /> This is being reported, in accordance with 10 CFR 50.73(a) (2) (iv), as an unplanned automatic actuation of an Engineered Safety Feature.
3341994008 | Beaver Valley 1 | 07/19/1994 | 08/18/1994 | 9408240137 | <strong>Reactor Trip Rresulting from Main Transformer Fire Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1994 at 1610 hours, with Unit 1 operating at 100% power, an insulating bushing external flash-over on the Unit 1 Main Unit Transformer initiated an immediate Unit 1 generator/turbine trip followed by subsequent Unit 1 reactor trip. The flash-over of the insulating bushing on the Main Unit Transformer occurred during a transformer fire protection system actuation. Water spray from the fire protection nozzles allowed flash-over from the 'C' phase bushing to its base and grounded fire protection piping and conduit beneath the bushing. This damaged the bushing, caused protection relays to isolate the transformer from the electrical grid, and initiated a generator/turbine trip. The unexpected fire protection system actuation that initiated this event occurred when heat detectors sensed conditions that exceeded their actuation setpoint, even though no fire protection system actuation was required. The suspect heat detectors were subsequently tested and verified to be actuating prematurely. Actions have been implemented to improve main transformer fire protection compatibility with the high voltage transformer application. There were no safety implications as a result of this event. The reactor protection system actuated as designed. The Engineered Safety Feature Systems actuated as required. This report is being submitted in accordance with 10CFR50.73.a.2.iv.
3341994009 | Beaver Valley 1 | 11/03/1994 | 12/02/1994 | 9412140059 | <strong>Operation Prohibited by Technical Specifications - Inadequate Reactor Coolant System Relief Path</strong><br /><i>Abstract:&nbsp;</i>On 11/3/94 with Unit 1 in mode 1 at 100 percent power, a technical review identified that the pressurizer power operated relief valves (PORVs) have a vent diameter of 1.625 inches instead of 2 inches as previously believed. The vent area of a 2 inch diameter opening is 3.14 in**2, while a 1.625 inch diameter opening provides a vent of 2.07 in**2. When a non-isolated RCS cold leg temperature is less than or equal to 329 degrees F, plant Technical Specifications require a reactor coolant system (RCS) vent of greater than or equal to 3.14 in**2 if the over-pressure protection system is inoperable. Believing that PORVs had a 2 inch vent diameter, plant practice during outages was to mechanically block open one PORV to meet the 3.14 in**2 vent requirement. Since the PORVs only have a 1.625 inch diameter vent, the area requirement was not met. The most recent instance of a blocked open PORV was on 5/13/93. <br /><br /> Analysis is ongoing to determine if the 2.07 in**2 vent area of a single PORV has adequate relieving capability to protect the RCS from over-pressure transients. If so, a Technical Specification amendment will be considered to replace 3.14 in**2 with a revised vent requirement. There were no over-pressure transients while PORVs were blocked open; therefore, there were minimal safety implications as a result of this event. This report is submitted in accordance with 10CFR50.73 a.2.i.B.
3341994010 | Beaver Valley 1, Beaver Valley 2 | 11/14/1994 | 12/14/1994 | 9412220108 | <strong>Low Air Pressure in the Control Room Ventilation Damper Seals</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1994, with both Units #1 and #2 at 100% power, a control room pressurization system control air low pressure alarm actuated. This alarm monitors an air system that supplies pressure to the sealing bladders that surround the control room ventilation inlet and exhaust dampers. Upon investigation, an air leak was found at an air system drain trap and system pressure was at 15 psig. It was conservatively assumed that the pressure in the bladders was below the vendor recommended minimum pressure of 20 psig. As a result, at 1610 hours the Control Room Emergency Habitability System (CREHS) was determined to be inoperable. This forced both units to enter Technical Specification 3.0.3. Following investigation, station operators isolated the leak and the system regained pressure. At 1634 hours the CREHS was declared operable and Technical Specification 3.0.3. was exited. Since there were no events in progress that would require the actuation of the CREHS and contingency actions were available to restore the pressure, the safety significance of this event is considered minimal. This event is being reported in accordance with 10CFR50.73.a.2.i.B, as a condition prohibited by the plant's Technical Specification.
3351994001 | St. Lucie 1 | 01/09/1994 | 02/07/1994 | 9402150202 | <strong>Manual Reactor Trip due to the loss of the 1B Steam Generator Feedwater Pump Caused By Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1994 at 1940 hours with St. Lucie Unit 1 in mode 1 at 100% power, the 1B Steam Generator Feedwater Pump tripped. Subsequently the reactor was manually tripped due to decreasing Steam Generator water levels. Emergency Operating Procedure-01, Standard Post Trip Actions, was performed and Steam Generator water levels were regained using the Auxiliary Feedwater System. Emergency Operating Procedure-02, Reactor Trip Recovery was completed, confirming an uncomplicated reactor trip. The plant was stabilized in Mode 3, Hot Standby.<br /><br /> The reactor was manually tripped by the utility licensed operators in anticipation of an automatic reactor trip due to low Steam Generator water level. The cause of the low Steam Generator water level was the 1B Steam Generator Feedwater Pump trip. The most likely cause of the 1B Steam Generator Feedwater Pump trip was a spurious signal from the pump protective low flow switch or its associated time delay relay. The purpose of the low flow switch is to protect the pump in the event of a low flow condition. <br /><br /> Corrective Actions for this event: 1) Instrumentation and Control Maintenance replaced the 1B Steam Generator Feedwater Pump low flow switch, 2) Electrical Maintenance replaced the low flow trip time delay relay, 3) Electrical Maintenance performed electrical continuity and ground checks, 4) Electrical and Instrumentation and Control Maintenance groups replaced the wiring between the low flow switch and the time delay relay, 5) System Engineers monitored Steam Generator Feedwater Pump operation prior to and following unit restart and 6) FPL Engineering has performed an autopsy of the low flow switch and the time delay relay and no specific component failure was identified.
3351994002 | St. Lucie 1 | 01/13/1994 | 02/08/1994 | 9402180076 | <strong>Inadvertant load shed of the 1A3 4160 volt bus due to procedural inadequacy.</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1994 Unit 1 was in mode 1 at 100% power. A surveillance test on the undervoltage relays for the 1A3 safety related bus was being performed. When the utility non-licensed operator initiated the test for the 27-1 relay, the relay did not operate. Per Technical Specification 3.3.2.1., the inoperable relay must be placed in the trip position within one hour. At 0134 hours, as per the surveillance procedure, the relay was placed in the trip position by utility maintenance personnel and an invalid undervoltage actuation signal was initiated. The safety related 1A3 4160 volt bus load shed, the 1A Emergency Diesel Generator started and load sequenced onto the bus. The plant remained in a stable condition throughout the event. Normal off-site power was restored to the 1A3 bus and the 1A Emergency Diesel Generator was secured at 0225 hours. <br /><br /> The root cause of the event was due to a procedural inadequacy in that the procedure did not specify valid initial test conditions prior to assessing the undervoltage relay functionality. A contributing factor was that the 2X-2 relay was subsequently proven to be in the trip position prior to the surveillance. With the 2X-2 relay in the trip position prior to the test, the test circuit is rendered inoperable. This is why the 27-1 relay did not operate during the test. When the 2X-1 relay was placed in the trip position the trip logic was satisfied, and an invalid undervoltage actuation signal was initiated. <br /><br /> Corrective actions for the event are: 1) Electrical Maintenance tested the 2X-2 relay and proved the relay to be functioning correctly at the time of testing, 2) The relay will be replaced during the next refueling outage opportunity and root cause analysis will be performed, 3) Operations implemented a change to test the undervoltage relay test circuit on a daily basis which will detect any undervoltage relays in the trip position, 4) Revise the surveillance procedure to provide instructions on how to confirm relay status prior to and after testing.
3351994003 | St. Lucie 1, St. Lucie 2 | 03/28/1994 | 04/26/1994 | 9405030248 | <strong>Automatic Reactor Trip caused by Manipulation of the Generator Exciter Field Breaker due to Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1994, St. Lucie Unit 1 was at 68% power for Condenser waterbox cleaning activities and Unit 2 was shutdown for a scheduled refueling outage. Utility Electrical Maintenance personnel requested a clearance for the Unit 2 main generator exciter switchgear breaker for preventive maintenance. The chief electrician requesting the clearance went to the work control center and signed on to the clearance which specified that the Unit 2 exciter breaker was in the open position. He then went to the Unit 1 exciter switchgear room and found the breaker closed . Unaware that he was on the wrong unit, the chief electrician tried to verify what he thought was the appropriate position by attempting to open the breaker. The breaker opened and Unit 1 immediately experienced a reactor trip by turbine trip. An uncomplicated automatic reactor trip was verified and Unit 1 was subsequently stabilized in mode 3. <br /><br /> The root cause of the event was due to cognitive personnel error by a member of the utility Electrical Maintenance department in failure to adhere to the clearance procedure. The procedure governing clearance orders provides direction to verify deenergization of the system prior to work proceeding. Station practices restrict personnel other than Operations from manipulating in-service equipment without a valid clearance boundary. A contributing factor was the lack of an identifier on the exciter switchgear housing or the exciter field breaker. <br /><br /> Corrective actions included: 1) Operations stabilized the unit in mode 3. 2) The individual responsible was counseled and disciplined. 3) Reviews will be held with plant maintenance personnel to re-emphasize the foreman's responsibilities in the clearance procedure. 4) Unit 1 and Unit 2 main generator exciter switchgear housings and breakers have been labeled. 5) Additional postings to ensure unit awareness will be installed.
3351994004 | St. Lucie 1 | 04/03/1994 | 05/03/1994 | 9405120067 | <strong>Automatic Reactor Trip caused by Control Element Drive Mechanism Bus Overcurrent and Undervoltage Transient due to Procedural Error</strong><br /><i>Abstract:&nbsp;</i>On April 3,1994 at 0036 hours with St Lucie Unit 1 in mode 1, the Control Element Drive Mechanism (CEDM) bus was deenergized, which tripped the reactor. The utility licensed operators carried out Emergency Operating Procedure-01, Standard Post Trip Actions. Emergency Operating Procedure-02, Reactor Trip Recovery, was completed confirming an uncomplicated reactor trip. The plant was stabilized in mode 3, Hot Standby.<br /><br /> The cause of the plant trip was an overcurrent condition on the CEDM bus caused by the CEDM Motor Generator (MG) sets being out of phase due to a procedural error. temporary change to an approved plant procedure, to isolate the 1A2 4.16 KV bus for repair of the 1A2 4.16 KV Startup Transformer Breaker. The running 1A Emergency Diesel Generator (EDG) switched to the isochronous mode when the 1A3 4.16 KV bus was separated from the grid. The electrical frequency of all components supplied by the 1A EDG then became independent from the B train components. The resulting phase mismatch between the A train MG and B train MG sets caused an overcurrent condition on the CEDM bus. Trip Circuit Breakers (TCBs) 4, 8, 9 and the A MG set output breaker opened as designed on instantaneous overcurrent. The root cause of the procedural error was due to personnel focusing on issues other than the potential for phase mismatch between the MG sets during the review of the temporary procedure change. <br /><br /> Corrective actions for this event: 1) Checks were performed on the CEDM system, MG sets, MG set output breakers, and TCBs with satisfactory results, 2) Training will be provided to reviewers of temporary changes to procedures to reinforce the need for prior Facility Review Group review of complex changes to procedures. 3) the affected breaker and associated components were replaced, 4) Onsite breaker cubicles of large frame breakers were inspected with satisfactory results.
3351994005 | St. Lucie 1 | 06/06/1994 | 06/13/1994 | 9406170200 | <strong>Automatic Reactor Trip caused by 1A Main Transformer Differential Current Trip due to contact with metal facia dislodged from a nearby building During inclement weather.</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1994, at 1508 with Unit 1 at 97% power, during a period of thunderstorm and high wind activity a piece of aluminum facia from a storage building became airborne and struck the Unit 1A Main Transformer. The aluminum facia contacted two phases on the output of the 1A Main Transformer which caused a Main Transformer differential current trip. The Unit 1 Main Turbine tripped from the Main Generator lockout and resulted in an automatic reactor trip. Standard post trip actions were performed, the normal Reactor Trip Recovery procedure was implemented and all safety functions were satisfactory. <br /><br /> The root cause of the reactor trip was due to natural phenomenon in the form of high winds from localized thunderstorm activity. Gusting winds from the thunderstorm tore loose a piece of aluminum facia from a permanent storage building in the vicinity of the 1A Main Transformer and caused it to become airborne and strike the transformer output bushings. <br /><br /> Corrective actions for this event include: 1) Operations stabilized the unit in mode 3. 2) A visual inspection for loose materials on buildings nearby the Main Transformers has been performed with satisfactory results. 3) An internal visual inspection was performed on the Main Generator with satisfactory results. 4) Electrical tests were performed on the Main Generator, Isophase buses, and the 1B Main Transformer with no damage observed. 5) The 1A Main Transformer will be restored and tested prior to ascension to full rated power. 6) The facia on the storage facility was secured using additional fasteners. 7) Additional review criteria will be developed for periodic inspections of buildings in the vicinity of the transformers.
3351994006 | St. Lucie 1 | 10/23/1994 | 12/02/1994 | 9412080150 | <strong>Containment integrity outside of FSAR assumptions under limited circumstances due to design error.</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1994, Unit 1 was in mode 1 operating at 100% steady state power. Differential pressure testing of a motor operated valve resulted in the lifting of a suction supply header relief valve for the Emergency Core Cooling System (ECCS). On 23 October, an engineering evaluation confirmed that this relief valve could lift under certain accident conditions and result in sump inventory loss in excess of design basis into the Reactor Auxiliary Building. <br /><br /> The root cause of the deficiency was design error in the Iodine Removal System. A common header in that system permitted cross train pressurization of an idle Containment Spray pump, pressurization of the ECCS suction header and the potential to lift the relief valve on that header. This design deficiency had existed since the Iodine Removal System was installed in 1978. <br /><br /> Corrective actions: 1) The relief valve path in the Iodine Removal system was isolated. 2) FPL Engineering evaluated the effects of increased pressure in the ECCS suction header with satisfactory results. 3) The two reliefs were then disabled. 4) A satisfactory leak check test of the ECCS suction header system was performed. 5) The Architect Engineer of the Iodine Removal System was informed of the design deficiency. G) A Unit 1 and 2 design review indicated no other similar problem in the ECCS. 7) The common header was physically separated prior to restart from the refueling outage.
3351994007 | St. Lucie 1 | 10/26/1994 | 11/23/1994 | 9411300331 | <strong>Automatic Reactor Trip on Loss of Electrical Load due to Flashover on 240 KV Switchyard Potential Transformer</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1994, Unit 1 was in mode 1 and operating at 100% steady state power. At 1426 utility personnel observed a flash in the area of the 240 KV switchyard near the Unit 1 synchronizing potential transformer. At this time Unit 1 experienced an automatic reactor trip on Loss of Electrical Load predicated by Main Generator differential current condition. Standard post trip actions were performed, the normal Reactor Trip Recovery procedure was implemented and all safety functions were satisfactory. Subsequently a fire was reported at 1445 in the 240 KV switchyard at the affected synchronizing potential transformer outside the protected area. The fire was controlled and allowed to extinguish itself. <br /><br /> The root cause of the failed potential transformer is attributed to an external fault to the transformer across its insulator. This fault was most likely induced by marginal component design insulation level and contributed to by salt contamination of the insulator. <br /><br /> Corrective actions were: 1) Operations stabilized the unit in mode 3. 2) The affected potential transformer has been replaced. 3) Contamination preventive coatings are scheduled for both units synchronizing potential transformers 4) The unit 1 Main Transformers and Isophase bus have been tested. 5) The Main Generator was visually inspected with satisfactory results.
3351994008 | St. Lucie 1, St. Lucie 2 | 11/04/1994 | 04/17/1995 | 9504240135 | <strong>Inadvertent Containment Isolation Signal (CIS) caused by failure of the B Instrument Inverter concurrent with channel D CIS in tripped condition.</strong><br /><i>Abstract:&nbsp;</i>The D channel of Containment Isolation Signal (CIS) had been placed in trip on 9/12/94 per Technical Specification 3.3.2.1. On 11/4/94 St. Lucie Unit 1 was in Mode 6 during a scheduled refueling outage. At 0615 an invalid/inadvertent Engineered Safety Features Actuation Signal (ESFAS) occurred on the CIS. The B Instrument Inverter tripped which deenergized the B channel of CIS. The CIS is a deenergize to actuate ESFAS signal. This resulted in two ESFAS channels (MB and MD) being in the tripped state which made up the required two of four logic for a CIS Actuation. <br /><br /> The cause of the event was CIS channel D being in the tripped state during Mode 6 concurrent with failure of the B Instrument Inverter. The root cause of the Instrument Inverter failure was a failure of the oscillator board. <br /><br /> Corrective actions were: 1) The CIS was reset. 2) The affected radiation detector channel was bypassed as allowed by Technical Specifications and subsequently returned to service after repairs. 3) The inverter was repaired and returned to service. 4) Operating procedures were changed to bypass certain measurement inputs of ESFAS during Modes 5 and 6 as allowed by Technical Specifications.
3351994009 | St. Lucie 1 | 11/22/1994 | 04/07/1995 | 9504190136 | <strong>Inadvertent Safety Injection Actuation Signal/Containment Isolation Signal due to Failed Pressure Transmitters.</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1994, Unit 1 was in mode 5 with utility licensed operators in the process of filling and venting the Reactor Coolant System. At 2137, with Pressurizer pressure at approximately 65 psia the control room operators received alarms indicating a Safety Injection Actuation Signal (SIAS) and a Containment Isolation Signal (CIS) had actuated. The operators noted that C and D channels of Pressurizer pressure were indicating 2300 psia and 1840 psia respectively. All components actuated as required.<br /><br /> The cause of the event was due to the pressure transmitters on C and D channels of Pressurizer pressure drifting high and allowing the SIAS block signal to become removed. The root cause of Pressurizer pressure drifting high is hydrogen gas within the isolating diaphragm (capacitive cell). <br /><br /> Corrective actions: 1) FPL Quality Assurance performed a record search with Rosemount to identify the affected transmitters. 2) Engineering performed an Operability Assessment of the identified transmitters. 3) I&C maintenance personnel will complete replacement of the subject transmitters on both units Pressurizers by 4/30/95. 4) Rosemount notified the NRC under 10 CFR Part 21 that pressure transmitters were supplied to customers with unqualified isolating diaphragm materials. 5) Until further information is available from Rosemount, FPL Quality Control has instituted a requirement for onsite material verification of all safety related Rosemount transmitters during receipt inspection.
3351994010 | St. Lucie 1, St. Lucie 2 | 11/24/1994 | 04/07/1995 | 9504140145 | <strong>Inadvertent B train Engineered Safeguards Features Actuation Signal (ESFAS) due to a deficient Instrument and Control Test Procedure.</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1994 St. Lucie Unit 1 was in Mode 5 during a scheduled refueling outage with Pressurizer level at 36%. At 1412 an inadvertent Engineered Safety Features Actuation Signal (ESFAS) occurred on the B train of the Safety Injection Actuation Signal (SIAS) and on the B train of the Containment Isolation Signal (CIS). The A train of SIAS and CIS had been placed in block per the Instrument and Control test procedure. Therefore, the A train of SIAS and CIS did not inadvertently actuate.<br /><br /> The cause of the event was a deficient Instrument and Control (I&C) test procedure. The Pressurizer pressure measurement bistables are removed to bypass the trip input received during response time testing. The Pressurizer pressure measurement bistables were not removed far enough away from the circuit board to prevent inadvertent contact. When inadvertent contact occurred the bypass was removed and the B train SIAS and CIS components actuated.<br /><br /> Corrective actions were: Operations reset the B train Safeguards Equipment. I&C has revised 'Reactor Protective and Engineering Safeguards System Response Time Testing' to ensure appropriate channels are bypassed by using additional ESFAS bypass keys. I&C has reviewed other applicable procedures to ensure bistables are withdrawn sufficiently.
3361994001 | Millstone 2 | 01/18/1994 | 06/25/1997 | 9707020421 | <strong>Failure of Auxiliary Feed Regulating Valves to Meet Inservice Test Stroke Time</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1994 at 1518 hours, during performance of auxiliary feedwater pump monthly surveillance procedure (SP) 2610A "Motor Driven AFPs and Regulating Valves Operability Test", Auxiliary Feedwater Regulating Valve (AFRV) 2-FW-43A and B both failed to open in the In-Service Test required time. At the time of discovery of this event, the unit was in Mode 1 at 96% power. <br /><br /> The original LER submittal concluded that an unidentified blockage of the valve positioners bleed-off port was the cause of this event. Further investigation concluded that the valves were fully capable of performing their safety function at all times. Therefore, this event is not reportable under the requirements of the LER rule. <br /><br /> This report is being submitted to provide additional information regarding the recurrence of the event, actual event cause, discrepancies identified during the investigation of this event, and final corrective actions. This revision is a complete revision of the original LER.
3361994002 | Millstone 2 | 02/04/1994 | 05/31/1994 | 9406080287 | <strong>Failure to Meet Acceptable Isolation For Class 1E Protection Instrument Channels</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1994, at approximately 1420 hours, an ongoing engineering review revealed that safety grade (1E) electrical isolation requirements were not satisfied. Two non-safety related, inter-connected, pressure control channels powered from separate Class 1E vital instrument buses via Foxboro Spec 200 instrument rack power supplies were not adequately isolated.<br /><br /> On March 10, 1994, at 0900 hours the review identified inadequate isolation between 1E Spec 200 powered reactor coolant cold leg temperature detector control loops and the non - 1E main feedwater control loops. <br /><br /> On April 29, 1994 at 1826, the review identified inadequate isolation between the non-1E reactor regulating system nuclear instrumentation control loops and the 1E Spec 200 Anticipated Transient Without Scram Mitigating System Actuation Circuitry.<br /><br /> The root cause of the events is personnel error due to inadequate interface of design and equipment condition. Design interpretation errors during previous design change processes resulted in the compromising of safety related instrument channels. <br /><br /> Design changes to provide acceptable isolation have been completed.
3361994003 | Millstone 2 | 02/18/1994 | 03/18/1994 | 9403240160 | <strong>Degraded Inverter Synchronizing Circuit Effect on Main Steam Line Break Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>At approximately 0700 hours, on February 18, 1994, an engineering review revealed that degradation of the synchronizing capability between inverters providing normal and alternate 120 VAC to a vital instrument bus had the potential to invalidate an assumption for the main steam line break scenario in containment. The event was determined to be a condition outside the design basis of the plant. Specifically for a main steam line break (MSLB) in containment with loss of a DC bus, credit is taken for transfer between inverters to isolate feedwater flow to a faulted steam generator to limit containment pressure. Degradation of the synchronizing capability between inverters had the potential to inhibit the transfer between inverters if this design basis accident were to occur coincident with sync failure. <br /><br /> A reactor downpower was commenced to allow isolation of Main Feedwater.<br /><br /> Inverter testing identified setpoint drift of the alternate source underfrequency circuit as the cause of intermittent sync failure alarms. An adjustment was made and the synchronizing circuit was declared operational at 1548 hours. Reactor downpower was halted. <br /><br /> The root cause of the event was the failure to completely incorporate administrative restrictions into procedures or Unit Technical Specifications to encompass the assumptions made in the analysis for the main steam line break in containment event.
3361994004 | Millstone 2 | 03/19/1994 | 04/14/1994 | 9404190087 | <strong>Failure to Perform Adequate ASME Leakage Test</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1994, at 1918 hours, with the plant in Mode 1 at 99.8% power, an adequate post work ASME leakage test was not performed on 2- FW-43A, one of two Auxiliary Feedwater Regulating Valves (AFRVs), as required. This event was discovered on March 21, 1994, at 1100 hours during a review of the test results. The test was conducted with the valve in the incorrect, closed position. <br /><br /> The pre-approved test plan requirements, for the valve to be open during leakage testing, were based on an evaluation of the valve's internal components. During the post work valve testing, a change to the test method was made by the Shift Supervisor and Test Coordinator without consulting the test plan originators. This change was based solely on the drawing of the valve included in the Maintenance AFRV overhaul procedure. The drawing showed the valve bonnet exposed to pressure with the valve in both the open and closed position. Therefore, the valve was leak tested using Auxiliary Feedwater pump discharge pressure with the valve closed. On March 21st, during closeout documentation review, the test method change was called into question. The valve vendor was contacted due to questions concerning the Maintenance procedure drawing. It was determined that the drawing was not representative of the valve installed. The valve was immediately declared inoperable, bypassed and isolated. Following re-testing in the open position, and with no leakage detected, the valve was returned to operable status. <br /><br /> The root cause is considered to be a combination of personnel error and procedural deficiency. A personnel error occurred when the Shift Supervisor and Test Coordinator changed the test method without consulting the test plan originators. Although this is not required by procedure, good work practices dictates that the originator and approvers of the test plan be consulted. The inaccurate drawing in the Maintenance Procedure is considered a procedural deficiency. The drawing is being changed to reflect the installed valve. Drawings in other component specific procedures for safety related equipment are to be reviewed for accuracy.
3361994005 | Millstone 2 | 04/01/1994 | 04/29/1994 | 9405090058 | <strong>EBFS Surveillance Requirements Not Satisfied</strong><br /><i>Abstract:&nbsp;</i>At approximately 1430 hours, on April 1, 1994, it was determined that both facilities of the Enclosure Building Filtration System (EBFS) had never been properly tested in accordance with Technical Specification Surveillance 4.6.5.1.a. Technical Specification Surveillance 4.6.5.1.a requires that the EBFS system be demonstrated OPERABLE, in part, 'by verifying that the train operates for at least 10 hours with the system heaters on.' The existing surveillance procedure performs this test with the system operating in Auto, however, the heaters only energize when the moisture control switch senses a relative humidity greater than 70%. Consequently, the heaters would not be energized for the required 10 hour surveillance run if the relative humidity was less than 70%.<br /><br /> This condition resulted in both trains of EBFS being considered inoperable and the plant being outside the Limiting Condition for Operation (LCO) for the EBFS system. The plant entered Technical Specification Action Statement 3.0.3 and Surveillance 4.0.3. A bypass/jumper was processed to jumper out the moisture control switch and to energize the heaters continuously. The 10 hour surveillance run was then performed satisfactorily for both trains of the EBFS system. <br /><br /> The root cause of this event was program failure/personnel error resulting in procedure deficiencies. The failure to account for the actual system operating configuration during development of the surveillance procedure resulted in the failure to incorporate into the surveillance procedure, a method to ensure that the system heaters operate continuously for the required 10 hour surveillance run.
3361994006 | Millstone 2 | 04/07/1994 | 05/02/1994 | 9405100220 | <strong>Entered L-30A to Grease Motor Bearings of F32A</strong><br /><i>Abstract:&nbsp;</i>At 1100 on April 7, 1994, with the plant in MODE 1, it was determined that the plant did not meet the requirements of LCO 3.7.6.1, requiring two independent control room emergency ventilation systems. As a result, Technical Specification 3.0.3 was entered. The unit was in Technical Specification Action Statement (TSAS) 3.7.6.1 for maintenance to be performed on the 'A' Control Room Air Conditioning (CRAC) System Filter Fan (F32A). The 'A' and 'B' CRAC Filter Fans share a common suction plenum. Opening either filter housing door effectively breaches the Control Room Air Conditioning Filtration boundary rendering both trains of CRAC INOPERABLE. The filter housing door was opened to perform maintenance without a dedicated operator as required by plant procedures. The unit logged out of Technical Specification 3.0.3 at 1110, April 7, 1994.
3361994007 | Millstone 2 | 04/12/1994 | 05/11/1994 | 9405170065 | <strong>Emergency Charcoal Filters Tested to Wrong Standard</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1994, at 1715 hours, with the plant in Mode 1 at 100% power, it was identified that the Facility 2 Control Room Air Conditioning (CRAC) and Enclosure Building Filtration System (EBFS) were inoperable because previous charcoal testing was performed to an industry standard different from the standard referenced in the Millstone Unit 2 Technical Specifications. <br /><br /> Upon determining that the testing criteria specified in the Unit 2 Technical Specifications could not be performed, a Notice of Enforcement Discretion (NED) was requested to perform testing of charcoal adsorbers in accordance with ASTM D3803-89, the more stringent procedure for establishing the capability of new and used activated carbon to remove radio-labeled methyl iodide from air streams. The charcoal for all four trains of equipment, two facilities of CRAC and two facilities of EBFS, were tested utilizing ASTM D3808-89 with results greater than 95% efficiency as specified in the proposed change to the Millstone Unit 2 Technical Specifications.
3361994008 | Millstone 2 | 03/29/1994 | 04/28/1994 | 9405040325 | <strong>Procedure Data Recording Error for ESF Response Time Test</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1994, at approximately 1100 hours, with the plant in Mode 1 at 100% power, during a review of response time data records, it was discovered that the data in OPS Form 2604P-2, 'Engineered Safety Features Equipment Response Time Testing,' was recorded incorrectly. On March 29, 1994, the unit's licensing group determined that this event was reportable as a condition prohibited by the plant's Technical Specifications. <br /><br /> On January 11, 1993, Operations Department personnel completed SP 2604P, 'Engineered Safety Features Equipment Response Time Testing.' One of the data sheets associated with this surveillance, OPS Form 2604P-2, calculates the circuit response time by totaling the instrument response time, diesel sequence time, and equipment response time. The operators did not consider the equipment sequencing time when they were calculating 'diesel sequence time' data on the surveillance form. The form requested 'diesel sequencer time' when it should have used the term 'DG start and sequencing time.' <br /><br /> Upon discovery, the response times were recalculated and a new procedure data sheet was completed. The recalculated response times met the acceptance criteria. <br /><br /> This test is performed in accordance with Technical Specifications surveillance requirement 4.3.2.1.3.
3361994009 | Millstone 2 | 04/23/1994 | 06/30/1994 | 9407080186 | <strong>Manual Reactor Trip and Technical Specification Non- Compliance</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1994, at 2100 hours, with the plant in Mode 1 at 99.8% power, a planned shutdown was commenced to repair a degraded Reactor Coolant Pump seal. At 2113 hours, it was identified that Control Element Assembly (CEA) 7-65 not inserting with the other CEAs in its group. The Shift Supervisor had the indication investigated and declared the reed switch CEA position indicator channel for CEA 7-65 inoperable at 2143 hours and logged into the applicable Technical Specification action statement. The downpower had been terminated when the CEA 7-65 indication problem was identified and was recommenced at 2207 hours. <br /><br /> At 0055 hours on April 23, 1994 with reactor power at approximately 25% and CEA Group 7 at approximately 110 steps, the operators began to suspect that CEA 7-65 was at the fully withdrawn position. At 0115 hours the Shift Supervisor declared CEA 7-65 immovable and logged into the applicable Technical Specification action statement. <br /><br /> At approximately 0230 hours, it was identified that the Technical Specification action statement requirements for an immovable CEA had not been performed within the specified time. <br /><br /> At 0250 hours with the reactor in Mode 2 at approximately 10**-5% power and Group 7 CEAs at approximately 90 steps (with the exception of CEA 7-65), power was removed to the Control Element Drive Mechanism (CEDM) for CEA 7-65 and the CEA fully inserted into the core. At 0251 hours the reactor was manually tripped.
3361994010 | Millstone 2 | 05/13/1994 | 06/08/1994 | 9406130254 | <strong>Inadvertent Actuation of ESAS Equipment</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1994 at 0700 hours, with the plant shutdown in mode 5, an inadvertent actuation of the Engineered Safety Features Actuation System (ESAS) took place. The actuation resulted in the starting of the Facility II Charging pump, both Boric Acid pumps,and opening of the Charging Pump Make-Up Bypass Valve 2-CH-514. <br /><br /> The cause of the inadvertent actuation was believed to be Electromotive Force (EMF) noise generated by the resetting action of the actuation relays. This noise was of sufficient level to cause the Diesel Generator load sequencer to resequence which resulted in the starting of the A&B Boric Acid and B Charging pumps and opening of 2-CH-514. <br /><br /> This is being reported pursuant to requirements of paragraph 50.73(a)(2)(iv) reporting any event or condition that resulted in a manual or automatic actuation of any engineered safety feature.
3361994011 | Millstone 2 | 04/27/1994 | 05/27/1994 | 9406030034 | <strong>"B" Emergency Diesel Generator Deficiencies During 18 Month Inspection</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1994 at approximately 1200 hours, with the plant in Mode 5, Reactor Coolant System (RCS) temperature of 110 degrees Fahrenheit and approximately 20 psig, a review of the cumulative problems discovered on the 'B' Diesel Generator (DG) was performed. A conservative conclusion, though not supported by actual engine performance, was that the DG may not have been capable of meeting its action mitigation requirements. A 10CFR50.72 report was conservatively made. This 50.73 report has not resulted in any evidence to support the fact that the DG would not have been able to respond when required but provides the details of the problems discovered during the engine overhaul. <br /><br /> There were no safety implications as a result of this event. Prior to the shutdown, the engine performed satisfactorily with no indications of any problems and there is no evidence that the engine would not have continued to perform properly.
3361994012 | Millstone 2 | 05/05/1994 | 06/01/1994 | 9406080158 | <strong>Design Deficiency in the ESAS Undervoltage Modules</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1994, at 1400 hours, with the plant shutdown in Mode 5, a design deficiency in the Engineered Safety Features Actuation System (ESAS) undervoltage modules that could have prevented automatic undervoltage actuation was discovered. The design deficiency was discovered by an I&C technician who was reviewing previous undervoltage module failures. <br /><br /> The safety consequences of this event have been determined to be negligible since the Engineered Safety Features Actuation System (ESAS) is slightly degraded, but operable. <br /><br /> This is being reported pursuant to requirements of Paragraph 50.73(a)(v)(D), any event or condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident.
3361994013 | Millstone 2 | 05/10/1994 | 08/16/1994 | 9408240197 | <strong>Technical Specification Surveillance not performed within required time interval</strong><br /><i>Abstract:&nbsp;</i>On 5/10/94, at 1200 hours, with the plant in Mode 5, 107 degrees F, during a review of surveillances, the Operations Assistant discovered that an 18 month surveillance had not been performed within its required surveillance period. SP 2614D, 'Auxiliary Exhaust Actuation Signal (AEAS) Operability Determination,' was last performed on 6/20/92. This surveillance verifies proper positioning of AEAS associated equipment in response to a Spent Fuel Pool Area high radiation signal. Technical Specification surveillance requirement 4.0.2 allows a maximum extension time not to exceed 25% of the surveillance time interval (18 Months x 1.25), therefore the surveillance was required to be performed by 5/5/94. The AEAS surveillance was immediately performed and was accepted as satisfactory.
3361994014 | Millstone 2 | 05/10/1994 | 06/08/1994 | 9406160272 | <strong>Missing Support on Service Water Pipe</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1994 at 1500 hours, with the plant shutdown in Mode 5, an overstress condition was discovered in a common discharge line from the vital DC switchgear room coolers. The overstressed condition, which existed in the seismic load case only, was discovered while performing piping stress analysis for a future plant design modification. <br /><br /> The safety consequences of this event have been determined to be negligible. An operability evaluation demonstrated that alternate cooling provisions in existing plant operating procedures were adequate to ensure adequate room cooling water would be available following a seismic event. The missing support has been installed.
3361994015 | Millstone 2 | 05/19/1994 | 06/17/1994 | 9406240059 | <strong>Automatic Auxiliary Feedwater Initiation Circuit Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>At approximately 1424 hours on May 19, 1994, an engineering review revealed that the Automatic Auxiliary Feedwater Initiation (AAFI) control circuit does not meet the single failure criterion. The single failure identified was a short circuit across two conductors of the actuation relays associated with the initiation logic matrix. <br /><br /> The root cause of the event is personnel error due to inadequate interface of design and equipment condition. A design interpretation error during the installation of the AAFI design resulted in the compromising of both trains of the AAFI system.<br /><br /> No immediate operator actions were required. A failure modes evaluation concluded that the conductor to conductor short circuit failure was a low probability event to preclude actuation of the AAFI. <br /><br /> As corrective action, a design change is being evaluated for possible implementation during the refueling outage currently scheduled for the Fall of 1994. <br /><br /> To prevent recurrence, a lessons learned presentation on this event will be provided to engineering personnel.
3361994017 | Millstone 2 | 06/01/1994 | 02/09/1995 | 9502140381 | <strong>Inadvertent ESAS Actuations</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1994 at 2212 hrs, with the Plant in mode 5 with the RCS temperature at 135 deg. F and pressure at 170 psia, an unanticipated actuation of the Enclosure Building Filtration Actuation System (EBFAS) and Control Room filter fan occurred. The event occurred during the deenergizing of the Engineered Safety Features Actuation System (ESAS) Facility 2 actuation cabinet. <br /><br /> This is to be reported pursuant to requirements of 10CFR50.73 (b)(2)(ii), reporting any event or condition that results in a manual or automatic actuation of any engineered safety feature. <br /><br /> Corrective action consisted of revising operations procedure 2384 to require that fuse replacement be accomplished under a detailed work plan. A detailed work plan will come in the form of a work order with a procedure or component manipulation form attached to provide instruction and sequence for fuse removal and replacement. In addition, the ESAS actuation cabinet power supplies are being replaced during the current refueling outage.
3361994018 | Millstone 2 | 06/02/1994 | 07/01/1994 | 9407130060 | <strong>Design Deficiency in the Control Room Ventilation Cleanup System</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On June 2, 1994 at 1612 hours, with the plant in Mode 5 at 0% power, it was identified that the filter fans (F-32A and F-32B) for Control Room Air Conditioning System (CRAC) appeared to be feeding the opposite supply train, i.e. F-32A supplied the B-train and F-32B supplied the A-train. In this configuration, there was potential to supply the control room with less than the Control Room Habitability analysis assumption of 2500 CFM of filtered air during accident situations. Plant Design Change 2-035-94 was implemented on June 5, 1994 to swap the power leads for F-32A and F-32B as well as their dampers and associated limit switches, thus correcting this situation. Subsequently, it was further identified that: 1) due to the original system design, proper system function could not be ensured for all accident conditions without operator action and 2) the radiological dose analysis assumed that control room operators would don self contained breathing apparatus (SCBA) within 20 minutes of event initiation and that the CRAC purge system would be initiated 30 minutes after the event initiation. These requirements were not fully addressed in plant operating procedures. These discrepancies were resolved with a combination of credited operator actions and re-analysis with modified assumptions which included using new ICRP-30 thyroid dose conversion factors and reduced airborne activity assumptions. information was transmitted to the NRC staff in a letter dated June 13, 1994.
3361994019 | Millstone 2 | 07/26/1994 | 06/07/1996 | 9606180130 | <strong>Reactor Coolant Pump Motor Oil Leaks</strong><br /><i>Abstract:&nbsp;</i>At 0600 on July 27, 1994, with the plant in Mode 1 at 100% power, a power reduction was started in response to a Reactor Coolant Pump (RCP) oil system low flow alarm. A containment entry was made to inspect the RCP motor by maintenance and engineering personnel. While no smoke or fire was observed, accumulated oil was noted on and around the 'A' and 'D' RCPs. Upon completion of the inspections, a decision was made to continue the ongoing power reduction to shutdown and the plant entered Mode 5 at 1932 on July 28, 1994. <br /><br /> An assessment was made which concluded the RCP oil collection system was not in compliance with Appendix R since it did not collect oil from all potential pressurized leakage sites. A prompt report was made pursuant to 10CFR50.72. <br /><br /> Revision 1 of this LER provides additional information regarding the leakage of oil from six of the eighteen high pressure hoses internal to the upper reservoir of the 'A' RCP oil system. Evidence suggests that the hoses were degraded due to the use of an inappropriate chemical solvent during a motor overhaul performed by a vendor in December of 1991. The RCP motor overhaul specification has been modified to restrict the use of chemical solvents by vendors performing the motor overhauls.
3361994020 | Millstone 2 | 07/22/1994 | 07/18/1995 | 9507210182 | <strong>DG Fuel Oil Supply Less than IEEE Standard</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1994, at 1605 hours, the plant was in model 1, 100% power, when the determination was made that the plant was not in compliance with a design document. A recently revised engineering calculation determined the inventory (24,000 gallons) of safety-related emergency diesel generator (EDG) fuel oil was sufficient to support EDG operation for 6.17 days. fuel inventory be maintained on-site. An operability determination evaluated the situation and determined the EDGs were operable based on compliance with Technical Specifications. Conservatism exist in the now calculation and Millstone 2 has an underground storage tank that has two pumps (powered from vital power supplies) that automatically make-up to the 24,000 gallon technical specification supply. Additionally, emergency response procedures require that we evaluate the need to order additional fuel from off-site sources within four hours following the accident. <br /><br /> The root cause of the event is increasing the EDG loading scheme without re-evaluating the fuel consumption rates and the more conservative methods and assumptions used for calculating the fuel oil supply today versus the methods and assumptions used during original plant design. The original calculation utilized a best estimate methodology.<br /><br /> Beyond reporting, no operator actions were taken as a result of this event since the amount of fuel oil available complies with the technical specifications, and is sufficient to provide emergency power until fuel oil supplies can be replenished from off-site sources. <br /><br /> A technical specification change has been submitted that clarifies the fuel oil supply issue.
3361994021 | Millstone 2 | 06/15/1994 | 07/11/1994 | 9407190063 | <strong>Non-Seismic Shielding Installed Around 3/4" Body Drain Line 2-SI-709</strong><br /><i>Abstract:&nbsp;</i>At 1220 hours on June 15, 1994, with the plant in mode 3 at 0% power (532 degrees F, 1500 PSIG), it was determined that a shielding installation adjacent to valve 2-SI-709 would result in unacceptable stresses during a design basis earthquake.<br /><br /> The shielding had been installed without processing a temporary shielding request. Upon determination of a seismic concern the installation was immediately removed.
3361994022 | Millstone 2 | 06/22/1994 | 07/22/1994 | 9407260332 | <strong>Two Hydrogen Analyzers Inoperative</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1994 at 0503 hrs with the Plant in mode 1, monthly surveillance tests were started on the plants two hydrogen analyzers. The first analyzer successfully passed its surveillance test criteria. The second analyzer failed its surveillance test and was considered inoperable from the time of its last surveillance due to the nature of the failure. Because a Technical Specification Action Statement was entered to perform the surveillance on the first analyzer, the Supervisory Control Operator (SCO) made a conservative decision to report both analyzers inoperable during the time the surveillance was being performed on the first analyzer. <br /><br /> This is being reported pursuant to requirements of 10CFR50.73(a)(2)(vi) redundant equipment in the same system was not available to perform the required safety function.
3361994023 | Millstone 2 | 07/25/1994 | 08/24/1994 | 9408310097 | <strong>Inadvertent Start of "B" Charging Pump</strong><br /><i>Abstract:&nbsp;</i>On July 25, at 0147 hours, with the plant in mode 1, 100% power, operations personnel were changing the Charging Pump running and starting sequence by moving the selector switch (Charging Pump Backup Control Switch) from position 1&2 to 2&3. The selector switch provides the control of which Charging Pump is running, and which pump is the first and second to start automatically on a low level in the Pressurizer. <br /><br /> Due to a failure of the selector switch, when the operator changed the switch position, the Charging Pumps did not respond as required and there was an unexpected automatic start of one of the Charging Pumps. This failure effected the normal level control circuit, and had no affect on the normal ESF response of the Charging Pumps.<br /><br /> The root cause of the event is a worn detent mechanism within the General Electric SB - 1 control switch. the switch contacts properly, and in this case two Charging Pumps did not receive a stop signal. To prevent a recurrence, the switch will be replaced during the upcoming refueling outage. The selector switch has been caution tagged to alert operators that the switch position and performance, must be verified, due to the worn detent mechanism. <br /><br /> There are no other similar events.
3361994024 | Millstone 2 | 09/22/1994 | 10/17/1994 | 9410270295 | <strong>Two Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1994, at 1347 hours with the plant in mode 1, 100% power, the B Diesel Generator (DG) was out of service for corrective maintenance due to a service water leak. Preparations were in progress to perform a 'quick start' on the A DG to prove its operability when the DG disable alarm was received in the control room as the fuel rack was being verified reset. No local alarms were received. The alarm was reset. This action was repeated with the same result. On the third attempt no alarms were received. On the fourth attempt the DG disable alarm sequence as above repeated itself. The A DG was declared inoperable from the time of the original event. The alarms were reset and the pre-start continued with no unusual events. The 'quick start' was performed without incident and the A DG was declared operable.
3361994025 | Millstone 2 | 09/07/1994 | 10/07/1994 | 9410140242 | <strong>Seismic Monitor Channel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1994, at approximately 1300 hours with the Plant in Mode 1, at 100% power, it was determined that a Special Report required by Technical Specification 3.3.3.3, addressing a seismic monitor recorder that had been inoperable for greater than 30 days, had not been submitted. The seismic monitor had been found to be inoperable on July 14, 1994, and subsequently it was determined that it was likely that it has been inoperable since the previous surveillance test performed on June 13, 1994. The Plant Technical Specifications requires that an inoperable seismic monitor channel must be returned to service within 30 days or a Special Report submitted within the next 10 days. The recorder was immediately repaired, however, the need to submit a Special Report was not recognized at this time. Therefore, based on the information available from the subsequent investigation, the plant classified this event as an operation prohibited by Technical Specifications since the Special Report was not submitted within 10 days. <br /><br /> This is being reported pursuant to requirements of 10CFR50.73(a)(2)(i)(B) any operation prohibited by Technical Specifications.
3361994026 | Millstone 2 | 08/25/1994 | 02/06/1995 | 9502140318 | <strong>Vital 120 Volt AC System Degradation</strong><br /><i>Abstract:&nbsp;</i>At approximately 1622 hours, on August 25,1994, with the plant in Mode 5, at 0% power, an determination concluded that vital 120 VAC buses VA10 and VA20 were inoperable with the Hydrogen Analyzers energized from their respective buses due to exposure to potential High Energy Line Breaks (HELBs) from Auxiliary Steam lines in the same room. These HELBs could cause consequential short circuits which would adversely affect the vital buses due to the electrical characteristics of the inverters, static switches, and circuit breakers. With the Auxiliary Steam system isolated, VA10 and VA20 were considered operable on August 26, 1994. On August 30, 1994, with the plant in Mode 3, VA10 and VA20 were again declared inoperable due to an additional HELB concerns from a potential Main Steam Line Break (MSLB) scenario. A design change was implemented to install fuses which were intended to permanently protect the vital 120 VAC buses from HELB induced short circuits in the energized Hydrogen Analyzers. <br /><br /> A recently completed fuse clearing study invalidated two key assumptions previously relied upon. A design change has been initiated to address isolation requirements as a result of the study. This design change will be completed during the current refueling outage.
3361994027 | Millstone 2 | 09/03/1994 | 08/20/1996 | 9608300065 | <strong>Channel "B" Linear Range NI Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1994, at 0426 hours, with the plant in mode 1, at approximately 5% power, it was determined that the Channel 'B' Linear Range Nuclear Instrument (NI) was inoperable when the plant changed operating modes from mode 2 to mode 1. Instrument technicians called in to investigate, found High Voltage (HV) Connector J6 disconnected from its jack on the back of Channel 'B' Drawer. If A is not connected, the High Voltage supply to the ion chambers is interrupted and the drawer output will fail low. This event is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B), 'any operation or condition prohibited by the plant's Technical Specifications.'<br /><br /> The cause of this event is personnel error. It was concluded that HV Connector A on the Linear Range NI Power Drawer was not properly reconnected following maintenance. It is believed that subsequent and repeated opening and closing of the Drawer caused the connector to loosen. Initial corrective actions reconnected HV Connector J6 and ensured proper operation of the Channel 'B' Linear Range NI.<br /><br /> This supplement 1 of this LER clarifies the cause of the event, and modifies the corrective action. <br /><br /> There were no automatic or manually initiated safety systems activated as result of this event.
3361994028 | Millstone 2 | 09/23/1994 | 10/17/1994 | 9410270300 | <strong>Technical Specification Surveillance Not Performed Within Required Time Interval</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1994, at 1105 hours, with the unit in Mode 1 at 100% power, it was discovered that surveillance procedures SP 2605C, 'Containment Leak Test, Type B,' SP 2605D, 'Containment Leak Test, Type C,' and SP 2605E, 'Containment Personnel Air Lock Leak Test,' were not performed for 69 of 91 containment isolation penetrations within the time interval specified in Technical Specification 4.6.1.2.d. These three procedures verify individual and combined leakages for all containment isolation valves (CIVs) and Type B penetrations are maintained within Technical Specification and Appendix J limits. Local leak rate tests (LLRTs) are required to be performed at intervals no greater than 24 months from the previous test. <br /><br /> The cause of the missed surveillances was due to the historical practice of assuming that the 24 month LLRT surveillance interval began after all LLRTs were completed from the current refuel outage. Corrective action will involve identifying a separate due date for each Appendix J CIV and Type B penetration in the surveillance tracking program and documenting an interpretation of Appendix J Technical Specification requirements.
3361994029 | Millstone 2 | 10/03/1994 | 11/01/1994 | 9411090181 | <strong>Stack Gaseous Radiation Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0951 on October 3, 1994, with the plant shutdown in Mode 4, instrument and Control technicians secured sample flow to the Stack Gaseous and Particulate Radiation Monitor Skid to support preventive maintenance on the Particulate Radiation Monitor. It was not recognized that during this work that flow would be lost to both radiation monitors on the skid. The Technical Specification Action Statement (TSAS) for both channels being inoperable was not entered. No grab samples were taken within 12 hours pursuant to the requirements of TSAS 3.3.3.10, Table 3.3-13, ACTION 1. Alternate grab sampling of gaseous radionuclides was initiated 29 hours after flow was secured. No additional operator actions were required as a result of this event. No automatic or manual safety system actuations were initiated.
3361994030 | Millstone 2 | 10/01/1994 | 10/28/1994 | 9411100241 | <strong>Millstone Unit 2 Main Steam Safety Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1994, at 1030 hours, the plant conducted routine main steam safety valve setpoint testing as required by Technical Specification Surveillance 4.7.1.1. Plant conditions were as follows: Hot Standby (Mode 3), 0% power, 521 degrees Fahrenheit, and 2273 psia. Ten of the sixteen valves failed to lift within the required tolerance of +/-1% on the initial actuation. Of the ten that failed, eight had setpoints below the required tolerance and two had setpoints above the required tolerance. Accident analyses have been completed that demonstrate acceptable results for up to 3% setpoint drift on all valves. Nine of the ten failed valves were within 3% of their nominal setpoint and therefore, are bounded by these analyses. One valve was 3.5% below its nominal setpoint. The Steam Generator Tube Rupture event was reviewed with respect to this valve. This review indicated that there would be no significant impact. Six Main Steam valves were sent to an outside facility for routine maintenance and adjustment. Three of the ten valves that failed the initial test were included in this group. The remaining seven valves either passed subsequent tests without adjustment or were adjusted to acceptable setpoints. The plant complied with the requirements of Technical Specification Action Statement 3.7.1.1.a. The cause of setpoint drift is unknown.
3361994031 | Millstone 2 | 10/18/1994 | 11/16/1994 | 9411250196 | <strong>Fire Watch Not Established</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1994, at 2100 hours, with the plant in mode 6, a fire watch was not established within the A Diesel Generator room for a period of five hours. The fire watch was required to compensate for two fire doors blocked open to facilitate exhaust ventilation for welding. Upon discovery by Operations, Technical Specification Action Statement 3.7.10.a.2 was entered and a fire watch was established in the A Diesel Generator room.<br /><br /> Welding in the adjacent Enclosure Building Filtration System (EBFS) area was then secured, the ventilation removed, the doors shut and the Technical Specification Action Statement was exited.
3361994032 | Millstone 2 | 10/28/1994 | 11/22/1994 | 9412010246 | <strong>Post Incident Recirculation Fan Flow Below Design</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1994, at 0945 hours, with the plant in Mode 6 at 0% power, it was determined that neither Facility 1 nor 2 Post Incident Recirculation (PIR) fans met the required air flow rate per the design basis of Millstone Unit 2. <br /><br /> The root cause is unknown but is probably related to age, changes in test methodology or testing equipment accuracies. The first air flow test was performed in October 1974 and the second test performed in October 1994.
3361994033 | Millstone 2 | 10/31/1994 | 11/30/1994 | 9412060232 | <strong>Loss of Containment Integrity Associated with Outage Equipment Door</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1994, at 0945 hours, with the plant in Refueling (Mode 6), a loss of containment integrity was discovered during the course of irradiated fuel movement within containment. The outage equipment door was found to not be leak tight. A faulty ventilation damper controller is suspected to be the root cause of the pressure increase which caused the door to leak. <br /><br /> All fuel movement was stopped in accordance with Technical Specification Action Statement 3.9.4. The permanent equipment hatch was installed, ventilation lineups were investigated and fuel movement resumed the following day.
3361994034 | Millstone 2 | 11/01/1994 | 11/29/1994 | 9412070123 | <strong>Spent Fuel Pool Door Opened (Blowdown Room) While Fuel Was Being Moved in SFP</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1994, at approximately 2250 with the plant in Mode 6, the Reactor core was being offloaded. A scheduled Fire Watch turnover was needed in the Blowdown Room, which is accessed via the spent fuel pool area. Fuel handling operations were suspended by the Reactor Engineer (RE) while the fire watch relief was performed. When a longer than normal time had passed, the RE on the Spent Fuel Pool (SFP) floor sent the on duty Health Physics (HP) Technician to locate the fire watch people. HP could not locate the fire watch personnel, and reported this to the RE. Without determining the location of the fire watch personnel, the RE then directed the fuel handler on the Spent Fuel Handling Machine (SFHM) to proceed with moving fuel. This required meeting Technical Specification 3.9.14 for spent fuel pool area ventilation, which requires that the SFP area doors be closed. While a fuel bundle was being moved, one of the Fire Watch individuals exited the Blowdown Room, violating the SFP Area closure requirements during fuel movement. The fuel assembly being moved was placed into its storage location (the closest secure location at the time of the event), and fuel movement activities were suspended until proper conditions could be reestablished. Additional controls to prevent further breaches of the ventilation boundaries were implemented, and fuel activities were restarted.
3361994035 | Millstone 2 | 11/02/1994 | 12/02/1994 | 9412060226 | <strong>Failure to Post a Continuous Fire Watch</strong><br /><i>Abstract:&nbsp;</i>On November 2,1994, at approximately 0800, the plant was in Mode 6 and fuel offload was being performed. A discovery was made that the type of fire watch established for a breached electrical penetration did not satisfy the Technical Specification requirements. A roving fire watch was established when the requirement was for a continuous fire watch. Upon discovery, a continuous fire watch was established.
3361994036 | Millstone 2 | 11/04/1994 | 11/29/1994 | 9412070127 | <strong>Missed Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1994 at 1600 hours with the plant in Mode 6, during a review of the Millstone Unit 2 Operations Department Surveillance Data program, the Operations Assistant discovered that an 18 month surveillance of fire protection coating inspection had not been performed within its required period. Once the problem was identified, operator action was to perform and complete the surveillance on November 5, 1994.
3361994037 | Millstone 2 | 11/20/1994 | 12/20/1994 | 9412280245 | <strong>Battery Charger Surveillance</strong><br /><i>Abstract:&nbsp;</i>On November 20,1994, with the plant in a defueled condition, during a review of surveillance, plant performance records, personnel discovered that the 18 month surveillance for the 'A' Battery Charger capacity had not been performed within its required surveillance period. Maintenance Surveillance Procedure, 2736G, 'Battery Charger Capacity Test,' was last performed on November 20, 1992. Technical Specification surveillance requirement 4.0.2 allows a maximum extension time not to exceed 25% of the surveillance time interval (18 months x 1.25), therefore the surveillance was required to be performed by October 3, 1994. Since the 'A' Battery Charger is scheduled for replacement during the current refueling outage and it is not required by Technical Specifications due to the current defueled condition, the 'A' Battery Charger remains available and in service.
3361994038 | Millstone 2 | 10/26/1994 | 11/23/1994 | 9412010351 | <strong>Containment Penetrations Not Adequately Local Leak Rate Tested</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1994, at 1640 hours, with the unit in mode 6 for refueling outage 12, it was identified that local leak rate testing was not adequately performed on two containment penetrations. This condition was identified as a result of a review of the LLRT Program initiated prior to the start of the refueling outage. The surveillance procedure, SP 2605D, should have included the flange seal of the rupture disks associated with these penetrations during local leak rate testing. The unit had historically removed the rupture disks and inserted temporary blank flanges prior to performing the LLRT on these two containment penetrations. The flange seal is part of the containment penetration boundary and must be tested to comply with Appendix J requirements.
3361994039 | Millstone 2 | 10/31/1994 | 03/07/1996 | 9603210059 | <strong>Components Not Included in the Inservice Test Program</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1994, at 1100 hours, with the unit in mode 6 for its refueling outage, it was identified during a review of the Inservice Test (IST) Program that some components were potentially not included in the Millstone Unit 2 (MP2) IST Program. Since this program review has not been completed, a conclusive determination for their inclusion in the program has not been verified although it is expected that some will be identified as omissions from the program. For those components which are identified as omissions, the applicable testing required under Section XI of the ASME Boiler and Pressure Vessel Code would not have been performed as required by Technical Specification 4.0.5. Revision 01 of this LER documents the completion of the review, which identified one valve that needed to be added to the program and seventeen valves that required testing beyond that specified in the program.
3361994040 | Millstone 2 | 12/06/1994 | 09/11/1995 | 9509180230 | <strong>Ventilation Design Deficiency Affecting Enclosure Building Integrity</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1994, at 2223 hours, with the plant defueled, it was determined that a release path existed from the Enclosure Building that would allow for a direct discharge to atmosphere following a Loss of Coolant Accident (LOCA) that would not receive charcoal filtration. <br /><br /> Further investigation revealed that there were other potential single failure scenarios that could have resulted in a release path from the Enclosure Building that would allow a direct discharge to the atmosphere without charcoal filtration following a LOCA if Enclosure Building Purging operations were being performed. <br /><br /> The root cause is a deficiency in the original design.
3361994041 | Millstone 2 | 12/08/1994 | 01/06/1995 | 9501120009 | <strong>Turbine Building 45'-6" Cable Vault Floor Leak to 31'-6" 4160 Volt Vital Switchgear Room</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1994, at 1600 hours, with the plant defueled, a review of an event which occurred on October 20, 1994, indicated a loss of electrical facility separation due to the degraded condition of the floor drains and leakage collection systems. <br /><br /> Due to the clogged drain and the deteriorated cofferdam and floor in the 45'-6' cable vault, water draining from the 54'-6' 4160 volt switchgear room (Z1 facility) leaked through to the 31'-6' 4160 volt switchgear room (Z2 facility). This leak path creates a loss of separation of facilities (required by 10CFR50, Appendix A, Criteria 17 Electric Power Systems and IEEE 308-1971, Standard Criteria for Class IE Systems) which allows a common mode failure to remove redundant facilities from service. Design modifications are being prepared to correct the deteriorated cofferdam and floor, and repairs will be completed prior to startup.
3361994042 | Millstone 2 | 12/22/1994 | 01/18/1995 | 9501270247 | <strong>Installation of Unqualified ESAS Power Suppliers</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1994, at 1600 hours, with the plant defueled, a Procurement Engineer, while reviewing the status of procurement related nonconformance reports, discovered that Engineered Safety Features Actuation System (ESAS) cabinet drawer power supplies had been installed from. 1988 to 1994 without proper qualification as class 1E.<br /><br /> The root cause is a lack of procedural detail for making notification to the plant when inspection at a supplier's facility identifies a potentially significant quality problem that could affect installed equipment. <br /><br /> The power supplies were replaced as part of the 1994 refueling outage. The organization responsible for assessing vendor activities has been relocated to the plant and works to plant procedures for reporting incidents which affect plant equipment. Additionally, a procedure has been specifically developed by this organization for evaluating quality problems with supplier's programs which may affect installed equipment.
3361994043 | Millstone 2 | 12/30/1994 | 02/23/1995 | ML09152054 | <strong>Charcoal Filter Iodine Removal Efficiency Failure Associated With Enclosure Building Filtration and Control Room Air Conditioning</strong><br /><i>Abstract:&nbsp;</i>On December 2,1994, with the plant defueled, charcoal samples from both the Facility 1 and Facility 2 Enclosure Building Filtration System were sent to an independent laboratory to be analyzed for Iodine removal efficiency. The laboratory test report, which identified unsatisfactory results was reported to the utility on December 30, 1994. In a similar event on December 17, 1994, with the plant defueled, charcoal samples for the Facility 1 Control Room emergency filtration system were sent to the same laboratory to be analyzed for its Iodine removal efficiency. The laboratory test report which identified unsatisfactory results was reported to the utility on January 9, 1995. Previously, in April of 1994, samples from these filtration systems had been tested with satisfactory results. <br /><br /> The root cause of the Enclosure Building Filtration system charcoal efficiency reduction has been attributed to exposure to cleaning and painting chemicals.
3381994001 | North Anna 1, North Anna 2 | 01/22/1994 | 02/21/1994 | 9403030157 | <strong>Voluntary Report - Emergency Diesel Generator Fuel Oil Transfer Pumps Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1994, at 0038 hours, with Units 1 & 2 operating at 100 & 95 percent power, respectively, (Mode 1) the fourth of eight Emergency Diesel Generator (EDG) fuel oil transfer pumps was declared inoperable. The inoperable pumps included one pump to the Unit 1 H EDG, both pumps to the Unit 1 J EDG, and one pump to the Unit 2 H EDG. Technical Specification (TS) 3.8.1.1 requires a separate fuel oil system to be operable for each EDG. Subsequently, the 1J EDG was declared inoperable and the appropriate TS action was entered. The TS Action on 1J EDG was cleared on January 22, 1994 when the IJA fuel oil transfer pump were declared operable. This event is being reported as a Voluntary Licensee Event Report due to possible industry impact. <br /><br /> The primary cause of the inoperable FO transfer pumps was improper greasing of the pump motor bearings. in addition, the severe cold weather (i.e. minus 2 degrees Fahrenheit on January 19, 1994, to 23 degrees Fahrenheit on January 21. 1994) was also a contributing factor in that it caused additional torque on the motors due to grease hardening. <br /><br /> No significant safety consequences resulted from this event because both Unit 2 EDGs and one Unit 1 EDG were available throughout this time period. The second Unit 1 EDG was returned to operable status within the time required by the TS Action. Therefore, the health and safety of the public were not affected at any time during this event.
3381994002 | North Anna 1, North Anna 2 | 04/20/1994 | 05/24/1994 | 9405270186 | <strong>Postulated Failure Of High Head Safety Injection Pump Discharge Check Valve</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1994, with Units 1 & 2 in Mode 1 (100 percent power) a concern that the single failure of the "A" charging pump discharge check valve failing to seat could prevent adequate High Head Safety Injection (HHSI) flow to the reactor core was identified. A Safety Injection (SI) signal automatically starts the "B" and "C" charging pumps and trips the "A" charging pump if it is in operation. If the discharge check valve for the "A" charging pump fails to close this could result in a major portion of the SI flow being diverted through the idle "A" charging pump. This scenario was identified during a review of the Unit 2 "C" charging pump discharge check valve, 2-CH-208, which momentarily failed to seat during a charging pump swap over evolution on April 18, 1994. This event is being reported as a Voluntary Licensee Event Report due to possible industry impact. <br /><br /> The cause of 2-CH-208 to momentarily hold open could not be positively determined during subsequent inspections. <br /><br /> No significant safety consequences resulted from this event because sustained failure of a check valve to close simultaneously with a Design Basis Accident was determined to be improbable. Therefore, the health and safety of the public are not affected by this event.
3381994003 | North Anna 1, North Anna 2 | 04/26/1994 | 05/17/1994 | 9405230288 | <strong>Containment Hydrogen Analyzer Inoperable Due To A Failed Tubing Fitting</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1994, at 0815 hours, with both units in Mode 1, 100 percent power, a seven day action was entered per Technical Specification (TS) 3.6.4.1 to leak check piping associated with the containment hydrogen analyzers as required by TS 6.8.4. At approximately 1100 hours a leak was discovered on the Unit 1 containment hydrogen analyzer inlet sample fitting. The fitting was inspected and noted to be tight, and required above normal tightening force to stop the leak. System leakage testing was completed and the TS action was cleared at 1612 hours on April 26, 1994. It was postulated that this condition had existed since the last performance of an instrument calibration procedure on February 2, 1994. This condition rendered the analyzer inoperable for that time period. As such, the allowed 30 day outage time for one of the shared analyzers required by TS 3.6.4.1.a was exceeded. The condition is prohibited by TS and is reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of the event is mechanical failure of the fitting resulting in an inoperable analyzer. <br /><br /> This event posed no significant safety implications since alternative means were available to sample containment hydrogen levels throughout the event. Therefore, the health and safety of the public were not affected at any time.
3381994004 | North Anna 1 | 06/21/1994 | 07/20/1994 | 9407250027 | <strong>Missed Surveillance On Control Rod Position Verification Due To Computer Points Being Off Scan</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1994, at 0820 hours with Unit 1 operating at 100 percent power (Mode 1) sixteen individual control rod position analog computer points were discovered 'off scan' during performance of the weekly station process computer point review. With these points 'off scan' the automatic rod position deviation monitor, used to satisfy Technical Specification (TS) 3/4.1.3.1.1, could not perform its intended function of comparing the rod positions against their group step counter demand positions. As such, the rod position deviation monitor was inoperable and the rod position surveillance frequency was not increased to once every four hours as required by TS 4.1.3.1.1. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B). <br /><br /> Cause of the missed surveillance was due to the analog computer points for control rod position values being off scan. <br /><br /> No significant safety consequences resulted from this event because the control rods were able to perform their safety function throughout the event and the ability to move control rods was never compromised. Therefore, the health and safety of the public were not affected at any time during this event.
3381994005 | North Anna 1 | 09/09/1994 | 10/06/1994 | 9410120251 | <strong>ESF Actuation When Main Feedwater Pumps Tripped Due To Steam Generator High High Level</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1994, at 0020 hours with Unit 1 operating at 8 percent power (Mode 1), and being removed from service for a refueling outage, an Engineered Safety Feature (ESF) actuation occurred. A High High level in the 'A' Steam Generator (S/G) resulted in isolation of the main feedwater (MFW) system. As a result, the auxiliary feedwater (AFW) pumps automatically started. A four hour report was made to the NRC at 0142 hours pursuant to 10 CFR 50.72 (b)(2)(ii). This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) as an automatic actuation of ESF components. <br /><br /> The High High level in the 'A' S/G was due to an unexpected turbine trip caused by a failed reheat pressure transmitter. Automatic actuation of the AFW pumps was due to the MFW system isolation. <br /><br /> No significant safety consequences resulted from this event because core cooling was maintained and all safety systems responded appropriately. Therefore, the health and safety of the public were not affected at any time during this event.
3381994006 | North Anna 1 | 09/17/1994 | 10/11/1994 | 9410140204 | <strong>Pressurizer Safety Valves Outside Technical Specification Limits Due To Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1994, with Unit 1 in Mode 6 (Refueling), the 'as found' set pressures for one Pressurizer Safety Valve was found to be outside the setpoint tolerances allowed by Technical Specifications 3.4.3. On September 18, 1994 a second Pressurizer Safety Valve was also found to be outside the setpoint tolerances allowed by Technical Specifications. These events are reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for conditions prohibited by Technical Specifications. <br /><br /> Three pressurizer safety valves and fifteen main steam safety valves were sent to Wyle Labs for testing to ensure conformance to Technical Specifications requirements. The 'as found' set pressures for two Pressurizer Safety Valves were found to be outside Technical Specification tolerance of plus or minus 1 percent of the setpoint pressure of 2485. The safety valves were repaired and readjusted within the correct setpoint tolerance allowed by Technical Specifications. <br /><br /> This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. The health and safety of the public were not affected at any time during this event.
3381994007 | North Anna 1 | 09/14/1994 | 10/04/1994 | 9410120045 | <strong>Missed Surveillance On A Main Steam Trip Valve Snubber Due To Administrative Process Error</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1994, with Unit 1 in Mode 6 (refueling) a missed surveillance was identified associated with the visual inspection of a one and a half inch small bore hydraulic snubber on the Main Steam System. Technical Specification 4.7.10.a allows the next inspection interval to be twice the previous interval but not greater than forty eight months depending on the number of unacceptable snubbers identified during inspections. The snubber in question was believed to have been removed as a result of a design change in January 1989. The snubber database and inspection procedures were revised to reflect the snubber removal and the inspections were discontinued. This is a condition prohibited by the Technical Specifications and is reportable pursuant to 10CFR50.73 (a)(2)(i)(B). <br /><br /> The cause of the inadvertent deletion of the snubber from the inspection program was due to an administrative process change error which occurred in January 1989. A more thorough review of the DCP would have revealed that the snubber was to be relocated and not deleted. <br /><br /> No significant safety consequences resulted from this event because the snubber could perform its intended function as determined by functional testing. Therefore, the health and safety of the public were not affected at any time during the event.
3381994008 | North Anna 1, North Anna 2 | 12/15/1994 | 01/04/1995 | 9501100245 | <strong>Inadequate Missile Protection Due To Incomplete Procurement/Design Review Of Manhole Covers</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1994, at 1045 hours, with Unit 1 and 2 in Mode 1, 100 percent power, it was determined that the plant was in a condition outside its design basis. A walk down of all missile protected manholes identified 15 manhole covers which did not provide the level of protection required by the Updated Final Safety Analysis Report (UFSAR), Section 3.5.4. At 1110 hours a non-emergency one (1) hour report was made to the NRC Operations Center in accordance with 10 CFR 50.72 (b)(1)(ii)(B). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(ii)(B) for a condition that was outside the design basis of the plant. <br /><br /> The most probable cause of the event has been determined as inadequate procurement instructions to ensure the proper manhole covers were purchased and installed during original plant construction. <br /><br /> This event posed no significant safety implications because the probability of a tornado on site is 3.25 x 10(-5) as identified in the UFSAR, Section 2.3.1.3.2. A specific missile strike, as a result of a tornado, on one of the manhole covers is even more remote. Additionally, North Anna has not experienced weather conditions which could produce a missile meeting the tornado criteria as described in the UFSAR. Therefore the health and safety of the public were not affected at any time during this event.
3391994001 | North Anna 2 | 01/05/1994 | 01/17/1994 | 9402020266 | <strong>Two Of Three Auxiliary Feedwater Pumps Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1994, at 1600 hours with Unit 2 operating at 100 percent power (Mode 1) the steam driven auxiliary feedwater pump (2-FW-P-2) inlet trip valve closed when the manual trip lever was accidentally actuated rendering the pump inoperable. The 2J Emergency Diesel Generator had been previously tagged out for scheduled maintenance which administratively rendered a second motor driven auxiliary feedwater pump inoperable per Technical Specification (TS) 3.0.5 when 2-FW-P-2 was isolated. The inlet trip valve was reset within five minutes and 2-FW-P-2 was returned to operable status. Although the requirements of the TS were satisfied it was determined that this event alone could have prevented the fulfillment of the system's safety function to mitigate the consequences of an accident. A four hour report was made to the NRC at 1757 hours pursuant to 10 CFR 50.72 (b)(2)(iii)(D). The event is reportable pursuant to 10CFR50.73 (a)(2)(v)(D). <br /><br /> Actuation of the inlet trip valve was due to personnel error while a maintenance engineer was performing an inspection of the steam driven auxiliary feedwater pump packing glands. <br /><br /> No significant safety consequences resulted from this event since one AFW subsystem remained operable and 2-FW-P-2 was promptly reset. Therefore, the health and safety of the public were not affected at any time during this event.
3391994002 | North Anna 2 | 01/06/1994 | 01/31/1994 | 9402070149 | <strong>ASME Section XI Code Examinations Not Performed As Required</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1994, at 1000 hours with Unit 2 operating at 100 percent power (Mode 1) it was discovered that ASME Code examinations conducted pursuant to North Anna Technical Specification (TS) Surveillance Requirement 4.0.5.a had not been performed as required. Seven bolted connections with indication of previous leakage did not receive a VT-3 examination as required by the test procedure. The unit entered the provision of TS 4.0.3 which provided a 24 hour period to perform the surveillance. A Relief Request, from ASME Section XI, was pursued from the NRC. The Action of TS 4.0.3 was cleared at 0957 hours on January 7, 1994 when the NRC approved the relief request. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B).<br /><br /> The cause of the missed surveillance was due to personnel error for failure to follow procedure, A lack of full understanding of the Code by maintenance personnel was also a contributing factor. <br /><br /> No significant safety consequences resulted from this event because failure of the fasteners would not cause a catastrophic failure of any equipment required for the mitigation of analyzed accidents. Increased leakage at bolted connections may occur, but this situation is bounded by existing accident analysis. Therefore, the health and safety of the public were not affected at any time during this event.
3391994003 | North Anna 2 | 01/22/1994 | 08/15/1994 | 9408230194 | <strong>Automatic Reactor Trip Due To Closure Of Maine Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1994, at 0644 hours with Unit 2 operating at 95 percent power (Mode 1) an automatic reactor trip occurred. The initiating signal was the 'A' Steam Generator (SG) low level coincident with a steam flow greater than feedwater flow mismatch caused by closure of the 'A' Main Feedwater Regulating Valve (MFRV). This resulted in a reactor and turbine trip. A four hour report was made to the NRC at 1014 hours pursuant to 10 CFR 50.72 (b)(2)(ii) and (vi). This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) as an automatic actuation of a Reactor Protection System. <br /><br /> The cause of the 'A' MFRV closure was due to a component failure of the upper pneumatic booster relay on the valve positioner. <br /><br /> No significant safety consequences resulted from this event because all safety systems responded appropriately. Therefore, the health and safety of the public were not affected at any time during this event.
3391994004 | North Anna 2 | 03/18/1994 | 04/12/1994 | 9404190003 | <strong>Multiple Individual Rod Position Indicators Inoperable Due To Faulty Capacitor</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1994, at 0558 hours with Unit 2 operating at 100 percent power (Mode 1) multiple IRPI alarms were received for Individual Rod Position Indicators (IRPI) being out of agreement with the group step demand indication. Technical Specification (TS) 3.1.3.2, Action a was entered and IRPI indication adjustments were initiated. At 0700 hours, during calibration of the IRPI for control rod K08, the IRPI for control rod F08 exceeded the TS limit of greater than 12 steps from the group step demand indication for approximately 2 minutes. Technical Specification 3.0.3 was entered from 0702 to 0704 hours for exceeding the TS Limiting Condition for Operation. This event is reportable pursuant to 10CFR50.73.(a)(2)(i)(B) for a condition prohibited by TS. <br /><br /> The cause of the event was due to an intermittent failure of a capacitor on the IRPI power supply voltage regulator control card. The voltage regulator failed to its maximum voltage output causing the IRPI indication to increase. <br /><br /> No significant safety consequences resulted from this event because the control rods were able to perform their safety function (i.e. able to trip) throughout the event and the ability to move control rods was never compromised. Therefore, the heath and safety of the public were not affected at any time during this event.
3391994005 | North Anna 2 | 06/01/1994 | 06/24/1994 | 9407010316 | <strong>Unit 2 Shutdown Due To Reactor Coolant System Leakage Exceeding Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1994, at 2121 hours with Unit 2 operating in Mode 3 a Notification of Unusual Event was declared in accordance with Emergency Plan Implementing Procedures. Leakage was identified from a nozzle weld on a small diameter seal injection line associated with the 'B' Reactor Coolant Pump which is part of the Reactor Coolant System pressure boundary. The initial report of a Notification of Unusual Event was transmitted to the State and local governments at 2128 hours. On June 2, 1994, at 0946 hours, with the unit in cold shutdown, State and local authorities were notified that the Notification of Unusual Event was terminated. <br /><br /> Preliminary examination of the fracture surface indicates that the seal injection line nozzle weld failed as a result of high cyclic fatigue. A root cause evaluation of the weld leak is in progress.<br /><br /> No significant safety consequences resulted from this event since core cooling was not challenged and there was no release of radioactive material to the environment. Therefore, the health and safety of the public were not affected during this event.
3411994001 | Fermi 2 | 01/27/1994 | 02/28/1994 | 9403100174 | <strong>Loss of Division I Power Due to Weather and Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1994 at 1305 hours with the plant in Cold Shutdown, a loss of Division I power was experienced. As a result of this, power was lost to Division I RPS and Division I Emergency Diesel Generators received an auto-start initiation on bus undervoltage. All expected Engineered Safety Feature actuations/isolations occurred. Within 58 minutes, shutdown cooling was restored. All safety related buses were restored to offsite power by 1630 hours. <br /><br /> The cause for the loss of all three Division I incoming offsite feeds was related to an ice storm in conjunction with the failure of an incoming feed breaker to open. The probable cause of the breaker failure was the trip linkage on the 'Y' phase was mechanically inhibited due to water intrusion creating ice in combination with below freezing weather conditions. <br /><br /> Power was restored to Division I utilizing two of the three incoming offsite feeds. pending replacement of Swan Creek overhead lines and troubleshooting the failure of the breaker to open on that line.
3411994002 | Fermi 2 | 07/14/1994 | 08/15/1994 | 9408230156 | <strong>Safety Relief Valve Set Pressures Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>The Main Steam System is equipped with fifteen Target Rock two-stage pilot-operated Safety Relief Valves (SRVs) to prevent over-pressurization of the Nuclear Steam Supply System (NSSS). Technical Specification 3.4.2.1 requires that at least eleven of the fifteen SRVs be operable with specified lift settings during Operational Conditions 1, 2 and 3. <br /><br /> All fifteen SRV pilot assemblies were removed during the fourth refueling outage and sent to a vendor laboratory for testing. On July 14, 1994, the vendor notified Detroit Edison that six of the fifteen SRVs failed to lift within their specified setpoint tolerance range and that one SRV pilot leaked excessively, such that setpoint pressure could not be confirmed by testing. <br /><br /> All fifteen SRV pilot assemblies have been replaced with refurbished and certified spare assemblies. SRV setpoint upward drift is an industry problem related to SRV pilot disc-to-seat oxide bonding. Detroit Edison is following Industry developments in this area. The excessive downward drift associated with two of the SRVs along with the excessive pilot leakage associated with one other SRV will be investigated further during the upcoming refurbishment of the corresponding pilot assemblies.
3411994003 | Fermi 2 | 07/15/1994 | 09/13/1996 | 9609200113 | <strong>Inadequate Logic Functional Test</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1994 during a routine review of surveillance procedure 42.302.02, 'Calibration and Logic System Functional Test of Division 1 4160 Volt Emergency Bus 64B and 11EA Undervoltage Circuits', it was determined that the permissive interlocks for the bus undervoltage relays had not been tested to the degree necessary to fully meet the requirements of Technical Specification section 3.3.3. Further testing deficiencies were identified on September 9, 1994 related to the starting and the loading of the Emergency Diesel Generators. <br /><br /> Additional testing deficiencies were identified on October 20 and November 1, 2, 5 and 10, 1994 related to Core Spray and Residual Heat Removal System logic functional testing, Reactor Protection logic, Main Steam Isolation Valve Leakage Control System, Remote Shutdown functional testing, Primary Containment manual valves, Alternate Shutdown panel transfer switches, and Low-Low set logic of Safety Relief Valves and Alternate Rod Insertion logic. <br /><br /> The cause of this event can be attributed to procedural deficiencies. Corrective actions include revising the deficient procedures and performing the surveillances, reviewing similar surveillances, and creating electrical overlap drawings,
3411994004 | Fermi 2 | 08/22/1994 | 09/21/1994 | 9409280110 | <strong>Inadequate Closing Force For Air Operated Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1994, at 1500 hours, it was discovered that air operated, spring closing isolation valves B3100F014A/B and -F016A/B may not be capable of performing their Reactor Coolant Pressure Boundary (RCPB) function of isolating against Reactor Coolant System (RCS) pressure at their current actuator spring preload settings. The cause of this event was inadequate control of the valve actuator settings which resulted in insufficient preload being maintained on the actuator closing springs. <br /><br /> The spring preload settings will be increased to a value sufficient to ensure adequate valve closure prior to plant startup. Controls will be put In place to ensure that these settings are maintained. The Design Basis Documents (DBDs) for Primary Containment Isolation and for the Recirculation System will be reviewed and revised as necessary to ensure that they contain an adequate level of detail regarding the containment and RCPB isolation requirements. A Plant Engineering Critique will be performed and the Lessons Learned from this event will be distributed to the appropriate personnel.
3411994005 | Fermi 2 | 08/26/1994 | 09/26/1994 | 9410030304 | <strong>Actuation of Isolation Logic due to Power Interruption During Logic Modification</strong><br /><i>Abstract:&nbsp;</i>Installation of Engineering Design Package (EDP) 26310 was in progress on August 26, 1994 at 1604 hours, when electricians loosened the screw on terminal strip AA-58 per the EDP work request. This interrupted power to portions of the Nuclear Steam Supply Shutoff System control logic, causing actuations of Engineered Safety Feature Systems and isolations. Reactor Building Heating Ventilation and Air Conditioning isolated, Standby Gas Treatment System division 2 started, Control Center Heating Ventilation and Air Conditioning shifted to the recirculation mode, Control Air Compressor division 2 started, Torus Water Management System isolated, Drywell Equipment Drains Sump isolated, Drywell Pneumatics division 2 isolated, and Reactor Recirculation Seal Purge outboard isolation valves isolated. At 1903 hours, the restoration of the actuations and isolations associated with the interruption of power in panel H11-P623 was complete. <br /><br /> The cause of this event was procedural weakness. Procedures for modification implementation and work control will be revised to address the Identified weakness.
3411994006 | Fermi 2 | 09/03/1994 | 10/03/1994 | 9410070154 | <strong>Core Alterations with Inoperable Source Range and Intermediate Range Monitors</strong><br /><i>Abstract:&nbsp;</i>When initiating reload of the core, three irradiated and one new fuel assembly were placed around Source Range Monitor (SRM) B. The SRM remained downscale. When irradiated fuel was placed beside SRM C, it indicated four counts per second. Fuel movement was stopped and the operability of SRM B further investigated. <br /><br /> The SRM B cable connector under the vessel had become disengaged sometime during the outage. Upon discovery, the cable was properly connected and tested. SRMs A and D were also tested to verify connector integrity, and fuel loading resumed. Subsequent investigation revealed that Intermediate Range Monitor (IRM) channels C, F, and G were also inoperable for similar reasons. <br /><br /> Connector integrity will be verified for downscale SRMs and IRMs during future refueling outages after work which could Impact connector integrity has been performed. Also, a procedure revision will be made to provide guidance on the expected response of the SRMs when loading fuel. Potential improvements for accessibility under the vessel will be evaluated.
3411994007 | Fermi 2 | 10/31/1994 | 11/30/1994 | 9412050203 | <strong>Improperly Installed Control Center Heating Ventilation and Air Conditioning Duct Hanger</strong><br /><i>Abstract:&nbsp;</i>October 27, 1994 the Insulation was removed from the control center heating ventilation and air conditioning [(CCHVAC)(VI)] return air fan discharge duct as part of the implementation of Engineering Design Package [EDP] 26868 for fire damper modifications. determined that a nine foot length of C channel, which had been wedged against a piece of unistrut and partially wrapped inside the duct insulation, had not been seismically supported. The channel is located above the control room panel H11-P808 containing controls for both safety related and non safety related plant equipment. The cause of the problem was an engineering error which occurred in 1983 when the structural channels were unbolted from the control room ceiling. To correct the situation, the affected (south) channel has been welded to the adjacent channels, and the south channel was re-bolted to the control room ceiling. Engineering has revised (i.e., posted) the drawing which specifically references the weld configuration of this structural channel and has conducted a review of similar configurations.
3411994008 | Fermi 2 | 11/08/1994 | 12/08/1994 | 9412120264 | <strong>Unrecognized Entry into Technical Specification Action Statements</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1994 Residual Heat Removal Service Water Pump C was removed from service for maintenance. The operators did not recognize entry into Technical Specification Action 3.7.1.1.b which requires that associated shutdown cooling loop be declared inoperable and that action be taken as required by Action 3.4.9.2. This action requires that operability of an alternate method of decay heat removal be verified within one hour. An approved alternate method of decay heat removal was known to be available; this was not consciously verified because the operators did not recognize entry into these action statements. This event occurred because the operators failed to adequately review all of the applicable Technical Specifications. Poor shift communication and inadequate use of the job impact statement contributed to this event. <br /><br /> The individuals involved in this event have been counseled regarding this event, and they have presented lessons learned from this event to the other operating shifts. This event is being reported voluntarily.
3411994009 | Fermi 2 | 11/10/1994 | 12/12/1994 | 9412200151 | <strong>Unplanned Primary Containment Isolation of Torus Water Management System</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1994 at 1046 hours, the Torus Water Management System (TWMS) containment isolation valves automatically closed due to a High-High water level in the drywell floor drain sump. This occurred during the pumping of water from the drywell equipment drain sump to the drywell floor drain sump to allow Radwaste Decontamination Personnel to clean the equipment drain sump. Isolation of the TWMS primary containment isolation valves is reportable as an actuation of an Engineered Safety Feature (ESF). <br /><br /> The cause of this event was poor communications and failure to adequately monitor and control the pump out of the drywell equipment drain sump. Lessons learned from this event will be provided to operations and radwaste personnel.
3411994010 | Fermi 2 | 11/11/1994 | 12/12/1994 | 9412200157 | <strong>Unplanned Automatic Isolation of Shutdown Cooling Due to Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On Friday, November 11, 1994 at 1657 Hours, Residual Heat Removal Shutdown Cooling suction line inboard containment isolation valve closed automatically during the performance of an Instrumentation and Controls (I&C) surveillance. The surveillance procedure identified that this action would occur, however, Operations personnel had not adequately reviewed this procedure and had not established appropriate plant conditions prior to authorizing the surveillance. This isolation was unplanned and resulted in the interruption of shutdown cooling operation. This event was caused by inadequate review prior to authorizing the surveillance. Poor communications between Operations and I&C personnel contributed to this event. <br /><br /> The individuals involved in this event have been counseled regarding this event, And they have presented lessons learned from this event to the other operating shifts. Further training on this event will be provided to I&C and Operations personnel. Also, impact statements for the related surveillance procedures will be revised to stipulate that shutdown cooling shall not be in operation during these surveillances.
3411994011 | Fermi 2 | 11/23/1994 | 01/11/1995 | 9501190267 | <strong>Loss Holddown Screws in the SRM and IRM Instrument Drawers</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1994, erratic indication was observed for Intermediate Range Monitor (IRM) 'E' during testing of Source Range Monitor (SRM) 'C'. This occurred because loose and worn holddown screws for circuit cards allowed for movement, disturbing continuity of the card connector pins. Worn screws were replaced and tightened for the SRM's and IRM's. Additionally, several bottom connector bridges which were found to be bowed, allowing slight movement, were also repaired. On December 12, it was determined that the holddown screws are essential for the seismic qualification, therefore the as found condition is reportable as a condition outside the design basis. <br /><br /> This event was attributed to low sensitivity on the part of personnel for the need to correct seemingly minor discrepancies. Additionally, I&C personnel were unaware of the significance of the holddown screws. <br /><br /> Procedures will be revised to ensure proper tightening of the holddown screws and circuit card seating. I&C personnel will be trained regarding these holddown screws and proper circuit card seating. Also, training will be provided to maintenance personnel to reinforce the expectation that the plant be maintained in the condition to which it was designed and licensed.
3461994001 | Davis-Besse | 06/08/1994 | 07/08/1994 | 9407180145 | <strong>Inoperable Safety Features Actuation System Instrument Strings</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1994, with the Reactor operating at approximately 100 percent Rated Thermal Power (RTP), it was discovered that a Technical Specification (TS) Safety Features Actuation System (SFAS-JE) Channel 4 trip setpoint required in Mode 6, Refueling had been calibrated at greater than the required setpoint during past Refueling operations. Technical Specification 3.3.2.1, SFAS Instrumentation, requires a minimum of 3 high containment radiation instrument strings operable. The trip setpoint and allowable value for a containment radiation string is required to be less than 2 times background. The background radiation readings at the location of RE2007 are approximately 2 to 3 millirem per hour. The containment radiation high setpoint for RE2007 during Mode 6, Refueling operations had been calibrated at 15 mrem/hr. Channel 2 SFAS radiation instrument string was inoperable during core alterations conducted between October 1 and 7, 1984. With the channel 4 setpoint incorrectly calibrated, only 2 SFAS containment high radiation strings were operable. The cause of this occurrence is incorrect evaluation of the required setpoint implemented as a result of a facility change in 1982. This occurrence has had no impact on the health and safety of the public or plant personnel. Background radiation for RE2007 was confirmed to be approximately 2.5 mrem/hr on July 1, 1994. Prior to conducting core alterations or movement of fuel in containment, trip setpoints will be adjusted, as necessary to comply with Technical Specifications.
3461994002 | Davis-Besse | 07/28/1994 | 08/29/1994 | 9409090007 | <strong>Anticipatory Reactor Trip System Inoperable Due To Failure To Trip Main Feed Pump Turbine</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1994 at approximately 0300 hours, with the plant in Mode 1 at approximately 55% power, Number 2 Main Feed Pump (MFP) was removed from service and isolated to effect repairs to a minor steam leak on a vent line for the pump. The MFP turbine was not tripped. Since the MFP turbine was not tripped, the turbine governor hydraulic control oil remained at normal pressure and caused the Anticipatory Reactor Trip System (ARTS) logic, which uses MFP turbine oil pressure to indicate a running MFP, to sense that two MFPs were in service when actually only one pump was running and the other one was isolated. In the event that only Number 1 MFP turbine tripped, the ARTS would not have tripped the reactor as designed. This condition was later recognized by Operations management and at 0939 hours Number 2 MFP turbine was tripped. Technical Specification (TS) 3.3.2.3 requires that the ARTS logic channels for the trip of both MFP turbines be operable in Mode 1. Although the ARTS would have actuated properly had both MFP turbines or the main turbine automatically tripped, or the Steam and Feedwater Rupture Control System (SFRCS) actuated, a trip of the running MFP by itself would not have caused the ARTS to actuate. During the time period from approximately 0300 hours to 0939 hours, the ARTS was incapable of performing its intended function and all four channels were inoperable, contrary to the requirements of TS 3.3.2.3. This event is being reported as a condition prohibited by the Technical Specifications under 10CFR 50.73(a)(2)(i)(B).
3461994003 | Davis-Besse | 10/08/1994 | 11/07/1994 | 9411150615 | <strong>Spent Fuel Pool Gate Moved in Spent Fuel Pool While Emergency Ventilation Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1994 at approximately 1130 hours with the plant shutdown in Mode 6, the Spent Fuel Pool (SFP) to Fuel Transfer Tube Pit Gate was moved in the SFP area using the Spent Fuel Pool Cask Crane with the Emergency Ventilation System (EVS) servicing the SFP area inoperable. The SFP area EVS was inoperable because the Containment Equipment Hatch was removed, the Containment Purge Supply and Exhaust Fans were running, and a door leading from the SFP area to the outside atmosphere was opened during the evolution. This event was a violation of Technical Specification (TS) 3.9.12, Action b., which prohibits crane operations and movement of loads over the SFP with the SFP area EVS inoperable. This event involved personnel error by the maintenance crew performing the evolution in that the Control Room was not notified immediately prior to the move as was previously arranged so that SFP area ventilation system operability could be restored. This event is being reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications.
3461994004 | Davis-Besse | 10/14/1994 | 11/14/1994 | 9411220209 | <strong>Containment Hydrogen Purge Inlet Screen Not Installed</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1994 with the plant shutdown in Mode 6, a piping system walkdown of the Containment Hydrogen Purge (CHP) System was being conducted by Toledo Edison (TE) personnel. During the walkdown, the system engineer discovered that a screen on the inlet to the CHP line was not installed per the isometric drawings of the system. An evaluation of this discrepancy revealed that this screen is necessary to assure operability of the CHP system and the containment isolation valves as required by Technical Specifications (TS) 3.6.4.4 and 3.6.3.1. Corrective actions included replacement of the inlet screen during the Ninth Refueling Outage. This condition is being reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the TS.
3461994005 | Davis-Besse | 11/03/1994 | 12/05/1994 | 9412140246 | <strong>RPS Channel 4 Response Times Exceeded</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1994, with the plant in Mode 5, response time testing of Reactor Protection System (RPS) Channel 4 indicated that RPS Technical Specification (TS) functional units Reactor Coolant (RC) Low Pressure and RC High Pressure had exceeded the allowable TS response time limits. Subsequent evaluation identified that an incorrect buffer amplifier module had been ordered from the warehouse and installed in the RPS Channel 4 cabinet in 1990 during the Sixth Refueling Outage (6RF0). A review of Cycle Nine reactor trip data indicated that it was likely that these RPS channel 4 functional unit response times had exceeded the allowable TS limits during Cycle Nine operation making them technically inoperable. <br /><br /> The correct buffer amplifier was installed on November 3, 1994 and successfully tested on November 4, 1994. The remaining RPS channel RC pressure string buffer amplifiers were verified to be the correct type. <br /><br /> Current part information, work practices, and procedure notification steps provide adequate assurance that recurrence of a similar event is unlikely. <br /><br /> This condition is being reported as a condition prohibited by TS under the provisions of 10CFR50.72(a)(2)(i)(B).
3481994001 | Farley 1, Farley 2 | 05/21/1994 | 06/13/1994 | 9406200297 | <strong>1A CCW Pump Failure to Start Due to Supply Breaker Prop Latch Spring Detachment</strong><br /><i>Abstract:&nbsp;</i>On 5/21/94, the 1A component cooling water pump (B-train) failed to start when being placed in service to allow sampling of that train of component cooling water (CCW) for chemical analysis. An investigation revealed that the supply breaker (1-DG04) would not close because the spring charging motor did not charge the closing springs following the previous breaker closure. For approximately 6 days the B-train of CCW was inoperable due the uncharged springs on the B-train pump and the fact that the swing pump was aligned to the other train. Thus, the 72 hour limiting condition for operation for CCW was not met. This event occurred because both prop latch springs on 1-DG04 had become detached, which resulted in the closing linkages not fully resetting. FNP has experienced previous problems with prop latch springs on these type breakers, with three other cases impacting breaker closing. FNP developed a comprehensive program that has determined the root causes of prop latch spring detachments, and is implementing permanent corrective action on all Siemens type MA350-C breakers. Corrective actions have been completed on breaker 1-DG04. Overall breaker operability is not compromised by this problem due to the fact that, out of 133 breakers in service with a total of approximately 42,463 cycles, there have been only 4 breakers that failed to close as a result of prop latch spring problems. The breaker tripping function does not rely on the prop latch springs and has therefore not been affected in any of these cases. However, as an additional precaution for the interim, FNP is periodically verifying the closing springs are charged on ESF breakers.
3481994002 | Farley 1 | 03/26/1994 | 04/13/1994 | 9404180223 | <strong>Steam Generator Tube Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>The following report is being submitted in accordance with Technical Specification 4.4.6.5.a to report the number of steam generator (S/G) tubes plugged or repaired, and in accordance with Technical Specification 4.4.6.5.c to report the results of S/G tube inspections which fall into Category C-3. During the Unit 1 Twelfth Refueling Outage (U1RF12), eddy current inspections were performed on 100 percent of the available tubes in all three steam generators. As a result of this inspection, 1C steam generator had 48 tubes in service during Cycle Twelve that were found to be defective (1.47 percent of the total number of tubes inspected in 1C steam generator), which requires inspection results to be classified as Category C-3. These tubes were either plugged or sleeved. Following these actions, the equivalent tube plugging percentage in each steam generator is: 4.74 percent in 1A, 2.61 percent in 1B, and 3.70 percent in 1C. This results in an overall equivalent tube plugging of 3.69 percent. In addition to the required tube plugging and sleeving, several ongoing programs have been established to reduce the probability of future tube degradation.
3481994003 | Farley 1, Farley 2 | 06/03/1994 | 06/13/1994 | 9406210228 | <strong>Main Steam Safety Valves Setpoint Test Errors</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications require that Main Steam Safety Valves (MSSVs) be operable with a lift setting of +/-1% of designated settings. During the Unit 1 eleventh refueling outage and the Unit 2 ninth refueling outage, several MSSVs were found to have lift settings outside the +/-1% tolerance band, Although the lift settings exceeded the +/-1% tolerance band, the MSSVs continued to provide sufficient protection against over- pressurization of the secondary system. <br /><br /> The discovery of MSSV setpoints outside the +/-1% tolerance band is attributed to two causes: <br /><br /> 1. Test system accuracy as allowed by the ASME Code, Section XI, and ASME PTC 25.3-1976; and <br /><br /> 2. An inaccuracy in the Mean Seat Area term of the equation used to Trevitest system. <br /><br /> An increased band for the acceptable MSSV setpoints will be requested in an amendment to the technical specifications. Additionally, the Farley procedure used for calculating MSSV lift setpoints with the Furmanite Trevitest system has been revised to include the revised Mean Seat Area term.
3481994004 | Farley 1, Farley 2 | 06/02/1994 | 09/15/1994 | 9409270197 | <strong>Valve Actuator Spacer Bolts Found to be of Incorrect Material</strong><br /><i>Abstract:&nbsp;</i>On or about June 2, 1994, during metallurgical examination of failed valve actuator spacer bolts, it was determined that incorrect material had been used in the bolts' manufacture. The failed bolts had rendered the 1A Main Steam Isolation Bypass valve inoperable. Previously, on April 10, 1994, while in a refueling outage, Operations personnel had manually closed the valve in order to verify the valve position. In the process, the force applied by the manual handwheel caused the failure of two of the four actuator spacer bolts and deformed the two remaining bolts. The valve actuator was repaired during the outage. <br /><br /> The vendor's drawing shows the spacer bolts as being made from ASTM-A-193 grade B7 material. However, when the failed bolts were tested it was determined that they were made of a mild carbon steel of the ASTM-A-108 family. The most probable cause of the bolts' failure appears to be the yield strength of the incorrect (ASTM-A-108 family) material used in the assembly of the actuator being exceeded by the force applied by way of the manual handwheel. <br /><br /> Corrective action for this event included administratively restricting the use of the manual handwheel on all valves of this style (a total of sixteen ), performing a torque preload test, and an engineering evaluation which determined the acceptability of the existing bolts on these valves when operated by the air actuator. All valves of this style will have the spacer bolts replaced with the correct material.
3481994005 | Farley 1, Farley 2 | 10/21/1994 | 03/18/1997 | 9703250057 | <strong>Missile Protection for Condensate Storage Tanks</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1994, during a self-initiated safety system assessment (SSSA) of the Farley Nuclear Plant (FNP) auxiliary feedwater system (AFW), the assessment team identified several connections to the Unit 1 and Unit 2 condensate storage tanks (CSTs) that were not missile protected. <br /><br /> Southern Nuclear Operating Company (SNC) performed an analysis using probabilistic risk analysis techniques which indicated that the probability of an accident due to the lack of missile protection on the subject connections to the CSTs was negligible. A safety evaluation was performed which concluded that an unreviewed safety question was not involved. Therefore, the FNP Final Safety Analysis Report (FSAR) was revised in November, 1994 to include the missile protection analysis results and to delete the requirement for missile protection for the subject CST connections. SNC wrote LER 94-005-00 (shared) to report this issue. The NRC reviewed the safety evaluation and determined that it was correctly performed in accordance with 10CFR50.59 requirements. <br /><br /> In February 1997, an NRC design basis inspection team inspecting FNP's AFW system expressed a concern that a potential unreviewed safety question did exist. Following re-assessment SNC concluded that FNP had inappropriately applied PRA and deterministic assessment analyses in the safety evaluation. <br /><br /> The cause of the lack of missile protection for these connections was an oversight of the design organization. Interim measures have been taken until the missile protection issue for these connections is resolved. Installation of missile protection for these connections will be evaluated in conjunction with a revision to the FSAR.
3521994001 | Limerick 1 | 01/14/1994 | 02/14/1994 | 9403020005 | <strong>Manual actuation of the Reactor Protection System due to the unexpected failure of an indicating light bulb During reinstallation into its socket.</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1994, at 1930 hours, a manual reactor scram was initiated by the licensed main control room reactor operator as directed by procedure in response to the loss of both recirculating water pumps. These pumps tripped as designed to reduce reactor power in response to an automatic reduction of main turbine load because of the loss of main generator stator water cooling. This loss of cooling was the combination of the 1A stator water coolant pump being out of service for maintenance work, and a 1B stator water coolant pump trip. The 1B pump trip was due to the unexpected failure of an indicating light bulb during reinstallation into its control panel socket by an operator. The indicating light is an integral part of the motor control circuit for the pump. The broken bulb created a short that energized a trip coil within this circuit. Plant systems functioned as designed. Operations personnel quickly responded by implementing the appropriate transient response procedures. The cause of this event was the lack of expectations concerning the replacement of indicating light bulbs. Expectations regarding the need to exercise care when replacing indicating light bulbs have been communicated to the applicable plant personnel, and will be included in plant staff continuing training.
3521994002 | Limerick 1, Limerick 2 | 01/16/1994 | 02/09/1994 | 9402160213 | <strong>Manual isolation of the Reactor Enclosure Secondary Containment, an Engineered Safety Feature Actuation, due to equipment problems encountered with the Auxiliary Boiler system.</strong><br /><i>Abstract:&nbsp;</i>On 1/16/94, at 0030 a manual isolation of the Unit 1 Reactor Enclosure (RE) Secondary Containment (SC), an Engineered Safety Feature (ESF) actuation, was inserted due to a low differential pressure (dp) condition between the RE SC and the outside environment. Following the isolation, the Standby Gas Treatment System and the Reactor Enclosure Recirculation System, also ESFs, started per design. On 1/15/94, at 2343 the 'A' Auxiliary Boiler tripped on low steam drum water level due to a frozen instrument line. As a consequence of the frozen instrument line, a second Auxiliary Boiler also tripped. This resulted in a loss of steam to the RE ventilation system heating coils, causing the RE exhaust fans to be unable to extract enough air to maintain the negative dp. The RE SC isolation signal was inserted after operators concluded that the one operating Auxiliary Boiler could not provide sufficient steam to maintain the RE dp. The isolation was reset at 1650 on 1/16/94, after the frozen instrument line was repaired, and the RE ventilation system was restarted. The consequences of this event were minimal. An inspection of areas of the Auxiliary Boiler system susceptible to freezing was performed, and repairs were implemented.
3521994003 | Limerick 1 | 02/06/1994 | 03/08/1994 | 9403160159 | <strong>Residual Heat Removal Service Water system erroneously shutdown while supporting decay heat removal.</strong><br /><i>Abstract:&nbsp;</i>On 2/6/94, during a Unit 1 refueling outage, the Unit 2 Chief Operator (CO) erroneously interrupted Residual Heat Removal Service Water (RHRSW) flow to the 1B RHR heat exchanger (HX) instead of securing flow to the 2A RHR HX resulting in a loss of Unit 1 residual heat removal. The Unit 1 CO was monitoring Unit 1 reactor coolant temperature every 15 minutes and 36 minutes after the error the Unit 1 CO informed Shift Supervision that the temperature was continuing to increase. The B RHRSW pump and the 1B RHR HX were then returned to service. The planned monitoring of reactor coolant by the Unit 1 operators led to the quick identification, correction, and minimization of the interruption. All of the required safety injection and cooling systems remained operable. The primary cause of this event was personnel error due to a failure to perform self check. The Unit 2 CO was disciplined. This event was determined to be not reportable since the RHR and RHRSW systems remained operable and the redundant trains of RHR and RHRSW were unaffected by the error. Following discussions with the NRC it was agreed that a voluntary LER would be issued.
3521994004 | Limerick 1 | 02/12/1994 | 03/14/1994 | 9403250172 | <strong>LER concerning an event where a Primary Containment Isolation Valve inadvertently isolated, an ESF, causing a loss of RHR shutdown cooling due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On 02/12/94 at 0857 hours, I&C technicians were performing procedure ST-2-036-704-1, 'Excess Flow Check Valve Functional Test.' Per the procedure, an I&C technician notified the Main Control Room at 0915 hours to reset any isolations that were generated. HV-051-1F015B, a Primary Containment Isolation Valve (PCIV), had inadvertently isolated constituting an ESF actuation. The isolation was reset at 0915 hours and the PCIV was reopened. The consequences were minimal in that during the period of isolation the reactor cavity was flooded, and per the outage plan, the Fuel Pool Cooling and the Reactor Water Cleanup systems were in service and fully capable of removing decay heat. The cause of the event was personnel error by the I&C technician. Contributing factors include a weak pre- job briefing, poor self-check, procedure human factors, and improper response to an unexpected result. The corrective actions include counseling of the I&C technician and supervisor, enhancements to procedure ST-2-036-704-1, an I&C group all-hands meeting, and the issuance of a I&C Training Bulletin. Other I&C procedures are being reviewed for similar enhancements.
3521994005 | Limerick 1 | 10/26/1984 | 03/25/1994 | 9404010010 | <strong>Main Steam Isolation Valve - Leakage Control System inoperability due to a seismic interaction interference affecting a valve</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1994 a PECO Energy employed engineer discovered that Main Steam valve HV-001-108, required for the outboard subsystem of the Main Steam Isolation Valve Leakage Control system (MSIV LCS) operability, did not have the proper seismic interference clearance. This condition could have caused an electrical fault and therefore would have prevented the valve from performing its function during and following a seismic event. The clearance discrepancy was identified during a seismic walkdown for a proposed MSIV LCS modification. The valve and outboard subsystem of the MSIV LCS were declared inoperable. On March 5, 1994, the seismic interference condition was corrected. This condition affecting the operability of the outboard subsystem of the MSIV LCS has existed since October 26, 1984, the date of issuance of the Unit 1 Low Power Operating License. The cause of this event was concluded to be a failure by construction personnel to properly install the identified equipment. The consequences of this condition were minimal in that no electrical fault condition actually occurred. The walkdown which discovered this condition was performed for both Unit 1 and Unit 2 and no other interference non-conformances were identified. No further actions are planned.
3521994006 | Limerick 1 | 03/15/1994 | 04/14/1994 | 9404180341 | <strong>Isolation of a PCIV, an ESF actuation, after an incorrectly installed instrument tube became disconnected causing an excess flow check valve to isolate due to an installation error.</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1994, while investigating a leak near the excess flow check valve (EFCV), XV-042-1F047B, a maintenance technician agitated the leaking EFCV instrument tube causing it to suddenly disconnect from its fitting resulting in the automatic closure of the EFCV. Closure of the EFCV caused a Reactor Protection System (RPS) half SCRAM signal and a partial Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) signal to be generated; however, no valve actuations occurred. The EFCV is a Primary Containment Isolation Valve and its automatic closure constitutes an Engineered Safety Feature actuation of the PCRVICS. The instrument tube was repaired, the half SCRAM signal was reset, an the EFCV was returned to service. The consequences of this event were minimal in that the EFCV performed its intended design function to isolate the instrument line. The primary cause of this event was an installation error in that the subject instrument tube was not properly connected to its fitting during a 1989 modification. A contributing factor was the agitation of the leaking instrument tube by the maintenance technician. A random sample of similar fittings will be performed and actions will be taken as necessary.
3521994007 | Limerick 1, Limerick 2 | 04/27/1994 | 05/23/1994 | 9406010161 | <strong>Refuel Floor Secondary Containment Isolation on Low Differential Pressure due to a Severe Storm.</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1994, at 1554 hours, the Limerick Generating Station (LGS) Refuel Floor (RF) Secondary Containment isolated and both trains of the Standby Gas Treatment System (SGTS) initiated due to a low negative differential pressure condition between the RF and the outside atmosphere. Both of these systems are common to LGS Units 1 and 2, and represent Engineered Safety Feature (ESF) actuations. The low negative differential pressure condition was the result of high winds associated with a passing storm front. The RF Secondary Containment and the SGTS responded as designed to maintain Secondary Containment integrity. Operators restored normal RF ventilation at 1704 hours on April 27, 1994, and reset all isolation signals when the high wind conditions cleared. As a result of a similar event in 1989, a note was added to Special Event (SE) procedure SE-9, "High Winds" to further heighten the operators' awareness that high wind conditions can cause Secondary Containment isolations. In addition, LGS shift operations personnel will be forewarned of severe weather activity in the area which may involve high winds by PECO Energy Company's Load Dispatcher. Based on these actions, future similar events will not be reported.
3521994008 | Limerick 1 | 05/30/1994 | 06/27/1994 | 9407050114 | <strong>ESF actuation after a Secondary Containment barrier block valve closed due to personnel error During performance of a surveillance test.</strong><br /><i>Abstract:&nbsp;</i>On 05/30/94, Instrumentation and Controls (I&C) technicians were performing procedure ST-2-026-624-1. At 1934 hours the reactor recirculation pump seal purge block valve, HV-046-127, automatically closed, constituting an Engineered Safety Feature actuation. The Secondary Containment valve HV-046-127 provides a water seal during an accident condition to prevent fission products from being potentially released to the environment. Following the event, an I&C technician identified that a step in the ST procedure had been inadvertently omitted. The procedural step ensures an isolation signal is reset to prevent closure of HV-046-127. At 1940 hours Operations personnel re-opened HV-046-127 after resetting the isolation signal. The consequences of this event were minimal. After HV-046-127 closed, the recirculation pump seals were automatically serviced by reactor vessel water, and no problems or abnormalities were identified during this period. The cause of this event was personnel error. The I&C technician who erred was counselled, an I&C group all-hands meeting was conducted, and each I&C Supervisor is scheduled to hold a one hour meeting with their groups to reiterate the importance of self check principles.
3521994009 | Limerick 1 | 06/17/1994 | 07/12/1994 | 9407190359 | <strong>Radiation Monitor Alarm Circuit Card Malfunction results in an inadvertent isolation of Several Primary Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 6/17/94, at 0601 hours, the '1D' Reactor Enclosure Heating Ventilation and Air Conditioning exhaust plenum high radiation monitor inadvertently tripped. This resulted in various Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations, Engineered Safety Feature actuations. The isolation signal closed various Primary Containment sampling and block valves. The radiation monitor alarm circuit was replaced, and operations personnel reset the PCRVICS isolation signal and returned all affected valves to their normal positions by 1745 hours. The actual consequences of this event were minimal. The affected PCRVICS isolation valves repositioned and functioned as designed in response to the isolation signal. Due to a malfunction of the radiation monitor alarm circuit card, the radiation monitor hi-hi alarm setpoint dropped below the measured radiation reading. This caused the radiation monitor hi-hi alarm to trip resulting in the isolations. This type of failure has not occurred previously at Limerick Generating Station. No similar failures of this equipment have been identified to the manufacturer. This malfunction is considered to be an isolated occurrence.
3521994010 | Limerick 1 | 06/26/1994 | 07/26/1994 | 9408010236 | <strong>Two Primary Containment Isolation Valves inadvertently isolated, an ESF, due to a personal error During the application of a clearance</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1994, during the process of clearance application to support scheduled work on the Unit 1 cooling tower stilling well heater, the Unit 1 Reactor Operator pulled an incorrect fuse which caused the indicating lights for the containment leak detector outboard Primary Containment Isolation Valves to extinguish. The RO immediately reinstalled the fuse, and the CO identified that the valves had closed on the loss of power, thereby constituting an Engineered Safety Feature (ESF) actuation. The CO then re-opened the valves. The actual and potential consequences of this event were minimal. The affected valves repositioned and functioned as designed in response to the loss of power. The primary cause of this event is less than adequate attention to detail in that the RO and CO did not exercise proper self-check techniques. Corrective actions include disciplining the involved individuals regarding the importance of proper self-checking practices, increased requirements for the evaluation of self-checking by Operations personnel in the Main Control Room, and the publication of lessons learned from self checking related events and distribution to appropriate personnel to reinforce the importance of self checking.
3521994011 | Limerick 1 | 08/22/1994 | 09/21/1994 | 9409280232 | <strong>Radiation Monitor Power Supply Malfunction Results in an Inadvertant Isolation of Several Primary Containment Isolation Valves.</strong><br /><i>Abstract:&nbsp;</i>On 8/22/94, at 1220 hours, the '1D' Reactor Enclosure Heating Ventilation and Air Conditioning exhaust plenum high radiation monitor inadvertently tripped. This resulted in various Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations, Engineered Safety Feature actuations. The isolation signal closed various Primary Containment sampling and block valves. The radiation monitor power supply was replaced, and Operations personnel reset the PCRVICS isolation signal and returned all affected valves to their normal positions by 0115 hours on 8/23/94. The actual consequences of this event were minimal. The affected PCRVICS isolation valves repositioned and functioned as designed in response to the isolation signal. The malfunction of the radiation monitor power supply caused a radiation monitor inoperable trip resulting in the isolations. The failed power supply has been sent to the manufacturer for further analysis. Two previous events have occurred involving spurious trips of this specific radiation monitor where the exact causes could not be determined. Further analysis is being performed to determine if the failed power supply could be related to the previous events.
3521994012 | Limerick 1, Limerick 2 | 10/14/1994 | 11/28/1994 | 9412080266 | <strong>Failure to perform a Weekly Surveillance Inspection of The Safeguard Battery Pilot Cell Due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 10/27/94, following a review of Surveillance Test (ST) procedure and computer records, station personnel determined that two ST procedures scheduled to be performed on 10/12/94 had not been completed as required. The ST procedures provide for a weekly inspection of the pilot cells in each of the four (4) Unit 1 and four (4) Unit 2 Safeguard Batteries to verify acceptable electrolyte level, float voltage, and specific gravity. The Safeguard Batteries were not declared inoperable and the associated Technical Specifications (TS) Section 3.8.2.1 actions were not taken resulting in a condition prohibited by TS. All eight (8) of the Safeguard Batteries were fully capable of fulfilling their design function during the two weeks between inspections. An Operations Work Control Supervisor (who is a licensed operator) inadequately reviewed the Operations shift closeout meeting report to verify that all scheduled ST procedures were performed on the day shift of 10/12/94. A contributing cause was a less than adequate mechanism to ensure that unperformed ST procedures are identified before the TS time interval expires. Verbal and written communications have been issued to reinforce that scheduled ST procedures should be completed to comply with TS requirements. The mechanism to identify ST procedures that are approaching the TS overdue date has been upgraded.
3521994013 | Limerick 1 | 12/08/1994 | 01/06/1995 | 9501230051 | <strong>Condition Prohibited by Technical Specifications Resulting From an Inoperable Reactor Protection System Level Switch due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 12/08/94, Instrumentation and Controls (I&C) technicians discovered that level switch LSH-047-1N013A was valved out of service while performing a surveillance test (ST). Technical Specifications. This level switch is a Reactor Protection System (RPS) SCRAM Discharge Volume (SDV) float switch, which initiates a half channel SCRAM signal on a SDV high level condition. The ST was last performed on 09/14/94, and contains 2 sign-off steps which verify that the isolation valves are restored to the 'OPEN' position. On 12/08/94, the ST was completed and the level switch was declared operable. The consequences of this event were minimal in that a SDV high level condition did not occur while the level switch was inoperable. Had a SDV high level condition occurred 3 remaining level switches were available to initiate an RPS actuation. The most probable cause of this event was ascertained to be personnel error in that inadequate position verifications of the isolation valves were performed following completion of the ST on 09/14/94. Corrective actions include an inspection of other SDV level switches, participation of an I&C technician in the investigation, instrument valving refresher training, a discussion of this event with I&C personnel, and inclusion of this event in the 'STAR Performance' newsletter.
3531994001 | Limerick 2 | 03/01/1994 | 04/04/1994 | 9404110351 | <strong>Condition prohibited by Technical Specifications in that a surveillance requirement was not completed following replacement of isolation actuation trip unit</strong><br /><i>Abstract:&nbsp;</i>On 3/2/94, Main Control Room (MCR) operators determined that a Surveillance Test (ST) procedure for a Unit 2 isolation actuation instrument trip unit (TU) had not been performed on 3/1/94, following replacement of the TU. The appropriate Technical Specifications (TS) ACTIONs had not been implemented within the specified time and a condition prohibited by TS had occurred. The channel was immediately placed in the tripped condition as required by the TS ACTION. The appropriate ST procedure was then performed and the channel was declared operable. The TU was found to be functioning properly when tested on 3/2/94. The cause of this event is personnel error. The MCR Shift Supervisor (SS) failed to adequately review the work order to determine the operability requirements and the associated TS ACTION statement time limits. The SS involved in this event was counseled. The requirement that non-ST work orders (even if done concurrently with ST procedures) be reviewed and evaluated to ensure that the applicable TS actions are clearly identified and tracked has been communicated to all operations shift supervision.
3531994002 | Limerick 2 | 03/29/1994 | 04/22/1994 | 9405030290 | <strong>Inadvertent automatic closure of Primary Containment Isolation Valves, ESF Actuations, due to a malfunctioning handswitch caused by a weak electrical contact spring.</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1994, a Main Control Room (MCR) Reactor Operator (RO) was verifying the positions of various Primary Containment Isolation Valves (PCIV) for the Independent Verification of Restoration section of a Surveillance Test procedure. At 2230 hours, the RO deliberately touched the pistol grip handswitch, HS-057-232, while in the 'AUTO' position, and inadvertently caused three solenoid valves to momentarily close and then re-open following a second touch. These solenoid valves are PCIVs, and are also sampling valves associated with the Primary Containment Hydrogen/oxygen Analyzer System. The automatic closure of these PCIVs constitutes Engineered Safety Feature actuations. Troubleshooting identified that the handswitch was malfunctioning and the handswitch was replaced. There were no adverse consequences as a result of the momentary closing and reopening of the sample valves. Subsequent inspection and testing of the removed handswitch revealed that a weak spring existed under a set of electrical contacts. The corrective actions include the inspection and testing of a random sample of the same type of handswitches located in the MCR, and an inquiry via the Nuclear Plant Reliability Data System.
3531994003 | Limerick 2, Limerick 1 | 04/20/1994 | 05/20/1994 | 9405270152 | <strong>Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) Engineered Safety Feature Actuations resulting from a PCRVICS fuse which blew due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1994, during performance of a Surveillance Test (ST) procedure, various actuations of the Units 1 and 2 Primary Containment and Reactor Vessel Isolation Control System (PCRVICS), and a Unit 2 Reactor Enclosure Secondary Containment isolation occurred due to a blown fuse on Unit 2. These are Engineered Safety Feature actuations. The fuse blew after an Instrumentation and Controls (I&C) technician inadvertently grounded an electrical lead while attempting to reconnect the lead using a self-holding screwdriver. The fuse was replaced and all isolations were reset within 45 minutes. The actual consequences of this event were minimal. All affected systems responded as designed and there was no release of radioactive material to the environment as a result of this event. The cause of the isolations was the blowing of Unit 2 PCRVICS fuse B21H-F15D. The cause of the blown fuse was personnel error. The I&C technician involved in this event was counseled regarding the importance of attention to detail. An analysis of the techniques and tools used to lift and reconnect energized electrical leads is currently being performed, and corrective actions will be implemented as necessary.
3531994004 | Limerick 2 | 04/22/1994 | 05/19/1994 | 9405270199 | <strong>Inadvertent automatic closure of Primary Containment Isolation Valves, ESF Actuations, due to a failed trip unit card that caused the control circuit fuse to blow.</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1994, Main Control Room operators received annunciation of a Unit 2 half scram and a Division 1 Main Steam Isolation Valve half isolation signal. Additionally, three (3) Primary Containment Isolation Valves (PCIVs) inadvertently closed constituting an Engineered Safety Feature actuation. The three solenoid valve PCIVs are the sample valves for one of the Unit 2 Primary Containment hydrogen/oxygen analyzers. Personnel identified that a logic circuit fuse had blown resulting in the PCIV closures. Troubleshooting identified a bad trip unit circuit card in the logic circuitry associated with the fuse. The circuit card was replaced at 1721 hours, the isolation signal was reset, and the annunciators were cleared. The analyzer was then returned to normal operation. The redundant Primary Containment hydrogen/oxygen analyzer was unaffected by this event and all systems and components responded as designed following the failure of the trip unit circuit card. An electronic component failed on the trip unit circuit card causing a short circuit to ground resulting in the blown fuse. This failure has been evaluated to be a random failure with no pattern of recurrence.
3531994005 | Limerick 2 | 02/19/1994 | 05/31/1994 | 9406060187 | <strong>Failure to comply with Technical Specifications Section 3.7.7 in that a one hour firewatch inspection was not performed due to cognitive personnel error.</strong><br /><i>Abstract:&nbsp;</i>On 02/19/94, at 1000 hours, contracted security force personnel identified that the two previous hourly firewatch patrols of an area in the Unit 2 Reactor Enclosure had not been performed by the assigned Security Force Member (SFM). The patrol was required per the action of Technical Specification (TS) Section 3.7.7 due to an inoperable fire rated boot seal contained in the floor of the specific area. The patrol was performed at 1006 hours. This event was originally determined to be not reportable since adequately trained workers were in the area at the time of the missed inspections. The NRC concluded that such workers did not meet the TS requirements and the event resulted in a condition prohibited by TS. The defense in depth concept utilized in the design and operation of the plant make the actual and potential consequences of this event extremely minimal. The primary cause of this event was personnel error. The SFM became focused on the other responsibilities and forgot to perform the patrol as stipulated in the written post orders. The specific SFM was appropriately disciplined. All SFMs have been briefed on the event. A shift security supervisor will notify the assigned security responder prior to the time that the next firewatch patrol inspection is to be performed.
3531994006 | Limerick 2 | 01/10/1994 | 06/17/1994 | 9406240241 | <strong>This LER reports a condition where the 'B' Inboard and Outboard MSIVs were inoperable and the required TS Actions were not taken due to a failure to perform a ST.</strong><br /><i>Abstract:&nbsp;</i>On 5/20/94, an Instrumentation and Controls (I&C) supervisor identified that the 'B' Inboard and Outboard Main Steam Isolation Valves (MSIVs) were out of surveillance since 1/10/94. Operations personnel were immediately notified and the valves were satisfactorily tested on 5/20/94 at 1620 hours. The actual and potential consequences of this event were minimal in that the MSIVs were verified to be operable following the event, and would have functioned as designed had an accident or operating transient occurred during the time period in which the valves were out of surveillance. The primary cause of this event was a less than adequate review of Surveillance Test (ST) data by the system manager which led to an incorrect decision not to perform the 'B' Inboard and Outboard MSIV stroke test. The failure to stroke the valves during the next scheduled performance was due to unclear procedural guidance and less than adequate pre-job briefing to the technicians on the change to the requirements and the scope of the revised I&C STs. Corrective actions include: a review of this event with Site Engineering personnel along with expectations on how to confirm whether a procedure has been satisfactorily complete, and review and revision as appropriate of the specific I&C ST procedures to more clearly identify the need to stroke the MSIVs.
3531994007 | Limerick 2 | 03/28/1994 | 08/31/1994 | 9409130116 | <strong>Reactor Coolant System Recirculation Flow Units Inoperable and the Required Tech Spec ACTIONS not Taken Due to a Failure to Perform a Surveillance Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On 8/1/94, during an audit of the Surveillance Testing Program, a Quality Assurance auditor identified that the weekly performance of Instrumentation and Controls (I&C) Surveillance Test (ST) procedure ST-2- 074-424-2 had not been performed by the required due date. This ST procedure was performed satisfactorily on 3/21/94, but not again until 4/4/94. As a result, the 'A' and 'C' Reactor Coolant System Recirculation flow units were inoperable. Since personnel were not aware at the time that the ST procedure had not been performed, the associated Technical Specification (TS) Section 3.3.1.1 action was not taken resulting in a condition prohibited by TS. The actual and potential consequences of this event were minimal in that the affected flow units were satisfactorily tested on 4/4/94, and only a slight adjustment was made at that time due to a planned core flow change, not due to instrument drift. The causes of this event are less than adequate administrative controls and communications. The performance of the ST procedure is normally accomplished on the afternoon shift, however, the computer generated work list (foreman's list) for the afternoon shift I&C foreman did not include this ST procedure. The computer program that automatically schedules the weekly ST procedures has been revised to include the appropriate foreman codes for all weekly ST procedures for all work groups.
3531994008 | Limerick 2 | 08/13/1994 | 09/09/1994 | 9409190218 | <strong>Unit 2 maximum power level of 100% exceeded by approximately 2.6%, due to a malfunction of the 'A' recirculation pump M/G set scoop tube positioner servo amplifier.</strong><br /><i>Abstract:&nbsp;</i>On 08/13/94, the 'A' Motor/Generator (M/G) set scoop tube positioner inadvertently increased the M/G set speed, resulting in an increase of speed on the 'A' reactor recirculation pump. As expected, this increased reactor core flow added positive reactivity to the reactor core, thereby raising reactor core power to approximately 102.6%. Within one minute following the transient, the reactor operator lowered reactor power to less than 100%. A notification was made per the Facility Operating License NPF-85 Section 2.E, since a non-compliance with License Condition 2.C.1 resulted, which specifies a maximum power level of 100%. The actual consequences of this event were minimal. A review of Section 15 of the Updated Final Safety Analysis Report showed that this event is bounded by an event explicitly analyzed. The reactor power excursion occurred during an electrical transient when a 500 kilo-volt transmission line tripped during a storm, causing the 'A' M/G set scoop tube positioner to inadvertently increase the M/G set speed. An investigation identified that the inadvertent positioner increase is believed to be due to an increased sensitivity with the scoop tube positioner servo amplifier. The problem is isolated to the 'A' recirculation pump M/G set. Adjustment of this amplifier is planned to be completed by 09/30/94.
3531994009 | Limerick 2 | 08/29/1994 | 11/02/1994 | 9411080248 | <strong>A Core Spray Subsystem was inoperable and the Required Tech Spec Actions Not Taken When a Fuse Was Incorrectly Specified to be Removed by a Clearance</strong><br /><i>Abstract:&nbsp;</i>On 10/3/94, station personnel identified that the Unit 2 'A' Core Spray System (CSS) subsystem had been inadvertently rendered inoperable during planned maintenance on the D21 Emergency Diesel Generator (EDG). Between 8/29/94 and 9/6/94, an approved clearance incorrectly specified removal of a fuse from the D21 EDG breaker auxiliary control power circuit that would prevent the 'A' CSS subsystem from automatically starting. The Technical Specifications (TS) actions were not taken, resulting in a condition prohibited by TS. No transients occurred requiring the affected equipment to perform its design function. The cause of the incorrect clearance was a less than adequate review of the impact of the removal of the fuse by the clearance preparer and reviewer, both licensed operators. Additionally, a non-licensed Instrumentation and Controls work planner incorrectly recommended this fuse be removed. Clearances that would be used in the future for similar maintenance work are being revised to indicate the correct fuse. The recommended blocking contained in the work order library and all scheduled copies for similar work have been revised to ensure the correct blocking is specified. The expectation that recommended blocking is to be researched to ensure that accurate blocking is specified in the clearances will be reinforced to appropriate individuals.
3531994010 | Limerick 2 | 10/19/1994 | 10/13/1995 | 9510240202 | <strong>Reactor SCRAM and Actuation of Various Engineered Safety Features Resulting from a Relay Coil Failure and Inappropriate Action By a Licensed Reactor Operator.</strong><br /><i>Abstract:&nbsp;</i>On 10/19/94, a licensed operator (LO) performing a surveillance test inadvertently de-energized the D24 4KV Safeguard Bus. Immediately following the de-energization, the Reactor Feedwater Pump (RFP) minimum flow control valves fully opened. A reactor SCRAM occurred on low reactor water level, as designed. During the transient, reactor water level reached the low-low level setpoint, and the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection systems received initiation signals. The RCIC system injected to recover reactor water level. Actuation of the Primary Containment and Reactor Vessel Isolation Control System also occurred, as designed, as a result of the vessel low-low water level signal. The reactor shutdown was accomplished with no abnormalities. The reactor SCRAM was caused by the failure of the N-relay coil in the RFP minimum flow control valve control power supply transfer logic. The cause of the N-relay coil failure was insulation breakdown, and is considered isolated. De-energization of the D24 Safeguard Bus occurred due to an inappropriate action by a LO when securing the D24 Emergency Diesel Generator following testing. Corrective actions included a failure analysis of the relay coil, an evaluation of the normal to alternate power supply transfer circuits, and discipline of the involved LO.
3531994011 | Limerick 2 | 12/21/1994 | 01/20/1995 | 9501310239 | <strong>Condition Prohibited by Technical Specifications (TS) in that a TS Surveillance Requirement for the D23 and D24 EDGs was not met due to an Inadequate Review of a TS Change.</strong><br /><i>Abstract:&nbsp;</i>On 12/21/94 during review of the Loss of Coolant Accident/Loss of Offsite Power (LOCA/LOOP) surveillance test (ST) procedures, station personnel discovered that the Unit 2 Emergency Diesel Generators (EDG) D23 and D24 were out of surveillance with respect to the Technical Specifications (TS) Surveillance Requirement (SR) 4.8.1.1.2.e.8.B. This TS SR requires that on an 18 month frequency the capability of the EDGs to perform a 5 minute hot restart be demonstrated. The D23 and D24 EDGs were immediately declared inoperable, and EDG testing was initiated. By 0202 hours on 12/22/94 both EDGs were declared operable. The consequences of this event were minimal in that the EDGs and the offsite AC power sources were fully capable of-performing their safety function during the period in question. The cause of this event was an inadequate review of the 18 month to 24 month refueling outage TS change, and its impact on the LOCA//LOOP ST procedures. The ST procedures were revised on 12/09/94 to a 24 month frequency; however, the procedure sections which demonstrate the 5 minute EDG hot restart should have remained on an 18 month test interval. Corrective actions include revision to the appropriate EDG LOCA/LOOP ST procedures, an analysis of other EDG procedures, and a sample evaluation of station ST procedures potentially impacted by the TS change.
3541994001 | Hope Creek | 03/05/1994 | 03/23/1994 | 9404080013 | <strong>Engineered Safety System Actuation - Isolation and Loss of Shutdown Cooling due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On Saturday, March 5, 1992, a data chart recorder was being installed to support performance of an Operations Department 18 month surveillance test of the Primary Containment Isolation System PCIS/Nuclear Steam Supply Shutoff Systems (NSSSS). During installation of the recorder, in accordance with the procedure, an inadvertent initiation of the 'All Channel NSSSS occurred resulting in a loss of shutdown cooling and a loss of reactor water cleanup. The Instrument and Controls technician (I&C tech - non licensed) installing the recorder was directed to remove the test equipment. The isolation signal was reset, shutdown cooling and reactor water cleanup were placed back in service. The total duration of the loss of shutdown cooling was approximately two minutes. All valve isolations that occurred were expected for current plant conditions. The root cause of this event is personnel error in that the technician interrupted the circuit to install test jacks without prior notification to the SNSS/NSS or his immediate supervisor for concurrence. Corrective actions will include a review of this event with all technicians emphasizing the necessity of understanding the potential consequences of intended actions and the expectation that all monitoring equipment (recorders, etc.) be installed in a non-intrusive manner, unless discussed and agreed with the supervisor and the shift. Additionally, the lead technician involved has been counseled on this event. The surveillance procedure will be revised to incorporate lessons learned and additional test jacks installed as appropriate.
3541994002 | Hope Creek | 03/21/1994 | 04/14/1994 | 9404220143 | <strong>Discovery of past occurrence where operator stood watch on shift in dual role as NSS/STA without meeting STA educational requirements.</strong><br /><i>Abstract:&nbsp;</i>On Monday, March 21, 1994, Hope Creek management confirmed that an operator with a Senior Reactor Operator's license had served on shift in the dual role capacity as Nuclear Shift Supervisor/Shift Technical Advisor (NSS/STA) without meeting the educational requirements for the STA position. The individual has not served on shift since January 1991. Hope Creek Technical Specification Table 6.2.2-1, footnote '*', states that an individual may serve on shift in the dual role capacity of NSS/STA if the individual 'has a Senior Reactor Operator's (SRO) license and is a qualified STA, and has a Professional Engineer's license... or a bachelor's degree in a scientific, engineering or engineering technology discipline... ' Since the individual did not have a Professional Engineer's license or bachelor's degree when serving as STA, the requirements of this Technical Specification were not met. <br /><br /> This incident posed minimal safety significance since, while not having a bachelor's degree, the individual had completed significant course work in mechanical engineering and successfully trained for and received an SRO license. Corrective actions include terminating the employment of the subject individual, verifying that all individuals currently performing STA duties at Hope Creek Generating Station meet the educational requirements of footnote '11 and conducting an independent investigation. The results of this investigation will be used to assess and strengthen our current employee qualification process.
3541994003 | Hope Creek | 04/05/1994 | 05/04/1994 | 9405090207 | <strong>Engineered Safety System Actuation - Loss Of Shutdown Cooling Due Nuclear System Supply Shutoff System Actuation On False High Pressure Signal</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, April 5, 1994, at 1616 hours, a loss of shutdown cooling occurred due to an inadvertent high reactor pressure isolation signal. All systems and components functioned as required for the existing plant conditions. Control room personnel verified all automatic actions were completed and instructed Instrument and Controls technicians (I&C techs) to investigate the cause of the inadvertent pressure signal. As technical specification did not require the logic to be operable under current plant conditions, the isolation signal was bypassed to permit restoration of shutdown cooling while troubleshooting was conducted. The I&C techs reported back that the pressure transmitters associated with the logic were valved out of service. They also believed that with the transmitters isolated, thermal expansion of the water in the isolated transmitter may have caused the spurious high pressure signal. It was decided to vent the transmitter after which the indicated pressure returned to a nominal value. As the cause of the malfunction was understood it was decided to return the isolation logic to normal operation. When the I&C techs cleared the bypassed isolation logic a second isolation occurred. This was due to the logic being placed in service without first resetting the logic. Control Room personnel reset the isolation logic and returned shutdown cooling to service. The root cause of this event was procedural inadequacy. A contributing factor to the second isolation was an inadequate troubleshooting plan. Procedures will be revised to ensure the transmitters are returned to service prior to the isolation logic being restored.
3541994004 | Hope Creek | 04/19/1994 | 05/18/1994 | 9405250065 | <strong>Engineered Safety System Actuation - Main Steam Isolation Valve Closure due to procedural defficinecy</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, April 19, 1994, with the plant in Operational condition 4, Control Room personnel were performing a reactor coolant system pressure boundary test, in support of the fifth refuel outage. Reactor coolant system heat up was in progress with the reactor pressurized to approximately 500 PSIG. A number of additional activities involving scheduled repair, surveillance testing and system restorations were also being performed in support of the outage One of the activities which had been approved for work involved testing of the turbine combined intermediate valves. At 0827 hours, an inboard Main Steam Isolation Valve (MSIV) closure was received. The Nuclear Control Operator (NCO -RO licensed) verified all appropriate automatic actions were complete, verified reactor pressure was within allowable limits and terminated other surveillance tests which could have caused the isolation. The MSIV closure was initiated due to a low vacuum condition with the turbine stop valves open. The turbine stop valves had been opened under the direction of the Instruments and Controls (I&C) test procedure for the combined intermediate valve testing. The turbine stop valves were closed, the MSIV isolation logic was reset and the MSIV's were reopened to support the pressure boundary testing. The root cause of this event was procedural deficiency. Contributing factors were personnel error and inadequate communications during the pre-job briefing. Procedures for both the vessel hydro and turbine valve testing will be revised. Personnel will be counseled on proper communications and work control practices.
3541994005 | Hope Creek | 04/20/1994 | 05/18/1994 | 9405250271 | <strong>Engineered Safety Feature Actuation - Residual Heat Removal System isolation due to design deficiency.</strong><br /><i>Abstract:&nbsp;</i>On 4/20/94, control room personnel were performing an 18 month reactor pressure vessel hydrostatic surveillance test as the fifth refuel outage was nearing completion. Concurrent activities included scheduled repair, testing and system restorations in preparation for plant startup. One of the activities involved removal of the reactor protection system (RPS) motor-generator (MG) set for bearing replacement which required the "B" RPS bus to be powered via its alternate power supply. At 0005 hours the nuclear control operator (NCO - RO licensed) initiated a start of the "C" station service water pump. When the pump started the alternate RPS power supply electric protection assembly (EPA) breaker tripped resulting in a loss of RPS power, actuation of the Nuclear Steam Supply Shutoff System (NS4) logic and closure of the outboard main steam line drain valves. The NCO verified all appropriate automatic actions were complete and verified reactor pressure was within the allowable limits of the vessel pressure/temperature curves. The RPS EPA was reset, the NS4 logic was reset and the steam line drains were reopened. Initial investigation determined the breaker had tripped on undervoltage when the service water pump was started. operation continued on the alternate power supply, until the M-G set was returned to service, with no further incidents. The root cause of this event is design deficiency. Less than timely implementation of corrective actions was a contributing factor for this event.
3541994006 | Hope Creek | 04/26/1994 | 05/24/1994 | 9405310061 | <strong>Engineered Safety Feature Actuation - Actuation of the Nuclear Steam Supply Shutoff System outboard isolation System due to loss of logic power.</strong><br /><i>Abstract:&nbsp;</i>On 4/26/94, control room personnel were performing a reactor startup following completion of the fifth refuel outage. At 0504 hours, an actuation of the nuclear steam supply shutoff system (NS4) occurred resulting in a closure of the main steam line drain valves, reactor water sample valve and a reactor water cleanup system isolation. The NCO verified all appropriate automatic actions were complete. Initial investigation determined the isolation was due to a loss of the reactor protection system (RPS) motor generator (MG) set which powers the NS4 logics. The power supply was switched to the alternate feed, the NS4 logic was reset and all isolation valves were returned to their normally open positions. The root cause of this event is equipment failure. A tank heater in the radwaste system had shorted resulting in a ground fault trip of the feeder breaker for the motor control center powering the above equipment. The heater has been replaced but will remain de-energized until the root cause of the failure is determined. Additionally, engineering is currently reviewing the ground fault protection scheme to determine if changes are warranted to prevent similar occurrences where an entire motor control center is tripped due to a ground fault on an individual component.
3541994007 | Hope Creek | 05/15/1994 | 06/14/1994 | 9406210369 | <strong>Engineered Safety Feature Actuation - Reactor scram on low level due to design and training deficiencies.</strong><br /><i>Abstract:&nbsp;</i>On Sunday May 15, 1994 at 1207 hours Nuclear Control Operators (NCO - RO licensed) commenced a reactor power reduction from 100% to 95% to remove the 'A' Reactor Feed Pump (RFP) from service for planned maintenance to repair a bearing temperature problem. At 1300 hours the 'A' RFP was secured from feeding the reactor vessel and at 1315 operators began a power increase to 100% of rated using the reactor recirc pumps. At 1317, and 1318 respectively, the new Digital Feedwater Control System (DFCS) automatically transferred the remaining 'B' & 'C' RFP's speed control from auto to manual. Reactor water level began to decrease due to the feedpumps being in manual and the increase in power from recirc pump speed increases. At 1322 the NCO received a Level 4 alarm (+30 inches) and an invalid intermediate runback occurred on the 'A' reactor recirculation pump. The control operator attempted to restore reactor level by manual operation of the 'B' and 'C' feedpumps. Due to the non linear response of the newly installed DFCS, operators could not mitigate the level transient resulting in a low reactor level scram at 1325. The root causes of this event were attributed to design deficiencies associated with enhancements made to the DFCS and inadequate training for manual operation of the new control system. Corrective actions included design changes to correct problems noted in the DFCS and additional simulator training with the feedwater controls.
3541994008 | Hope Creek | 06/02/1994 | 06/30/1994 | 9407060094 | <strong>Condition prohibited by Plant Technical Specifications - noncompliance with technical specification 3.3.7.11, action for out of service radiation monitoring instrumentation.</strong><br /><i>Abstract:&nbsp;</i>On Thursday, June 2, 1994, Instrument and Controls technicians (I&C techs - non licensed) requested permission to remove the south plant vent (SPV) radiation monitor from service to perform a sensor calibration. The rad monitor being tested had been inoperable from the previous day and alternate sampling had been instituted in accordance with the requirements of technical specification 3.3.7.11 for that monitor. Supervisor (NSS - SRO licensed), and as a limiting condition for operation (LCO) had been entered the previous day for the rad monitor, the NSS granted permission for the work to begin. The test was started at 0915. At 1500 hours, the Senior Nuclear Shift Supervisor (SNSS - SRO licensed) requested an update on the status of the testing prior to the afternoon turnover meeting. During the review of the test progress it became apparent that the testing had removed the entire skid from service which required additional actions. A review of technical specification 3.3.7.11 revealed that an action to estimate the flow once every four hours had been missed. Flow rate estimates were performed at 1600 hours as required for the specification. The SPV skid was returned to service at 1653 on 6/5/94. The root cause of this event was personnel error. Less than adequate review of the work package prior to the start of the activity resulted in a missed technical specification action. The supervisor who approved the work was counseled in regard to improper work practice.
3541994009 | Hope Creek | 07/18/1994 | 08/17/1994 | 9408230065 | <strong>Condition prohibited by Plant Technical Specifications - noncompliance with technical specification 3.3.7.4, Remote Shutdown System controls.</strong><br /><i>Abstract:&nbsp;</i>During the Hope Creek fifth refuel outage, plant personnel performing an 18 month surveillance test of the remote shutdown system (RSS), discovered a design deficiency in the original plant design. The deficiency resulted in a technical specification non-compliance as the remote shutdown system redundant control for a single residual heat removal system suction valve would not operate as required. The incident report investigation and interim corrective actions were completed prior to reactor startup on April 25, 1994. In July a design change, which installed a new type control switch, was implemented as the permanent corrective action. The new control switch failed its post installation retest and a second incident report was generated. The root cause of the second failure was a personnel error. The control circuit wiring was revised and the valve tested satisfactorily. During a review of the second incident, and the corrective action closeout for the first event, it was determined that the initial event met the reporting requirements of 10CFR 50.73 and that an LER was required. Corrective actions for this event include counseling for the engineer who prepared the design change, as well as the Operations and Technical department personnel responsible for reviewing the initial event for reportability. Additional corrective actions include revising the 18 month RSS surveillance test and performing an evaluation of the surveillance and post maintenance retest program to determine if modifications are required.
3541994010 | Hope Creek | 07/20/1994 | 08/24/1994 | 9408300063 | <strong>Condition prohibited by Plant Technical Specifications - noncompliance with technical specification 3.6.5.3, Filtration, Recirculation and Ventilation System due to a missed surveillance</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1994, during a work order system computer scan, as part of an unrelated investigation, personnel in the Planning and Scheduling Department discovered that a work order for a monthly surveillance test, of the Filtration, Recirculation Ventilation System (FRVS), was not closed out properly. The scan focused on work orders that were not printed but updated as 'work complete'. A review of the scan results determined that the work order activity had been taken to the work complete stage, but that no record of a completed surveillance test or hard copy of the work order existed. They presented the finding to operations and Quality Assurance personnel who could not find any evidence of the surveillance being performed. All monthly FRVS surveillance tests were verified to have been performed since this event. <br /><br /> Additionally, a review of all surveillance tests that were statused work complete, from the institution of the current work order system in 1987, was performed to ensure they had been completed. The root cause investigation determined that the work order was mistakenly updated by personnel in the work control center. Corrective actions are to continue monitoring the work order system with a similar search that uncovered this discrepancy and review of this event in continuing training.
3541994011 | Hope Creek | 08/01/1994 | 08/28/1994 | 9409060081 | <strong>Reactor Protection System actuation - Reactor Scram During routine surveillance testing due to faulty test equipment</strong><br /><i>Abstract:&nbsp;</i>On 8/1/94, Instrument and Controls technicians (I&C techs non-licensed) were in the process of installing measuring and test equipment (M&TE) in order to perform an intermediate range neutron monitor (IRM) surveillance. As the final connection was being made, a spark occurred at the connector shocking the technician and causing two average power range monitors (APRM's) (one each in channel A and B) to invalidly indicate upscale high initiating a reactor scram. The plant response was per design and the operator response was appropriate and effective. The root cause was a damaged isolation transformer that placed a 120VAC signal on the IRM C cable shield. The voltage on the IRM C cable shield induced currents in the adjacent LPRM signal cables resulting in a sensed false high neutron flux input to APRM's C and D. Additionally, failure to inspect the test equipment prior to use, failure to perform routine activities which the technicians are trained to perform and inadequate procedural guidance to enable the testing to be performed in a safe manner, collectively contributed to this event. corrective actions for this event include a program to provide periodic maintenance and inspection of non-calibrated test equipment and a review of the event with appropriate personnel for lessons learned in regard to the hazards to personnel and the plant when working with intentionally ungrounded equipment. Personnel have been instructed that any equipment which has been inadvertently bumped or dropped must be checked and repaired prior to use. Additionally, all procedures which utilize 'floated' test equipment will be revised, as necessary, to provide clear instructions within the body of the procedure on how test equipment is to be 'floated' and checked for personnel safety.
3541994012 | Hope Creek | 08/30/1994 | 09/29/1994 | 9410040259 | <strong>Reactor Protection System and Engineered Safety Actuation: Safety Auxiliaries Cooling System isolation actuation and subsequent reactor scram.</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, August 30, 1994, with the plant operating at 100% power, Maintenance department personnel were performing 24 month environmental qualification preventive maintenance on a fuel pool heat exchanger motor operated valve. During the course of the inspection, at the valve operator, a short circuit occurred which caused a trip of the logic system for the associated channel. The loss of the logic power resulted in a partial isolation of the 'A' Safety Auxiliaries Cooling System (SACS) which was supplying the Turbine Auxiliaries Cooling System (TACS) at the time of the event. This resulted in a loss of cooling water to the turbine-generator coolers as well as other nonessential loads. The 'B' SACS loop auto initiated per design to supply TACS, but due to the incomplete isolation of the 'All SACS loop, the 'B' SACS loop isolated on low head tank level as water transferred from the 'Bit to 'All head tanks. A turbine-generator load runback resulted from the loss of cooling followed by a reactor scram on high pressure (1037 PSIG). Following the scram operators were able to restore the 'A' SACS loop to supply TACS. The root causes of this event were an incorrectly sized fuse in a logic module and failure of the standby SACS loop to supply TACS loads. Corrective actions included installing the proper size fuse, a check of the components downstream of the oversized fuse, work practice changes regarding both fuse replacement and energized work. Additionally a design review of the SACS transfer scheme will be conducted, as well as a review of this event during continuing training with all departments involved in this event.
3541994013 | Hope Creek | 09/15/1994 | 09/06/1995 | 9509150093 | <strong>Condition Prohibited by the Plant Technical Specifications - Noncompliance with the shift manning requirement of technical specification 6.2.2.a, shift manning requirements</strong><br /><i>Abstract:&nbsp;</i>This supplemental LER is being submitted to provide additional information concerning an alleged event which is assumed to be valid and was discussed in the previous supplement, and to provide an update on the corrective actions. The original LER, and the first supplement, were submitted due to occurrences of not meeting the requirements of Tech Spec 6.2.2.a. The LER is being reported under 10CFR50.73(a)(2)(i)(B). The root cause of one of the events was attributed to less than adequate administration of the guidelines contained in NUREG 1262. The root cause of the other events was attributed to personnel error as the NSS's involved allowed themselves to become distracted by other activities and inadvertently left the control room area. Corrective actions for these events include administrative procedure changes regarding proficiency requirements, a review of the NUREG with appropriate personnel, and inclusion of the requirements in operators requalification training. A mechanical restraint is currently being placed over a watchstander's security badge to prevent personnel who are meeting the control room manning requirements from carding out of the area. The Senior Nuclear Shift Supervisor and NSS's involved in these events have also been counseled and disciplined as appropriate.
3541994014 | Hope Creek | 10/02/1994 | 10/31/1994 | 9411040294 | <strong>Reactor Protection System Actuation - Invalid Main Turbine trip results in reactor scram due to design deficiency</strong><br /><i>Abstract:&nbsp;</i>On Sunday evening, October 2, at 2036, with the unit operating at 100% of rated power, a reactor scram occurred due to a sudden trip of the main turbine generator. The main turbine trip and trip of the 'B' reactor feed pump were not preceded by any alarms or indications of a problem with either component. Control room personnel took appropriate actions to verify the scram and that all automatic actions were complete. A review of the alarm chronolog did not indicate the source of the turbine trip. A review of the turbine first hit panel (local EHC cabinet) indicated the customer trip (Reactor Level 8 @ +54'), caused the main turbine trip. The main turbine control valve closure input to RPS provided the scram signal. The turbine trip resulted in a high reactor pressure above the LO-LO SRV setpoint for H and P valves and opening of 'K' on its safety valve function. In addition a dual recirc pump trip and alternate rod insertion signals were provided when pressure increased above the ARI and RRCS initiation setpoints. The reactor water cleanup isolation valve 1BG-HV-F001 also closed due to level instrument ringing. The cause of the main turbine trip and subsequent scram, was due to a design deficiency in the Digital Feedwater Control System (DFCS). The design was to require two redundant high level signals to cause a main turbine trip. The system was actually configured such that either of two signals would trip the turbine. Corrective actions included a design change to correct the deficiency, as well as, testing of the bailey logic card which is suspected of failing and initiating this event. The Engineering department has also completed a review of the DFCS and is confident that critical portions of the system have been designed, installed, modified and tested appropriately to assure proper operation.
3541994015 | Hope Creek | 10/07/1994 | 11/04/1994 | 9411080242 | <strong>Reactor Protection System Actuation - Main Turbine Trip due to component failure in Electro Hydraulic Control System.</strong><br /><i>Abstract:&nbsp;</i>On Friday, October 7, 1994, with a reactor startup in progress, operators were preparing to roll the main turbine generator. The reactor was operating at approximately 15% of rated with 6 turbine bypass valves open. The Nuclear Control Operator (NCO - RO licensed) had selected the 100 RPM speed demand at the Electro Hydraulic Control System (EHC) panel which should have brought the turbine to the selected speed. The NCO monitoring the turbine roll initially observed normal responses from the Turbine Stop Valves (TSV's) position indicators, the 'all valves closed' light extinguishing and the 'speed increasing' light illuminating. The operator then observed that all turbine bypass valves had closed. This unexpected response was immediately recognized and communicated to other control room personnel by both the NCO and Shift Technical Advisor (STA - SRO licensed). Control room personnel concurrently noted turbine speed had exceeded the 100 RPM selected speed and was accelerating rapidly. The Nuclear Shift Supervisor (NSS - SRO licensed) directed the NCO to trip the main turbine. The NCO recommended to shut down the turbine by selecting 'all valves closed'. When the turbine 'all valves closed' was selected and the valves began to close, a reactor scram occurred. The root cause of this event was attributed to failed components in the EHC control circuit. A contributing factor was operators not recognizing the abnormal plant conditions indicated on the EHC panel when the turbine was reset prior to initiating the turbine roll. Corrective actions included replacement of the EHC card, revising the turbine roll procedures and expanding operator training to include actions to be taken when abnormal plant responses are noted.
3541994016 | Hope Creek | 11/02/1994 | 11/30/1994 | 9412050225 | <strong>Engineered Safety System Actuation - Emergency Diesel Generator start due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, November 2, 1994, with the plant operating at 100% of rated power, control room personnel received alarms and indications of a diesel generator start. The Nuclear Control Operator (NCO - RO licensed) verified the diesel generator had started and observed that it had not loaded onto its associated bus, and that no valid start signals (Loss of Coolant or Bus Feeder Undervoltage) were present. The NCO dispatched an Equipment Operator (NEO - non licensed) to check the diesel and the local relay indicators. The NEO reported that the diesel was running unloaded and that the local relays were in the normal (reset) condition. Instrument and Controls Technicians (I&C techs) were also dispatched to verify that the diesel did not receive a start signal via the logic channel. Operators secured the diesel and returned it to a standby lineup. A root cause investigation was initiated which later determined that a technician working in a diesel relay cabinet had unknowingly started the diesel when he bumped against a diesel start relay. The technician was preparing to perform a test of a low oil pressure alarm circuit. The root cause of this event was attributed to improper work practices by the technician and less than adequate planning and risk assessment on the part of the supervisor. The technician involved in this event has been counseled in regard to the improper work practice. The work supervisor involved in this event has been counseled in regard to the improper work planning and less than adequate risk assessment. This event will also be reviewed with all I&C technicians and supervisors for lessons learned.
3541994017 | Hope Creek | 11/10/1994 | 12/08/1994 | 9412120191 | <strong>Single condition which could have affected the operation of multiple systems - failure of cooling water isolation valves for diesel generators to stroke open</strong><br /><i>Abstract:&nbsp;</i>On Saturday, October 22, 1994, during performance of a quarterly In Service Test of the Safety Auxiliary Cooling System (SACS) two room cooler isolation valves failed to stroke open. The valves were associated with the diesel room coolers for the 'B' and 'D' diesel generators. The valves are air operated and designed to fail open on loss of air to the actuator. The valves were mechanically agitated and subsequently stroked open. The air supply to these two isolation valves was tagged closed and the valves were left in the open position to ensure the safety function to provide cooling in the diesel generator room was satisfied. System Engineering was contacted and informed of the failure as this was a repeat of a similar condition identified in September of 1993. System Engineering immediately initiated a root cause investigation to determine the cause of the stroke failures. On November 10, 1994, the investigation determined that a common mode failure existed and that the condition was reportable. The valve stroke frequency was increased to weekly from quarterly because at this frequency no failures have been noted. The root cause of this event is design deficiency. All valves will be stroked weekly until the packing configuration is corrected.
3541994018 | Hope Creek | 12/07/1994 | 01/04/1995 | 9501100243 | <strong>Discovery of a design defficency common to the redundant Station Service Water Traveling Screens.</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, December 7, 1994, a design deficiency was discovered associated with the Service Water (SW) System Traveling Screen Spray Wash Booster Pump flow sensing device. The determination of a design deficiency was made while System Engineering was performing a root cause investigation into a setpoint discrepancy noted during a calibration of the flow sensor. The deficiency could result in the SW traveling water screen (TWS) operating without the booster pump being in service. Interim actions were initiated to have operations personnel verify booster pump operation hourly for all in service TWS from the control room and increased frequency of operator rounds which includes a check of pump flow and spray nozzle cleanliness locally. The root cause of this event is a design deficiency incorporated into the initial plant design. A design change has been prepared to eliminate the use of the flow switch in the traveling screen logic and verify booster pump operation via pump breaker position.
3541994019 | Hope Creek | 12/13/1994 | 01/11/1995 | 9501200014 | <strong>Unplanned Inoperability of the High Pressure Coolant Injection System due to water contamination of the lubricating system.</strong><br /><i>Abstract:&nbsp;</i>On 12/13/94, results of a High Pressure Coolant Injection (HPCI) system oil sample indicated a moisture content above the limit specified for turbine operation. At approximately 0400 hours, Operations personnel had drawn a sample of the HPCI oil reservoir for a routine monthly sample analysis. The sample was taken to the counting room prior to removal from the Radiological Controlled Area and checked for contamination. At approximately 1130, Chemistry personnel, who perform the contamination check, notified the HPCI System Engineer that the sample appeared milky with some separation at the bottom of the sample bottle. Based on this information two additional samples were requested by the System Engineer. The additional samples were drawn at approximately 1315, one by the normal method at the auxiliary oil pump (AOP) discharge and another taken by dipping the reservoir. Both samples appeared milky and HPCI was declared inoperable at 1455 based on the visual indication of water in the oil. All three samples were delivered to the on-site lab and were analyzed for water content. The results were provided at 1630. The two samples taken from the AOP discharge had 4.0% water and the one dipped from the reservoir had 1.5% water. All three samples exceeded the water content limit of 0.2%. The root cause of this event is steam leakage through the turbine steam admission valve. Corrective actions include increased sampling of the reservoir, design changes and repair of the steam admission valve in the upcoming outage.
3611994001 | San Onofre 2, San Onofre 3 | 02/10/1994 | 03/14/1994 | 9403280065 | <strong>Manual ESF Actuation Of TGIS To Satisfy Tech Spec Action Statement</strong><br /><i>Abstract:&nbsp;</i>At 1520 on February 10, 1994, Train A of the Control Room Toxic Gas Isolation System (TGIS) VI! was manually actuated as required by Technical Specification 3.3.2, "Engineered Safety Features Actuation System Instrumentation," Action Statement B when both trains of TGIS instrumentation became inoperable. Train A was inoperable due to sample pump replacement. Train B became inoperable at approximately 1430 when the discharge fire-damper of Control Room Cabinet Area Emergency Unit E426 became inoperable during surveillance testing. Train A TGIS components operated correctly. E426 was restored to operability at 1640 and TGIS Train A was reset at 1730. <br /><br /> The cause of E426 inoperability was the inadvertent dropping into the ventilation duct, during an 18-month surveillance test, of the fusible link that holds the discharge fire damper of E426 open. Corrective action was to retrieve and reinstall the fusible link, thereby restoring the fire damper to operability, and to reset TGIS Train A. No further corrective action is required for this event; however, the timing of the surveillance of the fire damper associated with E426 with respect to potential cross-train impact is being reviewed separately for lessons learned. <br /><br /> Because TGIS Train A was manually actuated and operated as designed, this event had no safety significance. Additionally, there was no toxic gas present.
3611994002 | San Onofre 2, San Onofre 3 | 03/16/1994 | 04/19/1994 | 9404250095 | <strong>Missed Fire Protection Surveillance</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1994, during a review of fire protection [KP] surveillances, Edison noted that an 18 month Technical Specification (TS) visual inspection of fire water spray nozzles for Train B Control Room Emergency Air Cleanup System (CREACUS) [VI] charcoal filters may not have been performed in August 1992 as required. <br /><br /> On March 16, 1994, Edison's search for the missing surveillance record concluded that the visual surveillance for the CREACUS Train B units spray nozzles required by TS 4.7.8.2, 'Spray and/or Sprinkler Systems,' had not been performed when required in August 1992. During a review of past surveillances, Edison concluded, on March 28, 1994, that the previous two 18 month TS visual inspections of the fire water spray nozzles for the Hydrogen Purge Exhaust [BB] units 2A082 and 3A082 for Units 2 and 3, respectively, had not been performed in early 1991, and late 1992 as required. Edison is reporting this event in accordance with 10CFR50.73(a)(2)(i). <br /><br /> These surveillances were missed due to inattention to detail during revisions of the fire protection surveillance procedure. <br /><br /> On March 17, 1994, Edison completed the TS required visual surveillance of the CREACUS Train B units spray nozzles. On April 8, 1994, Edison completed the TS required visual surveillance of the Hydrogen Purge Exhaust units spray nozzles.<br /><br /> Edison will reemphasize the need to follow guidelines for procedure revisions.
3611994003 | San Onofre 2, San Onofre 3 | 04/22/1994 | 01/17/1995 | 9501250380 | <strong>Missed Fire Protection Surveillances Due to Inattention to Detail and Lack of Management Oversight</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1994, during a reliability centered maintenance review of the Fire Protection System, Edison noted that a three year Technical Specification (TS) air flow test for six manual deluge open head spray/sprinkler system had not been performed for the following components: <br /><br /> Unit 2 Charcoal Filter for Containment Hydrogen Purge Exhaust (2A- 082) <br /><br /> Unit 3 Charcoal Filter for Containment Hydrogen Purge Exhaust (3A- 082) <br /><br /> Two Common Charcoal Filters for Control Room Emergency Ventilation (A-206 & 207) <br /><br /> Two Common Charcoal Filters for Control Room Emergency AC (E-418 & 419) <br /><br /> Additionally, on May 9, 1994, Edison discovered that a 31 day operability TS surveillance for a Unit 2 containment recirculation unit filter (CRUF) manual isolation valve was not being performed. Edison reported these occurrences in accordance with 10CFR50.73(a)(2)(i), and is submitting this supplemental report to identify the causes of the missed surveillances. <br /><br /> These missed TS surveillances were caused by individual inattention to detail and lack of management oversight during procedure revision processes. <br /><br /> On May 13, 1994, Edison completed the required air flow surveillance tests for the six manual deluge open head spray/sprinkler systems and confirmed the systems were operable. Based on a review of Unit 2 Cycle 7 refueling outage documentation, Edison has confirmed that the CRUF manual isolation valve is in its correct (locked open) position. Edison has reviewed all Fire Protection Equipment listed in TS Table 3.7-5 and confirmed that all other required testing is being accomplished. Edison has developed the necessary administrative controls for the required surveillances.
3611994004 | San Onofre 2 | 06/19/1994 | 09/29/1994 | 9410050186 | <strong>Inoperable Emergency Chilled Water System</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1994 at 1410, with Unit 2 at 98 power, Edison removed high pressure safety injection (HPSI) pump P017 from service for maintenance and declared the pump inoperable. The two other HPSI pumps, and thus both HPSI trains, remained operable. maintenance was also planned for ECWS room cooler ME417 (the cooler for the room containing HPSI pump P017) and it was also declared inoperable. When equipment control planners scheduled the work for ME417, they failed to recognize that Technical Specification (TS) 3.7.10, 'Emergency Chilled Water System' would be applicable. When ME417 was removed from service on June 19, 1994, the action statement for Technical Specification (TS) 3.7.10, should have been entered, but was not. On June 23, at 0730, when the control room supervisor identified that TS 3.7.10 should have been entered, the associated time limits of TS 3.7.10.b had been exceeded; Therefore, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). Edison completed the TS 3.7.10.b required verifications at 0840 on June 23, 1994 and returned cooler ME417 to service at 1115 on June 23, 1994. <br /><br /> This event occurred due to an incomplete and inadequate evaluation of the work planned for P017 and ME417 and was compounded by an incomplete evaluation of an alarming control room annunciator (cognitive error). <br /><br /> Edison has coached all individuals directly involved and has reviewed this event with the operating crews and shift technical advisors (STAs). In a separate one-hour 'standdown' meeting with each crew, the operations Manager clarified management's expectations regarding attention to detail, and the need to consider the broader implications of planned work. Additionally, guidance will be developed identifying elements associated with effective document review. The Annunciator Response Good Operating Practices will also be reviewed by the operating crews.<br /><br /> There was minimal direct safety significance to this event.
3611994005 | San Onofre 2 | 10/12/1994 | 11/08/1994 | 9411220400 | <strong>Voluntary Tech Spec 3.0.3 Entry Due to Declaring Both Trains of ECCS Inoperable in Mode 1</strong><br /><i>Abstract:&nbsp;</i>On 10/12/94, with Unit 2 in Mode 1 at 98% power, first stage pressure reducing valve [RG] 2PCV6418 in the Backup Nitrogen System (BNS) supply to the Train B Component Cooling Water (CCW) System [CC] surge tank, was found to be leaking nitrogen to atmosphere. Valve 2PCV6418 was isolated for replacement, rendering Train B CCW BNS inoperable. Edison declared Emergency Core Cooling System (ECCS) [BQ] [BP] [CB] [CA] Train B inoperable, replaced valve 2PCV6418, and returned Train B CCW BNS and Train B ECCS to service. However, on 10/12/94, Edison had administratively removed a Train A Shutdown Cooling System (SDCS) [BP] valve from service to perform planned motor operated valve actuator testing, and had conservatively declared ECCS Train A inoperable. <br /><br /> Edison considers the SDCS to be part of the ECCS and conservatively requires the SDCS to be operable in Modes 1 - 3, a requirement not mandated by the TS. When Train B of the ECCS became inoperable with Train A administratively controlled as if it were inoperable, Edison conservatively treated the inoperability of train B CCW BNS as if both trains of ECCS were inoperable, a condition not allowed by the TS. Edison administratively entered TS 3.0.3 for 35 minutes.<br /><br /> Edison's evaluation is that the valve malfunction was due to a small accumulation of dirt in the close fitting parts of the relief mechanism. Edison replaced the leaking BNS valve and determined that no further corrective actions are required.
3611994006 | San Onofre 2, San Onofre 3 | 10/23/1994 | 11/18/1994 | 9411300297 | <strong>Violation of Technical Specification 6.2 Shift Manning</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1994, with both Units 2 and 3 in Mode 1 at approximately 98% power, an NRC resident inspector was in the control room area to observe a planned plant evolution. Upon entering the control room, it was not immediately apparent if the required number of Senior Reactor Operators (SRO) were in the control room area. Edison, in response to an NRC question, determined that both onshift Control Room Supervisors (CRSs) had been outside the Technical Specification (TS) defined control room area and had met at the work authorization control (WAC) desk to discuss a planned work activity for a few minutes (See attachment 2). The WAC desk is located outside the control room area as defined by the current TS by a few feet, but within 'audible range' of the Control room operators. Because the Shift Superintendent (SS) was touring the plant and was not in the control room area, the manning requirements of the TS 6.2.2 were not satisfied for a few minutes. Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). <br /><br /> The onshift SROs did not have a clear understanding of the control room area boundaries as described in TS figure 6.2-3. The lack of an obvious boundary contributed to the misunderstanding of the actual boundary by the CRSs. As a result, the CRSs did not realize that they had inadvertently stepped outside the TS defined control room area, violating TS 6.2.2. <br /><br /> Edison has revised administrative procedure SO123-0-30, 'SHIFT MANNING,' to clarify and place more restrictive administrative limits on the allowable movement of the SRO holding the Control Room Command Function about the Control room area. requirements. A preshift brief was given on the procedure revision to each crew. There was minimal safety significance to this event.
3621994001 | San Onofre 3 | 04/12/1994 | 05/25/1994 | 9406020094 | <strong>Containment Emergency Sump Level Instrument Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 16, 1994, with the Unit 3 in mode 1, at 96 percent power, channel B containment emergency sump level (CESL) lumigraph indicator 3LI-9389-2 was observed with no light bars illuminated. In accordance with station procedures, operators (Utility, licensed) verified channel B CESL indication on the Qualified Safety Parameter Display System (QSPDS). Based on a normal QSPDS indication, operators believed that the indication was operable and only the lumigraph was inoperable. On April 20, 1994, during maintenance for 3LI-9389-2, it was discovered that a signal converter in the instrument loop had failed, not 3LI-9389-2.<br /><br /> Technical Specification (TS) 3.3.3.6 'Accident Monitoring Instrumentation' and TS 3/4.5.2, 'ECCS Subsystems, T(ave) greater than 350 degrees,' allow one train of CESL to be inoperable for 7 days and 72 hours respectively. Subsequent review of plant historical data determined that the signal converter had failed on April 12, 1994. Therefore, Edison realized that the out of service time limits of TS 3.5.2 and 3.3.3.6 had been exceeded and is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). <br /><br /> Edison replaced the failed signal converter on April 20, 1994. Additionally, because the design of the CESL input to QSPDS delayed diagnosis of the failed signal convertor, Edison will evaluate and implement potential changes to QSPDS if appropriate.
3621994002 | San Onofre 3 | 09/12/1994 | 10/11/1994 | 9410170079 | <strong>Class 1E 4 kV Bus Loss of Voltage Due to Jarring of Door-mounted Protective Relay</strong><br /><i>Abstract:&nbsp;</i>On 09/12/94, at 1237, with Unit 3 at approximately 97 percent power and all relevant systems and components operable, the normal supply breaker to bus 3A06 [EA] opened due to an inadvertent actuation of its overcurrent lockout relay, causing a momentary loss of voltage on bus 3A06 and a Loss of Voltage signal. The power supply for bus 3A06 automatically transferred to Unit 2 through the bus cross tie. The associated Unit 3 diesel generator automatically started and remained unloaded, as designed. The momentary loss of voltage also resulted in a Train B Toxic Gas Isolation Signal and associated component actuations, as expected. <br /><br /> The cause of this event was inadvertent actuation of the breaker due to mechanically induced actuation of its overcurrent lockout relay. When a utility maintenance worker attempted to repair a door fastener, the worker jarred the door, causing contacts on the relay to actuate, opening the breaker. <br /><br /> Edison restored normal power to bus 3A06 within the 72 hours allowed by the Technical Specifications. The maintenance worker was reminded of the need to be careful not to bump or jar panels or cabinets that may contain relays which could cause a plant trip or ESFAS actuation. Report and will implement further corrective actions, if required.
3641994001 | Farley 2 | 08/05/1994 | 09/02/1994 | 9409160118 | <strong>Manual Turbine/Reactor Trip due to Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>At 1459 on August 5, 1994, with the Unit in Mode 1 and operating at approximately 100 percent reactor power, the main turbine was manually tripped due to degrading condenser vacuum. This manual trip of the main turbine from 100 percent power initiated a reactor trip as designed.<br /><br /> Previous to the trip, work had been performed on a low pressure turbine gland seal regulator to repair a steam leak. Upon valving the regulator in after the repair, it was noted that the gland seal steam pressure was being maintained slightly above the normal band as indicated on the local pressure indicator. The regulator was adjusted to lower the gland seal pressure to the proper range as indicated on the local pressure gauge. This adjustment was made by an Instrument and Controls technician who was assisted by an Operations systems operator. The local pressure indicator was subsequently determined to be inaccurate and actual gland seal pressure was too low to prevent air in-leakage into the main condenser. Shortly after completion of the above adjustments, condenser vacuum degraded rapidly, and upon reaching the administrative main turbine manual trip criteria of 2.7 psia, the control room operators tripped the main turbine. This initiated an automatic reactor trip per design. The Operations crew responded to the reactor trip as directed by plant procedures. The faulty gauge was replaced and the Unit was returned to service.
3641994002 | Farley 2 | 12/14/1994 | 01/10/1995 | 9501180133 | <strong>Surveillance Not Performed on Service Water Pumps' Lube and Cooling Valves</strong><br /><i>Abstract:&nbsp;</i>At 1652 on 12/14/94, with the Unit 2 reactor in mode 1 operating at 100 percent reactor power, it was determined during a surveillance schedule review, that the required surveillance for the Unit 2 service water pumps' lube and cooling valves had not been performed and had exceeded the allowable grace period. Failure to perform this inservice test within the specified surveillance interval required the A and B train service water systems to be declared inoperable. The missed surveillance test was performed satisfactorily and completed by 1747 on 12/14/94. <br /><br /> This event was caused by cognitive personnel error. The last date performed and the due date on the surveillance schedule was inadvertently changed during the transcription process and verification by an independent reviewer was not performed. Contributing to this was a misinterpretation of requirements by responsible personnel, in that they did not understand that all changes to the surveillance schedule, including transcriptions, required independent verification.<br /><br /> All surveillance schedules were reviewed to ensure correct schedules were in place. Although, additional transcription errors were noted, none of those errors resulted in a missed surveillance. This event has been discussed with personnel responsible for updating surveillance schedules. The requirement of independent verification for all changes, including transcriptions, has been communicated to the responsible personnel.
3641994003 | Farley 2 | 12/18/1994 | 01/17/1995 | 9501250057 | <strong>Reactor Trip Due To Turbine Control System Intermittent Failure</strong><br /><i>Abstract:&nbsp;</i>At 03:52 on December 18, 1994, with Unit 2 in Mode 1 operating at 100 percent reactor power, the reactor tripped due to low-low level in the 2C steam generator (SG). The low-low SG level occurred as a result of a load transient initiated by the digital electro-hydraulic control (DEHC) system closing all four governor valves. The rapid load reduction resulted in SG level shrink sufficient enough to generate a reactor trip signal. <br /><br /> A root cause investigation which included a review of the DEHC system and plant computer data attributed the event to an intermittent failure in the 63AST-2 auto stop oil pressure switch circuit that provides an electrical input to the DEHC governor control auto stop latch circuitry. <br /><br /> The suspect pressure switch was replaced. Additionally, a temporary recorder was installed to monitor auto stop oil pressure. The unit was returned to power operation on 12/19/94 at 1806. <br /><br /> Subsequently, on December 25, 1994, with Unit 2 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip caused by an intermittent failure of the DEHC overspeed protection circuitry. A root cause investigation of this subsequent event indicated that although the sequence of events of the referenced reactor trips were different, both reactor trips were most likely caused by an intermittent DEHC system processor failure. Subsequently, six cards associated with the DEHC system have been replaced and forwarded to the vendor for evaluation.
3641994004 | Farley 2, Farley 1 | 12/25/1994 | 01/24/1995 | 9501310225 | <strong>Reactor Trip Due To A Loss of Turbine DEHC Overspeed Protection</strong><br /><i>Abstract:&nbsp;</i>At 1534, on December 25, 1994, with Unit 2 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a loss of digital electro-hydraulic control (DEHC) overspeed protection. Investigations indicated the primary overspeed protection (OPC) controller (DROP 2) failed in a manner which prevented the redundant OPC controller (DROP 52) from assuming control of the turbine DEHC overspeed protection function within the required time frame. This resulted in a turbine trip due to a loss of both OPC controllers. Six cards associated with the DEHC system (three associated with the DROP 2 processor) have been replaced and forwarded to the vendor for evaluation. <br /><br /> The unit was returned to power operation at 2123 on December 26, 1994. Subsequently, on January 13, 1995, with Unit 1 in mode 1 operating at 100 percent power, the reactor tripped due to a turbine trip in response to a loss of DEHC overspeed protection. An evaluation of this Unit 1 event indicated that both reactor trips could have been caused by the vulnerability of the DEHC OPC processors and their associated power supplies to minor voltage transients. Modifications have been performed to the Unit 1 DEHC in order to reduce the vulnerability to minor voltage transients. Preparations to perform DEHC modifications on Unit 2 are currently in progress.
3661994001 | Hatch 2 | 02/01/1994 | 02/22/1994 | 9403040262 | <strong>Failed Relay Coil Results in Unplanned Actuations of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 2/1/94 at 2025 EST, Unit 2 was in the Run mode at a power level of 1705 CMWT (70 percent of rated thermal power). At that time, the coil of relay 2A71-K57 failed, causing the relay to move to its deenergized state. In addition, when the coil failed, the fuse which supplies its power, 2A71B-F22, also blew. These events initiated several actuations of Engineered Safety Features, including closure of the outboard small-bore Group 1 Primary Containment Isolation System (PCIS) valves and closure of various outboard Group 2 PCIS valves. Licensed plant operations personnel inspected panels in the Main Control Room and discovered the failed relay coil. failed relay, and the blown fuse had been replaced. Subsequently, affected valves were reopened and their associated systems were placed back in service with the exception of the small-bore Group 1 PCIS valves mentioned above. By 2/3/94, the relay coil was replaced and the Group 1 PCIS valves were placed back in their normal system lineups. <br /><br /> The cause of this event was a failed coil in relay 2A71-K57. <br /><br /> Corrective actions for this event include replacing the blown fuse and failed relay coil and returning affected systems and valves to their normal lineups. These actions are complete.
3661994002 | Hatch 2 | 03/01/1994 | 03/29/1994 | 9404070158 | <strong>Manufacturing Error, Normal Wear, and Personnel Error Result in Inoperable HPCI System</strong><br /><i>Abstract:&nbsp;</i>On 3/1/94 at 0918 EST, Unit 2 was in the Run mode at a power level of 1705 CMWT (70 percent of rated thermal power). At that time, plant personnel began the monthly operability test of the High Pressure Coolant Injection (HPCI) system. During this test the turbine thrust bearing temperature increased to approximately 437 degrees F before rapidly decreasing below 200 degrees F. Licensed personnel did not shut down the turbine when the bearing temperature exceeded the procedural limit of 160 degrees F. On 3/2/94, the HPCI system was declared inoperable, the turbine bearing was disassembled, and found damaged. HPCI was returned to service by 0246 EST on 3/11/94. <br /><br /> The causes of this event were a manufacturing error in the thrust bearing housing, normal wear in the turbine to pump coupling, and personnel error. <br /><br /> Corrective actions for this event included replacing the failed bearing and worn coupling, modifying the oil hole, temporarily removing the involved individuals from licensed duties, and holding discussions with operations shift personnel. This event will be covered in licensed training to alert licensed personnel to the lessons teamed. This action will be completed by 6/1/94. Other spline gear type shaft couplings on both units'HPCI systems will be inspected during upcoming refueling outages.
3661994003 | Hatch 2 | 03/17/1994 | 04/15/1994 | 9404190269 | <strong>Fuse Actuation Results in ESF Actuation and Interruption in Shutdown Cooling Flow</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 3/17/94, at 1131 EST, Unit 2 was in the Cold Shutdown mode, one day into a scheduled refueling outage. Reactor coolant temperature was 168 degrees Fahrenheit. The 'B' loop of the Residual Heat Removal (RHR) System was in operation in the Shutdown Cooling (SDC) mode. At that time, a non-licensed engineer was tracing the routing of a control wire in a Control Room panel when he observed an arc in the panel and heard several relays actuate. He notified the licensed Shift Supervisor. Subsequent walkdown of the control room panels revealed that the loop 'B' SDC discharge valve, 2E11-F015B, was closed and SDC flow was zero. An operator attempted to open the valve with the control switch but was unsuccessful. Shift personnel then entered procedure 34AB-E11-001-2S, 'Loss of Shutdown Cooling,' and began, with engineers' assistance, to investigate the cause of the valve isolation. At 1202 EST, the cause of the event had not been determined, and it was decided to place the 'A' loop of RHR in the SDC mode. By 1250 EST, SDC flow had been restored via the 'A' loop of the RHR system. Bulk average reactor coolant temperature did not exceed 212 degrees Fahrenheit throughout the event. However, investigation showed that the reactor vessel pressurized to approximately 9 psig during the event. The cause of the event was inadvertent grounding of a Primary Containment Isolation System logic circuit resulting in a fuse actuation and isolation of the SDC discharge valve. Corrective actions include replacing the fuse, repairing a wire termination, revising procedures, changing an alarm setpoint and training personnel.
3661994004 | Hatch 2 | 04/18/1994 | 05/17/1994 | 9405240128 | <strong>Improperly Seated Fuse Results in Unplanned Engineered Safety Features Actuations</strong><br /><i>Abstract:&nbsp;</i>On 04/18/94 at 0445 EDT, Unit 2 was in the Refueling mode with core loading in progress. At that time, a non licensed electrician was removing a fuse in Main Control Room Panel 2H11-P623 per an equipment clearance when several valves in the Group 2 Primary Containment Isolation System (PCIS, EIIS Code JM) automatically closed. The licensed Shift Supervisor went to the panel to ask if any indications that a circuit had been grounded were observed. As the Shift Supervisor came to the panel, the electrician was replacing the cover on an enclosure within the panel. The Shift Supervisor asked that the cover be removed and upon inspection, fuse 2A71B-F22 was found not fully seated. The electrician repositioned the fuse and pushed it into place. Once secured, licensed shift personnel reset the Group 2 PCIS trip signal and returned affected valves and systems to the appropriate lineups.<br /><br /> The cause of this event was personnel error. However, it has not been determined who was responsible for the personnel error. <br /><br /> Corrective actions for this event included reseating fuse 2A71B-F22, resetting affected logic, and returning affected systems to the appropriate lineups. In addition, this event will be covered with Maintenance Department personnel in Tool Box meetings and with Operations Department personnel in Beginning of Shift Training. This action will be completed by 5/27/94.
3661994005 | Hatch 2 | 04/23/1994 | 05/23/1994 | 9405270219 | <strong>False Low Reactor Water Level Signal Results in Automatic Actuation of Engineered Safety Features</strong><br /><i>Abstract:&nbsp;</i>On 04/23/94 at 1550 EDT, Unit 2 was in the Cold Shutdown mode near the end of a refueling outage. At that time, licensed Control Room operators observed that a full Reactor Protection System (RPS) actuation and a partial Group 2 Primary Containment Isolation System (PCIS) actuation had occurred. All control rods were already fully inserted; therefore, no control rod movement occurred. Licensed personnel reset the RPS signal within approximately three minutes and subsequently returned valves affected by the Group 2 PCIS actuation to their required lineups. <br /><br /> The cause of this event was an inadvertent action on the part of an Instrument and Control technician. The technician was performing a procedure to recalibrate a reactor water level instrument for cold shutdown conditions. During the calibration, he inadvertently bumped the valve handle on an instrument isolation valve which partially opened the valve and depressurized the associated instrument variable leg. This caused a false low reactor water level signal affecting both channels of RPS logic and one channel of PCIS logic. <br /><br /> Corrective actions for this event included resetting the RPS signal and returning affected systems to the lineups required for the plant condition. In addition, the responsible technician has been made aware of the consequences of his inappropriate action.
3661994006 | Hatch 2 | 04/30/1994 | 05/24/1994 | 9406010015 | <strong>Missed Technical Specifications Surveillance Caused By Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 4/30/94 at 0400 EDT, Unit 2 was in the Run mode at 15% rated thermal power when shift operations personnel determined the jet pump operability surveillance required by Unit 2 Technical specifications Section 4.4.1.2 had not been performed within the requisite frequency. The surveillance, last completed at 2016 edt on 4/28/94, is required by tech specs to be performed at least once every 24 hours while the unit is in the startup and run modes. Technical specifications allow an extension of not greater than 25% of the surveillance interval. Therefore, the surveillance was required to be completed by 0216 EDT on 4/30/94. When personnel realized at 0400 EDT that the surveillance had not been performed, the required frequency plus 25% grace period had been exceeded. Personnel completed the surveillance at 0435 EDT on 4/30/94. <br /><br /> The cause of this event was personnel error. Opera tions personnel responsible for performing the jet pump operability surveillance failed to review, in a timely manner, surveillance information from the previous shifts. As a result personnel did not realize the surveillance was to be completed by 0216 EDT on 4/30.94. At 0400 EDT, when reviewing previous shift's information, personnel relized the surveillance was past due. The surveillance was satisfactorily completed at 0435 EDT. <br /><br /> Corrective actions for this event inclu ded performing the required surveillance and counseling and retraining involved personnel.
3661994007 | Hatch 2 | 08/30/1994 | 09/23/1994 | 9410040141 | <strong>RPS Control Switch Overtravel Results in an Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 8/30/94, at 1007 EDT, Unit 2 was in the Run mode at 2436 CMWT (100 percent rated thermal power). At that time, the power supply for Reactor Protection System (RPS) bus 'A' was being transferred from the alternate to the normal power supply when a full RPS actuation occurred along with a Group 1, 2, and 5 Primary Containment Isolation System (PCIS) actuation. As a result, all control rods fully inserted and various PCIS valves automatically closed. Immediately following the RPS actuation, the reactor water level began decreasing as expected. The lowest level reached during the level transient was approximately 43 inches below instrument zero (approximately 115 inches above the top of the active fuel). As the reactor water level decreased to the appropriate setpoints, the following engineered safety features initiated: High Pressure Coolant Injection System (HPCI), Reactor Core Isolation Cooling System (RCIC), Standby Gas Treatment System (SGT), and the Recirculation Pump Trip System (RPT). All systems functioned as designed. Reactor water level was restored by the Reactor Feedwater Pumps (RFP) and RCIC. The highest reactor pressure reached during the event was 1092 psig. Eight Safety Relief Valves opened to reduce pressure. The SRVs subsequently closed at the appropriate pressures as the pressure decreased. The cause of the event was a slight overtravel of the RPS power select switch. An intolerance for overtravel of the switch positions resulted in a momentary loss of power to both RPS busses and the consequent actuations. Corrective actions include replacing the switch, installing a warning placard, and considering a design change.
3661994008 | Hatch 2, Hatch 1 | 09/28/1994 | 10/25/1994 | 9411030227 | <strong>Less Than Adequate Procedure and Personnel Error Result in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 9/28/94, at 1445 EDT, Unit 2 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time during performance of a technical specification surveillance, it was determined that the oxygen concentration in the Suppression Chamber, a portion of the Primary Containment, was 5.5% by volume. The Technical Specifications require that the Primary Containment oxygen concentration be less than 4% by volume. If this limit is exceeded, the Technical Specifications require the unit to be in the Startup mode within eight hours. Consequently, at 1445 EDT, a shutdown action statement was entered. Licensed personnel initiated nitrogen makeup to the Suppression Chamber using the Containment Atmospheric Dilution System to reduce the oxygen concentration. By 2115 EDT, the oxygen concentration in the Suppression Chamber was less than 4% and the shutdown action statement was terminated. An event review team was formed to investigate the event and its causes. <br /><br /> Causes of the event include a less than adequate procedure and personnel error on the part of vendor personnel and on the part of plant personnel. Corrective actions include revising procedures and training personnel.
3661994009 | Hatch 2 | 12/20/1994 | 01/13/1995 | 9501190073 | <strong>Component Failure Results in Unplanned Engineered Safety Feature System Actuation</strong><br /><i>Abstract:&nbsp;</i>On 12/20/94 at 1415 EST, Unit 2 was in the Run mode at a power level of 2436 CMWT (100 percent rated thermal power). At that time, several Group 2 Primary Containment Isolation System valves unexpectedly closed. This resulted in isolation of the Fission Product Monitoring and H sub 2 O sub 2 Analyzer systems. Operations personnel entered Limiting Conditions for Operation (LCOs) 2-94-505 and 2-94-506 for the inoperable systems as required by the Unit 2 Technical Specifications and plant procedures. Instrument and Controls personnel investigating the unexpected isolation discovered the coil for relay 2C61-K23 had failed, resulting in the relay going to the de-energized state and several Group 2 valves closing per design. Maintenance personnel replaced the failed coil and, at 1755 EST, Operations personnel reset the Group 2 isolation signal. The Fission Product Monitoring and H sub 2 O sub 2 Analyzer systems were returned to service, and LCOs 2-94-505 and 2-94-506 were terminated at 1820 EST. <br /><br /> This event was caused by component failure. Specifically, the coil for Primary Containment Isolation System relay 2C61-K23 failed. This resulted in the relay going to the de-energized state and several Group 2 valves closing per design. <br /><br /> The relay coil was replaced, the Group 2 isolation signal was reset, and the affected systems were returned to service.
3681994001 | Arkansas 2 | 03/12/1994 | 11/21/1994 | 9411300293 | <strong>Technical Specifications Requirements For Logarithmic Power Level Instrumentation Operability Not Met Due to Inadequate Post-Maintenance Test</strong><br /><i>Abstract:&nbsp;</i>With the plant in Hot Standby conditions at the start of a refueling outage, excore nuclear instrumentation channels were being tested for electronic noise. When a jumper bypassing a filter was removed from the cable of one channel, the high voltage pin came loose and remained with the jumper. Without high voltage to the detector, the logarithmic power high trip function from that channel was inoperable. Performance of the functional test and comparison with other channel outputs failed to reveal the condition since all indications were near the lower end of the scale. Another channel was placed in bypass for testing. The broken pin was found in the jumper connector while establishing test conditions of the subsequent channel. The configuration of one channel in bypass and another inoperable but not tripped along with having an inoperable channel neither bypassed nor tripped for greater than one hour are conditions prohibited by Technical Specifications. The noncompliance with Technical Specifications existed for one hour and thirty-two minutes and was corrected immediately upon discovery. The root cause was determined to be an inadequate post-maintenance test because connector failure was not considered. Corrective actions included enhancement of the post-maintenance test method and discussion with appropriate maintenance personnel.
3681994002 | Arkansas 2 | 04/22/1994 | 05/20/1994 | 9405250043 | <strong>Steam-Driven Emergency Feedwater Pump Inoperable Longer Than Allowed By Technical Specifications Due To Inadequate Specification Of Replacement Valve Characteristics</strong><br /><i>Abstract:&nbsp;</i>During a refueling outage at Arkansas Nuclear One Unit 2, a solenoid valve in the steam supply line to the steam turbine-driven emergency feedwater pump was replaced with a different model in an attempt to improve reliability. Surveillance testing to verify operability cannot be performed until the plant is in Mode 3 with steam pressure greater than 800 psia. This testing revealed that the pump was inoperable due to the new solenoid valve failing to allow sufficient steam flow to the turbine. Enforcement discretion was obtained from the NRC to allow completion of repair and testing while remaining in Mode 3. The valve was replaced with the pre-modification model. The pump was restored to an operable status after the plant had exceeded the Technical Specifications allowable outage time by 8 hours and 35 minutes. A significant contribution to exceeding the allowable outage time was problems with replacement valves. The root cause of the condition has been determined to be failure to apply self-checking during specification of valve characteristics in the design of the modification. Personnel directly involved with the modification have been counseled. Appropriate engineering personnel will be informed of this condition and management expectations regarding design review activities.
3681994003 | Arkansas 2 | 08/24/1994 | 09/23/1994 | 9409290164 | <strong>Control Element Assembly Position Indication Surveillance Testing Not Performed as Required By Technical Specification Due To Personnel Error Associated With Computer Software Change</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1994, with the unit operating at full power steady-state conditions, ANO-2 Operations personnel discovered that surveillance testing of Control Element Assembly (CEA) position indication had not been completed as required by Technical Specifications (TS). The surveillance is required at least once per 12 hours and is normally completed each 8 hours by reviewing a report generated by the Plant Monitoring System (PMS) computer. The communication data link between the CEA Calculators and PMS had failed. No failure alarm was generated and the report did not clearly indicate invalid data as expected. When the problem was discovered, the data link was restored and the surveillance was completed to verify that no CEA position deviation existed. The total time of non-compliance with TS requirements was approximately 29 hours and 28 minutes. The root cause of the condition was determined to have been a personnel error in failing to fully specify requirements for a computer software change that inadvertently omitted indication of data quality attributes that had previously existed to identify a data link failure. Corrective actions include software corrections and a review of the condition with the responsible project manager. There have been no previous similar events reported by ANO as LERs.
3681994004 | Arkansas 2 | 10/07/1994 | 11/04/1994 | 9411090349 | <strong>Surveillance Testing Of One High Pressure Safety Injection Pump Did Not Verify Operability As Required By Technical Specifications Due To Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1994, Arkansas Nuclear One, Unit 2 identified that surveillance testing of an Engineered Safety Features (ESF) component had not been performed in a manner that adequately verified operability as required by Technical Specifications (TS). The condition involved testing the 'swing' High Pressure Safety Injection (HPSI) pump start feature when powered from either Emergency Diesel Generator (EDG). Further review revealed that testing had not been performed to verify that two Service Water (SW) pumps would not start on a bus being powered from one EDG. Upon discovery, actions were taken to ensure compliance with TS requirements. Interim administrative controls were established. Testing verified operability of components of potential concern. The cause of the condition was inadequate surveillance procedures. Appropriate procedures will be revised prior to their next use. A task force has been established to develop rules and guidelines for determining ESF testing requirements.
3681994005 | Arkansas 2 | 11/21/1994 | 12/16/1994 | 9412290175 | <strong>Entry into Technical Specification 3.0.3 Due to Two Channels of the Plant Protective System Being Simultaneously Inoperable as a Result of a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1994, at approximately 1407 hours, an ANO Instrumentation and Control (I&C) technician performing the 'B' channel Plant Protective System (PPS) monthly surveillance procedure inadvertently reset the variable setpoint (VSP) for the 'A' channel of the low steam generator (S/G) pressure trip causing Channel 'A' trip setpoints to be below the minimum allowable Technical Specification (T.S.) value. Since channel 'B' was in bypass for testing, ANO-2 entered T.S. 3.0.3 based on two channels of PPS being inoperable simultaneously. The technician and the Control Board Operator (CBO) both recognized the error and immediately suspended PPS testing. Channel 'B' PPS was returned to operable status by removing it from bypass. Channel 'A' of PPS was placed in bypass and T.S. 3.0.3 was exited at 1412. The S/G low pressure trips on channel A' were reset to the required value of 751 psia and channel 'A' was declared operable at 1414. The root cause of this event was a personnel error on the part of the I&C technician involving inattention to detail and lack of adequate self-checking during performance of the' B' PPS surveillance procedure. The technician involved was individually counseled by his first line supervisor. In addition, the other I&C crews were briefed on the event and on the practice of self-checking.
3691994001 | McGuire 1, McGuire 2 | 12/07/1993 | 02/05/1994 | 9406090154 | <strong>Technical Specification Violations Due To A Non- conservative Calculation Caused By Failure To Consider System/Component Interaction.</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1993, Systems Engineering (SES) personnel were investigating a problem involving valve 2NI-54A, Cold Leg Accumulator 2A Discharge Check Valve. The investigation revealed the potential stem leakoff from the valve was flowing in a direct path to the Reactor Coolant (NC) system Drain Tank (NCDT). This potential leakage path was included as input to the NCDT and; therefore, considered as identified NC system leakage. The addition of any leakage from this path would result in the figures for the unidentified NC system leakage calculation being non-conservative. Further analyses revealed that both Units probably have exceeded the 1 gpm limit for unidentified NC system leakage as specified by Technical Specification (TS) 3.4.6.2, when considering the effect of this leakage path. Because plant personnel were not aware the TS limits had been exceeded at those times, no actions had been taken to reduce the leakage rate to within limits or shutdown as required by the TS. This event is assigned a cause of Failure To Consider System/Component Interaction. Both units were in Mode 1 (Power Operation) at 100 percent power at the time of the event discovery. Corrective actions include determining the best way to permanently remove non-NC system related inputs from the NC system Leakage Calculation, and including appropriate information in the Design Basis Document for the NC system Leakage Calculation.
3691994002 | McGuire 1, McGuire 2 | 04/06/1994 | 05/06/1994 | 9405120089 | <strong>Failure To Comply With Technical Specifications Action Statement For Reactor Coolant Leakage Detection Systems Due To The Omission Of Relevant Information.</strong><br /><i>Abstract:&nbsp;</i>Engineering and Regulatory Compliance personnel initiated an investigation into the stations ability to meet the requirements of Technical Specification (TS) 3.4.6.1, Reactor Coolant System Leakage Detection Systems. On April 8, 1994, Engineering personnel determined that the systems which are specified in TS 3.4.6.1, were past inoperable on both units. This inoperability was due to their inability to provide an alarm in the Control Room of an increase in Reactor coolant system leakage, of >/= 1 gallon per minute, within 1 hour. Technical Specification 3.4.6.1 is applicable in modes 1 (Power Operation), 2 (Startup), 3 (Hot Standby), and 4 (Hot Shutdown). The alarm requirements are specified in Regulatory Guide 1.45, dated May, 1973. The cause of the event is the omission of relevant information in the original design requirements. Both units were in mode 1 at 100 percent power at the time of the event discovery. Corrective actions include modifications to the Operator Aid Computer to allow monitoring of portions of the Liquid Waste systems to detect Reactor Coolant system leaks. Additional corrective actions changed the allowable alarm setpoint of the containment atmosphere radiation monitors and will include changes to the design basis documents for the Liquid Waste and Radiation Monitoring systems.
3691994003 | McGuire 1, McGuire 2 | 02/08/1994 | 03/10/1994 | 9403160209 | <strong>Failure to Perform A Technical Specifications Required Surveillance Due To An Inappropriate Action.</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1994, a question was raised concerning the required testing of the power range Nuclear Instruments (NI). Specifically, the testing in question was the monthly Analog Channel Operational Test (ACOT) associated with the high flux trip (low setpoint) signal. The monthly ACOT is performed in accordance with procedure, PT/0/A/4600/14D (E,F,G), NIS Power Range Analog Channel N-41 (N-42,N-43,N-44) Operational Test. McGuire Engineering personnel determined that the low setpoint bistable was not being tested using the test procedure as it was written. The procedure superimposes a test signal over and above the signal which exists on the circuitry. Therefore, when the output of the NI detector was greater than the actuation point of the bistable, the bistable was not being appropriately tested. Further investigation revealed that at various times in the past, both units at McGuire were operated when this bistable was required and had not been adequately tested within the required surveillance frequency. Unit 1 was in Mode 5 (cold shutdown) and Unit 2 was in Mode 1 (power operation) at the time of the discovery. Corrective actions include changing the test procedure to require disconnecting the detector from the circuitry, during the ACOT, to allow testing of all of the channel bistables.
3691994004 | McGuire 1 | 05/12/1994 | 06/10/1994 | 9406160123 | <strong>A Unit 1 Reactor Trip Occurred Due To The Improper Use Of Equipment</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1994, at 1353, Unit 1 experienced a Reactor trip. Prior to the event Unit 1 was in Mode 1 (Power Operation) at 100 percent power. The event occurred when a screwdriver rolled off a divider barrier in electrical board 1EB5, striking one or more relays in the reverse power circuitry for the Unit 1 Generator. This resulted in the opening of both Unit 1 Generator Power Circuit Breakers. A full load rejection was initiated, followed by a Reactor trip due to a Nuclear Instrumentation System Power Range High Negative Flux Rate Reactor Trip signal. This event is assigned a cause of Improper Use of Equipment because the divider barrier in an electrical panel was used as a tool rest. Corrective actions to be taken to prevent recurrence include communicating to Instrument and Electrical (IAE) personnel that divider barriers in electrical equipment are not to be used as tool rests and procedure changes to caution IAE personnel not to use divider barriers as tool rests. Unit 1 was returned to service on May 13, 1994, at 0643.
3691994005 | McGuire 1 | 07/11/1994 | 08/10/1994 | 9408180023 | <strong>Boron Dilution of the Unit 1 Spent Fuel Pool During Drain Down and Decontamination of the Transfer Canal.</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted voluntarily to provide information and lessons learned regarding a Reactivity Management Event. On July 10, 1994, with Unit 1 operating in Mode 1 (Power Operation) at 100 percent power, Mechanical Maintenance personnel began the drain down of the Unit 1 Spent Fuel Pool Transfer Canal. During the drain down, a demineralized water misting system was used to keep the pool walls wet to minimize potential airborne contamination. Approximately 28,000 gallons of demineralized water wall added to the pool during the decontamination process. The addition of the demineralized water lowered the Boron concentration from 2105 parts per million (ppm) to 1957ppm. The Technical Specification requires a Boron concentration >/= 2000ppm. The Action Statement to suspend fuel movement while the Boron concentration is less than 2000ppm was not violated. Boric Acid was added to the pool to bring the Boron concentration above 2000ppm. This event has been assigned a cause of improper Managerial Methods. Corrective actions include heightening the awareness Of site personnel to Reactivity Management concerns, evaluation of work processes/controls, rewrite of the procedure used, incorporation of work involving complex evolutions and multiple interfaces into the Risk Assessment Process.
3691994006 | McGuire 1 | 09/09/1994 | 10/09/1994 | 9410130272 | <strong>Failure To Perform A Slave Relay Test Associated With One Containment Isolation Valve Due To Improper Work Practices.</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1994, at 0845, a staff member in the Operations Procedure group was preparing a procedure change for both Unit 1 and Unit 2 Slave Relay Test Procedures. While comparing the procedures, a discrepancy was noted. Generator 1B, Blowdown Line Sample Inside Containment Isolation Valve, 1NM200B, was not included in the Unit 1 procedure. The staff member revised the procedure and had the slave relay test performed. The test verified that the valve would have operated as designed. The valve is normally Closed. The slave relay associated with this valve was periodically tested as required; however, the contacts associated with valve 1NM200B were not verified operable. The cause of this event is attributed to improper Work Practices due to the failure to identify an error made during a procedure revision. The valve was inadvertently omitted from the procedure during a revision in August, 1991. Corrective actions include a review of all Slave Relay Test procedures to assure all equipment is tested and continuing training for all Qualified Reviewers. Unit 1 was in Mode 1, Power Operation, at 100% power, at the time of discovery.
3691994007 | McGuire 1, McGuire 2 | 10/24/1994 | 03/17/1995 | 9503220379 | <strong>Unit 1 Diesel Generator 1B And Unit 2 Diesel Generator 2A Experienced Inadvertent Starts Due To Unanticipated Interaction Of Components.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: October 24, 1994, Unit 1 - Mode 3 (Hot Standby) at full temperature and pressure. December 12 and 13, 1994, Unit 2 - No Mode, Reactor Coolant System drained. <br /><br /> Event Description: On October 24, 1994, during performance of procedure PT/1/A/4350/026, Diesel Generator (DG) 1B Operability Test, control power had been removed from the DG Control Panel. When control power was restored, the DG started. The initial investigation revealed no valid reason for the start. After verification that no Engineered Safety Features Actuation system signal had been received, the DG was shut down. Subsequently, the DG was tested and declared operable. A cause of Unknown, Possible Equipment Malfunction was assigned at that time.<br /><br /> Corrective actions included further investigation of DG circuitry to validate that no problems existed. On December 12 and again on December 13, 1994, during DG testing runs, DG 2A experienced the same type of inadvertent start when the control power was restored. Further investigation and extensive troubleshooting was performed and it has been determined that the inadvertent starts were caused by a combination of factors related to interaction of several components associated with the DG control circuitry. <br /><br /> Event Cause: It has been determined that the inadvertent starts were caused by Unanticipated Interaction Of Components in the control circuitry of the DGs, when restoring Control Power during testing. <br /><br /> Corrective Action: Actions taken to correct this problem were to modify the DG control circuitry, eliminating the potential for this type interaction.
3691994008 | McGuire 1 | 11/01/1994 | 12/02/1994 | 9412050243 | <strong>Three Auxiliary Feedwater To Steam Generator Isolation Valves Were Determined To Be Past Inoperable Due To A Fabrication Deficiency in Vendor Supplied Testing Software.</strong><br /><i>Abstract:&nbsp;</i>Valves 1CA-0042, 1CA-0046, and 1CA-0058 (Auxiliary Feedwater Pumps to Steam Generator Isolations) were determined to be past inoperable on November 1, 1994. Differential pressure testing conducted during the Unit 1 End Of Cycle (EOC) 9 outage revealed the valves would not sufficiently close against design basis system conditions to isolate flow. These valves were differential pressure tested during the 1EOC7 outage using the VOTES diagnostic testing system. Liberty Technologies subsequently issued a 10CFR50 Part 21 notification regarding problems with the test software used during the 1EOC7 outage. The testing conducted during the 1EOC9 outage was being performed to validate differential pressure test data taken during the 1EOC7 outage and to determine the operability status of the valves. This event is assigned a cause of Fabrication Deficiency because the data taken for these valves during the 1EOC7 testing was determined to be nonconservative due to a problem in vendor supplied software. Unit 1 was in Mode 1 (Power Operation) at 100 percent power at the time valves 1CA-0042, 1CA-0046, and 1CA-0058 were determined to be past inoperable. Corrective actions taken as a result of this event include the implementation of a minor modification to install a 95% close torque switch bypass on valves 1CA-0042, 1CA-0046, 1CA-0058 and 1CA0062 and the re-evaluation of all differential pressure tests using the VOTES 2.31 software.
3691994009 | McGuire 1 | 11/25/1994 | 01/20/1995 | 9501240381 | <strong>Boron Dilution Of The Unit 1 Volume Control Tank Due To Procedural Deficiencies Caused By Inadequate Self Checking.</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted voluntarily to provide information and lessons learned regarding Reactivity Management. On November 25, 1994, with Unit 1 operating in Mode 1 (Power Operation) at 100 percent power the Unit 1 Chemical And Volume Control (NV) Auto Control system made-up level in the Unit 1 Volume Control Tank (VCT). After the make-up was completed, the Unit 1 Operations (OPS) Reactor Operator (RO) noted an increase in the Unit 1 Reactor Coolant (NC) system temperature. He checked appropriate parameters and found no reason for the increase. He then attempted addition of Boron to control the increase via both normal and emergency flow paths from the Boric Acid tanks. He was unable to establish flow. At that time, the OPS RO inserted Control Rods to achieve the appropriate NC system temperature. OPS personnel determined that valve 1NV-381, Suction to Unit 1 Boric Acid Tank Pumps, had been closed by Chemistry personnel in accordance with a procedure for realignment of the Boric Acid tanks. The closed valve had prevented addition of Boron from the Boric Acid tanks during the auto make-up to the VCT and later when the OPS RO attempted to add Boron. The valve was reopened and flow was restored from the Boric Acid tanks. Additionally, the Boric Acid Flow deviation instrumentation had malfunctioned at some time prior to the auto make-up to the VCT. This malfunction had prevented actuation of both the annunciator alarm and the automatic termination of make-up to the VCT when Boric Acid flow was not established during the make-up. This incident has been assigned a cause of Procedural Deficiency due to technical inaccuracies created by inadequate self checking by personnel when implementing a procedure change. Appropriate changes have been made to correct the procedural deficiencies. Subsequent testing proved that the alarm circuitry did not function correctly due to failure of a time delay relay associated with the circuit. The circuitry was repaired and functionally tested satisfactorily.
3691994010 | McGuire 1, McGuire 2 | 11/30/1994 | 05/11/1995 | 9505230103 | <strong>Failure To Perform Technical Specifications Required Surveillances Because Testing Was Not Specified Due To The Need Not Being Recognized.</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1994, Operations (OPS) personnel discovered that an abandoned/spare Unit 2 Containment penetration, 2-M313A, was not included in procedure PT/2/A/4200/02C, Containment Integrity Verification During Core Alterations. Investigation into the problem identified other similar abandoned/spare instrument penetrations on Units 1 and 2 which had not been included in the respective units procedure. The investigation also revealed these penetrations had not been included in procedures PT/1 and 2/A/4200/02B, Cold Shutdown Containment Integrity Verification. As a result, these abandoned/spare instrument penetrations had not been verified to be closed in accordance with Technical Specification surveillances 4.9.4.1 and 4.6.1.1a. Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 6 (Refueling) at 0 percent power at the time this problem was initially discovered. On February 27, 1995, it was determined that additional abandoned/spare instrument penetrations existed which had not been included in procedures PT/1 and 2/4200/02B and 02C. Both units were in Mode 1 at 100 percent power at the time. This event is assigned a cause of Required Testing Not Specified Because The Need Was Not Recognized. Inspections of the original group of abandoned/spare instrument penetrations in the Unit 1 and Unit 2 annulus on December 21 and 29, 1994, and the additional Unit 1 and 2 abandoned/spare penetrations on April 13 and April 3, 1995, respectively, identified no missing caps. These penetrations are accounted for during Integrated Leak Rate Testing and are concluded to have been closed when required. Planned corrective actions include the tack welding of the caps on abandoned/spare penetrations and surveillance of the abandoned/spare instrument penetrations until they are tack welded.
3701994001 | McGuire 2 | 01/24/1994 | 02/23/1994 | 9403070393 | <strong>A Technical Specification Surveillance Was Missed Due To An Inappropriate Action.</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1994, at 0520 with Unit 2 in Mode 1 (Power operation) at 100%, Operations personnel removed the control power from the Unit 2 Train A (2A) Nuclear Service Water (RN) Pump for preplanned maintenance. This rendered the 2A Diesel Generator (DG) inoperable. With only one DG operable, Technical Specifications require that an off-site power source verification be completed within one hour and every eight hours thereafter until the DG is returned to operable status. The Control Room Senior Reactor Operator (CRSRO) did not initiate the required surveillance. At 1630 the problem was discovered and the surveillance was successfully performed. The off-site power sources were available during the time the DG was inoperable; however, the availability was not documented as required by procedures. This event is assigned a cause of Inappropriate Action due to the CRSRO not ensuring that the surveillance was performed. Corrective Actions include revising the Operations Management Procedures controlling tagouts and Technical Specification Action Item Log entries to emphasize responsibilities. Also, this event will be communicated to appropriate personnel to re-emphasize the importance of proper communications.
3701994002 | McGuire 2 | 05/19/1994 | 06/19/1994 | 9406210233 | <strong>Failure To Comply With A Technical Specification Required Surveillance Because Of Improper Work Practices.</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1994, Chemistry Scientist A reviewed the Chemistry data trend graphs for the previous week and discovered that the result of the Unit 2 Reactor Coolant (NC) system Fluoride and Chloride analysis performed on May 13, 1994 was nonrepresentative of the typical water sample. The review of the chromatogram generated by the Dionex 4500i (analyzer) on May 13, 1994, indicated that some instrument malfunction had occurred for that particular analysis; therefore, an inadequate surveillance was performed. Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time the event occurred. This event is assigned a cause of Improper Work Practices because, due to an oversight, the Chemistry specialist performing the analysis did not adequately check the chromatogram to determine if the sample results were representative of a typical water sample. Corrective actions to prevent recurrence include procedure changes and controls to check the validity of all data generated by the analyzer.
3701994003 | McGuire 2 | 08/15/1994 | 09/15/1994 | 9409210101 | <strong>Failure To Perform A Technical Specifications Required Surveillance Due To Improper Work Practices.</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1994, Diesel Generator (D/G) room sump pump 2B2, associated with the 2B D/G was made inoperable for maintenance. After the maintenance activities were complete, the pump was returned to its normal alignment to allow functional testing. The Control Room Senior Reactor Operator (CRSRO) declared the 2B2 D/G room sump pump operable based upon the pump being returned to normal alignment. However, an operability test had not been performed. On August 16, 1994, at 0553, the night shift CRSRO declared 2B3 D/G room sump pump inoperable for maintenance., During the turnover process, the day shift Work Control Center Senior Reactor Operator (WCCSRO) realized that the retest had not been performed on the 2B2 D/G room sump pump, and that the 2B3 D/G room sump pump was inoperable. With both of the safety related D/G room sump pumps inoperable, the D/G is inoperable. the circuits which are supplying the unit with offsite power. This required surveillance had not been performed. The WCCSRO took immediate action to return the 2B3 sump pump to operable status and to perform the required offsite power verification. The required surveillance was performed and the 2B3 sump pump was returned to service by 0735. Corrective actions for this event include counseling of the CRSRO. Unit 2 was in mode 1 (Power Operation), at 100% power at the time of the event.
3731994001 | LaSalle 1, LaSalle 2 | 01/17/1994 | 02/14/1994 | 9402280213 | <strong>1B Reactor Protection System (RPS) Motor Generator (MG) Set Underfrequency Trip</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1994, at 1413 hours, a half scram and several isolations or half isolations occurred. At the time, both Reactor Protection System (RPS) Buses were powered from their respective Motor-Generator (MG) Sets. The half scram was caused by a trip of motor-generator set output breaker on the 1B RPS MG set. The trip was caused by the failure of an underfrequency relay located inside the MG Set Cabinet. After the 1B RPS Bus was placed on its alternate supply, the half scram was successfully reset and all systems which isolated were placed back in service. The cause was the upward drift of the under-frequency relay setpoint. This relay was replaced. A circuit card failure of the EPM breaker was also found during subsequent testing and repaired. An adverse trend evaluation was initiated to review long term testing and preventive maintenance of RPS buses. <br /><br /> This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv) due to an automatic actuation of an engineered safety feature (ESF).
3731994002 | LaSalle 1 | 01/22/1994 | 02/15/1994 | 9402240019 | <strong>Single Control Rod Scram Due To Bad Fuse Clip</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1994 during half scram testing (LOS-RP-M1) on Unit 1 with power at 74%, control rod 54-47 (5A-peripheral rod) scrammed to the full in position. The unit was dropped 75 MWE per LOA-RD-06, 'Control Rod Drift/Individual Rod Scram'. No thermal limits were exceeded with this rod being at the full in position. A Qualified Nuclear Engineer (QNE) was notified that the rod was at the full in position and the QNE stated no further action was required for the scrammed rod. The event was reported to the NRC per 10CFR50.72(b)(2)(ii) within the required four hours.<br /><br /> Investigation revealed the 'B' RPS fuse was loose in its clip. This coupled with the half scram from 'A' Reactor Protection System (RPS) from the performance of LOS-RP-M1 caused the rod to scram in. <br /><br /> A work Request L26894 was written and the control rod was removed from service. The fuse block was found cracked and subsequently satisfactorily replaced. Since this work does not affect the scram time of the control rod, no additional tests were required on the control rod prior to returning the rod to service. <br /><br /> A new parts evaluation (l-94-0014) was performed and concluded that the electrical box assembly supplied by GeneraL Electric (part # 922d234G001) which contains the fuse holder on a terminal board is not safety related. <br /><br /> Any failure of the terminal board would result in a control rod scram. It is the first time that this particular part had to be replaced at the station. This is considered an isolated event and rio further action is required. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature ESF.
3731994003 | LaSalle 1 | 01/20/1994 | 02/15/1994 | 9402250235 | <strong>Limiting Condition For Operation Exceeded Due To Freezing Weather</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1994 Unit 1 was in Operational Condition 1 (Run) at 94% power. At 1800 hours, monthly functional tests for three Reactor Protection System (RPS) Instrumentation 'Functional Units' Listed in Table 4.3.3.1-1, of Technical Specification Surveillance Requirement 4.3.3.1, exceeded the specified monthly surveillance interval and the allowed factor of 1.25 times the surveillance interval. LaSalle received a Notice of Enforcement Discretion (NOED) from the NRC at 1300 hours on January 20, 1994, which allowed for an additional 48 hours in which to complete the surveillance testing on Unit 1. <br /><br /> Reactor Protection System (RPS) Instrumentation Surveillances cause multiple half-scrams (one of the two RPS trip systems tripped at a time). During half-scram testing, a single equipment failure or error may cause a full reactor scram. Therefore, LaSalle pursued requesting an NOED to postpone three half-scram surveillances until an adequate reserve margin based on power availability and system stability was reestablished. The subject RPS instrumentation surveillances were Main Steam Line isolation Valve - Closure, Turbine Stop Valve - Closure, and Turbine Control Valve Fast Closure, Valve Trip System Oil Pressure - Low. <br /><br /> The apparent cause of the event was an unstable grid system combined with an extremely Low reserve on the Commonwealth Edison Company (CECo) distribution system and extremely cold weather. <br /><br /> The Technical Specification Surveillances were completed at 0608 hours on January 22, 1994. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Plants Technical Specifications.
3731994004 | LaSalle 1 | 01/05/1994 | 02/22/1994 | 9403040310 | <strong>Control Rod Position Indication System Failed Due To Card Failure</strong><br /><i>Abstract:&nbsp;</i>The LaSalle County Station Unit One Control Rod Position indication System (RPIS) was determined to be inoperable at 2307 hours on January 4, 1994. Technical specification 3.1.3.7 requires that the RPIS be returned to operable status within one hour or the unit be placed in at least Hot Shutdown within the following 12 hours. <br /><br /> The RPIS failure was caused by one of two components, a failed Probe Multiplexer Card or a diminished output amplitude from a File Control Card. Both are electronic cards within the RPIS. Repair and operability testing time exceeded the time allowed by Technical Specification 3.1.3.7, Control Rod Position Indication. Commonwealth Edison Co. requested and was granted a Notice of Enforcement Discretion at 1200 hours on January 5, 1994 to not enforce compliance with Technical Specification 3.1.3.7 for a period of 6 additional hours.<br /><br /> At 1340 hours on January 5, 1994 the RPIS was declared Operable following repair and testing. The time allowed to reach at Least Hot Shutdown was exceeded by 93 minutes. This violation of Technical Specification 3.1.3.7 is reportable within 30 days per 10CFR50.73(a)(2)(i)(8).
3731994005 | LaSalle 1, LaSalle 2 | 03/09/1994 | 04/08/1994 | 9404130085 | <strong>Control Rod Blade Transfer With A Technically Inoperable Hoist During Refuel Outage Due To Bypassing Up-Limit To Allow Transfer To Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On 3/9/94, licensing personnel from another utility contacted LaSalle Station Personnel for information on the method used for control blade movements during refueling. The question concerned bypassing the upper limit of the auxiliary hoist to provide enough clearance to move control blades from the reactor vessel to the fuel pool. Technical Specification (T.S.) 3.9.6 requires all cranes and hoists used for handling fuel assemblies or control rods within the reactor vessel to be operable. Part of the Technical Specification Surveillance requirement is that the up-travel stops when the grapple is lower than or equal to eight feet below the platform rails. <br /><br /> Following the conversation, LaSalle's Fuel Handling Supervisor was contacted and it was determined that bypassing the up-travel limit was commonly done when moving control blades during refueling outages. By defeating the up-travel interlock, the Technical Specification Surveillance criteria is no longer met, rendering the hoist inoperable. Therefore, Technical Specification 3.9.6 was violated and the action statement was not met. It was determined that the up-travel interlock was set overly conservative, not allowing the control blade to be raised high enough to clear the refueling chute. The up-travel interlock was overridden to provide the clearance needed for transferring the control blade to the fuel pool. The safety significance of this event was minimal. Bypassing the up-travel interlock increases the drop height assumed for the bundle drop accident in the UFSAR. 400 pounds less than the weight of a fuel bundle. Therefore, the impact energy and the damage from dropping a control blade would be much less than that of the bundle drop accident. The up-travel limits have been reset on the Unit 1 (currently in refuel) hoists to meet the Technical Specification requirements and still allow enough clearance for the control blades to pass through the refueling chute. The Unit 2 hoist limit switches have also been reset in the same manner. Procedures have been revised to provide better guidance on setting the up-travel limits and precautions on defeating this refueling interlock.
3731994006 | LaSalle 1 | 03/30/1994 | 04/29/1994 | 9405050045 | <strong>ASME Code Support Found Not Fully Installed During Surveillance Due To Unknown Reasons</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1994 at 1000 hours, piping strut RH50-1016X on line 1RH50A-20' at the flange to Spool Piece 1FC27A-20' for Fuel Pool Cooling Assist mode of the B Residual Heat Removal (RHR)[BI] System was found not fully installed per drawing M09-RH50-1016X, Revision E. This condition was discovered during an ASME VT-3 Inspection in accordance with LaSalle Technical Surveillance, LTS-600-17, 'Mechanical Component Support Inservice Inspection Program'. Unit 1 was shutdown and De-Fueled for the unit's sixth refuel outage (L1R06). Unit 1 Primary Containment and the A, B and C RHR Systems were not required to be operable. <br /><br /> An investigation/review was performed to determine the root cause of the event and to determine the safety significance of the incomplete installation of the pipe strut. Piping Subsystem 1RH-07 was evaluated with pipe support RH50-1016X in its present incomplete configuration. <br /><br /> The result of this evaluation showed that the pipe support is acceptable in its present configuration and Piping Subsystem 1RH-07 is fully Operable. A Drawing Change Request (DCR) will be initiated to update Support Drawing M09-RH50-1016X to reflect the current pipe support configuration and revised support loadings. <br /><br /> This event is being reported voluntarily to the Nuclear Regulatory Commission as a Licensee Event Report in recognition of the potential for Primary Containment (a Principal Safety Barrier) being inoperable for an indeterminate amount of time. Additionally, the A, B and C RHR Pumps, and all their modes of operation, could have been operated outside the design basis for an indeterminate amount of time had the analysis been found unacceptable.
3731994007 | LaSalle 1 | 05/17/1994 | 06/16/1994 | 9406210344 | <strong>Residual Heat Removal System Shutdown Cooling Isolation Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1994, at 0155 hours, an isolation signal to the Residual Heat Removal (RHR)[BO] Shutdown Cooling Inboard Isolation Valve, 1E12-F009, was received, causing it to close. At the time of this event, Unit 1 was in Operating Condition 5 (Refuel).<br /><br /> The event occurred during the performance of LTS-800-105, 'Diesel Generator 1A Twenty-Four Hour Run Surveillance'. During this test, a loss of off-site power is simulated, causing the Diesel Generator to auto-start and reenergize its associated Bus 142Y. At the point when the Diesel Generator reenergized Bus 142Y, restoring power to shutdown cooling inboard isolation valve, the valve closed, isolating shutdown cooling. Subsequent investigation determined the isolation signal was generated when power was restored to the Leak Detection System, also powered from Bus 142Y. The closure of this valve caused the 1A RHR Pump to trip resulting in a loss of Shutdown Cooling flow to the reactor. <br /><br /> The cause of the event was inadequate procedural guidance for establishing initial conditions for the deenergization of the bus. Specifically, steps should have been included in the procedure to preclude shutdown cooling isolation during this test. Procedures are being revised accordingly. <br /><br /> This event is being reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature (ESF) System.
3731994008 | LaSalle 1 | 06/07/1994 | 07/06/1994 | 9407130031 | <strong>Standby Liquid Control System Operation Above Technical Specification 4.1.5.c.3 Limit Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>During review of previously completed work requests related to Standby Liquid Control (SBLC, SC)[BR] Pump Discharge Safety Relief Valves, test data was discovered which determined 1C41-F029A relief valve setting had been above 1400 psig, which is the limit of Technical Specification 4.1.5.c.3. <br /><br /> On July 20, 1985, a relief valve setting of 1410 psig was accepted even though Procedure LOS-SC-R1 required a setting of less than or equal to 1400 psig. The unit entered Mode 2 on July 27, 1985, when the SBLC System was required to be operable. The relief valve setting was not corrected until March 7, 1986. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3731994009 | LaSalle 1 | 06/03/1994 | 07/01/1994 | 9407060248 | <strong>Isolation of Shutdown Cooling Due to High Suction Flow</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1994, at 0220 hours, while in the process of swapping Residual Heat Removal (RHR) [BO] Shutdown Cooling (SDC) from A Loop to B Loop, a High Suction Flow Isolation was received shortly after starting the 1B RHR Pump, isolating the SDC System. At the time of this event Unit 1 was in Operating Condition 5 (Refuel). <br /><br /> On June 5, 1994, at 0836 hours, while starting a second RHR Pump to support the Reactor Vessel Leakage Test, a High Suction Flow Isolation was again received. After verifying no leaks in the system, jumpers were installed, per procedure to bypass the High Suction Flow Isolation signal. Both 1A and 1B RHR Pumps were restarted. When the jumpers were removed, at 1039 hours, another High Suction Flow Isolation was received. At the time of these events Unit 1 was in Operating Condition 4 ( Cold Shutdown). <br /><br /> On May 18, 1994, an Out of Service (OOS) had been hung so that maintenance could be performed on Excess Flow Check Valve 1E12-F359A. This OOS required draining the sensing lines to Differential Pressure Switches (DPS) DPS-1E12-N012AA and DPS-1E12-N012AB. When the OOS was cleared on May 30, 1994, the sensing lines for the DPS were apparently not backfilled. <br /><br /> The RHR System was verified to have no leaks, and then restarted in the Shutdown Cooling mode following each isolation.
3731994010 | LaSalle 1 | 07/05/1994 | 11/02/1994 | 9411210290 | <strong>Scram Due to Reactor Water Level Control Signal Loss to the 1B Turbine Driven Reactor Feed Pump</strong><br /><i>Abstract:&nbsp;</i>At 0336 hours on July 5, 1994, Unit 1 scrammed from a power level of 601 MWe and 56.4% Core Thermal Power. The unit had been in Operational Condition 1 (Run) with the 1B Turbine Driven Reactor Feed Pump (TDRFP, FW)[SJ] in 3 element control and the Motor Driven Reactor Feed Pump in manual. The 1A TDRFP was unavailable pending additional post modification testing of the feedwater control system. Just prior to the scram, a loss of the Reactor Water Level Control signal caused the 1B TDRFP to ramp to minimum speed, resulting in a decrease in Reactor Vessel level. The reactor scrammed on a Reactor Low Water Level Scram (12.5 inches). The lowest reactor vessel level during the transient was -6 inches. Normal level was restored using the Motor Driven Reactor Feed Pump. Subsequent investigation determined the cause of the feedwater transient was due to a failure of the Manual Control Board Unit. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an event that resulted in automatic actuation of the Reactor Protection System. This revision updates the Corrective Action taken with respect to the failure of the Manual Control Board Unit.
3731994011 | LaSalle 1 | 07/08/1994 | 08/08/1995 | 9508230054 | <strong>Unit 1 Scram Due to a Feedwater Signal Spike</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1994, at 0550 hours, the unit was at 58% power preparing for power ascension. When the 1D Condensate Pump was started, the 1B Turbine Driven Reactor Feed Pump (TDRFP) developed flow swings of 2 million pounds per hour. Flow was stabilized with minor adjustments to the Motor Driven Reactor Feed Pump. the Manual/Automatic (M/A) station output signal, which produced oscillations in the control valve. During an attempted adjustment to the signal gain, a spike occurred resulting in a loss of speed on the 1B TDRFP, a loss of feed flow from the pump, and reduction of reactor vessel level. Repeated attempts to control level by use of the raise and lower pushbuttons at the manual and manual backup stations resulted in vessel level fluctuations until vessel level reached the 55.5 inch High Level Turbine trip and resulted in a Reactor Scram at 0947 hours. <br /><br /> The 1B Emergency Diesel Generator (EDG), which was synchronized to the grid for a scheduled surveillance, assumed an abnormal amount of current and VAR's as a result of the grid disturbance caused by the loss of the Unit 1 generator. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in automatic actuation of the Reactor Protection System.
3731994012 | LaSalle 1, LaSalle 2 | 08/15/1994 | 09/13/1994 | 9409220082 | <strong>Untested Contacts in the NR and RP Systems Due to Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1994, at 1500 hours, the station was informed that NUS, as part of the Safety Related Contact Testing Adequacy review, had identified several relays in the Neutron Monitoring System which had not been tested for either Unit 1 or Unit 2. The relays which were identified are 1(2)C51B-K18/PS12, PS22, PS31, PS32, PS41, and PS51. These relays are interlocked with the Reactor Mode Switch in order to determine the setpoint of the Average Power Range Monitor (APRM) high neutron flux trip channels. At the time of this event, Units 1 and 2 were in Operating Condition 1 (Run). <br /><br /> The cause of this event is attributed to procedural deficiencies. The relays have never been included in any LaSalle surveillance. <br /><br /> An Operability Determination was performed and it was determined that the APRM channels are operable in the Run Mode, but are not operable in any other operational condition until this interlock is satisfactorily tested. Therefore, within one hour of either unit being taken out of Run, the respective Reactor Mode Switch shall be locked in the Shutdown position until the interlock is satisfactorily tested. This will be controlled administratively through the Degraded Equipment Log. <br /><br /> This event is being reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(i)(B) due to operation or condition prohibited by the plant's Technical Specifications because of the surveillance testing not having been performed.
3731994013 | LaSalle 1 | 11/14/1994 | 12/13/1994 | 9412200213 | <strong>RCIC Declared Inoperable Due to Control System Oscillation</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1994, at 1000 hours with Unit 1 in Operating Condition 1 (Run) 100% power, the Reactor Core Isolation Cooling (RCIC) System was declared inoperable. During the performance of procedure LOS-RI-Q5, 'Reactor Core Isolation Cooling (RCIC) System Pump operability, Valve Inservice Test in Conditions 1, 2, 3 and Cold Quick Start', rapid oscillation of the turbine governor valve (1E51-F361) occurred, causing unstable turbine speed and flow response.<br /><br /> The cause of this event has been determined to be the failure of a sub-component within the speed controller (EG-M). Repairs and component replacements were made on the RCIC Turbine Speed and Flow Control System. On November 20, 1994, a cold quick start per LOS-RI-Q5, was successfully completed. The RCIC System was subsequently declared operable. <br /><br /> This event is reportable pursuant to 10CFR50.73(s)(2)(v) due to RCIC being declared inoperable.
3731994014 | LaSalle 1 | 11/23/1994 | 12/20/1994 | 9412290097 | <strong>High Pressure Core Spray (HPCS) Pump Made Inoperable In Unplanned/Not Clearly Understood Manner Due To Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1994, at 0327 hours, with Unit 1 in operational Condition 1 (Run) at 100% power, the High Pressure Core Spray (HPCS)[BG] Pump was unexpectedly made inoperable. The equipment operator had opened the power supply breaker (1E22P301A-CB6) from the Unit 1 battery and charger to DC Bus 113 in accordance with Out Of Service(OOS) 940013153. The OOS was intended to isolate Control Power to the 1B Diesel Generator to troubleshoot or replace the K-15 relay which had failed the previous shift. Alarms were immediately received in the Main Control Room indicating loss of control power to the HPCS Pump when the breaker CB6 was opened. The Operating Supervisor in the Control Room determined that Bus 113 had been deenergized during the implementation of the OOS. HPCS was restored to operable condition by 0620 hours on November 23, 1994 by reconfiguring the OOS. <br /><br /> The Root Cause of this event is management deficiency in that clear instructions were not provided and the scope of the OOS was not properly identified. <br /><br /> Additional training will be provided to operators to ensure compliance to the administrative requirements for preparing and reviewing OOS packages in accordance with LaSalle Administrative Procedure LAP-900-4, 'Equipment Out-of-Service'. <br /><br /> This event is reportable pursuant to 10CFR50.73(a)(2)(v) due to HPCS being declared inoperable.
3731994015 | LaSalle 1, LaSalle 2 | 12/12/1994 | 05/15/1998 | 9805210088 | <strong>Unit 1 Primary Containment Isolation and Scram due to Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1994, Unit 1 was in Mode 1 (Run) at 92% power. At 2132 hours, a Group 1 Main Steam Isolation Valve (MSIV) Primary Containment Isolation (PCIS) occurred due to a spurious Main Steam Line (MSL) High Flow signal on one PCIS channel while a calibration was being performed on the other channel. The closure of the MSIVs caused the Reactor to scram. All control rods fully inserted. Three Safety Relief Valves (SRVs) lifted and reset at appropriate pressures. Two additional scram signals were generated due to reactor level perturbation caused by the manual operation of SRVs to control reactor pressure. <br /><br /> The cause of the scram was a Group 1 Isolation signal initiated by the spurious trip and reset of MSL High Flow switch 1E31-N009C. This occurred during the performance of Instrument Surveillances LIS-MS-102 and LIS-MS-302. Investigation determined the 1E31-N009C Static-O-Ring Switch had failed. This switch was replaced. The failed switch was disassembled and inspected to determine the cause of failure. The cause of the failure was oil contamination of an internal switch assembly. Due to the age and isolated nature of the failure, the root cause can not be determined. <br /><br /> While performing a review of documents, it was discovered that an NTS item tracking the generation of a supplemental LER had been closed without submission of the required supplement. <br /><br /> This report is being submitted per 10 CFR 50.73(a)(2)(iv) due to an automatic actuation of the Reactor Protection System.
3741994001 | LaSalle 2 | 01/18/1994 | 02/15/1994 | 9402230274 | <strong>Unit 2 Reactor Scram When in Shell Warming on the Main Turbine Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1994, Unit 2 was in Operational Condition 2 (startup). Work on Main Steam Isolation Valve (MSIV) Limit switches was in progress. At 0133 hours during the Main Turbine Shell Warming Process, first stage pressure increased sufficiently to cLear the thirty (30) percent bypass of the Turbine Stop Valve Closed Scram. A Reactor Scram occurred as the Turbine Stop Valves were already in a closed position.<br /><br /> All components functioned as designed. The required notifications were made, and equipment was returned to normal operating status. <br /><br /> An investigation was performed and the root cause was determined to be Operator Personnel Error. The Operator at Lowed himself to become distracted white being interviewed by an off-site evaluator and did not closely monitor the shell warming process. <br /><br /> This is reportable per 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature (ESF) and unplanned automatic Reactor Protection System (RPS) Reactor Scram.
3741994002 | LaSalle 2, LaSalle 1 | 02/21/1994 | 03/22/1994 | 9403290053 | <strong>Reactor Core Isolation Cooling System Inoperable Due to Turbine Exhaust Line Pressure Spike</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1994, at 1127 hours, Unit 2 Reactor Core Isolation Cooling System (RCIC) turbine exhaust rupture discs ruptured during system testing. Both discs ruptured immediately upon admittance of steam to the turbine. The Control Room Operator responded to various annunciations and tripped the RCIC turbine approximately 30 seconds later, and the system was declared inoperable.<br /><br /> It was subsequently determined that the discs ruptured due to a pressure spike in the turbine exhaust line. The pressure spike was caused by an accumulation of condensate in the exhaust One from previous system operation. The mater accumulation was due to a combination of a configuration control deficiency will a foreign material exclusion deficiency which Led to blockage of the turbine exhaust drain line. <br /><br /> On March 6, 1994, at 1615 hours, the Unit 2 RCIC System was restored to operability. Unit 1 RCIC System will be restored to operable status prior to operating Condition 1 (Run) from the current refuel outage. <br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(v), loss of a safety function; 10CFR50.73(a)(2)(ii)(B), condition outside the Design Basis; and 10CFR50.73(a)(2)(i)(B), condition prohibited by Technical Specifications.
3741994003 | LaSalle 2 | 06/16/1994 | 07/13/1994 | 9407210044 | <strong>Technical Specification Surveillance Exceeded Time Interval Due to Extremely Hot Weather</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1994, Unit 2 Technical Specification Surveillance Requirement 4.7.10.a, Main Turbine Bypass System (TBP), exceeded the specified weekly surveillance interval. <br /><br /> On June 17, 1994, Unit 2 Technical Specification Surveillance Requirement 4.3.1.1, for monthly functional tests of four (4) Reactor Protection System (RPS) Instrumentation of the Average Power Range Monitors (APRMs) Functional Units listed in Table 4.3.1.1-1, exceeded the specified weekly surveillance interval. <br /><br /> LaSalle requested and received a Notice of Enforcement Discretion (NOED) from the NRC at 1800 hours on June 15, 1994, which allowed an extension of surveillance testing until 2359 hours on June 19, 1994. The cause of the event was the combination of an extremely low reserve on the Commonwealth Edison Company (ComEd) distribution system and extremely hot weather. <br /><br /> The RPS Technical Specification Surveillances were satisfactorily completed at 0300 hours on June 18, 1994. The Turbine Bypass System surveillance was satisfactorily completed at 0335 hours on June 18, 1994. <br /><br /> This event is submitted pursuant to the requirements of 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Plant's Technical Specifications.
3741994004 | LaSalle 2 | 06/21/1994 | 07/14/1994 | 9407210068 | <strong>Reactor Scram Due To Tripping the Feed Breaker to Switchgear 231A/B</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1994, Unit 2 was in operating condition 1 (Run) operating at approximately 1110 MWe. At approximately 2230 hours, the feed breaker from 6900 Volt Switchgear 251 to 6900-480/277 Volt Transformers 231A and 231B tripped. The supply breaker to Transformers 231A and 231B opening resulted in the loss of power to numerous pieces of balance of plant equipment. Several air operated valves were affected by the loss of power: the 'A' Turbine Driven Reactor Feed Pump Minimum Flow valve failed open, all Condensate/Condensate Booster Minimum Flow valves failed open, and the 'A' Heater Drain Pump Forward valve failed closed. The failing of these valves resulted in a reduction of feedwater flow to the reactor. Due to this loss of feedwater flow, a Level 3 reactor scram was received. The plant responded as expected to this event.<br /><br /> The cause of the breaker tripping was a degraded trip output Silicon Controlled Rectifier (SCR) on the Transformer 231B 6900 KV ground fault relay. <br /><br /> This event is being reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature (ESF) and unplanned automatic Reactor Protection System (RPS) reactor Scram.
3741994005 | LaSalle 2 | 08/08/1994 | 10/19/1994 | 9410260352 | <strong>Failure of RCIC Turbine Exhaust Diaphragm Pressure Switch Relay Actuation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 8,1994, at 0525 hours, Unit 2 was in Operational Condition 1 (Run) and Surveillance LIS-RI-209, 'RCIC Turbine Exhaust Diaphragm High Pressure Isolation Calibration', was being performed.<br /><br /> During the performance of LIS-RI-209, the RCIC turbine exhaust diaphragm 2E51-N012A pressure switch failed to actuate as required. The cause of the pressure switch failure to actuate during the surveillance was the incorrect identification by the Instrument Maintenance (IM) Department Technicians of the lead to be lifted from terminal point EE1. Also, the second person verification process did not identify the error, resulting in the wrong lead being lifted and the pressure switch actuation signal not being received. The RCIC System was isolated and declared inoperable per Technical Specification 3.7.3. <br /><br /> A root cause investigation was performed and the root cause was determined to be personnel error. The LIS-RI-209 Surveillance was later successfully performed, and the RCIC System was declared operable at 1252 hours on August 8, 1994. <br /><br /> This report is being submitted per 10CFR50.73(a)(2)(v) due to any event or condition that alone could have prevented the fulfillment of a safety system function.
3741994006 | LaSalle 2 | 08/25/1994 | 09/21/1994 | 9409280217 | <strong>Reactor Scram Due to Spurious Opening of Main Turbine Bypass Valves</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1994, Unit 2 was in Operating Condition 1 (Run) operating at approximately 1118 MWe. At approximately 0328 hours, the Main Turbine Control Valves (CV) began to drift closed. In response to this closure, the Main Turbine Bypass Valves (BPV) began to open sequentially to control Reactor pressure. Approximately 13 seconds after the CV's began to close the BPV's closed, which resulted in an increase in Reactor pressure. The increasing pressure collapsed voids in the core which increased moderation and in turn caused power to increase. When Reactor pressure reached approximately 1023 psig, a Reactor Scram occurred due to reaching the Average Power Range Monitor (APRM) Hi Flux Scram setpoint. <br /><br /> The apparent cause of the CV and BPV movement was due to high frequency noise on three of the cards in the Electro-Hydraulic Control circuitry. <br /><br /> An additional contributing cause was nine cards were found not fully seated in their connectors. <br /><br /> This event is being reported to the Nuclear Regulatory Commission as a Licensee Event Report in accordance with 10CFR50.73(a)(2)(iv) due to an actuation of an Engineered Safety Feature (ESF) and unplanned automatic Reactor Protection System (RPS) reactor Scram.
3741994007 | LaSalle 2, LaSalle 1 | 10/03/1994 | 11/02/1994 | 9411090339 | <strong>Division 1 Group 2 and Group 4 Primary Containment and Reactor Building Ventilation Isolation Signal Due to a Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1994 Units 1 and 2 were in Operational Condition 1 (Run) at 99 percent and 74 percent power, respectively. At 2357 hours a Division 1 Group 2 and Group 4 Primary Containment Isolation System (PCIS) and Reactor Building Ventilation (VR) Isolation Signal occurred. The Unit 2 Standby Gas Treatment System (SBGT) auto-started and was subsequently shutdown. operability surveillance.) <br /><br /> After verification that no valid isolation signal was present, LaSalle Operating Abnormal (LOA) procedure LOA-VR-01 was entered. PCIS Group 1 High Temperature and High Delta Temperature isolations were defeated to prevent Main Steam Line (MSL) Isolation on High Delta Temperature, and a one-hour timeclock was entered. <br /><br /> The cause of the spurious isolation was traced to a blown fuse . The fuse was replaced, utilizing LaSalle Administrative Procedure (LAP) LAP- 400-11, and all systems were restored to normal lineup. Upon restoration of the VR System, the Unit 1 Steam Tunnel temperatures returned to normal, isolations were restored to normal operating status, and the timeclock was exited.<br /><br /> This event is reportable pursuant to 10CFR 50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature (ESF).
3741994008 | LaSalle 2 | 10/19/1994 | 04/04/1995 | 9504190050 | <strong>Reactor Scram Due to Electro-hydraulic Control Line Break</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1994, Unit 2 was in operational Condition 1 (Run). Turbine Control Valve oscillations were first observed at 1015 hours. Plant personnel were unable to immediately determine the cause of the oscillations and as a result, Turbine Electro-hydraulic Control (EHC,EH)[TG] piping, which was subjected to the same oscillations hydraulically, began to leak. The piping eventually broke due to low cycle fatigue. A Main Turbine trip occurred due to the loss of EHC fluid pressure, and the reactor scrammed on high neutron flux when the turbine control valves closed.<br /><br /> Reactor Core Isolation Cooling (RCIC, RI)[BN] and Anticipated Transient Without Scram-Recirc Pump Trip/Alternate Rod Insertion (ATWS-RPT/ARI) initiated on spurious low reactor water level (Level 2, -50') signals. Six Safety Relief Valves (SRVs) opened sequentially following the turbine trip. The required notifications were made, and troubleshooting and investigation were initiated. <br /><br /> An investigation was performed, and the root cause for the EHC control valve oscillations was due to a faulty connector on the EHC permanent magnet generator (PMG) 30 Vdc power supply. The faulty connector allowed the 30 Vdc power to cycle between the house supplied power supply and the PMG power supply. <br /><br /> EHC piping and the electrical connector were repaired and an extensive inspection of EHC piping was completed prior to starting up Unit 2.
3741994009 | LaSalle 2 | 11/02/1994 | 12/02/1994 | 9412080076 | <strong>RCIC Declared Inoperable Due to Inability to Determine System Filled and Vented</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1994, at 1050 hours with Unit 2 in Operating Condition 1 (Run) at 95% power, the Reactor Core Isolation Cooling (RCIC) System was declared inoperable. The steam supply was isolated to the RCIC turbine when Operating Personnel could not determine that the system was properly filled and vented. <br /><br /> The RCIC pump had been lined up to take a suction from the Pressure Suppression Pool (PSP) to support scheduled maintenance on the PSP suction motor operated valve (MOV)(2E51-F010). The procedure for aligning the system in this method required that a once per shift verification of system fill and vent status be made. When the verification was made during the day shift on November 2, 1994, the Auxiliary operator performing the verification could not visually determine the fill and vent of the system at the system high point vent sightglass. <br /><br /> The RCIC System was declared inoperable at 1050 hours on November 2, 1994, and removed from standby operation. An investigation into the cause of the problem was initiated. The investigation determined that the system was properly filled and vented by monitoring input into the Reactor Building Equipment Drain Tank (RBEDT) when the high point vent was open. The tank input stopped when the high point vent was closed. The sightglass flow indication 'flapper' was in the open position, and when combined with the clarity of the water, the Operator was not able to detect flow through the sightglass. <br /><br /> The System was subsequently declared operable at 2215 hours on November 2, 1994.
3741994010 | LaSalle 2 | 12/14/1994 | 01/12/1995 | 9501190303 | <strong>Division 2 Emergency Core Cooling System and Reactor Core Isolation Cooling Initiation Due to the Pressure Switch Isolation Valve Leaking</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1994 at 1015 hours, with Unit 2 in Operational Condition 1 (Run) at 100% power, a Division 2 Emergency Core Cooling System (ECCS) and Reactor core Isolation Cooling (RCIC) low level initiation occurred. The initiation occurred while Instrument Maintenance (IM) Technicians were performing LaSalle Instrument Surveillance, LIS-NB-418B, 'Unit 2 Reactor Vessel Low Pressure and Injection Line Low Pressure, RHR 'B'/RHR 'C' (LPCI) Injection Valve Open Permissive Monthly Functional Test'. The IM Technicians were in the process of valving out pressure switch 2B21-N413D, when a pressure spike in a common sensing line/reference leg caused a low reactor vessel level initiation signal for Division 2 ECCS and RCIC to occur. <br /><br /> At the time of this event, the 2A Diesel Generator was out of service for planned maintenance. All ECCS Systems were fully operable. Operations verified that the RCIC and RHR B/C initiations were inadvertent and restored these systems to normal standby operation. <br /><br /> This report is being per 10CFR50.73(a)(2)(iv) due to an automatic actuation of an Engineered Safety Feature.
3741994011 | LaSalle 2 | 12/20/1994 | 01/18/1995 | 9502010231 | <strong>High Pressure Core Spray (HPCS) Inoperable Due to HPCS Diesel Generator Cooling Water Pump Trip Due to a Design Logic Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1994, at approximately 1251 hours with Unit 2 in Operational Condition 1 (Run) at 100% power, LaSalle Operating LOP-DG-05, 'Startup of 1B(2B) Diesel Generator (DG) 1(2)E22-S001', was being performed. <br /><br /> Approximately one minute after shutting down the 2B DG per LOP-DG-05 with the 2B DG Cooling Water Pump running, the pump's control handswitch was taken to the Normal-After-Start position per the procedure. At this time, the pump tripped, and the 2B DG Cooling Water Pump Trip Alarm came up. The pump breaker was found to be tripped. Subsequently, the pump breaker was inspected, as was the motor and pump, and no problems were found. A megger test on the motor was done with no damage found. The pump was started with acceptable current and voltage readings. The breaker was inspected and the control switch was tested. The Control Switch was subsequently changed as a precautionary measure.<br /><br /> The High Pressure Core Spray (HPCS) System was declared inoperable due to its room cooler being inoperable. <br /><br /> The cause of this event is a design error. caution cards were hung on the 1B and 2B Diesel Generator Cooling Pump Control Room control switches describing the design deficiency and steps needed to avoid an inadvertent pump trip.
3741994012 | LaSalle 2 | 12/21/1994 | 01/19/1995 | 9501270359 | <strong>High Pressure Core Spray Declared Inoperable Due to 2B Diesel Generator Exceeding Its 72 Hour technical Specification</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1994, at 2120 hours, the Unit 2 High Pressure Core Spray (HPCS) Diesel Generator (DG) B was declared inoperable and taken out of service for planned maintenance to install a shutdown solenoid and replace the DG synchronizing motor. This placed the HPCS DG in a 72 hour Technical Specification Limiting Condition for Operation (LCO). <br /><br /> On December 21, 1994, at 1830 hours during the post maintenance test (PMT) run of the 2B DG, it was discovered that the replacement synchronizing motor was wired such that the speed of the governor reacted in the reverse direction of the Control Room switch indication. Troubleshooting and subsequent repair of the synchronizing motor caused the 72 hour timeclock to be exceeded. The Technical Specification LCO Action Statement was met in that the HPCS System was declared inoperable at the time that 72 hours had elapsed. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(v), any event that alone could have prevented the fulfillment of a safety function needed to remove residual heat.
3821994001 | Waterford 3 | 01/18/1994 | 02/17/1994 | 9403020157 | <strong>Component Cooling Water System Cross-Connected Through Incorrect Valve Positioning</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1994 Waterford 3 was at 100% power when it was discovered that component cooling water(CCW) valves CC-8241A and CC-8251B were open approximately 30%. These valves were required to be fully closed. This condition was discovered while troubleshooting what was originally thought to be a leak past the seats of CCW valves CC-807B, CC-823B and CC-835B. With valves CC-8241A and CC-8251B open, train A and train B of the CCW system were incorrectly cross-connected which placed the CCW system outside of its design. <br /><br /> The root cause of this event was a lack of work instructions for the change-out of the operators of these valves when station modification package 1960 was implemented. Valves CC-8241A and CC-8251B operators changed from pneumatic to manual without the aid of work instructions. The valves were apparently installed with the disc partially open but with the position indicator showing closed. During the evaluation of this event the plant determined that the CCW system was operable. As a result, this event did not compromise the health and safety of the public. LER 91-023 documents a similar occurrence where the CCW system was incorrectly cross-connected.
3821994002 | Waterford 3 | 08/08/1984 | 03/11/1994 | 9403160196 | <strong>Sealed Sources in Use Not Leak Tested per TS Due to Inadequate Controls</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1994, at 1455 hours, Radiation Protection (RP) personnel determined that five radioactive sealed sources had not been leak tested. On February 17, 1994, at 0800 hours, RP personnel identified another source that had not been leak tested. All six sources were received at Waterford 3 during the period December 22, 1983, to February 28, 1991. Technical Specification (TS) 4.7.9.2a requires that all sealed sources in use and containing radioactive material in excess of 100 microcuries of beta and/or gamma emitting material or 5 microcuries of alpha emitting material to be tested for leakage and/or contamination at least once per six months.<br /><br /> The root cause of this event is inadequate administrative controls regarding the identification and control of sources that need to be leak tested. The sealed sources were satisfactorily leak tested on the same day the conditions were discovered. The appropriate procedure will be revised and training will be conducted by June 24, 1994. LER 88-024 reported a similar event. This event did not compromise the health and safety of the public.
3821994003 | Waterford 3 | 03/05/1994 | 04/01/1994 | 9404070141 | <strong>Reactor Protection Instrumentation Inoperable Due to Missed Surveillances</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 003%. On March 5, 1994 at approximately 0525 hours, while shutdown for refueling outage, it was discovered that the surveillance requirements of T.S. Table 4.3-1 were not completely satisfied for Manual Reactor Trip, Logarithmic Power Level-High, Reactor Protection System Logic, and Reactor Trip Breakers prior to enabling Control Element Assembly movement. This placed the Reactor Protective instrumentation in a condition prohibited by T.S.. This condition was discovered while performing Plant Protection system surveillances in preparation for scheduled maintenance on the Control Element Drive Mechanism Control System. The root cause for this condition is the omission of relevant prescriptive information from the applicable operations procedures. Immediate corrective actions for this event included opening the Reactor Trip Switchgear Breakers to place the plant in a mode where the specifications did not apply. Actions to prevent recurrence include, in part, procedural improvements and personnel debriefing. This event did not compromise the health and safety of the public or plant personnel.
3821994004 | Waterford 3 | 03/07/1994 | 04/05/1994 | 9404110133 | <strong>Degraded CCW Heat Exchanger Discovered While Shutdown, Due to Biological Fouling</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1994, during plant shutdown for Refuel 6, it was determined that Component Cooling Water (CCW) Heat Exchanger 'A' was degraded according to performance testing conducted in response to Generic Letter 89-13. The CCW system is designed to provide cooling water to safety-related components at a maximum temperature of 115 degrees F under accident conditions. Evaluation of test results, extrapolated to design accident conditions, predicted a CCW outlet temperature of 117.2 degrees F. The degraded condition of CCW Heat Exchanger A is believed to be outside the design basis of the system in that the required capacity of the heat exchanger may not have been available for maximum design accident conditions. The root cause of the degradation is biological fouling of the heat exchanger. Corrective actions included chemical cleaning of CCW Heat Exchangers 'A' and 'B'. An engineering review concluded that the heat exchanger would have fulfilled its intended safety function prior to shutdown because the heat removal capacity of the degraded CCW Heat Exchanger would have been adequate to remove accident heat loads. Therefore, this event did not compromise the health and safety of the general public or plant personnel.
3821994005 | Waterford 3 | 04/15/1994 | 05/13/1994 | 9405190094 | <strong>Valves in the Inservice Test Plan - Pump and Valve, not Tested</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1994, a Shift Technical Advisor discovered that several valves were not being tested per the requirements of ASME section XI. Specifically valves SI-6011, SI-6012, CVR-401A and CVR-401B remote position indicators were not being observed at least once every two years to verify that valve position matched remote indication. Also identified was that power operated valves SBV-113A, SBV-113B, SBV-114A and SBV-114B were not being timed in their closed stroke direction. Technical Specification 4.0.5(a) requires that inservice testing of ASME Code Class 1, 2, and 3 pumps and valves be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code. <br /><br /> The root cause of this event is inappropriate action resulting in a failure to properly incorporate IST Plan requirements into the appropriate operating procedures during initial IST Plan implementation. A Pump & Valve Review Team has been established to perform an in depth review of the Plan and the associated implementing documents. This event did not compromise the health and safety of the public.
3821994006 | Waterford 3 | 11/03/1992 | 05/11/1994 | 9405130277 | <strong>Error in RCS Mass Balance Equation</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1994, Waterford SES Unit 3 was shutdown for refueling in Mode 5 while conducting a compliance review check of previous Reactor Coolant System (RCS) leak rate calculations that were based on Attachment 10.4 of Revision 8 to Operating Procedure OP-903-024. At this time it was determined that on November 3, 1992, during the previous refueling outage (Refuel 5), that an unidentified RCS leak rate of >1 GPM had occurred during Mode 5 before entering Mode 4, which constituted noncompliance with Technical Specification (TS) 3.0.4. <br /><br /> The root cause of this event was inadequate technical review of a change made to the RCS mass balance equation in Attachment 10.4 of Revision 8 to OP-903-024. Immediate corrective action included a temporary approved change to Attachment 10.4, correcting the equation. Action to prevent recurrence will be to have Operations personnel review this event. The event did not compromise the health and safety of the public.
3821994007 | Waterford 3 | 04/26/1994 | 05/24/1994 | 9405260114 | <strong>Relay Failure Causes Reactor Power Cutback & Subsequent Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 0808 on April 26, 1994, a Reactor Power Cutback and Turbine Setback to 50% governor valve position occurred while placing the Reactor Power Cutback system in service at 70% reactor power. An automatic reactor trip occurred approximately 2 minutes later due to a low Pressurizer Pressure Core Protection Calculator Auxiliary trip set at 1860 psia. The Reactor Power Cutback actuation was caused by the presence of an erroneous Feedwater pump 'B' trip input signal to the Reactor Power Cutback circuitry. The subsequent low Pressurizer pressure and reactor trip resulted from the cooldown induced by a mismatch between turbine power and reactor power following the Reactor Power Cutback. The root cause of the erroneous Feedwater pump 'B' trip input signal was found to be a failure of a Westinghouse model BFD44S non-safety relay which provides 'B' Feedwater pump trip status input to the Reactor Power Cutback circuitry. Immediate corrective actions included replacing the faulty relay and removing the Reactor Power Cutback system from service. Subsequent corrective actions will include, in part, evaluations and enhancements along with event review by operations personnel. This event did not compromise the public health and safety.
3821994008 | Waterford 3 | 05/03/1994 | 07/07/1994 | 9407120338 | <strong>Circuitry Problem Affects ESF Filtration Unit Heaters</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1994, Engineering identified a circuitry problem involving the response times of the temperature controllers and time delay relays for the ESF filtration unit heaters. The temperature controllers for the ESF filtration unit heaters were replaced between 10/92 and 4/93 via Design Change 3292. The response time problem potentially existed since those replacements. The root cause of this event is inadequate design change verification with respect to replacement part critical characteristics. A contributing cause existed in that personnel missed opportunities to promptly identify concerns involving ESF filtration unit performance. This event did not compromise the health and safety of the public.
3821994009 | Waterford 3 | 02/18/1994 | 06/20/1994 | 9406230239 | <strong>Encapsulation Tube Containing Fuel Rod Hanging From Spent Fuel Handling Machine</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1994 at 1030, Waterford 3 was operating in Mode 1 at 100% power when a Senior Reactor Operator (SRO) with the Operations Refueling Group discovered an object hanging from the Spent Fuel Handling Machine (SFHM). The object was later determined to be a fuel encapsulation rod containing a damaged fuel rod from a previous fuel reconstitution campaign. <br /><br /> The root cause of this event is inadequate barriers in that the controls in place for the SFHM were not sufficient to prevent manipulation of the SFHM hoist and an unauthorized lift of Special Nuclear Material. A contributing cause is the design of the fuel encapsulation tube. <br /><br /> Corrective action included deengergizing the power strip to the computer, controlling the power cabinet and override keys and revising an Operation's procedure and lesson plan. Further action will include long term controls on the SFHM and development of actions to prevent lifting of the encapsulation tube with the SFHM tool. This event did not compromise the health and safety of the public and plant personnel.
3821994010 | Waterford 3 | 06/07/1994 | 09/09/1994 | 9409160323 | <strong>Boron Dilution While Purging Letdown Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1994, Waterford 3 was at 100% power when a purge of the Letdown Radiation Monitor was initiated. Personnel performing the purge were unaware that the purge flow was routed back to the Chemical Volume & Control System. This resulted in an inadvertent boron dilution in the Reactor Coolant System (RCS) and an increase in reactor power. <br /><br /> The root cause of this event was an inadequate review of the Station Modification Package (SMP) which installed the monitor. Contributing causes which resulted from the SMP are inadequate procedures, drawings, and training which all led to false assumptions regarding the purge water flow path. Corrective action includes reviewing previous SMP's on systems that can alter the boron concentration of the RCS for the potential to cause such an event. <br /><br /> This event did not compromise the health and safety of the public and plant personnel in that no Technical Specification limits were exceeded and the event was resolved expeditiously. No similar events have been reported as LER'S. This report is being submitted as a voluntary LER.
3821994011 | Waterford 3 | 07/20/1994 | 09/15/1994 | 9409210255 | <strong>Boron Dilution Due to Improper Makeup Blend</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1994 at 2000 hours, Waterford 3 was in Mode 1 at 100% power when a Primary Nuclear Plant Operator (PNPO) commenced the addition of an improper blend of makeup water to the Volume Control Tank (VCT), which caused the Reactor Coolant System (RCS) temperature and reactor power to increase. Upon realizing what happened, the PNPO added boric acid to the RCS causing the RCS cold leg temperature to drop below 544 degrees F and reactor power to drop to 97%. The PNPO stabilized the plant by reducing the turbine load.<br /><br /> The root cause of this event was personnel error due to a lack of self- checking by not ensuring intended actions were correct. A contributing cause was neglecting to communicate information to the Control Room Supervisor (CRS). <br /><br /> Corrective action included counseling the PNPO in accordance with the Improving Human Performance (IHP) Program. Further action will be to have Operations Personnel review this event. This event did not compromise the health and safety of the public.
3821994012 | Waterford 3 | 09/07/1994 | 10/07/1994 | 9410130068 | <strong>Noncompliance with EDG Surveillance Requirements Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1994, Waterford 3 training personnel discovered the failure to perform Technical Specification (TS) Surveillance Requirements 4.8.1.1.2.d.3a and 3b and 4.8.1.1.2.d.5a and 5b for the 4160V Bus 3AB and 480V Bus 31AB load groups. These surveillance requirements demonstrate operability of the Emergency Diesel Generators (EDGs) by ensuring that during a loss-of-offsite power by itself, or in conjunction with a safety injection actuation test signal, the emergency buses will deenergize, load shed, and properly reload. By 1316 hours that same day, EDG B had been declared inoperable and TS Action 3.8.1.1.b entered. Buses 3AB and 31AB were aligned to the B-train at that time. The most probable root cause of this event is an inadequate procedure. Corrective actions include tests of loads from Buses 3AB and 31AB, reviews of selected surveillance procedures and appropriate procedure revisions. TS Bases for 3/4.8.1 will be revised to clarify what is meant by permanently connected loads. The missed surveillance requirements will be fully implemented prior to startup following Refuel 7. This event did not compromise the health and safety of the public.
3821994013 | Waterford 3 | 08/19/1994 | 11/04/1994 | 9411090412 | <strong>Boron Dilution While Rinsing CVC Ion Exchanger</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1994, an undesired boron dilution of the Reactor Coolant System (RCS) occurred while performing blended makeups to the Volume Control Tank (VCT) during the rinsing of a CVC Ion Exchanger. During this process, boric acid flow to the VCT decreased significantly, due to erratic behavior of the boric acid makeup header check valve (BAM-146). <br /><br /> The most probable cause of this event was the failure of BAM-146 to function properly. Unconservative decision making by Control Room personnel is considered a contributing factor. Corrective actions include replacing BAM-146 and increasing Operator awareness on reactivity management significance. <br /><br /> This event did not compromise the health and safety of the public and plant personnel in that no Technical Specification limits were exceeded and reactor power remained within the acceptable band. Two other boron dilution events have been reported as voluntary LER's by Waterford 3 this year, but neither was similar in cause. This report is being submitted as a voluntary LER.
3821994014 | Waterford 3 | 06/10/1994 | 11/23/1994 | 9411250214 | <strong>Hot Leg Injection Isolation Valve Circuit Breaker Left in the Open Position</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1994, Waterford 3 was in Mode 1 at 100% power when the circuit breaker for the Hot Leg 2 Injection Isolation Valve was discovered to be open. An investigation revealed that this circuit breaker had been opened eleven days earlier to comply with the Technical Specifications when the Hot Leg 2 Injection Flow Control Valve was declared inoperable due to a mispositioned valve stem anti-rotation device. When the flow control valve was declared operable, the circuit breaker for the isolation valve was inadvertently left in the open position. <br /><br /> The root cause of this event is personnel error. Procedure requires that an Equipment Out of Service Checklist be initiated unless restoration will occur prior to the end of the shift. The Control Room Supervisor (CRS) did not initiate this checklist prior to shift turnover. Corrective actions included counseling the CRS in accordance with the Improving Human Performance (IHP) Program and the on-shift Shift Supervisors have reviewed this event with their operating crews. This event did not compromise the health and safety of the public. This report is being submitted as a voluntary LER.
3821994015 | Waterford 3 | 09/16/1994 | 11/22/1994 | 9411250222 | <strong>Boric Acid Addition to Reactor Coolant System</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1994 at approximately 1640 hours, Waterford 3 was in Mode 1 at 100% power when an addition of boric acid was made directly to the Reactor Coolant system (RCS) instead of to the Volume Control Tank (VCT). This erroneous action was noted quickly and appropriate actions were taken to prevent exceeding Technical Specification (TS) limits on RCS Cold Leg Temperature. <br /><br /> The root cause of this event was personnel error due to a lack of self-checking to ensure intended actions were correct. A contributing cause was the non-continuous use of Chemical and Volume Control procedure OP-002-005. <br /><br /> Corrective action included counseling the Primary Nuclear Plant Operator (PNPO) in accordance with the Improving Human Performance (IHP) Program and temporarily assigning the responsible PNPO to an Off-Shift status. This event did not compromise the health and safety of the public. This report is being submitted as a Voluntary LER.
3821994016 | Waterford 3 | 07/21/1994 | 12/16/1994 | 9412220079 | <strong>Lube Oil Flow to Emergency Diesel Turbocharger Under Loss of Control Air</strong><br /><i>Abstract:&nbsp;</i>Waterford 3 was informed by Cooper Energy Services ('Cooper' or 'Cooper-Bessemer'), the vendor for the Emergency Diesel Generators (EDGs), that they could not locate documentation to prove that lube oil flow to a Cooper Model ET-18 turbocharger would be adequate upon loss of control air to assure that the turbocharger would survive a seven day run at full load. In response, Waterford 3 initiated a corrective action document, determined that the EDGs were operable, performed an engineering evaluation that confirmed the operability determination, and issued an Operations Standing Instruction to direct operator action to restore EDG control air pressure should it be lost. Additionally, the Cooper-Bessemer Owner's Group Technical Committee requested MPR Associates to perform test work on a Cooper Model ET-18 turbocharger. Test results indicate: (1) the Model ET-18 turbocharger can operate for at least seven days with a reduced oil-supply pressure, and (2) adequate time is available to take corrective action in the unlikely event control air is lost post-accident. This condition does not compromise the health and safety of the public. This is a Voluntary LER.
3821994017 | Waterford 3 | 11/22/1994 | 12/21/1994 | 9412280260 | <strong>Load Rejection Testing Requirements for Emergency Diesel Generators Not Met</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1994, Waterford 3 personnel discovered that the Technical Specification (TS) Surveillance Requirements of 4.8.1.1.2.d.1 had not been satisfied during previous refuel outage testing. These surveillance requirements demonstrate operability of the Emergency Diesel Generators (EDGs) by assuring the EDGs have the capability to reject the largest single emergency load without exceeding the specified output voltage and frequency constraints. Testing was performed during past refuel outages utilizing a load of approximately 230 Kilowatts (KW). The TS requires the rejected load to be at least 498 KW. The most probable root cause of this event is an inadequate procedure. The immediate corrective actions included the successful surveillance testing of the EDGs during the TS allowed 24 hour time interval. An alternate testing method will be investigated and TS 3/4.8.1 will be reviewed and revised as necessary. The discovery of this event was the result of a corrective action follow-up from LER-94-012-00. This event did not compromise the health and safety of the public.
3821994018 | Waterford 3 | 11/23/1994 | 12/28/1994 | 9501030142 | <strong>Liquid Radioactive Waste Released From Waste Condensate Tank 'A'</strong><br /><i>Abstract:&nbsp;</i>At approximately 0818 hours on November 28, 1994, liquid radioactive waste was released from Waste Condensate Tank 'A' with an incorrect and non-conservative permit release setpoint on the liquid waste Radiation Monitor. An investigation was initiated, and the investigation established on November 30, 1994, that the permit release setpoint was non-conservative. The actual release, based on the average monitor readings during the release period, was significantly less than and did not exceed the limits of 10CFR20, Appendix B, Table II. The root cause of this event was human error due to lack of self-check by the technician involved. The corrective actions include: counseling for appropriate personnel, training for HP count room technicians, changing the composite data input process, performing a QA independent audit of composite files and logs, the implementation of new computer software, and reviewing miscommunications with HP staff. The health and safety of the public were not compromised during this event.
3871994001 | Susquehanna 1, Susquehanna 2 | 01/02/1994 | 01/31/1994 | 9402070328 | <strong>Emergency Diesel Generator 'C' Unplanned Automatic Start</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1994, with Unit 1 in Condition 5 (Refueling) (O% power) and Unit 2 in Condition 1 (Run) (95% power) an unplanned start of the 'C' Emergency Diesel Generator (EDG) occurred during performance of surveillance testing. Following initial investigation, the 'C' EDG was shutdown. The test was then resumed and completed satisfactorily. This event was determined to be reportable per 10CFR50.73(a)(2)(iv) in that an unplanned Engineered Safety Feature actuation occurred when the 'C' EDG automatically started. There were no safety consequences or compromises to the public health or safety nor to plant personnel. This cause of this event was failure to perform procedural steps in the required order due to inadequate training for the person assisting the Test Director. We are evaluating the scope of training for those personnel who assist in the performance of testing activities. This training will be implemented for those personnel who assist in test performance in the future.
3871994002 | Susquehanna 1 | 01/22/1994 | 02/22/1994 | 9403040023 | <strong>Fire Watches Not Performed During Area Evacuation</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1994, with Unit 1 in Condition 1 at 20% power, an unexpected chemical reaction occurred while adding chemicals to the Reactor Building Closed Cooling Water System. This reaction caused irritating fumes in the area and resulted in evacuation of the affected elevation of the Reactor Building. The area was evacuated for approximately three and one half hours while recovery from the event was accomplished. During this time, hourly fire watches in place for inoperable fire barriers were not performed. The cause and corrective action for the chemical event are being addressed in a separate station operating occurrence report. The failure to perform required fire watches was due to evacuation of the affected area. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as an operation prohibited by Technical Specifications in that required fire watches for inoperable fire barriers were not performed while the affected area was evacuated. Once the affected area was declared safe for inhabiting, the hourly fire watches were resumed.
3871994003 | Susquehanna 1 | 02/01/1994 | 03/02/1994 | 9403110116 | <strong>Fire Barrier Penetration Not Sealed; Fire Watch Not Performed</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1994, with Unit 1 in Condition 1 at 100% power, an electrical penetration through a fire rated barrier was discovered which was not sealed as required. A Nonconformance Report was then generated. The Technical Specification LCO action statement was entered and the required fire watch was established. Investigation of the problem revealed that this same condition was identified during Appendix R walkdowns performed in 1988. The investigation further revealed that at that time the LCO action statement requiring establishment of a fire watch was not entered. The cause of this condition was an oversight by the responsible work group after this non-sealed penetration was initially discovered. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specification in that the required LCO action statement was not entered and the required fire watch was not performed. Upon discovery of the inoperable penetration on February 1, 1994, the required LCO action of establishing an hourly fire watch was taken. The penetration will be properly sealed per the applicable specification.
3871994004 | Susquehanna 1, Susquehanna 2 | 01/28/1994 | 03/17/1994 | 9403230317 | <strong>Fire Protection Damper Not Installed in Fire Rated Barrier</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1994, with Units 1 & 2 in Condition 1 at 100% power, it was discovered during a surveillance inspection that a fire protection damper was not installed in a fire rated barrier. On February 16, 1994, it was determined that an Engineering Study which was in progress at the time of discovery indicated that the damper is not required. However, this study is not yet approved; therefore, the damper is required to be installed and operable by the existing Fire Protection Program. The required Technical Specification LCO action of establishing an hourly fire watch was taken. The cause of this condition was an initial construction deficiency. The cause of failing to previously identify this condition was mistaking a different fire damper in the same duct for the missing damper. This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specification in that the required LCO action had not been taken for the damper which was not installed. Once the final determination as to the requirement for this damper is made, the appropriate action will be taken.
3871994005 | Susquehanna 1 | 03/08/1994 | 04/06/1994 | 9404110202 | <strong>Unit 1 Turbine Building SPING Alternate Sampling Became Disconnected</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1994, at 1335 hours with Unit 1 in Condition 1 at 100% power, it was determined that the alternate continuous sampling required by Technical Specification 3.3.7.11 action 112 for an out of service Unit 1 Turbine Building Sping was not being completed as required. The Unit 1 Turbine Building Sping was removed from service at 1015 hours on 3/8/94. At 1335 hours on 3/8/94, Chemistry personnel were performing required four hour flow checks of the alternate sampling and discovered the sample tubing from the SPING vent to the alternate pump suction disconnected. Technical Specification 3.3.7.11 action 112 was not being met from 1015 hours to 1335 hours when continuous alternate sampling was not performed. The cause of the event was that the sample tubing became disconnected from its fitting at the alternate sample pump. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. The Unit 1 Turbine Building Sping samples just prior to the event and immediately after were lower than the lower limit of detection. The condition did not create a degradation in the Station's ability to protect the health and safety of the public and /or plant personnel. The tubing was reattached to the alternate pump and subsequently secured with clamps. The action to prevent recurrence was to revise the applicable Chemistry procedure to require clamps on the tubing for this sampling method.
3871994006 | Susquehanna 1 | 03/08/1994 | 04/07/1994 | 9404120026 | <strong>Fire Protection Halon for Panel Inoperable with Panel Door Open</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1994, with Unit 1 operating at 100% power, a panel door for a panel protected by Halon fire suppression equipment was found open, thus rendering the Halon protection for the panel inoperable. The door was open to facilitate installation of temporary test equipment. The Technical Specification LCO action statement was entered until the temporary equipment was removed and the door was then closed. The cause of this event was determined to be lack of sufficient direction in the work package used to install the temporary equipment. This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications in that the required LCO action statement was not entered during the time from which the door was open until the condition was discovered. There were no safety consequences and minimal safety compromises as a result of this event. The temporary equipment was removed and the door was closed. The actions to prevent recurrence include the following: adding signs to the panel doors to identify the effects of leaving a door open, revising applicable training courses with respect to this subject, and revising the procedure on fire protection equipment status as to requirements for enclosures of Halon protected equipment.
3871994007 | Susquehanna 1, Susquehanna 2 | 03/28/1994 | 08/25/1994 | 9409060041 | <strong>Inoperable Fire Barrier - Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1994, with Unit 1 at 100% power, a fire rated wall was discovered to contain gaps where it meets the ceiling, rendering the barrier inoperable. The Technical Specification LCO action statement was entered and an hourly fire watch was established. This condition appears to have existed since initial construction. Failure to previously identify this condition was attributed to inadequate inspections. A causal factor was procedural weakness. This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by Technical Specification in that the LCO action statement had not been entered for inoperable fire barriers. There were no safety consequences as a result of this event. Work documents were generated to repair this condition and to inspect other areas with similar configuration. On July 26, 1994, the inspection was completed and three areas with similar conditions were noted. These additional areas will also be repaired. The surveillance procedure was revised to emphasize the requirement to inspect the wall to ceiling joint. This event will be reviewed with those personnel who perform these inspections with emphasis on this requirement.
3871994008 | Susquehanna 1, Susquehanna 2 | 03/31/1994 | 08/04/1995 | 9508080182 | <strong>Class 1E 125 VDC, 250 VDC and 480 VAC Load Centers Outside Dynamic Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1994, at 2250 hours with Unit 1 in Condition 1 at 100% power and Unit 2 in Condition 5 at 0% power, it was determined that breaker lifting devices mounted on all station class 1E 125 VDC, 250 VDC and 480 VAC load centers caused the load centers to be outside of their dynamic (seismic and hydrodynamic) qualification design basis. On 3/30/94, an Engineering Discrepancy Report (EDR) was generated to document the potential that the lifting devices may render the load centers unable to function as designed during a design basis seismic event. As a result of the above condition, the decision was made to remove the sliding assemblies and trolley portions of the devices while the operability analysis was in its final stages as a prudent measure. On 3/31/94 the operability assessment of the EDR was finalized and it determined that the load centers were outside their dynamic (seismic and hydrodynamic) qualification design basis. The results of the operability assessment also showed that the DC load centers were operable in their current configuration with the devices removed. The same assessment also concluded that the AC load centers were operable. The lifting devices were installed on the load centers during the original construction per design documents and not addressed in the dynamic analysis. Investigation into the causes for this oversight concluded that during the construction of Susquehanna SES our AE provided drawings that showed the lifting devices on the load centers to the vendor who performed the seismic qualification calculations. However, when the vendor provided the seismic qualification calculation to PP&L and our AE for review, the seismic qualification calculation did not contain the lifting devices as part of the load centers. No documentation could be found for not including the lifting devices as part of the load centers. The load centers have been evaluated and are now within their dynamic design basis. Actions to prevent recurrence included updating the applicable design drawings and installation and operating manuals for the load centers to show that the breaker lifting devices are not part of the load center's dynamic qualification. A review of other safety related equipment was performed to determine if they contained accessor equipment used only for maintenance purposes. No equipment of this type was identified.
3871994009 | Susquehanna 1, Susquehanna 2 | 06/07/1994 | 07/06/1994 | 9407110125 | <strong>Technical Specification Requirements For Time Response Testing Not Completed</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1994, at 1700 hours with Unit 1 in Condition 1 at 100% power and Unit 2 in Condition 4 at 0% power, it was determined that the Technical Specification surveillance test requirements for Section 4.3.2.3 were not being totally satisfied and is reportable per 10CFR50.73(a)(2)(i)(B), in that Units 1 and 2 had been in a condition prohibited by the Technical Specifications. A review of an 18 month Time Response Test of the Reactor Vessel Water Level and High Drywell Pressure switches showed that the test was not in compliance with the requirements of Technical Specification 4.3.2.3 to test the channels every 18 months. The Technical Specification surveillance requirement allows for testing 'redundant' channels every other refueling outage; however, Technical Specification 4.3.2.3 Table 3.3.2-1, trip functions 1.a.1 and 7.a. and trip functions 1.b and 7.e did not have 'redundant' channels and should have been tested every 18 months. The cause for this event was the applicable Time Response Testing surveillance procedures incorrectly interpreted the associated trip channels as 'redundant' within a trip system. Tested on an 18 month cycle, the additional time between tests did not negatively impact the applicable systems. The condition did not create a significant degradation in the Station's ability to protect the health and safety of the public and/or plant personnel. The applicable Time Response Test Procedures have subsequently been revised and reperformed. Additional Time Response Tests that utilize the 'redundant' channel allowance have been reviewed and were found to be satisfactory.
3871994010 | Susquehanna 1, Susquehanna 2 | 05/13/1994 | 07/05/1994 | 9407130102 | <strong>Access Hatch Between Fire Zones Not Fire Rated As Required</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1994, with Unit 1 at 100% power and Unit 2 in Refueling, an inspection was being performed in preparation for repairing damaged penetration seals. During this inspection, it was noted that an access hatch in the ceiling of the upper relay rooms (Unit 1 & 2) was not a fire rated door/assembly. The ceilings are fire rated barriers separating different fire zones. An Engineering Deficiency Report was generated and the fire barrier was determined to be inoperable. An hourly fire watch was established and the system status file was updated. The cause of this condition was an initial construction deficiency. This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications in that the required Limiting Condition for Operation Action Statement had not been entered for an inoperable fire rated assembly. There were no safety consequences as a result of this condition and safety compromises were minimal. The subject hatches will be upgraded by addition of fire retardant material to achieve the required fire rating. Until this activity is complete, the fire watches will remain in effect.
3871994011 | Susquehanna 1 | 07/07/1994 | 08/04/1994 | 9408090475 | <strong>RWCU Containment Isolation Valves Isolated on High Differential Flow</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1994, at 0947 hours with Unit 1 in Condition 1 at 100% power, an Engineered Safety Feature (ESF) actuation occurred when the Reactor Water Cleanup (RWCU) System's containment isolation valves automatically closed due to a high differential flow signal. The high differential flow signal was attributed to leakage past a work boundary valve (air operated - failed closed) and then out of system drains. The leakage was subsequently collected in the Reactor Building floor drain system. The leakage into the isolated section of the RWCU system and out of the drain valves was sufficient to isolate the entire system on high differential flow. Upon discovery of the condition, Operations closed the affected drain valves and leakage from the system was stopped. The RWCU was subsequently returned to service. There was no significant loss of coolant inventory nor was there any damage or degradation of the RWCU system during the event. There were no safety consequences or compromise to the public health or safety as a result of this event. The RWCU containment isolation valves performed as expected during the event. Corrective actions include changing the applicable procedure to show that involved valves should not be used as work boundaries and to review the acceptability of other station air operated - fail closed valves as a work boundary.
3871994012 | Susquehanna 1, Susquehanna 2 | 08/02/1994 | 08/03/1995 | 9508080111 | <strong>Loss of Fire Detection/Suppression - Condition Prohibited By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1994, at 2131 hours, with Units 1 & 2 at 100% power, the Fire Protection Simplex System was disabled by an electrical impulse from an apparent lightning strike on site. The Technical Specification action statements were entered and compensatory measures were begun. Between the time of this event and 0730 on 8/3/94, only hourly fire watches were established, contrary to the required continuous fire watches within one hour. Between the hours of 0230 and 1210 identification of fire zones requiring continuous fire watches was completed and manning of the zones was in progress. At 1145 hours, the system was repaired and returned to service and at 1250 hours the fire watches were discontinued. The causes of failing to comply with Technical Specifications were: 1) Difficulty in determining required firewatch coverage and obtaining the large number of personnel required, 2) Inadequate corrective actions from previous Simplex System Events, and 3) Communication problems during assessment of this event. The details of why previous corrective actions were inadequate are described in this report. The event was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications in that the required LCO action was not taken within the required action time. There were no safety consequences as a result of this event and safety compromises were minimal as described. Corrective actions included: 1) Development of a comprehensive instruction to assist in timely evaluation and response for this type event, 2) Training of Operations personnel on this event and the new instruction, 3) Emphasis on Technical Specifications compliance and a review of expected communications practices provided to Nuclear Department personnel, 4) Review of the Simplex System design for operational enhancements.
3871994013 | Susquehanna 1 | 08/25/1994 | 09/21/1994 | 9409270221 | <strong>Unplanned Closure of HPCI Steam Isolation Valve (ESF); HPCI Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0823 hours on August 25, 1994, with Unit 1 in Condition 1 (Power Operation) at 100% power, the Unit 1 High Pressure Coolant Injection (HPCI) system steam supply outboard isolation valve unexpectedly closed during the performance of Residual Heat Removal (RHR) equipment area temperature instrument calibrations. This constituted an unplanned Engineered Safety Feature actuation, reportable per 10CFR50.73(a)(2)(iv). Closure of the isolation valve also rendered the HPCI system inoperable, which is reportable per 10CFR50.73(a)(2)(v)(D) as a condition that alone could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. Since one loop of RHR ('B' Pump) had already been declared inoperable for performance of the instrument calibrations, this condition was not bounded by the provisions of Technical Specification LCO 3.5.1, necessitating the entry into LCO 3.0.3. Entry into LCO 3.0.3 is reportable as a condition prohibited by the plant's Technical Specifications per 10CFR50.73(a)(2)(i)(B). The cause of this event was personnel error in that a multimeter was placed across incorrect terminals resulting in shunting of trip contacts and closure of the isolation valve. The HPCI system was restored to normal standby alignment. The involved I&C personnel were counseled on the importance of self-checking and the event will be reviewed with all I&C personnel to emphasize the importance of remaining attentive during repetitive tasks.
3871994014 | Susquehanna 1, Susquehanna 2 | 08/18/1994 | 09/19/1994 | 9409270327 | <strong>Loss of Fire Detection / Suppression - Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1994 with Units 1 and 2 at 100% power, an apparent electrical surge from a lightning strike in the area of this site disabled the 'A' panel of the Fire Protection Simplex System. Operations personnel (utility, licensed) tried unsuccessfully to transfer panels. This was unsuccessful since the transfer switch was placed in the over-travel position. The Technical Specification action statements were entered. Instrument and Controls personnel (utility, non-licensed) discovered the problem with the transfer switch and returned the Simplex System to operation. Before the system was restored, most of the compensatory fire watches were in place. The cause of the inability to properly transfer panels was switch design and labeling. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications in that the required action of establishing a continuous fire watch within one hour was not accomplished for all affected areas. There were no safety consequences as a result of this event. The applicable procedures will be enhanced to include instruction of re-setting and re-start of the system. The transfer switch was re-labeled to clearly mark positions. The transfer switch will be evaluated for improvement via change in switch design or addition of mechanical stops at the required positions.
3871994015 | Susquehanna 1, Susquehanna 2 | 09/12/1994 | 05/20/1996 | 9605280078 | <strong>Postulated Failures of SGTS Components are Outside of Design Basis</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1994, at 1640 hours with Unit 1 and Unit 2 in Condition 1 at 100% power, it was concluded that either of two postulated single failure event types in conjunction with a design basis Loss Of Coolant Accident (LOCA) could cause the plant to be outside of its design basis. The postulated single failure event types are associated with the Standby Gas Treatment System and the Reactor Building recirculation system.<br /><br /> The first event type would result in either the Division I or Division II outside air supply damper of the SGTS being in the open position during a 'draw-down' of secondary containment. This would result in doses that are within the 10 CFR 100 and 10 CFR 50 G.D.C. 19 limits but exceed the design limits described in the station's Final Safety Analysis Report. The second postulated event type involves either Reactor Building recirculation fan damper being in the open position while its respective recirculation fan is not operating. The probabilities of these events are low and must be in existence at the time of a design basis accident in order to exceed the design basis doses. In January, 1995, the postulated failure of the Reactor Building recirculation system damper was determined to be non-credible. In March, 1996, the postulated SGTS single failures were dispositioned by a modification. Separate from this report, PP&L is continuing to pursue whether or not the SGTS single failures should have been included in the original plant design basis. This action is being tracked in our corrective action program.
3871994016 | Susquehanna 1, Susquehanna 2 | 09/25/1994 | 10/24/1994 | 9410310163 | <strong>Loss of Fire Detection/Suppression-Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1994, at 1650 hours, with Units 1 & 2 at 100% power, one channel of the Fire Protection Simplex System failed when a transponder card failed. The channel was declared inoperable and the appropriate Technical Specifications were entered. At 1840 hours, all required compensatory fire watches were in place. The failed card was an installed spare and was removed from the system. The Simplex System was restored at 2325 hours, the LCO's were cleared, and the fire watches were discontinued. The cause of the Simplex failure was a ground in the CPU chip of a system transponder card. The cause of failing to post all required fire watches within one hour was misleading wording in the Operating Instruction for response to Simplex System failures. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibitied by Technical Specifications in that the required action of establishing continuous fire watches was not accomplished within one hour as required. There were no safety consequences as a result of this event. The Operating Instruction was revised to clarify compensatory actions for loss of a channel of Simplex. The Simplex System will be modified to remove spare transponder cards, since their failure can cause loss of the system.
3871994017 | Susquehanna 1 | 11/30/1994 | 12/29/1994 | 9501050100 | <strong>Feedwater Transient Resulting in Power Excursion</strong><br /><i>Abstract:&nbsp;</i>At 2030 hours on November 30, 1994, with Unit 1 operating at 100% power, a feedwater transient occurred, resulting in a power excursion in excess of 102% for approximately twenty-one (21) seconds with a maximum power level of approximately 104% reached. All major equipment operated per design during the transient, and no abnormal operator actions were required to place the unit in a stable condition. The feedwater transient was caused by a short circuit through a DC arc suppressor. This short blew fuses which power B feedwater flow instruments. The feedwater control system responded as expected upon loss of B feed low signal. The DC arc suppressor shorted because it's heat sink was loose and could not dissipate heat. Investigation into the design revealed that an improved DC arc suppressor for this circuit was installed on Unit 2. This event was determined to be reportable pursuant to NRC Document SSINS #0200, 'Discussion of Licensed Power Level' (AITS.F14580HZ) dated August 22, 1980. This document states that there is no allowance for power excursions reaching levels in excess of 102% power. Review of data identified that the average core thermal power during the eight hour shift was approximately 3290 MWth, which is less than the rated core thermal power of 3293 MWth. Review of the data from the event also indicated that the core response for this event was within the expected envelope of responses. The transient was within the bounds of the Feedwater Controller Failure - Maximum Demand analysis presented in the Decrease in Reactor Coolant Temperature accident of Chapter 15 in the SAR.
3881994001 | Susquehanna 2, Susquehanna 1 | 01/03/1994 | 01/31/1994 | 9402180105 | <strong>Condition Prohibited By Plant's Technical Specifications (LCO ACTION 3.0.3)</strong><br /><i>Abstract:&nbsp;</i>At 0115 hours on January 3, 1994, with Unit 2 in Condition 1 at 98% power, 18 month surveillance test SE-124-207, '18 Month Emergency Diesel Generators (EDG) B and D Auto Start and ESS Buses 1B and 1D Energization on Loss of Offsite Power With a LOCA - Plant Shutdown' was being performed on Unit 1, which was in Condition 5 at 0% power. As part of this test, the undervoltage start signals from the 1B and 1D ESS Buses to the B and D EDGs are disabled. With the undervoltage circuits (degraded voltage protection) disabled, ESS Buses 1B and 1D (2 load groups) are considered not energized per Technical Specification 3.8.3. Since Unit 2 Technical Specification 3.8.3.1 requires that the Unit 1 load groups remain energized for common A.C. distribution system loads and only contains provisions for one (1) load group being not energized, entry into LCO ACTION 3.0.3 on Unit 2 was required. The surveillance test was successfully completed on Unit 1 and LCO ACTION 3.0.3 was exited on Unit 2 at 0217 hours on January 3, 1994. PP&L is performing reviews to determine if entry into LCO ACTION 3.0.3 was necessary and, if so, whether procedural testing methods can be revised and/or the Technical Specifications can be amended to eliminate the need for entry into LCO ACTION 3.0.3 for conducting this testing.
3881994002 | Susquehanna 2 | 01/20/1994 | 02/22/1994 | 9403040148 | <strong>Reactor Scram Following Turbine Trip on Loss of Generator Stator Cooling</strong><br /><i>Abstract:&nbsp;</i>At 0150 hours on January 20, 1994, with Unit 2 in Condition 1 at 100% power, a reactor scram occurred, per design, when the Main Turbine tripped due to a loss of main generator stator cooling. Reactor water level dropped to + 2 inches. Reactor Level 3 isolations occurred per design. Reactor pressure peaked at 1083 psig, momentarily cycling Safety Relief Valves A, B, C, D, H, R and S. All Primary Containment parameters remained normal throughout the event. The loss of generator stator cooling was caused by failure of mechanical linkage in a controller for a temperature control valve on the stator cooling water system. Failure of the controller resulted in the temperature control valve closing, resulting in loss of cooling water flow to the generator stator. The plant was safely shutdown and there were no safety consequences or compromise to public health or safety during this event, nor would there have been under different initial operating conditions. This transient is within the bounds of a turbine trip as analyzed in Chapter 15 of the FSAR. The controller was repaired and the unit was returned to operation. Investigations into longer term actions to prevent recurrence are in progress.
3881994003 | Susquehanna 2 | 01/21/1994 | 07/25/1994 | 9408010252 | <strong>Operation Prohibited By Technical Specification 3.0.4</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1994, at 0605 hours with Unit 2 starting up in Condition 2 at 0% power, the acoustic monitor for the 'S' MSRV was declared inoperable and Technical Specification 3.3.7.5 action 80b and 3.4.2 action c were entered. Repair of the monitor required a primary containment entry and due to weather related emergency circumstances, a discretionary enforcement from the applicable Technical Specifications was granted. Startup of Unit 2 then continued. Even though NRC permission was granted, this event is reportable per 10CFR50.73(a)(2)(i)(B), in that Susquehanna Unit 2 was in a condition prohibited by the Technical Specifications when Unit 2 entered condition 1 while the acoustic monitor was inoperable. The cause of the acoustic monitor failure was determined to be a faulty charge converter. Operation of Unit 2 with the 'S' MSRV acoustic monitor inoperable did not create a significant degradation in the Station's ability to protect the health and safety of the public and/or plant personnel. The monitor provides valve position indication only. There are alternate indications and symptoms discernible by control room personnel for determining MSRV position.
3881994004 | Susquehanna 2 | 03/07/1994 | 04/06/1994 | 9404110166 | <strong>HPCI Inoperable Due to Broken Connection at Level Switch</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1994 at 1630 hours with Unit 2 in Condition 1 at 100% power, a monthly surveillance test was being performed on a level switch which provides the signal to transfer the suction supply of the High Pressure Coolant Injection (HPCI) system from the Condensate Storage Tank (CST) to the Suppression Pool on low CST level. Upon loosening a states link screw in the instrument circuit, for performance of the test, the screw broke. Since this rendered the circuit for the level switch inoperable, the HPCI system was declared inoperable. Declaring HPCI inoperable is reportable per 10CFR50.73(a)(2)(v)(D) as a condition that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. However, HPCI did remain functional with its suction source as the CST and the capability existed to manually transfer the suction source to the Suppression pool, if needed. It is believed that corrosion on the states link screw threads was the most probable cause for the screw failure. This failure was considered to be an isolated event in that corrosion has not been observed on similar circuits for Unit 1 HPCI or Unit 1 and Unit 2 Reactor Core Isolation Cooling Systems. The states link and its terminal box were replaced and the system was restored to operable status.
3881994005 | Susquehanna 2 | 03/14/1994 | 07/20/1995 | 9507240345 | <strong>Technical Specification Required Shutdown Due to Check Valve Surveillance Failure</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1994, with Unit 2 at 99% power, a reactor instrumentation line excess flow check valve failed its' surveillance test when it would not seat. The applicable Technical Specification action statement requires isolating the affected instrument line; which in turn rendered the associated instrument (#7 jet pump flow) inoperable. The action statement for the inoperable jet pump flow instrument requires being in at least Hot Shutdown within 12 hours. The shutdown was completed approximately 8 hours after entering the action statement. This condition was determined to be reportable per 10CFR50.73(a)(2)(i)(A) in that a Technical Specification required shutdown was completed. There were no safety consequences as a result of this event. The defective valve was replaced. Inspection and evaluation of the failed check valve was unable to determine the exact cause of the failure.
3881994006 | Susquehanna 2, Susquehanna 1 | 04/13/1994 | 05/10/1994 | 9405130165 | <strong>Condition Prohibited By Technical Specifications - Fire Rated Elevator Doors Not Surveilled</strong><br /><i>Abstract:&nbsp;</i>During 1993, PP&L initiated two engineering studies as part of our fire protection drawing upgrade project. On April 13, 1994, two discrepancies identified by these studies were determined to be reportable. The elevator doors in the control structure and a floor in a room on 749' elevation of the Unit 2 Reactor Building were determined to require inspection per the Technical Specification surveillance requirement but were not included in the surveillance procedures. The cause of these conditions was oversight during initial procedure preparation and during preparation and review of the Fire Protection Review Report. The condition was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications in that the required Limiting Condition for Operation action statement had not been entered for fire barriers which had not had their surveillance requirements met. These were no safety consequences as a result of this condition. The subject barriers were inspected per the surveillance requirement and are being added to the applicable surveillance procedures. The applicable drawings and door schedules will be updated to denote the fire protection criteria.
3881994007 | Susquehanna 2 | 05/07/1994 | 06/03/1994 | 9406130075 | <strong>Fuel Loaded in Reactor Core Quadrant With Inoperable Source Range Monitor</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1994, during refueling of Unit 2, it was determined that fuel had been loaded into a core quadrant whose Source Range Monitor (SRM) instrument was inoperable. The SRM inoperability was due to miscalculating the signal-to-noise ratio during the shiftly channel check surveillance. Core reloading was terminated and a formal investigation was begun. There were several causes for this event including: SRM detector failure, cognitive error in decimal placement during signal- to-noise ratio calculation, human factors in display format for SRM indication and lack of specifying which indicator to use for data acquisition in the procedures. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B) as an operation prohibited by Technical Specifications in that fuel was loaded into a core quadrant whose SRM was inoperable. There were no safety consequences as a result of this event. The following actions were completed prior to re-commencing fuel load: the SRM detector was replaced and its cable connector reworked, the event was reviewed with Operations personnel, and the procedures were changed to indicate which SRM indications are to be used for recording data. The following additional actions will be taken: Evaluate human factors design of SRM indication format, evaluate methods to assure detector cable connectors installations/ repairs are accomplished in accordance with vendor instructions, and revise weekly functional test to provide specific criteria for allowable deviations between channels.
3881994008 | Susquehanna 2 | 05/25/1994 | 06/24/1994 | 9406290027 | <strong>Emergency Switchgear Room Cooling Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1994, at 1100 hours with Unit 2 in Condition 5 at 0% power, both Emergency Switchgear Room Cooling subsystems were conservatively declared inoperable and was determined to be reportable per 10CFR50.73(a)(2)(v)(D). While performing a scheduled Loss Of Offsite Power surveillance test of the Unit 2 'A' 4.16 KV bus, the 'A' Emergency Switchgear Room Cooling subsystem failed to restart as required. Investigation of the condition discovered that a false 'motor high temperature' signal was received by the 'A' DX Unit upon restoration of power following the simulated LOOP and that prevented the subsystem from reliability operating as designed. The condition was found to occur intermittently and was due to a 'relay race' within the DX Unit control circuitry. The identical configuration was found in the 'B' DX Unit control circuitry also and both Emergency Switchgear Room Cooling subsystems were declared inoperable. This condition rarely occurs and only occurs randomly depending upon the results of the 'relay race' when power is restored to the DX Unit Control Panel. The exact cause of the 'relay race' is not definitively known since the logic was the original design. However, the difference in pick-up and drop-out times of the involved relays are on the order of milliseconds and any slight variation could have caused the condition. The condition did not create a significant degradation in the Station's ability to protect the health and safety of the public and/or plant personnel. A manual reset and start of the subsystems would have been possible to restore Switchgear Room Cooling. The DX Unit control circuitry was modified and successfully tested to correct the condition.
3881994009 | Susquehanna 2 | 10/24/1994 | 11/23/1994 | 9412020142 | <strong>Unplanned ESF Actuations Due To Fault On ESS 480 Volt Bus</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1994 at approximately 0520 hours, with Unit 2 in Condition 1 (Power Operation) at 100% power, Engineered Safeguard System (ESS) 480 Volt Motor Control Center (MCC) 2B236 tripped as a result of a seismic restraint clip failing in to the bus work and causing a phase-to-phase fault. This resulted in unplanned Engineered Safety Feature actuations when containment isolation valves for Reactor Building Chilled Water automatically closed. Drywell Temperature increased to a maximum of 149.85 degrees F and Drywell Pressure increased to a maximum of 0.95 psig. All equipment functioned per design in response to the event. The causes of the event were attributed to failure by work group personnel to capture and communicate prior experience, installation of a shorter than required seismic restraint clip screw and seismic restraint clip design (i.e., not a captive design and made of conductive material). The MCC was inspected and restored. Followup actions include repairing the bus during the next refueling outage, inspecting all 'Q' MCCs for proper clip screw size, reviewing and revising, as appropriate, all related procedures and training modules to address seismic clip requirements, conducting training on this event for maintenance personnel and reviewing seismic clip design with respect to captive design, material composition and seismic requirement issues.
3891994001 | St. Lucie 2 | 02/17/1994 | 02/24/1994 | 9403040267 | <strong>Pressurizer Auxiliary Spray Out of Service caused by a Mispositioned Isolation Valve due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>At 0030 on February 17, 1994, Unit 2 was in mode 5 at the beginning of a refueling outage. Operations was attempting to collapse the pressurizer steam space bubble. When the use of Auxiliary Spray was attempted the utility licensed operators noted that Pressurizer pressure was not decreasing as expected. During a subsequent valve lineup verification process a utility non-licensed operator found the Auxiliary Spray isolation valve V2483 to be mispositioned and locked closed. Valve V2483 is a manually operated 2 inch gate valve which is normally in the locked open position. The non-licensed operator was instructed to place valve V2483 in the locked open position. At this point the Auxiliary Spray system functioned as anticipated. <br /><br /> The root cause of the valve mispositioning was due to cognitive personnel error by utility non-licensed operators.<br /><br /> Corrective actions include: the valve was correctly realigned; all applicable plant records involving this valve were reviewed; the Final Safety Analysis Report was reviewed to determine that there was no safety significance for the absence of Auxiliary Spray; the non-licensed operators involved were counseled and appropriate disciplinary actions are being taken in accordance with current corporate policy; the position of accessible Unit 1 locked valves have been verified to be correct, Unit 1 inaccessible locked valves will be verified at the next opportunity, all Unit 2 locked valves are being verified; the corporate disciplinary policy on procedural noncompliance will be revised to specifically include more severe disciplinary actions for valve mispositionings, and a Human Performance Enhancement System evaluation was performed. <br /><br /> This Licensee Event Report is being submitted voluntarily. Auxiliary Spray is not required in any Technical Specification LCO, and alternative methods are available for depressurization of the Reactor Coolant System.
3891994002 | St. Lucie 2 | 03/16/1994 | 04/11/1994 | 9404180036 | <strong>Pressurizer instrument nozzle weld cracking due to fabrication defects.</strong><br /><i>Abstract:&nbsp;</i>On 16 March, 1994 Unit 2 was in mode 6 during a refueling outage. FPL Engineering personnel identified trace amounts of boric acid on the exterior of the Pressurizer steam space C instrument nozzle during an inspection. Subsequently, Quality Control (QC) personnel performed interior dye penetrant examination and identified unacceptable indications at the A, B and C steam space instrument nozzle welds. The D instrument nozzle weld was acceptable. The unacceptable weld indications were in the 'J' weld between the alloy 690 nozzle and the clad on the inside of the Pressurizer.<br /><br /> The probable root causes of the condition include: 1) Usage of the Shielded Metal Arc welding process and I-182 filler material which is susceptible to Primary Water Stress Corrosion Cracking. 2) High residual stresses due to multiple nozzle rework and replacements performed in 1987 and 1993. 3) Less than optimum conditions for the welding process during interior Pressurizer repairs performed in 1993. Adverse conditions increased the likelihood of slag inclusions and lack of weld fusion. <br /><br /> The corrective actions: 1) FPL Engineering performed a root cause analysis on the condition. 2) A more suitable weld material will be used in repairing the steam space nozzles prior to unit restart. 3) The nozzle repair method will relocate the welds to the exterior of the pressurizer and away from the high residual stress zones. 4) An automated welding machine will be used in the repair efforts. 5) Mechanical Maintenance will coordinate the inspections and repair efforts performed by a contractor with experience in this technique.
3891994003 | St. Lucie 2 | 04/23/1994 | 05/12/1994 | 9405180193 | <strong>Automatic Reactor Trip During Functional Testing of the Reactor Protective System Due to Bypass Circuit Miswiring During Original Construction</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1994 Unit 2 was at 29% reactor power, following a refueling outage. Instrumentation and Control Maintenance (ICM) was performing Linear Power Range Safety and Control Channel Monthly Calibration procedure number 2-1220052 on Reactor Protective System (RPS) channel B, which required the channel to be in bypass. RPS channel D High Power, High Rate of Change of Power (HRCP), Thermal Margin/Low Pressure (TM/LP), Loss of Load and Local Power Density (LPD) bistables were in trip per the Technical Specifications as the Linear Power Range Nuclear Instrumentation card had failed its monthly calibration. Upon commencing channel B calibration the coincidence logic of 2/4 was satisfied and the reactor tripped at 1318. The utility licensed operators carried out Emergency Operating Procedure-01, Standard Post Trip Actions, and Emergency Operating Procedure-02, Reactor Trip Recovery. The plant was stabilized in mode 3, Hot Standby.<br /><br /> The root cause of the reactor trip was an improperly wired bypass circuit on the RPS channel B Local Power Density bistable. With RPS channel D High Power, High Rate, TM/LP, Loss of Load and LPD bistables in trip and channel B bistables in bypass a trip should not have occurred. Testing by Instrumentation and Control Maintenance (ICM) after the trip indicated that the channel B LPD bypass circuit did not function. The reason was due to a wiring error from the original fabrication. The wiring error did not impact the normal RPS safety function, however ft did prevent the LPD trip unit in channel B from being bypassed. <br /><br /> Corrective actions for this event: 1) ICM repaired RPS channel B LPD bypass circuit, 2) ICM tested all Unit 2 RPS channel bypass circuits satisfactorily and Unit 1 RPS channel bypass circuits will be tested during the next Unit 1 refueling outage, 3) ICM completed calibration of RPS channel B and channel D Linear Power Nuclear Instrumentation and 4) The RPS vendor has been notified of the wiring error in the bypass circuit.
3891994004 | St. Lucie 2 | 06/28/1994 | 07/08/1994 | 9407180003 | <strong>Plant Vent Wide Range Gas Monitor Out of Service due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 6/28/94 at 0800, with Unit 2 at 100% power, utility Instrumentation and Control Maintenance (ICM) personnel began calibration of the Plant Vent Wide Range Gas Monitor (WRGM) flow meters and discovered that the low and high range sample lines were disconnected. calibration procedure was completed. The Plant Vent WRGM was placed back in service at 2115 on 6/28/94. After extensive data review, it was determined that the WRGM had apparently been out of service since Unit 2 entered mode 4, Hot Shutdown, on 4/13/94. <br /><br /> The root cause of this event is personnel error. ICM technicians, who last performed the calibration of the WRGM flow meters on 4/6/94, apparently did not reconnect the low and high range sample lines per the calibration procedure. This error was undetected since the WRGM normally indicates background radiation levels. In addition, disconnecting the sample inlet would cause the WRGM to take atmospheric samples and not change its normal indicated output. Functional test results of the monitoring circuitry would not detect the abnormal condition. <br /><br /> Corrective Actions include: 1) The Plant Vent WRGM was placed back in service. 2) Utility chemistry personnel checked all other process radiation monitors, on both units, to ensure all sample lines were properly connected. 3) ICM added a restoration signoff and an Independent Verification check to the existing restoration steps of ICM procedures to ensure that the radiation monitor low and high range sample lines are reconnected. 4) Operations has revised OP 1 & 2-0530021, Controlled Gaseous Batch Release to Atmosphere, to include a channel check of plant vent radiation monitor channels during all planned releases. 5) ICM and Chemistry will review other monitoring instrumentation work control processes, on both units, for procedural enhancements where restoration steps for disconnected equipment are necessary.
3891994005 | St. Lucie 2 | 07/08/1994 | 07/29/1994 | 9408100270 | <strong>Technical Specification 3.0.3 entered when Emergency Core Cooling Systems Limiting Condition for Operation was not met due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On 7/8/94 Unit 2 was at 100% power in mode 1. Due to simultaneously having the 2A Low Pressure Safety Injection (LPSI) pump and 2B Charging pump out of service, Technical Specification 3.0.3 was entered at 0820. The Nuclear Plant Supervisor had identified that the condition of the Emergency Core Cooling System (ECCS) was in violation of Technical Specification 3.5.2 'ECCS Subsystems with Tavg greater than or equal to 325 Fahrenheit.' Operations expeditiously restored the 2A LPSI System at 0849 and exited Technical Specification 3.0.3. <br /><br /> The root cause of the event was cognitive personnel error by a utility-licensed operator in that all opposite train ECCS equipment was not verified operable prior to removing the 2A LPSI System from service. <br /><br /> Corrective Actions for this event include: 1. The 2A LPSI pump and the 2B Charging pump were returned to service. 2. Operations has revised the format of the Equipment Out of Service Log for both units to enhance the awareness for minimum equipment required to be in service. 3. The Operations Department supervisor issued a Night order to all licensed operators on the need to perform a thorough review of Technical Specifications and the Out of Service Equipment Log prior to taking safety-related equipment out of service. 4. A further process change to address equipment clearances will require a signoff for the ANPS to verify opposite train equipment availability immediately prior to issuance of a clearance. 5. During the 1994 Licensed Operator Requalification training program, the Training Department will review this event with all utility licensed operators and shift technical advisors.
3891994006 | St. Lucie 2 | 07/14/1994 | 09/13/1994 | 9409210247 | <strong>Trip Circuit Breaker Failure due to a Broken Piece of Phenolic Block Lodged in the Trip Latch Mechanism Results in a Technical Specification Required Shutdown.</strong><br /><i>Abstract:&nbsp;</i>On 7/14/94, Unit 2 utility licensed Reactor Operators commenced the Reactor Protective System periodic logic matrix test. While testing the fourth logic matrix (AC matrix), of the Reactor Trip Circuit Breaker (TCB) Five failed to open. TCB-5 had opened three times previously on demand from other matrix tests. Following several attempts to open TCB-5, it was declared out of service. The reactor was shut down to repair or replace TCB-5. <br /><br /> The cause of the failure of TCB-5 to trip has been identified as obstruction of motion on the trip latch lever due to a broken piece of insulating material. A small piece of broken phenolic insulating material approximately 1/4 inch square in size was found lodged between the trip latch lever and the access slot in the base for the trip latch. <br /><br /> The phenolic fragment was found to have originated from the cutoff switch used in the breaker anti-pump circuitry, which is physically located directly above the trip latch mechanism. Upon further inspection, it was determined that a screw used in the assembly of the cutoff switch had become loose. This screw holds the switch to the mounting block and if loose will allow the two halves of the switch to separate when the breaker is operated. This most likely led to switch misalignment and breakage of the phenolic block. <br /><br /> Corrective Actions include: 1) Electrical Maintenance (EM), FPL Engineering and a GE representative inspected the remaining Unit 2 TCBs and the MG Set Output Breakers with satisfactory results. 2) EM will inspect Unit 1 TCBs during the next scheduled quarterly maintenance and the MG Set Output Breakers during the next scheduled periodic maintenance. 3) EM has incorporated the inspection of the cutoff switch phenolic block and screw into Unit 1 & 2 periodic maintenance procedures.
3951994001 | Summer 1 | 01/13/1994 | 02/11/1994 | 9402280112 | <strong>Outside Design Basis For Appendix R Analysis</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted pursuant to requirements of 10 CFR50.73 and satisfies the requirements of 10 CFR 21.2(c). On January 13, 1994, at approximately 1550 hours, a condition was identified for the Appendix R analysis where the plant has been determined to be outside the design basis due to analysis for circuits that may be susceptible to 'hot shorts.' A modification was made which installed solenoid operated isolation valves in the chill water supply to the lube oil coolers associated with the charging/safety injection (C/SI) pumps. During the review of a modification to replace the now installed valves, it was identified that thirteen circuits associated with the original installation are routed in fire zones which are 'prohibited' for the associated piece of equipment. <br /><br /> Immediate corrective action taken included establishing hourly fire watch patrols in the affected zones, control power leads to the valve associated with the C/SI pump to be maintained in operation were lifted to preclude closure due to a hot short, and notification was made as required by 10CFR50.72(b)(1)(ii)(B). Additional corrective action will be the revision of the Fire Emergency Procedures to include action to 'fail open' the chill water isolation valves for fires in the affected zones. This action will return the plant to within the Appendix R analysis requirements and will be completed by March 1, 1994.
3951994002 | Summer 1 | 01/28/1994 | 02/25/1994 | 9403080013 | <strong>Outside Design Basis Pressure For Charging/Safety Injection System</strong><br /><i>Abstract:&nbsp;</i>Engineering review of a runout test for the Charging/Safety Injection pumps identified a condition which was outside the design basis for the plant. Actual operating pressures were found to exceed the ASME design pressure of 2735 psig, as provided by the plant's Architect Engineer. During system operation, the plant has observed discharge pressures of 2740-2750 psig on the "A" pump and 2775-2800 psig on the "B" pump. <br /><br /> This event resulted from personnel error in failing to reconcile differences between actual pressure conditions and design documents. Source document review determined that while a non-conforming condition did exist, there was no impact on the ability of the system to perform its function. Component operation and system function are not impaired with normal operating pressures of to 2900 psig. <br /><br /> Operation and Surveillance procedures have been revised to limit the system normal operating pressure to normal operating pressures for other safety-related systems to confirm that this error was an isolated event. Additional actions will involve (1) an Engineering personnel review of this event and its consequences by April 15, 1994, (2) evaluation of safety-related systems to reconcile any design documentation discrepancies within existing programmatic controls by September 2, 1994, and (3) modify all design documentation for the Charging/Safety Injection System by December 31, 1994.
3951994003 | Summer 1 | 02/09/1994 | 03/11/1994 | 9403280195 | <strong>Level Switches for Fuel Oil Day Tank Level Not Seismically Qualified</strong><br /><i>Abstract:&nbsp;</i>This report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(ii)(B) and 10CFR21.2(c). At 1718 hours, February 9, 1994, a condition was identified for the Emergency Diesel Generators (EDGs) where seismic qualification could not be verified for the level switches providing automatic control of the fuel oil day tank level. The subject switches were manufactured by MAGNETROL,INC.(EIIS-MO40) model A-103F-MPG-TDM-S1M3DC-S1M3DC. The EDGs are supplied by Colt-Pielstick (Coltec Industries/EIIS-C470) and the day tank and associated level switches were provided as seismically qualified components. One hour notification as required by 10CFR50.72(b)(1)(ii)(B) was made at 1759 hours, February 9, 1994. A Station Order (SO 94-04) was immediately issued directing that an operator be dispatched should a seismic event occur and take manual control of the fuel transfer pump. The switch associated with 'A' EDG was replaced February 11 and the switch associated with 'B' EDG was replaced February 13, 1994, with seismically qualified components.
3951994006 | Summer 1 | 12/05/1994 | 01/03/1995 | 9501110520 | <strong>Reactor Coolant System Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1994, at 1530, a pressure boundary leak in the reactor coolant system was identified, resulting in a controlled shutdown of the plant, in accordance with Technical Specifications Section 3.4.6.2, 'Operational Leakage'. A Notification of Unusual Event was declared at 1531 due to pressure boundary leakage. On December 6, 1994, at 0514 cold shutdown (Mode 5) was established satisfying the action requirements of Technical Specifications. The Notification of Unusual Event was terminated at 0617. The breach of the pressure boundary was a crack in the weld attaching the 'C' Reactor Coolant Pump Seal Injection Line to the pump's thermal barrier. The leak was contained inside the reactor building. There were no adverse environmental consequences due to this event.
3971994001 | Columbia | 12/30/1993 | 03/31/1994 | 9404070150 | <strong>Untested Fuel Transferred To The Emergency Diesel Generator Fuel Oil Storage Tanks</strong><br /><i>Abstract:&nbsp;</i>During the period from December 14 through December 21, 1993, diesel fuel that included untested fuel was transferred from the Auxiliary Boiler Fuel Oil Storage Tank (FO-TK-1) to each of the three Emergency Diesel Generator (EDG) Fuel Oil Storage Tanks (DO-TK-1A, DO-TK-1B, and DO-TK-2). This event occurred during post modification testing of the recently installed Fuel Oil Filter Polisher System. Plant personnel involved in the testing identified the problem and initiated a Problem Evaluation Request (PER 293-1438) on December 30, 1993. An operability assessment was performed on December 30, 1993 to determine the status of EDG operability. All three EDGs (DG-1, DG-2, and DG-3) were determined to be operable. This event was inconsistent with Technical Specification Surveillance (TSS) Requirement 4.8.1.1.2.c, which requires that diesel fuel be sampled prior to addition to the EDG storage tanks. <br /><br /> As an immediate corrective action, personnel clearance tagged the Auxiliary Boiler suction valve for the Fuel Oil Filter Polisher System to assure the valve remains closed. This will prevent further transfer of fuel from the Auxiliary Boiler storage tank to the EDG storage tanks until a design review and Safety Evaluation are completed. In addition, fuel oil samples were taken from all four fuel oil storage tanks and sent to an independent chemical testing facility for analysis. <br /><br /> The root causes for this event were: (1) that the nonsafety-related Fuel Oil Filter Polisher System design change documentation did not include a 10CFR50.59 Safety Evaluation or an adequate evaluation of the nonsafety-related to safety-related system interactions, and (2) Operating Procedure PPM 2.8.15, 'Diesel Fuel Oil Filter/Polisher System,' did not include procedural controls to assure that TSS 4.8.1.1.2.c fuel cleanliness and testing requirements were satisfied during system operation.
3971994002 | Columbia | 02/15/1994 | 07/01/1994 | 9407130092 | <strong>Fire Barrier Penetration Seals</strong><br /><i>Abstract:&nbsp;</i>During December, 1993, the Supply System initiated an investigation of an employee concern related to fire barrier penetration seals. Information collected during the initial stages of the investigation led to an in- depth evaluation of the fire barrier penetration seal (seal) program. On February 15, 1994, following the completion of a preliminary analysis of the seal program, the seals were conservatively declared inoperable. This action was taken based upon the determination that some installed seal configurations could not readily be qualified with the available fire test reports, and that sufficient documentation had not been assembled to demonstrate the qualification of the remainder of the seals. In summary, the Supply System has not, in some cases, implemented or maintained the commitment reflected in Appendix F of the FSAR to have fire tests or appropriate engineering evaluations to demonstrate the qualifications of seals. The fire watches established in accordance with the commitments in Appendix F of the FSAR will be continued until the seal qualification issue has been resolved. This event has minimal safety significance at WNP-2 because of the defense in depth protection provided by the fire protection program and because the seals, although not fully qualified, provide a substantial level of fire resistance.
3971994003 | Columbia | 02/22/1994 | 03/24/1994 | 9403300088 | <strong>Undersized Motor Operator Could Prevent Mitigation of a Postulated High Energy Line Break</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1994, during a review of motor-operated valve (MOV) thrust and setpoint calculations, the Supply System determined that due to inadequate motor operator capability, the Reactor Core Isolation Cooling (RCIC) System steam supply bypass valve, RCIC-V-76, could fail to automatically close following a High Energy Line Break (HELB). Although a redundant isolation valve was available, this condition resulted in the containment isolation system not meeting single failure design criteria.<br /><br /> The cause of this condition was inaccurate information from the vendor that led to an erroneous conclusion that the motor operator was adequately sized and adjusted to provide the required thrust to isolate an HELB. <br /><br /> Corrective actions taken or planned include deactivating RCIC-V-76 in its normally closed position, reviewing the thrust and setpoint calculations for similar valves, and modification of RCIC-V-76. <br /><br /> The safety significance of this condition was negligible due to the low probability of a HELB occurring while RCIC-V-76 was open with a concurrent failure of the redundant isolation valve. This condition posed no threat to the health and safety of plant personnel or the public.
3971994004 | Columbia | 03/07/1994 | 04/06/1994 | 9404120005 | <strong>Containment Isolation Valve Technical Specification Actions Not Met</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1994 it was determined that two in-series containment isolation valves, MS-V-16 and MS-V-19, had been inoperable since December 17, 1993 but the appropriate Technical Specification required actions had not been identified and performed. The immediate corrective action was to de-energize these normally closed valves in the closed position. The root cause of this event was ambiguous wording in an operability assessment performed in December, 1993. Contributing causes to this event were inadequate training of support personnel relative to equipment operability, and POC's failure to identify the need to declare the valves inoperable. Plant procedures will be modified to require a clear and concise statement of operability for each piece of equipment being addressed in an operability assessment. Additional training will be provided for those personnel that would generally be expected to perform operability assessments. This training will enhance personnel understanding of operability and the expectations for clear, easily identified operability conclusions within these assessments. Expectations for POC performance were distributed to the POC members on February 16, 1994, and this issue was discussed at the April 6, 1994 POC meeting.
3971994005 | Columbia | 03/26/1994 | 06/24/1994 | 9406290232 | <strong>Failure of Control Rod to Scram Due to Degradation of Pilot Valve Elastomers Caused by In-service Aging</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1994, Control Rod 06-39 failed to scram during routine scram time testing. This was the first failure at WNP-2 of a control rod to scram. The control rod was manually inserted into the reactor and disarmed. The scram solenoid pilot valves (SSPVs) for the control rod had degraded exhaust and pressure diaphragms which had been in service for just under 4 years. The remaining 184 control rods were scram time tested; these control rods scrammed normally with scram times within Technical Specification limits.<br /><br /> The cause of the failure of Control Rod 06-39 to scram was an unusual combination of degradation of both the SSPV pressure and exhaust diaphragms. The cause of the degradation is believed to be accelerated aging due to manufacturing differences in diaphragm composition.<br /><br /> Corrective actions included weekly scram time testing of all operable control rods and expedited replacement of SSPV diaphragms. Following disassembly of the SSPV, direction was provided to plant operators to perform an orderly plant shutdown if any additional control rod failed to scram. The SSPVs were rebuilt. <br /><br /> This event had low safety significance since only one rod failed to scram, Technical Specification scram time requirements were met for all other control rods, and several backup systems were available to insert control rods or otherwise shut down the reactor. This report is submitted to meet the requirements of 10 CFR Part 21.
3971994006 | Columbia | 03/30/1994 | 04/29/1994 | 9405040329 | <strong>Broken HPCS-B1-DG3 Battery Flag Terminal Weld</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1994, at 1330 hours, with the plant at 84.5% power, a system engineer walking down the High Pressure Core Spray system (HPCS) discovered a broken weld between the flag terminal and the negative post of HPCS battery HPCS-B1-DG3 cell #58. This flag terminal joins the HPCS battery feeder cable to its associated post. <br /><br /> At 1415 hours, main control room personnel declared the HPCS system inoperable. At 1526 hours, control room personnel notified the NRC via ENS of the event. Immediate corrective action consisted of replacing the damaged battery cell. <br /><br /> The probable cause for this event was poor equipment design of the HPCS battery enclosure. The enclosure hampers personnel from effectively performing associated maintenance activities. Further corrective action includes improving the design of the battery enclosure. <br /><br /> This event had no safety significance. After HPCS battery cell replacement, engineering and electrical maintenance personnel tested the damaged cell and determined that the cell was able to perform its safety function in its as-found condition. The HPCS system was inoperable for less than twenty-four hours during replacement of the battery cell and verification of replacement-cell operability.
3971994007 | Columbia | 04/10/1994 | 05/11/1994 | 9405170237 | <strong>RCIC Level 8 Isolation Miscalibration</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1994, at 1900 hours, with the plant at 64.6% power, an Instrument and Control (I&C) Maintenance Supervisor reviewing trend data determined that a Reactor Core Isolation Cooling system (RCIC) Level 8 Isolation instrument had been calibrated outside of its Technical Specification Allowable Value from November 9, 1993 to January 29, 1994. At a predetermined Reactor Pressure Vessel (RPV) high-water-level, the Level 8 Isolation closes the RCIC turbine steam supply valve RCIC-V-45, which in turn stops RCIC makeup to the vessel. <br /><br /> Technical Services and I&C personnel initiated an evaluation of applicable Technical Specification surveillance procedures to ensure that similar calibration errors did not exist. The root cause of this event was a failure to self-check to ensure the intended action is correct before it is performed. Further corrective action includes ensuring similar calibration errors that could impact equipment operability currently do not exist. <br /><br /> This event had no safety significance. The miscalibration would have caused the Isolation to occur 0.85 inches above the Technical Specification Allowable Value of 56 inches reactor water level (above instrument zero). Even with the identified condition, the RCIC system was still able to provide high-pressure makeup to the RPV upon demand.
3971994008 | Columbia | 04/26/1994 | 05/26/1994 | 9406020024 | <strong>Manual Scram Due To Observed Reactor Core Power Fluctuations</strong><br /><i>Abstract:&nbsp;</i>At 1010 hours on April 26, 1994, with the plant at 50% reactor power and 55% core flow, plant Control Room Operators (CROs) observed slight reactor power fluctuations on the six average power range monitors (APRMs). Based on an indication of potential core instabilities, Control Room personnel manually scrammed the reactor in accordance with Plant Abnormal Operating Procedure PPM 4.12.4.7, 'Unintentional Entry Into Region of Potential Core Power Instabilities.'<br /><br /> Immediate corrective actions were taken by the Control Room staff to bring the plant to a safe shutdown condition in accordance with Emergency Operating Procedure (EOP) 5.1.1, 'RPV Control,' and Recovery Procedure PPM 3.3.1, 'Reactor Scram.' <br /><br /> The root causes for this event were the degraded condition of a Reactor Recirculation (RRC) flow control valve (FCV) position transmitter and the lack of procedural criteria to determine when to 'lock up' the degraded FCV. <br /><br /> Further corrective actions include: (1) replacement of the RRC FCV position transmitters, (2) calibration and testing of the replacement FCV position transmitters, and (3) required reading of this Licensee Event Report (LER) by WNP-2 licensed operators. <br /><br /> This event posed no threat to the health and safety of either the public or plant personnel.
3971994009 | Columbia | 04/19/1994 | 05/18/1994 | 9405250140 | <strong>Incorrect Isolation Valve Component Selection</strong><br /><i>Abstract:&nbsp;</i>On 19 April, 1994, it was determined that containment isolation provisions for two containment monitoring systems were inoperable because the inboard valves for the sampling return lines could not function as containment isolation valves in the event of a LOCA. The immediate corrective action taken was to close the outboard containment isolation valves for these two lines. The root cause is that excess flow check (EFC) valves were installed in these two locations during initial plant construction, and the design of the valves is such that they cannot satisfy the containment isolation function required by General Design Criterion (GDC) 56. A plant modification will be executed during the current refueling outage to replace the two EFC valves with simple check valves, which will satisfy GDC 56.
3971994010 | Columbia | 08/10/1994 | 09/09/1994 | 9409160286 | <strong>Fire Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>In April 1994, the WNP-2 Quality Assurance (QA) Directorate initiated a special focused audit of the licensing basis fire safe shutdown procedures and associated calculations and programs. In response to the QA findings, a detailed system by system evaluation was performed. This evaluation included consideration of both safe shutdown and non-safe shutdown systems and components. Through this evaluation it was identified that a start of Residual Heat Removal (RHR) pump 2B and a fire induced failure to open of the minimum flow control valve (RHR-FCV- 64B) could have resulted in damage to the pump. <br /><br /> The cause of this event was lack of an adequate analysis of the potential fire impact on the minimum flow control valve circuitry. Interim corrective actions have been put in place, and potential long term corrective actions are being evaluated. Given the multiple safe shutdown paths that could be available, the short time frame in which this condition must occur, and the comprehensive fire protection program utilized at WNP-2, this event was deemed to have minimal safety significance.
3971994011 | Columbia | 06/24/1994 | 07/28/1994 | 9408040162 | <strong>Failure To Complete Weekly Manual Scram Surveillance Requirements Within The Allowed Technical Specification Interval Due To Inadequate Communication</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1994, with WNP-2 in Mode 5 (Refueling) at 0% power, it was determined that the weekly manual scram channel functional test had not been performed within the Technical Specification (TS) allowed interval. As a result, the TS operability requirements had not been met for all four Reactor Protection System (RPS) manual scram trip channels during a 3.4 day period from 2103 hours on June 24, 1994 until 0541 hours on June 28, 1994. Since this condition was not identified until June 30, 1994, all TS required actions had not been performed. <br /><br /> No immediate corrective actions were necessary because at the time of discovery all four manual scram trip channels were operable. <br /><br /> The root cause for this event was inadequate communication between Operations Senior Reactor Operator (SRO) support personnel and the Control Room staff. Corrective actions included a programmatic change and counseling of responsible personnel. <br /><br /> This event posed no threat to the health and safety of either the public or plant personnel.
3971994012 | Columbia | 06/23/1994 | 07/22/1994 | 9407260203 | <strong>Control Room Emergency Filter Wma-Fu-54b Inoperable Due To Leaking Deluge Supply Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>At approximately 2310 hours on June 23, 1994, during maintenance with the reactor in cold shutdown, water was discovered in the bottom of control room emergency filter unit WMA-FU-54B. The water originated from leakage past a deluge system isolation valve and rendered the unit's charcoal filter inoperable. The root cause of this event was a leaky manual isolation valve installed in the unit's deluge supply line. Contributing causes were missed opportunities for earlier detection of water within the unit and inadequate communications. Immediate corrective actions included replacing the leaky valve and restoring filter unit operability. Further corrective actions included revising the appropriate deluge system valve station lineups to preclude recurrence and training on the lessons learned from this event. Because the charcoal filter was inoperable, this event had potential safety significance.
3971994013 | Columbia | 06/22/1994 | 10/14/1994 | 9410190125 | <strong>Design Error In Electrical Circuitry For Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1994 it was determined that containment isolation provisions for both Containment Monitoring Systems were inoperable because the design of the electrical circuitry was such that failure of a single electrical relay could prevent closure of the solenoid-operated containment isolation valves associated with those particular systems. The plant was in an annual refueling and maintenance outage. The root cause is design error during initial plant construction. A plant modification was executed to revise the electrical circuitry to eliminate the design flaw causing the deficiency. In addition, a detailed review of the logic circuits for the other electrically powered isolation valves listed in Technical Specification 3.6.3 was performed. One other case was discovered in which failure of a single relay could prevent closure of solenoid-operated containment isolation valves associated with the hydraulic control system for the two flow control valves for the Reactor Recirculation System. A request for enforcement discretion and an emergency Technical Specifications Amendment was processed to allow continued operation until the next shutdown at which time a modification will be implemented to eliminate the design flaw causing the deficiency.
3971994014 | Columbia | 07/06/1994 | 08/05/1994 | 9408110241 | <strong>Engineered Safety Feature Actuation Due to Test Lineup Error Caused by Noncompliance with Testing Procedure</strong><br /><i>Abstract:&nbsp;</i>At 1236 hours on July 6, 1994, Instrumentation and Control (I&C) technicians were back filling instrument lines to support excess flow check valve testing. Due to a lineup error, the differential pressure sensed by in-service reactor vessel level detectors was increased creating an invalid low level indication which caused several automatic actions including a low pressure core spray system actuation and injection. The control room operator secured the injection after verifying no actual low level condition existed. The cause of the event was the failure of the technicians to follow the back fill procedure. Corrective actions include counseling the technicians, discussing the event with the I&C shop, and developing and delivering further training to I&C technicians. This event had negligible safety significance since plant safety systems responded as designed, no actual low level condition existed, and the stresses induced by the injection were small due to the small differential temperatures and pressures involved.
3971994015 | Columbia | 07/04/1994 | 09/22/1994 | 9409290162 | <strong>Voluntary Report Of A Spurious ESF Component Actuation Cause By Tubing Valve Manipulation</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted as a voluntary report. On July 4,1994, the plant was in an annual refueling/maintenance outage. An actuation of the High Pressure Core Spray System (HPCS) diesel engine and half-scram condition occurred at 2029 hours due to manipulation of instrument tubing valves in the reactor pressure vessel (RPV) level sensing instrumentation in preparation for reactor startup. No water was injected into the reactor pressure vessel (RPV) by the system because the HPCS pump had been properly removed from service. The actual water level in the RPV was normal. No plant condition existed that warranted actuation of the HPCS, and the actuation occurred as designed to the extent the existing system line-up permitted. The half-scram was reset and the diesel engine was shut down from the control room. The cause was inadequate identification of the status of equipment undergoing a modification and testing process.
3971994016 | Columbia | 07/01/1994 | 07/29/1994 | 9408030163 | <strong>Failure To Conduct Control Rod Maximum Scram Insertion Time Testing Due To Nonconservative Interpretation Of Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>The Technical Specification Surveillance Improvement Program has heightened awareness of system operability and Technical Specification requirements fostering a proactive attitude to question procedure/ Technical Specification compliance. As a result of this heightened awareness, on July 1, 1994 WNP-2 staff determined that Control Rod (CR) Scram Time testing (per Technical Specification surveillance 4.1.3.2.b following CR or control rod drive system maintenance or modification prior to entry into Operational Conditions 1 and 2) had not been conducted during previous outages. Extensive post maintenance testing (PMT) and scram time testing at approximately 25 % power per 4.1.3.2.a (at > / = 950 psig prior to exceeding 40 % power) had been performed. The cause was a nonconservative Technical Specification interpretation. The interpretation concluded that comprehensive PMT confirmed that maintenance or modification had not affected the scram times. Corrective action was to obtain a change to the Technical Specifications to accept a low pressure test provided the test is repeated at > / = 950 psig prior to exceeding 40% power. This event had negligible safety significance because testing per 4.1.3.2.a at > / = 950 psig at less than 40 % power confirmed the scram times to be within limits.
3971994017 | Columbia | 10/20/1994 | 11/21/1994 | 9411300264 | <strong>Technical Specification Limit Exceeded Due to Improper Calibration Of The Suppression Pool Narrow Range Level Transmitters.</strong><br /><i>Abstract:&nbsp;</i>At 1544 hours on October 20, 1994, the Control Room was informed the suppression pool narrow range water level transmitters had been improperly calibrated. Due to the improper calibration, the suppression pool actual water level was approximately two inches greater than indicated level. The difference between actual and indicated level resulted in exceeding the high level limit of Technical Specification 3.6.2.1. Suppression pool water level was lowered to within Technical Specification limits and the narrow range level transmitters were recalibrated. The calibration error resulted from a failure to recognize the impact on the transmitter zero reference point when a transmitter utilizes a wet sensing line and a dry reference line and account for this in the calibration procedure. The error occurred in 1983 during original development of the calibration procedure for one transmitter and during a procedure revision in 1985 for the other two transmitters. Corrective actions include changing the calibration procedures, calibrating the transmitters, and reviewing calibration procedures for other transmitters using the same calibration methodology. Because the suppression pool volume increase was determined to have a negligible impact on plant safety, the condition described in this report did not have an effect on the safe operation of the plant or the health and safety of the public.
3971994018 | Columbia | 11/15/1994 | 03/02/1995 | 9503080384 | <strong>Failure To Comply With A Technical Specification Action Requirement When Inoperable Control Rod Block Instrumentation Exceeded The Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>A replacement Channel 'A' Scram Discharge Volume (SDV) high water level control rod block level switch was installed during the Spring 1994 Refueling Outage and calibrated and tested on June 30, 1994 to verify operability. The switch failed the first quarterly channel functional test (CFT) on October 11, 1994. The switch was recalibrated and functionally tested several times to assure repeatability, and as a precaution, the surveillance frequency was increased. The CFT was successfully performed approximately two weeks later, but the switch failed the CFT on November 9, 1994 and was declared inoperable. During an evaluation of the repeat failure, it was discovered that the level switch is not designed to be adjustable, and the previous switch calibrations could have caused the switch actuation failures. As a result, on November 15, 1994, with -2 in Mode 1 at 100% power, it was determined that the Channel 'A' level switch had been technically inoperable from June 30, 1994 to November 9, 1994 without the Technical Specification required action having been performed. With only the Channel 'B' level switch and trip function operable, the number of operable channels was less than that required by Technical Specification 3.3.6.b and Table 3.3.6-1, Trip Function 5.a. <br /><br /> Immediate corrective action was taken at 1527 hours on November 9, 1994 to place the Channel 'A' SDV high water level control rod block trip function in the tripped condition. Actions were then taken to restore the Channel 'A' level switch and trip function to operable status. The level switch and trip function were declared operable at 1914 hours on November 11, 1994.
3971994019 | Columbia | 11/21/1994 | 12/21/1994 | 9412290254 | <strong>Gasket Missing From Main Control Room Air Handler WMA-AH- 51B Precludes Associated Emergency Fan WMA-FN-54B From Sufficiently Pressurizing The Control Room</strong><br /><i>Abstract:&nbsp;</i>At 1130 hours on November 21, 1994, with the plant at 100 percent power, during performance of Technical Specification Surveillance (TSS) procedure PPM 7.4.7.2.8 'Control Room Ventilation Pressurization Flow Test,' emergency fan unit WMA-FN-54B failed to pressurize the main control room sufficiently to meet the associated surveillance requirement (a slight positive pressure was achieved, however). A missing gasket, removed October 26, 1994 from an access door of main control room air handling unit WMA-AH-51B, caused the failure. Because WMA-FN-54B discharges into the control room via WMA-AH-51B, leakage past the missing gasket precluded sufficient control room pressurization. The root cause of this event was that the design of WMA-AH-51B was modified without the proper authorization, design reviews, or controls. Corrective actions consisted of counseling the Mechanical Maintenance Supervisor and discussing the lessons learned from this event with the maintenance crafts. This event has no safety significance, because WMA-FN-54B did pressurize the control room, redundant emergency fan WMA-FN-54A remained capable of pressurizing the control room, and control room pressurization was not required during this short time period.
3971994020 | Columbia | 11/11/1994 | 12/12/1994 | 9412210161 | <strong>Potential Of Spurious Actuation Of Pneumatic Supply Valve To Impair Operation Of Main Steam Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1994, WNP-2 was operating at 100% power in Mode 1. An engineer postulated that a Main Control Room fire could induce a hot short that could result in spurious closure of motor-operated containment isolation valve CIA-V-20. This might result in depletion of pneumatic supplies for Main Steam Relief Valves during the interval between evacuation of the Control Room and assumption of plant control from remote shutdown panels. No fire actually occurred. The NRC was notified of this event at 1726 (PST) pursuant to 10CFR50.72(b)(2)(iii)(A). Subsequent analysis revealed that the event was due to inadequate analysis rather than a condition that would have prevented maintaining the reactor safely shut down in event of a Control Room fire and should be reported only under 10CFR50.73(a)(2)(iii)(A). The cause of the event was a design deficiency due to lack of adequate consideration of the plant response during the interval between Control Room evacuation due to a fire and assumption of plant control from the remote shutdown panels. <br /><br /> A continuous fire watch was established for the area, and a procedure revised to assure an operator would be immediately prestaged at a remote shutdown panel to transfer control of certain Main Steam Relief Valves from the Control Room to a remote shutdown panel in event of a Control Room fire. A design change will be implemented to eliminate the problem, and a procedure governing analysis of equipment used for safe shutdown after a Control Room fire will be changed to require consideration of on-going plant processes during the interval between Control Room evacuation and assumption of control from remote panels.
3971994021 | Columbia | 11/23/1994 | 12/22/1994 | 9412290260 | <strong>Holes Cut In Main Control Room Floor Penetration 5016 Precludes Redundant Emergency Fans WMA-FN-54A(B) From Pressurizing The Control Room Sufficiently To Meet The Applicable Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 0935 hours on November 23, 1994, with the plant at 100 percent power, an investigation determined that a flow path created by a barrier impairment in the control room floor to the cable spreading room in penetration 5016 located under control room instrument panel H13-P682 prevented emergency fan unit WMA-FN-54B from pressurizing the main control room sufficiently to meet Technical Specification Surveillance (TSS) procedure PPM 7.4.7.2.8 'Control Room Ventilation Pressurization Flow Test' performed at 0300 hours that same morning. The barrier impairment consisted of two 5' X 6' holes, which were opened on November 22, 1994, for routing conduit associated with a 'reactor recirculation pump adjustable speed drive' plant modification. By 1045 hours, the holes were resealed and pressurization capability of redundant emergency fans WMA-FN-54A(B) was verified. Root cause analysis indicated that the work planning procedure was deficient because it did not provide adequate guidance for assessing the need for a barrier impairment. Corrective actions included improving guidance contained in the applicable procedures. WNP-2 acknowledges that this event would have prevented both redundant emergency fans WMA-FN-54A(B) from pressurizing the control room sufficiently to meet the surveillance requirement; however, an Engineering assessment of surveillance test results determined that the control room would still have been amply pressurized to prevent infiltration of air during a postulated accident involving a radioactive release. Therefore, this event had no safety significance.
4001994001 | Harris | 05/02/1994 | 06/01/1994 | 9406080114 | <strong>Technical Specification surveillance violation due to not verifying actuation of valve 1ED-121 in the quarterly slave relay test for relay #K623.</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1994, Operations personnel discovered that the slave relay test for relay #K623 did not verify the actuation of the Reactor Coolant Drain Tank Pumps Discharge Valve (1ED-121). This valve is a containment isolation valve that receives a shut signal upon a Containment Phase 'A' Isolation and is therefore categorized as an Engineered Safety Features (ESF) component. Technical Specification (TS) Surveillance 4.3.2.1 requires a quarterly slave relay test for ESF components that includes, as a minimum, a continuity check of actuated components. Operations Surveillance Test (OST-1044) was developed prior to plant operation to satisfy the TS requirement and has verified that the relay functions, as indicated by actuation of its other components, but has never included verification of valve 1ED-121 closure. This constitutes a TS surveillance violation and is being reported per 10CFR50.73(a)(2)(i)(B). <br /><br /> The event was caused by a procedural deficiency in OST-1044. Inadequate technical review during initial procedure development resulted in the omission of valve 1ED-121. Investigation revealed that the format and configuration of design drawings contributed to confusion as to which relay included the actuation circuitry for valve 1ED-121. <br /><br /> Corrective actions included a revision to OST-1044 and a review of other ESF output relays to ensure that required testing is being conducted. Additional actions will include training on this event for appropriate personnel.
4001994002 | Harris | 07/17/1994 | 08/16/1994 | 9408240111 | <strong>Technical Specification surveillance violation due to failure to perform required Radiation Monitoring System compensatory measures.</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1994, at 0738, the Turbine Building Wide Range Gas Monitor (WRGM) was declared inoperable due to a communication loss with the RM-11 in the Main Control Room. At 1500 that day, a reactor operator performing Technical Specification (TS) channel checks did not question or verify the operability status of the Turbine Building Vent Stack Flow Rate Monitor and incorrectly assumed that it was declared inoperable as a result of the WRGM communication loss. Based on this incorrect assumption, the operator did not perform the required 12-hour channel check, nor did he ensure that the TS compensatory 4-hour flow estimates were being performed. Flow rate monitor channel checks were not performed until the condition was discovered at 2300 on the following day (July 17, 1994). This period of time exceeded the TS surveillance interval of 24 hours plus a 25% margin (30 hours total). Upon discovering that the channel check surveillance frequency had been exceeded, the stack flow rate monitor was declared inoperable and the compensatory measure of performing a 4 hour flow estimate was commenced. On July 19, 1994, at approximately 1000, an omission of two fans was discovered in the flow rate estimate log book which is used by the control room staff to perform the estimate of total flow being directed through the vent stacks. This condition resulted in inaccurate stack flow rate estimates that did not satisfy TS requirements. Both incidents constitute a violation of TS and are being reported in accordance with 10CFR50.73. Corrective actions will include revisions to applicable procedures and training/counseling for appropriate personnel.
4001994003 | Harris | 07/18/1994 | 11/10/1994 | 9411160233 | <strong>Improperly analyzed single failure in the Emergency Service Water System that could potentially result in the Charging/Safety Injection Pumps not performing their safety function.</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1994, a potential single failure was identified in one train of the Emergency Service Water System (ESW) that, without reasonably expected operator action, might prevent the Charging/Safety Injection Pumps (CSIP) from performing their safety function due to inadequate oil cooling. This postulated scenario would occur due to elevated temperature cooling water being supplied to the CSIP Oil Coolers. Specifically, if the 'A' train auxiliary reservoir return valve (1SW-270) failed to open, the 'A' train of ESW would be dead-headed at a higher pressure than the 'B' train. This difference in pressure, coupled with a pressure gradient within the 'A' train due to the action of the Service Water Booster Pump, would result in cooling water back-flowing through the Emergency Diesel Generator (EDG) jacket water coolers before entering the CSIP oil coolers. With the EDG running and loaded, the back flow would be heated above the oil cooler maximum design temperature. This condition was caused by not adequately identifying and considering the effects of an active valve failure on the cross-connection at the CSIP's during initial ESW design and operational valve line-up development. Subsequent system design assessments and reviews also did not identify the abnormal flow path. This was due to the scope of these reviews, which focused on passive type failures such as line breaks in the common piping between headers and their effects on opposite train operability, not the detailed flow and temperature analysis that eventually identified the cited condition. Additional engineering analysis concluded that, upon normally expected identification and mitigating actions by operators in the main control room, the event would have been terminated prior to any adverse effects on the CSIP'S. Immediate corrective actions for this event were to close the train cross connects at the CSIP lube oil coolers, thus eliminating the possibility of the described scenario. Additional corrective actions include further engineering review and evaluation in the Emergency and Normal Service Water Systems as well as other systems that may have similar cross connection problems.
4001994004 | Harris | 08/05/1994 | 09/01/1994 | 9409130488 | <strong>Technical Specification surveillance violation due to failure to perform Emergency Diesel Generator Testing at the required increased frequency and on a staggered test basis.</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1994, it was discovered that two failures of the 'B' Emergency Diesel Generator (EDG) had occurred within the last twenty valid tests without a test frequency increase to once per seven days as required by Technical Specification Surveillance Requirement 4.8.1.1.2.a. On August 13, 1994, it was also discovered that the required 'staggered test basis' interval had been exceeded when both diesels were placed on increased test frequency on August 5, 1994. These problems constitute a violation of the TS surveillance requirement and are being reported in accordance with 10CFR50.73. <br /><br /> The cause of this event was inadequate administrative process and procedural controls to ensure proper and timely EDG test failure evaluation and initiation of EDG testing at the increased test frequency on a staggered test basis.<br /><br /> Immediate corrective actions were to test the 'B' EDG and implement an increased test frequency of once per seven days on a staggered test basis. Additional corrective actions will include revising appropriate procedures to clarify the EDG testing evaluation process, enhancing the Surveillance Test Scheduling System weekly EDG test task sheets, and performing training on this event to appropriate personnel. <br /><br /> There were no adverse safety consequences as a result of this event. Satisfactory testing was performed on each Emergency Diesel Generator, which demonstrated the ability to perform the required safety function, as required by Technical Specifications.
4001994005 | Harris | 09/01/1994 | 09/30/1994 | 9410070254 | <strong>Technical Specification surveillance violation due to failure to perform an analysis of a batch release prior to the release.</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1994, it was discovered that the contents of the Treated Laundry & Hot Shower Tank (TL&HS) 'A' had been released prior to an analysis being performed as required by Technical Specification (TS) Surveillance Requirement 4.11.1.1.1. This constitutes a violation of the TS surveillance requirement and is being reported in accordance with 10CFR50.73. The cause of this event was personnel error during the sample analysis process. A grab sample of the TL&HS Tank 'A' was obtained in preparation for the release and was placed into detector #2 of a multiple channel analyzer. However, data acquisition (sample analysis) was performed on detector #1, which was empty at the time. The analysis results of the empty detector were then used to complete the release permit for the TL&HS Tank 'A' and to establish the alarm setpoints for the release path radiation monitor. Immediate corrective actions were to correctly reanalyze the sample and revise the release permit to indicate the actual activity that was released from the tank. The personnel directly involved were counseled. The event was also reviewed with other applicable E&C personnel to reemphasize the need for good self-checking techniques and to stress attention to detail. Additional corrective actions will include an evaluation to determine if human factor enhancements can be made to alleviate this problem in the future. There were no adverse safety consequences as a result of this event. The analysis of the TL&HS grab sample indicated no abnormal radioactivity levels. Additionally, the TL&HS radiation monitor alarm setpoints were set at a value more conservatively than had they been set using the correct sample results. Also, the radiation monitor operated for the duration of the release and indicated no adverse levels of radioactivity.
4001994006 | Harris | 11/16/1994 | 12/15/1994 | 9412200181 | <strong>Cell voltage verification required by Technical Specifications was not performed when the safety related B-SB station battery individual cell voltage values fell outside the allowable limits.</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1994 surveillance testing revealed that the inter-cell float voltage (ICV) for cell #50 of the B-SB safety related battery was between the 2.13 volt 'limit' and 2.07 volt 'minimum allowable value' of Technical Specification (TS) Table 4.8-2. The battery is still considered operable with the voltage value in this range, provided that the voltage is restored to greater than the 2.13 volt 'limit' within 7 days. Discussion related to this testing requirement resulted in a review of documentation from recently performed surveillance tests. This review identified that cell recharge verification had not been performed within 7 days as required following testing the previous month on October 19, 1994. Upon identification of this condition, the control room staff declared the B-SB battery inoperable and commenced a single cell charge on cell #50 to raise the voltage back to acceptable levels. Subsequent investigation revealed nine additional instances where this verification had not been performed within 7 days as required. These occurrences constitute a violation of TS and are being reported per 10CFR50.73. <br /><br /> The cause of this condition was a combination of a deficient test procedure and poor work practices on the part of those involved in performing and reviewing the tests. Immediate corrective actions included restoring the cell voltage to an acceptable value, reviewing other battery testing procedures and revising the deficient maintenance surveillance test procedure. maintenance personnel to enhance their understanding of procedural and TS requirements. There were no safety consequences as a result of this condition. Even though testing was not performed as required by TS, the battery ICV values were always above the 'allowable level', therefore the battery was capable of performing it's safety function. There have been no previous reports submitted related to the failure to perform TS battery testing.
4001994007 | Harris | 11/28/1994 | 12/21/1994 | 9412300245 | <strong>Violation of Technical Specification minimum control room staffing requirements.</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1994 with the plant in mode-1 at 100% power, the main control room staff was reduced to one SRO licensed individual for a period of 4 minutes. This individual was filling the Senior Control Operator position and was at the controls area during this entire period. This condition violates Technical Specifications section 6.2.2.b, which requires at least one Licensed Operator and at least one Licensed Senior Operator to be in the control room with the plant in modes 1 through 4. The cause of this event was personnel error on the part of the control room staff. Immediate corrective actions included counseling the involved operations personnel and communicating the various aspects of the event to other appropriate operations personnel. Additional actions will include the development and implementation of a formal process for temporary relief for operators in the main control room. The safety consequences of this event were minimal. During the entire 4 minute period, the Senior Control Operator was in the control room 'at the controls' area and would have been able to respond to any control board annunciator and take immediate actions accordingly. The Shift Technical Advisor was also in the control room 'at the controls' area during the entire period. The Balance of Plant (BOP) Operator was within the control room envelope, in a kitchen area behind the main control board. He could have been back 'at the controls' in less than 10 seconds if needed. The Reactor Operator was in the Work Control Center, which is in an adjoining room. However, he would have been beyond audible range of control board annunciators and would had to have been summoned back to the control room via the site PA system. His transit time to the control room 'at the controls' area, if needed, would have been less than 20 seconds. There have been no previous reports submitted related to control room minimum staff violations.
4101994001 | Nine Mile Point 2 | 03/12/1994 | 06/10/1994 | 9406200077 | <strong>Reactor Scram and ESF Actuations Caused by a Faulty Test Switch</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1994 at 1923 hours, Nine Mile Point Unit 2 (NMP2) experienced several Engineered Safety Feature actuations. Specifically, an automatic reactor scram caused by turbine control valve fast closure and primary containment and reactor vessel isolations caused by low (Level 3) reactor vessel water level. At the time of the event, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at approximately 100 percent of rated thermal power. <br /><br /> The cause of the event was a faulty pushbutton test switch in the power/load unbalance trip circuit of the Turbine Electrohydraulic Control (EHC) system. This caused the power/load unbalance trip circuit to become energized and subsequently, the turbine control valves to fast close on a power/load unbalance trip signal initiating this event. The root cause of this event is poor equipment design. <br /><br /> Corrective actions include replacement of the faulty test switch, a review of similar switches used in similar applications and a review of all safety related control circuitry for the impact of a similar failure. Changes to the power/load unbalance and the backup overspeed test circuit designs and test frequencies will be evaluated. Additional corrective actions identified will be implemented by the completion of the next refueling outage.
4101994002 | Nine Mile Point 2 | 05/02/1994 | 05/31/1994 | 9406070219 | <strong>Reactor Water Cleanup Isolation on High Pump Room Temperature Caused by a Pump Seal Failure</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1994 at 0352 hours, Nine Mile Point Unit 2 (NMP2) experienced the actuation of an Engineered Safety Feature (ESF). Specifically, the Reactor Water Cleanup System (WCS) isolated on high air temperature in the WCS pump room. At the time of the event, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at approximately 100 percent of rated thermal power. <br /><br /> The high air temperature was caused by a seal failure on Reactor Water Cleanup pump 2WCS-P1A. The root cause of the seal failure was inadequate managerial methods. Three Contributing causes were pertinent information not transmitted to appropriate personnel, management's expectations not adequately communicated, and specific training in mechanical seals not provided to appropriate personnel. <br /><br /> Immediate operator actions included verification of correct WCS response and following the Emergency Operating Procedures for Secondary Containment Control. Additional corrective actions include: 1) replacing the failed seal; 2) revising the work control process to ensure that degrading conditions result in re-evaluation of existing corrective action plans; 3) evaluating System Engineer turnover process; 4) reinforcing with operators the need to adjust priorities when component deficiencies degrade; 5) briefing System Engineers on expectations of increased monitoring; 6) developing training to communicate management expectations for vital component deficiencies; and 7) providing mechanical seal training to appropriate personnel.
4101994003 | Nine Mile Point 2 | 08/30/1994 | 10/31/1994 | 9411070419 | <strong>Surveillance Tests of Service Water not Performed per Technical Specification Requirements Because of Inadequate Managerial Methods</strong><br /><i>Abstract:&nbsp;</i>At 1430 hours on August 30, 1994, with the reactor at 100 percent power with the mode switch in RUN (Operational Condition 1), it was discovered that the surveillance testing of the service water pumps was not in compliance with Technical Specification requirements. At this time, it was also determined that the surveillance testing of the Intake Heater Deicing System was not in compliance with Technical Specification requirements. The required surveillance testing had been performed during plant operation, however, the Technical Specifications require that these specific surveillances be performed during shutdown. As a result of the investigation of these deviations, another similar deviation was identified. Two Service Water System valves were tested before rather than during the third refueling outage as required by the In-Service Testing (IST) program plan. <br /><br /> The root cause for the non-compliance with the Technical Specification requirements is inadequate managerial methods in that administrative procedures did not provide the necessary guidance and controls for procedure development. The root cause for the improperly performed IST test was inadequate managerial methods. <br /><br /> Corrective actions for these events included: Submitting an Application for Amendment to delete the 'during shutdown' requirement for the referenced surveillance requirements; increased management review of procedure preparation and review activities; initiation of a comprehensive verification program of Technical Specification surveillance requirements; performing service water valve testing on a quarterly basis; and reviewing the IST program for other errors and revising the ambiguous 'R' frequency code.
4101994004 | Nine Mile Point 2 | 09/16/1994 | 10/17/1994 | 9410250089 | <strong>Technical Specification Violations Caused by an Inadequate Post-Maintenance Test</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1994, during a review of Riley temperature switch replacements, a violation of the Nine Mile Point Unit 2 (NMP2) Technical Specifications was discovered. Specifically, an inadequate Post- Maintenance Test (PMT) was conducted after replacement of five (5) Riley temperature switches. The PMT did not test the relay contacts that initiate the trip function. This caused a violation of Surveillance Requirement (SR) 4.3.2.2, 'Logic System Functional Test' for Isolation Actuation Instrumentation. A subsequent review of Riley temperature switch replacements that were performed earlier identified that approximately one-half had inadequate PMTs. A verification of the review, performed on October 10, 1994, identified an additional Riley temperature switch that was replaced with an inadequate PMT. These also were violations of Technical Specification Surveillance Requirement 4.3.2.2. At the time of discovery, NMP2 was in Operational Condition 1 and operating at approximately 100% power. <br /><br /> The root cause of this event is poor work practices; specifically, design documents were not consistently used during work package preparation and review, causing the inadequate PMTs. A contributing cause of this event is inadequate managerial methods in that the policy for PMTs was not adequately defined.<br /><br /> The immediate corrective action was to declare the five affected temperature switches identified on September 16, 1994 inoperable. All five of the temperature switches were tested, and the trip contacts were found to function as designed in the 'as found' condition. Maintenance Department supervisors will review this event with their personnel to reinforce the requirements of a PMT. Procedure GAP-SAT-02, 'Post- Maintenance Testing' will be revised to provide additional guidance for proper post-maintenance testing.
4101994005 | Nine Mile Point 2 | 10/11/1994 | 11/10/1994 | 9411210346 | <strong>Technical Specification Violation Caused by Inadequate Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>At 0759 hours on October 11, 1994, with the reactor at 100 percent power and the mode switch in RUN (Operational Condition 1), it was discovered that the surveillance testing of the Safety Relief Valve (SRV) acoustic monitors was not in compliance with Technical Specification 4.4.2.1 requirements. Specifically, Acoustic Monitoring Procedure, N2-ISP-SVV-Q002, performed quarterly, did not meet Technical Specification requirements for a Channel Functional Test. <br /><br /> The root cause of this event was determined to be inadequate managerial methods which allowed approval of procedures without adequate critique or technical review. The non-compliance with respect to the Channel Functional Test of the acoustic monitors existed since the initial licensing of Unit 2. The identification of this deviation was made because of a heightened awareness and a questioning attitude developed as a result of recent management emphasis on the preparation and review of technical procedures. <br /><br /> The immediate corrective action was to declare all the SRV acoustic monitors inoperable. All the monitors were adequately tested and restored to service within the time limits of the Limiting Condition for Operation (LCO). Other corrective actions included review of other acoustic monitor test procedures, revision of the quarterly channel functional test procedure, and increased management review of procedure preparation and review activities.
4101994006 | Nine Mile Point 2 | 10/24/1994 | 11/22/1994 | 9412020246 | <strong>Technical Specification Violation Resulting From a Missed Action Statement Caused by Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1994 at approximately 0950 hours, Control Room Operators at Nine Mile Point Unit 2 (NMP2) did not perform all Technical Specification Actions within the required timeframe. Specifically, two Control Rod Drive Hydraulic Control Unit accumulators were made inoperable for pre-planned maintenance without immediately verifying a Control Rod Drive (CRD) pump was running. Action Statement a.2.a of Technical Specification 3.1.3.5, requires that an operating CRD pump be verified immediately by inserting at least one withdrawn control rod at least one notch. This Action was not completed until 25 minutes after the Action Statement was entered. For the duration of this event, the reactor mode switch was in the 'RUN' position (Operational Condition 1) with the plant operating at approximately 90 percent of rated thermal power. <br /><br /> The root cause of this event was inadequate work practices caused by the failure of the operating shift supervision to recognize and implement the requirement to immediately verify a CRD pump operating. Contributing to the event were poor work plan implementation along with inadequate verbal communications. <br /><br /> The immediate corrective actions included Control Room Operators completing the Technical Specification Actions and returning one of the CRD Hydraulic Control Units to an operable status. Additional corrective actions include: 1) counseling and discipline of the SSS/ASSS involved;2) reinforcing management's expectation for utilization and implementation of the Technical Specifications; 3) improving Operator training; and 4) enhancing the Work Control and scheduling process.
4101994007 | Nine Mile Point 2 | 12/09/1994 | 01/09/1995 | 9501230070 | <strong>RPS and ESF Actuations and a Technical Specification Violation Occurring During Completion of a Technical Specification Required Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1994 at 1418 hours, while Nine Mile Point Unit 2 (NMP2) was performing a normal reactor shutdown required by Technical Specifications, actuations of the Reactor Protection System (RPS) and Engineered Safety Feature (ESF) System occurred. Specifically, operators initiated a manual reactor scram, from approximately 22 percent rated core thermal power, after the offgas system isolated and condenser vacuum started to decrease. After the scram, reactor vessel water level decreased to level 3, as expected, initiating a Group 4 (Residual Heat Removal) and Group 5 (Shutdown Cooling) isolation signal. Additionally, a violation of Technical Specification Surveillance Requirements occurred when the drywell and suppression chamber atmospheres were purged without first performing required sampling of the suppression chamber. At the time these events occurred, NMP2 was in an Unusual Event due to increased unidentified reactor coolant system leakage in the drywell. <br /><br /> The root cause of the Technical Specification required shutdown, due to reactor coolant system leakage, is poor managerial methods. During the drywell inspection following shutdown, valve 2CSH*HCV120 was found to have a packing leak. This valve was previously scheduled to be repacked during the third refuel outage (Fall 1993), but was removed from the outage work schedule without the risks and consequences being adequately assessed. The root cause of the Technical Specification violation has been determined to be inadequate written communications. The packing leak on valve 2CSH*HCV120 was repaired.
4121994001 | Beaver Valley 2 | 01/15/1994 | 02/14/1994 | 9402180279 | <strong>Refueling Water Storage Tank Lo-Lo Level Transmitters Freezing</strong><br /><i>Abstract:&nbsp;</i>At 0053 hours on 1/15/94, the control room received channel 'D' Refueling Water Storage Tank (RWST) LO-LO Level bistable indication. This was determined to be the result of the transmitter sensing lines freezing during low ambient temperatures. This channel is one of four transmitters required to be operable by Technical Specifications (TS). In accordance with TS, the other three channels were demonstrated to be operable and the bistable for the 'D' channel was bypassed. Actions were implemented to thaw the sensing lines. At 0640 hours, the 'D' channel was taken out of bypass to obtain voltage readings. The LO-LO bistable light was dark indicating normal conditions at this time. At 0820 hours, the control room received indication for the channel 'A' RWST LO-LO Level bistable. The 'D' channel displayed normal indications, but the declaration of operable was being held until voltage data could be evaluated. With one less than the required three operable transmitters available, TS 3.0.3 was applied. Actions to thaw both sensing lines were expedited and preparations to shut down the unit were initiated. A load reduction was commenced at 0942 hours. At 1202 hours, both transmitters were restored to operable status and TS 3.0.3 was exited. This event is being reported under 10CFR50.73.a.2.i.B, as a condition prohibited by Technical Specifications.
4121994002 | Beaver Valley 2 | 03/10/1994 | 04/10/1994 | 9404110380 | <strong>Insufficient Design Review Results in Condition Outside Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On 2/21/94, with Unit 2 operating at 100 percent power, the plant staff determined that a plant design change, which retired in place the High Head Safety Injection (HHSI)/Charging Pump alternate minimum flow (mini-flow) recirculation flow-path, failed to address the single failure requirements of Nuclear Regulatory Commission Branch Technical Position ICSB 18. The design change had been implemented during the last refueling outage (4R). Actions were immediately taken to place the HHSI/Charging Pump's normal mini-flow recirculation flow-path in compliance with the Branch Technical Position by deenergizing in the open position the normally open charging pump mini-flow discharge header isolation valve 2CHS-MOV373, common to all three Charging Pumps. An evaluation was performed to determine reportability. On 3/10/94, it was determined that failure to place an electrical lockout on 2CHS-MOV373, before retiring the alternate mini-flow path in place, resulted in the plant being outside its Design Basis and therefore the event was reportable. The NRC was notified via the Emergency Notification system at 1023 hours on 3/10/94, in accordance with 10 CFR 50.72 (b) (1) (ii) (B). This written report is being submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B).
4121994003 | Beaver Valley 2 | 03/14/1994 | 04/13/1994 | 9404190374 | <strong>Operation Prohibited By Technical Specifications - Inoperable Service Water System</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1994, while returning the train A service water pump to service, Technical Specification 3.0.3. was inadvertently entered for under 1 hour. The cause of this event was an improper testing sequence that resulted in securing the only operable service pump (2SWS-P21B) prior to completing testing on the pump being returned to service (2SWS-P21A). There were no safety implications due to this event. Sufficient service water flow was maintained on both trains of the service water system. Test results finalized after the event proved that the involved pumps were operable. Because Technical Specification 3.0.3 was entered, this event is being reported in accordance with 10CFR50.73.a.2.i.B as a condition prohibited by Technical Specifications.
4121994004 | Beaver Valley 2 | 03/15/1994 | 04/12/1994 | 9404180243 | <strong>Inadvertent ESF Actuation During Solid State Slave Relay Testing</strong><br /><i>Abstract:&nbsp;</i>During performance of a Solid State Protection slave relay actuation test, an Engineered Safety Feature actuation occurred when an incorrect test switch was actuated. Surveillance testing was being performed on relays associated with the Safety Injection (SI) System due to recent realignments of the Service Water (SW) pumps, which receive a start signal from an SI signal via the slave relays. On 3/15/94, pump alignments were performed to permit SI Train A relay testing for SW pump 2SWS*P21A. A test procedure was being utilized by a licensed operator to actuate a test switch in the Train A relay test cabinet. After successful Train A relay testing, pump realignments were performed to permit SI Train B relay testing of the Train B supply breaker for SW pump 2SWS*P21C. The same licensed operator was assigned to actuate the relay test switch in the Train B relay test cabinet, again using a test procedure. When the operator went to perform the test, he inadvertently opened the door to the Train A test cabinet and actuated the Train A test switch which started the Train A containment hydrogen analyzer (an ESF actuation). Other equipment associated with the Train A relays did not actuate as they were properly removed from service. operations personnel reset the Train A actuation signal and following supervisor event review, the Train B slave relay test was completed correctly.
4121994005 | Beaver Valley 2 | 04/07/1994 | 05/06/1994 | 9405090195 | <strong>Improper Locking of Charging Suction Valve</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1994, the chain locking mechanism on a Charging Pump Suction Isolation Valve, 2CHS*MOV8130A, was found broken. This valve is one of four series on valves that can be aligned to provide separate suction flowpaths following a loss of coolant accident. This valve is normally locked and de-energized in the open position. The chain was found routed through the valve yoke such that when the valve was energized and closed, the chain was stressed and broken. In addition, the valve handwheel stem was bent. The last valve closure occurred on 10/23/93 in support of a tag-out evolution and it appears that this valve stroke stressed and fractured the chain. Technical Specifications require this valve to either be locked in the open position or verified open by surveillance once every 31 days. A new chain was immediately placed on the valve handwheel and routed such that valve stroking will not interfere with the chain. All padlocked motor operated valves outside containment were inspected and found to have the chain locking mechanism routed in the correct manner. There were no safety implications as result of this event. The Charging Pump Suction Isolation Valve , 2CHS*MOV8130A, was maintained de-energized in the open position throughout the time period when the locking mechanism was believed to be degraded.
4121994006 | Beaver Valley 2 | 06/03/1994 | 07/01/1994 | 9407060099 | <strong>ESF Actuation - Auxiliary Feedwater Pump Start During Residual Heat Relief Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1994, at 2200 hours, with the unit in mode 3, the Steam Driven Auxiliary Feedwater (AFW) Pump started due to low level in the 'C' Steam Generator. The low level resulted from closing the Residual Heat Release (RHR) Valve following check valve testing. Closing the RHR valve caused the level to decrease (shrink) in the 'C' steam generator to the low low level automatic AFW Pump start setpoint. <br /><br /> There were no safety implications due to this event. All engineered safety systems functioned as designed. <br /><br /> This event was reported in accordance with 10CFR50.72(b)(2)(ii) as an event that resulted in an automatic actuation of an engineered safety feature.
4121994007 | Beaver Valley 2 | 06/11/1994 | 07/11/1994 | 9407140180 | <strong>ESF Actuation - Feedwater Isolation Due to Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1994 at 0741 hrs, with the unit in mode 3 and 380 degrees F, a Feedwater Isolation (FWI) signal automatically initiated due to high - high water level in 'A' steam generator. The high - high level resulted when operators opened the 'A' Main Steam Line Isolation Valve (MSIV). Opening the 'A' MSIV, with steam generator narrow range level approximately 46% narrow range level, caused indicated level to 'swell' (increase) above the steam generator water level high - high FWI setpoint, initiating the Engineered Safety Feature (ESF) actuation.<br /><br /> Steam generator 21A level was restored to normal. The only feedwater equipment in service at the time of the FWI were the containment feedwater isolation valves and main feedwater bypass flow control valves, which were reopened upon reset of the FWI signal. <br /><br /> There were no safety implications due to this event. All engineered safety systems functioned as designed. <br /><br /> This event was reported in accordance with 10CFR50.72(b)(2)(ii) as an event that resulted in an automatic actuation of an engineered safety feature.
4121994008 | Beaver Valley 2 | 06/15/1994 | 07/15/1994 | 9407190282 | <strong>PORV - Inoperability - Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1994 at 1015 hrs, with the unit at 100% power, a pressurizer Power Operated Relief Valve (PORV) 2RCS-455D was removed from service for minor seat leakage using plant procedures. The PORV block valve was closed in accordance with Technical Specification 3.4.11.a. In addition, heat trace was de-energized in accordance with plant procedures. <br /><br /> On June 16, 1994 at 1440 hrs, the valve was additionally determined to be inoperable due to the heat trace being de-energized. Power was then removed from its associated block valve in accordance with Technical Specification 3.4.11.b <br /><br /> Since Technical Specification 3.4.11.b requires power be removed from the associated block valve within 1 hour and power was not removed until the following day, a condition prohibited by Technical Specifications resulted. <br /><br /> There were no safety implications due to this event. Heat Trace is required to minimize downstream piping stress during PORV discharge. Because the PORV block valve was closed, no discharge to downstream piping could occur. <br /><br /> This event is being reported in accordance with 10CFR50.73(a)(2)(i)B as a condition prohibited by Technical Specification.
4121994009 | Beaver Valley 2 | 08/12/1994 | 09/09/1994 | 9409220069 | <strong>Condition Prohibited by Technical Specifications- Inoperable Recirculation Spray System Pump</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1994, with the Unit at 100 percent power, the 'A' Recirculation Spray System (RSS) Pump (2RSS-P21A) was declared inoperable when it was determined that the pump could not meet the Technical Specification (TS) Surveillance requirement for differential pressure at the required flow. The inability of 2RSS-P21A to meet this flow requirement was discovered during the process of evaluating prior RSS performance. An inconsistency was discovered between the calibration curves for the RSS Pump flow elements and their associated flow transmitters. The inconsistency produced a higher than actual flow measurement for the RSS pumps during surveillance tests. Correction of the calibration data resulted in a revised predicted flow for 2RSS-P21A. When the corrected data was projected along the pump performance curve, it yielded a differential pressure less than that required by TS, at the TS required flow. Data obtained from the other RSS Pumps (2RSS-P21B, C, & D), was corrected for the same concern and the pumps were found to be acceptable. A TS amendment has been approved and implemented permitting continued plant operation until the next refueling outage, or until an outage of an expected duration of 30 days or greater. This written report is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant Technical Specifications.
4131994001 | Catawba 1 | 01/11/1994 | 02/10/1994 | 9402280032 | <strong>Turbine/Reactor Trip Due To Low Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1994, at 2258 hours, a Unit 1 Reactor (Rx) trip occurred due to a main Turbine trip on low condenser vacuum. Unit 1 was in Mode 1, Power Operation, at 989. power, when a two inch 'B' heater extraction line sheared off approximately six feet from entry into 'A' condenser, resulting in a loss of vacuum to 'A' condenser. The cause of the sheared extraction line was fatigue failure as a result of vibration over an extended period of time. Corrective actions included repairing the 'B' heater extraction line and examination of other extraction lines on both units. Engineering is evaluating options to reduce the amount of vibration on the extraction lines. Following the Rx trip, a main feedwater (CF) isolation occurred as a result of the Rx trip with low Reactor Coolant average temperature (Tave). Both motor driven auxiliary feedwater system pumps autostarted as expected, when three out of four CF isolation valves closed within two minutes of turbine load decreasing below 40%. A P-12 (Lo-Lo Tave) actuation occurred when one bank of steam dump valves opened causing Tave to decrease below the P-12 setpoint of 553 degrees F. The cause of the P-12 actuation is that a procedure step was not followed correctly. A contributing cause was controller windup due to a pressure transmitter that was reading higher than expected. Corrective actions include meeting with all Control Room Operators to discuss procedure adherence, controller windup, changes to Emergency Procedures that will provide more detail for transferring to the pressure control mode, and performing a calibration on the pressure transmitter.
4131994002 | Catawba 1, Catawba 2 | 02/03/1994 | 03/07/1994 | 9403160141 | <strong>Missed Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1994, Unit 1 and Unit 2 were in Mode 1, Power Operation. While reviewing the Technical Specification (T/S) surveillance requirements for Reactor (Rx) Trip Instrumentation, it was discovered that the monthly Analog Channel Operational Tests (ACOT) for the Power Range (P/R) Neutron Flux Low Setpoint and Intermediate Range (I/R) Neutron Flux Instrumentation (NIS) had not been performed prior to entering the applicable condition/mode. All other NIS surveillance tests were performed as required. In situations where the unit had been operating above P-10 for more than 30 days since the last NIS ACOT with conditions that require the power level to be reduced and maintained below P-10, the I/R ACOTs and P/R Neutron Flux Low Setpoint ACOTs had expired. The I/R ACOTs and P/R Neutron Flux Low Setpoint ACOTs are to be performed when Rx power is reduced to and maintained below P-10. The T/S Limiting Condition for Operation requires that the NIS I/R be operable along with the P/R low setpoint when the respective unit is in Mode 2, Startup, and in Mode 1, below the P-10 setpoint. This incident is attributed to change management. Corrective actions include a determination of the ACOT requirements along with T/S clarification.
4131994003 | Catawba 1, Catawba 2 | 02/22/1994 | 03/24/1994 | 9403290040 | <strong>Missed Technical Specification 3.3.1 Action Statement</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1994, with Units 1 and 2 in Mode 1, Power Operation, at 97,% and 50% power level respectively, Safety Assurance determined that Technical Specification (T/S) 3.3.1, Table 3.3-1, Action Statement violations had occurred. A review of Excore Nuclear instrumentation (ENB) System (NIS) Power Range channel calibration/testing documentation indicated instances in which a channel of the Over Power Delta Temperature (OPDT) reactor trip function was inoperable for greater than 6 hours without its associated OPDT bistable being placed in the tripped position as required by T/S. T/S Amendments 101/95 and 107/101 included adding current (neutron flux) differential (Delta-1) from the NIS Power Range instrumentation to the OPDT reactor trip function. This change resulted in a channel of the OPDT reactor trip function being inoperable during NIS Power Range channel calibration/testing. Per T/S, the inoperable channel must be placed in the tripped position wi 6 hours. Procedures were not updated to ensure that the affected OPDT reactor trip function bistable was placed in the tripped position during NIS Power Range - channel calibration/testing. This event is attributed to Change Management due to change related documents not being revised. Corrective action includes revisions to Operations and Instrument and Electrical (IAE) procedures, a revision to the T/S interpretation of Reactor Trip System instrumentation, and a review of Catawba Site Directive 2.1.7, T/S Amendments,to determine if enhancements associated with the review of documents associated with T/S changes are warranted.
4131994004 | Catawba 1 | 03/18/1994 | 04/18/1994 | 9404250079 | <strong>Missed Technical Specification 3.4.6.1 Action Statement</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1994, at 1735 hours, Unit 1 was in Mode 1, Power Operation, at 97% power. During a procedure completion review, Operations personnel discovered that the minimum number (two) of Reactor Coolant (NC) System Leakage Detection systems were not operable during the time the Operator Aid Computer (OAC) was out of service. The action statement for Technical Specification (T/S) 3.4.6.1 states that with less than two of the three NC Leakage Detection systems operable be in at least Hot Standby within the next six hours. With the OAC out of service for six hours and 41 minutes, the six hours action statement was violated. This was discovered after the OAC was returned to service. The cause of this event is attributed to less than adequate written communication associated with Leakage Detection System instrumentation documentation. After the event, Engineering performed a past operability review and determined that the NC Leakage Detection Systems were past inoperable. Corrective actions included providing instructions to Operations describing actions to take for each NC Leakage Detection system when the OAC is out of service, revising setpoints for Radiation Monitor EMF39, OAC program change, and revising the Loss of OAC procedure, T/S Interpretation, Final Safety Analysis Report (FSAR), and Design Basis Documents.
4131994005 | Catawba 1, Catawba 2 | 04/25/1994 | 05/26/1994 | 9406010245 | <strong>Technical Specification 3.7.6 Limits Exceeded Due To Procedure Problems</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1994 at 0300 hours, with Units 1 and 2 in Mode 1, Power Operation, at 100 % power, the Limiting Condition for Operation for Technical Specification (T/S) 3.7.6 Action Statement for Mode 1 operation was exceeded due to the 'A' Train Control Room Area Ventilation System being inoperable for greater than seven days. While performing routine maintenance, technicians found a damaged microswitch in the chiller's program timer. The microswitch was replaced. Upon completion of maintenance, a functional test of the chiller was performed. Due to the unique functional characteristics of the timer, the scope of the testing was inadequate to ensure that the program timer would perform all of its intended functions. running with the chiller off. Technicians found the program timer was not in its expected position due to the recently installed microswitch being misaligned. The program timer was reset, properly aligned the microswitch, and performed an appropriate functional verification. This event is attributed to specific procedures not being provided to perform maintenance and testing on the program timer. A contributing cause was that an intended continuity verification was not performed. Corrective actions include changes to the troubleshooting procedure, evaluation of the need for other procedures for the chiller's control circuit, development of procedures for the chiller's control circuit, including the program timer and changes to the System Directive for Post Maintenance Test.
4131994006 | Catawba 1, Catawba 2 | 10/18/1994 | 11/17/1994 | 9411220261 | <strong>Technical Specification 3.0.3 Entered Due To Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1994, at 0438 hours, with Unit 1 and Unit 2 both in Mode 1, Power Operation, at 100 percent power, Operations tagged out Train B of the Control Room Ventilation and Chilled Water (VC/YC) System. At 0830 hours, Technical Specification 3.0.3 was unknowingly entered when maintenance opened access panels on B Train VC/YC to begin routine maintenance. Outward air flow through the open access panels as a result of an unsecured backdraft damper created a bypass leakage flowpath, causing the running VC/YC Train A to be inoperable in that it was not capable of adequately pressurizing the Control Room. The access panels were closed at 0940 hours and Technical Specification 3.0.3 was exited. This event is attributed to work practices, in that a Non-Licensed Operator chose an inappropriate tagged position for the backdraft damper during the development of a 'preplan' tagout. Corrective actions include Operations' management review of key aspects of this event with all operators to ensure a clear understanding of their responsibilities when tasks cannot be completed as required.
4131994007 | Catawba 1, Catawba 2 | 06/08/1994 | 07/07/1994 | 9407130294 | <strong>Missed Technical Specification Surveillance 4.7.6.b Due To Work Practices</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1994, at 0830 hours, with Unit 1 in Mode 1, Power Operation, at 100% power, and Unit 2 in Mode 5, Cold Shutdown, Operations discovered during a review of the Periodic Test (PT) Database Past Due Report that the surveillance interval had been exceeded for Technical Specification (T/S) Surveillance 4.7.6.b for Train A of the Control Room Area Ventilation (VC) System and Control Room Chilled Water (YC) System. The VC/YC Train A outside air pressure filter train surveillance interval was exceeded on June 2, 1994, at 1155 hours. The periodic test was successfully performed and VC/YC Train A was declared operable at 2315 hours on June 8, 1994. This event is attributed to Work Practices, intended or required verification not performed. Error detection practices were not adequately performed during reviews of the PT Database Past Due Report to identify that periodic testing of VC/YC Train A had not been performed. A contributing cause of inadequate Verbal Communication is also assigned due to miscommunication leading to testing VC/YC Train B rather than Train A on May 22, 1994. Corrective action includes the Unit Lead personnel (Operations Test Coordinators) and Operations PT Crew being instructed to thoroughly review the PT Database Past Due Report to identify PTs requiring performance, a review of the PT Database Past Due Report during Operation's daily meeting, inclusion of this event into Operation's proficiency training, and including T/S periodic testing into the Work Management System (WMS).
4131994008 | Catawba 1 | 07/14/1994 | 08/12/1994 | 9409150046 | <strong>Missed Technical Specification Surveillance Due to Improper Work Practices</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1994, Unit 1 was in Mode 1, Power Operation, at 100 percent power. A Nuclear Regulatory Commission (NRC) inspector performing a Nuclear Service Water (RN) system valve checklist walkdown as part of the Service Water System Operational Performance Inspection (SWSOPI) identified that RN valves 1RN-E13 and 1RN-E14 were properly positioned but not properly secured (Pinned Open) as required per procedure OP/0/A/6400/06C, Enclosure 4.3. Further evaluation determined that only valve 1RN-E14 was not properly secured and did not meet the surveillance requirements of Technical Specification 4.7.4. This event is attributed to Work Practices; System alignment, ragout, restoration not verified. Appropriate verification of the specified return position of valve 1RN-E14 was inadequately performed during the restoration portion of maintenance Removal and Restoration (R&R) tagout 13-2954. Subsequent corrective action included properly securing valve 1RN-E14 and verification of all locked and administratively controlled valves. Planned corrective action will include revising the monthly valve verification procedure (PT/1/A/4400/02C) to incorporate valves 1RN-E13 and 1RN-E14 into the checklist.
4141994001 | Catawba 2 | 05/17/1994 | 06/23/1994 | 9406290158 | <strong>Technical Specification Violation Due To An Inoperable Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1994, with Unit 2 in No Mode, Defueled, Eddy Current Testing (ECT) data was obtained and subsequently analyzed for Steam Generator (S/G) 2B tube 41-64. The analysis determined that this tube exceeded the 40% Technical Specification (T/S) through wall limit and required plugging. ECT data for tube 41-64 from the Unit 2 End Of Cycle 5 (2EOC5) refueling outage was obtained and reviewed, which revealed that the tube exceeded the T/S limit during that outage and should have been plugged prior to entering Mode 4, Hot Shutdown. As a result of a missed S/G tube indication discovered in August 1993 at the Duke Power McGuire Nuclear Station by the ECT analysis group, a Quality Improvement Project (QIP) was chartered to review the ECT analysis process and provide recommendations for improvement. This incident is attributed to less than adequate work practices and error detection practices. Corrective actions taken include analysis of the 2EOC5 data for S/G 2B tube 41-64 and plugging of the subject tube during 2EOC6. To prevent recurrence of this problem, the recommendations of the QIP will be implemented.
4141994002 | Catawba 2 | 06/15/1994 | 11/07/1996 | 9611210029 | <strong>Reactor Trip Breakers Opened Due To Component Failure</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1994, at 1340 hours, Unit 2 Reactor Trip Breakers (RTBs) were manually opened due to an intermittent component failure of the Rod Control (IRE) System Group 'C' Firing Card. Unit 2 was in Mode 5, Cold Shutdown, performing Digital Rod Position Indicator (DRPI) Alignment and Functional test. The Rod Control Bank Selector Switch was selected to Shutdown Bank (SDB) 'B' and the Control Room Operator (CRO) began withdrawing rods on SDB 'B' with the demand counters indicating that both groups of rods for SDB 'B' were withdrawing. When the rods got to the point (6 steps) to receive the first DRPI light-emitting diode (LED), DRPI indicated that rods in group 2 of SDB 'B' and group 1 of Control Bank (CB) 'D' were six steps withdrawn. The CRO immediately inserted all rods and opened the RTBs. 'D' withdrawing at the same time is attributed to an intermittent component failure in the IRE System Group 'C' Firing Card. Corrective Action included replacing the failed Firing Card, testing the remaining Firing Cards in stock, and adding a procedure step to verify that the correct Group Select Lights are illuminated on the IRE System Power Cabinets before rods are withdrawn.
4141994003 | Catawba 2 | 07/10/1994 | 08/12/1994 | 9408180156 | <strong>Manual Reactor Trip on Loss of Normal Feedwater Due to System Performance</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1994, at 1347 hours with Unit 2 in Mode 1, Power Operation, at 100% power, a turbine runback occurred following manual trip of a malfunctioning Main Feedwater Pump (CFP). Following the runback, a loss of Main Feedwater (CF) occurred, caused by one of the Steam Generator's (S/G) levels reaching the 'High-High' level ESFAS Interlock Setpoint. This resulted in ESFAS actions to trip the Main Turbine (MT), trip both CFPs, and isolate CF. Tripping of both CFP initiated an ESFAS signal to start both Motor Driven Auxiliary Feedwater Pumps. No automatic reactor trip signal was initiated because the unit was below the Reactor Trip on Turbine Trip Interlock Setpoint. The reactor was manually tripped at 1355 hours from 65% power. The unit was stabilized in Mode 3, Hot Standby, using 'Reactor Trip Response' Emergency Operating Procedure. The Root Cause of this event is attributed to the performance of the CF System following level recovery from low S/G levels. The initial trip investigation did not reveal any anomalies in the response of the S/G Level Control System. Following restart, additional information indicated the need for continuing evaluation of the S/G Level Control System performance. The performance of the S/G Level Control System transient response is a unit availability/reliability concern and not a nuclear safety issue. Corrective actions include evaluation of secondary systems interactions and responsiveness of the S/G Level Control System including the CF Control Valves.
4141994004 | Catawba 2 | 08/30/1994 | 09/29/1994 | 9410050204 | <strong>Missed IWV Stroke Time Tests Due to Written Communication</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1994, with Unit 2 in Mode 1, Power Operation, at 100% power, missed inservice valve (IWV) stroke time tests for valves 2KC82B and 2NM200B were discovered during an Engineering self assessment. These valves received quarterly IWV stroke time tests on June 12, 1994, and were identified as having an increase in stroke times greater than the allowable limit specified in the American Society of mechanical Engineers (ASME) Boiler and Pressure Vessel Code, Section XI, Subsection IWV-3417. The use of this code is specified in Technical specification 4.0.5. Per the requirements of Subsection IWV-3417, the test frequency of these valves shall be increased to monthly until corrective action is successfully completed. The test frequency of these valves was not increased. Due to a procedure revision, the normal expectations of which Station group was responsible for initiating the increase in test frequency was changed. This event is attributed to Written Communication, omission of relevant information. This event has also been assigned a contributing cause of work Practices, required verification not performed, due to untimely review of the IWV stroke time documentation. Corrective action included IWV stroke time testing of the valves and increasing the test frequency of the valves to monthly. Planned corrective action includes revising the affected procedures, additional training for System Engineers concerning management's expectations for timely reviews of completed test documentation, and an industry review to identify improvements for Catawba's T/S surveillance program.
4141994005 | Catawba 2 | 08/30/1994 | 09/27/1994 | 9410060012 | <strong>Reactor Trip Due to a Drawing Error</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1994 at 2130 hours, Unit 2 Reactor (Rx) Trip occurred while maintenance personnel were investigating the cause of the Reactor Trip/Safety Injection events recorder point being in alarm. Unit 2 was in Mode 1, Power Operation at 100% power. As a part of investigating the cause of the alarm a maintenance technician determined that it would be necessary to open a sliding link. The link as shown on the drawing used by the technician should have been in the Rx Trip/ Safety Injection events recorder point circuitry; however, it was actually in the Manual Safety Injection/Reactor Trip circuitry. This is the circuit that supplies 48 volts direct current (vdc) from the Solid State Protection System (SSPS) to the undervoltage trip coil for the Reactor Trip Breaker (RTB). When the link was opened, the 48vdc was removed from the RTB undervoltage (UV) trip coil resulting in an UV trip immediately followed by a shunt trip induced by the UV coil tripping and a Rx Trip. The subsequent investigation revealed that the wrong link was opened due to being incorrectly identified on the drawing. This event is attributed to less than adequate work practices in that self-checking was not properly applied because the error was not recognized during an earlier revision to the drawing. Corrective actions include revising the drawing, changes to the Engineering guideline for checking drawings, and evaluation of the troubleshooting process.
4141994006 | Catawba 2 | 09/13/1994 | 10/04/1994 | 9410130105 | <strong>Reactor Trip Due to Closure of a Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1994, at 1854 hours, Unit 2 was in Mode 1, Power Operation at 100% power, when an automatic Reactor/Turbine Trip occurred on Over Power Differential Temperature after the Main Steam Isolation Valve (MSIV) for 'C' Steam Generator closed unexpectedly. Following the trip, a main feedwater system isolation occurred as a result of a Reactor Trip with low Reactor Coolant System average temperature. Auxiliary Feedwater (CA) System motor driven and turbine driven pumps autostarted as expected, due to lo-lo Steam Generator levels. Letdown isolation occurred due to Pressurizer level decreasing below 17% as a result of cooldown caused by CA system operation. The root cause of this event is equipment failure. The MSIV closure was caused by the failure of an auxiliary relay in the control circuit for the MSIV. A short circuit occurred in a normally energized coil in a Series D26 Cutler Hammer relay. Corrective actions included replacing the relay and evaluating the failure rate of these types of relays to determine if similar relays needed to be replaced. Engineering concluded that this failure was a random failure. During the event, the control room operators entered the correct emergency response and abnormal procedures and performed the required steps to maintain the plant in a safe shutdown condition. All safety systems responded as designed to shutdown the Reactor and maintain it in a safe shutdown condition.
4141994007 | Catawba 2 | 10/18/1994 | 11/17/1994 | 9411220344 | <strong>Reactor Trip and Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1994 at 0955 hours, with Unit 2 in Mode 1, Power Operation Trip, at 100% power, a Reactor Trip occurred. Two Instrumentation and Electrical (IAE) teams were performing independent tests on components of the Reactor Trip System when both trains of the Solid State Protection System (SSPS) received General Warning indications, causing the Reactor Trip Breakers to open. The Train B General Warning was expected; the Train A General Warning occurred unexpectedly when an IAE technician moved the SSPS Train A multiplexer test switch through 'Inhibit'. Document Use Practices, with a contributing cause of less than adequate Management Directions. Corrective actions for the Reactor Trip include communication of expectations for procedure use, philosophies for cross train work, and identifying uncompleted work to Work Control. Following the trip, with Unit 2 in Mode 3, Hot Standby, the Auxiliary Feedwater (CA) Pumps were secured and the discharge flow control valves for the Motor Driven Pumps (2A and 2B) were closed. On October 21 at 0435 hours, with Unit 2 in Mode 1 at 100% power, an operator discovered during a routine Control Board walkdown that the valves were closed. Subsequent investigation revealed the CA system had not been placed in standby readiness per the operating procedure after the system was secured. The root cause of this event is due to Written Communication, with a contributing cause of less than adequate Work Practices. Corrective actions for the closed CA valves include procedure revisions and clarifying/communicating a clear philosophy on operator responsibilities.
4161994001 | Grand Gulf 1 | 01/27/1994 | 02/24/1994 | 9403070029 | <strong>Technical Specification Log Readings not Taken Within Required Time Period</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1994, at 1215, Control Room operators discovered that they had failed to take log readings required by Technical Specifications (TS) and a site Surveillance Procedure. Since some of these log readings are required to be taken every four hours and were over four hours past due, the 25% grace period allowed by TS 4.0.2 was exceeded and the event is reportable per 10CFR50.73(a)(2)(i).<br /><br /> Immediate action was to take the overdue log readings which were completed at 1250. This resulted in no readings that were out of specification. The plant remained in a stable condition at 80% power throughout the event. The decreased power level was due to inclement weather conditions. This incident did not degrade the ability of plant systems or equipment to perform their intended function.<br /><br /> The Grand Gulf Nuclear Station (GGNS) Root Cause Analysis Group identified the root causes to be less than adequate personal accountability for assigned responsibilities on the part of the licensed operator and inadequate verbal communication between licensed operators on shift concerning how they would share assigned tasks. Corrective actions include discipline of the responsible licensed operators per company policy. Also, a Shift Supervisor sign-off will be added to the site Surveillance Procedure verifying timely completion of logs. <br /><br /> The missed log readings did not compromise the safe operation of GGNS Unit 1. The safety and health of the general public were not compromised by this event.
4161994002 | Grand Gulf 1 | 02/25/1994 | 06/28/1996 | 9607030178 | <strong>Supplements to LER 94-002 "ESF Switchgear Room Temperature Could Exceed Allowable Limits"</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1994, Design Engineering personnel identified that temperatures in four ESF Switchgear rooms would exceed previously evaluated values during post-LOCA conditions if the associated room cooler was not in operation. The condition identification was based on calculations of ventilation cooling loads. The availability of equipment in these rooms could not be guaranteed. Specific actions, which are commensurate with this condition, were implemented to address room coolers being out of service. <br /><br /> An investigation revealed that non-conservative assumptions were made in the original design calculation performed by the Architect/Engineer. The original calculation did not address all heat loads that would be expected during accident conditions, i.e., created by certain electrical cables, space heaters, etc. Subsequent reviews of this condition and reporting requirements revealed that this condition did not meet the criteria of a reportable condition. The health and safety of the public are not compromised as a result of this condition.Therefore, the reportable of status this Licensee Event Report is being changed to voluntary.
4161994003 | Grand Gulf 1 | 03/10/1994 | 04/11/1994 | 9404200008 | <strong>Degradation of Fasteners on the Standby Service Water (SSW) Pump Coupling</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1994, unacceptable vibration readings were obtained while conducting a routine run of the 'B' Standby Service Water (SSW) pump and the subsystem was declared inoperable. Discretionary enforcement was granted on March 4, 1994, to extend the 72 hour Technical Specification LCO to 7 days. Inspection of the pump revealed deterioration of the coupling bolts and washers which caused the impeller to rub into the wear rings resulting in premature and excessive wear of the pump bowl and impeller. Repairs were completed and the pump declared operable on March 7, 1994.<br /><br /> Testing indicated the 'A' pump met all vibration and performance criteria. However, since the 'A' and the 'B' pumps are the same type, the 'A' pump was also taken out of service on March 10, 1994, for inspection. This inspection revealed similar deterioration but not to the extent found in the 'B' pump. The damage was repaired and the pump declared operable on March 11, 1994. <br /><br /> Long term corrective actions are: <br /> -Incorporate a preventive maintenance program which includes total lift readings, vibration trending analysis and a periodic inspection. <br /> -Evaluate changing present coupling assembly to stainless steel bolt/washer material. <br /><br /> The plant remained in a stable condition at 100% power throughout the event. This event could have eventually resulted in a condition that alone might have prevented the fulfillment of the SSW system safety function. This incident did not degrade the ability of other plant systems or equipment to perform their intended function. The safety and health of the general public were not compromised by this event. This condition is reportable per 10 CFR 50.73(a)(2)(v).
4161994004 | Grand Gulf 1 | 03/26/1994 | 04/26/1994 | 9405030317 | <strong>Multiple Control Rods Failing Technical Specification Scram Time Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1994, scram time testing was being performed which found five slow rods. Although these failures did not constitute a violation, the plant was ordered shutdown in consideration of Technical Specification 3.1.3.2 Action c.1. An additional 163 control rods were analyzed at 0001 on March 27, 1994, when the reactor was manually scrammed and scram times recorded. Of these rods, 44 additional rods were slow moving but all were satisfactory for insertion to position 13. <br /><br /> The cause of the slow moving control rods was determined to be contamination of the internal surfaces of the scram solenoid pilot valve head assemblies. A thread sealant used during maintenance on the valves caused the seats in the top head assembly to adhere slightly to adjacent surfaces resulting in a delay in the initial opening of air exhaust ports. In its uncured state, the sealant attacked the viton seats and may have caused metallic moving parts to stick. <br /><br /> Immediate remedial actions included installing the pilot valve top head assemblies using a thread sealant tape rather than the sealant previously used and using an approved detergent to clean 193 new assemblies. Long term corrective actions are: evaluate training maintenance personnel on proper use of various thread sealants, write generic procedure on proper use of various thread sealants and evaluate, in other applications, the use of sealants and other similar generic materials. <br /><br /> A review of operating data determined that all safety systems behaved as expected. This incident did not degrade the ability of other plant systems or equipment to perform their intended function. The safety and health of the general public were not compromised by this event.
4161994005 | Grand Gulf 1 | 05/17/1994 | 06/14/1994 | 9406200325 | <strong>Failure to Adequately Incorporate Existing Design Into GGNS Operating and Emergency Procedures</strong><br /><i>Abstract:&nbsp;</i>During containment pressurization for the Integrated Leak Rate Test during Refueling Outage Six, substantial leakage was found and was determined to be from the Drywell Fission Product Monitor and Post Accident Sample System sample lines. The lines were isolated and the Integrated Leak Rate Test was completed on November 21, 1993. A Material Non-Conformance Report was written to document the leakage problem. During the evaluation, it was discovered that there was no clear guidance to close the containment isolation valves for the Drywell Fission Product Monitor and Post Accident Sample System when required post-accident. This condition is reportable per 10 CFR 50.73(a)(2)(ii)(C). <br /><br /> The apparent cause of the condition is failure to adequately incorporate the existing design into GGNS operating and emergency procedures. The dual function of the line supplying the Drywell Fission Product Monitor and Post Accident Sample Systems apparently caused a procedural oversight.<br /><br /> Corrective actions include generating a Minor Change Package to incorporate the auto-isolate feature on the subject penetration isolation valves and evaluating other potential containment post-accident bypass leak paths. <br /><br /> Conservative analyses based on as-found leakage rates confirmed that the safety and health of the general public were not compromised by this condition.
4161994006 | Grand Gulf 1 | 05/28/1994 | 07/22/1994 | 9408010218 | <strong>Update to Voluntary Report Due To Slow Scram Times of Multiple Control Rods</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1994 during scram time testing of control rods, plant personnel identified that the scram times (to notch 43) for two control rods were not acceptable as defined by GGNS Technical Specifications. The two failures only constituted 10 percent of the random sample of rods which is an acceptable number of failures as specified by GGNS TS. Therefore, further testing was not required by GGNS TS. However, testing continued due to recent concerns with delayed operation of the scram pilot valves identified on March 26, 1994 and reported in LER 94-004, dated April 26, 1994. Subsequently, all control rods were tested. Out of all rods tested, 38 had unacceptable scram times. As a part of the continued testing, pilot valves associated with slow rods were reworked, retested and returned to service. All TS requirements were met during testing. Based on current fuel exposure, an engineering evaluation indicated that the Minimum Critical Power Ratio safety limit would not have been exceeded as a result of the observed scram times. Therefore, the health and safety of the public were not compromised as a result of this condition. <br /><br /> The malfunction is believed to be the retarded release of the disc material from the seating surface in the upper valve body. Subsequent test results indicate that the elastomer disc material is different from the disc material in pilot valves and rebuild kits installed prior to RF06. The affected valves have been reworked using a more reliable top head assembly vintage. Rebuild kits or top head assemblies manufactured after 1989 appear to be suspect. <br /><br /> Even though this condition does not meet reporting criteria as specified in 10 CFR 50.73, it is being submitted as a voluntary event report. pursuant to 10 CFR 21.
4161994008 | Grand Gulf 1 | 07/27/1994 | 08/26/1994 | 9409010301 | <strong>Voluntary Report of Inadequate Thermo-Lag Installations</strong><br /><i>Abstract:&nbsp;</i>In accordance with NRC Bulletin 92-01 and as part of Grand Gulf Nuclear Station's (GGNS) efforts to resolve generic issues related to Thermo-Lag 330 fire retardant material, detailed walkdowns and destructive tests were conducted. These efforts revealed instances where Thermo-Lag is not installed in strict conformance with GGNS installation guidelines. As a result of these deficiencies, GGNS conservatively made a one hour telephone notification in accordance with 10CFR50.72(b)(1)(ii)(B). After further consideration, these particular deficiencies in GGNS Thermo-Lag (similar to generic issues presently being evaluated by the NEI Thermo-Lag initiative), only warrant voluntary notification. <br /><br /> Hourly fire watches were initiated in mid 1992 due to generic Thermo-Lag concerns (NRC Bulletin 92-01), and have continued to date. No adverse effects resulted from the period of operation prior to the hourly fire watch being established. Considering the availability of fire detection and suppression systems, as well as the hourly fire watch, this condition should not adversely impact public health and safety. <br /><br /> Resolution of these deficiencies have been incorporated into the ongoing Thermo-Lag requalification effort. <br /><br /> This is being submitted as a voluntary report.
4161994009 | Grand Gulf 1 | 09/29/1994 | 02/17/1995 | 9502240285 | <strong>Technical Specifications Violation Due to Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1994, Entergy Operations, on behalf of Grand Gulf Nuclear Station (GGNS) informed the NRC of a deficiency discovered during an ongoing review of surveillance procedures in preparation for implementation of GGNS Improved Technical Specifications (TS). This deficiency was the result of a procedural inadequacy which failed to test one of four sets of contacts in the 'B' Containment Spray Train high drywell pressure initiation logic. In that submittal a commitment was made to submit any additional deficiencies discovered, during this review as supplements to LER 94-009-00.<br /><br /> On January 18, 1995, an additional deficiency was discovered. This deficiency resulted from the failure to verify the Average Power Range Monitor flow biased simulated thermal power-high time constant for all 8 channels on an eighteen month frequency as specified by GGNS Reactor Protection System TS 4.3.1.1. Therefore, this report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B) as supplement 01 to LER 94-009-00. <br /><br /> Upon discovery of these conditions, the requirements of TS 4.0.3 were entered and the surveillances were successfully completed. Additionally, deficiency reports were initiated to address these events. <br /><br /> The above deficiencies did not adversely impact the performance of systems important to safety. Therefore, the health and safety of the public was not compromised.
4161994010 | Grand Gulf 1 | 09/30/1994 | 10/20/1994 | 9411010339 | <strong>Potential Breach of Control Building Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>During a walkdown of Control and Auxiliary Building pressure doors, Control Building pressure door OC312 was found propped open. Door OC312 is one of the pressure doors for the Control Building designed to withstand 3 PSID due to tornado depressurization. An evaluation of non- pressure door OC313, which is normally closed in lieu of door OC312, indicated that it could not withstand 3 PSID. Since the Off-Normal Event Procedure for Hurricanes, Tornadoes, and Severe Weather only specified that the outside doors be shut in case of severe weather, there was no way to ensure that door OC312 would be closed. <br /><br /> The apparent cause of the condition is attributed to inadequate procedural guidance. A night order was issued informing Operations of the requirement to shut the pressure door on detection of an approaching tornado. A change was initiated to the Off-Normal Event procedure which specified that door OC312 be closed on detection of an approaching tornado.
4161994011 | Grand Gulf 1 | 11/01/1994 | 12/01/1994 | 9412050260 | <strong>Reactor Scram While Performing Reactor Protection System Surveillance</strong><br /><i>Abstract:&nbsp;</i>A reactor scram occurred on November 1, 1994 while plant maintenance personnel were performing a quarterly surveillance on the reactor protection system. All control rods inserted fully and vessel level was maintained with the reactor feedwater pumps.<br /><br /> Causes of the event were determined to be the ground detection circuit for the Division 1 125 VDC system which had been modified recently in conjunction with a bolted ground fault on the Division 1 backup scram solenoid valve. The bolted fault was found to be on the negative pole lead of the solenoid located at its pigtail condulet. The modification of the ground detection circuit was determined to increase the sensitivity of system components to ground faults which could result in inadvertent actuations. While the ground detection system modification had focused on the safety design basis, it failed to consider potential operational impact such as inadvertent actuations upon postulated ground faults. <br /><br /> Immediate corrective action included repairing the bolted ground fault on the negative pole lead for the valve's coil. Also, the continuous monitoring ground detection circuit of the 125 VDC ground detection system was eliminated to preclude similar adverse consequences. Local periodic monitoring for system grounds was not affected by eliminating the continuous monitoring circuit. Long term corrective actions will evaluate modification of continuous monitoring circuits in all Class 1E DC ground detection systems. <br /><br /> This incident did not impair the ability of any system to perform its safety function. Health and safety of the public were not compromised by this event.
4231994001 | Millstone 3 | 01/20/1994 | 02/18/1994 | 9403030208 | <strong>Inadequate Overtemperature Delta T and Overpower Delta T Channel Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1994, with the plant in Mode 1 at 86% power, it was discovered that the Overtemperature Delta T (OT Delta T) and Overpower Delta T (OP Delta T) CHANNEL CHECKs were not being adequately performed every 12 hours. The method of satisfying the CHANNEL CHECK surveillance requirement for OT Delta T and OP Delta T channels included a comparison of the OT Delta T and OP Delta T trip setpoints, however, the loop Delta T channels were not included in satisfying these surveillance requirements. The OT Delta T and OP Delta T trips will actuate when any two of the four Delta T channels exceed the variable OT Delta T and OP Delta T trip setpoints. Therefore, the four Delta T channels should have been included in the OT Delta T and OP Delta T CHANNEL CHECKs to ensure the process outputs, in addition to the trip setpoints, are within an allowed tolerance. <br /><br /> There were no adverse safety consequences as a result of this event. <br /><br /> The root cause for the failure to adequately perform OT Delta T and OP Delta T CHANNEL CHECKs has been determined to be a program failure due to a procedure deficiency. Procedures did not require a channel check of the loop Delta T instruments. <br /><br /> The immediate corrective action was to perform a CHANNEL CHECK on the four Delta T channels, and to implement supplemental monitoring until a change to the Technical Specification logs was implemented. Additionally, the MODE 1 and MODE 2 Technical Specification logs have been revised to reflect this omission, and all Technical Specification CHANNEL CHECKs are being reviewed to ensure existing CHANNEL CHECK methodology is in full compliance with existing requirements.
4231994002 | Millstone 3 | 01/23/1994 | 02/18/1994 | 9403010272 | <strong>Shift Turnover Without Shift Technical Advisor Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1994, with the plant in MODE 1 at 88% power, following shift turnover at 0725 hours, the oncoming Shift Supervisor (SS) noticed that the Shift Technical Advisor (STA) was absent. As immediate corrective action the oncoming SS reviewed the shift schedule to identify the STA, and called him to report to work. The oncoming STA arrived 30 minutes later, at 0755 to provide coverage. <br /><br /> This condition is reported in accordance with 10CFR50.73(a)(2)(i)(B), as an operation or condition prohibited by Technical Specifications. Technical Specification 6.2.2. Facility Staff, requires that each on-duty shift shall be composed of at least the minimum shift crew composition (which includes the STA function). The off-going shift provided STA coverage through shift turnover, but STA coverage did not exist from the time of shift turnover until the oncoming STA arrived. <br /><br /> There was minimal safety significance because there were no plant conditions that required STA action during this period.<br /><br /> The root cause is personnel error. Work practices were not followed by the oncoming SS to ensure a full shift compliment as part of the shift turnover. As action to prevent recurrence the 'STA' position has been added to the Shift Turnover Report, for the SS to log formal STA turnover.
4231994003 | Millstone 3 | 01/25/1994 | 05/27/1994 | 9406080253 | <strong>Unlocked Manual Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1994, at 0130 hours, with the plant in Mode 1 at 88% power, the outboard containment isolation valve for the Integrated Leak Rate Test (ILRT) pressurization/depressurization line was found unlocked. The control room was immediately informed, and the valve was relocked. The valve had been unlocked to verify that it was closed before tagging it closed to support a work order for downstream maintenance. The total time between the unlocking and relocking was 4 hours 10 minutes. <br /><br /> This condition is reported as a violation of Technical Specification 4.6.1.1 which requires containment integrity to be demonstrated by verifying that all penetrations not capable of being closed by OPERABLE containment automatic isolation valves, are closed by valves, blind flanges, or deactivated automatic valves secured in their positions. The outboard isolation valve was always maintained closed and was therefore capable of performing its intended isolation function. However, while it was tagged closed for downstream maintenance, it was not locked. The condition did not have safety significance. The containment penetration was isolated by the OPERABLE key locked closed automatic inboard isolation valve, which was also always maintained closed throughout this condition. <br /><br /> The root cause was a program failure; attributable to a procedure deficiency and a management deficiency on expectations. As action to prevent recurrence, procedures have been revised and additional training and expectations are being provided.
4231994004 | Millstone 3 | 01/26/1994 | 02/23/1994 | 9403110149 | <strong>Feedwater Isolation Values Potentially Inoperable as a Historical Condition</strong><br /><i>Abstract:&nbsp;</i>On January 26,1994, with the plant in MODE 1 at 85% power, an engineering review determined that the Feedwater Isolation Valves may not have met design and Technical Specification closure requirements prior to 1989. <br /><br /> This is a report of a historical condition. It is reported as a condition outside the design basis, because there may not have always been sufficient nitrogen accumulator volume and/or pressure, which is needed for the valves to meet the closure times that are credited in the accident analysis. It is also reported as a non compliance with Technical Specifications, because the surveillance procedures may not have been adequate to determine if there was always sufficient nitrogen accumulator volume and/or pressure prior to 1989. <br /><br /> There is no current safety significance. Historically, if the valves may not have met the closure times credited in the accident analysis, then the mass and energy releases to the containment from a postulated feedwater or steamline rupture might have exceeded analyzed values, assuming a single active failure. <br /><br /> The historical concern was identified as a result of questions raised by the plant offsite safety review committee. This led to a review of the valve accumulator design adequacy. It was determined during the engineering review on January 26,1994, that the design deficiency could have existed, and the NRC was promptly notified. <br /><br /> The root cause involved program failure and an inadequate design of the original Feedwater Isolation Valve nitrogen accumulator. No corrective actions are needed because design changes and procedure changes were made that have precluded the potential condition since 1989.
4231994005 | Millstone 3 | 02/10/1994 | 03/11/1994 | 9403160089 | <strong>Inoperable Containment Drain Sump Level and Pumped Capacity Monitoring System Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1994, with the plant in MODE 1 at 100% power, it was discovered that the Containment Drain Sump Level and Pumped Capacity Monitoring System was not performing in accordance with the Bases of Technical Specifications (TS). A conservative determination and prompt report was subsequently made as a condition being outside the design basis described in the Final Safety Analysis Report (FSAR). <br /><br /> The condition has historically existed since the first cycle of plant operation because the system was not capable of promptly detecting a one gallon-per-minute change in unidentified leakage within one hour, which is a sensitivity/response requirement. <br /><br /> The condition had low safety significance because the leakage was being monitored once per shift, which met the TS surveillance interval requirements, and a change in leak rate of 1 gpm would have been identified during the surveillance. In addition, there is a Containment Atmosphere Gaseous and Particulate Radioactivity Monitoring System for monitoring Reactor Coolant System Leakage. <br /><br /> The root cause of the condition was personnel error in change management. Changes in the operation of the system missed the requirements in the FSAR. As corrective action the TS Action Statement was entered, and the original sump/pump was placed back into service after making design and procedural improvements. As action to prevent recurrence: there is an ongoing procedure upgrade program, the process for changing setpoints has been improved, and a policy is being developed for evaluating alternate plant configurations.
4231994006 | Millstone 3 | 03/15/1994 | 04/14/1994 | 9404190074 | <strong>Auxiliary Feedwater Pipe Restraints Inadequate Design Due to Design Error</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1994, with the plant in MODE 1 at 100% power, an engineering review determined that portions of the Auxiliary Feedwater (AFW) system did not meet design requirements for normal use, due to inadequate pipe rupture restraints. <br /><br /> This condition has historically existed since the first cycle of plant operation. It is reported as a condition outside the design basis because the AFW system was not adequately designed to restrain a high energy line break (HELB) when the system was used for normal plant startup, hot standby, and shutdown. <br /><br /> The condition has low safety significance because the existing supports on the line meet the 'faulted' stress limits. The missing HELB restraints have no affect on the loading combinations required for the AFW system to perform its design basis safety functions. Thus, the AFW system is fully operable per Technical Specifications to perform all credited safety functions.<br /><br /> The root cause of the condition was a design error. The plant design for the AFW system includes a postulated HELB, so that the AFW system can be used during normal plant startup, hot standby, and shutdown. Restraints on portions of the AFW system were not installed during the original plant construction, due to changes in the intended use of the AFW system. As corrective action, the condition was promptly reported when self-identified, and night orders were issued to limit use of the AFW system for normal plant operation. Plans are being made to strengthen several pipe supports, and make permanent procedure changes to isolate moderate energy portions of the system, so that the AFW can be used during limited portions of normal startup, hot standby, and shutdown.
4231994007 | Millstone 3 | 04/14/1994 | 05/13/1994 | 9405190038 | <strong>Violation of Engineered Safety Feature Response time for Quench Spray System</strong><br /><i>Abstract:&nbsp;</i>On April 14,1994, with the plant in MODE 1 at 100% power, an engineering review determined that the valve stroke time acceptance criterion exceeded the system response time identified in Technical Specifications for Engineered Safety Features (ESF) actuation of the Quench Spray System (QSS).<br /><br /> Although, at the time of discovery, the required ESF response time was acceptable, a review of historical data identified that an unacceptable condition has sporadically existed since initial plant startup. Specifically, when the quarterly QSS header isolation valve actual stroke times are added to the instrument response times, two instances were identified that exceeded the Technical Specification (TS) surveillance acceptance criterion. Additionally, when the actual stroke times were added to the Loss of Normal Power (LNP) acceptance criterion, many instances occurred where the TS surveillance acceptance criterion was exceeded. This condition was not previously identified because an inadequate valve/stroke time was used in the surveillance. This is reported as a condition prohibited by the Technical Specifications. <br /><br /> The condition had low safety significance because the actual QSS actuation time met the response times that are used in the QSS design/safety analysis. The ESF system is fully operable to perform all credited safety functions. <br /><br /> The root cause of the condition was a programmatic error during initial startup. An unacceptable valve stroke time was identified. The disposition accepted time stroke 'as-is' based on the safety analysis. However the disposition allowing the increased stroke time did not correct the TS acceptance criterion. As initial corrective action, the QSS valve stroke time acceptance criterion has been administratively reduced. A proposed change to the TS has been submitted to the NRC which would allow Northeast Nuclear Energy Company (NNECO) to change the ESF actuation acceptance criterion to be consistent with the design/safety analysis, to prevent recurrence.
4231994008 | Millstone 3 | 05/05/1994 | 06/02/1994 | 9406080171 | <strong>Westinghouse 7300 Process Control System Surveillance Deficiency Due to Program Failure</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1994, with the plant in Mode 1 at 100% power, Instrumentation & Controls personnel identified a deficiency in surveillance testing for the bypass feature of Lead/Lag (NLL) relay cards in Westinghouse 7300 cabinets. The relay cards support the surveillance testing of lead/lag compensated channels by providing a bypass test feature. The normally closed relay card contacts were not verified to be closed when returning the bypass to the normal alignment in the channel surveillances and lead/lag surveillances. <br /><br /> The inadequate surveillance is reported as a condition prohibited by the Technical Specifications. The condition had low safety significance. Immediate evaluations determined that some circuits would be susceptible to undetectable failure modes. However, testing verified that all circuits with the lead/lag bypass feature were operable and capable of performing all credited safety functions. <br /><br /> The root cause of the condition was a program failure which resulted in a procedure deficiency. When a design improvement was made during plant construction, emphasis was placed on safely placing the channels into a test configuration. The possibility of a normally closed relay contact failure when returning the NLL bypass to the normal alignment was not considered. To prevent recurrence the surveillance procedures will be modified to verify bypass relay card contact closure.
4231994009 | Millstone 3 | 07/05/1994 | 08/02/1994 | 9408110245 | <strong>Digital Rod Position Indication Failure Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1994, with the plant in Mode 1, at 100% power, Control Room Operators identified unreliable control rod position indications. A number of control rods in Control Bank D had unreliable position indications. An immediate shutdown commenced as required by Technical Specification 3.0.3 when more than one rod had questionable indications. The NRC was promptly notified in accordance with 10CFR50.72(b)(1)(i)(A) of the initiation of a shutdown required by Technical Specifications. <br /><br /> This is being reported under 10CFR50.73(a)(2)(i)(B) since the plant was in a condition prohibited by the Technical Specifications. The condition had low safety significance. Flux mapping confirmed that the rods in Control Bank D were moving together. Additionally, the plant computer has individual rod position indication which was unaffected by this failure. <br /><br /> The cause of the condition was a failed instrument card in the Digital Rod Position Indication (DRPI) system. As corrective action the failed card was replaced before completing the shutdown, surveillances were performed to ensure the system was fully operable, and the plant was returned to 100% power.
4231994010 | Millstone 3 | 07/26/1994 | 08/24/1994 | 9409020278 | <strong>Both Trains of Charging Inoperable Due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1994, with the plant at 100% power, both trains of Charging were declared inoperable. The A Train of Charging was inoperable for a routine surveillance. While the A Train was inoperable, an Operator determined that the B Charging Pump Cooling Pump was inoperable because of low bearing oil level. Since the acceptance criterion was not met, the B Charging Pump was also declared inoperable. With both trains of Charging inoperable, the plant was in noncompliance with Technical Specifications, and an entry into Technical Specification 3.0.3 was required. <br /><br /> This condition is reported under 10CFR50.73(a)(2)(i)(B), because the plant was declared to be in a condition prohibited by Technical Specifications. This is reported for information only. A review determined that a reportable condition had been conservatively declared due to an overly restrictive Technical Specification surveillance acceptance criterion. <br /><br /> A conservative decision was made to promptly report and the NRC was notified under 10CFR50.72(b)(1)(ii). However, the condition had no safety significance. An engineering review determined that the cooling pump was operable because the observed oil level had no effect on the cooling pump. Thus, the B Charging Pump was always operable and capable of performing its safety function. <br /><br /> The cause of the condition was an overly restrictive acceptance criterion for the cooling pump bearing oil level. As immediate corrective action the A Train was returned to operable status by terminating the routine surveillance. To prevent recurrence, the acceptance criterion for the cooling pump oil level has been changed to provide a more appropriate indication of operability.
4231994011 | Millstone 3 | 09/08/1994 | 10/07/1994 | 9410130343 | <strong>Manual Reactor Trip Due to Main Steam Isolation Valve Failure During Part-Stroke Test</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1994, with the plant at 100% power, a manual reactor trip was initiated. The reactor was manually tripped in anticipation of an automatic trip, due to the 'C' Main Steam Isolation Valve (MSIV) failing closed during surveillance testing. The plant responded normally with the exception that two of the Main Steam safety valves appeared to open momentarily below the Technical Specification tolerance. Feedwater isolation occurred. The auxiliary feedwater pumps started on Low-Low Steam Generator level, and the turbine-driven Auxiliary Feedwater pump tripped off eight seconds after starting. <br /><br /> The manual trip of the reactor protection system is reported under 10CFR50.73(a)(2)(iv). The Main Steam safety valves lifting below their Technical Specification tolerance is reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.<br /><br /> The cause of the MSIV closure was equipment failure. A pin failed in a solenoid on the 'C' MSIV, which resulted in the MSIV failing closed during surveillance testing. The cause of the Main Steam safety valves lifting prematurely is believed to be due to setpoint drift. <br /><br /> As immediate corrective action the control room Operators manually tripped the reactor and performed the actions required by emergency operating procedures. As corrective action, the solenoid and a number of pins were replaced, and the MSIVs were tested satisfactorily. The turbine-driven Auxiliary Feedwater pump was returned to operable status, and two Main Steam safety valves were replaced.
4231994012 | Millstone 3 | 09/09/1994 | 10/07/1994 | 9410140222 | <strong>Reactor Coolant System Pressure Boundary Leak Due to Instrument Line Socket Weld Failure</strong><br /><i>Abstract:&nbsp;</i>On September 9,1994, with the plant in Mode 4, at 0% power, a leak was discovered in 3/4-inch socket weld on a 'C' Reactor Coolant System (RCS) Loop Flow Instrumentation line. The weld was removed for analysis during which liquid penetrant testing identified a circumferential crack approximately, 5/8-inch long. Initial metallurgical analysis indicated that the root cause of the socket weld failure was most probably a weld defect, believed to result from a lack of fusion in the weld root pass. The defect propagated to the weld surface. <br /><br /> This condition is being reported in accordance with 10CFR50.73(a)(2) (i)(B), as an operation or condition prohibited by Technical Specifications. Technical Specification 3.4.6.2 requires 'No Pressure Boundary Leakage' (i.e., nonisolable fault). Although this incident involved a reactor coolant leak, it had low safety significance. Leakage was collected within the containment drain system. The port to the RCS loop is a 3/4-inch diameter restriction, which would have minimized leakage from the RCS in the event of total failure. The normal makeup system has sufficient capacity to maintain pressurizer level and compensate for a failure of this line. <br /><br /> A review of similar events identified a previous RCS socket weld failure, that was discovered in cold shutdown on May 18, 1992. This LER also documents that historical condition which was not previously reported. For the same reasons as identified above, that incident had low safety significance.
4231994013 | Millstone 3 | 09/16/1994 | 10/17/1994 | 9410270286 | <strong>Main Steam Isolation Valves and Turbine Driven Auxiliary Feedwater Pump, Inadequate Technical Specifications for Mode Change</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1994, with the plant in cold shutdown, it was determined that previous plant start-ups were conducted with several operability tests not performed prior to entry into Modes 4 and 3. The affected equipment included the Main Steam Isolation Valves, the engineered safety features actuation system, and the turbine-driven Auxiliary Feedwater pump. Since the plant was shut down at the time of discovery, changes to the Technical Specifications were necessary to allow the plant to enter Modes 4 and 3 to perform the required operability tests. <br /><br /> The missed operability testing was a historical condition that is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications. <br /><br /> The cause of the historical Technical Specification noncompliance was a misinterpretation of the Technical Specifications. This was an administrative oversight that has been corrected in the new Westinghouse Standard Technical Specifications (NUREG - 1431). <br /><br /> As immediate action, the plant remained in cold shutdown while a request was submitted to the NRC on September 17, 1994, to change the Technical Specifications. Timely enforcement discretion was granted on September 17, 1994, to allow the plant to conduct the required tests in Modes 4 and 3, as appropriate, and allow the plant to resume operation. A License Amendment that granted relief from Technical Specification 4.0.4 was subsequently issued on September 29, 1994. This change allows future startups to be conducted by performing the required tests in Modes 4 and 3, as appropriate, for the affected equipment. <br /><br /> As action to prevent recurrence, a review of all Technical Specifications was performed. The review determined that a clarification to the Reactor Trip System Instrumentation Surveillance is needed, and a license amendment request will be submitted. The review also identified an isolated historical noncompliance with a cold shutdown surveillance involving a check of isolation valves, and a procedure change has been made to amplify the surveillance frequency.
4231994014 | Millstone 3 | 11/21/1994 | 12/20/1994 | 9412280255 | <strong>Turbine Driven Auxiliary Feedwater Pump Surveillance Failure Due to Trip Linkage Problems</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1994, with the plant in Mode 1 at 100% power, the turbine driven auxiliary feedwater pump (TDAFW) failed to start during a cold start surveillance test. The cause of the surveillance failure was potentially attributable to preexisting conditions in the TDAFW trip valve linkage. The conditions may have made the TDAFW pump inoperable for a period of time that exceeded the Technical Specification Action Statement. Accordingly, this event is reported under 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the Technical Specifications.<br /><br /> Inspections revealed potential problems with the trip valve linkage which could have caused the surveillance failure. Corrective maintenance was performed on the linkage, and a cold start retest was successful. As action to prevent recurrence: a procedure change was made to ensure the trip linkage is properly engaged; an accelerated surveillance schedule was implemented to provide increased assurance of operability; measures are being taken to monitor condensate accumulation in the steam supply lines; and a utility review group has been formed to identify other measures to improve TDAFW reliability. <br /><br /> The event had moderate safety significance because the other two motor-driven auxiliary feedwater pumps remained operable in accordance with Technical Specifications. It was conservatively assumed, for purposes of reporting the event, that there were preexisting conditions that could have made the TDAFW pump inoperable, although this cannot be conclusively determined. Assuming the TDAFW pump was inoperable, a loss of offsite power would result in the motor-driven AFW pumps being powered from emergency electrical buses.
4231994015 | Millstone 3 | 12/29/1994 | 01/26/1995 | 9502010208 | <strong>Shift Turnover Without Shift Technical Advisor Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1994, with the plant in Mode 1 at 100% power, the Control Room day shift did not have a Shift Technical Advisor (STA) for 35 minutes. During this time, actions were taken to locate a replacement STA. It was determined that the oncoming (swing shift) STA, who agreed to report to work early, would provide STA coverage for the remainder of the day shift, through the swing shift. <br /><br /> This condition is reported as an operation or condition prohibited by Technical Specifications. Technical Specification 6.2.2, Facility Staff, requires that each on-duty shift will be comprised of at least the minimum shift crew composition (which includes the STA function). The day shift had STA coverage provided by the Shift Supervisor who was STA qualified (in a dual role). The SS left at 1209 hours for an appointment. However, his replacement SS was not dual role qualified. STA coverage did not exist from 1209 hours until the oncoming STA arrived at 1244 hours. There was minimal safety significance because there were no plant conditions that required STA action during this period. <br /><br /> The root cause is personnel error on the part of both SS's. It is the responsibility of the oncoming SS and the off going SS to ensure a full shift compliment as part of the turnover. As action to prevent recurrence, the Shift Turnover Report was changed to include a 'sign-out' box for Control Room staff positions; training is being conducted to review the event with all operators; and the SS's in this event will be counseled. As a long term action to prevent recurrence, NNECo is working toward shift staffing changes so that each shift will have an individual STA and the SS's will not have to fulfill a dual role.
4241994001 | Vogtle 1 | 02/02/1994 | 02/21/1994 | 9403180052 | <strong>Reactor Trip/Safety Injection Due To False Pressurizer Low Pressure Signal</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1994, personnel were replacing a pressurizer pressure transmitter in the containment building. During the work, the transmitter swung on one of its mounting bolts and impacted the handle of the isolation valve for its sensing line, causing the valve to open enough to momentarily vent pressure from the sensing line. This sensing line is shared with another pressure transmitter. The momentary venting of the sensing line caused the second pressure transmitter to sense a false low pressure, which completed a two out of four logic for initiating a reactor trip and a safety injection (SI), at 0557 EST. Within seconds, the technician performing the work closed the isolation valve. Control room operators responded to the reactor trip and SI using the emergency operating procedures (EOPs) and the SI signal was reset at 0607 EST. A Notification of Unusual Event (NOUE) was declared at 0610 EST, due to the safety injection into the reactor vessel. The unit was stabilized and normal operation resumed in Mode 3 (hot standby). The NOUE was terminated at 0750 EST. <br /><br /> The cause of this event was a cognitive personnel error by the technician involved when he lost physical control of the pressure transmitter, such that it swung and bumped open the instrument isolation valve, initiating the sequence of events. Appropriate personnel are being briefed regarding this event, with emphasis being placed on attention to detail when performing work on critical plant components.
4241994002 | Vogtle 1, Vogtle 2 | 03/11/1994 | 04/07/1994 | 9404130295 | <strong>Inadequately Performed Differential Temperature Channel Checks</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1994, the reactor engineering supervisor (RES) was reviewing an industry notice of a concern regarding channel checks for over power delta-T (OPDT) and over temperature delta-T (OTDT) reactor trip instrumentation. The notice identified that the OPDT and OTDT channel checks at another nuclear power plant were not being adequately performed. The channel check consisted of monitoring the variable OPDT and OTDT trip setpoints as stated explicitly in Technical Specification (TS) Table 4.3-1. It did not include monitoring the process variable itself, delta-T. The OPDT and OTDT trips actuate when delta-T from two of the four channels exceeds the setpoints. Therefore, the notice concluded that the four delta-T channels should have been included in the channel checks to ensure the process indications, in addition to the trip setpoints, are properly functioning. <br /><br /> The RES realized that a similar condition existed at both units of Plant Vogtle since delta-T readings were not considered to be part of the OPDT and OTDT surveillance channel checks. At 0945 EST, control room personnel were advised. Prompt action was taken to monitor and log the delta-T values and to enhance the surveillance procedures for both units, in order to more fully comply with the intent of the TS.
4241994003 | Vogtle 1 | 04/26/1994 | 06/17/1994 | 9406220095 | <strong>Closed Dampers Render Two Trains Of HVAC Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1994, exhaust dampers in both trains of the piping penetration area filtration and exhaust system (PPAFES) were found to be closed due to circuit breakers being deenergized while a design change was being performed on another air filtration system that utilized the same circuit breakers. The exhaust dampers were reenergized and restored to service. Concurrently, an initial determination was made, based on test results, that this condition had not rendered the system inoperable. On April 26, 1994, a further engineering evaluation determined that having the exhaust dampers closed would limit the ability of the PPAFES to control radioactive releases in a post-LOCA scenario. <br /><br /> The cause of this event was drawing discrepancies in a single line diagram and an electrical load list. Also, cognitive personnel errors and lack of attention to detail resulted in inadequate reviews of the circuit breaker clearances associated with the design change. Additionally, surveillance guidance for verification of damper position was unclear. Furthermore, subsequent personnel errors occurred which delayed the identification and resolution of the problem. The single line diagram and electrical load list were corrected. Personnel were counseled and additional training will be conducted to emphasize the importance of clearance reviews for proper configuration control.
4241994004 | Vogtle 1, Vogtle 2 | 06/19/1994 | 07/14/1994 | 9407190017 | <strong>Deenergized Heaters Results In Control Room HVAC Degradation</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1994, a plant operator noticed that a control room emergency filtration system (CREFS) heater reset button was not lit. This led to the discovery that filtration heaters for three of four trains of CREFS were deenergized. The heaters' power source control relays were reset, thereby restoring power to the heaters. The day after this discovery, a system engineer performed a walkdown of other similar systems and found a similar condition on both trains of unit 2 piping penetration area filtration and exhaust system heaters and on one train of fuel handling building post accident filtration system heaters. The power source control relays for these heaters were also reset. <br /><br /> The apparent cause of this event was a power disturbance to plant electrical systems. A fault recorder in the plant switchyard registered a disturbance during the passing of a thunderstorm on June 17, 1994. The root cause of the event was the failure of an automatic reset function to operate following the power disturbance. Further evaluation of this event is in progress and recommendations for any necessary changes will be made by August 5, 1994.
4241994005 | Vogtle 1 | 08/10/1994 | 09/01/1994 | 9409130142 | <strong>Containment Ventilation Isolation Automatic Actuation Circuitry Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1994, a containment ventilation isolation (CVI) occurred. An investigation found that the radiation monitor involved, 1RE-2565, was displaying normal values, had no radiation alarms or trouble alarms, and the only change in the system had been to place a CVI block switch to 'normal'. Personnel concluded that the block switch was the source of the false CVI signal and the block switch was left in its 'normal' position pending further investigation. On August 9, 1994, in order to facilitate the inputting of the new release permit parameters into 1RE- 2565, and in conjunction with troubleshooting the cause of the CVI, SSPS leads were lifted and another CVI occurred. However, this time the block switch was not being manipulated. A follow-up investigation found that a failed relay inside of the radiation monitor had caused a CVI signal to be continuously sent from 1RE-2565 to the solid state protection system (SSPS) and resetting from the first CVI had simply blocked the CVI signal at the SSPS input. The failed relay was replaced. On August 10, 1994, it was determined that this condition would have prevented a valid automatic CVI signal from being processed by the SSPS in response to high radiation in the containment building. <br /><br /> This report is required because this represents a condition that alone could have prevented fulfillment of a safety function needed to control the release of radioactive material, when the radiation monitors' automatic actuation circuitry for CVI was inoperable. Additionally, this represented unit operation in a condition prohibited by the Technical Specifications.
4241994006 | Vogtle 1 | 09/11/1994 | 09/30/1994 | 9410050071 | <strong>Reactor Trip At Low Power Due To Neutron Detector Failure</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1994, Unit 1 was being shut down in preparation for a refueling outage by inserting control rods into the reactor. The source range neutron detector NI-0032 automatically energized, as required. Upon energization at 0036 EDT, NI-0032 sent a high flux signal that initiated an automatic reactor trip. A normal trip sequence ensued and personnel continued unit operations in Mode 3 (hot standby). <br /><br /> The cause of this event was found to be a loose capacitor in the NI-0032 neutron detector pre-amplifier that was causing a spiked signal to be generated as it intermittently made contact. This spiking was interpreted by the detector's circuitry to be a high flux condition. The pre-amplifier was replaced and NI-0032 was returned to service.
4241994007 | Vogtle 1 | 10/04/1994 | 10/28/1994 | 9411030106 | <strong>Surveillance Not Performed Prior To Restoring Radiation Monitor To Service</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1994, containment radiation monitors 1RE-0002 and 1RE-2565 were in service to provide automatic containment ventilation isolation (CVI) capability per Technical Specification (TS) requirements to have two monitors operable during refueling. At 0228 EDT, another containment radiation monitor, 1RE-0003, was returned to service. However, a TS special condition surveillance requirement applicable during core alterations, to verify that a CVI occurs on a high radiation test signal from IRE-0003, had not been performed. At 0236 EDT, 1RE-2565 was removed from service for a period of 3 hours and 12 minutes. As a result, 1RE- 0003 and 1RE-0002 were relied upon during this period as the two required instruments to provide automatic CVI actuation capability. Although 1RE- 0003 had been demonstrated to be functional, the special condition surveillance had not been performed prior to the return to service. This represented unit operation in a condition prohibited by the TS. On October 4, 1994, the Unit Shift Supervisor (USS) discovered this event during a review of logs from the previous day. <br /><br /> The cause of this event is a cognitive personnel error on the part of the USS who did not ensure that the special condition surveillance had been performed prior to returning 1RE-0003 to service. The USS will be counseled regarding the importance of ensuring that all applicable surveillances are satisfactorily completed prior to returning TS components to service.
4241994008 | Vogtle 1 | 10/27/1994 | 11/18/1994 | 9411300317 | <strong>Piping Penetration Area Filtration And Exhaust System Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1994, while implementing a design change to delete the Electrical Penetration HVAC System, personnel removed fourteen circuit cards for both Train A and Train B of the system. On October 28, 1994, personnel investigating the cause of a damper problem in the Train A Piping Penetration Area Filtration and Exhaust System (PPAFES) determined that the removal of two of these circuit cards had rendered the exhaust dampers for both trains of the PPAFES inoperable. This represented a degraded condition of a safety function of a system needed to control the release of radioactive material. Technical Specification 3.0.3 was entered for 23 minutes until one train of PPAFES was restored to service. <br /><br /> The design change process did not identify that certain circuits for both the Electrical Penetration HVAC System and PPAFES were contained on the same circuit cards. Several engineering drawings did not contain an engineering aid to advise the user that other circuits were contained on these circuit cards. Another key reference, the 'card load list,' contained better information, but was not referenced during the design change process. Vendor drawings are being corrected. The card load list has been updated and will be available for use when reviewing future design changes to determine the impact of pulling cards on system operation.
4251994001 | Vogtle 2 | 01/07/1994 | 02/01/1994 | 9403140211 | <strong>Automatic Reactor Trip Due To Turbine Trip Resulting From Trip Of Switchyard Breakers</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1994, at 2253 EST, the Unit 2 reactor automatically tripped as a result of a generator/turbine trip. The initiating event for this reactor trip was the operation of a differential relay on a shunt reactor in the high voltage switchyard (HVS) which resulted in the trip of two 500 kV air blast circuit breakers (ACB), one of which is the Unit 2 main generator ACB. After operation, the two ACBs had low air pressure indications which served as a permissive in the breaker failure protective relaying scheme. This resulted in simultaneously tripping of the back-up breakers, including the remaining Unit 2 main generator ACB. The shunt reactor was removed from service pending further testing and analysis. With air pressure restored to normal levels, the breakers operated properly. The main generator ACBs were returned to service, allowing unit startup to commence. <br /><br /> The causes of this event were the operation of a differential relay on a shunt reactor and the failure of the 500 kV ACB compressed air refill pressure system switches to operate properly and maintain adequate air pressure prior to breaker tripping. This activated a breaker failure protective relaying scheme which tripped back-up breakers including the remaining Unit 2 main generator ACB and, ultimately, tripped the turbine and reactor. A loss of off-site power (LOSP) did not occur and the safety busses remained energized throughout the event.
4251994002 | Vogtle 2 | 01/19/1994 | 02/11/1994 | 9402160245 | <strong>Turbine/Reactor Trip Due To Water Entering Moisture Separator Reheaters</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1994, at 0938 EST, control room personnel received an alarm for a trip of the 'B' heater drain tank (HDT) pump. Personnel immediately initiated a power reduction and started a third condensate pump to make up for the loss of feedwater from the HDT. However, at 0940 EST, with reactor power at 98.5 percent power, a turbine/reactor trip occurred due to high water levels in the 'C' and 'D' moisture separator reheaters (MSRs). <br /><br /> The initiating cause of this event was the loss of the 'B' HDT pump, likely caused by the spurious actuation of a low level sensor. The 'B' HDT high level dump valve was out of service for maintenance, and when the HDT high level switch actuated, the normal drain valves for the 'C' and 'D' moisture separator drain tanks (MSDTs) closed, as designed. Malfunctions of the MSDTs level controllers and switches allowed overflow from the MSDTs to enter into the 'C' and 'D' MSRs where level switches initiated a turbine trip. <br /><br /> A steam leak on the upper tap of the HDT low level sensor was repaired. The 'B' HDT high level dump valve was returned to service. The MSDT level controllers were recalibrated and level switches and sensing lines were cleaned and tested to verify correct operation.
4251994003 | Vogtle 2 | 01/27/1994 | 02/23/1994 | 9403040083 | <strong>Personnel Error Results In Improper Temperature Readings</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1994, a plant equipment operator (PEO) was performing temperature measurements in the equipment building as required by Technical Specification (TS) 4.7.10. The PEO mistakenly measured the temperature in two different areas of room A009, rather than take separate measurements in rooms A009 and A008. This scenario was repeated on the same shift for the next two days. After completing the temperature measurements on January 27, 1994, the PEO questioned why there was no temperature rounds marker in what he believed to be room A008. An investigation revealed the misunderstanding and a temperature reading was performed at the correct location in room A008. These incidents represented unit operation in a condition prohibited by the TS because the temperature in room A008 was not measured at least once per 12 hours on January 25th and 26th, as required by TS 4.7.10. <br /><br /> The cause of this event was a cognitive personnel error by the PEO in failing to measure the temperature in room A008. The PEO has been reminded of the importance of attention to detail. Appropriate shift personnel were advised of this event during shift briefings and it will be further addressed in operators' continuing training.
4251994004 | Vogtle 2 | 07/01/1994 | 07/21/1994 | 9407260196 | <strong>Inadequate Tech. Spec. Surveillance Due To High Point Not Vented</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1994, it was found that the unit had operated in a condition prohibited by the Technical Specifications (TS). It was determined that a surveillance procedure for venting an emergency core cooling system did not appropriately specify that a particular residual heat removal (RHR) high point vent should be opened to check that the system was full and free of gas. The high point was successfully vented utilizing a test connection, with no entrapped gasses detected. <br /><br /> The cause of this event was an apparent oversight during the development of the Unit 2 surveillance procedure, prior to initial startup. Unit 2 was essentially constructed as the mirror image of Unit 1, and the corresponding high point in Unit 1 is vented by way of valve 1-1205-X4-013. However, there is no mirror image valve in Unit 2 at the corresponding location. Personnel developing the Unit 2 surveillance procedure utilized the Unit 1 procedure without requiring the corresponding high point to be vented. Valve 2-1205-U4-041 at a test connection has been added to the monthly surveillance procedure for venting of ECCS high points
4251994005 | Vogtle 2 | 07/23/1994 | 08/16/1994 | 9408240237 | <strong>Pressure Boundary Leakage Found Following Unit Shutdown</strong><br /><i>Abstract:&nbsp;</i>This report is required per 10 CFR 50.73 (a)(2)(i)(B) because pressure boundary leakage was discovered after the unit was shutdown to repair what appeared to be stem leakage due to diaphragm failure of a drain line isolation valve. <br /><br /> An increasing trend of containment sump activity and radiation monitor activity, together with reactor coolant system (RCS) inventory balances, led personnel to believe that leakage existed in the containment building. This unidentified leakage was estimated to be approximately one-half gpm. Plant personnel were able to identify the source of this leakage on July 22, 1994, when an investigation using a remotely operated camera inside the biological shield wall found what appeared to be stem leakage due to diaphragm failure at the loop 3 intermediate leg drain line isolation valve. On July 23, 1994, the unit was shutdown to Mode 3 (hot standby) to repair the leak. Once the reactor was subcritical, personnel were able to access the area for a firsthand inspection which subsequently determined that RCS pressure boundary leakage had existed due to a leaking socket weld at the valve, rather than stem leakage due to diaphragm failure.<br /><br /> The root cause of this event was a welding defect. Inspection of the weld found an area of deep-seated porosity that would not have been expected to be detected by the liquid penetrant testing that was performed during original construction. The leaking weld was completely removed and a new weld performed. The unit returned to power on August 4, 1994.
4401994001 | Perry | 01/18/1994 | 02/16/1994 | 9402280149 | <strong>Reactor Water Cleanup Isolation Due To Loss Of Auxiliary Building Ventilation</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1994 at 0737 and 0738 system containment isolations occurred due to Reactor water Cleanup (RWCU) system valve nest room high differential temperatures. The high differential temperature occurred as a result of tripping of the Auxiliary Building (AB) Ventilation system supply fans due to low inlet air temperature. The loss of cooling air to the valve nest room resulted in the high differential temperature. At the time of these events outside air temperature was approximately minus 20 degrees Fahrenheit. The RWCU system was isolated at 0736 by plant operators in anticipation of the isolation signal. Plant operators verified that no leakage existed and the RWCU system was returned to service on January 21, 1994. <br /><br /> Corrective actions were to replace the AB Ventilation system supply fans inlet temperature switches and relocate the associated capillary tubing.
4401994002 | Perry | 01/28/1994 | 02/28/1994 | 9403070401 | <strong>Manual Reactor Scram Following Reactor Recirculation Pump Automatic Downshift</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1994 at 1944, both Reactor Recirculation system pumps automatically downshifted from fast speed to slow speed. Due to the decrease in core flow, reactor parameters entered the region of potential instability on the power to flow map. In accordance with plant procedures, the control room operator initiated a manual scram at 1945 with reactor power level at 47 percent. No power oscillations indicating core power instability were observed while within the instability region of the power to flow map. <br /><br /> The cause of this event was an equipment failure. A relay on alarm card 1C34-K618B failed open causing the low feedwater flow relays to initiate a recirculation pump downshift. The cause of the relay failure could not be determined. A review of the failure history for this model card did not identify any generic concerns or adverse failure trends. As a result of this event, the alarm card with the failed relay and the alarm card in the redundant trip system were replaced. Two other alarm cards of the same model that could cause a recirculation pump downshift were also replaced.
4401994003 | Perry | 01/29/1994 | 02/28/1994 | 9403100169 | <strong>Technical Specification Violation Involving Containment Airlocks</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1994, at 0714 hours with the outer door of the primary containment's lower air lock inoperable, the inner door was opened for approximately one (1) minute to permit entry into the containment. This action was not in compliance with Technical Specification (TS) 3.6.1.3. Prior to opening the lower air lock's inner door, enforcement discretion was requested and obtained for issues related to TS 3.6.1.3. <br /><br /> The immediate cause was the failure of a seal on the outer door to deflate as a result of a broken stem on the air supply line's 1/2 inch three way ball valve. The inflated seal prevented door opening, necessitating the need to puncture the seal. This rendered the outer door inoperable. The root cause of this event is the design of the mechanical linkage which positions the ball valve when the door is operated. A contributing factor was the inoperable status of the upper air lock's outer door at the time the lower air lock's door failed.<br /><br /> Additionally, the current TS do not consider the need to access containment through an air lock with an inoperable door for reasons other than to repair an inoperable inner door. <br /><br /> The ball valve was repaired, the punctured seal replaced and the lower air lock tested and returned to OPERABLE status. Changes to the design of the air lock's mechanical linkage are being considered.
4401994004 | Perry | 02/08/1994 | 03/08/1994 | 9403140186 | <strong>Containment Penetration leak Rates Exceeding Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>Between February 8 and February 15, 1994, during the fourth refueling outage, three containment penetrations exceeded local leak rate test (LLRT) failure criteria for non Main Steam Isolation Valve (MSIV) leakage, as defined by Technical Specification 3.6.1.2.b and 3.6.1.2.d. <br /><br /> The cause of the excessive leakage has not yet been determined. This LER is based upon the results of testing which has been completed as of February 20, 1994. As of February 20, 1994, the involved valves have not yet been repaired. Additionally, local leak rate testing is currently ongoing, with the potential for identifying additional test failures. This LER will be supplemented after completion of the current refueling outage to provide these results as well as corrective actions for these and any additional non MSIV LLRT failures which meet 10 CFR 50.73 reporting criteria.
4401994005 | Perry | 02/09/1994 | 10/28/1994 | 9411030170 | <strong>Loss of Both Trains of Control Room Emergency Recirculation Due to Low Emergency Closed Cooling Temperature</strong><br /><i>Abstract:&nbsp;</i>During preparation for Residual Heat Removal (RHR) heat exchanger testing on February 5, 1994 Emergency Closed Cooling (ECC) system division 1 temperature was observed to be below 55 degrees F. Design of the Control Complex Chillers requires inlet condensing water temperature from ECC to be greater than 55 degrees F. At temperatures below 55 degrees F the Control Complex Chillers may trip on low refrigerant temperature causing the associated train of Control Room Heating, Ventilation and Air Conditioning (CRHVAC) Emergency Recirculation mode to be inoperable. <br /><br /> A review was performed to determine if this condition could have existed at any time where both trains of ECC were affected. It was determined on February 9, 1994 that between January 28 and January 29, 1994 for approximately 10 hours and 47 minutes that both trains of ECC were affected. Therefore, during this time period both trains of the CRHVAC Emergency Recirculation mode would be inoperable. <br /><br /> Immediate corrective actions were to revise appropriate system operating procedures to maintain ECC temperature above 55 degrees F. <br /><br /> This revision updates the corrective actions.
4401994006 | Perry | 02/10/1994 | 03/11/1994 | 9403160190 | <strong>Procedure Deficiency Results in Unexpected Reactor Core Isolation Cooling Isolation</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1994 at 1620, a Reactor Core Isolation Cooling (RCIC) system inboard containment isolation occurred during the performance of an isolation logic system functional surveillance instruction. Investigation of this isolation determined that the surveillance instruction adjusted trip units 1E31-N685A & B close to their trip setpoints. When the inboard containment isolation valves were opened as directed by the surveillance instruction, a pressure perturbation in the steam supply line resulted in an isolation signal being generated by the trip units. <br /><br /> The root cause of this event was an inadequate procedure. The surveillance instruction did not ensure that the input to the trip units was adjusted with sufficient margin to the trip setpoints during the performance of the instruction. <br /><br /> As a result of this event, the surveillance instruction will be revised to ensure that the trip setpoints are cleared by a sufficient margin during the performance of the surveillance instruction. Additionally, a review of other similar surveillance instructions will be performed to identify those instructions that contain similar inadequacies. These surveillance instructions will be revised to provide sufficient margins to the associated trip setpoints.
4401994007 | Perry | 02/17/1994 | 03/21/1994 | 9403240138 | <strong>Water Intrusion Leads to Passive Seismic Instrument Failure</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1994, during performance of a surveillance on the sealed passive seismic monitoring system instrument located in the High Pressure Core Spray Pump (HPCS) Room, it was discovered that water had entered the housing corroding several of the sensors. The water was assumed to have entered the instrument during the flooding of the HPCS Pump Room during the March 26, 1993, Service Water pipe break event. <br /><br /> The affected instrument, the Peak Acceleration Recorder, has been replaced. All other Peak Acceleration Recorders are being replaced this outage. In the future, these instruments will be replaced with either a new or rebuilt instrument during each calibration, or, if not practical, the gasket will be inspected, and if necessary a new gasket will be installed during each calibration and inspected to ensure proper fit. <br /><br /> This report also satisfies the requirements of Technical Specification 3.3.7.2, Action a., which requires a Special Report to be submitted when a seismic monitoring instrument is inoperable for more than 30 days.
4401994008 | Perry | 02/25/1994 | 04/08/1994 | 9404140001 | <strong>Unexpected Safety Relief Valve Openings due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On February 25 and 26, 1994, during the performance of channel calibration surveillance instructions (SVI), two safety relief valves (SRV) unexpectedly opened a total of eight times. When the unexpected SRV opening was identified, the SVI was terminated, the SRV was closed, and an investigation of the event was initiated. <br /><br /> The root cause of this event was inadequate instructions that resulted in inadvertent openings of two SRVs. The preparation and review process of the last revision of the affected SVIs was inadequate to ensure that the seal-in logic was reset to preclude the opening of the SRVs. Also contributing to this event was inattention to detail by the control room operators of one shift for failing to recognize the SRV openings as an unexpected result of the SVIs. <br /><br /> As a result of this event, the affected SVIs have been revised. <br /><br /> Additional corrective actions will include training of licensed operators on this event and a review of the preparation and review process for instructions to identify appropriate enhancements. <br /><br /> This event is being submitted as a voluntary report due to the generic interest and lesson learned from,the information contained herein.
4401994009 | Perry | 03/19/1994 | 04/18/1994 | 9404210077 | <strong>Diesel Generator Returns to Rated Speed During Shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1994 at 1526 hours, during testing of the Division 1 Diesel Generator (D/G) trip logic the D/G engine unexpectedly returned to rated speed during shutdown when a manual engine stop signal was removed. The D/G had been placed in the Emergency mode of operation for the trip logic tests, which deactivated all shutdown signals except for local or remote manual stop, and engine overspend and generator differential trips. Engine shutdown from the retest was attempted by a remote manual stop signal prior to returning the engine to normal operating mode. The stop signal was removed when the D/G control switch was released from the STOP position and the D/G returned to rated speed from coastdown, as appropriate for the emergency mode of operation. Both trains of the D/G Building Ventilation System (DGBVS) were initially running in support of the retest. One train which had been shut down to standby readiness during the retest, restarted as designed when engine speed reached 441 rpm, increasing. <br /><br /> The D/G was returned to normal operating mode, the engine was successfully shut down by placing the D/G control switch in the stop position and the DGBVS was shutdown to standby readiness. <br /><br /> The cause of the event was personnel error, failure to follow procedures, in that test personnel did not recognize the need to obtain proper authorization of a deviation from the instruction used for testing.
4401994010 | Perry | 04/14/1994 | 05/11/1994 | 9405180178 | <strong>ESF Actuation Due to Loss of Power to Level Instruments Caused by Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1994 at 1303 hours while deenergizing 125 Vdc bus ED-1-B, an unanticipated automatic start of the Emergency Service Water (ESW) pump A and Emergency Core Cooling (ECC) pump A occurred due to actuation of Reactor Core Isolation Cooling (RCIC) initiation logic. At the time of event, the reactor was in a defueled condition with the vessel depressurized and a reactor coolant temperature of approximately 90 degrees Fahrenheit. <br /><br /> The automatic start of ESW pump A and ECC pump A was initiated by RCIC initiation logic as a consequence of loss of power to Division II reactor vessel level instrumentation. The root cause for this event is a procedural deficiency. At 1423 hours, after completion of deenergization of ED-1-B, the RCIC initiation signal was reset. <br /><br /> The load lists for deenergization of the loads from the ED1B08 disconnect number 5 will be revised to clearly indicate the result of opening this disconnect will be a RCIC initiation signal with the consequential automatic start of both the ESW Pump A and ECC Pump A. Load lists in the Plant Data Book (PDB) will be reviewed to determine if any other content changes were inadvertently introduced. Based on the result of this review, a revision to the PDB load list will be implemented as appropriate.
4401994011 | Perry | 04/21/1994 | 05/20/1994 | 9506070267 | <strong>Containment Isolation Valve Actuations During Restoration from Divisional Bus Outage</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1994, at 2225, several containment isolation valves automatically closed during the restoration from a Division II electrical bus outage. Investigation identified that auxiliary relays in the isolation logic were de-energized due to a newly installed transformer which had not been properly placed into operation. <br /><br /> A Human Performance Evaluation System (HPES) evaluation was performed to identify the causes that contributed to this event. It was determined that a combination of inadequate instructions and failure to follow procedure allowed the newly installed transformer to be placed into service without ensuring that it was supplying power to its electrical bus. <br /><br /> Corrective actions include design change and work management program improvements as well as an improved computer-based Work Order preparation system. Additionally, a post-maintenance test manual is being developed to provide a consistent set of requirements for testing following maintenance, and the fuse policy has been revised to address the installation of fuses for design changes. <br /><br /> This report is submitted in accordance with 10CFR50.73(a)(2)(iv).
4401994012 | Perry | 05/14/1994 | 11/14/1995 | 9511200138 | <strong>Equipment Malfunction Leads to Two Unexpected Annulus Exhaust Gas Treatment System Auto Starts</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1994, at 2256, during post-maintenance testing, train B of the Annulus Exhaust Gas Treatment System (AEGTS) automatically started twice. The cause of this event could not be conclusively determined; however, it appears that either the Flow Controls Incorporated (FCI) flow switch or the FCI flow switch calibration device (FCI calibrator) was not functioning properly. Testing by the vendor, the corporate measurement and test equipment laboratory, and by plant personnel failed to conclusively identify the root cause(s) for the AEGTS auto starts. <br /><br /> The AEGTS train A flow switch was replaced with a new flow switch which was calibrated utilizing a different flow switch calibrator. Both trains were then retested for proper operation. The removed FCI flow switch was tested and evaluated by plant personnel and by the vendor; however, no failure mechanisms were identified. The flow switch calibrator was modified and returned to the field. Signs, warning personnel not to use radios, have been posted at the doors to each AEGTS room and at each FCI flow switch. No further occurrences of inadvertent AEGTS initiation have been experienced. This report is submitted in accordance with 10CFR50.73(a)(2)(iv) as an Engineered Safety Features system actuation.
4401994013 | Perry | 05/18/1994 | 06/21/1994 | 9406290249 | <strong>Valve Status Not In Compliance With Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1994, with core alterations in progress, plant operators noted that the Low Pressure Coolant Injection (LPCI) 'C' loop injection valve was closed, but energized. The valve was required to be closed and de-energized to comply with a Technical Specification action statement to isolate penetrations affected by inoperable containment isolation valves during core alterations. Core alterations were suspended until containment integrity was re-established. The valve had been properly positioned and de-energized to comply with the Technical Specification action statement during preparations for core alterations on May 16, 1994. <br /><br /> The valve was subsequently energized during system line-ups to support test evolutions on May 16 and 17, 1994, and remained energized. On May 18, 1994 containment integrity was set and the plant entered the refueling mode at 1655 hours, and core alterations were authorized to commence at 1945 hours. A condition prohibited by the plant's Technical specifications existed from the time core alterations commenced on May 18, 1994 until core alterations were suspended on May 22, 1994. <br /><br /> The cause of the event is attributed to a program weakness. Procedures for tracking Limiting Conditions for Operations did not provide a method to verify that components under Operations administrative control are returned to the status required by Technical Specifications subsequent to manipulation.
4401994014 | Perry | 05/24/1994 | 11/17/1994 | 9411230271 | <strong>Failure to Meet Technical Specification Limits for Main Steam Line Leakage Rates</strong><br /><i>Abstract:&nbsp;</i>During the investigation of local leak rate testing (LLRT) results on the main steam line (MSL) containment penetrations, it was determined that the testing methodology utilized was not representative of design basis accident conditions. Therefore, the LLRT testing did not satisfy the surveillance requirements of Technical Specifications. Additionally, the as found leakage from MSLs B, C, and D exceeded the limit of Technical Specification 3.6.1.2. <br /><br /> The root cause of the nonrepresentative testing of the MSLs has been attributed to inadequate procedures. The procedures for the LLRTs performed on the MSLs allowed nonconservative testing of the main steam isolation valves (MSIV) in that additional seating force was allowed to be applied to the MSIVs by non-safety related instrument air. The cause of the excessive leakage of the MSLs was valve seat misalignment on three MSIVs and excessive packing leakage on a MSIV leakage control system valve due to a bent stem. <br /><br /> As a result of this event, a design change was implemented during the refueling outage to provide a safety related air supply to the actuators for the outboard MSIVs. Additionally, the MSIVs with identified excessive seat leakage and the identified packing leaks were reworked. LLRT testing of the MSLs was performed satisfactorily prior to restarting from the refueling outage.
4401994015 | Perry | 06/09/1994 | 09/30/1994 | 9410050092 | <strong>Potential Loss of Emergency Service Water System Due to Loss of Keepfill</strong><br /><i>Abstract:&nbsp;</i>At 1102 on June 2, 1994 Emergency Service Water (ESW) system keepfill supply was transferred to the normal supply, the Service Water (SW) system, from alternate keepfill supply after completion of a design change to the SW system. At 0001 on June 9, 1994 a plant operator reported that ESW loop A keepfill pressure was 10.5 psig; required pressure is greater than or equal to 13.5 psig. At 1030 keepfill pressure for ESW loops B and C was reported as out of specification low. An engineering review of system line-up and parameters determined that ESW A, B, and C loops were operable during the June 2 to June 9 time period. The engineering review also identified that during periods of low Lake Erie water temperature operability of the ESW system could be affected. Immediate corrective actions were to verify system valve line-up, start additional SW system pumps and finally to return ESW system keepfill to the alternate supply. <br /><br /> The cause of the reduced keepfill system pressure was identified as a deficiency in a SW system design change. The ESW keepfill system has been aligned to the alternate supply pending final determination of long term corrective actions. <br /><br /> This supplement revises the design change corrective action completion date, and acknowledges multiple ESW alternate supply sources.
4401994016 | Perry | 06/29/1994 | 07/29/1994 | 9408010248 | <strong>Overdue Surveillance Requirements Result in Noncompliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1994 control room operators identified that one page was missing from the weekly Technical Specifications rounds (TSR) sheets binder and determined that the surveillance requirements for Emergency Core Cooling system (ECCS) actuation instrumentation channel checks had not been performed on two previous shifts. The allowable surveillance interval had been exceeded and actions required by Technical Specifications (TS) to place the instrument channels in the trip condition and declare the associated ECCS systems inoperable had not been accomplished. The channel checks were immediately performed upon identification of the overdue surveillances, with satisfactory results. TS action requirements for associated ECCS systems were satisfied when the surveillance was satisfactorily completed. The instrument channels also provide actuation signals to two divisional diesel generators; however, no applicable action was required by the associated TS.<br /><br /> The event is attributed to personnel error, inattention to detail, in that pages had been removed from and reinserted into the TSR binder without pagecheck verification, and subsequent reviews of the TSR results by the control room shift supervisor did not identify the missing TSR sheet. <br /><br /> Corrective action included discussion of the event at shift briefings and counseling of involved personnel. In addition, training will be provided to other licensed operators on this event. Human factors enhancements for TSR sheets will be evaluated.
4401994017 | Perry | 07/11/1994 | 08/10/1994 | 9408160048 | <strong>Inadequate Work Order Results in Residual Heat Removal "B" Shutdown Cooling System Isolation</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1994, at 2154, an automatic isolation of the Residual Heat Removal (RHR) System Shutdown Cooling Suction Outboard Containment Isolation Valve occurred during the pressure testing of a reactor pressure transmitter instrument isolation valve. Although the suction valve responded as designed to the isolation signal, RHR 'B' pump trip logic did not function properly, and the pump was turned off by an operator. On July 11, 1994, at 2247, the RHR B loop of shutdown cooling was restored. <br /><br /> The cause of the event is personnel error, inattention to detail, on the part of the personnel who prepared, reviewed, and approved the work order. The work order made no provision for preventing the isolation signal, which was generated as a result of work activities, from causing the actual isolation. <br /><br /> The event has been reviewed with the personnel involved with the planning and approval of the work order with emphasis placed on thoroughness of reviews and responsibility for determining plant impact. The work order process for Instrumentation and Controls work orders will be reviewed to assess improvements in the areas of technical reviews and standardized methods of conveying plant impact information within work orders.
4401994018 | Perry | 07/29/1994 | 08/26/1994 | 9408310125 | <strong>Automatic Actuation of Annulus Exhaust Gas Treatment System Standby Train</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1994 the standby train of the Annulus Exhaust Gas Treatment System (AEGTS) automatically started due to a low flow condition on the operating AEGTS train. <br /><br /> The cause of the event was failure of a signal selector card in the operating AEGTS train control loop. The card failure resulted in a low flow condition on the operating train, and the standby train started as designed. <br /><br /> Corrective actions for the event included replacement of the failed signal selector card and subsequent retest to verify proper system operation. In addition, licensed plant operators will receive training on this event as a part of requalification training.
4401994019 | Perry | 06/20/1994 | 08/17/1994 | 9408240302 | <strong>Reactor Core Isolation Cooling System Secondary Containment Bypass Leakage</strong><br /><i>Abstract:&nbsp;</i>An engineering review of the Reactor Core Isolation Cooling system (RCIC) design determined that credit for RCIC as a closed system outside containment relied upon the non-safety, non-seismic gland seal air compressor (GSAC). This design is not in compliance with the requirements of 10CFR50 Appendix A General Design Criteria. Therefore, leakage paths which are sealed by the GSAC can be considered as potential Secondary Containment Bypass Leakage paths. These paths were not previously accounted for in Secondary Containment Bypass Leakage totals.<br /><br /> Corrective action was to revise the Updated Safety Analysis Report and appropriate administrative procedures to identify the leakage paths as potential Secondary Containment Bypass Leakage.
4401994020 | Perry | 08/31/1994 | 10/25/1994 | 9411030365 | <strong>Failure to Recognize diesel Generator Inoperability Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>At 1146 on August 31, 1994, Control Room Operators identified that the Division III diesel generator was inoperable as of 0918 due to a calibration being performed on the diesel tachometer. The one hour action required by Technical Specifications (TS) to verify the availability of off-site power sources was not completed by 1018. This action was completed at 1212. Other required actions were completed within the required times. <br /><br /> The cause of this event is personnel error; failure to identify that the calibration of the tachometer would place the Division III diesel generator in an inoperable condition. Immediate corrective actions were to complete Technical Specification required actions and restore the Division III diesel generator to operable status. <br /><br /> This revision clarifies the extent of diesel inoperability and corrects information regarding start signals for diesel generator support systems.
4401994021 | Perry | 11/08/1994 | 12/08/1994 | 9412120276 | <strong>Inoperable Division 2 Diesel Generator Results in a Technical Specification Violation and Operating License Violation</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1994, at 1045 a maintenance mechanic identified a bridge clamp was installed on the Division 2 diesel generator testable rupture disc (TRD). Installation of the clamp may have prevented the TRD from lifting, resulting in the Division 2 diesel generator being inoperable. Investigation of the condition identified that the clamp had remained installed after completion of maintenance on the TRD during the previous refuel outage. This condition resulted in Technical Specification violations during shutdown and operating conditions, and a violation of the Operating License. <br /><br /> The root cause of this event is inadequate work procedure and personnel error/failure to follow procedure. The work procedure utilized for TRD maintenance did not provide positive steps for controlling the work. Post maintenance inspection was not performed to the extent necessary to identify that the clamp remained installed. <br /><br /> Immediate corrective actions included verification that a similar condition did not exist on the Division 1 and 3 diesel generators and restoration of the Division 2 diesel generator to OPERABLE status at 2115 on November 9, 1994.
4401994022 | Perry | 11/11/1994 | 12/12/1994 | 9412160182 | <strong>Failure to Perform Diesel Generator Testing Utilizing Staggered Test Basis</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1994, as the result of a continuing review of an operational experience item, it was determined that testing of the diesel generators did not meet the definition of Staggered Test Basis as required by Technical Specification Surveillance Requirement 4.8.1.1.2.a. At the time of discovery of this event, each diesel generator had been tested within 31 days as required by Technical Specifications with the latest test being performed on the Division 2 diesel generator November 9, 1994. Therefore, the diesel generators were operable and no immediate surveillance testing was required. <br /><br /> The root cause of this event was a failure of the surveillance test program to properly schedule diesel generator testing in accordance with the Technical Specification definition of Staggered Test Basis. Performance of diesel generator testing in the past was not scheduled utilizing the Staggered Test Basis, but was only based on individual diesel generator surveillance frequencies. <br /><br /> As a result of this event, surveillance testing intervals for the diesel generators have been revised to ensure that testing will conform to the Staggered Test Basis as defined by the Technical Specifications.
4401994023 | Perry | 12/12/1994 | 01/11/1995 | 9501230060 | <strong>Slow Control Rod Scram Insertion Times Result in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1994, at 2045, during Technical Specification (TS) Surveillance testing of control rod scram insertion times, TS Limiting Condition for Operation (LCO) 3.1.3.2 ACTION c.1 was entered due to the number of 'slow' control rods exceeding twenty percent of a ten percent sample. Enforcement discretion was requested from the NRC and granted. On December 12, 1994, at 0845, the TS LCO ACTION was exceeded when the plant was not placed into HOT SHUTDOWN condition. <br /><br /> The cause of this event is attributed to degradation of the batch 314 Viton seating material located in the disk holder sub-assembly used in some of the Scram Solenoid Pilot Valves (SSPVs) replaced during the last refuel outage. The degradation of the seating material causes it to stick to the seating surface after long periods of solenoid energization, resulting in a delay in the valve opening after solenoid de-energization. The delay, in turn, causes the subject control rod to exceed its TS Control Rod Scram Maximum Insertion Time requirement to notch position 43. <br /><br /> The SSPVs containing batch 314 Viton seating material were replaced. Perry Nuclear Power Plant, General Electric, and the Automatic Switch Company are working to resolve the SSPV problem. Augmented Control Rod Scram Maximum Insertion Time testing will be performed to provide further confidence in the effectiveness of the corrective actions taken.
4431994001 | Seabrook | 01/25/1994 | 03/25/1994 | 9403290113 | <strong>Reactor Trip and Safety Injection due to Inadvertent MSIV Closure</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1994, at 0934 an automatic reactor trip from 100 percent power occurred when a main steam [SB] isolation valve (MSIV) closed during MSIV quarterly surveillance testing. The reactor trip, which was due to low-low narrow range steam generator level, was followed by a Safety Injection and Main Steam Isolation. This event was reported to the NRC at 1000 on January 25, 1994 as a one-hour notification pursuant to 10CFR50.72(b)(2)(ii), actuation of the Reactor Protection System (RPS) an Engineered Safety Feature (ESF) System. <br /><br /> There were no adverse safety consequences as a result of this event. <br /><br /> The physical cause of the MSIV malfunction was determined to be a combination of contaminated hydraulic fluid, a sticking main dump valve, and other related hardware issues. Collectively, these factors allowed the hydraulic pressure to bleed off and cause the MSIV to continue to close during testing. A root cause analysis was performed at two levels: the first to evaluate MSIV hardware specific issues and a second to evaluate organizational and programmatic performance. The root causes for this event include inadequate failure analysis of previous MSIV events, an inadequate preventative maintenance program for the MSIVs, and inadequate workmanship and quality assurance practices when the MSIV hydraulic subsystems were rebuilt in 1991. <br /><br /> North Atlantic has taken actions to correct the hardware specific MSIV conditions. North Atlantic will implement actions to address the root and contributing causes of this event.
4431994002 | Seabrook | 02/10/1994 | 04/08/1994 | 9404150247 | <strong>Inadequate Slave Relay Testing</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1994, while conducting a Solid State Protection System (SSPS) procedure review, it was determined that the method for performing Slave Relay Testing on three Charging System valves did not completely satisfy the Technical Specification Definition of a Slave Relay Test. Specifically, a continuity check was not performed on some testable actuation devices. <br /><br /> Changes made to the procedures for performing slave relay testing revised the method by which the valves were prevented from closing. The procedure change verified slave relay closure but did not verify continuity of the associated testable actuation devices. <br /><br /> The cause of the event is the omission of relevent information from surveillance procedures. Immediate corrective actions were to change procedures to correctly perform a Slave Relay Test and to retest the subject valves.
4431994003 | Seabrook | 02/17/1994 | 03/17/1994 | 9403230211 | <strong>Operation at Reduced Power Levels with Inoperable MSSVs</strong><br /><i>Abstract:&nbsp;</i>In September 1992, North Atlantic conducted Main Steam Safety Valve Setpoint testing as required by Technical Specification 4.0.5 and Section XI of the ASME Boiler and Pressure Vessel Code. During this testing the plant was in MODE 1, at approximately 65% RTP, with power levels being gradually reduced in preparation for Refueling Outage 2. North Atlantic determined on February 17, 1994, that the MSSV setpoint testing conducted in September 1992 was reportable pursuant to 10CFR 50.72 (b)(1)(ii)(A) and (B) (unanalyzed condition and a condition outside the design basis) and made the requisite 1 hour non-emergency notification. This determination was based on new information contained in Westinghouse Nuclear Safety Advisory Letter 94-01. NSAL 94-01, 'Operation at Reduced Power Levels With Inoperable MSSVs' provides notification that Technical Specification Table 3.7-1 which allows plant operation at reduced power levels as determined by the neutron flux high trip setpoint, may not be conservative at the reduced power levels. During the MSSV setpoint testing, North Atlantic operated in the configuration allowed by Seabrook Station Technical Specification Table 3.7-1. However, on the basis of the new information provided in NSAL 94-01, operation per Table 3.7-1 may have resulted in secondary side overpressurization in the event of a Loss of Load/Turbine Trip transient. Westinghouse concluded in NSAL 94-01 that this issue does not represent a substantial safety hazard and that there is no loss of safety function to the extent that there is a major reduction in the degree of protection provided to the public health and safety. <br /><br /> Short term corrective actions included the calculation of conservative Technical Specification Table 3.7-1 values. A calculation performed by North Atlantic using the algorithm provided in NSAL 94-01 to determine these values and a Technical Clarification TS-011 was approved and issued to ensure that the values are administratively controlled until such time that the Technical Specifications are revised.
4431994004 | Seabrook | 02/24/1994 | 03/25/1994 | 9403280163 | <strong>Missed Surveillance - Technical Specification 3.3.3.10, Radioactive Gaseous Effluent Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1994, North Atlantic Energy Service Corporation (North Atlantic) determined that Technical Specification Surveillance Requirement 4.3.3.10, which requires a source check of the plant vent Wide Range Gas Monitor Noble Gas Activity Monitor [VL] to be performed monthly, had been missed. <br /><br /> On November 9, 1993, the plant vent Wide Range Gas Monitor (WRGM) was declared inoperable and Technical Specification 3.3.3.10, Action b entered to implement a design modification. During the period of November 9, 1993 to December 6, 1993 the required actions associated with the inoperable WRGM were performed. On December 6, 1993 the WRGM was declared OPERABLE and required actions discontinued. On December 8, 1993 it was determined that the WRGM had been declared OPERABLE on December 6, 1993 without having performed all required source checks. A satisfactory source check was performed pursuant to Technical Specification 4.0.3, and the WRGM returned to OPERABLE status on December 8, 1993. <br /><br /> There were no adverse safety consequences as a result of this event. <br /><br /> The root cause of this condition has been determined to be an inadequate method used to track Technical Specification surveillances which are due to be performed when the equipment is removed from service for a design modification. <br /><br /> North Atlantic will revise the maintenance procedure to require verification that outstanding Technical Specification surveillances have been performed prior to returning equipment to OPERABLE status, following a design change or minor modification.
4431994005 | Seabrook | 03/01/1994 | 05/27/1994 | 9406020048 | <strong>Non-Compliance with Technical Specification Action Statement Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1994, North Atlantic Energy Service Corporation (North Atlantic) found the auxiliary sample pump for the Wide Range Gas Monitor Noble Gas Activity Monitor [VL] not running. Technical Specification Surveillance Requirement 4.3.3.10, Table 3.3-13 ACTION 35 requires continuous auxiliary sampling equipment be in service when the plant vent Wide Range Gas Monitor (WRGM) is inoperable. <br /><br /> North Atlantic entered Technical Specification 3.3.3.10 Action b on February 17, 1994 when the Wide Range Gas Monitor (WRGM) was taken out of service in order to implement a design modification. On March 1, 1994, lighting transformer 1-ED-X-17C, which supplies power to Lighting Panels L27 and L32, was removed from service for breaker and transformer inspections. The ragout isolation was completed on March 1, 1994 at 1008 deenergizing the WRGM auxiliary pump required by Technical Specification Action Table 3.3-13 Action 35. This condition remained undetected until 1220 that same day when a chemistry technician performing the Technical Specification LCO Surveillance identified the WRGM auxiliary sample pump not running. <br /><br /> There were no adverse safety consequences as a result of this event. <br /><br /> The root cause of this event was determined to be an inadequate descriptive name on the lighting panel schedule used to prepare the tagging order. <br /><br /> The immediate corrective action taken in response to WRGM auxiliary sample pump found not running was to restore power to the pump and place it back in operation. In addition, lighting panel schedule drawings will be revised and power supply circuit breakers for this monitor will be labeled to alert personnel of potential consequences of opening these breakers.
4431994006 | Seabrook | 03/17/1994 | 04/15/1994 | 9404220191 | <strong>Unanalyzed Tornado Loading Ventilation Dampers/Ductwork and Metal Partitions</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1994, North Atlantic Energy Service Corporation (North Atlantic) determined that a reportable condition existed involving the tornado design of ventilation dampers, associated ductwork, and Diesel Generator Building metal partitions. Specifically, design documentation to support the analysis of the effects of differential pressure loadings on these components in vented buildings, and the effects of positive pressures, during a tornado, could not be substantiated for the design basis tornado. <br /><br /> There were no adverse safety consequences as a result of this event. The components in question were capable of meeting the original design basis tornado criteria as defined in the Seabrook Station UFSAR at all times. <br /><br /> The root cause of this condition has been determined to be an oversight in the design control process during construction, either in not considering these components when analyzing tornado loading or in not properly controlling the design documents. <br /><br /> North Atlantic has prepared the design documentation to support the capability of these components to withstand the design basis tornado and will maintain these documents as part of the plant design basis.
4431994007 | Seabrook | 05/10/1994 | 06/09/1994 | 9406200182 | <strong>Voluntary LER 94-007-00, Inadequate High Radiation Area Controls</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1994, at 1100 a Health Physics (HP) Supervisor on rounds discovered a High Radiation Area barrier repositioned which allowed access into the Volume Control Tank (VCT) area without the proper controls. The HP supervisor replaced the barrier to the proper position and searched the room for personnel, finding none. Two independent surveys of the VCT tank room were performed yielding the same results. The surveys determined that the radiation levels in this room indicated a maximum dose of 100mR/hr at 30 centimeters. <br /><br /> Technical Specification 6.11 requires that each High Radiation Area, as defined in 10CFR20, be conspicuously posted and barricaded. The radiation levels specified in 10CFR20 for a High Radiation Area are 'in excess' of 100mR/hr at 30 centimeters. Based on the two radiation surveys performed after the barrier was found repositioned, the area did not meet the strict definition of a High Radiation Area and therefore posting and barricading, while unquestionably appropriate, was not required based on strict language of 10CFR20. Since the two independent surveys indicated radiation levels right on the High Radiation Area threshold, reporting of the barricade repositioning is in keeping with North Atlantic's conservative reporting philosophy. <br /><br /> There were no adverse safety consequences as a result of this event. <br /><br /> The root cause of this event was determined to be personnel error and/or inattention to detail. Although it could not be verified, it appears that the barrier was not properly replaced when personnel completed moving equipment in and out of the room. <br /><br /> The immediate corrective action taken in response to the repositioned High Radiation Area barrier was to immediately replace the barrier and to verify no workers present in the room. The barrier was subsequently replaced with a swing gate type. The Health Physics posting procedure will be revised to provide additional guidance on proper posting and barricade setup. This event was described in three site wide publications to stress to personnel that HP posting shall not be tampered with, modified or otherwise altered.
4431994008 | Seabrook | 04/25/1994 | 09/12/1994 | 9409190313 | <strong>Non-compliance with Technical Specification 3.8.4.2 Action Requirements</strong><br /><i>Abstract:&nbsp;</i>During replacement of the Nuclear Instrumentation Audio Count Rate/ Timer-Scaler, North Atlantic Energy Service Corporation (North Atlantic) discovered that non-safety related Nuclear Instrumentation (NI) drawers were connected to a safety related Class 1E power panel without a Class 1E protective device. In addition, the drawers did not have the required seismic and associated circuit interaction analysis. On May 18, 1994, North Atlantic determined that this was a condition prohibited by Technical Specification 3.8.4.2, Containment Penetration Conductor Overcurrent Protective Devices and Protective Devices for Class 1E Power Sources Connected to Non-Class 1E Circuits. <br /><br /> After reviewing similar circuit interactions during refueling outage 3, North Atlantic determined that during a design basis seismic event with the postulated simultaneous failure of all non-qualified non-Class 1E loads, the resultant interaction would cause a loss of power to safety related power panels. Because of the potential loss of safety related equipment, on August 25, 1994, North Atlantic reported this event pursuant to 10CFR50.72(b)(2)(i).<br /><br /> The non-conforming conditions were corrected prior to plant startup from refueling outage 3. There were no actual adverse safety consequences as a result of this event.
4431994009 | Seabrook | 05/04/1994 | 07/26/1994 | 9407290148 | <strong>Voluntary LER for Potential Safety Injection Pump Run-out Condition</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER is submitted to document a condition where the Safety Injection pumps (SIP) had the potential to exceed their run-out flow rate, hence resulting in the SIPs becoming degraded or inoperable. This condition could only have existed following a LOCA after hot leg recirculation had been initiated where the SIPs are receiving suction boost via both Residual Heat Removal pumps (RHRPs) [BP] and the Reactor Coolant System (RCS) had been depressurized. This condition could not have occurred for the small break LOCAs where the resultant RCS pressure would have precluded SIP run-out. <br /><br /> There are no adverse safety consequences as a result of this condition. This condition could only have caused the SIPs to experience run-out at a point in an accident scenario after they had fulfilled their intended safety function. of the Emergency Core Cooling System (ECCS) and are explicitly relied upon during the injection phase. The SIPs are not, however, explicitly relied upon during the recirculation phase of core cooling following RCS depressurization. For a depressurized RCS one Train of RHR is capable of providing adequate flow to ensure core cooling and mitigation of boron precipitation. <br /><br /> This condition does not represent a deviation from the single failure criteria since it only occurs after the SIPs have performed their intended safety function. The ECCS was always in compliance with 10 CFR 50.46 and GDC 35. North Atlantic has rebalanced the SI hot leg flow to ensure that the SIP run-out flow rate, provided by the vendor, is not exceeded.
4431994010 | Seabrook | 06/03/1994 | 01/16/1995 | 9501250148 | <strong>Potential Fuel Damage Due To RCP Turning Vane Capscrew Locking Cup Failure</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1994 North Atlantic Energy Service Corporation (North Atlantic) identified foreign material resting on the reactor vessel lower core plate. The material was discovered during a routine refueling inspection. Subsequent detailed inspections of the reactor vessel identified portions of one Reactor Coolant Pump (RCP) Turning Vane Cap Screw (TVCS) and two TVCS locking cups in the reactor vessel. An inspection of the fuel assemblies identified erosion on fourteen fuel assembly bottom nozzles, but no degradation to the fuel pins. <br /><br /> The TVCS attaches the RCP turning vane to the thermal barrier flange. The TVCS locking cups prevent the TVCS from turning during plant operation. North Atlantic has replaced the TVCS and locking cups on all four RCPs with a new design. The root cause of the TVCS and locking cup release is that the original equipment design did not adequately consider the flow induced vibration of the locking cup and the loss of TVCS preload torque. <br /><br /> There were no adverse safety consequences as a result of the event. The fuel assembly degradation was limited to the bottom nozzles with no degradation being found on the fuel pins themselves.
4431994011 | Seabrook | 06/21/1994 | 09/09/1994 | 9409210237 | <strong>Non-compliance With High Radiation Area Controls</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1994 at approximately 2340 EDT, the requirements of Seabrook Station Technical Specification 6.11, 'High Radiation Area', were not met. <br /><br /> Seabrook Station Technical Specification 6.11.1 requires individuals who enter high radiation areas to either have in their possession alarming dosimetry or a dose rate monitoring device, or to be escorted by a Health Physics (HP) Technician having one of these devices. Contrary to this requirement, a contractor mechanic entered a high radiation area, Reactor Coolant Pump (RCP) cubicle, for approximately 10 seconds without possessing alarming dosimetry or a dose rate radiation monitoring device. <br /><br /> There were no adverse safety consequences as a result of this event. The individual that entered the RCP cubicle did not receive any excessive doses. <br /><br /> The root cause for this event was determined to be a failure to implement self checking on the part of the contractor. <br /><br /> Immediate corrective actions included directing the individual to leave the area. Other corrective actions included counselling and disciplinary actions for the individual. In addition the event was discussed in a station publication, reviewed with station radiation workers stressing the importance of High Radiation Area controls and relationship to Technical Specifications. Long term corrective actions to prevent reoccurrence include: revising radiation worker training to include a discussion of this and similar events emphasizing the consequences for violating High and Locked High Radiation Area entry requirements and, routinely placing Radiation Protection poster boards at the HP Control Points to reinforce High Radiation Area control requirements.
4431994012 | Seabrook | 07/14/1994 | 08/12/1994 | 9408180086 | <strong>Non-compliance With High Radiation Area Controls</strong><br /><i>Abstract:&nbsp;</i>On July 14, 1994 at approximately 1100 EDT, the requirements of Seabrook Station Technical Specification 6.11, 'High Radiation Area', were not complied with. <br /><br /> Seabrook Station Technical Specification 6.11.1 requires individuals who enter High Radiation Areas to either have in their possession: alarming dosimetry, or a dose rate monitoring device, or to be escorted by an individual qualified in radiation protection procedures who has a radiation dose rate monitoring device. Contrary to this requirement, a test engineer entered a High Radiation Area for approximately 2 minutes without possessing the aforementioned requisite controls. <br /><br /> There were no adverse safety consequences as a result of this event. The individual that entered the posted area did not receive any excessive doses. <br /><br /> The root cause for this event was determined to be a failure to implement self checking on the part of the test control engineer. Specifically, the test control engineer failed to follow the procedural requirements which allow entry into a High Radiation Area.<br /><br /> Immediate corrective actions included escorting the individual from the Containment Building. Other corrective actions included counselling and disciplinary actions for the individual. In addition the following corrective actions will be implemented to help prevent events of this type from recurring: North Atlantic management will evaluate the need for a specific disciplinary policy which will address violations of the radiation protection program, Health Physics procedures will be revised to require workers to wear alarming dosimeters for entries into High Radiation Areas, a radiation worker refresher training program will be developed for presentation to radiation workers prior to their working in future refueling outages, and High Radiation Area postings will be enhanced to incorporate the use of alarming swing arm gates and evaluated for permanent use based on their effectiveness.
4431994013 | Seabrook | 05/09/1994 | 08/19/1994 | 9408240062 | <strong>Non-Compliance with Technical Specification 3.9.12 Action Requirement</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.9.12, Action b states: 'With no trains of the Fuel Storage Building Emergency Air Cleaning System OPERABLE, suspend all operations involving movement of fuel within the storage pool or crane operation with loads over the storage pool until at least one train of the Fuel Storage Building Emergency Air Cleaning System is restored to OPERABLE status and is in operation.'<br /><br /> On May 15, 1994 it was discovered that rod control cluster assemblies (RCCAs) and thimble plugs had been shuffled among fuel assemblies in the spent fuel pool while both trains the Fuel Storage Building (FSB) Emergency Air Cleaning System were inoperable. The FSB Emergency Air Cleaning System had not had the specified retests completed subsequent to a modification to the Fuel Storage Building rollup door and therefore, both trains were technically inoperable. During the time that both trains of the FSB Emergency Air Cleaning System were inoperable, one train was in operation and capable of performing its intended safety function. <br /><br /> On July 21, 1994 North Atlantic Energy Service Corporation (North Atlantic) concluded that the effects of dropping the RCCA change tool onto a spent fuel assembly could not be conclusively determined without extensive analysis. Therefore, in keeping with North Atlantic's conservative reporting philosophy, it was determined that the event was reportable pursuant to 10CFR50.73(a)(2)(i). <br /><br /> There were no adverse safety consequences as a result of the event.
4431994014 | Seabrook | 07/24/1994 | 09/02/1994 | 9409120151 | <strong>Missed Technical Specification Surveillance on Containment Air Locks</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1994, while returning to power operation from a refueling outage, it was discovered that the Containment equipment hatch air lock seal leakage surveillance had not been performed as required by Technical Specification Surveillance Requirement 4.6.1.3a. This surveillance which demonstrates operability of the Containment air locks, requires the air lock seal leakage measured to be less than 0.01 La within 72 hours following each closing during operational MODES 1 through 4. Contrary to this requirement, the plant entered MODE 4 on July 24, 1994 without performing the requisite operability surveillance on the Containment equipment hatch air lock. The surveillance was subsequentially successfully performed on August 5, 1994 and the Containment equipment hatch air lock was declared OPERABLE. <br /><br /> There were no adverse safety consequences as a result of this event. The requisite Containment equipment hatch air lock leakage test was immediately performed upon determination that the surveillance had not been performed. This test demonstrated that the seal leakage was less than the Technical Specification requirements for the same. <br /><br /> The root cause for this event was determined to be an inadequate surveillance tracking mechanism used to differentiate between the two required surveillance activities. <br /><br /> The Containment equipment hatch air lock seal leak test was performed immediately upon determination that the surveillance had not been completed. An additional corrective action will include separating the containment air lock surveillance into two separate activities.
4431994015 | Seabrook | 09/09/1994 | 10/11/1994 | 9410170381 | <strong>Missed Technical Specification 4.0.5 Surveillances on Main Steam Drain Valves</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1994 it was discovered that two Main Steam Drain (MSD) valve stroke time surveillances had not been performed as required by Technical Specification Surveillance Requirement 4.0.5. This surveillance demonstrates the operability of the MSD containment isolation valves and requires these valves to be stroke tested every 92 days, or 115 days including the 25% extension allowed by Technical Specification 4.0.2. Contrary to this requirement, the requisite operability surveillances on MSD-V44 and MSD-V47 were not performed within the required timeframe, including the 25% extension allowed by Technical Specification 4.0.2, by approximately 5 days. On May 17, 1994 the surveillance was successfully completed on MSD-V44 and MSD-V47. Thus the next required surveillance end date should have been September 9, 1994. These surveillances were subsequently successfully performed on September 14, 1994.<br /><br /> There were no adverse safety consequences as a result of this event. The requisite containment isolation valve stroke tests were immediately performed upon determination that the surveillance had not been performed. This test demonstrated that the stroke time was less than the Technical Specification requirements for the same. <br /><br /> The root cause for this event was determined to be an inadequate procedure which did not provide the necessary guidance required to complete repetitive task sheets and/or provide specific guidance for situations when taking credit for previously performed surveillances. <br /><br /> The MSD valve stroke tests were performed immediately upon determination that the surveillance had not been completed. In addition, the Data Management Group reviewed all outstanding date changes to ensure there were no other activities that required credit date updates. Long term corrective actions include: revising procedures governing Repetitive Task Sheets and surveillance activities, and providing training to Work Group Supervisors regarding these procedure changes.
4431994016 | Seabrook | 10/19/1994 | 12/29/1994 | 9501050286 | <strong>Non-Compliance with Technical Specification 3.3.2 Action Requirements</strong><br /><i>Abstract:&nbsp;</i>During the process of implementing the corrective actions for a Station Information Report (SIR) concerns were raised over compliance with Technical Specification action requirements associated with the undervoltage (UV) protection circuitry for the station's 4160VAC emergency busses {EB}. <br /><br /> Since December 1988, when Seabrook Station initially entered MODE 4, surveillance procedures MX0513.06 and MX0513.07 have been performed monthly to satisfy the Trip Actuating Device Operational Test (TADOT) surveillance requirements of Technical Specification 4.3.2.1. <br /><br /> The performance of those procedures resulted in both channels of either the first or second levels of UV protection associated with one emergency bus being rendered simultaneously inoperable for brief periods of time during the performance of surveillance testing. The OPERABILITY requirements of 3.3.2, Table 3.3-3, Functional Units 9a and 9b were not satisfied during those instances and the plant was operated in a condition prohibited by the Technical Specifications. <br /><br /> There were no adverse safety consequences associated with this event. At least one emergency bus was available at all times to provide power to equipment necessary for safe shutdown of the plant. <br /><br /> The root cause of this event was determined to be the acceptance of inappropriate Technical Specification requirements regarding emergency bus UV protection.
4431994017 | Seabrook | 11/02/1994 | 12/02/1994 | 9412050333 | <strong>Service Water Cooling Tower Pump Bolt Degradation</strong><br /><i>Abstract:&nbsp;</i>During Seabrook Station Refueling Outage 3 an inspection of the cooling tower basin by divers revealed two degraded column flange bolts on the "A" cooling tower Service Water Pump KE! (1SW-P-110A). Subsequent metallurgical testing revealed that these bolts experienced intergranular corrosion due to a "sensitized" condition that resulted from an improper manufacturing process.<br /><br /> North Atlantic initiated actions to test and replace suspect safety-related bolting material on all of the station's six Service Water (SW) pumps. <br /><br /> All four ocean SW pumps were refurbished with no widespread bolting material degradation observed. However, the refurbishment of the "A" cooling tower SW pump (1SW-P-110A) revealed additional degradation to the extent that the pump may not have been able to perform its intended safety function following a seismic event. Since the condition of bolting material for the redundant "B" cooling tower SW pump (1SW-P-110B) was not known, it was conservatively declared inoperable. Subsequent refurbishment of 1SW-P-110B revealed some bolting material degradation, however, the number of functional bolts supported prior OPERABILITY. <br /><br /> The inoperability of the "A" cooling tower SW pump for an indeterminate period of time and the unknown condition of the "B" pump was reported on November 2, 1994, as a condition that is outside of the design basis of the plant pursuant to 10CFR50.72(b)(1)(ii). <br /><br /> There were no adverse safety consequences of this event. <br /><br /> The cause of the event was determined to be the bolt manufacturer's failure to perform an adequate heat treatment on the bolting material as required by the material specification.
4431994018 | Seabrook | 11/28/1994 | 12/28/1994 | 9501050202 | <strong>Missed Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On November 28, 1994 at approximately 1600 hours, part of the Main Plant Computer System (MPCS)[ID] experienced a power loss that caused the Rod Deviation Monitor to become inoperable. <br /><br /> The Rod Deviation Monitor is a MPCS software program that is used to compare the rod position demanded by the Rod Control System to the rod position detected by the Digital Rod Position Indication (DRPI) system. <br /><br /> Technical Specification 3.1.3.1 Limiting Condition for Operation requires that demanded rod position be in agreement with detected rod position within + or - 12 steps. The surveillance requirement that verifies this condition is normally performed every 12 hours, however, if the Rod Deviation Monitor is inoperable the Surveillance must be performed every 4 hours. <br /><br /> When the aforementioned power loss occurred, the MPCS assigned the shutdown rod position data as 'unreliable' and a 'Rod Deviation Monitor Inoperable' alarm was received on the Video Alarm System (VAS)in the main control room. Operators did not immediately recognize that receipt of this alarm necessitated the initiation of the 4 hour surveillance. The 12 hour surveillance continued until 1030 hours on November 29, 1994, at which time the 4 hour surveillance was initiated. <br /><br /> Since a period of time exceeding the 4 hour Surveillance requirement elapsed while the Rod Deviation Monitor was inoperable, a condition prohibited by Technical Specifications existed. <br /><br /> There were no adverse safety consequences associated with this event. During the period of time where the 4 hour surveillance was missed, there was no call for rod motion. In addition positive indication of rod position remained available while the Rod Deviation Monitor was inoperable. <br /><br /> Two causes of the event have been determined; the lack of an alarm response procedure for the 'Rod Deviation Monitor Inoperable' alarm, and the misunderstanding of rod position data as presented by the MPCS.
4431994019 | Seabrook | 01/24/1994 | 02/27/1995 | 9503080154 | <strong>Voluntary LER For Electrical Relay Failures</strong><br /><i>Abstract:&nbsp;</i>This LER is being submitted as a voluntary LER by North Atlantic Energy Services Corporation (North Atlantic). There have been numerous test failures of General Electric model 12HEA61BRD235X2 and 12HEA61BRD237X2 high speed lockout relays. These relays are installed in safety related switchgear, and function to trip circuit breakers when energized by an equipment protective relay. <br /><br /> There are no adverse safety consequences as a result of this event. North Atlantic has determined that a worst case failure of a lockout relay would not result in the plant being outside of its design basis or in an unanalyzed condition. The worst case scenario results in a loss of off-site power. North Atlantic has determined that this condition did not constitute a substantial safety hazard pursuant to 10CFR21. <br /><br /> The root cause of this condition has been determined to most likely be damaged roller bearings on the relay coil assembly. This damage was most likely a combination of the following:<br /><br /> (1) Insufficient bolt torque for the switch tie rods. <br /> (2) Omission by design of the bottom support bracket. <br /> (3) Excessive force against the latch after manually resetting. <br /> (4) Original bearing design <br /><br /> Other contributing causes may have been hardened grease, dirt accumulation and improper gear meshing. <br /><br /> North Atlantic has replaced all installed General Electric HEA relays with Electroswitch LOR-1 relays. North Atlantic has determined that the Electroswitch relays meet or exceed the characteristics of the HEA relays and have had fewer failures.
4451994001 | Comanche Peak 1 | 02/01/1994 | 02/28/1994 | 9403110212 | <strong>Turbine Trip/Reactor Trip Due To Indication Of Primary Flow Low In The Generator Stator</strong><br /><i>Abstract:&nbsp;</i>At 9:38 p.m. February 1, 1994, an indicated low flow condition on primary water to the Main Generator Stator caused a Turbine/Reactor trip. There was no actual loss of stator flow. TU Electric believes that the trip was caused by a spurious signal. Corrective actions included monitoring key points for power supply and instrument signal stability, and evaluation by the vendor.
4451994002 | Comanche Peak 1, Comanche Peak 2 | 05/10/1994 | 06/06/1994 | 9406070122 | <strong>Broken Missile Shield Door Latching Mechanism Caused The Door To Be Considered Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1994 the control room missile shield door was declared inoperable. The broken missile shield door latching mechanism was deemed to be the cause of inoperability. Comanche Peak Steam Electric Station (CPSES) Unit 1 was placed into the applicable action statement of Specification 3.0.3. <br /><br /> Corrective actions were to repair the door, evaluate for potential design changes, preventive maintenance, and to restrict the use of the missile shield doors.
4451994003 | Comanche Peak 1 | 05/03/1994 | 06/27/1994 | 9407010105 | <strong>Less Than Adequate Procedures Led To Deficient Surveillances Of Unit 1 Power Operated Relief Valves</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.0.5b requires Inservice Testing (IST) of ASME Code Class 1, 2 and 3 pumps and valves to be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code and applicable Addenda as required by 10CFR50.55a.<br /><br /> On June 8 and 12, and November 5, 1990, during stroke testing of Reactor Coolant System Power Operated Relief Valves (PORV) (EIIS: (RV)(AB)), the stroke times recorded and accepted were in excess of 2 seconds. The safety function stroke time acceptance criteria for these valves is equal to or less than 2 seconds. <br /><br /> The cause of the events was deemed to be a less than adequate IST procedure. The procedure governing the IST allowed rounding off or rounding down to the next whole number if the fractional times were less than or equal to 0.5 seconds, and did not consider limiting values (i.e., maximum allowed stroke time).<br /><br /> Corrective actions have been in place since August 1993 prohibiting rounding down when a maximum allowable stroke time has been exceeded.
4451994004 | Comanche Peak 1, Comanche Peak 2 | 08/22/1994 | 09/22/1994 | 9409260264 | <strong>Failure Of Annunciator - Required Technical Specification Actions For Quadrant Power Tilt Ratio Were Not Performed</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1994, following a Unit 1 load reduction at approximately 11:00 a.m., the Quadrant Power Tilt Ratio (QPTR) exceeded the Technical Specification (TS) 3/4.2.4. limits of 1.02. However, the QPTR annunciator did not annunciate and the Plant Computer calculated points did not appear on the Dynamic Alarm Display (DAD) screen or on the Control Room Plant Computer Alarm Printer. The Control Room Operators (utility, licensed) identified the problem at 3:15 p.m. the same day. At the time of discovery, Unit 1 was at approximately 50 percent power. <br /><br /> The reason the QPTR alarm did not annunciate as required was the Plant Computer alarm was set at 1.05 in lieu of 1.02. <br /><br /> The immediate action was to modify the Plant Computer database constant point to establish the QPTR alarm at 1.02; and compliance with the TS Action Statement was then reestablished for both units.
4451994005 | Comanche Peak 1, Comanche Peak 2 | 08/31/1994 | 09/30/1994 | 9410050030 | <strong>Surveillance For Steam Generator And For Containment Pressure Channels Were Not Performed In 1992/1993 Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1994, during a Quality Assurance audit it was discovered that Technical Specification surveillances were not performed on Unit 1 for the following transmitters; three of the Steam Generator Water Level Hi-Hi channels (EIIS)(SGLI)(SB)) and for Containment pressure (EIIS)(PI(VA)). <br /><br /> Technical Specifications require all instrument channels that monitor the Containment pressure and the Steam Generator (SG) Water Level have response time testing surveillances completed in 'n' times 18 months where 'n' equals the number of channels. Personnel responsible for this surveillance activity failed to properly schedule the surveillances based on the frequency and function. The corrective actions were to review the surveillance database and correct the frequency as required. .
4451994006 | Comanche Peak 1 | 11/29/1994 | 12/29/1994 | 9501050235 | <strong>Turbine Trip/Reactor Trip Due To Low Cooling Water Stator Flow Indication</strong><br /><i>Abstract:&nbsp;</i>At 9:21 p.m., CST November 29, 1994, an indicated low flow condition on cooling water to the Main Generator Stator caused a Turbine/Reactor trip. There was no actual loss of stator flow. TU Electric believes that the trip was caused by a sensing line hydraulic anomaly, most likely gas bubbles. Immediate actions were to change the negative slope of the sensing lines to a positive slope to prevent gas accumulation. Corrective actions were to schedule a design modification, which will install separate sensing lines in the primary water flow stator circuit and will install alarms to warn the operators of impending problems with primary water tank level and temperature.
4461994001 | Comanche Peak 2 | 01/06/1994 | 02/02/1994 | 9402100142 | <strong>Procedure Weakness Caused The Personnel Air Lock Outer Door Equalizing Valve To Be Left In Mid-Position</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1994, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, power operations, with reactor power at 100 percent. <br /><br /> During testing activities performed earlier on the Containment Personnel Air Lock (PAL) a pressure equalizing valve was inadvertently left in the open position. The cause of the event was deemed to be procedural weakness. Corrective action was procedural enhancement.
4461994002 | Comanche Peak 2 | 01/06/1994 | 02/07/1994 | 9402220126 | <strong>Engineered Safety Feature Actuation Due To Emergency Diesel Generator Voltage Card Failure</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1994, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation with reactor power at 100 percent. <br /><br /> At approximately 4:23 a.m. on January 6, 1994, while performing a post maintenance Train A Diesel Generator Load Performance Test, Diesel Generator 2-01 tripped on an apparent field ground while carrying the safety bus loads. <br /><br /> The corrective action was to replace a voltage regulator card.
4461994003 | Comanche Peak 2 | 03/05/1994 | 03/31/1994 | 9404050025 | <strong>Initiation Of Manual Reactor Trip Due To Main Turbine Load Swings</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1994, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, with reactor power at 75 percent. The Balance of Plant Operator noticed Turbine/Generator (TG) load swings. Abnormal Operating Procedure was entered to stabilize the plant while the problem was being diagnosed. Because possible problems with the Electro-Hydraulic Control (EHC) Converter #1 were indicated, load control was switched to the Mechanical-Hydraulic Controller. The load swings temporarily subsided. The load swings returned and were increasing and the load was shifted to EHC Converter #2. This action did not stabilize the load swings. Without the ability to control the load swings the Unit Supervisor directed a manual reactor trip.After extensive troubleshooting, and correcting Unit 2 was restarted at 3:45 p.m., CDT on March 13, 1994. During the restart with the load at approximately 120 MWe, all four control valves abruptly closed. The BOP Operator immediately tripped the turbine.<br /><br /> It was determined that a feedback (Collins) coil in the EHC system had shorted/failed. Corrective actions involved troubleshooting of the EHC system and replacement of the feedback coil.
4461994004 | Comanche Peak 2 | 04/22/1994 | 05/23/1994 | 9405270300 | <strong>Reactor Protection System Actuation Due To A Spike On Source Range</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1994, while performing the actuation logic and master relay testing of Train B solid State Protection System (SSPS), an inadvertent reactor trip occurred due to the failure of Source Range N32 to deenergize when Train B SSPS input error inhibit switch was placed in inhibit. N32 spiked to greater than the source range trip setpoint causing reactor trip breaker 'A' and bypass trip breaker 'B' to open. <br /><br /> The event was most likely caused by a faulty relay from the SSPS which had an abnormally high resistance for a closed contact due to some oxidation buildup on the contacts. <br /><br /> Corrective actions were to replace the relay.
4461994005 | Comanche Peak 2 | 05/19/1994 | 05/05/1995 | 9505150046 | <strong>Continued Vibration Induced Fatigue Led To Failures Of Welds In The Containment Spray System</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1994, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 5 during its midcycle outage, when a weld leak was identified in the Containment Spray (CT) system. The immediate corrective actions were to repair the weld and inspect for additional leaks. On May 19, 1994, additional leaks were discovered on the second train. Based on the discovery of the leak in the second train, this event was deemed reportable pursuant to 10CFR50.73. <br /><br /> The cause of the leaks was determined to be vibration induced fatigue which resulted from the interaction between the CT pumps and associated suction/discharge piping. TU Electric has implemented corrective actions including configuration changes which have significantly reduced the effects of vibration in the system.
4461994006 | Comanche Peak 2, Comanche Peak 1 | 05/26/1994 | 05/30/1995 | 9506070024 | <strong>Under Voltage Relays Were Found To Be Out Of Calibration Which Resulted In A Failure To Fully Satisfy Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1994, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 5, during its midcycle outage. During the performance of Unit 2 Train B undervoltage relay calibration and response time surveillance testing, the as found calibration data appeared to be outside the Technical Specification allowables. fourth refueling outage. While performing the Unit 1 Train A and Train B undervoltage relay calibration and response time surveillance testing, the same condition of the as found calibration data outside the Technical Specification allowables was observed, for the undervoltage relays (Train A anomaly was discovered on March 14, and Train B on March 22, 1995). The cause of these events was determined to be the methodology/instrumentation used to calibrate the Asea Brown Boveri relays, type ITE-27H and ITE-27N. Corrective actions were to adjust the relays, and provide additional guidance with respect to calibration. This voluntary report is being submitted due to recognition of the significance and generic interest of the event.
4461994007 | Comanche Peak 2 | 06/17/1994 | 07/13/1994 | 9407190136 | <strong>Engineered Safety Feature Actuation Due To Hi-Hi Steam Generator Level Signal</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1994 Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 4, and was in the process of recovery from its midcycle outage. A Spurious Steam Generator (EIIS:(SG)(SB)) HI-HI Signal (P-14) (EIIS:(LA)(SB)) was generated while heating up and pressurizing the Main Steam System. <br /><br /> The cause of the spurious signal was due to the shortcoming of the procedure, which did not specifically require that pressure on each side of the Main Steam Isolation Valve (MSIV) to be monitored during secondary plant heatup with the Main Steam Isolation Bypass valve prior to opening the MSIV (EIIS:(ISV)(SB)). <br /><br /> Corrective actions were to revise the procedure to include the required parameters for monitoring prior to opening the MSIVs.
4461994008 | Comanche Peak 2 | 06/18/1994 | 08/12/1994 | 9408180053 | <strong>Entry Into Technical Specification 3.0.3 Due To High Level On Two Safety Injection Accumulators</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1994, at approximately 4:58 p.m., the Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 3, during plant heatup to normal operating temperature and pressure. <br /><br /> The Unit Supervisor (utility, licensed) identified that two Safety Injection (SI) Accumulators (EIIS:(ACC)(BQ)) had exceeded the Technical Specification allowable level limits of 61 percent (indicated level was identified as 62 percent). CPSES Unit 2 was placed into Technical Specification 3.0.3. <br /><br /> The cause of the event was attributed to back leakage through the check valves (EIIS:(V)(AB)) in the Reactor Coolant System (RCS) (EIIS:(AB)). <br /><br /> The immediate corrective actions were to drain the SI Accumulators to their normal level, and provide caution statements with respect to SI Accumulator fill to shift crews via shift orders.
4461994009 | Comanche Peak 2 | 06/19/1994 | 07/13/1994 | 9407190014 | <strong>Entry Into Technical Specification 3.0.3 Due To Two Feedwater Isolation Valves Being Declared Inoperable While The Unit 2 Reactor Was At Power</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1994, Comanche Peak Steam Electric Station was in Mode 1, at approximately 20 percent power. At approximately 6:40 p.m. on June 19, 1994, two Feedwater Isolation Valves (FWIVs) were declared inoperable when the low pressure nitrogen alarm did not clear. The cause of the event was concluded to be lack of specificity in the procedures, which did not direct the operators to verify nitrogen pressure prior to opening the FWIVs. Corrective actions were to establish proper nitrogen pressure and revise the procedures.
4461994010 | Comanche Peak 2 | 06/27/1994 | 07/22/1994 | 9407250124 | <strong>Reactor Trip/Turbine Trip Due To A Short In The Current Transformer Cable</strong><br /><i>Abstract:&nbsp;</i>On On June 27, 1994 at approximately 4:54 p.m. Comanche Peak Steam Electric Station (CPSES) Unit 2 experienced an automatic reactor trip from a turbine generator trip. The plant sequence of event recorder logged a generator differential lock-out relay actuation. All required systems functioned as designed. <br /><br /> The event was caused by a short in the lead of the B phase neutral current transformer on the generator. <br /><br /> Corrective actions were to replace the lead in accordance with plant procedures.
4461994011 | Comanche Peak 2 | 07/22/1994 | 08/19/1994 | 9408240345 | <strong>Personnel Error Resulting In Failure To Satisfy Technical Specification Staggered Test Basis Requirement</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1994, a surveillance test coordinator discovered that Technical Specification surveillance testing of the Solid State Logic Protection System had not satisfied the staggered test basis requirement. Early testing of one train and subsequent postponement of testing the alternate train resulted in testing of the alternate train at a subinterval which exceeded the specified subinterval plus maximum allowable extension. The event was caused by personnel error during test scheduling. Immediate corrective action was taken and satisfactory performance of the surveillance was accomplished on July 22, 1994. Personnel involved were counselled as to their responsibilities in scheduling staggered test basis surveillances.
4461994012 | Comanche Peak 2 | 08/15/1994 | 09/13/1994 | 9409190202 | <strong>Manual Reactor Trip And Auxiliary Feedwater Auto-Start Due To Steam Generator Lo-Lo Level Signal</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1994, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 with reactor power at 75 percent. The unit was in the process of being shut down due to an oil leak on Main Transformer (EIIS:(XFMR)) (2MT2) High Voltage Phase Bushing. At 10:45 a.m. CST the unit was manually tripped to deenergize the main transformer in order to prevent damage to the bushing and/or the transformer. During the unit trip, Reactor Coolant Pump (EIIS:(P)(AB)) (RCP 2-01) tripped due to an electrical transient caused by the Unit trip. Repeated Auxiliary Feedwater pump (EIIS:(BA)) auto-start Engineered Safety Feature (ESF) initiation signals occurred due to Steam Generator (EIIS:(SG)(SB)) LO-LO level signals. <br /><br /> The oil leak was the result of cracking/failure of the bushing housing on 2MT2. The failed bushing assembly has been sent to the vendor for analysis. The ESF actuation occurred as a normal result of the Steam Generator level shrink from the reactor trip following the closure of the turbine stop valves. Subsequent ESF initiation signals occurred due to a failed control card in the Steam Dump control circuit (EIIS:(SB)(ECBD)). The corrective actions were to replace the failed circuit card.
4461994013 | Comanche Peak 2 | 08/17/1994 | 09/16/1994 | 9409270083 | <strong>Four Main Steam Valves Were Declared Inoperable When They Failed Their Technical Specification Setpoint Surveillance Testing (T/S 4.05)</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1994, the Main Steam Safety valves (MSSVs) (EIIS:(RV)(SB)) were tested in accordance with the approved procedure. Four of twenty valves tested had lift settings outside the plus or minus 1 percent setpoint tolerance stated in CPSES Technical Specifications. The cause was determined to be a drift in the setpoints. <br /><br /> The lift setpoints observed do not indicate a material problem with the valves. The test results were within the 3 percent criteria requirement for valve testing per Part 1 of ASME/ANSI OM-1987. Discussions with the valve vendor concluded that deviations within this range do not call into question the condition or functionality of the valves. This conclusion is supported by the fact that the valves demonstrated satisfactory test results after adjustment.
4461994014 | Comanche Peak 2, Comanche Peak 1 | 10/07/1994 | 11/07/1994 | 9411140139 | <strong>Manual Reactor Trip Initiated Due To A Digital Rod Position Failure Indication</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1994, Comanche Peak Steam Electric Station Unit 2 was in Mode 2 startup and less than 1 percent reactor power. Plant shutdown was in progress for the first refueling outage. Control bank D was at 118 steps. At 5:20 p.m., a manual reactor trip was initiated due to digital rod position indication failure for control bank D control rod H-8. The cause of the event, i.e., Digital Rod Position Indication (DRPI) (EIIS:(ZI)(AA)) for control rod H-8 not responding correctly, was attributed to a loose connector. The loose connection will be corrected during the refueling outage and the DRPI tested prior to reactor startup.
4461994015 | Comanche Peak 2 | 10/14/1994 | 11/14/1994 | 9411210377 | <strong>Containment Ventilation Isolation Due To No Available Bypass Power When Normal Power Was Deenergized</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1994, a Containment Ventilation Isolation (CVI)(EIIS:(IK))signal occurred when a clearance (to deenergize) was hung on Instrument Inverter IV2C3 (EIIS:(INVT)(IK)). <br /><br /> The required bypass power for the inverter was not available due to a scheduled bus outage. When the panel was transferred to bypass power, a relay was deenergized causing a CVI to occur. The event was caused when the outage planning personnel and personnel approving the clearance, did not consider that placing the clearance was not compatible with the electrical bus outage. Cognizant personnel were made aware of this event, as a lessons learned.
4461994016 | Comanche Peak 2 | 10/16/1994 | 11/14/1994 | 9411220156 | <strong>Missed Refueling Machine Auxiliary Monorail Hoist Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1994, with the reactor vessel head removed, control rod drive shafts were being unlatched from the control rods in preparation for core offloading. This evolution involves the use of a load indicator in line with the refueling machine auxiliary hoist. During this process, some difficulty was experienced due to the size of the load indicator. Supervisor to change the load indicator to a smaller one which had been staged in the area. This smaller indicator had been properly calibrated but had not been load tested within the previous 100 hours as required by Technical Specification (TS) 4.9.6.2. <br /><br /> During subsequent shift relief, it was discovered by one of the oncoming Fuel Handling Supervisors that the TS surveillance (load test) had not been performed on this second indicator. The Fuel Handling Supervisor directing operations in Containment was immediately notified to cease the control rod unlatching evolution. This was done and the second indicator was replaced by the original indicator prior to continuing operations. <br /><br /> The root cause of this event was personnel error. Corrective actions included counseling of the personnel involved.
4461994017 | Comanche Peak 2 | 10/20/1994 | 12/01/1994 | 9412070314 | <strong>480 Volt Switchgear Declared Inoperable Due To Inadequate Supports On The Current Transformer</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1994, at approximately 9:00 p.m., the Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 6 for the first refueling outage. <br /><br /> Maintenance personnel (utility, non-licensed) identified that a spare current transformer [EIIS:(SCT)] in the rear of one of two Train B 480 volt switchgear [EIIS:(SWGR)] was inadequately supported. The switchgear was subsequently determined to be inoperable for a period of time which exceeded Technical Specification allowed outage times associated with safety-related loads connected to the switchgear. <br /><br /> The cause of the event was that this deficiency, which was identified and documented during a vendor walkdown in November 1990, was not adequately described in the work documents initiated to correct the deficiency and therefore was not corrected as intended.
4461994018 | Comanche Peak 2 | 10/25/1994 | 11/21/1994 | 9411300294 | <strong>Pressurizer Safety Valves Discovered To Be Inoperable From As-Found Testing</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1994, using saturated steam as the test medium, three Pressurizer Safety Valves (PSV) were found to have setpoints outside the setpoint tolerance allowed by Technical Specifications (TS). All three PSVs were subsequently reset within TS limits.
4461994019 | Comanche Peak 2 | 11/06/1994 | 12/05/1994 | 9412090009 | <strong>Containment Ventilation Isolation Caused By Generator Rotor Ground Circuit</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1994, a Containment Ventilation Isolation (CVI)(EIIS:(IK)) signal occurred due to a spurious generator rotor ground signal.<br /><br /> The rotor ground signal occurred when the sensing leads were inadvertently shorted together, which resulted in a loss of the non safety bus which was supplying power to the radiation monitor relay 2-RX13/RMS. When the power was lost to 2-RX13/RMS it caused a containment ventilation isolation signal. Cognizant personnel were made aware of this event, and management's expectations with respect to good maintenance practices for taping the lifted leads was re-emphasized. Additionally, TU Electric is evaluating changes to the processes when backfeeding the auxiliary transformer is in progress.
4461994020 | Comanche Peak 2 | 11/09/1994 | 12/05/1994 | 9412090011 | <strong>Engineered Safety Feature Actuation While Performing Testing On Train B</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1994, while I&C technicians were performing testing of the blackout sequencer on Unit 2 Solid State Safeguard Sequencer Train B, an Engineered Safety Feature (ESF) actuation occurred. In response to the actuation the control room Heating, Ventilation and Air Conditioning (HVAC)(EIIS:(VI)) system shifted to emergency recirculation and Train B Auxiliary Feed Water (AFW) flow control valves (EIIS:(FCV)(BA)) shifted to AUTO. A Reactor Operator (RO) instructed the technicians to stop testing because of the HVAC alarms. After observing the sequencer step lights indicating a Blackout Sequence (BOS) was in progress and with concurrence of the RO the technician immediately placed the BOS block switch in the 'BLOCK' position to stop the sequence. Placing the switch in the block position would not have prevented or stopped an actual safeguard actuation. <br /><br /> Although the cause of the event could not be determined, TU Electric believes that the event was caused by a spurious signal. The corrective action to prevent recurrence of this event is to revise test procedures to place the BOS switch in the 'BLOCK' position prior to testing.
4461994021 | Comanche Peak 2 | 11/19/1994 | 12/19/1994 | 9412280395 | <strong>Missed Shiftly Routine Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At approximately 07:45 p.m. CST on November 19, 1994, it was noted that MODE 4 Technical Specification (TS) surveillances had not been completed as required. The surveillances were previously completed at 00:32 a.m. that same day in preparation for entry into MODE 4 in accordance with TS 4.0.4. Since the allowable time between these surveillances is 15 hours, they were supposed to be completed by 3:32 p.m. November 19, 1994, instead, they were completed by approximately 7:30 p.m. <br /><br /> This event occurred because supervision thought that the time interval between surveillances was to be measured from approximately 8:00 a.m., the time MODE 4 was declared, rather than from the time of the last completed surveillances and thus did not perform them on that shift. <br /><br /> Subsequent reviews of various logs indicated that all of the missed surveillances but one (containment sump total flow) had been accomplished through other logs and activities and credit was taken for their accomplishment. <br /><br /> The root cause of this event was personnel error. Corrective actions included counseling of personnel involved and training of all licensed personnel.
4461994022 | Comanche Peak 2 | 11/24/1994 | 05/19/1995 | 9505240202 | <strong>Labeling Error Leading To Inoperability Of The Power Range Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1994, at approximately 11:00 a.m., during Unit 2 power ascension channel N-41 Axial Flux Difference (AFD) indicated approximately 2 percent lower than channels N-42, 43, and 44 at 15 percent of Rated Thermal Power. Reactor Engineering personnel (utility, nonlicensed) reviewed this issue, in conjunction field verification by I&C Technicians (utility, nonlicensed) identified that cable connections of channel N-41 had been physically reversed due to labeling differences. Corrective action was to reinstall the cables in accordance with the design.
4541994001 | Byron 1, Byron 2 | 02/01/1994 | 03/01/1994 | 9403070296 | <strong>Several Valves may not Stroke Under High Differential Pressure Conditions due to Inadequate Torque Switch Setting</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1994, with Unit 1 and Unit 2 in Mode 1 at 99% power, it was discovered the minimum required torque to open and/or close Essential Service Water System valves 0SX147, 2SX005, 1/2SX033 and 1/2SX034 under high differential pressure conditions may not be available with the presently installed torque switch settings. Additionally, valve actuator, motor gearing, and gearbox torque limits for valves 1/2SX033 and 1/2SX034 could be exceeded if these valves were operated manually against high differential pressures. The questionable ability of valves 1/2SX033 and 1/2SX034 to close during an internal flooding event with a high differential pressure is reportable under 10CFR50.72(b)(2)(iii)(D). No systems or components were declared inoperable as all applicable Technical Specification requirements were met with all six valves in these conditions. The cause of this event was determined to be due to inappropriate actuator sizing and torque switch setting specifications by the manufacturer and/or the utilization of a different methodology for determining minimum required torque capability for these valves. Compensatory actions were put in place to ensure correct operation of these valves in their present condition. <br /><br /> This event is reportable for valves 1/2SX033 and 1/2SX034 pursuant to 10CFR 50.73(a)(2)(v), any event or condition alone that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
4541994002 | Byron 1, Byron 2 | 03/10/1994 | 04/06/1994 | 9404130062 | <strong>Main Steam Safety Valves Setpoints Outside Of Tolerance Due To Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On 03/09/94, Commonwealth Edison was notified by Furmanite America, Inc. that the trevitest performed at Byron Station on the Main Steam Safety Valves may have left them outside of the Technical Specification required setpoint tolerance of +/- 1 %. An incorrect value for mean seat area was used in the trevitest calculation to determine the setpoint. As a result, 16 valves on Byron Unit 1 and 19 valves on Byron Unit 2 fell outside the Technical Specification tolerance. <br /><br /> A Notice of Enforcement Discretion was requested, and granted, to permit continued operation of both units. An amendment to the Tech Specs to allow a tolerance of +/- 3% has been requested. The valves' setpoints will be retested by May 09, 1994. <br /><br /> The event is reportable per 10CFR50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications.
4541994003 | Byron 1, Byron 2 | 03/14/1994 | 01/12/1995 | 9502010331 | <strong>Auxiliary Feedwater Isolation Valve Exposure To Potentially Harsh Environment Due To Flood Seal Removal Supplement</strong><br /><i>Abstract:&nbsp;</i>On 03/14/94, the design bases of the Flood Seal Openings (FSO) located between the Main Steam Tunnel (MS)[SB] and the Auxiliary Feedwater (AF)[BA] Tunnel was questioned since these flood seal openings have been occasionally removed during operation to allow access to the AF tunnel. Byron Station's Safety Evaluation Report (SER) states that the flood seal opening plates between the Main Steam tunnel and the Auxiliary Feedwater tunnel separate equipment in the AF tunnel from the environment created in the event of a main steamline break (MSLB) in the MS safety valve room or steam pipe tunnel and ensure a watertight environment in the AF tunnel in the event of turbine building flooding due to a circulating water pipe break. The AF isolation valves in the AF tunnel are not in the Equipment Qualification (EQ) Program since the environment is considered mild, and therefore, since they have not been analyzed for a harsh environment they cannot be relied upon to mitigate consequences of an event occurring while the FSO plates are removed. However, the plates have been removed for periods of time during plant operations which exposed the equipment in the AF tunnel to potentially harsh environments. <br /><br /> Immediate corrective actions included verifying that the AF tunnel FSO plates were in place on both units and requiring the FSO plates to remain in place until this issue has been evaluated and acceptable resolution achieved. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(v) any condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
4541994004 | Byron 1 | 04/23/1994 | 05/23/1994 | 9405310089 | <strong>Waste Gas Decay Tank Curie Content Surveillance Missed Due To Poor Work Practices</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1994, with Unit 1 and Unit 2 in Mode 1 at 99% power, it was discovered that the OC Waste Gas Decay Tank had not been sampled after an addition of radioactive materials within twenty-four hours as required by Technical Specifications. The OC Waste Gas Decay Tank had been automatically aligned to service at 21:57 on 4/21/94. This tank was sampled by Chemistry at 08:22 on 4/22/94. The OC Waste Gas Decay Tank was automatically isolated at 13:45 on 4/22/94. The realignment was not recorded in the logbook, but was recorded on the turnover sheet. When Chemistry called at approximately 07:30 on 4/23/94 for Waste Gas Decay Tanks requiring samples, the OC Waste Gas Decay Tank was not reported as having been in service. The OC Waste Gas Decay Tank was not sampled after 08:22 on 4/22/94, although it remained in service until approximately 13:45 on 4/22/94. The causes of the event were determined to be poor work practices, inadequate training, and inadequate procedural guidance. Corrective actions to address each of the causes will be tracked.<br /><br /> This event is reportable (no immediate notification required) pursuant to 10CFR50.73(a)(2)(i)(B).
4541994006 | Byron 1, Byron 2 | 07/15/1994 | 08/15/1994 | 9408220257 | <strong>Fuel Assembly Located In Wrong Region Of Spent Fuel Pool Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1994, System Engineering Department (SED) found fuel assembly U38J located in Region II of the Spent Fuel Pool (SFP). The fuel assembly did not meet the burnup requirements specified in Technical Specifications (TS) Section 5, 'Design Features,' Figure 5.6-1, 'Minimum Burnup Versus Initial Enrichment for Region II Storage.' The Nuclear Component Transfer List (NCTL) incorrectly specified the placement of U38J into Region II at location HM5. The NCTL also did not place the assembly into Region II in a checkerboard pattern. Administrative controls require any assembly that does not meet minimum burnup to be placed into Region II in a checkerboard pattern. The assembly was placed into the incorrect region of the SFP on September 26, 1993 during a refueling outage on Unit 2. <br /><br /> The error was discovered while preparing for the next refueling outage. The assembly was moved to Region I on July 16, 1994. <br /><br /> This event involved no safety concerns. The safety significance of the misplaced assembly is within the safety analysis presented in the UFSAR. This event is reportable in accordance with 10CFR 50.73(a)(2)(i)(B). Any operation or condition prohibited by the plant's Technical Specifications.
4541994007 | Byron 1 | 08/01/1994 | 08/26/1994 | 9409060105 | <strong>1B Wide Range Hot Leg RTD Indication Spiked Low And Could Not Be Restored Within LCO Time Limit</strong><br /><i>Abstract:&nbsp;</i>During the Reactor Containment Fan Cooler (RCFC) monthly surveillance the 1B Wide Range Hot Leg RTD spiked low. Instrument Maintenance replaced an amplifier card and calibrated the circuit, but oscillations still existed when the RCFC's were started in low speed. On July 28, 1994, Byron declared the 1B Wide Range Hot Leg RTD inoperable and requested relief from Technical Specification 3.3.5-1a 'Remote Shutdown Instrumentation'. <br /><br /> The Root Cause of this instrument failure is the splice at the RTD pigtail and field cable. This area can not be accessed during power operations. The current splice is a bolted lug splice. A butt splice will be installed during the next refueling outage. <br /><br /> Even though the NRC has granted a Notice of Enforcement Discretion (NOED) for the inoperable RTD, this event became reportable pursuant to 10CFR50.73 (a)(2)(i)(B),an operation prohibited by Technical Specifications, after the 7 day LCO time limit was exceeded on 8-1-94.
4541994008 | Byron 1, Byron 2 | 08/03/1994 | 08/30/1994 | 9409130246 | <strong>Containment Spray Valves Not Stroke Time Tested In Closed Direction Due To Misinterpretation Of Tech Spec Requirements</strong><br /><i>Abstract:&nbsp;</i>On 08/03/94 a System Engineer discovered that since startup through 03/04/94, the valves 1CS007A, 1CS007B, 2CS007A, and 2CS007B were not stroke time tested in the closed direction. Technical Specification 3.6.3 lists these valves as having a 30 second requirement for the valve to go to its isolation position. The cause of the event stems from a combination of factors that relate to this valve having a unique configuration as a containment isolation valve. The valves open on a Containment Spray Signal. They do not receive an automatic close signal. The valves had been tested in the open direction since start up. <br /><br /> As immediate corrective action, the valves were verified as being tested in the closed direction since their addition to the IST program on 03/04/94 and that the surveillances were within frequency. As longer term corrective action, the IST review that added these valves was verified as complete and the other valves added to the program were verified as not having any specific timing requirements associated with them. <br /><br /> This event is not considered safety significant since these valves were stroke time tested in the open direction using a 10 second acceptance criteria since the beginning of the IST program. Byron Station feels that this testing would have identified any valve degradation and indirectly ensured that the valve would meet the required stroke time in the closed direction. <br /><br /> This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B); and operation or condition prohibited by Technical Specifications.
4541994009 | Byron 1 | 09/08/1994 | 03/31/1995 | 9504110125 | <strong>Reactor Trips planned shutdown due to Solid State Protection System failure - Supplement</strong><br /><i>Abstract:&nbsp;</i>Event 1: On September 8, 1994 at 01:25, Byron Unit 1 unexpectedly tripped at approximately 10 percent power. The event occurred during a controlled shutdown for the sixth refueling outage on Byron Unit 1 (B1R06). The unit tripped from high flux on source range (SR) nuclear instrument channel 31 (N31) [IG]. SR N31 re-energized when permissive P10 energized. Both intermediate range (IR) nuclear instrumentation channels (N35, N36) [IG] were above P6. The probable cause of the reactor trip was a faulty logic card in the Solid State Protection System (SSPS) [JG]. This generated a P6 signal for SR N31 before both IR channels were below the setpoint for P6. The Permissive Signal P6 setpoint for re-energizing the SR channels is less than 1.0 E-10 amps on both IR channels. The failure mode of the faulty logic cards was not determined. The failed cards were replaced.<br /><br /> Event 2: On September 8, 1994, at 14:52, a second reactor trip signal occurred. The signal was from high flux on SR N31. Station personnel inadvertently generated the signal during trouble shooting activities. The personnel were investigating the spurious P6 signal that caused the 01:25 reactor trip. Unit 1 was in Mode 3 with all control rods filly inserted. The cause of this event was a personnel error during the trouble shooting activities. Awareness of the cause of this event was heightened with the affected departments. <br /><br /> These events are reportable under 10CFR50.73(a)(2)(iv) as a Reactor Protection System Actuation.
4541994012 | Byron 1 | 10/06/1994 | 11/03/1994 | 9411160227 | <strong>Increased Tube Degradation In The Byron Unit 1 Steam Generators</strong><br /><i>Abstract:&nbsp;</i>A steam generator (SG) eddy current inspection was performed in accordance with Technical Specification Surveillance Requirement (TSSR) 4.4.5.0 during the Byron Unit 1 Cycle 6 refuel outage. The results of this inspection classified each of the four SGs as category C-3, as defined in TSSR 4.4.5.2. Category C-3 was declared due to more than 1 % of the tubes inspected having degradation that exceeded the repair limit. All defective tubes were removed from service by plugging. The primary mode of the tube degradation was axial oriented Outer Diameter Stress Corrosion Cracking (ODSCC) at the hot leg tube support plates. Packed tube support plate crevices under caustic chemistry conditions with susceptible tube material is considered to be the root cause of the ODSCC. <br /><br /> Preventative measures have been taken to mitigate the initiation of ODSCC. These measures include chemical cleaning, contaminant ingress reduction, and iron transport reduction measures. The occurrence of ODSCC has been experienced in previous outages, but to a lesser extent than the C-3 category. This mode of degradation has been experienced at a number of other plants in the industry. Industry efforts are on-going to determine corrective actions to mitigate ODSCC. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(ii).
4541994013 | Byron 1, Byron 2 | 10/10/1994 | 10/31/1994 | 9411080315 | <strong>SX Basin Level Switch Breaker Left In Wrong Position After Maintenance</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1994, the Limiting Condition for Operation for Technical Specification 3.7.5 was entered in conjunction with an Auxiliary Power Unit Substation (AP) outage which de-energized a level switch associated with Essential Service Water (SX)[BI] Makeup Pump auto start capabilities. When reenergizing the Unit Substation, Operations believed the level switch was also reenergized and the Limiting Conditions were exited. It was later discovered that a breaker, opened during maintenance, had prevented the level switch from being reenergized and that operations had occurred outside of the requirements of Technical Specifications for a duration of 9 hours and 50 minutes. <br /><br /> This event is reportable per 10CFR50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications.
4541994014 | Byron 1, Byron 2 | 09/15/1994 | 10/17/1994 | 9410250039 | <strong>Diesel Generator Inoperability In Mode 5 Due To Misinterpretation Of Technical Specification Requirement</strong><br /><i>Abstract:&nbsp;</i>On September 14, 1994, with Unit 1 in Mode 5, a problem identification form (PIF) was written which identified a concern on the operability of the 1B Diesel Generator (DG) if the Safeguard Sequencing Cabinet was deenergized as scheduled. At the time, the 1B Diesel Generator was meeting the requirements for the operable DG as required by Technical Specification 3.8.1.2. The sequencing cabinet was later deenergized which made the 1B DG inoperable . The cause of the event was determined to be a misinterpretation of regulatory requirements related to technical inconsistencies in the Technical Specifications.<br /><br /> This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
4541994018 | Byron 1 | 12/08/1994 | 01/06/1995 | 9501100299 | <strong>Operation Of A Safety Injection Pump In Mode 4 Without Two Modes Of Isolation From The RCS Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>With Unit One in Mode 4 at 210 degrees F, the 1B Safety Injection (SI)[BQ] Pump administrative Out of Service (OOS) was lifted to run the pump to make up to the SI Accumulators per Byron Operating Procedure BOP SI-5 'Raising SI Accumulator Level with SI Pumps'. To prevent an inadvertent injection to the Reactor Coolant System (RCS)[AB], the Cold Leg Injection Isolation valve 1SI8835 was closed as required by the procedure BOP SI-5 main body. However, the valve was not also de- energized as required by a footnote to Technical Specification Surveillance Requirement 4.5.3.2 'ECCS Subsystems- Tavg< 350 degrees F' and referenced in the Limitations and Actions Section of BOP SI-5. <br /><br /> This was a cognitive personnel error in that the appropriate Tech Spec requirements were not located, and implemented, prior to making the 1B SI Pump operable. The corrective actions will include counselling to the individuals involved, and a procedural enhancement to BOP SI-5. The 1B SI Pump was returned to the OOS condition after discovery of the violation of Technical Specifications. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications.
4541994019 | Byron 1 | 12/15/1994 | 01/11/1995 | 9501240118 | <strong>Missed Technical Specification Surveillance Due To Operator Not Recording Information</strong><br /><i>Abstract:&nbsp;</i>While performing Technical Specification surveillances for Reactor Coolant System Pressure/Temperature Limit (RC)[AB] and Pressurizer Temperature Limit (RY)[AB], during a Unit One plant heatup, one set of data was not recorded in the required time interval. A Licensed Reactor Operator (RO) was continually monitoring the Unit One primary system pressure and temperature but failed to record the necessary data for one (30 minute) interval due to personnel error. The RO was distracted from recording the data by another operator. This was a failure to comply with Surveillance Requirements 4.4.9.1.1 and 4.4.9.2. <br /><br /> A review of plant computer records indicated that a Reactor Coolant System heatup of 5 degrees F. had occurred (10 degrees F. per hour rate) during the interval in question. No actual heatup had occurred in the Pressurizer, although the surveillance was still being performed.<br /><br /> Primary system pressure and temperature remained within the limits of the Technical Specifications Limiting Condition for Operations 3.4.9.1 and 3.4.9.2 during this period. The RO involved was counselled to maintain proper documentation of surveillance requirements. A reorganization of the Operating Shift Management staff is also in progress to increase oversight of shift activities. <br /><br /> This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications.
4551994001 | Byron 2 | 02/19/1994 | 03/16/1994 | 9403230273 | <strong>Room Temperature Reading Taken At Wrong Location Causing A Missed Tech Spec Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>While investigating the operability of 2TIC-VX03 following repair, operators discovered that a Technical Specification required temperature reading for the Division 22 Cable Spreading Room was not being taken from the correct location in the room. The temperature was obtained from the correct location on third shift on February 19, 1994 by using a Doric hand held temperature probe. The temperature had last been taken from the correct location on first shift on January 30, 1994. There was approximately 21 days between properly obtained temperature readings in this area. Technical Specifications require checking the temperature every 12 hours.<br /><br /> The root cause of this event was an incorrect determination of the proper location for taking temperature readings during repair of 2TIC-VX03, due to confusion on the physical layout of the adjoining rooms and cable tunnel. <br /><br /> This event is reportable per 10CFR 50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications.
4551994002 | Byron 2 | 09/23/1994 | 10/23/1994 | 9410270247 | <strong>Rod Drive 2bd Power Cabinet Urgent Failures And Subsequent Reactor Trip Due To A Dropped RCCA.</strong><br /><i>Abstract:&nbsp;</i>To repair an intermittent indication-only Urgent Failure on the Unit Two Rod Control System (RD)[AA], Instrument Mechanics replaced a Moving Firing Card in the 2BD Power Cabinet. While performing a surveillance for post maintenance operability, a Stationary Regulation Urgent Failure developed that caused a mismatch of control rods. <br /><br /> Subsequent troubleshooting indicated possible problems with a Stationary Firing Card or a Stationary Regulation Card. During the testing of the effectiveness of the repairs, control rod C07 fell into the core which initiated a negative flux rate reactor trip. <br /><br /> The Urgent Failure was caused by a bad Stationary Firing Card. The dropped control rod was caused by a failed rack connector socket carrying the full current order to the Stationary Regulation Card.
4551994003 | Byron 2 | 09/24/1994 | 10/21/1994 | 9410270260 | <strong>Auto Start Of The 2B Aux Feed Pump On LO LO Steam Generator Level Due To Equipment Failure.</strong><br /><i>Abstract:&nbsp;</i>While performing a surveillance for post maintenance testing of the Unit 2 Rod Control System, a rod dropped into the core resulting in a reactor trip and corresponding Aux Feedwater actuation. When Steam Generator levels had been restored above the Lo Lo level setpoint, the 2B Aux Feed Pump was secured. When the Steam Dumps responded to an erratic signal from the Main Steam Header Pressure Controller, level in the Steam Generator dipped below the Lo Lo level setpoint which caused the 2B Aux Feed Pump to automatically start. <br /><br /> The root cause of this event was a failure of the Main Steam Header Pressure Controller. <br /><br /> To prevent recurrence, the Controller has been replaced. <br /><br /> This event is reportable per 10CFR 50.73(A)(2)(iv) any condition that results in the actuation of the ESF System.
4561994001 | Braidwood 1, Braidwood 2 | 02/02/1994 | 03/04/1994 | 9403090105 | <strong>Valves may not stroke under certain conditions due to a design deficiency</strong><br /><i>Abstract:&nbsp;</i>Engineering operability margin review calculations identified that the minimum required torque to open and close valves 1/2SX033 and 1/2SX034 under high differential pressure conditions was greater than the motor gearing capability of the actuator. Additionally, valve actuator and gearbox torque limits for these valves could be exceeded if these valves were operated manually against high differential pressures. It was determined that the questionable ability of valves 1/2SX033 and 1/2SX034 to close during an internal flooding event with a high differential pressure was reportable under 10CFR50.72(b)(2)(iii)(D). Engineering calculations also determined that the current torque switch settings for valves 1/2SX005 were too low to provide the minimum required torque for closure. The cause of the event is due to inappropriate valve actuator sizing and torque switch setting specification by the manufacturer and/or the utilization of a different methodology for determining minimum required torques. Although calculations indicate possible operability concerns, plant operating history has indicated no operational problems with the opening or closing of these valves. Corrective actions included providing guidance to the operators for the closing/opening of the affected valves if required. No similar occurrences have been identified.
4561994002 | Braidwood 1, Braidwood 2 | 02/18/1994 | 03/21/1994 | 9403250188 | <strong>Main Control Room Ventilation Dampers Declared Inoperable Due to Battery Failure</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1994, Braidwood began investigating a potential problem with the batteries in several of the damper actuators of the Control Room Ventilation (VC) System. At 1405 on February 18 the Station declared both trains of VC inoperable. Technical Specification 3.0.3 was entered. The Station requested discretionary enforcement, which the NRC granted. The Station exited 3.0.3 at 1027 on Sunday, February 20. The root cause of the event was a Programmatic Deficiency in that there was no preventative maintenance for the damper actuators. surveillance to check the condition of the battery. Additionally, these damper actuators were improperly taken out of service prior to 1992, resulting in battery drainage. <br /><br /> The corrective actions include establishing preventative maintenance programs for the damper actuators and the batteries, and the scheduling of periodic surveillances of the batteries. The procedures associated with deenergizing electrical buses feeding these actuators were revised to include pulling actuator fuses. This minimized battery drainage. There have been no previous reportable occurrences at Braidwood Station of battery failures due to the causes identified above. This issue was initially identified at South Texas.
4561994003 | Braidwood 1, Braidwood 2 | 03/11/1994 | 04/11/1994 | 9404130132 | <strong>As Found Integrated Leak Rate Test Failures Due to Preservice Construction Deficiencies</strong><br /><i>Abstract:&nbsp;</i>During A1R04 the Unit 1 Primary Containment Type A Integrated Leakage Test (ILRT), BwVS 6.1.2.a-1, the as-found condition was in excess of the value allowed by Technical Specifications for surveillance testing. During walkdowns of the potential leakage areas of containment it was discovered that air was escaping from around the containment emergency hatch outer barrel. Attempts to quantify the leakage were not successful. Unexpected leakage was detected at the emergency hatch and a decision was made to depressurize containment and perform an internal inspection of containment. It was revealed that the emergency personnel hatch barrel was missing welded caps on all six of its concrete vent pipes which are required per original design. The ILRT was reperformed. Initially it appeared that the test would fail. Isolation of a known leakage source, the Service Air (SA) penetration, reduced the leakage of containment below the acceptable leakage value (0.75 La or 5.78 scfm). The ILRT was successfully completed, and the containment as-left leakage met surveillance requirements. An inspection of the Unit 2 containment revealed the emergency hatch concrete vent pipe caps were also missing. A 96 hour NOED was obtained from the NRC and the concrete vent pipes were capped and tested satisfactorily. There have been previous similar occurrences of ILRT failures on Units 1 and 2.
4561994004 | Braidwood 1, Braidwood 2 | 03/09/1994 | 04/08/1994 | 9404130108 | <strong>Main Steam Safety Valves Declared Due to Calculational Inaccuracies With the Trevi-Test Method</strong><br /><i>Abstract:&nbsp;</i>At about 1730 on March 9, 1994, Braidwood Systems Engineering received a phone call from the Furmanite Company indicating that an improper value for mean seat area was used in the Trevitest calculation for the Main Steam Safety Valve (MSSV) setpoints for both Units. Technical Specifications state that with one or more MSSVs inoperable, operation in MODES 1, 2, and 3 may proceed provided the valve is restored to OPERABLE status or the Power Range High Flux trip setpoints are reduced within 4 hours. Notice of Enforcement Discretion was requested, approved and an emergency Technical Specification amendment was submitted to the NRC on March 21, 1994. The cause of the event was a programmatic deficiency on the part of the Furmanite Company. The methodology used by Furmanite was erroneous. All valves that fell outside of the required +/-1% Technical Specification tolerance were declared inoperable and the NRC was contacted and appraised of the situation. Based upon unit operating schedules and Furmanite availability, the MSSVs for Braidwood Unit 2 will be reset on or before May 9, 1994. Braidwood Site engineering is reviewing all pertinent Trevitest data on our valves to determine what, if any, effect the higher setpoints may have had on system overpressurization. There has been no previous reportable occurrence of this type at Braidwood Station.
4561994005 | Braidwood 1 | 03/23/1994 | 04/11/1994 | 9404180280 | <strong>Inadvertent Start of 1B Diesel Generator During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On March 23, 1994, the 1B Diesel Generator Safety an Bus Undervoltage Surveillance Tests were in progress. Surveillance 1BwVS 8.1.1.2.f-16, 1B Diesel Generator Loss of ESF Bus Voltage with No SI Signal had been entered. At 0253, a miscommunication occurred, and ESF Bus 142 undervoltage relay was actuated by OAD personnel prior to the step in the procedure which called for this action. The plant response was per ESF design; 1B DG automatically started and appropriate B-train equipment sequenced on to Bus 142, per the safe shutdown sequencer. Operations personnel paralleled offsite power (SAT) to Bus 142 at 0303, and opened the 1B DG output breaker at 0307. The 1B DG was secured at 0322. The primary cause was a miscommunication. Contributing causes were high noise level in the area, inadequate pre-job briefing, and inadequate procedural adherence. Immediate corrective actions taken by operations personnel were to restore offsite power to Bus 142 and then secure the 1B DG. Actions to be taken to prevent recurrence include the following items. The System Engineering Department will conduct training on 1) the hazards of communicating in high noise level areas, 2) HLA meeting expectations prior to performance of BwVS's, and 3) the expectations for Continuous Use procedures, specifically when more than one individual is performing steps. There have been no previous manual inadvertent ESF Bus UV actuations of this type.
4561994006 | Braidwood 1, Braidwood 2 | 03/30/1994 | 04/29/1994 | 9405040245 | <strong>Missed Technical Specification Surveillance Due to Personnel Error and Programmatic Deficiencies</strong><br /><i>Abstract:&nbsp;</i>At 1415 on 03/30/94, it was discovered that the Braidwood Cooling Lake Hydrographic Survey, an 18-month surveillance to verify the depth of the Essential Service Cooling Pond (ESCP), was not completed within the required time. The root cause of the event was a personnel error. The System Engineer stated that it was his understanding that the Surveillance must be started prior to the due date and completed as soon as possible. Also, windy conditions which are typical during the fall/winter make performance of the Surveillance difficult because wave action causes erratic bottom readings. A contributory cause was a programmatic deficiency. The document used to track surveillances was updated with the start date and this was interpreted as a completion acknowledgement. The Surveillance was completed within the 24 hour surveillance period extension allowed in the Technical Specifications. It is planned to have all surveillance packages reviewed and filed with surveillance tracking personnel. There have been previous occurrences of missed Technical Specification Surveillances associated with personnel errors.
4561994007 | Braidwood 1 | 04/07/1994 | 05/06/1994 | 9405110333 | <strong>Steam Generator Tubes Degraded due to Axial Outer Diameter Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>A Steam Generator (SG) Tube Inservice Inspection initiated on Braidwood Unit 1 revealed SGs 1A, 1C, and 1D as Category C-3. In addition to tubes that showed indications >/= 40% through wall, inspections revealed many distorted indications at the hot leg tube support plate intersections which when confirmed with Rotating Pancake Coil (RPC) required plugging or repair. Braidwood submitted an Emergency Technical Specification Amendment to implement a SG tube interim plugging criteria (IPC). Amending the Technical Specification would allow tubes with flaw indications at the tube support plates to remain in service regardless of depth provided they meet certain criteria. A total of 932 tubes, which under the previous criteria would have required plugging or repair, were not plugged as a result of the IPC. The primary cause of the event is Axial Outer Diameter Stress Corrosion Cracking. The application of IPC causes no significant negative impact on any system, equipment, or operating mode. Corrective actions include the investigation of secondary side SG cleaning during the Braidwood Unit 1 Cycle 5 Refuel Outage, implementation of a secondary side boric acid addition program with the start of Cycle 5, review of other alternate amines, eddy current testing of the remaining fourth water box, and continuation of the molar ratio and elevated hydrazine programs.
4561994008 | Braidwood 1 | 04/21/1994 | 05/20/1994 | 9405250233 | <strong>Both Diesel Generators Inoperable due to Misinterpretation of Surveillance Data</strong><br /><i>Abstract:&nbsp;</i>Braidwood Unit 1 was in a refueling outage with diesel generator surveillances being performed. One diesel generator was required to remain operable. Braidwood surveillance 1BwVS 8.1.1.2.f-20, "1B Diesel Generator 5500KW Load Rejection" was performed as required and considered acceptable. The 1A diesel generator was operable at this time. Later, 1BwVS 8.1.1.2.f-19, "1A Diesel Generator 5500KW Load Rejection" was performed. During this surveillance it was observed that the 1A diesel generator output voltage exceeded the Technical Specification limit during the 5500KW load rejection. As part of the investigation, the data for the 1B diesel generator output voltage was reevaluated. The reevaluation recognized that the 1B diesel generator output voltage had also exceeded the Technical Specification limit. This resulted in both diesel generators being declared inoperable. The appropriate action statement of Technical Specification 3.8.1.2 was entered and complied with. The primary cause of this event was a personnel error, the 1B diesel generator output voltage value was misinterpreted. The Diesel Generator 5500KW Load Rejection tests for both the 1A and 1B DGs were reperformed after adjusting KVAR loading. The surveillances for the diesel generators will be revised to record the maximum generator voltage.
4561994009 | Braidwood 1 | 04/25/1994 | 05/25/1994 | 9406020135 | <strong>Unexpected Reactor Protection System actuation due to a procedural deficiency</strong><br /><i>Abstract:&nbsp;</i>An unexpected reactor trip actuation occurred while performing refueling outage activities. Reactor trip breakers were closed to support testing and a steam generator was being drained for chemistry. The Solid State Protection System (SSPS) had been disabled for Mode 5 operation per procedure BwOP RP-7. Upon reaching the low low level in the steam generator, the reactor trip breakers unexpectedly opened. The root cause of this event was a procedural deficiency with BwOP RP-7. The procedure specifically identifies two systems that are not disabled when performing the procedure. The Reactor Protection System is not among the systems identified and the belief was that it was disabled. Corrective actions include revising BwOP RP-7 to identify the fact that the reactor trip function is not disabled by this procedure.
4561994010 | Braidwood 1 | 05/15/1994 | 06/14/1994 | 9406170208 | <strong>Diesel Generator Declared Inoperable due to a Blown Exhaust Line Rupture Disc</strong><br /><i>Abstract:&nbsp;</i>The 1A Diesel Generator (DG) was shutdown after receiving a high intake filter Delta P alarm. An investigation of the exhaust line rupture disc and muffler room revealed a blown exhaust rupture disc and the relief on the silencer had lifted. The air intake filters were clogged by DG exhaust and silencer insulation debris. An exhaust header pressure transient occurred which resulted in the blown rupture disc and lifted relief. The cause of the exhaust header pressure transient is currently indeterminate. The 1A DG was declared inoperable with the 2A DG out of service for planned maintenance. Having both of these DGs inoperable required a Technical Specification Action Statement to be entered. A Notice of Enforcement Discretion was received from the NRC to allow for repair of the rupture disc. The rupture disc was replaced and a maintenance run performed successfully. An engine analysis will be performed on the 1A Diesel Generator in an attempt to determine the cause of the event. Pieces of rupture disc, air filter, and debris particles have been sent away for analysis.
4561994011 | Braidwood 1, Braidwood 2 | 08/03/1994 | 09/02/1994 | 9409060142 | <strong>1/2 CS007A & B Valves Not Stroke Time Tested Per Technical Specifications Due To A Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>During a review of IST/Technical Specification Requirements associated with a proposed UFSAR change, it was discovered that valves 1CS007A, 1CS007B, 2CS007A, and 2CS007B were not stroke time tested in the closed direction prior to their addition to the Braidwood IST program. Technical Specification 3.6.3 lists these valves in table 3.6-1 as having a maximum isolation time of 30 seconds. The cause of this event is a management deficiency due to a combination of factors. These factors in conjunction with the interpretation that the 'isolation' position and most significant safety function for these valves is open led Braidwood Station to believe that it was complying with Tech. Spec. 3.6.3 by stroke time testing the valves in the open direction. Due to the fact that these valves are tested quarterly in the open direction using a more conservative acceptance criteria (less than 30 seconds), Braidwood station feels that this event is not safety significant. The appropriate LCOARs were entered, procedures changed, and close stroke times performed successfully.
4561994012 | Braidwood 1 | 08/11/1994 | 09/09/1994 | 9409160027 | <strong>Inadvertent Main Steam Line Isolation at Power due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1028 a.m. on August 11, 1994, Braidwood Unit 1 experienced a spurious Train 'A' Main Steam Line Isolation followed by an automatic reactor trip from Low Low water level on the 1C Steam Generator. Both Pressurizer PORV's cycled as designed to relieve the RCS pressure transient. Steam was released to the atmosphere via the steam generator PORV's and Main Steam safety valves. Control Room Operators stabilized the plant using the Emergency Operating Procedures. All systems operated as designed following the MSIV closure to mitigate the transient. During subsequent cooldown of the RCS a second Main Steam Line Isolation signal was received which closed all four MSIV Bypass valves. failure of the Q7 output transistor on the A516 Safeguards Output Driver Board in Train A of the Solid State Protection System. The failed A516 circuit board was replaced and the Train 'A' SSPS bimonthly surveillance was performed satisfactorily.
4571994001 | Braidwood 2 | 01/31/1994 | 03/02/1994 | 9403090281 | <strong>Valves not included in Primary Containment Integrity Verification Surveillance due to Preservice Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>Three Primary Containment Integrity valves were not checked on a monthly basis as required by the Technical Specifications. Technical Specifications, but are among those required to ensure containment integrity. The root cause of this event is a Preservice Design Deficiency. The original surveillance (written in 1987) did not include these valves. It is suspected that the reason the valves were not on the original procedure was an oversight. This event ha no effect on plant or public safety. The valves were immediately verified to be closed in the field, a partial surveillance was performed on the valves to verify isolation, and the surveillance procedure was revised to add the missing isolation devices. There has been a previous occurrence.
4571994002 | Braidwood 2 | 03/31/1994 | 04/29/1994 | 9405090005 | <strong>Inadvertant Automatic Start of the 2A Auxiliary Feedwater Pump Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>Prior to the event, Braidwood operating Quarterly Slave Relay Surveillance was in progress. Step F.1.22 of the surveillance verified that slave relay K639 contact 1-2 was open by measuring its resistance greater than 25 ohms. This is to prevent an inadvertant Auxiliary Feed pump start when the blocking relay is reset. Step F.1.23, which places the test switch back to NORMAL, was then performed. However, the ohm meter probes had not yet been removed. This resulted in the 2A Auxiliary Feed pump auto starting. The root cause of this event was a procedural deficiency. The procedure does not instruct the operators to remove the volt/ohm meter prior to proceeding to the next step. Additionally, the physical layout of the panels is such that the two operators performing the test are not in visual contact. The 2A Auxiliary Feed pump was immediately secured by placing the control switch in the pull out position. The ohm meter was removed. This surveillance will be revised to include a step to verify ohm meter probes removed prior to taking the test switch to Normal. A review of the other slave relay surveillances will be performed to see if this change needs to be included. There have been similar events involving the misapplication of a volt-ohm meter.
4571994003 | Braidwood 2 | 04/05/1994 | 05/05/1994 | 9405090099 | <strong>Reactor Trip Due to Main Power Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>At 1539 on April 5,1994 a Reactor Trip was received. The 2E Main Power Transformer (MPT) had a sudden pressure and a differential current trip which caused a turbine trip and a subsequent reactor trip. The cause of this reactor trip was Equipment Failure. A review of the oscillograph traces indicated a high side B phase fault on the 2E Main Power Transformer. The fault was initiated at the transformer and damage was extensive to the 2E MPT. A detailed investigation for collateral damage was performed which covered the following items: A generator crawlthru inspection; the 2W MPT and both UAT'S were electrically tested; and oil samples on the 2W MPT and both UAT'S were taken. The results of all of these activities indicated that there was no additional damage to any equipment beyond the 2E MPT. The 2E MPT will be replaced with a spare transformer. Additionally, instrumentation associated with the transformer will be calibrated prior to operation. Finally, a Company task force has been developed to investigate this recent failure. There have been previous similar occurrences where electrical system problems have resulted in a reactor trip. The root cause(s) and corrective actions of the previous similar occurrences do not apply to this event. There is no adverse trend.
4571994004 | Braidwood 2 | 04/06/1994 | 05/06/1994 | 9405110327 | <strong>Missed Technical Surveillance Requirement for Shutdown Margin Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 5th, 1994 at 539 Braidwood Unit 2 tripped from 99% power due to a fault in the 2E Main Power Transformer. Control rod K2 failed to fully insert during the trip and remained out of the core at an indicated 210 steps. Following the reactor trip, data for a shutdown margin calculation was obtained within 1 hour following the reactor trip, however calculations were not completed until 2044. This exceeded the 1 hour requirement of Technical Specifications. The next shutdown margin surveillance was performed at 0158, April 6th, 1994. The shift operating crew reviewed the surveillance requirements for shutdown margin and determined that the 12 hour requirement for shutdown margin calculations did not apply. This decision was reviewed on April 6th by Station Management and found to be incorrect. A shutdown margin calculation was begun at 1833 and completed at 2025 on April 6th, 1994. This calculation exceeded the 12 hour surveillance requirement by 3 hours and 27 minutes. The primary cause of the event was a procedural deficiency. Applicable procedures will be revised to direct the performance of a shutdown margin calculation if any control rod fails to fully insert following a reactor trip. There has been previous reportable occurrences of missed Technical Specification surveillance requirements as a result of procedural deficiency. The root causes and corrective actions for the previous events are not applicable.
4571994005 | Braidwood 2 | 08/02/1994 | 09/01/1994 | 9409060048 | <strong>Reactor Trip Due to LO-2 Level in 2A Steam Generator Due to O-ring Failure in Feedwater Regulating Valve Positioner</strong><br /><i>Abstract:&nbsp;</i>Braidwood Unit 2 tripped due to a low low level in the 2A Steam Generator. The cause of this event was Equipment Failure; an o-ring in the Feedwater Regulating Valve positioner failed. The entire positioner was replaced, tested, and placed into service.
4571994006 | Braidwood 2 | 09/20/1994 | 10/20/1994 | 9410240257 | <strong>Snubber for 2B CV Pump Inoperable due to a Programmatic Deficiency and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>A Chemical and Volume Control (CV) system snubber was removed in order to work on an adjacent Containment Spray (CS) valve. The required 72 hour Limiting Condition for Operation Action Requirement (LCOAR) was not entered upon its removal. Although the snubber was reinstalled eight hours after the valve work, the snubber was not tested and, therefore, could not be considered operable. The error was discovered, the appropriate testing was performed, and the snubber was found acceptable. A Programmatic Deficiency and Personnel Error were the root causes of this event. Corrective actions include a work control procedure revision, a technical review process evaluation, and a training evaluation.
4571994007 | Braidwood 2 | 10/15/1994 | 11/11/1994 | 9411210288 | <strong>Core alterations performed without establishing proper communications due to personnel error</strong><br /><i>Abstract:&nbsp;</i>While performing the lift of the Reactor Vessel Upper Internals, the Communications between the Control Room and the Containment where the core alteration was being performed was lost, contrary to Technical Specification 3.9.5. The Fuel Handling Supervisor in the containment filling the role of the Senior Operator License holder assumed the speaker phone with the open communications could be heard from his viewing area. As a result the control room could not contact the Fuel Handling Supervisor in the containment. The root cause for the event was determined to be Personnel Error. Corrective actions included personal counselling and the change to the phone used to maintain communication.
4571994008 | Braidwood 2 | 11/11/1994 | 12/12/1994 | 9412150163 | <strong>Failure to open Reactor Trip Breakers During D.R.P.I. operability checkout due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>While performing Digital Rod Position Indication (D.R.P.I.) Operability Checkout, BwVS 1.3.3-1, seven control rods from two Control Rod Banks were withdrawn due to an equipment failure. Control rods were manually inserted instead of opening the Reactor trip breakers as required by Technical Specifications. During subsequent control room activities the Unit Supervisor (US) directed the extra Nuclear Station Operator (NSO) to select and withdraw Control Bank D Rods to attempt to reproduce the problem. When this action was performed, the same indications were obtained, and control rods were manually inserted instead of opening the Reactor trip breakers. A cause for the initial problem could not be immediately determined. Testing was resumed and a Rod Control Urgent Failure was received. Subsequent troubleshooting determined that a firing card failure had occurred. The component was replaced and the testing was completed satisfactorily. The root cause for the event was determined to be a combination of Personnel Error, Programmatic Deficiency, and Equipment Failure. Corrective actions include personnel counselling, procedure enhancement, and training.
4571994009 | Braidwood 2 | 11/13/1994 | 12/13/1994 | 9412190191 | <strong>Failure to perform monthly SI Accumulator Isolation Valve Surveillancea due to personnel error.</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1994, it was discovered that the monthly SI Accumulator Isolation Valve Surveillance (2BwOS 5.1.1.c-1) predefine in Electronic Work Control System (EWCS) had been inadvertently deleted and the Surveillance had not been performed since 7/28/94. cause of this event was the inadvertent deletion of the surveillance predefine in EWCS. This event had no effect on plant or public safety. Even though the surveillance was not performed, the administrative Out-of-Service was in place that satisfies the intent of the surveillance. The corrective actions are: 1-Change the personnel who have edit capabilities to change/delete predefines. 2-Review all deleted surveillances to determine if any others had been inadvertently deleted. 3-Create a weekly report of deleted predefines to allow review of the same for correctness. 4-Perform the surveillance 2BwOS 5.1.1.c-1. All corrective actions have been completed with the exception of the weekly report. be active in early December, 1994. There have been other missed surveillances, but none due to the deletion of information in EWCS or the previous General Surveillance System database. This does not constitute an adverse trend.
4581994001 | River Bend | 01/07/1994 | 12/22/1994 | 9412290148 | <strong>Fire Barrier Separation Design Analysis Deficiencies in Fire Areas C-17 and C-24</strong><br /><i>Abstract:&nbsp;</i>Recent work on the control building chillers sensitized engineers to question previous assumptions used in the FHA. Further evaluation by the cognizant engineers led to the discovery that design analysis deficiencies existed for fire barrier separation in fire areas C-17 and C-24. Redundant trains of control building HVAC could be lost during a single exposure fire. This could cause the main control room, standby switchgear room 1B, and mechanical equipment room to heat up. Equipment in these rooms is credited for safe shutdown in the event of a fire in fire area C-17 or C-24. <br /><br /> The original design analysis did not adequately support the ability to ensure post-fire safe shutdown for a fire in fire area C-17 or C-24. This situation existed from initial plant startup until fire watches were established in 1991. Design analysis deficiencies were the root cause of this condition. The architect/engineering firm tasked with developing the RBS FHA and safe shutdown analysis did not have a clear understanding of Section III.G of 10CFR50, Appendix R. <br /><br /> Upon discovery of this condition an hourly fire watch was verified to be in place for fire areas C-17 and C-24. Appropriate changes to AOP-0052 have been made. As long term corrective action for fire area C-24, cable was re-routed for the affected safe shutdown component. For fire area C-17, use of the remote shutdown system will be evaluated. There was no impact on the safe operation of the plant or the health and safety of the public as a result of this event.
4581994002 | River Bend | 01/11/1994 | 02/10/1994 | 9402280076 | <strong>Airlock Interlock Rendered Inoperable During Maintenance Due To Ineffective Communication And Personnel Not Recognizing Cautions In A Work Package</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1994, maintenance was being performed on the reactor building door in the 171' containment airlock which rendered the handle locking solenoid mechanism, and therefore the interlock, inoperable. The Technical Specification requirements for an airlock door to be locked at aR times and dedication of an individual to assure that both doors are not opened simultaneously were not met. The investigation also revealed that during monthly preventive maintenance the interlock is similarly rendered inoperable without entry into the required Technical Specification action statement. <br /><br /> The primary causal factor for this event is that personnel authorizing and conducting the work activity did not effectively communicate the scope of work and recognize the cautions in the work package. Corrective actions include disciplinary action for responsible supervisory personnel. The preventive maintenance tasks and surveillance test procedures associated with the airlock doors will be reviewed by March 1, 1994 to assure full compliance with the Technical Specifications. As a conservative measure, until the procedure revisions resulting from the review are finalized, the Technical Specification action will be implemented whenever surveillances or maintenance activities are performed on the airlocks. Throughout the event, there was no breach of containment. At least one door was closed at afl times with its seal inflated throughout this event.
4581994003 | River Bend | 01/12/1994 | 02/10/1994 | 9402180044 | <strong>Missed Surveillance on Fire Barriers in Safety-Related Fire Areas</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1994, it was determined that surveillance inspections required by the RBS Technical Specifications for eight safety-related fire-rated assemblies had not been performed. <br /><br /> The original plant drawings identifying fire-rated assemblies were used to develop the list of fire barriers requiring inspection under procedure STP-000-3602. However, these drawings did not clearly identify the boundaries of fire areas necessary for separation of redundant safe-shutdown components credited in the event of a fire. The issue of incorrect original plant fire protection documentation was addressed in LER 91-008. <br /><br /> Upon discovery of this condition an hourly firewatch was verified to be in place for the listed fire-rated assemblies. Modification Request 92-0034 revised the plant drawings to accurately identify fire-rated assemblies. <br /><br /> The fire assemblies not previously inspected per Technical Specifications did not introduce a significant safety concern. One hour roving firewatches have been in effect for all normally accessible safety related areas of the plant since 1991. Therefore, there was no impact on the safe operation of the plant or the health and safety of the public as a result of this event.
4581994004 | River Bend | 01/13/1994 | 02/11/1994 | 9402280091 | <strong>Unidentified Non-Conservative Alarm Setpoint For Liquid Radwaste Gross Activity Monitor Due To Inadequately Conveyed Supervisory Expectations Concerning Quality Technical Reviews</strong><br /><i>Abstract:&nbsp;</i>During a Quality Assurance audit of the Offsite Dose Calculation Manual (ODCM) on January 13, 1994, a non-conservative alarm setpoint for the liquid radwaste gross activity monitor, 1RMS-RE107, was identified. The alarm set point was non-conservative with respect to the limits required by Technical Specification 3.11.1.1 and the ODCM. This condition is contrary to Technical Specification 3.3.7.10. <br /><br /> An error in the setpoint calculation existed in the ODCM from 1985 until the calculation was revised in June 1993. During this time period, supervision did not adequately convey expectations concerning quality technical reviews nor assure quality technical reviews for seven different revisions of the ODCM. In addition, the ODCM change in June 1993 was not adequately communicated to the department responsible for the implementing procedure. This procedure has been revised to assure that the alarm setpoint will be properly set for each batch release. Administrative controls combined with the results of a condition report database search provide confidence that the concentrations of both gamma and beta emitting radionuclides released to the unrestricted area have been below the limits specified in Technical Specification 3.11.1.1, 10CFR20, Appendix B and 10CFR50, Appendix I.
4581994005 | River Bend | 04/06/1994 | 05/05/1994 | 9405110249 | <strong>Automatic Actuation of Engineered Safety Features Caused by Electrical Transient Due to Failure of Offsite Protective Equipment</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1994 at 0154, with the plant in Operational Condition 1 (Power Operation) at 98 percent power, a voltage drop was experienced at River Bend Station due to an offsite electrical transient. During thunderstorm activity, a broken shield wire fell on a 230kV line located in the transmission system to which River Bend is connected. The voltage drop led to the actuation of several systems including the standby gas treatment system (SGTS), automatic start of the fuel building ventilation system and isolation of dampers in the fuel building and auxiliary building ventilation systems. <br /><br /> The operator at the controls was confronted with multiple coincident indications, and appropriately monitored and controlled plant parameters throughout the event. The root cause of this event was the failure of offsite protective equipment. Corrective actions included replacement and modernization of portions of this equipment. The ESF actuations and plant responses were either directly or indirectly due to the low voltage condition. Entergy has concluded that the plant systems responded as designed to this electrical transient.
4581994006 | River Bend | 04/14/1994 | 05/13/1994 | 9405170181 | <strong>Missed Containment Airlock Door Seal Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 0133 hours on April 14, 1994, with the reactor in Operational Condition 1 (Power Operation), the Shift Superintendent (SS) recognized that the required frequency for performing Surveillance Test Procedure (STP) 057-3705 had been exceeded. The SS recognized this condition when he was documenting the successful completion of this surveillance in the daily surveillance tracking sheet. The frequency had been exceeded by a small fraction of the required 72 hour frequency. This STP verifies the operability of the airlock door seals as required by Surveillance Requirement 4.6.1.4.a. <br /><br /> The root cause of this event is inadequate Supervisory Methods which did not adequately track and schedule the completion of STPs with a frequency of less than seven days. <br /><br /> Corrective actions include a review of associated Supervisory Methods and appropriate revisions to ADM-0015 to better define the division of responsibilities. <br /><br /> The satisfactory performance of the STP on April 14, 1994 demonstrated that the seals were operable and that the airlock doors were capable of performing their safety function during the 45 minutes that the required frequency was exceeded.
4581994007 | River Bend | 05/01/1994 | 08/30/1994 | 9409120321 | <strong>ESF Actuation Due To EPA Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>At 0339 and again at 1435 hours on May 1, 1994, with the reactor in Operational Condition 5 (Refueling), power to the reactor protection system (RPS) bus B was lost. When these events occurred, RPS bus B was being powered from its alternate power source. The loss of the alternate power source resulted from a trip of the electrical protection assembly (EPA) breakers 1C71*S003G and H. This transient caused a half-scram on RPS Channel B and resulted in various Engineered Safety Features actuations. This report is submitted pursuant to 10CFR50.73(a)(2)(iv) to document these ESF actuations. Proper plant response was verified and documented in accordance with Abnormal Operating Procedure, AOP-0010, 'Loss of One RPS Bus'. <br /><br /> A failure of the electrical protection logic card of EPA breaker 1C71*S003G is the root cause of this event. The most likely cause of the logic card failure is damage that occurred during the performance of the EPA channel calibration and channel functional test surveillance. <br /><br /> The original corrective actions included replacement of the faulty equipment and a revision to the surveillance procedure, STP-508-1600. The corrective actions added by this supplement include plans to replace the existing logic cards with new Generation III cards and the issuance of a new Operations Standing Order to effect more thorough trouble shooting of significant events. The logic card failure did not prevent the performance of the EPA breaker safety function to de-energize the RPS-B bus. All systems functioned in accordance with their design.
4581994008 | River Bend | 05/09/1994 | 06/08/1994 | 9406140055 | <strong>The Minimum Number of Operable Channels per Trip System for the Reactor Protection System was not Maintained due to Inadequate Work Package Review and Retest Requirements.</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1994 with the plant in Operational Condition 5 (Refueling), a condition report was written to identify that post-maintenance operability testing had not been performed for reactor protection system trip system 'B' prior to returning the system to operation. While subsequent testing verified the affected channel had indeed been functional, failure to take the actions required by T.S. 3.3.1 within the appropriate timeframe or to perform the required retest resulted in a condition in which less than the minimum number of operable channels were available for this trip system. The safety function of the RPS system was satisfied since all control rods were inserted. Subsequent investigation has revealed that the duration of the noncompliance was about 75 hours, from April 21, 1994 until April 24, 1994. <br /><br /> The root cause of this event consisted of (1) an inadequate work package review by the work management center supervisor (WMCS) due to inattention to detail and incorrect assumptions, and (2) the work package specified an incorrect surveillance procedure for retest of the relay. Corrective actions include evaluating the planning process to define improvements required to assure that correct LCOs are specified in maintenance work packages and surveillances. A night order has been issued to ensure that the WMCS will attend infrequent evolution briefings, and reviews for operations and maintenance personnel emphasizing the importance of retest requirements were conducted.
4581994009 | River Bend | 05/13/1994 | 06/10/1994 | 9406150349 | <strong>Piping Error During Construction Results in Incorrect Measurement of RCS Leakage</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1994, with the plant in Operational Condition 5 (refueling), Engineering's extensive investigation of problems with the drywell air cooler condensate flow transmitter led to the discovery that the condensate leakage from the drywell air coolers was incorrectly being counted as identified leakage rather than unidentified leakage because of a drain system piping discrepancy. As a result, the drywell floor sump drain flow monitoring system, 1DER-KC174, has been inoperable since initial plant start-up. This condition constitutes operation prohibited by RBS Technical Specification 3.4.3.1.b. <br /><br /> Based on the information available, the cause of this error is indeterminate. However, there are two causal factors which contributed to this condition not being detected earlier: 1) inadequate pre- operational testing of the reactor containment floor and equipment drain system within the drywell prior to initial plant start-up, and 2) inadequate acceptance criteria in the periodic preventative maintenance task for the inlet piping to the equipment and floor drain sumps. <br /><br /> Since other leak detection systems were available to indicate any significant reactor coolant pressure boundary leakage, there was no impact on the safe operation of the plant or the health and safety of the public as a result of this condition.
4581994010 | River Bend | 05/12/1994 | 11/01/1994 | 9411070307 | <strong>Deficient Overcurrent Penetration Protection For 120vac Hydrogen Igniter Circuits Due To Inadequate Communications And Oversight During Construction</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1994, at 1145, with the plant in Operational Condition 5 (Refueling), Plant Engineering was conducting a review of Calculation E- 190 for Minor Modification MM94-0055 when they discovered a condition of inadequate breaker protection for the electrical containment penetration associated with the 120 VAC hydrogen igniter circuits. The investigation also revealed that the hydrogen igniter system breakers should have been tested in accordance with Technical Specification 3/4.8.4.1 'Primary Containment Penetration Conductor Overcurrent Protective Devices.' A subsequent detailed evaluation has been performed which verified the design adequacy of all identified circuits which require penetration protective devices. However, additional examples of these circuits not being included in the Technical Specifications were identified. <br /><br /> Based on the information available, the cause of this event is indeterminate. However, there are two causal factors. First, the electrical calculation E-190 specified the correct breaker size required for the containment penetration but a design change document was not initiated. Second, the design engineering modifying the hydrogen igniter system failed to follow through with the necessary design modification document to implement the change in the plant.<br /><br /> Corrective actions include modifying the hydrogen igniter panels to provide proper backup overcurrent protection for the electrical containment penetrations and to revise surveillance test procedure(s) to require periodic testing of the hydrogen igniter breakers in accordance with Technical Specification 4.8.4.1.
4581994011 | River Bend | 05/15/1994 | 06/14/1994 | 9406200260 | <strong>Inadvertent Initiation of the Standby Service Water System Due to Procedural Ambiguity</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1994, at approximately 0140, with the plant in Operational Condition 5 (Refueling), an inadvertent initiation of the division I standby service water (SSW) system occurred during division II SSW in-service testing. Operations personnel restored the plant and notified the NRC pursuant to 10CFR50.72(b)(2)(ii) of the actuation of this ESF. The division II SSW system was inoperable for the performance of in-service testing. Therefore, the realignment of the system did not result in the loss of a required safety related system. The division I SSW system functioned as designed.<br /><br /> The root cause of this event was an ambiguous procedure. Based on a note and the direction provided in one of the steps, the test crew interpreted the procedure to mean that a division II SSW pump did not need to be running until after the division II supply header manual isolation valve was closed. When the valve was closed, a low pressure condition was created which initiated the division I SSW system. As corrective action, the procedure has been revised to improve the sequence of operator actions and eliminate ambiguity.
4581994012 | River Bend | 05/22/1994 | 06/23/1994 | 9406290126 | <strong>Containment Breach During Core Alterations Due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>At 0010 on 5/23/94, with the plant in a refueling outage, the heightened awareness and questioning attitude of an operator led to the discovery that air from the reactor building (RB) was leaving containment through the inclined fuel transfer system (IFTS) tube drain line to the fuel building (FB). Technical Specification (TS) 3/4.6.1.2 requires that primary containment integrity be maintained during fuel handling, core alterations, and operations with a potential for draining the reactor vessel. An investigation of the identified condition determined that a breach of primary containment to the FB existed during core alterations, which is a violation of this TS. <br /><br /> This condition was caused by inadequate design. A trap or water seal was not installed in the IFTS drain line. <br /><br /> There is no known instance of this condition existing during core alterations without secondary containment integrity - fuel building (SCI-FB). With SCI-FB in place, this condition is bounded by the analysis for a fuel handling accident in the FB. Therefore, there was no impact on the safe operation of the plant or the health and safety of the public as a result of this condition. No similar events have been reported.
4581994013 | River Bend | 06/02/1994 | 07/05/1994 | 9407110132 | <strong>Division III Diesel Generator Start Most Likely Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 0820 on June 2, 1994 with the unit in Operational Condition 5 (Refueling), a Division III Emergency Core Cooling System (ECCS) surveillance was being performed. Shortly after a continuity check had been performed across two LOCA relay contacts in the ECCS circuitry, the normal power supply breaker to the High Pressure Core Spray (HPCS) 4160 volt bus tripped. This condition led to an automatic start and load of the Division Ill diesel generator. <br /><br /> The cause of the normal supply breaker trip and the resulting start of the Division III diesel generator cannot be positively deter-mined. However, given that no physical condition could be identified which could have caused the event and that the event could be replicated by shorting adjacent contacts, personnel error during the performance of the surveillance is the most probable root cause of this ESF actuation. <br /><br /> Corrective action for this event include the formation of a multi-discipline team to evaluate maintenance practices and processes with a goal of reducing inadvertent ESF actuations during maintenance. <br /><br /> Since the diesel generator responded properly to the unplanned start signal, this event was of no safety significance. Similar LERs include 93-017 and 93-018.
4581994014 | River Bend | 06/02/1994 | 07/05/1994 | 9407110153 | <strong>Actuation of Multiple Division I Containment Isolation Valves Due to Inadequate Review of a Job Plan Change</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1994 at 1705, with the plant in Operational Condition 5 (Refueling), a division I balance of plant (BOP) containment isolation signal was generated during replacement of the base of a relay. This resulted in closure of several containment isolation valves in various systems. <br /><br /> The root cause of this event was inattention to detail by the electrical discipline technical specialist in that the risk and consequences of a change to the job plan were not adequately reviewed and assessed. The electrical discipline technical specialist was counseled in a meeting with his supervision and the general manager plant operations. <br /><br /> In accordance with Abnormal Operating Procedure, AOP - 0003, 'Automatic Isolations,' operations personnel confirmed that the plant responded properly to the ESF signal and each isolation occurred as expected. Therefore, this event did not compromise the health and safety of the public or plant personnel.
4581994015 | River Bend | 06/06/1994 | 07/06/1994 | 9407130164 | <strong>ESF Actuation Caused By Pin Failure In Test Equipment Patch Cord</strong><br /><i>Abstract:&nbsp;</i>At 0730 on June 6, 1994, with the reactor in Operational Condition 5 (Refueling), a fuse blew while test equipment required for performing STP-058-4802, 'Primary Containment Isolation System Manual Initiation Switches Time Response Test' was being installed. The Containment Atmosphere Monitoring System Hydrogen Analyzer, an ESF, auto-started as designed as a result of this blown fuse. <br /><br /> This event was caused by failure of a soldered joint in an Amphenol connector on a patch cord that was part of the M&TE used during the performance of this surveillance. The faulty connection created a high current condition that blew the fuse. The blown fuse was replaced and the faulty connector repaired. A detailed inspection of all of the Amphenol connectors on these patch cords will be performed to provide additional assurance that the remaining soldered connections are in good condition. <br /><br /> This hydrogen analyzer was not required to be operable during this event and no condition existed that would require hydrogen monitoring. Thus the actuation of this system had no impact on the safety of the plant. No similar LER's have been submitted.
4581994016 | River Bend | 06/10/1994 | 07/08/1994 | 9407140103 | <strong>Reactor Mode Switch Positioned for Testing With Required System Inoperable Due to Communication Error</strong><br /><i>Abstract:&nbsp;</i>On 6/10/94, with the plant in refueling, the reactor mode switch was placed in Start-Up/ Standby to allow the performance of surveillance testing. At that time, both divisions of the reactor protection system (RPS) were considered inoperable due to the replacement of relays which had not been functionally tested. The mode switch should have remained locked in the shutdown position per Technical Specification 3.3.1, Table 3.3.1-1, Action 9, until functional testing of the relays was completed. <br /><br /> The root cause of this condition was faulty communication between the Work Management Center Supervisor (WMCS) and the Control Room Supervisor (CRS). Contributing factors included inaccurate transfer of information to the CRS regarding the status of the RPS and an improperly written LCO action statement tracking document. <br /><br /> During the period that the reactor mode switch was not locked in Shutdown, the safety function of RPS was fully satisfied because all control rods remained fully inserted in the core. Therefore, there was no threat to the health and safety of the public. Corrective action includes required reading of the condition report associated with this LER, review and enhancement of Operations Policy # 16, 'Work Management Center Guidelines,' and the addition of this event to the industry events portion of the refuel training module. LER's 94-002 and 94-008 reported similar events.
4581994017 | River Bend | 06/17/1994 | 11/30/1994 | 9412060033 | <strong>Seven Testable Check Valves Not Properly Tested In Accordance With ASME Section XI Requirements</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1994 at 1300, with the plant in Operational Condition 4 (Cold Shutdown), seven testable check valves were discovered not properly tested in accordance with ASME Section XI requirements. These valves include five (5), 10-inch emergency core cooling system (ECCS) and two (2), 6-inch reactor core isolation cooling (RCIC) System testable check valves. The investigation revealed that applicable surveillance test procedures did not require that the force or torque required to reposition the valve be established, determined or noted. <br /><br /> Based on the information available, this condition appears to have existed since initial Inservice Testing (IST) program development. The cause of this event is indeterminate; however, there are two causal factors. First, there was a failure to implement a proper surveillance test method for manually exercising the testable check valves. Second, personnel failed to recognize the discrepancy between the test method described in ASME Section XI and the test method described in the applicable surveillance test procedures. <br /><br /> Corrective actions include revising the applicable surveillance test procedures to ensure proper testing and implementing an IST Improvement Plan to ensure that the existing IST program is technically and functionally adequate. This LER is submitted as a voluntary report.
4581994018 | River Bend | 06/23/1994 | 07/22/1994 | 9408010186 | <strong>Loss of Shutdown Cooling Due to Inadvertently Dropped Lead</strong><br /><i>Abstract:&nbsp;</i>As a result of River Bend Station's (RBS) pre-outage risk assessment, procedure TP-94-0010, 'Shutdown Cooling Reliability During Refueling Outages,' was developed to add special precautions to reduce the potential for losses of shutdown cooling (SDC). At 0507 on June 23, 1994 with the unit in operational condition 4 (cold shutdown), a fuse was blown during restoration of the plant from the TP-94-0010 configuration. The fuse blew due to a short created by a dropped lead. The blown fuse caused an isolation of the Residual Heat Removal System (RHR) and resulted in the only loss of SDC event that occurred during the outage. <br /><br /> The root cause of this event was personnel error due to an electrical shock received by the technician when removing a jumper. Corrective actions to prevent recurrence include an evaluation to enhance the human engineering aspects of this activity and adding an additional barrier to prevent a loss of SDC during shutdown conditions. The additional barrier may be established by re-sequencing the steps in the procedure such that the RHR suction isolation valves will be de-energized while connecting and disconnecting the jumpers. <br /><br /> This event was of no safety significance. Shutdown cooling was lost for approximately 18 minutes and only a slight increase of the reactor coolant temperature (less than 2 degrees Fahrenheit) was experienced. Alternate shutdown cooling was available via Reactor Water Clean-Up system but was not required.
4581994019 | River Bend | 06/24/1994 | 08/05/1994 | 9408110317 | <strong>Initiation of the Standby Service Water System Due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1994 at 0453 with the reactor in Operational Condition 4 (cold shutdown), the standby service water pumps automatically started during surveillance testing of the division II remote shutdown control circuitry. A part of the test was to operate the standby service water (SSW) supply and return valves to the reactor plant component cooling water (RPCCW) system. This step results in cross-connecting the two systems and creates the potential for ESF actuations. After the RPCCW supply valve was closed, a low pressure condition occurred which caused the SSW system initiation.<br /><br /> The root cause of the event was procedural deficiency in that pertinent information required to prevent the ESF actuation was not included in the text of the procedure. The corrective actions include revising the procedure prior to the next performance. In addition, a multi-disciplinary team will be formed to review the operating history and performance of the SSW system to determine if additional operator training, system modification or procedure improvements are required to prevent ESF actuations. <br /><br /> The operating crew confirmed that the SSW initiation occurred as designed. The SSW system was subsequently restored to a standby lineup.
4581994020 | River Bend | 07/07/1994 | 08/05/1994 | 9408150056 | <strong>TS Surveillance Not Properly Implemented For Water System Because of Inadequate Design Review</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1994, with the plant in Operational Condition 1 (Power Operation), a deficiency in STP 256-0201, 'SWP Valve Lineup Verification,' was identified as part of the ongoing Technical Specification Review Project. This deficiency occurred due to a 1986 Modification Request (MR) which failed to document Technical Specification 4.7.1.1. a surveillance requirements associated with certain locked valves. <br /><br /> The root cause of this event was an inadequate review of the Technical Specification surveillance requirements by the individuals responsible for developing the MR. Immediate actions were taken to verify the position of these valves and to add them to the STP. Corrective actions to prevent recurrence include enhancement of engineering procedure ENG-3-006, 'River Bend Station Design and Modification Request Control Plan,' and enhancement of the administrative process for controlling changes to locked valves. Recent LERs involving STP deficiencies include LERs 92-014, 93-002, 93-005, and 93-012. <br /><br /> Evidence exists that the valves were maintained in their safety position and therefore, this condition was of no safety significance.
4581994021 | River Bend | 07/12/1994 | 10/28/1994 | 9411040048 | <strong>Inadequate Surveillance Testing Of Charcoal Adsorber Filter Trains Due To Deficiencies In Procedures</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1994, with the plant in Operational Condition 1 (Power Operation), the ongoing review of River Bend Station surveillance test procedures (STPs) and Technical Specifications revealed discrepancies between the Technical Specifications and the corresponding surveillance test procedures for leak testing of charcoal adsorber filter trains in three safety related systems. Previous STP performances were determined to be inadequate. The affected equipment was declared inoperable. Following this, the equipment was properly retested and determined to be operable. <br /><br /> The root cause of this event is inadequate control and implementation of the procedure writing, review, and revision process. The affected procedures have been placed on hold to prevent issuance prior to revision to correct deficiencies. The Procedure Upgrade Project includes interim steps to address short-term improvement in procedure adequacy and the Long Term Performance Improvement Plan includes a comprehensive procedure improvement initiative. <br /><br /> The STPs in question did not adequately implement ANSI standards referenced in the licensing basis; however, the inadequacies involved leak detection criteria that was in use when leak detection technology was less advanced than it is today. Therefore, while past surveillances did not meet the ANSI standards, there was no impact on the ability of the systems to perform their safety functions.
4581994022 | River Bend | 09/07/1994 | 10/07/1994 | ML09153046 | <strong>Violation Of Technical Specifications Due To Inadequate Fire Watch</strong><br /><i>Abstract:&nbsp;</i>At 1732 hours on September 7, 1994 with the reactor in Operational Condition 1 (Power Operation), during restoration of a portion of the fire protection system, operations personnel identified that a continuous watch was not properly implemented in accordance with RBS Technical Specifications Section 3.7.6.2.c. The subsequent investigation revealed that the responsible individual left the assigned area approximately twenty-one (21) minutes prior to the sprinkler system being returned to an operable status. The system was returned to service at approximately 1730 hours. <br /><br /> The root cause of this event was attributed to a failure to ensure that the fire watch was maintained during system inoperability. Contract personnel failed to comply with requirements that the fire watch be maintained until the system had been properly restored. Corrective actions included disciplinary actions the responsible individuals and retraining of personnel associated with painting activities. <br /><br /> The area was without coverage for approximately 21 minutes. During this time, automatic sprinkler system AS-12 was operable for fire suppression. The area in the vicinity of the water curtain does not contain equipment which requires the storage of combustible materials for maintenance. Therefore, there was a low probability of a fire occurring in that area during the time of inadequate coverage. Due to other fire protection deficiencies, the Auxiliary Building was also being patrolled by hourly roving fire watch personnel. The health and safety of the public was not compromised as a result of this condition.
4581994023 | River Bend | 09/08/1994 | 12/12/1994 | 9412200148 | <strong>Reactor Scram Due To Spurious Signals From Undamped Rosemount Model 1153 Transmitters</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1994 at 8:28 PM, with the reactor at 97 percent power, an automatic reactor scram occurred due to a false high reactor water level condition sensed on channels C and D of the reactor water level instrumentation. During this event, the RCIC turbine tripped due to binding of the turbine governor valve. The conditions leading to this failure have been determined to be reportable pursuant to 10CFR21. Since the HPCS system was manually operated during this event, this supplement also finalizes the Special Report required by Technical Specification 3.5.1 concerning emergency core cooling system (ECCS) injections. <br /><br /> The cause of this event is spurious signals from undamped Rosemount model 1153 transmitters in response to process noise. The model 1153 transmitters that were in service in the reactor water level instrumentation application have been replaced with Rosemount model 1152s. Extensive monitoring was conducted as a conservative measure during the startup from the forced outage and continuing into power operation for a limited period of time. <br /><br /> The investigation of transmitter performance revealed that the model 1153 susceptibility to process noise would not have prevented the transmitters from functioning properly in an actual event. Equipment and radiological issues, including reactor vessel cooldown and the Technical Specification surveillance time limit non-compliances for radiological and chemistry sampling were evaluated and determined not to be safety significant. Therefore, this event did not compromise the health and safety of the public.
4581994024 | River Bend | 09/11/1994 | 10/10/1994 | 9410170335 | <strong>Drywell Isolation Check Valves Inoperable Due To Inadequate Housekeeping</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1994, with the plant in Operational Condition 4 (Cold Shutdown) four check valves required to satisfy Technical Specification 3.6.4 requirements for drywell isolation functions were found to be impaired by foreign debris. This condition was identified during a disassembly inspection of selected check valves as the result of RBS's activities to improve the Pump and Valve Inservice Testing Program. <br /><br /> These check valves are eight inch swing check valves and are part of the reactor equipment drain and floor drain systems. They have an active safety function in the closed direction for drywell integrity. The root cause of this condition is the failure to maintain adequate housekeeping during the construction and early operations phase of the plant. <br /><br /> The immediate corrective action was to restore the operability of each of the impaired check valves. To prevent recurrence, the reactor plant floor drain system was thoroughly flushed to ensure that no additional trash was present in the system which could impair the safety function of the system's check valves. Selected valves in both of these drain systems will be disassembled and verified operable during the next scheduled refueling outage. No similar event associated with poor housekeeping practices at RBS have been identified. This event was of no safety significance.
4581994025 | River Bend | 09/10/1994 | 10/10/1994 | 9410180130 | <strong>ADS Valve Inoperable Because Fire Wrap Not Replaced After Maintenance</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1994, plant personnel performing a walk-down of all main steam safety relief valve solenoid connections noted that the divisional power cables for the redundant solenoids associated with one Automatic Depressurization System valve were not properly wrapped to meet the requirements of Regulatory Guide 1.75. The plant was Operational Condition 4 (Cold Shutdown) at the time of discovery.<br /><br /> An investigation revealed that the cable wrapping had been removed during the fourth refueling outage as part of a troubleshooting maintenance work order (MWO) which was issued to confirm the existence of an apparent faulty cable connector. In anticipation of this finding, the troubleshooting MWO was issued with partial instructions regarding connector replacement. However, the planning group intended to revise the MWO and provide complete rework instructions once the troubleshooting had confirmed the discrepancy. This intention was not clearly communicated in the troubleshooting MWO and the technician in the field corrected the discrepancy using the partial work instructions without obtaining a revision to the MWO. The partial rework instructions in the troubleshooting MWO did not include appropriate steps to ensure that separation criteria would be maintained. <br /><br /> Wrapping was successfully placed on the valve cables on September 18, 1994. Subsequent to refueling outage 4, a procedure was issued to control troubleshooting activities. Additionally, an evaluation of maintenance procedures/processes will be performed and enhancements made to the program as necessary. The condition did not significantly compromise the safety of the plant because sufficient ADS valves remained operable to satisfy system demands.
4581994026 | River Bend | 09/15/1994 | 10/13/1994 | 9410180233 | <strong>Inadequate Surveillance Test Of Access Gate Limit Switches Due To Deficiencies In Procedures</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1994, with the plant in Operational Condition 4 (Cold Shutdown), a deficiency in STP 055-0101, 'IFTS Pre-Op and Weekly Interlock Operability Test,' was identified as part of the ongoing Technical Specification Review Project. This deficiency resulted in the failure to test gate position limit switches associated with the Containment Isolation Valve Room Gate, the Annulus Inclined Fuel Transfer System (IFTS) Support Room Gate, and the Fuel Building Mid-Support Room Gate interlock system as required to satisfy Technical Specifications 4.9.12.3 and 4.9.12.4. <br /><br /> Technical Specifications 4.9.12.3 and 4.9.12.4 require verification to ensure operability of the access interlocks which prevent operation of the IFTS while personnel are in the associated rooms. Testing requirements for the access gate limit switches were omitted from the surveillance test procedure (STP) during initial development. Other portions of the interlock system were tested. <br /><br /> The root cause of this occurrence was inadequate oversight of the STP development, review and revision process in that the gate position limit switches for the Containment Isolation Valve Room Gate, the Annulus IFTS Support Room Gate, and the Fuel Building Mid-Support Room Gate were not included during the initial procedure development or subsequent review and revisions. Investigation indicated that this condition had existed prior to plant start-up and was not identified during subsequent reviews and revisions of this procedure. Corrective actions to incorporate the applicable test requirements for the limit switches have been completed and test results indicate the limit switches were operable.
4581994027 | River Bend | 10/10/1994 | 11/09/1994 | 9411160196 | <strong>TGSCC of CRD Piping Due to Inadvertent Contamination with a Chloride Bearing Substance</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1994 at approximately 0100, with the plant in Operational Condition 4 (cold shutdown), a control rod drive (CRD) pipe was found to be cracked and leaking. This condition was identified by plant personnel exhibiting a noteworthy level of attention to detail during a scheduled walkdown/visual inspection of the drywell prior to plant startup. Investigations were performed which determined that a total of eight CRD pipes, and a section of the 'A' variable leg narrow range level pipe were affected and required repairs. Detailed analyses of this condition concluded that the failure mode was chloride induced Transgranular Stress Corrosion Cracking (TGSCC). The event which created the opportunity for the TGSCC is suspected to be a spill of high chloride bearing Therma-Cel 950 adhesive on the piping during the plant construction or early refueling outages. <br /><br /> Immediate corrective actions were taken to replace those sections of stainless steel pipe that exhibited crack indications. The balance of the plant equipment that could have been susceptible to this degradation has been addressed. To preclude recurrence, the chemicals used in the power block will be evaluated and additional control measures will be instituted, if appropriate. This condition did not pose a significant safety hazard. A review of LERs at RBS did not reveal any similar events.
4581994028 | River Bend | 10/28/1994 | 11/18/1994 | 9411290096 | <strong>Manual Reactor Scram Due To High LP Turbine Vibration Caused By Temperature Sensitive Rotor</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1994, with the plant in Operational Condition 1 (Power Operation) and decreasing power for a planned shutdown, vibration levels on main turbine bearings 5 and 6 increased to the trip set point of 10 mils. The plant was manually scrammed and the turbine manually tripped to prevent potential turbine damage due to high vibration. <br /><br /> The root cause of the event is increased temperature sensitivity of the Low Pressure Turbine Rotor B following its recent replacement in conjunction with step changes in rotor temperature caused by throttling the reheating steam supply valves. Corrective actions include limiting the rate of rotor temperature change by expanding the limitations at which the MSRs can be placed into or removed from service during plant start-up or shutdown. During the event, turbine vibration remained within acceptable levels and the temperature change requirements for the MSR were never exceeded. An evaluation determined that safety systems functioned as designed and concluded the event was of no safety significance.
4581994029 | River Bend | 11/18/1994 | 12/19/1994 | 9412290170 | <strong>Missed Surveillance Due To Inadequate Review Of Tech Spec Amendment</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1994, at 0830 hours with the plant in Operational Condition 1 (Power operation), it was discovered that Technical Specification (TS) surveillance requirements imposed by a recent TS amendment had not been performed within the specified implementation period. This TS amendment added a requirement to calibrate the reactor pressure-high trip units on a quarterly basis. The affected equipment was immediately tested and determined to be operable. <br /><br /> The root cause of this event was a personnel error due to an inadequate review during the implementation of Amendment 74 to the TS. Immediate corrective actions to incorporate the applicable test requirements for the trip units have been completed. Long-term enhancements to the TS amendment process have been identified. While several LERs have been submitted regarding STP deficiencies, no similar deficiency associated with the implementation of a TS amendment has been identified. This event was of no safety significance.
4581994030 | River Bend | 12/04/1994 | 12/29/1994 | 9501050269 | <strong>Reactor Scram Resulting From Inadvertent MSIV Isolation Due To Failure To Follow Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On December 4, 1994 with the plant in Operational Condition 1 (Power Operation), a reactor scram occurred when isolation logic was satisfied for a Main Steam Isolation Valve (MSIV) isolation. This isolation signal was the direct result of surveillance activities that were being performed prior to the event. <br /><br /> The root cause of the event was that a procedural step requiring removal of a half MSIV isolation signal was not performed as required. This action resulted in the failure to remove a half MSIV isolation signal on one test channel prior to proceeding to the next test channel where another half MSIV isolation signal was generated. Corrective actions consisted of reinforcing management expectations regarding personal accountability and procedure compliance. Also, the procedure revision process was modified to ensure that the appropriate verification requirements are considered during procedure revisions and reviews. The surveillance procedure was revised to incorporate the appropriate level of verification to ensure the MSIV isolation circuitry was restored before proceeding in the procedure. An evaluation determined that operator actions during the scram were appropriate and that safety systems functioned as designed.
4581994031 | River Bend | 10/03/1994 | 12/30/1994 | 9501050275 | <strong>Failure To Identify Technical Specification Non- Compliance Due To Inadequate Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1994, with the plant shutdown (Operating Condition 4) during a forced outage, review of reactor protection system (RPS) level transmitter response time data indicated that the Channel D RPS level transmitter had a response time of 1.197 seconds in February 1992 and the Channel C RPS level transmitter had a response time of 1.190 seconds in January 1994. In each case, it was not recognized at the time that these values exceeded the Technical Specification acceptance criteria of 1.05 seconds and, as a result, no action was taken to address the non-compliance with the Technical Specification 3.3.1 which was in effect at that time. <br /><br /> The primary root cause of this condition was procedure inadequacy. The procedure did not specify acceptance criteria or provide guidance on the various responsibilities required for procedure implementation. <br /><br /> Corrective actions include procedure revisions to incorporate the necessary acceptance criteria and provide guidance concerning the responsibilities of personnel both performing and reviewing this procedure and associated data. A safety evaluation concluded that no safety margins or design limits were exceeded and that the transmitters would have performed their safety function in the as-found condition.
4581994032 | River Bend | 12/14/1994 | 01/13/1995 | 9501200295 | <strong>Failure of the Division III Diesel Generator due to Improper Synchronization Attempt by an Operator</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1994 at approximately 1435, an operator improperly attempted to synchronize the division III diesel generator to bus 1E22*S004. The investigation of this event revealed a shorted Selenium rectifier in the generator exciter circuitry which resulted in loss of the safety function of the high pressure core spray (HPCS) diesel generator. This event also constitutes an invalid failure of the division III diesel generator per Regulatory Guide 1.108, Position c.2.e.(2). <br /><br /> The unit operator (UO) failed to look at the synchroscope before closing the output breaker due to tunnel vision. Corrective actions include consideration of disciplinary action for the individual involved, and continued performance monitoring testing of the diesel generator pending further evaluation of generator replacement. Installation of synch check relays to prevent recurrence, with scheduling to be evaluated prior to installation, is also a corrective action. <br /><br /> Loss of the HPCS system has been analyzed and is bounded by the safety analysis. During the time that the HPCS system was considered inoperable, the low pressure coolant injection and core spray systems, the automatic depressurization system, and the reactor core isolation cooling system were operable. The division III diesel and the HPCS system were restored to operability 5 days following the event.
4611994001 | Clinton 1 | 01/15/1994 | 02/14/1994 | 9402280138 | <strong>Unexpected Automatic Isolation of Reactor Core Isolation Cooling Systems During Channel Calibration Surveillance Due to Lifting Wrong Thermocouple Lead</strong><br /><i>Abstract:&nbsp;</i>With the plant at 100 percent reactor pressure, Control and Instrumentation Maintenance (C&I) technicians were performing a channel calibration surveillance on a Reactor Water Cleanup System heat exchanger room area temperature channel. The technicians reviewed the drawing to verify the correct field thermocouple termination to be lifted, but then inadvertently lifted a lead from a different terminal, placing the Reactor Core Isolation Cooling (RCIC) system equipment room ambient temperature channel in a tripped condition. As a result, a RCIC steam supply containment isolation valve automatically closed and the RCIC pump turbine tripped from the standby mode. The RCIC system was restored within sixteen minutes. The cause of this event is personnel error. The technicians performed inadequate double verification and self-checking in locating and lifting the field thermocouple lead. Unusual characteristics of the work area contributed to the cause of this event. Corrective actions include the technicians understanding their error, installing improved labeling and using maxi-grabbers to identify and mark leads to be lifted.
4611994002 | Clinton 1 | 02/01/1994 | 03/10/1994 | 9403150351 | <strong>Inoperable Division 2 Main Steam Isolation Valve Leakage Control System Dilution Air Flow Transmitter Due to Mispositioned Valves While Division I Emergency Diesel Generator was Out of Service</strong><br /><i>Abstract:&nbsp;</i>Control and Instrumentation (C&I) technicians identified closed instrument root valves for the Division 2 Main Steam Isolation Valve - Leakage Control System dilution air flow transmitter, making the transmitter inoperable. A definite time of mispositioning could not be determined; however, during a portion of the time that the transmitter was most likely inoperable, the Division 1 Emergency Diesel Generator (EDG) was also inoperable for routine inspection and maintenance. Since the inoperable status of the transmitter was unknown by operators, the requirements of Technical Specification 3.8.1.1, Action 'e' were not met. When Division 1 or Division 2 EDG is inoperable, Action 'e' requires a verification within two hours that all required systems, subsystems, trains, components and devices that depend on the remaining OPERABLE diesel generator as a source of emergency power are operable. The cause of this event is personnel error, most likely by C&I technicians who manipulated the transmitter's valves and failed to restore the instrument root valves to the open position. The lack of labels on the transmitter's valves most likely contributed to the cause of this event. Corrective actions include briefing C&I technicians on manipulating valves and installing labels on the transmitter's valves.
4611994003 | Clinton 1 | 04/15/1994 | 05/13/1994 | 9405230114 | <strong>Recirculation System Flow Transient Due to Solenoid Valve Failure Results in Thermal Power Level Exceeding the Operating License Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1994, at 1111 hours, reactor thermal power level exceeded 100 percent of rated thermal power due to an unexpected reactor recirculation system flow control transient. Prior to this event, the plant was in POWER OPERATION at about 100 percent of rated thermal power. Reactor power exceeded 100 percent for approximately 63 seconds. The cause of this event was failure of a solenoid valve in the hydraulic power unit for one of the two reactor recirculation flow control valves. The solenoid valve failure caused the affected reactor recirculation flow control valve to ramp full open. An investigation found that the isolate coil of the solenoid valve had burned out, causing the solenoid valve to fail. Corrective action for this event includes replacing the solenoid valve, replacing a programmable logic controller module, training Operations personnel about this event, and revising procedures and preventive maintenance tasks. This report is being submitted due to violation of Section 2.C(1) of the Clinton Power Station Operating License, which prohibits plant operation at reactor core power levels in excess of 100 percent rated thermal power.
4611994004 | Clinton 1 | 04/13/1994 | 05/06/1994 | 9405130192 | <strong>Minimum Control Room Staffing Not Met When Only Licensed Senior Reactor Operator In the Control Room Failed to Request Relief Before Exiting</strong><br /><i>Abstract:&nbsp;</i>With the plant in POWER OPERATION at about 95 percent reactor power, the Line Assistant Shift Supervisor (LASS), the only licensed senior reactor operator (SRO) in the main control room (MCR) area, experienced severe abdominal cramps, requiring him to leave the MCR area for about 3 minutes and 10 seconds to use the restroom. The Shift Supervisor (SS) and the Staff Assistant Shift Supervisor (SASS), the other shift crew SROs, were touring the screenhouse due to high lake water level caused by heavy rain. During the LASS' absence, no SRO was in the MCR, thus the requirements of Technical Specification (TS) 6.2.2.b were not met. TS 6.2.2.b requires at least one licensed SRO in the MCR while the plant is in POWER OPERATION, STARTUP, or HOT SHUTDOWN. No evolutions or power changes were in progress during the absence of SROs from the MCR. The cause of this event is attributed to untimely action by the LASS. When the LASS became aware of his developing discomfort, he delayed contacting the SS or the SASS for relief When the LASS realized he could no longer delay using the restroom, his condition was such that he had no time for contacting the SS or SASS. Corrective actions include counseling the LASS, and discussing this event with the reactor operators and senior reactor operators.
4611994005 | Clinton 1 | 04/08/1992 | 06/03/1994 | 9406090214 | <strong>Technological Advancements in Controlling Electrical Load Additions Result in Identification of Improper Second- Level Undervoltage Relay Setpoint</strong><br /><i>Abstract:&nbsp;</i>In 1992, electrical design engineers raised a concern that the setpoints for second-level undervoltage relay in the auxiliary power (AP) system may not be correctly set to provide adequate voltage for proper equipment operation. A plan to address the concern included installing an alarm to alert operators if bus voltage decreases to 3940 volts, providing an annunciator procedure for operator guidance in response to the alarm, training operators on the alarm and proper response, determining the minimum voltage required, and developing design change options to restore the plant to the design basis regarding degraded voltage. In 1994, an extensive study of the AP system response under Loss of Coolant Accident (LOCA) conditions identified the minimum voltage required by engineered safety features equipment at all levels from the 4160-volt to the 120-volt levels and concluded that the second-level undervoltage relay minimum reset point of 3799 volts would not ensure sufficient voltages for all equipment fed from the 120-volt motor control center distribution panels following a postulated LOCA scenario. The cause of the event is attributed to an initial design error in second-level undervoltage relay setpoint and reset point, which was identified by technological advancements in analyzing electrical load. Corrective actions included those actions discussed above, new computer tools for improved analytical modeling, and improved configuration controls.
4611994006 | Clinton 1 | 06/07/1994 | 08/19/1994 | 9408250038 | <strong>Failure of Optical Isolator Power Supply for Diesel Generator (DG) Output Wattmeter and Failure to Question Conflicting Indications During Surveillance Tests Results in Failure to Fully Load DG</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1994, Illinois Power identified that the Division 1 emergency diesel generator (DG) was not loaded to at least 3869 kilowatts (KW) as required by Technical Specification 4.8.1.1.2.a.5 during surveillance tests performed between June 7 and July 21, 1994, because the main control room (MCR) KW output meter used to verify the load value was inaccurate. The cause of this event is attributed to personnel error and equipment failure. Some personnel were aware of a conflict between the MCR meter and the local KW output meter indications since June 7, 1994, but failed to initiate appropriate action to resolve the discrepancy. A power supply for optical isolators in the circuit feeding the MCR meter had degraded causing the optical isolators to be out of calibration tolerance and the MCR meter to be inaccurate. Corrective actions included verifying that the DG was capable of being loaded to 3869 KW, replacing the optical isolator power supply, calibrating the optical isolator loop, briefing operators about this event, and revising a procedure to include guidance on assessing conflicting indication.
4611994007 | Clinton 1 | 08/08/1994 | 09/02/1994 | 9409160315 | <strong>Inattention to Detail Preparation for Plant Startup Results in Failure to Complete Intermediate Range Monitor Detector Not-Full- In Control Rod Block Functional Test Prior to Entering the Startup Mode.</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1994, a channel functional test of the intermediate range monitor (IRM) detector-not-full-in control rod block function was not completed as required prior to plant entry into Mode 2 (STARTUP). The cause of the event is attributed to a lack of attention to detail by the staff assistant shift supervisor (SASS). While completing the checklist of prerequisites for entry into Mode 2, the SASS noticed that a portion of a surveillance test procedure had not been performed but did not recognize that the portion was required to be completed prior to entry into Mode 2. The SASS then incorrectly initialed the checklist to indicate the test was current. The approach-to-critical integrated procedure contributed to the cause of this event because it did not contain a prerequisite to remind personnel that the test must be performed within seven days prior to plant startup. Corrective actions include the shift supervisor discussing the event with the SASS and emphasizing attention to detail, revising the approach to critical integrated procedure to include a prerequisite to verify the test is current prior to plant startup, and providing information about this event to Operations personnel.
4611994008 | Clinton 1 | 04/17/1994 | 10/28/1994 | 9411070427 | <strong>Reactor Recirculation (RR) Pump Discharge Valves Outside Seismic Design Bases Due to Loose Yoke Connections, Cause Unknown</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1994, engineers identified that the yoke connections of the discharge isolation valve (ISV) on both reactor recirculation (RR) loops did not meet seismic qualification requirements in the condition they were found on April 17, 1994. This condition was outside the plant's design basis. The plant was in COLD SHUTDOWN for a planned outage on April 17, 1994, when main control room operators attempted to electrically close the 'A' RR pump discharge ISV to isolate the loop for replacement of the pump seal. The valve would not fully close. Loose and missing studs/nuts found at the valve's yoke connection caused the valve and actuator to bind, preventing full closure. The 'B' RR discharge ISV also had loose studs/nuts in its yoke connection. An engineering evaluation concluded that the structural integrity of the yoke connections could not be assured during an operating basis earthquake event in the condition they were found. The cause of the loose bolts is unknown. Possible causes include piping vibration, thermal cycling, and improper installation during manufacturing/construction. Corrective actions for this event include applying Loctite to the threads of the studs/nuts and properly tensioning the yoke connections, and reinspecting the connections during the next refueling outage.
4611994009 | Clinton 1 | 12/20/1994 | 01/13/1995 | 9501250394 | <strong>Oversight by Licensed Operator Results in Failure to Demonstrate Operability of Offsite Alternating Current Power Sources Within One Hour After Declaring the Emergency Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1994, the plant was in POWER OPERATION at 100 percent reactor power and a planned maintenance outage was scheduled for Division 3 equipment. Due to the scope of the outage work, the Division 3 emergency diesel generator (EDG) and other equipment were declared inoperable at about 0500 hours. With the Division 3 EDG out of service for planned maintenance, action 'd' of Technical Specification (TS) 3.8.1.1 requires the operability of the offsite alternating current power sources to be demonstrated by performing TS Surveillance Requirement 4.8.1.1.1.a within one hour and at least once per eight hours thereafter. At about 0640 hours, operators realized that the one-hour action had not been completed. The action was completed by 0647 hours with satisfactory results. The TS actions for the other equipment were initiated as required. The cause of this event is attributed to licensed operator error. The operator tracking the implementation of the TS requirements forgot to perform the action within one hour. Corrective action for this event included reviewing the event and discussing the findings with involved personnel, issuing an Operations Night Order containing the shift supervisor's report of the event, and the plant manager discussing the event with the involved shift supervisor.
4821994001 | Wolf Creek | 12/14/1993 | 02/02/1994 | 9402100130 | <strong>Non-Safety Related Indicating Lamps Cause Equipment Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1993, at 0720 hours, a local indicating lamp short circuited causing an associated control power fuse to open, thus rendering the 'B' Centrifugal Charging Pump room cooler inoperable. Similar indicating lamps were installed as local indication for various other safety-related Motor Control Center starters. This created the potential for a common mode failure that could have led to multiple inoperable safety systems. Perhaps most significantly, the Boron injection Tank (BIT) isolation valves could have lost control power, thereby delaying the initiation of high-head safety injection in an accident situation.<br /><br /> The root cause of the open control power fuse was due to the indicating lamp failing in a manner which led to a lower circuit resistance, and increased current draw. Additionally, a misapplication of the lamps in seismically qualified equipment is possible as the vendor does not recommend their use under conditions of shock or vibration.
4821994002 | Wolf Creek | 01/24/1994 | 02/24/1994 | 9403080074 | <strong>Shutdown Required by Tech. Specs. Due to Control Rod M- 12</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1994, at 0841 hours (CST) Wolf Creek Generating Station (WCGS) entered Technical Specification 3.1.3.1, Action Statement c) (4), due to an electrical problem with Control Rod Drive Mechanism (CRDM) M-12. <br /><br /> Wolf Creek Nuclear Operating Corporation personnel determined that CRDM M12 could not be restored to OPERABLE status within the 72 hour Technical Specification Limiting Condition for Operation. Therefore, a plant shutdown was commenced on January 27, 1994, at 0244 hours. At 0423 hours, WCGS was shutdown by manual reactor trip. The expected Engineered Safety Features actuations occurred. A call was made to the NRC Operations Center at 0551 hours regarding this reactor trip. <br /><br /> The root cause for the misalignment of Control Rod M-12 was a loose cable connector for CRDM M12 which was not making the electrical connection between the pins in the connector and the coil receptacle socket on top of the reactor head. Upon completion of maintenance on the connector and replacement of a failed thyristor in a power supply cabinet the plant was returned to power operation.
4821994003 | Wolf Creek | 03/31/1994 | 05/06/1994 | 9405110261 | <strong>Programmatic Deficiency results in Unqualified Shift Technical Advisor Assigned on Shift Crew</strong><br /><i>Abstract:&nbsp;</i>Wolf Creek Generating Station Technical Specification Administrative Requirement 6.2-2. a specifies that the Unit Staff will include an individual qualified to fulfill the function of the Shift Technical Advisor when the unit is in Modes 1, 2, 3, and 4. <br /><br /> Contrary to the above, on March 31, 1994, an individual who did not fully meet the Wolf Creek Generating Station (WCGS) qualification requirements was assigned to fill the Shift Technical Advisor (STA) position. This incident is being reported under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. <br /><br /> The root cause of this occurrence is attributed to the failure of WCGS personnel to adequately review and compare the plant's programmatic requirements for the STA function with the existing training course descriptions. The six existing Shift Engineers were temporarily removed from their assigned Shift Crew duties and have now completed all required STA training courses.
4821994004 | Wolf Creek | 04/20/1994 | 05/25/1994 | 9405310218 | <strong>Loss of the 1E HVAC System Due to Inadequate Programmatic Controls</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1994, at 1217 hours, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel, while performing testing of the Fire Protection System KQ! simultaneously disabled both trains of the Class 1E Heating, Ventilation and Air Conditioning (HVAC) FG! System. The 'A' Train of the Class 1E HVAC System was disabled for testing. The 'B' Train of the Class 1E HVAC System became disabled due to human error while performing testing on the 'A' Train of the Class 1E HVAC System. The technician involved in the testing mistakenly jumpered the wrong terminals within the control panel causing the Electrothermal Links on one of the 'B' Train Dampers to melt; thus causing the damper to close. The closure of the damper effectively made the system inoperable. <br /><br /> Corrective actions included restoration of the 'A' Train of the Class 1E HVAC System, repair and restoration of the 'B' Train of the Class 1E HVAC System, counseling of the personnel involved in the incident and revision of the procedure used to perform the testing activity.
4821994005 | Wolf Creek | 06/08/1994 | 07/08/1994 | 9407130053 | <strong>Entry Into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1994, at 1430 hours, the Wolf Creek Generating Station entered Technical Specification 3.0.3 due to both Containment Spray Pumps [BE] being inoperable at the same time. Technical Specification 3.0.3 was exited on June 8, 1994, at 1447 hours when the 'B' Containment Spray Pump was returned to operable status.<br /><br /> The 'B' Containment Spray Pump was declared inoperable on June 8, 1994, at 0944 hours, to facilitate testing of the pump. The pump was returned to operable status on June 8, 1994 at 1447 hours, following successful testing.<br /><br /> At 1430 hours on June 8, 1994, it was determined that the 'A' Essential Service Water Train [BI] was inoperable due to the inoperability of the Essential Service Water Pump Discharge Strainer. Inoperability of the 'A' Essential Service Water Train results in the inoperability of the 'A' Containment Spray Pump. <br /><br /> Wolf Creek Nuclear Operating Corporation (WCNOC) has implemented a weekly program of manually initiating the backwash for each of the Essential Service Water Pump Discharge Strainers. This program was implemented to keep the strainers cleaned, gearing lubricated, and to minimize the buildup of corrosion products that may hamper operation of the strainers.
4821994006 | Wolf Creek | 06/15/1994 | 07/15/1994 | 9407200184 | <strong>Inadequate Review of Motor Operated Valve Retest Sequence Caused Unanticipated Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>Limitorque actuators on the Motor Operated Valves (MOV's) in the Essential Service Water (ESW) lines to and from the Component Cooling Water heat exchangers were sequentially changed out on both safety trains. During the subsequent retest activities, the ESW flow balance was altered and the related Emergency Diesel Generator (EDG) might not have received sufficient cooling water flow had that EDG been required to provide Safeguards power. <br /><br /> Technical Specification 3.8.1.1, Action statement 'b' requires, in part, that offsite A.C. power sources be demonstrated operable within one hour after declaring an EDG inoperable. That Action statement was not entered at the appropriate time for either train. Consequently the appropriate surveillance test procedure was not completed in the required time. Both incidents are therefore reportable under 10 CFR 50.73 (a) (2) (i) (B) as conditions prohibited by Technical Specifications. <br /><br /> The root cause of this occurrence was inadequate job scoping in that interaction with other systems was not adequately considered in the MOV retest sequence.
4821994007 | Wolf Creek | 01/24/1994 | 09/02/1994 | 9409120033 | <strong>Failure to Perform Emergency Diesel Generator Fast Load Test</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1994, during the performance of surveillance test procedure STS KJ-005A, Revision 20, 'Manual/ Auto Start, Synchronization, and Loading of Emergency Diesel Generator NE01' Wolf Creek Nuclear Operating Corporation Operation's personnel incorrectly marked step 5.2.10.2 as not-applicable. This step involves a requirement to fast load the 'A' Emergency Diesel Generator. The performance of a fast load test is required once every 184 days by Technical Specification 4.8.1.1.2f (programmatically required every January and July). The test had been scheduled to meet the requirements of Technical Specification 4.8.1.1.2f. <br /><br /> The root cause of this event is cognitive personnel error. Contributing factors include the time at which the test was performed (i.e., during shift turnover) and that step 5.2.10.2 of procedure STS KJ-005A did not clearly delineate the requirements of Technical Specification 4.8.1.1.2f. <br /><br /> Corrective actions included the revision of procedures STS KJ-005A and STS KJ-005B to clearly delineate the requirements of Technical Specification 4.8.1.1.2f, and the placement of Performance Improvement Request 94-1281 in the Operations Required Reading Program.
4821994009 | Wolf Creek | 09/18/1994 | 10/07/1994 | 9410190102 | <strong>Inoperable Boron Injection Flow Path</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1994, at 1130 hours, Wolf Creek Nuclear Operating Corporation (WCNOC) added hydrogen peroxide to the reactor coolant system. This addition constituted a positive reactivity insertion of less than 1 pcm, or 10 parts per million boron. Subsequently it was determined, this positive reactivity insertion occurred without an operable boron injection flow path. <br /><br /> The 'A' Centrifugal Charging Pump [BQ] was technically inoperable due to the 'A' Emergency Diesel Generator [EK] being inoperable. The 'A' Emergency Diesel was determined to be inoperable on September 19, 1994, at 2300 hours CDT and to have been inoperable since 0600 hours CDT on September 18, 1994, due to a loose overspeed trip limit switch, which could have caused the diesel to trip during a seismic event. <br /><br /> The 'B' Centrifugal Charging Pump was tagged out for cold over-pressure protection. <br /><br /> The loose limit switch was replaced. The retaining screws for the limit switch were coated in locking compound to prevent vibrational backout. The overspeed trip limit switch for the 'B' Emergency Diesel Generator was inspected and found to be in good physical condition.
4821994010 | Wolf Creek | 09/16/1994 | 10/14/1994 | 9410190173 | <strong>Engineered Safety Features Actuation due to Loss of Source Range Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1994, at 1812 (CDT), with Wolf Creek Generating Station in Mode 4, cooling down in preparation for refueling, Source Range Instrument SE N-31 was declared inoperable due to indicated counts increasing while there was no increase to input counts. Source Range Instrument SE N-32 exhibited the same characteristics and was declared inoperable at 0555 on September 17, 1994. The Shift Supervisor entered Technical Specification 3.3.1, Action Statement 5 b., and opened the Reactor Trip Breakers as required. When the Reactor Trip Breakers were opened, the Engineered Safety Features Actuation Signal for main Feedwater Isolation was actuated and the Main Feedwater Isolation valves closed as per design. <br /><br /> The root cause of this event is failure of the Source Range Instrumentation due to noise disturbance. Corrective action was to replace both channels of Source Range Instrumentation, SE N-31 and SE N- 32.
4821994012 | Wolf Creek | 09/01/1994 | 10/24/1994 | 9411010165 | <strong>Failure To Correctly Calibrate Refueling Machine Load Monitor</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1994, at 0509 hours CDT, Wolf Creek Nuclear Operating Corporation (WCNOC) commenced core off-load activities. While conducting the core off-load the Refueling Crew experienced difficulty due to receipt of underload indications on the Refueling Machine [DF] while inserting assemblies into the Upender. <br /><br /> Investigation into the underload indications determined the cause to be bowed assemblies. However, the investigation further determined that the Refueling Machine Primary Automatic Overload Cutoff had been set 100 pounds in the non-conservative direction when handling heavy assemblies (fuel assemblies with inserted control rod assembly). This resulted in WCNOC being in violation of Technical Specification 3.9.6 for the eleven heavy assemblies moved prior to the time of discovery. <br /><br /> The root cause of this event was determined to be an inadequate procedure controlling the calibration, setup, and checkout of the Refuel Machine Load Monitor and personnel misunderstanding the need to perform a field calibration of the load monitor. The procedure was revised and the load monitor was re-calibrated. The core off-load was then completed without further incident.
4821994013 | Wolf Creek | 09/17/1994 | 01/04/1995 | 9501120219 | <strong>Personnel Error Resulted in an Unanticipated Loss of Reactor Coolant Level</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1994, with the plant in MODE 4 at 300 degrees F and 340 psig, Wolf Creek Generating Station experienced an unanticipated decrease in Reactor Coolant level due to personnel error. The 'A' Residual Heat Removal (RHR) [BP] train was lined up to the Reactor Coolant System (RCS) [AB] providing cooldown. Efforts were in progress to place the 'B' RHR train in recirculation to sample and adjust boron concentrations prior to aligning the train to the RCS. Maintenance was performed to correct a packing leak and the Control Room Operators were stroking valve EJ HV-8716A (the 'A' RHR to Safety Injection System (SIS) Hot Leg Recirculation Loops 2 & 3 isolation valve) to seat the packing and to perform motor operated valve testing. When the Control Room operators stroked valve EJ HV-8716A, they noted a rapid drop in pressurizer level. They immediately diagnosed the problem and shut valve EJ HV-8716A. The root cause of this event was that Licensed Operators inappropriately allowed two incompatible evolutions to occur simultaneously. At the time of the event the 'B' RHR train was being lined up for RWST recirculation concurrent with the stroking of EJ HV-8716A. Corrective Actions include improved physical and administrative controls and additional operator training.
4821994014 | Wolf Creek | 11/02/1994 | 11/24/1997 | 9712010245 | <strong>Refueling Machine Technical Specification Limiting Condition for Operation Requirements Not Met in Past Outages</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1997, during review of an industry event involving Refueling Machine automatic overload cutoff settings, WCNOC personnel identified a historical violation of the Technical Specification Limiting Condition for Operation (LCO) requirements. FHP 03-001, "Refueling Machine Operating Instructions," did not ensure that the overload cutout or automatic load reduction trip would occur consistent with the LCO requirements. Although these requirements are not currently in the WCNOC Technical Specifications, this practice existed during the time the refueling machine requirements were in the WCNOC Technical Specifications (i.e., as late as 1994). Therefore, this LER is being written to document a historical violation of the WCNOC Technical Specifications. The cause of this event is an inadequate procedural controls that reflected the limitations of the refueling machine (even though bundle weight varied, the machine was only equipped with one or two groups of settings prior to 1996). Corrective actions completed in 1996 involved modifying the refueling machine and associated procedures, thereby allowing up to 6 groups of weight settings to be selected for loads to be handled. Additional process changes to ensure continued compliance with the refueling machine USAR requirements will be made.
4821994015 | Wolf Creek | 10/24/1994 | 10/15/1999 | ML99316003 | <strong>Technical Specification Surveillance Requirement Not Satisfied Prior to Entry into Mode 4</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1999, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel determined that in October of 1994, Wolf Creek Generating Station (WCGS) entered Mode 4 following the seventh refueling outage without satisfying a surveillance requirement. Technical Specification Surveillance Requirement 4.5.3.1 requires that one Emergency Core Cooling System (ECCS) subsystem be demonstrated operable per the applicable requirements of technical Specification Surveillance Requirement 4.5.2. The requirements of 4.5.2 include performing a flow balance test, during shutdown, following completion of modifications to the ECCE sub systems that alter the subsystem flow characteristics. The Reactor Coolant Pump Seal Injection throttle valves in this system had been replaced during the refueling outage. Mode 3 was also entered without satisfying the surveillance requirements. This is a historic event. The root cause of this event was a failure to verify the Technical Specification requirements of 3.5.2 and 3.5.3 with respect to plant conditions. Corrective actions for this event include: training operations crews and support staff Concerning this event, revising procedures STS BG-004 and STS EM-003A and the surveillance tracking program to address the requirements of Technical Specifications 4.5.2 and 4.5.3, and validating surveillance requirements to ensure they are properly tied to the applicable surveillance procedures. This event constitutes a reportable event in accordance with 10 CFR 50.73(a) (2) (i) (B). The safety significance of this event was minimal, because seal injection flow limit is not crucial at Mode 3 and Mode 4 conditions based on the operator actions assumed in the bounding analysis.
4831994001 | Callaway | 04/27/1994 | 05/16/1994 | 9405240144 | <strong>Tech Spec 3.5.1 Violation Due to High Pressure Alarm Condition on Two Safety Injection Accumulators Caused Tech Spec 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>At 1925 CDT on 4/27/94, the 'B' Safety Injection (SI) accumulator high pressure alarm annunciated. Technical Specification (T/S) 4.5.1.1 demonstrates the operability of each SI accumulator by verifying, by 'absence of alarms,' nitrogen cover pressure. The 'B' SI accumulator was declared inoperable and T/S 3.5.1 action (a) was entered. As the licensed reactor operator was preparing to vent the accumulator, the 'C' SI accumulator high pressure alarm annunciated at 1926. Because T/S 3.5.1 provides action only for one inoperable accumulator, T/S 3.0.3 was entered even though the actual pressure in both accumulators was lower than the high pressure of 648 psig specified in T/S 3.5.1. At 1927, the high pressure alarm on the 'C' SI accumulator was cleared. T/S 3.0.3 was exited. The plant was in Mode 1, Power Operations at 100 percent reactor power. <br /><br /> The high pressure in 'B' and 'C' SI accumulators is attributed to a gradual increase in ambient and containment temperature. Work on the 'B' train containment coolers contributed to the increase in containment temperature. <br /><br /> An operating license amendment was submitted, previous to this event, to change T/S 3/4.5.1 to remove the reliance on absence of alarms and allow the use of other means, such as installed instrumentation and main control board indications, to determine the operability of the SI accumulators.
4831994002 | Callaway | 07/08/1994 | 08/01/1994 | 9408050137 | <strong>Tech Spec 3.5.2 Violation and Subsequent Entry Into Tech Spec 3.0.3 Due to Leaking Boron Injection Tank Relief Valve EM8852</strong><br /><i>Abstract:&nbsp;</i>On 7/8/94 from 0918 CDT to 0928, both trains of the High Head Safety Injection System (HHSIS) were rendered inoperable in order to facilitate a modification to leaking Boron Injection Tank (BIT) relief valve EM8852. This was contrary to the requirements of Technical Specification (T/S) 3.5.2, therefore T/S 3.0.3 was entered at 0918 and exited at 0928. The plant was in Mode 1 at 94 % reactor power. <br /><br /> On 4/22/94, a utility equipment operator discovered a small trickle of water running from a tygon hose on the BIT surge tank to a floor drain. Utility engineers determined the source of this water was seat leakage past BIT relief valve EM8852. Utility engineers reviewed applicable code requirements for EM8852 and determined it was no longer required. On 6/15/94, EM8852 was gagged, however the leakage continued to increase. By 7/5/94, leakage had increased to approximately 0.69 gallons per minute. After approval by the plant On-Site Review Committee, EM8852 was replaced with a blank flange on 7/8/94. <br /><br /> Entry into T/S 3.0.3 was required to avoid a shutdown and cooldown transient that would be imposed on the plant by an unnecessary shutdown to Mode 4 conditions. Replacement of EM8852 with a blank flange eliminated the referenced 0.69 gpm leakage, thus maintaining containment bypass leakage into the Auxiliary Building within the 2 gpm plant Final Safety Analysis Report accident assumption.
4831994003 | Callaway | 07/08/1994 | 09/16/1994 | 9409220118 | <strong>Failure to Properly Perform Technical Specifications 4.3.3.6 and 4.4.6.1.a Due to Lack of Knowledge of a Commitment</strong><br /><i>Abstract:&nbsp;</i>On 6/2/94, a utility Quality Assurance (QA) engineer's surveillance of radiation monitors found that a 1989 utility engineering evaluation conflicted with the Final Safety Analysis Report's requirements for Regulatory Guide (RG) 1.97. RG 1.97 requires safety-related qualified equipment to be used for the Containment Area Radiation-High Range indicators. The evaluation mistakenly concluded the monitor channel was considered operable with it's safety-related indicator (RM-23) module inoperable provided the channel was monitored on the parallel non-safety- related RM-11 display.<br /><br /> Initial review of the 'PAMS CHANNEL CHECK' surveillance procedure by the QA engineer determined that a concern did not exist since it listed both RM-11 and RM-23. On 7/8/94, after the QA engineer questioned a licensed Reactor Operator, it was found that the operators were using only the RM-11. It was determined that the CHANNEL CHECK requirements of Technical Specification (T/S) 4.3.3.6 had not been met. The plant was in Mode 1 - 94% reactor power. <br /><br /> A similar concern was identified with the Containment Atmosphere Gas Detection indicators. RM-23s should have been used to meet RG 1.45 requirements and T/S 4.4.6.1.a. The plant was in Mode 1 - 100% reactor power. <br /><br /> Since receipt of the initial license on 6/11/84, utility personnel have not been aware that the safety-related display indication for these four (4) channels were to be only provided by the RM-23s and not the RM-11 displays. The engineering evaluation, work control database, and operation procedures have been revised to show the required use of the RM-23. Licensed personnel will review this event.
4831994004 | Callaway | 08/01/1994 | 08/31/1994 | 9409120316 | <strong>Failure to Properly Perform Surveillance of Tech Spec 4.11.2.6 on the Total Curie Content in 'E' Gas Decay Tank Due to a Cognitive Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On 8/15/94, the Radwaste Supervisor reviewing the Total Curie Content analysis result for the in-service 'E' Gas Decay Tank (GDT) taken that day, noted that the activity had steadily decreased over the last three weekly samples. Chemistry supervision was notified. On 8/16/94, a Chemistry Supervisor found that the three Chemistry technicians who had sampled the 'E' GDT on the sample dates had not opened HA-V-0109 (GDT Sample Header Bypass Throttle Valve) as required by the sampling procedure. Thus, Technical Specification surveillance 4.11.2.6, sampling of the in-service GDT, was improperly performed on 8/1/94, 8/8/94, and 8/15/94. The plant was in Mode 1 - Power Operations at 100% reactor power at the time of discovery. <br /><br /> A plant modification, performed in April 1992, changed the configuration of the GDT sample lines from requiring HA-V-0109 closed to open while taking a sample. A review of the GDT data was conducted back to the time of modification. Six additional sample surveillances were identified to be potentially in error due to their documented low activity levels. It is not possible to determine absolutely if these samples were correct due to the impact of variable plant conditions on the activity within the GDTs. <br /><br /> The root cause of this event is a cognitive human performance error. Corrective actions include: 1) counseling of the supervisors and technicians; 2) review of the event and appropriate sampling requirements by all Chemistry technicians; 3) moving the sole responsibility for the surveillance to Chemistry; 4) consolidating sample guidance into one procedure; and 5) evaluating the use of a device on the line to verify flow to the sample container.
4831994005 | Callaway | 08/20/1994 | 09/19/1994 | 9409260228 | <strong>Missed Tech Spec 4.3.3.6 Surveillance of the Thermocouple/Core Cooling Detection System Due to Inadequate Surveillance Procedures</strong><br /><i>Abstract:&nbsp;</i>On 8/20/94, licensed utility Reactor Operators were performing the monthly Technical Specification (T/S) 4.3.3.6 CHANNEL CHECK of the Thermocouple/Core Cooling Detection System when they discovered a discrepancy in the numbers taken from the Core Cooling Detection System printers versus known actual conditions. The plant was in Mode 1 at 100% reactor power at the time of event discovery. <br /><br /> A review by utility engineers indicated that incorrect T/S 4.3.3.6 surveillance data had been recorded on numerous occasions since 6/4/88. The printers would stop updating with current data if the Core Cooling Monitor was reset at the same time data was being sent from the processor to the printer. Surveillance procedure OSP-SH-00001, 'Post Accident Monitoring (PAM) CHANNEL CHECK', did not detail this fact. Upon discovery of this condition, both printers were reset and the surveillance was successfully performed on 8/23/94. <br /><br /> OSP-SH-00001 was revised to only allow the use of the calibrated Core Cooling Monitor local or remote display for meeting surveillance acceptance criteria until further detail can be added to clarify printer operation. Utility personnel reviewed other PAM instrumentation listed in T/S and associated surveillance procedures for compliance with T/S and Reg Guide 1.97. This event will be incorporated in utility licensed Operator requal training.
4831994006 | Callaway | 09/02/1993 | 02/04/1995 | 9502130215 | <strong>Missed Tech Spec 4.3.2.2 Surveillance of the Mechanical Turbine Trip Function and Subsequent Tech Spec 3.0.3 Entry Due to Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 9/2/93 at 2110 CDT, during routine Technical Specification (T/S) 4.3.4.2 Turbine Overspeed Protection (TORP) surveillance testing, the turbine electrical trip system failed its portion of the surveillance due to electrical trip solenoid valve CHFY0004A failing to actuate to the trip position. Subsequently, the mechanical turbine trip system was relied upon to fulfill the T/S 3/4.3.2, Table 3.3-3, Turbine Trip Engineered Safety Features Actuation System (ESFAS) function from 9/2/93 at 2110 CDT until 10/l/93 at 0201 CDT without having been response time tested in accordance with T/S 4.3.2.2. This event was due to cognitive personnel error and constituted an unintentional entry into T/S 3.0.3 during this time period. The plant was in Mode 1 at 100 % reactor power on 9/2/93. <br /><br /> On 12/8/94, during a review of a similar industry event, a utility engineer determined that the actual mechanical turbine trip response time had not been measured as required by T/S 3/4.3.2. <br /><br /> This event will be reviewed with pertinent utility personnel. requirements will be performed to ensure compliance. CHFY0004A was sent to General Electric for troubleshooting and refurbishment. No root cause of failure could be determined. A T/S change has been submitted to remove turbine trip response time testing requirements from T/S 3/4.3.2.
4981994001 | South Texas 1, South Texas 2 | 01/05/1994 | 02/07/1994 | 9402180160 | <strong>Small Gaps in the Reactor Containment Building Emergency Sumps Screens</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1994, Unit 1 was in Mode 5 at 0% power and Unit 2 was defueled while in a refueling outage. During an inspection of the emergency sumps in the Unit 1 Reactor Containment Building by the NRC Resident Inspectors, openings in the sump screen structures were found that exceeded the designed 1/4' diameter perforations. At each emergency sump screen the frame plate at the floor was warped creating a clearance up to approximately 5/8', and near the solid cover plate at each of the six angle iron supports, cut-out holes approximately 1.5' x 3.5' remained. Some additional gaps, larger than 1/4', were found in the area of the screen seams. Similar conditions were identified in Unit 2. The gaps remained from initial construction fabrication, welding and installation of the screen. The apparent cause of this event is the less than adequate attention to detail during the original design, fabrication, and installation, as well as various surveillance inspections subsequent to original construction. A plant change was issued providing the repair disposition and repairs were implemented. Engineering performed an assessment of the deficiencies and concluded there is no safety significance with regard to these deficiencies.
4981994002 | South Texas 1 | 01/15/1994 | 05/02/1994 | 9405090113 | <strong>Centrifugal Charging Pump 1A Discharge Bypass Valve Being Found in the Open Position Contrary to the Requirements of Technical Specification 3.1.2.3</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1994, at 1010 hours, Unit 1 was in Mode 5 at 0% power. Increased reactor coolant pump seal injection flow was identified following the start up of the Centrifugal Charging Pump 1A for testing. The pump was secured and subsequent investigation identified that the Centrifugal Charging Pump 1A discharge bypass valve (CV-MOV-8348) to the reactor coolant pump seal injection line hydro-pneumatically opened in violation of Technical Specification 3.1.2.3. The bypass valve opening was caused by a hydro-pneumatic transient that occurred when the Centrifugal Charging Pump 1A was started. The valve was manually closed. Corrective actions include performing a review to identify other valves that may be susceptible to this type of event, adding a caution to the equipment clearance order database for the affected valves and locally labeling all affected valves with a caution statement.
4981994003 | South Texas 1 | 01/24/1994 | 05/06/1994 | 9405120112 | <strong>Inoperable Tornado Damper</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1994, Houston Lighting & Power determined that a condition discovered on January 18, 1994 was reportable. On January 18, 1994, at approximately 1100 hours, with Unit 1 in Mode 5, Maintenance personnel discovered an interference between the plant exhaust vent tornado damper linkage and a gusset (ductwork structural stiffener). The damper consists of four sections, each of which has linkage that interconnects the individual damper blades. The gusset limited the closing travel of the damper linkage in the upper left section to approximately 40% of full stroke, thus preventing the section from closing. The cause of the condition was an undetected construction interference which was corrected by notching the gusset to allow free travel of the damper linkage.
4981994004 | South Texas 1, South Texas 2 | 01/19/1994 | 03/31/1994 | 9404050233 | <strong>Voluntary LER regarding Surveillance Testing of the Pressurizer Power Operated Relief Valves.</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1994, at 1700 hours, with Unit 1 in mode 5 and Unit 2 defueled while in a refueling outage, it was determined the surveillance performed to comply with Surveillance Requirement 4.4.4.1.b for Relief Valves needed to be enhanced because the pressurizer power operated relief valves were not tested from the Main Control Board. <br /><br /> Technical Specification testing requirements are captured in Surveillance Requirement 4.3.3.5.2 for the Remote Shutdown System and Surveillance Requirement 4.4.4.1 for relief valves. The requirements are addressed by performance of procedure 1(2)PSP03-RC-0010, Pressurizer Power Operated Relief Valve Operability Test. This is an 18 month cold shutdown test done in conformance with ASME Section XI and Technical Specification 4.0.5. It requires a stroke time test and remote verification. Historically the testing has been conducted only from the Auxiliary Shutdown Panel to meet both surveillance requirements. <br /><br /> Except for the Remote Shutdown System specification, the Technical Specifications do not specify from where the pressurizer power operated relief valves are to be tested, nor does the ASME Code. However, it is prudent to test the valves from both the Auxiliary Shutdown Panel and the Main Control Board. As part of the South Texas program to upgrade surveillance procedures, this requirement has been included.
4981994005 | South Texas 1, South Texas 2 | 02/01/1994 | 03/03/1994 | 9403110038 | <strong>Heating, Ventilating and Air Conditioning System Damper Battery Backup Failures</strong><br /><i>Abstract:&nbsp;</i>On February 1, 1994, Unit 1 was in Mode 5 at 0% power and Unit 2 was defueled while in a refueling outage. It was determined that the Unit 1 and Unit 2 Control Room Make-up and Fuel Handling Building Exhaust dampers were inoperable due to depleted lithium battery back-up power supplies. The cause of this event was the failure to understand that failure of the batteries affected the operability of the dampers and therefore should be covered in the Technical Specification Surveillance Program. A contributing cause was the failure to identify that the method of monitoring battery condition specified in the IEEE Qualification Test Report and subsequently, the vendor manual was not implemented in the as-built configuration of the plant. Immediate corrective actions were taken to replace the batteries and restore the Fuel Handling Building and Control Room Heating, Ventilating and Air Conditioning systems to operability. The Equipment Clearance Order database was modified to address the removal of the battery fuses as part of the Equipment Clearance Order process to prevent the cycling of the hydraulic system and subsequent depletion of the batteries. Additional corrective actions are addressed within the LER.
4981994006 | South Texas 1 | 02/14/1994 | 04/27/1994 | 9405090129 | <strong>Manual Reactor Trip Following Unanticipated Test Results.</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1994 at 0130 hours, Unit 1 was in Mode 3 at 0% power. Westinghouse Solid State Rod Control System post-modification testing was underway following the installation of a Westinghouse proposed modification to prevent uncontrolled asymmetric rod withdrawal. The reactor was manually tripped in accordance with the test procedure when unanticipated inward rod motion was observed. The cause of this event was a modification which failed post-modification testing. The test was terminated and the Solid State Rod Control System was returned to its original design configuration.
4981994007 | South Texas 1 | 02/24/1994 | 03/25/1994 | 9403300139 | <strong>Reactor Trip Bypass Breaker Testing Not in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1994 at 0930 hours, Unit 1 was in Mode 1 at 7% power when it was discovered that the station procedure for testing the Reactor Trip Bypass Breakers did not properly satisfy Technical Specification 4.3-1, item 22 which requires a test of the Bypass Breaker Local Manual Shunt Trip prior to placing the Bypass Breaker in service. The station procedure specified testing the Bypass Breaker after it had been racked in. Three other station procedures were identified with the same problem. These four procedures have been corrected. <br /><br /> The cause of this event was inadequate procedure preparation and review. The Technical Specification requirement was not properly incorporated into the procedure when it was written and reviewed. <br /><br /> Corrective actions include completion of the Surveillance Procedure Enhancement Program and development of a Basis Document for each procedure; establishing a 'Procedure Ownership Triangle' to ensure that procedures are administratively and technically correct and are capable of being performed as written; and evaluating the adequacy of the 10CFR50.59 safety evaluation training course as it pertains to procedure development and review.
4981994008 | South Texas 1 | 02/24/1994 | 03/28/1994 | 9404050169 | <strong>Failure to Stagger Reactor Trip Breaker Surveillance Test Intervals</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1994, Unit 1 was in Mode 1 at 7% power. While reviewing the performance history of the Solid State Protection System surveillance testing, it was determined that the reactor trip breaker surveillances associated with Technical Specifications 4.3.1 and 4.3.2 were not performed in accordance with Technical Specification requirements for staggered test intervals. This event occurred during the period in which the normal cyclic schedule was being re-established at the end of a long outage. The causes of this event were determined to be inadequate Surveillance Program (in that methods for assuring staggered intervals are restored following an outage and inadequate training of new Divisional Surveillance Coordinators. Corrective actions include conducting training for responsible surveillance coordinators with scheduling responsibilities for surveillances with Technical Specification stagger requirements and generating Conditional Surveillance Tasks in the Surveillance Task database for each division responsible for surveillance tasks subject to Technical Specification stagger requirements. These Conditional Surveillance Tasks will be required prior to increasing mode changes as appropriate.
4981994009 | South Texas 1 | 02/28/1994 | 06/23/1994 | 9406280301 | <strong>Manual Reactor Trip Due to Malfunctioning Main Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1994 at 2212 hours, Unit 1 was in Mode 1 at 29% power when a steam flow/feed flow mismatch alarm was received on Steam Generator ID. The reactor was manually tripped at 2213 hours following an unsuccessful attempt to take remote manual control of the ID Main Feedwater Regulating Valve. The malfunction of the 1D Main Feedwater Regulating Valve was caused by a failed transformer coil in the torque motor in the current to pneumatic convertor (Fisher Controls Type 546 Current to Pneumatic Converter). The root cause of the failed transformer coil has been attributed to a weak solder connection on one end of a wire which connects the two sets of transformer coils together in the torque motor section of the convertor. Corrective actions include performing failure analyses on the current to pneumatic convertor and the associated Westinghouse 7300 Series driver card which had failed and was replaced earlier. The failed current to pneumatic convertor was replaced as were two other Unit 1 current to pneumatic convertors.
4981994010 | South Texas 1, South Texas 2 | 07/19/1994 | 08/17/1994 | 9408250042 | <strong>Failure to Perform a Technical Specification Required Surveillance due to Inappropriate Use of the Equipment Clearance Order Process</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1994, at approximately 1630 hours, Unit 1 was in Mode 1 at 100% power. South Texas Project concluded that Unit 1 had failed to fully meet the surveillance requirements of Technical Specification 4.7.4, Essential Cooling Water System. It was determined that a formal surveillance requirement was not being performed on one essential cooling water system valve for each train, that was locked throttled per an Equipment Clearance Order. It was determined that the intent of the surveillance requirement is that 'locked, sealed, or otherwise secured in position' is to ensure a component is physically restrained from movement. An Equipment Clearance Order tag was being used to fulfill the requirement thus the valve was not fully restrained from movement. Immediate corrective actions included reviewing the current list of Technical Specification locked valves maintained in position by an Equipment Clearance Order, revising the Essential Cooling Water surveillance procedure to add throttle valves, which verifies the correct position per surveillance time interval. In addition, locking devices have been designed and installed on these valves.
4981994011 | South Texas 1 | 03/10/1994 | 04/18/1994 | 9404260278 | <strong>Inadvertent Actuation of the Safety Injection System During Performance of Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1994, Unit 1 was in Mode 5 at 0% power while in Mid-Loop operations. At approximately 1725 hours, while conducting a Logic Train S Functional Test, a Safety Injection actuation was received on trains A, B, and C. The following causes have been identified for this event: <br /><br /> o Inconsistent application of established management controls; <br /> o Failure to meet known management expectations; <br /> o Test performer performance lapses; and <br /> o Component malfunction. <br /><br /> Corrective actions and actions taken in response to the component malfunction are discussed within the text of this Licensee Event Report.
4981994012 | South Texas 1 | 03/11/1994 | 04/07/1994 | 9404120227 | <strong>Failure to Meet the Requirements of Technical Specification due to Standby Diesel Generator # 11 Being Technically Inoperable as a result of an Intermittent Failure of the K1 Contactor for the Voltage Regulator/Field Flash Circuit</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1994, Unit 1 was in Mode 5 at 0% power. At approximately 1000 hours, it was determined that the valid failures which had occurred on Standby Diesel Generator 11 on February 3, 1994 and March 1, 1994 were due to the same cause. In both cases, the Standby Diesel Generator failed to develop rated voltage upon starting. The cause of the valid failures was an intermittent failure of the Kl contactor for the Voltage Regulator/Field Flash circuit. Therefore, Standby Diesel Generator 11 was technically inoperable since February 3, 1994, resulting in a failure to meet the requirements of Technical Specifications. Corrective actions include: replacing the voltage release relays (VR1/2) in the voltage regulator circuits and the K1 contactor of Standby Diesel Generator 11, developing preventive maintenance activities for the Field Flash circuit, enhancing the existing preventive maintenance activities on the K1 contactor, and performing an independent assessment of the control panel installation by a qualified vendor.
4981994013 | South Texas 1, South Texas 2 | 08/04/1994 | 10/05/1994 | 9410120231 | <strong>Failure to Fully Meet the Requirements of the Station Blackout Rule</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1994, both Unit 1 and Unit 2 were in Mode 1 at 100% power. At approximately 0950 hours, a reportability review was concluded which determined that the Nuclear Regulatory Commission should be informed of a condition where the South Texas Project Units were not fully meeting the requirements of NUMARC 87-00 which implements 10CFR50.63, Station Blackout. <br /><br /> A self-assessment of the South Texas Project Station Blackout commitments identified two cases of the NUMARC 87-00, criterion not being satisfied. The criterion relate to the physical protection and electrical vulnerabilities of Alternate AC (AAC) power sources used for Station Blackout. Although a Standby Diesel Generator (Train B) is used at South Texas Project for providing electric power, the power distribution equipment used to transfer the power to the companion train instrumentation (A or C train) was not protected from likely weather- related events (high winds for the Gulf Coast) and was a single point of vulnerability for preferred, and Station Blackout (AAC) power. A change to the Severe Weather Guidelines was made the same day, to provide for plant shutdown prior to any predicted hurricane landfall, rather than prior to hurricane winds in excess of 120 mph. In addition, a Justification for Continued Operation was developed which shifted the Station Blackout shutdown strategy from reliance on the power transfer equipment in question to reliance on station batteries, consistent with NUMARC 87-00 in the unlikely event of loss of the power transfer capability. Subsequent to the initial findings, three additional issues were identified which were also bounded by the Justification for Continued Operation. As the self-assessment progresses, this report will be revised, if necessary, to ensure the Nuclear Regulatory Commission is fully informed of any additional issues.
4981994014 | South Texas 1, South Texas 2 | 08/10/1994 | 03/14/1995 | 9503200304 | <strong>Failure to Meet the requirements of Technical Specifications Due To a Failure To Perform an ASME Section XI Test on the Standby Diesel Generator Starting Air Receiver Inlet Check Valves</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1994, Unit 1 and Unit 2 were in Mode 1 at 100% power. At approximately 1645 hours, it was determined that the Standby Diesel Generator starting air receiver inlet check valves were not being surveillance tested in accordance with the requirements of American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code Section XI and Technical Specification 4.0.5. Unit 1 and Unit 2 entered Technical Specification 3.8.1.1.f at 1645 hours, and all six Standby Diesel Generators were declared technically inoperable. Technical Specification 4.0.3 was immediately invoked permitting up to a 24 hour delay to permit the completion of the missed surveillance. The valves were subsequently, checked to ensure that the valves were, in fact, functional. The cause of the event was determined to be an inadequate review of the function of the Standby Diesel Generator starting air receiver inlet check valves when the Inservice Test Program was initially developed. Corrective actions include testing all twelve diesel starting air receiver inlet check valves, developing a permanent test procedure for the subject valves and supplementing the Unit 1 and Unit 2 Pump and Valves Inservice Test Plans. In addition a comprehensive review of the Inservice Test Program will be performed to develop an Inservice Test Bases Document.
4981994015 | South Texas 1 | 09/20/1994 | 11/17/1994 | 9411250216 | <strong>Reactor Trip and Turbine Trip due to Low-Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1994, Unit 1 was in Mode 1 at 100% power. At 0105 hours, Unit 1 received an automatic reactor/turbine trip due to Steam Generator 1C low-low level. Immediately prior to the unit trip, efforts were in progress to reduce Reactor Power and Turbine Load following the unanticipated trip of the #13 Steam Generator Feedwater Pump. The cause of this event was that management expectations, procedural guidance, training, and personnel experience placed initial emphasis on expected plant response rather than actual plant conditions. This event was initiated when Steam Generator Feedwater Pump tripped on overspeed due to a failed speed feedback device (Tachometer Pack) in the speed control circuits. Contributing causes were determined to be inadequate communications and the Start-up Feedwater Pump recirculation valve not closing due to a coarse gain misadjustment on the flow controller card in the Miscellaneous Analog Cabinet and internal damage on the valve. Corrective actions include discussing managements expectations regarding the use of all indications for proper equipment operations and crew communications with the involved crew, revising the off-normal procedure, replacing a failed speed sensor, ensuring proper operation of the Start-up Feedwater Pump Recirculation Valve, developing a scenario similar to this event for the simulator and including this event in Operators lessons-learned training.
4981994016 | South Texas 1 | 09/23/1994 | 10/24/1994 | 9411010199 | <strong>Failure to Fully Meet the Requirements of Technical Specifications due to Not Placing the Control Room Envelope Heating, Ventilation and Air Conditioning System in the Required Mode</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1994, Unit 1 was in Mode 1 at 98% power. At 1125 hours, it was discovered that Toxic Gas Analyzer XE-9326 was operating with its multiplier voltage switched off (computer controlled switch), rendering it incapable of detecting toxic gas concentrations as required by Technical Specification 3.3.3.7. Upon review of archival information, it was determined that Toxic Gas Analyzer XE-9326 had been inoperable since 1450 hours on September 22, 1994. Similarly, on September 28, 1994, at 0957 hours, while troubleshooting Toxic Gas Analyzer XE-9326, it was discovered that Toxic Gas Analyzer XE-9327 was also inoperable. Subsequent review of archival computer data revealed that Toxic Gas Analyzer XE-9327 had become incapable of detecting toxic gas concentration at approximately 0300 hours. In these instances, the requirements of Technical Specification 3.3.3.7 were not met since the Control Room Envelope Heating, Ventilation and Air Conditioning system was not placed in toxic gas recirculation within one hour. The root cause of these events is an inadequate design of the toxic gas analyzers which did not support annunciating specific failure mechanisms. Corrective actions include troubleshooting and repairing the toxic gas analyzers, and implementing a modification to provide an alarm function in the Control Room for failures of toxic gas analyzers due to the indication dropping below the lower limits of the analyzers.
4981994017 | South Texas 1, South Texas 2 | 10/11/1994 | 02/17/1995 | 9502280083 | <strong>Gaseous Effluent Monitor Setpoints Not Calculated in Accordance with the Offsite Dose Calculation Manual</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1994, Unit 1 and Unit 2 were both in Mode 1 at 100% power. During a routine Quality Assurance Audit, the alarm setpoints for the Unit Vent Noble Gas Activity Monitors were evaluated using the Offsite Dose Calculation Manual. The evaluation showed that the gaseous effluent monitor setpoints had not been calculated in accordance with the Offsite Dose Calculation Manual calculational methodology. that the actual setpoint had not been recalculated as a result of revisions to the Offsite Dose Calculation Manual. Two revisions to the Offsite Dose Calculation Manual were made during January 1989 through January 1994, which changed the effluent monitor setpoint calculation methodology but never resulted in a change to the actual setpoint. The cause of this event was a failure to revise related change documents. A contributing cause was inadequate management follow-up. Corrective actions include verifying the Unit 1 and Unit 2 gaseous effluent monitors were operable with the current alarm setpoints.<br /><br /> In addition, the procedure which governs changes to the Offsite Dose Calculation Manual has been revised to ensure that management follow-up action is taken when the effluent monitor setpoint calculational methodology has been revised, utilizing the Corrective Action Program.
4981994018 | South Texas 1, South Texas 2 | 11/02/1994 | 11/30/1994 | 9412050239 | <strong>Failure to Fully Meet the Requirements of Technical Specifications Regarding the Control Room Envelope Heating, Ventilation and Air Conditioning System Boundary</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1994 Unit 1 and Unit 2 were in Mode 1 at 100 % power. At 1653 hours, Unit 1 and Unit 2 entered Technical Specification 3.0.3 when it was discovered that some areas of the Control Room Envelope Heating, Ventilation and Air Conditioning system of Unit 1 would not maintain the required 0.125 inches water gauge positive pressure relative to adjacent areas, as required by Technical Specification 4.7.7.e.3. For this reason, the Technical Specification surveillance was determined to be inadequate due to not testing area besides the Main Control Room within the Control Room Envelope, to ensure compliance with the surveillance requirements of Technical Specification 4.7.7.e.3. <br /><br /> Immediate corrective actions included the development of an detailed testing method and re-establishing appropriate Control Room Envelope air flows and pressures.
4981994019 | South Texas 1, South Texas 2 | 11/09/1994 | 04/14/1997 | 9704230256 | <strong>Failure to fully meet the requirements of Technical Specifications for time response testing of the Reactor Containment Fan Cooler; and Control Room Envelope Heating, Ventilation and Air Conditioning Systems.</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1994, Unit 1 and Unit 2 were in Mode 1 at 100% power. It was determined that time response testing of the Reactor Containment Fan Cooler, Control Room Envelope and Fuel Handling Building Heating, Ventilation and Air Conditioning systems was not fully adequate for the 18 month surveillance test procedure. Both Units entered Technical Specification 3.0.3. Subsequently, Technical Specification 4.0.3 was invoked to delay the action requirements of Technical Specification 3.0.5 for 24 hours in order to permit completion of the surveillance. The cause of the event was less than adequate preparation, review, and revision of the safety Injection Actuation and Response Time Test surveillance procedure. The calculation which supports the Updated Final Safety Analysis Report table, was not correctly applied in the development of the procedure. The following corrective actions have been taken as a result of this event. <br /><br /> Spin-up times were obtained for the affected fans of both Units using motor current decay measurements. This time was added to the previously performed procedure times to breaker closure and verified to be conservative to the Technical Specification required values for overall requirements. The Safety Injection Actuation and Response Time Test surveillance procedure was revised to include spin-up time for Reactor Containment Fan Coolers, Control Room Envelope and Fuel Handling Building Heating Ventilation and Air Conditioning systems. A comprehensive review of the accident calculations for the Fuel Handling Building Heating, Ventilation and Air Conditioning system determined the only time response for meeting the accident analysis is the ventilation system bypass dampers shutting within a specified time after a radiological release reaches the sample point inlet. Surveillance procedures were again revised to remove spin-up time measurement for the Fuel Handling Building Main Exhaust or Booster fans.
4981994020 | South Texas 1, South Texas 2 | 12/09/1994 | 01/09/1995 | 9501190282 | <strong>Failure to Fully Meet the Requirements of Technical Specifications Due to an Inadequate Surveillance for the Adjustable Molded Case Circuit Breakers</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1994, Units 1 and 2 were both in Mode 1 at 100% power. At approximately 1300 hours, a concern was raised by a Nuclear Regulatory Commission Inspector that the South Texas Project had misapplied the surveillance test tolerance for the 480 VAC 'adjustable magnetic' molded case circuit breakers which are used for containment penetration protection per Technical Specification 4.8.4.1.a.2. A data review of the previous surveillance test packages for the one hundred ninety-four potentially impacted circuit breakers determined that a combined total of sixty-six breakers were potentially out of tolerance. Thirty-four breakers in Unit 1 and thirty-two breakers in Unit 2 were declared 'inoperable' pending the satisfactory completion of the surveillance test for each. The event was caused by misinterpretation of the acceptance criteria, Corrective actions include revising the Molded Case Circuit Breaker Tests procedure and testing the sixty-six breakers in question against this revised criteria.
4991994001 | South Texas 2 | 03/01/1994 | 03/31/1994 | 9404050222 | <strong>Inadvertent Start of Standby Diesel Generator No. 21</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1994, Unit 2 was defueled while in a refueling outage. At 0155 hours Standby Diesel Generator 21 experienced an inadvertent start. The Standby Diesel Generator was secured but experienced a second start signal during the cooldown cycle. The control room then performed an emergency stop by placing controls in 'Pull-to-Lock'. The inadvertent start was caused by electrical component failures in the test circuit which permitted a start signal to be transmitted. Defective parts were identified and replaced and the Preventive Maintenance programs will be modified to address periodic replacement of these components. Standby Diesel Generator 21 was successfully tested and returned to service.
4991994002 | South Texas 2 | 03/02/1994 | 06/22/1994 | 9406290052 | <strong>Standby Diesel Generator 22 Piston Failure</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1994 Unit 2 was defueled in a refueling outage. Standby Diesel Generator 22 was classified as inoperable due to an ongoing 18 month surveillance inspection. Piston 4R was discovered to be damaged during this inspection. As a result an additional comprehensive inspection plan of each piston and cylinder liner was implemented and reviews of previous inspection videotapes for the other Standby Diesel Generators was conducted. These reviews determined that the conditions that existed in Standby Diesel Generator 22 were not present in the other Diesels. Extensive investigations, utilizing the Vendor (Cooper- Bessemer) and other consultants and metallurgical laboratories, determined the probable cause of the damaged piston was the introduction of foreign material into the cylinder. This introduction of foreign material caused increased friction and a loss of lubrication, increasing the dynamic stresses within the piston structure that resulted in the cracking. The engine was reassembled and an extended testing plan was successfully completed.
4991994003 | South Texas 2, South Texas 1 | 04/29/1994 | 05/31/1994 | 9406070057 | <strong>Inadvertent Test Mode Start of Standby Diesel Generators Unit 2: #21, and #22 and Unit 1: #13 due to Fiber-Optic Board Susceptibility to Noise in Conjunction with Transient DC Spikes</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1994, Unit 2 was in Mode 5 following a refueling outage. At 0202 hours, Unit 2 Standby Diesel Generator 21 experienced an inadvertent test mode start while in the Standby Mode. The start signal was received from the circuitry associated with the test mode which is automatically bypassed during emergency start. The start was not concurrent with any other plant activity or evolution. Similarly, on May 12, 1994, while Unit 1 was in Mode 1 at 100% power, Standby Diesel Generator 13 inadvertently started while in the test mode due to unknown reasons. Additionally, on May 15, 1994, while Unit 2 was in Mode 3, Standby Diesel Generator 22 inadvertently started while in the test mode for no apparent reason. The cause of the inadvertent test mode starts of Standby Diesel Generators 21, 22, and 13 has been determined to be the fiber-optic boards' susceptibility to noise in conjunction with transient DC spikes. A modification was installed in the DC distribution panel which supplies the Standby Diesel Generator 21 control panel, to attenuate the level of DC noise and spikes. An additional modification was installed on Standby Diesel Generator 21 to specific diesel control circuit relays to dampen the inductive responses of these relays to DC power disturbances. These modifications have been installed on the Unit 2 Standby Diesel Generators and will be installed on the Unit 1 Standby Diesel Generators during scheduled train outages.
4991994004 | South Texas 2 | 05/12/1994 | 06/13/1994 | 9406200265 | <strong>Engineered Safety Features Actuation due to Filling a Steam Generator to Approximately 90% Full</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1994 at 2210 hours, Unit 2 was in Mode 4 at 0% power. A Steam Generator Hi-Hi Level (P-14) signal was generated while performing Resistance Temperature Detector cross calibrations. Steam Generator levels were being maintained between 70% and 80% in accordance with the controlling procedure using Auxiliary Feedwater. Inadvertently, the P-14 setpoint was reached, actuating a P-14 signal. Because Main Feedwater was not in service and the main turbine was not on line, components actuated by a P-14 signal were already in their actuated condition, thus no components changed status. The cause of this event was inadequate control board awareness and turnover communications. Corrective actions included crew briefings, sitewide distribution of lessons learned and constructive discipline of involved personnel.
4991994005 | South Texas 2, South Texas 1 | 06/07/1994 | 07/19/1995 | 9509070007 | <strong>Inadvertent Test-Mode Starts of Standby Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On June 7, 1994, Unit 2 was in Mode 1 at 35% power. Standby Diesel Generator 22 had satisfactorily completed the monthly Standby Diesel Generator Operability test, been unloaded, and been placed in cooldown. Approximately three minutes into the cooldown cycle, the Standby Diesel Generator trouble alarm annunciated and generator voltage and frequency returned to normal operating parameters. Standby Diesel Generator 22 had received an unexpected test-mode start signal. Standby Diesel Generator 22 on July 25, 1994. Also, on August 1, 1994, Unit 1 Standby Diesel Generator 13, received a spurious test-mode start signal that resulted in a start of a portion of the Standby Diesel Generator auxiliaries with no actual start of the Standby Diesel Generator. Four additional test-mode starts occurred on May 4 and May 7 (Standby Diesel Generators 21 and 22, respectively) and May 18 (Standby Diesel Generators 13 and 22). An additional test-mode start occurred on August 1, 1995 on Standby Diesel Generator 21. This last failure involved a hard rather than intermittent failure of the D fiber optic board. As a result, the engine was kept in operation until plant conditions allowed securing the engine for entry into a Limiting Condition for Operation to affect repairs. Inadvertent test-mode starts would not prevent any of the Standby Diesel Generators from performing their safety function. Corrective actions include: installation of noise suppression devices to reduce the susceptibility of inadvertent starts due to electronic noise; replacement of fiber optic boards; and physical separation of AC and DC cables on safety class and non-safety class circuits, and installing a key-lock switch for each Standby Diesel Generator. In addition, fiber optic board performance will be pursued with the vendor.
4991994006 | South Texas 2, South Texas 1 | 06/22/1994 | 07/21/1994 | 9407260202 | <strong>Failure to Fully Meet the Requirements of Technical Specification Due to an Inadequate Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1994, at 1610 hours, Unit 2 was in Mode 1 at 100% power. It was determined that an event that was identified on June 21, 1994 at 0530 hours, was reportable. During performance of the monthly surveillance test (channel check) for Accident Monitoring Instrumentation, the Containment secondary sump level indicator was declared inoperable and the action statement was entered. During subsequent investigation as to the cause of the inoperable level indicator, it was discovered that the power supply breaker for the instrument was open. Further investigation revealed that the breaker had most probably been open since March 16, 1994. Unit 2 entered Mode 3, the applicable mode for Accident Monitoring, on May 16, 1994. <br /><br /> On July 11, 1994 at 1600 hours, both Units 1 and 2 were in Mode 1 at 100% power. During the follow-up review of the June 21 event it was discovered that a surveillance procedure used to verify operability of Accident Monitoring Instrumentation and Remote Shutdown Monitoring Instrumentation was inadequate in that it did not ensure operability of selected channels. This condition has existed since initial fuel load. <br /><br /> The cause of these events was an inadequate surveillance procedure. Surveillance procedures are used to satisfy Technical Specifications to ensure that the required equipment is operable. This procedure did not provide adequate guidance to allow detection of inoperable channels. Corrective actions are described within the Licensee Event Report.
4991994007 | South Texas 2 | 06/25/1994 | 08/01/1994 | 9408100284 | <strong>Turbine Trip and Reactor Trip Due to Main Transformer Lockout</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1994, Unit 2 was in Mode 1 at 47% power. At 1715 hours, a Main Transformer Lockout Relay actuated. This tripped the Main Turbine, the Generator output breaker, the breakers for all four 13.8 kV auxiliary buses and two switchyard breakers. This caused a loss of power to all Unit 2 auxiliary power busses which resulted in a loss of all Reactor Coolant Pumps and a reactor trip on Reactor Coolant Pump undervoltage at 1715 hours. The plant was stabilized in Mode 3. The cause of the trip was the failure of a capacitor within the pilot wire relay. Corrective actions are described within the Licensee Event Report.
5281994001 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/07/1994 | 08/19/1994 | 9409090217 | <strong>Surveillance Requirement 4.8.4.1 Not Fully Met</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1994, Palo Verde Units 1 and 2 were in Mode 1 (POWER OPERATION) at approximately 86 percent power and Unit 3 was in its 4th refueling outage with the core off loaded to the spent fuel pool when APS Maintenance Standards personnel determined that surveillance testing of the containment penetration conductor overcurrent protective devices (molded case circuit breakers) did not fully comply with Technical Specification Surveillance Requirement (TS SR) 4.8.4.1. This surveillance requires a sample of 'at least 10 percent' be tested for each breaker type. Additional breakers were satisfactorily tested in Units 1 and 2 to meet the TS SR. Test packages for Unit 3 (currently in an outage) were reviewed and additional breakers were added, as needed, to meet the 'at least 10 percent' sampling requirement. Test procedures will be changed to assure future breaker test sample sizes meet 'at least 10 percent' TS SR. <br /><br /> The most recent LER on incorrect surveillance test sample size is 528/93-007-00.
5281994002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/22/1994 | 10/28/1994 | 9411090398 | <strong>Technical Specification Limiting for Operation not Supported by Safety Analysis</strong><br /><i>Abstract:&nbsp;</i>At approximately 1300 MST on April 22, 1994, Palo Verde Units 1 and 2 were in Mode 1 (POWER OPERATIONS) and Unit 3 was in a refueling outage with the core off loaded to the spent fuel pool when APS Nuclear Fuel Management personnel determined that Technical Specifications (TS) 3.1.1.1, 3.3.1, and 3.9.1 Limiting Conditions for Operation (LCO) may not ensure that plant operation is maintained within the assumptions used in the associated safety analysis as required by 10CFR50.36. On June 7, 1994, while continuing to investigate the original condition, TS Table 4.3-1 was identified as having a similar condition On September 6, 1994, APS NFM personnel identified that the current operating procedure for exercising Control Element Assemblies (CEA) in Modes 3, 4, and 5, could allow conditions which violate assumptions used in the subcritical CEA bank withdrawal analysis. Administrative controls were implemented or verified in place while potential changes to analysis methodologies or amendments to TS are identified and reviewed. <br /><br /> There have been no previous similar events.
5281994003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/21/1994 | 06/07/1994 | 9406150118 | <strong>Raychem Heat Shrinkable 5kV Motor Splice Kit Installation Instructions Inadequate</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1994, at approximately 1200 MST, Palo Verde Units 1 and 2 were in Mode 1 (POWER OPERATION) operating at approximately 86 percent power and Palo Verde Unit 3 was in its third refueling outage with the core offloaded to the spent fuel pool when APS engineering personnel determined that the Raychem heat shrinkable high voltage (i.e., 5 kV) motor splice kit installation instructions do not ensure that the ribbon adhesive will thoroughly melt with each application, potentially impacting a uniform moisture seal. A moisture seal is required to meet PVNGS harsh environment equipment qualification requirements for Class 1E 4.16 kV motor terminal connections potentially exposed to high energy line break (HELB) accident conditions. electrically insulate both Class and non-Class 1E 4.16 kV non-HELB environment motor terminal connections. APS engineering personnel determined that the terminal connections were properly sealed for electrical insulation purposes. <br /><br /> An investigation determined that the Raychem splice kit installation documentation is inadequate in that the method prescribed does not ensure a proper seal in order to prevent moisture intrusion. Units 1, 2, and 3's Class 1E 4.16 kV motor terminal connections potentially exposed to HELB accident conditions were inspected and reheated if the adhesive ribbon for the moisture seal could not be visually verified to be fully melted. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5281994004 | Palo Verde 1 | 05/10/1994 | 06/09/1994 | 9406210370 | <strong>Control Room Isolation Damper Not Reconnected Following Preventive Maintenance</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1994, at approximately 1230 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 86 percent power when a HVAC Technician, during the performance of a preventive maintenance task, discovered that the actuator linkage was not connected to the Control Room Essential Air Handling Unit (AHU) Outside Air Intake Damper (HJB-M03). In this condition, damper HJB-M03 would not close from the remote shutdown panel, and therefore, was inoperable. Technical Specification 3.3.3.5, Table 3.3-9B requires HJB-M03 to be operable. <br /><br /> The apparent cause is personnel error when the equipment was not restored to its correct configuration during the performance of preventive maintenance on February 15, 1994. Additionally, further evaluation revealed that retest instructions were not adequate in assuring restoration of the linkage configuration. <br /><br /> As immediate corrective action, the actuator was stroked, the linkage was reconnected, the PM and retest were completed, and the damper was declared operable. The preventive maintenance task was revised. <br /><br /> There have been no previous similar events reported pursuant to 10 CFR 50.73.
5281994005 | Palo Verde 1 | 06/19/1994 | 06/28/1995 | 9507100215 | <strong>Core Protection Calculator, Delta-T Power Fluctuations</strong><br /><i>Abstract:&nbsp;</i>At approximately 2258 MST on June 19, 1994, Control Room personnel determined that the Core Protection Calculator (CPC) Channel D, Delta-T Power signal could no longer be adjusted to within +/- 2 percent of actual power as determined by secondary plant calorimetric and required by Technical Specification (TS) 3.3.1, Table 4.3-1, Notation (2). CPC Channel D was declared inoperable. This condition was caused by loop 2 Hot leg temperature (T-h) Resistance Temperature Detector (RTD) fluctuations. Fluctuations in T-h RTDs have been identified at other plants and attributed to temperature stratification. On June 29, 1994, after reviewing plant logs, the condition was determined to be reportable. The loop 2 (T-h) Resistance Temperature Detector (RTD) creating the Delta-T power fluctuations was electronically switched with the T-h RTD used in the Core Operating Limits Supervisory System. At approximately 1812 MST on July 2, 1994, CPC Channel D was calibrated and declared OPERABLE. The event did not adversely affect safe operation of the plant. <br /><br /> No previous similar events have been reported pursuant to 10CFR50.73.
5281994006 | Palo Verde 1 | 10/21/1994 | 06/28/1995 | 9507100218 | <strong>Spray Pond Pump Flow Greater than Design Basis Calculation</strong><br /><i>Abstract:&nbsp;</i>At approximately 1305 MST on October 21, 1994, Palo Verde Unit 1 was in Mode 1 (POWER OPERATIONS), when it was identified by Design Engineering personnel (utility, non-licensed) that the actual flow rates on the Unit 1 Spray Pond (SP) pumps may be exceeding design flow rates. This increased flow rate is due to oversized orifices in the Unit 1 SP return lines. The increased flow rate causes higher water losses from the spray ponds. Therefore, inventory may be depleted faster than the design analysis. <br /><br /> Unit 1 has established administrative controls to counter this condition until the correct orifices are installed. The work is being scheduled for the next refueling outage (1R5) in April, 1995. Also, pending Technical Specification (TS) and Updated Final Safety Analysis Report (UFSAR) amendments to reduce the SP inventory from 27 to 26 days may permit lifting some of the administrative controls or provide additional margin. <br /><br /> There have been no previously similar events reported pursuant to 10CFR50.73. <br /><br /> The purpose of this supplement is solely for the inclusion of EIIS codes, updating the status of corrective actions and correction of minor typographical errors
5281994007 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 11/03/1994 | 06/28/1995 | 9507100221 | <strong>Surveillance Requirement Missed for Containment Purge Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1994, at approximately 1030 MST, Palo Verde Units 1, 2, and 3 were in Mode 1 (POWER OPERATIONS), when it was identified by APS Design Engineering personnel that the thermal overload protection for the Containment Purge Refueling Isolation Valves was not being tested in accordance with Technical Specification Surveillance Requirements (TS SR) 4.8.4.2.1. TS SR 4.8.4.2.1 requires that the thermal overload protection shall be verified to be bypassed continuously or under accident conditions. These valves are to be tested at least once per 18 months, and following maintenance on the motor starter. <br /><br /> On November 17, 1994, this condition was confirmed by APS System Electrical/I&C Engineering. The procedures used to test the thermal overload bypasses did not adequately test the parallel path (Containment Purge Isolation Actuation Signal, CPIAS). Therefore, TS SR 4.8.4.2.1 has been missed since October 18, 1987, Unit 1's first refueling outage. reportable. <br /><br /> These valves are closed and de-energized in Modes 1 thru 4, therefore, they are performing their intended containment isolation function when in these modes. Administrative controls have been established to ensure that all three units do not enter plant conditions where these valves are needed until the complete circuitry has been tested and demonstrated to be operable. <br /><br /> There have been no previously similar events reported pursuant to 10 CFR 50.73 in the last three years. <br /><br /> This supplement is solely for the inclusion of EIIS codes, to update corrective actions, and the correction of minor typographical errors.
5281994008 | Palo Verde 1 | 11/26/1994 | 12/23/1994 | 9505190265 | <strong>Technical Specification Required Plant Shutdown to Repair Leaking Pressurizer Vent Path Valves</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1994, at approximately 2200 MST, Unit 1 control room personnel elected to voluntarily enter Technical Specification Limiting condition for Operation (TS LCO) 3.4.10, Action (A) to isolate and repair the pressurizer vent valves (RCA-HV-103 and RCB-HV-105) which were exhibiting symptoms of abnormal valve position indication and seat leakage. <br /><br /> On November 26, 1994, at approximately 0103 MST, Palo Verde Unit 1 was in Mode 1 (Power operation) operating at approximately 98 percent power when control room personnel commenced a controlled reactor shutdown to comply with TS LCO 3.4.10, action (A). At 0440 MST, the reactor was manually tripped from 19 percent reactor power in accordance with approved procedures and the plant was stabilitized in Mode 3 (Hot standby) by approximately 0538 MST. Control room personnel continued the reactor coolant system (RCS) cooldown and entered Mode 4 (hot shutdown) at 1400 MST on November 26, 1994. The plant shutdown and cooldown to Mode 4 were uncomplicated. <br /><br /> There have been no previous similar events reported pursuant to 10 CFR 50.73 in the last three years.
5281994009 | Palo Verde 1 | 11/18/1994 | 06/28/1995 | 9507100223 | <strong>Letdown Isolation Valve Leakage Impact On Appendix R Requirements</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1994, at approximately 1245 MST, Control Room personnel determined that letdown isolation valve 1JCHBUV0515 could not satisfy its 10CFR50 Appendix R related requirement to isolate letdown flow from the remote shutdown panel in the event of a Control Room fire, with an existing leakage of 40 gallons per minute (gpm). The valve leakage was first identified on December 8, 1992, but plant personnel overlooked the 10CFR50 Appendix R related requirement of the valve until noted by the NRC resident inspectors. <br /><br /> During the evaluation of this event it was determined that plant personnel also overlooked an applicable Technical Specification Interpretation (TSI) for the Remote Shutdown System. This TSI requires the components associated with the remote shutdown control circuits to be OPERABLE to meet the bases of Technical Specification 3.3.3.5. <br /><br /> Procedure changes were implemented which eliminated the reliance on 1JCHBUV0515 during remote shutdowns. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 in the last three years.
5281994010 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/09/1993 | 06/28/1995 | 9507100226 | <strong>Misalignment of Limitorque Torque Switch Contact Bar Prevented Remote Operation of MOVs</strong><br /><i>Abstract:&nbsp;</i>At approximately 1900 MST on April 9, 1993, Palo Verde Unit 2 was DEFUELED, when it was identified by Valve Services personnel that the close torque switch contact bar for Shutdown Cooling suction isolation valve 2JSIAUV0655, was misaligned. The evaluation at the time determined the misalignment of the close torque switch contact bar to be an isolated incident. <br /><br /> Similar events happened on January 27, 1994 (Unit 1), and June 7, 1994 (Unit 3). Based upon further evaluation, the above events were determined to have a common-mode failure. On January 10, 1995, the above events were determined to be reportable per 10CFR 50.73. <br /><br /> There have been no previously similar events reported pursuant to 10CFR 50.73. <br /><br /> The purpose of this supplement is solely for the inclusion of the appropriate EIIS codes and the correction of minor typographical errors.
5291994001 | Palo Verde 2 | 05/13/1994 | 06/08/1994 | 9406150194 | <strong>Emergency Diesel Generator and attendant equipment inoperable for greater than 72 hours</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1994, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) when members of the Plant Review Board determined that Unit 2's Emergency Diesel Generator 'B' (EDG-B) had been inoperable from approximately 0448 MST on May 10, 1994 to approximately 0855 MST on May 13, 1994. For approximately 76 hours and 7 minutes, the Train B Diesel Generator Building essential exhaust fan had been removed from service (i.e., breaker in the open position) with the fan's discharge damper wired in the closed position and had not been capable of performing its specified support function. The essential exhaust fan is necessary attendant equipment that is required for the EDG to perform its intended safety function. Therefore, EDG-B was inoperable and a condition prohibited by TS occurred when the unit did not comply with TS Limiting Condition for Operation (LCO) 3.8.1.1 ACTION b (i.e., restore the EDG to OPERABLE status within 72 hours). EDG-A remained operable during this event and was verified to be operable at approximately 1146 MST on May 13, 1994. <br /><br /> Although Operations personnel had reasonable expectation that the essential exhaust fan could be reenergized and manually started and that EDG-B was operable, Operations personnel failed to consider the essential exhaust fan as necessary attendant equipment that is required for the EDG to perform its intended safety function. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291994002 | Palo Verde 2 | 05/28/1994 | 06/23/1994 | 9407010303 | <strong>Reactor Trip Caused By Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1994, at approximately 1115 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION) operating at approximately 86 percent power when the Unit sustained a reactor trip. The trip was due to a low Departure from Nucleate Boiling Ratio signal which was a result of Reactor Coolant Pump (RCP) 1B tripping on a phase-to-phase electrical fault. The plant responded normally to the event. No safety functions were challenged and no Engineered Safety Features Actuation System actuations were received or required. The Control Room Supervisor classified the event as an uncomplicated reactor trip at 1130 MST and the Unit was stabilized in Mode 3 (HOT STANDBY). Management has conducted briefings with Operation and Maintenance personnel regarding the circumstances of the event. The 1B RCP supply cables and the penetration termination box have been repaired. At approximately 1515 MST on June 2, 1994, the Plant Review Board reviewed the status of the recovery/restart plan and approved entry into Mode 2 (STARTUP). Unit 2 returned to 86 percent power at approximately 1235 MST on June 5, 1994. An investigation of the event is continuing. <br /><br /> There have been two previous similar events (LER 528/88-011 and 529/92-006) reported pursuant to 10CFR50.73.
5291994003 | Palo Verde 2 | 09/27/1994 | 10/21/1994 | 9411020248 | <strong>Missed TS LCO ACTION for Monitoring Reactor Coolant System Boron Concentration</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1994, at approximately 1952 MST, Palo Verde Unit 2 was in Mode 5 (COLD SHUTDOWN), when the oncoming night shift Control Room personnel determined that the performance of the TS LCO 3.1.2.7 ACTION statement was required with one startup channel high neutron flux alarm inoperable and that it had been missed by the day shift Control Room personnel. TS LCO 3.1.2.7 ACTION a.1 states that at the time the alarm is determined to be inoperable and at subsequent applicable monitoring frequencies (i.e., every two hours), the reactor coolant system (RCS) boron concentration shall be determined by either boronometer or RCS sampling. The appropriate surveillance procedure was subsequently performed to comply with the TS LCO 3.1.2.7 ACTION statement. <br /><br /> An investigation of the event determined that the cause of the missed TS LCO ACTION requirement was attributed to personnel error by Control Room personnel. The Control Room personnel received appropriate counseling. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73 in the last three years.
5291994004 | Palo Verde 2 | 10/06/1994 | 06/28/1995 | 9507100227 | <strong>Class 1E Batteries in a Degraded Condition</strong><br /><i>Abstract:&nbsp;</i>At approximately 2200 MST on October 7, 1994, Palo Verde Unit 2 was in Mode 5 (COLD SHUTDOWN), when Train A (battery banks A and C) was declared inoperable because a projection of the test results based upon anticipated degradation indicated that they did not meet the 90 percent criteria of Technical Specification Surveillance Requirement (TS SR) 4.8.2.1.e, rendering both trains of Class 1E batteries inoperable. Train B (battery banks B and D) was declared inoperable (on October 1, 1994) because the measured capacity was slightly less than the required 90 percent capacity stated in TS SR 4.8.2.1.e. <br /><br /> Subsequent investigation has determined that Train B had been slightly below the 90 percent capacity as required by TS SR 4.8.2.1.e since February 1, 1994. Since both trains of batteries are required in Mode 1 (POWER OPERATION), Unit 2 operated in a condition prohibited by the plant's TS until it shutdown and reached Mode 5 on September 18, 1994. <br /><br /> The Equipment Root Cause of Failure Analysis (ERCFA) has determined that the failure mode results from a step decline in capacity caused by a loss of positive active material. The loss of capacity is most likely due to the result of poor production control during manufacturing. No credible mechanism for sudden discharge failure has been found. <br /><br /> There have been no previously similar events reported pursuant to 10CFR 50.73.<br /><br /> This supplement to LER 94-004 is being submitted to include EIIS codes, update corrective actions, and correct minor typographical errors.
5291994005 | Palo Verde 2 | 10/19/1994 | 07/28/1995 | 9508040044 | <strong>Technical Specification required shutdown due to the expiration of LCO time limit.</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1994, at approximately 1526 MST, Palo Verde Unit 2 was in Mode 2 (STARTUP), operating at approximately 2 percent power when Control Room personnel completed a plant shutdown as required by Technical Specification (TS) 3.5.2. The manual reactor shutdown was required because High Pressure Safety Injection (HPSI) valve SIA-UV-0627 had failed to satisfy ASME Section XI testing on October 16, 1994 and could not be restored to an operable condition within 72 hours as allowed by TS 3.5.2. Action (a). This condition rendered one subsystem of the Emergency Core Cooling System inoperable. A root cause evaluation determined the condition was unique to SIA-UV-0627 and was caused by the simultaneous occurrence of an over-the-seat pressure and a non-repeatable increase in the stem to disc friction. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5291994006 | Palo Verde 2 | 10/29/1994 | 11/23/1994 | 9412060114 | <strong>Reactor Trip on Low DNBR Due to Erroneous Penalty Factor</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1994, at approximately 2044 MST, Palo Verde Unit 2 was in MODE 1 (POWER OPERATION), operating at approximately 100 percent power when the reactor tripped on a low Departure from Nucleate Boiling Ratio (DNBR) trip signal. The trip signal was initiated from the Core Protection Calculators (CPC) after processing an erroneous DNBR penalty factor generated by Control Element Assembly Calculator (CEAC) #1. Required plant equipment and safety systems responded to the event as designed. and none were required. The Shift Supervisor diagnosed the event as an uncomplicated reactor trip. By approximately 2115 MST on October 29, 1994, the plant was stabilized in MODE 3 (HOT STANDBY). <br /><br /> The reactor trip was caused by an apparent malfunction in a processor board located in CEAC #1. As corrective action, the processor board was quarantined and replaced. An Equipment Root Cause Failure Analysis (ERCFA) was initiated on the processor board. <br /><br /> A previous similar event was reported in LER 528/89-004.
5291994007 | Palo Verde 2 | 12/06/1994 | 12/21/1994 | 9412290211 | <strong>Momentary Entry into TS 3.0.3 Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1994, at approximately 0908 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Unit 2 Control Room personnel momentarily entered and then exited Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 following a determination that the ACTION statement for TS LCO 3.7.7 had not been met with both trains of the Control Room Essential Filtration System (CREFS) inoperable in Modes 1 through 4. Prior to the TS LCO 3.0.3 entry, at approximately 0458 MST on December 6, 1994, Train A CREFS was declared inoperable for preplanned maintenance and TS LCO 3.7.7 was entered. <br /><br /> At approximately 0854 MST, Train B CREFS was momentarily rendered inoperable to support weekly chemistry sampling. At approximately 0908 MST, Control Room personnel recognized that for a brief moment at approximately 0854 MST, both trains of CREFS were inoperable and a condition warranting a TS LCO 3.0.3 entry had occurred. At approximately 1252 MST, Train A CREFS was returned to service and TS LCO 3.7.7 was exited. <br /><br /> The cause of the inadvertent entry into TS LCO 3.0.3 was attributed to personnel error. The Control Room Supervisor received appropriate counseling. <br /><br /> There have been no previous similar events reported pursuant to 10 CFR 50.73.
5291994008 | Palo Verde 2 | 09/29/1994 | 06/28/1995 | 9507100229 | <strong>Use Of Uncalibrated Boronometer Causes a TS SR To Be Missed</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1994, at approximately 1000 MST, Palo Verde Unit 2 was in Mode 5 (COLD SHUTDOWN) at approximately 15 psia and 95 degrees Fahrenheit (F), when the Shift Technical Advisor (STA) identified that the preventive maintenance (PM) task for calibrating the boronometer was overdue. Technical Specification (TS) 3.1.2.7 Limiting Condition for Operation (LCO) allows the Reactor Coolant System (RCS) boron concentration to be determined by either boronometer or RCS sampling. 10CFR50 Appendix B Criterion XII requires that devices used in activities affecting quality be properly calibrated. Therefore, the boronometer could not be used to satisfy the above TS requirement. <br /><br /> The evaluation of this condition revealed that on three separate occasions between February 17 and March 15, 1994, the boronometer was used by Operations personnel to satisfy TS LCO 3.1.2.7 ACTION a. In two of the cases (February 18 and March 15, 1994), only the initial RCS sample was required by TS due to the fact that the Startup (SU) Channels were returned to operable status prior to the need for additional RCS samples. In the third case (February 17, 1994), the boronometer was used by Operations personnel to satisfy TS 3.1.2.7 monitoring frequency requirements of the Core Operating Limits Report (COLR). Therefore, an uncalibrated piece of equipment was used by Operations personnel to meet TS LCO 3.1.2.7. This was in violation of the frequency needed for compliance with TS LCO 3.1.2.7. <br /><br /> There have been no previous similar events reported pursuant to 10CFR 50.73. <br /><br /> The purpose of this supplement is solely for the inclusion of EIIS codes and correction of minor typographical errors.
5301994001 | Palo Verde 3 | 02/17/1994 | 03/16/1994 | 9403210145 | <strong>Daily Surveillance Test for Reactor Power Channel Calibration Checks Not Satisfactorily Completed</strong><br /><i>Abstract:&nbsp;</i>At approximately 1700 MST on February 20, 1994, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) operating at approximately 85 percent power when Operations personnel identified that the February 17, 1994 performance of Technical Specification (TS) Surveillance Requirement (SR) 4.3.1.1 for reactor power channel calibration checks had not been satisfactorily completed. Contrary to the surveillance testing procedure, the absolute deviation between two of the power level values i.e., Channels A and B core protection calculators (CPC) calibrated neutron flux power) and actual power indication was greater than two percent. In accordance with Table 4.3-1, Reactor Protective Instrumentation Surveillance Requirements, Table Notation 2, if the absolute deviation is greater than two percent, the linear power level, the CPC delta T power, and CPC nuclear power signals are to be adjusted to agree with the calorimetric calculation. The daily required surveillance testing was satisfactorily completed the following night at approximately 2338 MST on February 18, 1994. <br /><br /> The cause of this event was cognitive personnel error in that Control Room personnel failed to identify the absolute deviation greater than two percent and as a result failed to complete the necessary power signal adjustments. As corrective action, positive discipline actions have been administered to all personnel involved. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301994002 | Palo Verde 3 | 03/17/1994 | 08/08/1994 | 9408240016 | <strong>Main Steam Safety Valve Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1994, Unit 3 was in Mode 1 (POWER OPERATION) at approximately 86 percent power with one Main Steam Safety Valve (MSSV) gagged when APS Engineering personnel completed Trevitesting of 13 of the 20 MSSV. The relief settings on 7 of the tested valves were found below the allowed - 1 percent tolerance limit specified in Technical Specification 3.7.1.1. All 7 valves were adjusted, certified, and returned to service. The relief setpoints of the other 6 valves were found within the allowed +/- 1 percent limit. On March 19, 1994, Unit 3 was shutdown for the start of the scheduled refueling outage, 3R4. During this outage the remaining 7 untested MSSVs and 4 Pressurizer Safety Valves (PSV) were removed and sent to the Westinghouse service facility for testing. Based upon a review of the Westinghouse test results, 6 of 7 MSSVs as-found relief settings were out of tolerance. This resulted in a total of 13 of 20 MSSV as-found relief setting being out of tolerance. Thirteen of the MSSV as-found relief settings were below specification and none were above specification. One valve was sent to Westinghouse gagged due to leakage during the previous operating cycle so no as-found data is available. Additionally, the review of the actual test results revealed that none of the PSV as-found relief settings were out of specification. None of the original Unit 3 MSSVs were returned to the Unit and all were replaced with pretested spares that had been included in the preventive maintenance program. The 4 original Unit 3 PSVs were tested and returned to the Unit. The most recent LERs on MSSV Out-of-Tolerance conditions are 528/93-009-02, 529/91-005-01, and 530/92-005-00.
5301994003 | Palo Verde 3 | 05/06/1994 | 06/04/1994 | 9406140351 | <strong>Technical Specification Violation Due to Missed Channel Check</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On May 7, 1994, at approximately 0200 MST, Palo Verde Unit 3 was in Mode 6 (REFUELING) at approximately 91 degrees Fahrenheit and at atmospheric pressure when the Unit 3 Control Room staff determined that the shiftly channel check of the startup neutron flux monitors had not been performed in accordance with Technical Specification (TS) Surveillance Requirement (SR) 4.9.2.a. An initial review of the shiftly surveillance records found that this channel check had not been performed for several previous shifts. With both of the required monitors inoperable, LCO ACTION b. requires that the boron concentration of the reactor coolant system be determined at least once per 12 hours during Mode 6. This resulted in 3.9.2, since the hours during Mode a violation of TS 3.9.2, since the channel check was not completed within the required 12 hour surveillance interval and the required ACTION was not completed. At approximately 0215 MST on May 7, 1994, the channel check was successfully completed. The cause of the missed channel check was due to a procedure error. As corrective action, the procedure was revised to correctly require channel check performance in Mode 6. There have been no previous similar events reported pursuant to 10 CFR 50.73.
5301994004 | Palo Verde 3 | 05/30/1994 | 06/27/1994 | 9407060262 | <strong>TS LCO 3.0.3 Entry to Restore ASME Code Class 2 Structural Integrity</strong><br /><i>Abstract:&nbsp;</i>On two separate occasions, at 1500 MST on May 30, 1994 and at 1542 MST on June 8, 1994, Palo Verde Unit 3 was in Mode 3 (HOT STANDBY) when Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 following the determination that secondary pressure boundary leakage existed and that the applicable TS LCO 3.4.9 Structural Integrity ACTION statement could not be met with the Reactor Coolant System (RCS) temperature greater than 210 degree Fahrenheit (F). On May 30, 1994 and on June 8, 1994, APS ASME Section XI engineering personnel determined that the leakage at two steam generator 2 (SG-2) nozzle penetrations was unacceptable (i.e., the structural integrity was in question). For the first occurrence involving a SG-2 instrument nozzle penetration leakage, at approximately 0454 MST on May 31, 1994, Control Room personnel returned the unit to Mode 5 (COLD SHUTDOWN), exited TS LCO 3.0.3, and remained in compliance with TS LCO 3.4.9 ACTION b (i.e., RCS temperature is less than or equal to 210 degrees F). For the second occurrence involving a SG-2 sample nozzle penetration leakage, at approximately 0256 MST on June 9, 1994, Control Room personnel returned the unit to Mode 5, exited TS LCO 3.0.3, and remained in compliance with TS LCO 3.4.9 ACTION b. For both events, the apparent cause of the nozzle penetration leakage was concluded to be due to a defective weld, most likely from original fabrication. Both nozzle penetrations were repaired. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.
5301994005 | Palo Verde 3 | 08/19/1994 | 09/16/1994 | 9409270341 | <strong>Reactor Trip Following the Degradation of Main Feedwater Flow</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1994, at approximately 1319 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred when Steam Generator Number 1 (SG-1) water level reached the Reactor Protection System trip setpoint for low steam generator water level following the degradation of main feedwater flow. Immediately following the reactor trip, a low steam generator water level alarm annunciated for SG-1, followed by the Engineered Safety Feature Actuation System (ESFAS) actuation of the Auxiliary Feedwater Actuation System (AFAS-1) on low-low steam generator water level for SG-1. The Steam Bypass Control System responded as designed to control the secondary system pressure. Required plant equipment and safety systems responded to the event as designed. No other ESF actuations occurred and none were required. Steam generator water level was restored to normal using auxiliary feedwater flow. The Control Room Supervisor diagnosed the event as an uncomplicated reactor trip. By approximately 1356 MST on August 19, 1994, the plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The reactor trip was initiated by an unexplained and unwarranted closing of the economizer valve on SG-1 which was later determined to be caused by an intermittent component failure of the feedwater control system (FWCS-1), most probably the master controller or associated circuitry. As corrective action, the controller was replaced.
5301994006 | Palo Verde 3 | 08/23/1994 | 09/22/1994 | 9410040104 | <strong>Shutdown Cooling Loop Inoperable Due to Pump Breaker Racked Down and in the Test Position</strong><br /><i>Abstract:&nbsp;</i>At approximately 1530 MST on August 23, 1994, Arizona Public Service Company (APS) formalized its response to Notice of Violation (NOV) 50- 530/94-12-03. In the response, APS revised Palo Verde's operability determination position on crediting manual operator action for maintaining 4.16 kV pumps OPERABLE with their associated 4.16 kV breakers racked down and in the test position. Based on the revision, racking a 'standby' Low Pressure Safety Injection (LPSI) pump supply breaker down and in the test position during shutdown cooling operations renders the 'standby' shutdown cooling loop inoperable. In retrospect, Palo Verde Unit 3, while operating in MODE 6 (REFUELING) with less than 23 feet above the reactor pressure vessel flange, performed Integrated Safeguards testing in a plant configuration prohibited by Technical Specification Limiting Condition for Operation (TS LCO) 3.9.8.2. The 'standby' LPSI pump supply breaker was racked down and in the test position which rendered the 'standby' shutdown cooling loop inoperable. TS LCO 3.9.8.2 requires two loops of shutdown cooling be maintained OPERABLE with one loop in operation. <br /><br /> Palo Verde's operability determination procedure has been revised to incorporate APS' current position. <br /><br /> There have been no previous similar events reported pursuant to 10 CFR 50.73.
5301994007 | Palo Verde 3 | 08/30/1994 | 09/24/1994 | 9410040165 | <strong>Reactor Trip Caused by an Increase in Main Feedwater Flow</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1994, at approximately 1500 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred when Steam Generator Number 2 (SG-2) water level reached the Reactor Protection System (RPS) trip setpoint for high steam generator water level caused by an increase in main feedwater (MFW) flow. In addition to the reactor trip, the unit received an Engineered Safety Feature Actuation System (ESFAS) actuation of the Main Steam Isolation System (MSIS A and MSIS B) on high steam generator water level for SG-2. The MSIS necessitated the use by Control Room personnel of the auxiliary feedwater pump (AFWP-B) and the atmospheric dump valves (ADVs) to control secondary heat removal (AFWP-B was used to feed the steam generators and the ADVs were used to stabilize secondary temperature and pressure). Required plant equipment and safety systems responded to the event as designed. No other ESF actuations occurred and none were required. The Shift Supervisor diagnosed the event as an uncomplicated reactor trip. By approximately 1530 MST on August 30, 1994, the plant was stabilized in Mode 3 (HOT STANDBY). <br /><br /> The reactor trip on high SG-2 water level was initiated by a malfunction in the Feedwater Control System (FWCS-2) which was attributed to a failed FWCS-2 master controller power fuse. As corrective action, the master controller was replaced.
5301994008 | Palo Verde 3 | 12/09/1994 | 03/17/1995 | 9503280263 | <strong>Power Operation Greater than 20 percent with Cross-Wired Incore Instruments Resulting in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1994, at approximately 1300 MST, Palo Verde Unit 3 was in MODE 5 (COLD SHUTDOWN) when a refuel handler discovered eight standard and eight mini incore instruments (ICI) cross-wired. Unit 3 operated at power above 20 percent from June 21, 1994 to November 26, 1994 with the input signals from the mini ICIs supplying the Core Operating Limit supervisory System (COLSS). Data processed in the COLSS is used for calculating power distribution in the core. The sensitivity and background correction factors used by the COLSS are different for each individual ICI. Cross-wiring the standard and mini ICIs resulted in a violation of Technical Specification Limiting Condition for Operation (TS LCO) 3.2.2 in that the measured PLANAR RADIAL PEAKING FACTORS (Fxy) were greater than the affected Fxy, used in the COLSS and the Core Protection Calculators (CPC), during power operation above 20 percent. As corrective action, the standard ICIs were reconnected to the COLSS, and the Plant Monitoring System (PMS) detector information database (DET) file was reconstructed. An investigation determined that there were no adverse safety impacts as a result of operating with the ICIs cross-wired. <br /><br /> There have been no previous similar events reported pursuant to 10CFR50.73.