## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
0101997001 | Dresden 1 | 02/10/1997 | 03/12/1997 | 9703170245 | <strong>Loss of the Main Chimney Alternate Iodine and Particulate Sampling System due to a breaker trip caused by an apparent management deficiency.</strong><br /><i>Abstract:&nbsp;</i>With Unit 1 defueled, the Main Chimney Monitoring System was removed from service for calibration and the Alternate Iodine and Particulate Sampling System was placed in service. At approximately 1430, on February 10, 1997, the 120 volt circuit breaker supplying the Alternate Iodine and Particulate Sampling System tripped. Upon discovery, at approximately 1055 on February 11, 1997, the system was restored to operation. The cause of this event is an apparent management deficiency of the installation process which allowed the Alternate Iodine and Particulate Sampling System to utilize the uncontrolled 120 volt circuit. Immediate corrective actions included disconnecting the auxiliary loads, restricting use of the outlets connected to the 120 volt circuit, and performing a surveillance to verify continued system operation. These immediate corrective actions will continue until permanent changes are implemented. No previous occurrence of this event has been identified.
1331997001 | Humboldt Bay 3 | 04/08/1997 | 05/15/1997 | 9705230009 | <strong>Process Monitor Alarm Settings</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1997, an operator performed a weekly surveillance test to set the liquid radwaste process monitor alarm settings. The operator observed that the as-found conditions set the previous week, on April 8, 1997, were too high and exceeded the limit in Technical Specification V.B.2.b. The process monitor warning alarm should have been set at 1500 counts per minute (cpm), but was found to be set at 41,000 cpm. The process monitor high alarm should have been set at 5000 cpm, but was found to be set at 300,000 cpm. The operator immediately set the alarm settings to the correct values. The root cause of the event was personnel error, cognitive, in that the operator who incorrectly set the process monitor alarm settings on April 8 read the wrong scale on the monitor. Corrective actions to prevent recurrence include: coaching and counseling the employee as part of the positive discipline program; and revising the test procedure to modify the method by which the alarm settings are verified, and to specify the proper scale to use.
1331997002 | Humboldt Bay 3 | 04/25/1997 | 05/29/1997 | 9706050178 | <strong>Demineralized Water Tank Level</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1997, plant operators responded to a low level alarm in the spent fuel pool (SFP) by transferring water from the dermineralized water tank (DWT) to fill the SFP to its normal level. Prior to the transfer, the operators calculated the amount of DWT water needed and determined that the DWT low level alarm would occur but that the DWT level would remain above the Technical Specification level of 2000 gallons upon completion of the transfer. The operators chose not to read an annunciator response guide (ARG) that requires the DWT to be refilled upon receipt of the DWT low level alarm. After completion of the water transfer, the operators observed that the DWT level dropped to 1900 gallons. The root cause of the event was personnel error, cognitive, in that the operators did not review and follow the ARG upon receipt of the DWT low level alarm. Contributing causes were the operators did not take into account other DWT water usage, and did not account for limitations of the SFP level recorder when used as indication for a change in DWT volume. Corrective actions to prevent recurrence include positive discipline for the responsible employees and enhancing procedures to address the causes of this event.
1551997001 | Big Rock Point | 01/02/1997 | 01/31/1997 | 9702050431 | <strong>Test Not Performed in Accordance With Appendix J to 10 CFR Part 50.</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3.7(d) requires that "containment sphere integrated leakage rate tests (Type A, B, and C) shall be conducted in accordance with the requirements specified in Appendix J to 10 CFR Part 50, as modified by approved exemptions". On January 2, 1997, at 1948 hours, plant procedure TV-02, Containment Integrated Leak Rate Test (ILRT), was initiated. The purpose of this procedure is to pressurize the containment sphere through penetration H-80 and its associated containment isolation valve VCI-1, then measure leakage after 8 hours. When the air compressors were valved in to supply air into the containment sphere, and the test could not be performed as expected, the engineers determined that a blind flange had been installed between system piping flanges. The blind flange is believed to have been in this location since 1992, the date of the last ILRT. This condition is contrary to Big Rock Point Technical Specification 3.7(d) because any Local Leak Rate Tests (LLRTs) conducted on this penetration since 1992 were not performed in accordance with Appendix J criteria. The root cause concluded that TV-02 did not provide adequate guidance for the control of this test. TV-02 will be revised to address the use of the blind flange.
1551997002 | Big Rock Point | 01/15/1997 | 02/10/1997 | 9702180324 | <strong>Penetration Inspection Not Performed in Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point Technical Specification 3.7(c) requires that 'Each reactor shutdown for refueling, but in no case at intervals greater than two years, all electrical and accessible piping penetration nipple welds be visually examined for evidence of corrosion, cracking or deterioration'. Contrary to the above, two containment electrical penetrations, H-115A and H-115B, had not been inspected since they were installed in 1985. Both penetrations are located on the bottom of the equipment air lock under the floor. The electrical penetrations had been considered inaccessible due to the floor plates being welded in place, therefore inspections during refueling outages were not performed. This discovery was made while the plant was shutdown, and containment integrity was not required. In 1985, TS 3.7(c) was interpreted to treat electrical and piping penetrations the same; that is, only accessible penetrations required inspection. Following closer review, the Big Rock Staff has concluded that this interpretation was incorrect. The penetrations were accessed by grinding/cutting the grating and flooring as required. The penetrations were inspected and no evidence of deterioration or cracking was detected. The grating/flooring was tack welded back in place to facilitate future inspections.
1551997003 | Big Rock Point | 01/28/1997 | 02/27/1997 | 9703050162 | <strong>Demineralized Water Piping Susceptible to Overpressurization During a Design-Basis Accident</strong><br /><i>Abstract:&nbsp;</i>During the evaluation of NRC Generic Letter 96-06: 'Assurance of Equipment Operability and Containment Integrity During Design Basis Accident Conditions' two systems were discovered to be susceptible to the overpressurization of isolated piping segments that could affect containment integrity during a postulated design basis accident. The two susceptible piping segments at Big Rock Point are in the functionally non-safety-related treated waste and demineralized water systems. A detailed response to Generic Letter 96-06 with commitments was provided to the NRC by Consumers Power Company letter dated January 28, 1997. Big Rock Point was designed prior to codes requiring consideration of fluid expansion affects (1955 ANSI B31.1.0). This code pre-dates most nuclear plant designs and likely did not consider the environmental effects of a containment structure during post-accident conditions. Corrective action includes an evaluation of surge protection for the demineralized water piping, and procedure changes for the treated waste system, to eliminate susceptibility to overpressurization during design basis accident conditions.
1551997004 | Big Rock Point | 04/10/1997 | 05/09/1997 | 9705160203 | <strong>Potential Loss of DC Power for the Primary Containment Spray and Liquid Poison Systems.</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1997, a load test was conducted on feeder breaker 72-12, DC Distribution Panel #1 as part of an action plan to verify breaker performance. The plant was in the cold shutdown condition. Following what was believed to be a successful performance of the magnetic load test, breaker 72-12 would not manually reset. Breaker 72-12 was opened, and verified to contain only a magnetic trip feature. Plant drawings indicated that it should have a thermal trip feature. On April 10th, 1997, approximately 1600, the Big Rock Point Staff concluded from an additional calculation that a loss of selective coordination over a minor portion of the interface between breaker 72-12 and other DC breakers in the circuit could have resulted in a loss of the panel due to a nonsafety-related fault. The safety-related loads supplied by the panel that could have been affected are MO-7064, Primary Containment Spray valve, and the Liquid Poison System squib valve control circuits. The root cause for this event is an inadequate design control program prior to 1976. No design review program covered the physical verification of this breaker. Breaker 72-12 was removed and replaced with a load-tested, thermal-trip-only spare breaker. Long term corrective actions include the performance and development of preventative maintenance tasks to remove and test the DC breakers associated with the panel.
1551997005 | Big Rock Point | 10/09/1997 | 11/05/1997 | 9711170120 | <strong>Violation of Facility Operating License</strong><br /><i>Abstract:&nbsp;</i>Big Rock Point's Operating License prohibits storage of materials in the area between spent fuel rack B and the east wall of the spent fuel pool so that local temperatures in the fuel pool will remain consistent with the cooling analysis of record. Contrary to this requirement, a stainless steel bucket was discovered on the spent fuel pool floor between rack B and the east wall of the spent fuel pool on October 9, 1997, at approximately 1330. In addition to the bucket, additional debris (such as old pvc padding, hook and cable) were discovered. The cause of the material resting on the floor between the "B" rack and the east SFP wall cannot be determined. The reason for not discovering the bucket earlier can be attributed to the lack of a surveillance procedure to confirm that materials were not located in this area. The bucket was removed, and facility procedures have been revised to ensure that this area is kept clear. An analysis confirmed that there was no immediate or past operational SAFETY CONCERN FINDING MATERIALS BETWEEN "B" rack and the east wall of the SFP.
2061997001 | San Onofre 1, San Onofre 2, San Onofre 3 | 01/07/1997 | 11/07/1997 | 9711140089 | <strong>Missed Security Test/Inspection</strong><br /><i>Abstract:&nbsp;</i>On 1/7/97, with Unit 1 permanently shutdown, Unit 2 shutdown for refueling and Unit 3 at 100 percent power, a review of security system [IA] records revealed that three (3) of twenty (20) E-field sectors had not been tested within the 92 days required by the physical security plan (PSP). Because this condition was not in conformance with the PSP, Southern California Edison (SCE) made the required 24-hour report on 1/7/97 (NRC Log No. 31553). Due to this discovery, SCE reviewed other Station records and, on 1/9/97, concluded the December monthly inspection for active Vehicle Barrier System bollards had not been completed on time. SCE made a similar 24-hour report on 1/10/97 (NRC Log No. 31569). As required by Condition 2.D of the Unit 1 Possession Only License, and Condition 2.G of the Units 2 and 3 Facility Operating Licenses, by letter dated January 20, 1997, SCE provided a 14-day follow-up report for these occurrences. This revised report is being submitted for the discovery of several other instances of late E-field sector testing and VBS surveillances. These occurrences were caused by cognitive personnel error. The individual responsible for security system tests/inspections failed to ensure they were completed as required. SCE implemented the required compensatory actions pending test/inspection completion. The E-field tests were successfully completed on 1/8/97; the active bollards inspections were successfully completed on 1/9/97. SCE confirmed the affected systems were always operable or the required compensatory actions were in place. Consequently, these occurrences had no safety significance. SCE has enhanced the security testing/inspection tracking process. LER 1-96-002 reported a missed inspection of security tamper switches. That event was caused by inadequate communication when capturing inspection requirements for a newly installed security system, a cause not present for the events reported herein.
2061997002 | San Onofre 1, San Onofre 2, San Onofre 3 | 10/27/1997 | 11/25/1997 | 9712030071 | <strong>Lost Copy of the Security Contingency Plan</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1997, at approximately 0825, a Security Supervisor opened an authorized storage cabinet to obtain his controlled copy of the Safeguards Contingency Plan (SCP) and discovered it was not in the cabinet. Two copies of the SCP were kept in the cabinet and several people had authorized access to the cabinet. Southern California Edison (SCE) immediately initiated a search of other potential locations where the SCP might have been. At approximately 1400 PST (time of discovery), Security personnel concluded the SCP copy was missing. As required by 10 CFR 73, Appendix G and Generic Letter 91-03, a 1-hour telephone notification was made at 1416 PST on October 27, 1997 (NRC Operations Log #33156). SCE confirmed that all copies of the Physical Security Plan and all other copies of the SCP were properly secured. SCE continued to search for the missing SCP without success. The preliminary investigation indicates the SCP was removed from the cabinet by an unknown, but authorized Security employee and not returned. SCE's investigation (Corporate Security) is continuing. SCE will revise this LER by December 19, 1997 to provide the results of this investigation. Short term compensatory measures included notifying the Security Force of the loss and an increased Security posture in and around the plants' protected areas. SCE is evaluating additional measures for controlling safeguards material. The planned revision to this LER will detail the corrective measures selected. In November 1995, SCE reported that safeguards material had been lost by the U.S. Postal Service (LER 1-95-002), a cause not present in this case.
2061997003 | San Onofre 1, San Onofre 2, San Onofre 3 | 05/20/1997 | 12/22/1997 | 9801050316 | <strong>Security Computer System Out of Service</strong><br /><i>Abstract:&nbsp;</i>On 5/20/97, at 0932 PDT, with Unit 1 permanently shutdown, Unit 2 at 100 percent full power, and Unit 3 shutdown, the main and backup security computers [IA] became inoperable. Within 10 minutes, Southern California Edison (SCE) posted roving compensatory guards for all plant vital areas. The computer system was restored at 1015 (43 minutes later) and the event recorded in Security Event Log (SEL) # 199-97. Similar events and corrective actions also occurred on 7/29/97 (73 minutes; SEL # 285-97) and 10/30/97 (93 minutes; SEL #445-97). During an NRC Inspection Exit interview on 11/21/97 (discovery date), an inspector indicated roving compensatory guards were insufficient to compensate for the inoperable computers, and the event should have been reported within 1 hour in accordance with SCE's security reporting procedure. On 12/19/97, at 1230 PST, SCE discovered the main and backup security computers again had become inoperable at 1226 PST. Within 10 minutes, SCE posted stationary compensatory guards. The main computer was returned to operation at 1246 PST (20 minutes later). Based on the NRC inspectors' earlier comments, SCE reported this event at 1320 PST (NRC Log No. 33436). SCE is providing this 30 day report as required by 10CFR73.71(d) for all events discussed herein. At the time of the 12/19 occurrence, Unit 1 remained permanently shutdown, Unit 2 was at 75 percent full power, and Unit 3 was at 99 percent power. SCE is completing an engineering review of the security computer system to determine required corrective actions to improve system reliability. SCE's security reporting procedure is being revised to clarify that failure of both security computers will be reported to the NRC within 1 hour of occurrence. Based on the short duration of each event and the continued availability of the security force, SCE believes these occurrences did not significantly impact plant safety, nor significantly reduce the effectiveness of the San Onofre security program.
2131997001 | Haddam Neck | 01/14/1997 | 02/11/1997 | 9702250307 | <strong>River Temperature Below UFSAR Analyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1997, at approximately 1530 hours, with the plant in a defueled mode, a reportability evaluation determined that the plant had been in a condition outside of the analyzed service water supply temperature range. Both the Haddam Neck Updated Final Safety Analysis (UFSAR) and the service water supply piping stress analysis reference 35 degrees F as the minimum service water supply temperature, however, historically, there have been times when the average supply (river water) temperature was below 35 degrees F. This condition was previously identified in February 1996 (LER 96-002-00). Although actions were initiated to update the UFSAR, the changes were never made resulting in a recurrence of the same condition. The cause was a program deficiency in that the design basis calculations were not updated in a timely manner. It was determined that there are no limiting effects associated with overcooling any components and that the lower supply temperature had no effect on existing emergency core cooling calculations or on the structural integrity of the service water system. Corrective action consists of revising the UFSAR and the design basis calculations to reflect the normal operating temperatures of the service water system. In addition there is a formal, ongoing effort to identify and correct UFSAR inaccuracies.
2131997002 | Haddam Neck | 02/06/1997 | 03/05/1997 | 9703130334 | <strong>Reactor Coolant Surveillance Sample Not Taken With Plant in Defueled Mode</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1997, with the plant in a defueled mode, a review of the plant's Technical Specifications by Chemistry personnel determined that the Technical Specification surveillance for sampling the reactor coolant system (RCS) for chlorides and fluorides had not been performed since November 15, 1996 when the residual heat removal system was shut down after the reactor core was offloaded. Technical Specification 3.4.7 requires that RCS chemistry be maintained within specified limits at all times; not just while in certain modes. The cause of the event was personnel error due to an incorrect interpretation of the Technical Specifications. It was incorrectly assumed that sampling could be terminated since surveillances are not generally performed on out of service equipment. Immediate corrective action was to reinitiate sampling of the RCS. The personnel involved were counseled on the importance of meeting all Technical Specifications at all required times. Also, all departments with surveillance responsibilities reviewed their surveillances and no other similar issues were identified. A review of records from previous refueling outages, in which the reactor was defueled, determine that this situation has occurred in the past. This event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131997004 | Haddam Neck | 02/19/1997 | 03/19/1997 | 9703250085 | <strong>Potential for Fuel Assembly Exceeding Maximum Load Limit Over Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1997, at 1415 hours, with the plant defueled, a preliminary engineering evaluation determined that fuel assembly loads in excess of the Technical Specification limit of 1650 pounds could have been potentially moved over spent fuel assemblies within the spent fuel pool. The cause of this condition was due to removing the exclusion for fuel assemblies from the Technical Specification requirements in 1989 in an attempt to remove ambiguity. During the time frame of the change, it was likely concluded that the weight of a fuel assembly would never exceed the 1650 pound limit; therefore the exclusion was not deemed necessary. Since then, new core designs for 24 month cycles have resulted in heavier fuel assemblies which have reduced the available load margin. Immediate corrective action was to prohibit movement of fuel assemblies over the fuel pool. The long term corrective action will be to amend the Technical Specifications in accordance with the guidance for Improved Standard Technical Specifications to restore the exclusion for fuel assemblies. This event is reportable under 10CFR50.73 (a) (2) (ii) (B) as a condition outside the design basis of the plant. It is also reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2131997006 | Haddam Neck | 02/27/1997 | 04/09/1997 | 9704150234 | <strong>Liquid Effluent Radiation Monitor (R-18) Determined Inoperable Due to Low Sensitivity</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 27, 1997, at approximately 1630 hours, with the plant defueled, it was determined that, in the present plant configuration, the service water effluent radiation monitor (R-18) does not have the sensitivity required to meet the requirements of the Offsite Dose Calculation Manual (ODCM) when the plant has no circulating water pumps in service. At the time of discovery the monitor had already been declared inoperable for a separate reason and compensatory sampling was already in place. Circulating water pumps have been taken out of service during previous outages, however, there is no documented evidence that monitor R-18 was declared inoperable during these periods. This would have required compensatory sampling in accordance with the Technical Specifications. Efforts to determine historical operability of the monitor proved inconclusive, therefore, on March 10, 1997, it was decided to conservatively report this event under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The cause of this event was determined to be an inadequate guidance within the ODCM for calculating monitor setpoints. Setpoint calculation methodology did not account for all possible plant configurations. Long term corrective action consists of revising the ODCM methodology for calculating the monitor setpoint to ensure that the resulting value is applicable for all possible plant configurations.
2131997007 | Haddam Neck | 03/11/1997 | 04/09/1997 | 9704150240 | <strong>Potential for Service Water System Water Hammer Following Loss of Normal Power</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1997, at approximately 1730 hours, with the plant defueled, a reportability evaluation determined that the service water (SW) supply line to the spent fuel pool (SFP) heat exchangers (HX) was inoperable. Following a loss of normal power (LNP), a potential exists for water hammer in the high point of the SW lines to the SFP HXs upon restart of a SW pump. The apparent cause of this event was that the original design of the plant and other earlier analyses did not identify the potential for water hammer. Short term corrective action consisted of revising a procedure and staging materials to allow installation of a temporary cooling line, using fire hose, in the event of the failure of the SW supply line to the SFP HXs. Long term corrective action consists of installing a check valve in the SW supply line to the SFP HXs which will hold the line full of water until pump restart following a LNP, thereby preventing water hammer.
2131997008 | Haddam Neck | 03/27/1997 | 04/23/1997 | 9705010040 | <strong>Wall Thinning Due to Corrosion Found in Service Water Piping for Spent Fuel Cooling</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1997 at 1905 hours, with the plant defueled, the service water return line from the spent fuel pool heat exchangers was declared inoperable based on a Generic Letter 90-05 wall thinning analysis. The degraded 3 inch area of piping had previously been examined in October 1996, using ultrasonic inspection techniques, and was determined acceptable with sufficient margin to last one year. The degraded area was found during a routine followup inspection. The cause of the wall thinning appears to be microbiologically influenced corrosion (MIC). At the time of discovery the SFP cooling system had already been declared inoperable since March 11, 1997 due to a potential water hammer issue in the service water supply line. Initial corrective actions taken as a result of the degraded return line consisted of approving a temporary procedure change to allow using fire hoses to establish an alternate flow path during piping replacement and/or following a seismic event. Other spent fuel pool service water piping areas were examined during augmented inspections which did not reveal any additional flaws below code allowable limits. Previously inspected areas of the supply piping will continue to be monitored for any changes in corrosion rates. The degraded piping has been replaced and the system was returned to operable status on April 17, 1997.
2131997009 | Haddam Neck | 04/04/1997 | 05/02/1997 | 9705070049 | <strong>Design Deficiency Found in Stack Radiation Monitor Isokinetic Nozzle</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1997, with the plant permanently shutdown, it was determined that the sample nozzle for the vent stack radiation monitor (R-14A) was not drawing the sample from the process stream in an isokinetic fashion as described in the plant FSAR. Isokinetic sampling is required for representative sampling of particulates in the process flow. The apparent causes of this condition were (1) the original design does not meet the later ANSI N13.1-1969 standards, and (2) an inadequate understanding of system design and operational requirements by Chemistry and Engineering personnel. Immediate corrective action was to declare the R-14A sample system out of service and perform compensatory sampling in accordance with the Technical Specifications. An alternate backup particulate and iodine sample system is being evaluated and a corrective action plan for the entire Radiation Monitoring System (RMS) has been developed which includes resolving the R-14A nozzle issue. This event is reportable under 10CFR50.73 (a) (2) (ii) (B) as a condition outside the design basis of the plant.
2131997010 | Haddam Neck | 04/10/1997 | 05/08/1997 | 9705150195 | <strong>Spent Fuel Pool Cooling Pump Net Positive Suction Head Inadequate (Historical)</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1997, at approximately 1200 hours with the plant in the permanently defueled condition, an engineering review of design basis documents determined that prior to 1975 the available net positive suction head (NPSH) for the spent fuel cooling pump at the maximum pool temperature (identified in historical licensing basis documents) could potentially be below the required NPSH. Cavitation of the pump could have occurred if the pool temperature exceeded approximately 153 degrees F with a single suction line open. The apparent cause of this event was a deficiency in the original (pre 1975) system design basis. Corrective action consisted of confirming that the existing design is adequate to support licensed operating conditions. As follow-up to the recent engineering review, the normal and abnormal operating procedures for the spent fuel pool cooling system were revised to include a caution that both suction valves are to be open prior to exceeding 140 degrees F to prevent pump cavitation. The applicable procedures) will also be revised to throttle the pump discharge valve as necessary to provide adequate NPSH for elevated fuel pool temperatures. under 10CFR50.72(b)(2)(i) and 10CFR50.72 (b)(2)(iii)(B).
2131997011 | Haddam Neck | 06/30/1997 | 08/29/1997 | 9709030063 | <strong>Spent Fuel Pool Cooling System Heat Removal Capability Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1997 at 1430 hours, with the plant permanently shutdown and defueled, an engineering evaluation determined that the Spent Fuel Pool Cooling (SFPC) system was incapable of removing the maximum design basis heat load of the spent fuel pool (SFP). The current design bases require the SFPC system to be able to remove 22.4 million Btu/hr following an emergency core offload at the end of the last licensed operating cycle (year 2007) with 90 degree F cooling water, while maintaining the pool at less than 150 degrees F. Calculations performed during normal operating conditions revealed the SFPC system could not currently meet this requirement. Also, on August 1, 1997 at 2108 hours, during surveillance testing of a check valve in the SFPC Service Water supply line, it was discovered that design basis flow could not be provided to the SFPC system. The design basis requires a minimum of 855 gpm, while only 820 gpm was measured. However, the system was fully capable of meeting the emergency full core offload requirements prior to the 1996 refueling. The cause of both events is believed to be siltation of the inservice SFPC heat exchanger. Since the current SFPC heat load is less than 3 million BTU/hr and decreasing, significant heat removal margin still exists. After backwashing the heat exchanger on August 19, 1997, 860 gpm was measured through the heat exchanger. This supplemental report documents two related events.
2131997012 | Haddam Neck | 07/24/1997 | 08/22/1997 | 9708270035 | <strong>Excessive Check Valve Seat Leakage in Service Water Supply Piping to Spent Fuel Pool Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1997, at approximately 2011 hours, with the plant permanently defueled, a check valve in the service water (SW) supply line to the spent fuel Pool (SFP) heat exchangers (HX) failed its seat leakage surveillance test and was declared inoperable. The valve had been installed in April 1997 to eliminate the potential for water hammer after a loss of normal power and restart of the service water pumps. The apparent cause is believed to be due to the variation in the surveillance test methodology which may have allowed debris to be backflushed into the valve seating area during system filling operations. Following an engineering determination, this event was reported on July 29, 1997. The valve was satisfactorily retested on July 29, 1997, using the original test lineup. Short term corrective action consisted of revising a procedure and staging materials to allow installation of a temporary cooling line, using fire hose, in the event of the failure of the SW supply line to the SFP HXs. Additionally, the test procedure was revised to ensure the surveillance test is performed in a manner which cannot backflush debris into the check valve. Although it is uncertain as to whether the valve was ever actually inoperable this event is being conservatively reported as a condition outside the design basis of the plant.
2131997013 | Haddam Neck | 08/07/1997 | 09/05/1997 | 9709100216 | <strong>Inadvertent Halon Discharge in Control Room Due to Camera Flash Results in Precautionary Control Room Evacuation</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1997, at approximately 0947 hours, with the plant in a permanently defueled condition, the control room Halon system was inadvertently discharged while a training instructor was taking flash camera pictures of the inside of a Halon control panel located in the control room. Because prolonged exposure to Halon, a chemical used to extinguish fires, can result in nausea and dizziness, the control room and the adjacent security central alarm station were evacuated as a precautionary measure. Upon exiting the control room, operators continuously monitored the control board through windows in the viewing area located immediately outside the control room. Operators were not prevented from reentering to perform timely actions if they had been required. The control room ventilation system was used to remove the Halon, the air was sampled and the control room reoccupied in approximately 45 minutes. No personnel injuries were sustained. Subsequent testing confirmed that the light from the camera flash affected a light sensitive circuit (EPROM) located inside the Halon control panel which initiated the actuation of the system without any time delay. Corrective action consisted of installing a protective cover over the EPROM window and evaluating other systems that use EPROM circuits. This event was reported as an Unusual Event and is being documented as a voluntary LER.
2131997014 | Haddam Neck | 08/08/1997 | 09/05/1997 | 9709100214 | <strong>ESF Actuation Due to Deenergiziation of High Containment Pressure Actuation Circuits</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1997, at approximately 0300 hours, with the plant in a permanently defueled condition, control room operators discovered the high containment pressure (HCP) relays in the tripped condition. At that time operators assumed that the relays had been placed in this position as part of a planned evolution. However, following further review, it was believed that the relays were inadvertently actuated on July 30, 1997 and therefore this event was reported on August 9, 1997, at approximately 1145 hours, as an Engineered Safety Feature (ESF) actuation. Although it was an invalid actuation and the system is not required with the plant in this mode, the event was deemed reportable since one or more containment isolation valves may have closed as a result of the HCP signal. The cause of the event was operator error. The on-shift crew was turning off circuits to equipment no longer in service which included the vital 120V AC circuits powering the high containment pressure circuits. Deenergization of the HCP circuits resulted in actuation of the HCP relays. Corrective action consisted of reemphasizing to Operations Department personnel the expectations of management for performing non-routine operational tasks and counseling the individuals involved in de-energizing the circuits.
2131997015 | Haddam Neck | 08/13/1997 | 09/12/1997 | 9709170039 | <strong>Functional Testing Radiation Monitoring System Not Performed as Defined in Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1997, with the plant permanently shutdown and defueled, it was concluded that the test method for performing the quarterly channel functional test of the Radiation Monitoring System (RMS) did not meet the Technical Specification definition of an Analog Channel Operational Test (ACOT). An ACOT is defined as the injection of a simulated signal into the channel as close to the sensor as practicable to verify operability of alarm, interlock and/or trip functions. During a recent effort to upgrade the RMS program it was noted that the RMS functions were being tested by manually lowering or raising the alarm setpoint to actuate the subject alarms. This is how the ACOT has been done ever since 1985 when the Haddam Neck plant started performing channel functional tests of the RMS. The cause of the event was a lack of understanding of the definition of ACOT (previously a channel functional test) which resulted in the failure to adequately incorporate Technical Specification surveillance requirements for the RMS. Immediate corrective action was to verify that recent testing of those RMS channels still required for the defueled condition provided sufficient overlap to satisfy the requirements of the ACOT. Long term corrective action is to revise the appropriate RMS surveillance procedures) prior to the next quarterly test to ensure they meet the definition of ACOT.
2131997016 | Haddam Neck | 08/25/1997 | 01/25/1999 | 9902020123 | <strong>Negative Pressure Not Maintained in Spent Fuel Building as Required by Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1997, with the plant permanently shut down and defueled, while preparing to perform air flow testing, a positive pressure was observed in the spent fuel building (SFB) following startup of the SFB supply fan. The SFB design basis states that the design flow of the exhaust unit exceeds the supply capacity maintaining a small continuous air infiltration into the SFB to prevent release of contamination from the building. Since the supply flow exceeded the exhaust flow from the building, this continuous infiltration was not met. Testing was conducted to determine the cause of this condition (i.e., whether the supply fan is supplying greater than design flow or the exhaust fan is exhausting less than design flow). It was noted that a positive building pressure only occurred while the SFB supply fan was operating. Since the SFB supply fan is required to be shutdown during fuel movement or crane operation with loads over the storage pool, a positive pressure was not experienced during the time the fuel storage building air cleanup system was required to be operable by the Technical Specifications. This event is reportable under 10CFR50.73 (a) (2) (ii) (B) since the system was outside its design basis. This supplemental LER details the test results, cause of the event and associated corrective actions.
2131997017 | Haddam Neck | 09/24/1997 | 11/18/1997 | 9711250141 | <strong>Plant Related Radioactivity Found in Landfill Soil Outside of Radiological Controlled Area - Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>Surveys performed in July 1997, in support of decommissioning site characterization activities, identified three locations of detectable plant related radioactivity (Cs-137 and Co-60) in an on-site landfill area. These locations are isolated to approximately a 15x15 meter area within the landfill, located approximately 3/4 of a mile east of the protected area within the owner controlled area. Information obtained from an ongoing historical site assessment has determined that this area was used for construction spoils as part of onsite construction activities. Based on present knowledge, levels of radioactive materials have not exceeded ten times 10CFR20, Appendix C values. Also, the potential doses calculated for this event do not exceed the regulatory limits set by 10CFR20.1302. Although the levels do not meet reportability criteria, on September 24, 1997 it was decided to conservatively submit this voluntary LER to document the discovery of this condition. Access to the area is controlled and has been secured with a fence with a locked gate and the area has been posted as a radioactive materials area. Plans are to further characterize the affected and surrounding areas for radioactivity. Remediation will be performed commensurate with the radiological hazard identified.
2131997018 | Haddam Neck | 10/03/1997 | 12/08/1998 | 9812150113 | <strong>Spent Fuel Building Exhaust Fan Flow Found Below Design During Testing</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1997, with the plant permanently shut down and defueled, air flow testing of the Spent Fuel Building (SFB) Ventilation System indicated that the SFB exhaust fan did not meet its design basis of exhausting 13,000 cfm when aligned to bypass the HEPA and charcoal filters. The fan exhausted approximately 11,500 cfm with one Primary Auxiliary Building (PAB) purge fan operating. When two PAB purge fans were operating, the SFB exhaust fan flow rate was approximately 6,500 cfm. The cause of the low SFB exhaust flow is a higher than expected pressure in the PAB exhaust ductwork. This is the ductwork into which the SFB exhaust discharges. The higher pressure is a result of a PAB purge fan modification in 1974 which replaced the original PAB fans with higher capacity fans. The original fans each had a capacity of approximately 35,000 cfm. The replacement fans are rated for 52,000 cfm each. The cause of this event is personnel error, in that the modification was not adequately designed or tested. Long term corrective action was to reduce the SFB supply fan flow and establish a design flow range for the exhaust fan. The purpose of this supplemental report is to provide information on the corrective action that has been implemented.
2131997019 | Haddam Neck | 08/08/1997 | 11/17/1997 | 9711210299 | <strong>Compensatory Sampling Frequency Exceeded with Radiation Monitoring System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1997, with the plant permanently defueled, a review of the plant's Technical Specifications by Chemistry personnel determined that, with the radiation monitoring system out of service (February 6, 1997 to July 1, 1997), sampling of gaseous effluent and service water effluent had not been performed within the required 12 hour frequency. Samples were obtained twice a day throughout the time frame the radiation monitors were out of service, however, on several occasions, the samples obtained exceeded the 12 hour requirement. The results of samples taken for the time period were within Technical Specification release limits. The cause of the event was personnel error due to an incorrect interpretation of the Technical Specifications. Chemistry personnel were under the impression that a twenty five percent maximum allowable extension was available to implement the action statement. Chemistry personnel were instructed that future compensatory sampling shall be conducted within the time frame required by LCO action statements and that the 25 percent allowable extension does not apply. This event was determined reportable on August 8, 1997, however, an LER was not issued until now due to personnel error in processing reportability evaluations.
2131997020 | Haddam Neck | 11/17/1997 | 12/16/1997 | 9712230059 | <strong>Radioactive Effluent Dose Calculations Not Performed Within Required Frequency</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1997, with the plant permanently defueled, a review of the plant's radioactive effluent dose Technical Specifications by Chemistry personnel determined that the surveillance frequency of once per 31 days for calculating radioactive effluent dose values had been exceeded on several occasions during 1997. Immediate corrective actions were to review the 1997 dose calculations and applicable Technical Specification requirements. All calculations have been performed and reviewed for the affected time period and all results were found to be well within the requirements of the Technical Specifications. The apparent cause of this event was procedure inadequacy. Additional causal factors which contributed to this event include a weak surveillance tracking program for dose calculations, personnel ownership and personnel turnover. Personnel involved were counseled on the importance of complying with the requirements of the Technical Specifications. Chemistry procedures will be revised to incorporate the lessons learned and training will be provided on the revised procedures. The surveillance tracking process for monthly dose calculations will be enhanced.
2191997001 | Oyster Creek | 01/03/1997 | 01/31/1997 | 9702070088 | <strong>Seven Drywell Penetrations Do Not Meet the Requirements Described in Generic Letter 96-06</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1997, during a review as requested by Generic Letter (GL) 96-06, 'Assurance of Equipment Operability and Containment Integrity During Design Basis Accident Conditions', seven penetrations in five systems did not meet the requirements as described in GL 96-06. Under the postulated conditions contained in GL 96-06, these seven penetrations are only required for containment integrity. An analysis was performed of each penetration while isolated. The analysis modeled the effects on internal fluid and piping in response to an external ambient temperature increase. The results revealed that although the piping did not meet the design requirements, the postulated pressures did not exceed ASME Section III, Appendix F criteria for piping. Additionally, the potential effects on the respective isolation valves were considered. A catastrophic failure of the valves is not considered credible. Therefore containment integrity for the penetration was maintained and the safety significance of this discovery is considered minimal. The cause for this condition was that previous analyses were performed without using the more conservative assumptions described in GL 96-06. Operability determinations were performed and further evaluations are ongoing to determine the need for modifications or procedural revisions.
2191997002 | Oyster Creek | 02/28/1997 | 03/27/1997 | 9704080248 | <strong>Reactor Boiling Vent Radiation Monitor Setpoints Exceed Technical Specification Limit Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1997, during calibration of the Reactor Building Ventilation Exhaust Radiation monitors, the trip setpoints of the monitors, which initiate a Reactor Building Ventilation Isolation and start the Standby Gas Treatment System, were inappropriately adjusted to values higher than allowed by Technical Specifications. This condition was not discovered until February 28, 1997. The safety significance of this event is considered minimal because the Reactor Building Isolation and Standby Gas Treatment System initiation would still have occurred, and offsite dose rates would still have been maintained well below 10CFR20 limits. The root cause of this event is personnel error. Corrective actions include resetting the monitors to the proper setpoint, verification that other improper calibrations had not been performed, and refresher training for all Instrument and Controls technicians.
2191997003 | Oyster Creek | 03/11/1997 | 04/10/1997 | 9704150235 | <strong>Suppression Pool Bypass Flow Path Created During Preventive Maintenance Due to Inadequate Safety Review</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 11, 1997, while post maintenance testing was in progress on torus spray valve V-21-18, operations personnel identified that the pressure suppression function of primary containment had been inadvertently degraded. By opening valve V-21-18, a flow path was created from the drywell to the torus airspace which would have bypassed the suppression pool in the event a loss of coolant accident (LOCA) occurred. This could result in inadequate steam suppression from the drywell and over-pressurization of the torus. The condition existed for a total of about ten minutes, therefore, exposure to the risk was minimal. The cause of this event has been determined to be an inadequate safety review of the change of PM 9441M from an outage task to an on-line task. This resulted in inadequate precautions in the job order and maintenance procedures that controlled the evolution. Upon discovery, shift supervisors notified affected operations personnel that when a torus spray valve is cycled, the associated test valve must be closed. A process will be developed and implemented to allow review of work activities and preparation of switching orders by operations personnel other than the on-shift control room staff. The process for revising PMs will be reviewed and revised to address potential impacts on performing a PM when the plant is in a different mode than specified.
2191997004 | Oyster Creek | 03/12/1997 | 04/25/1997 | 9705020266 | <strong>Reactor Water Cleanup Valve May Not Operate During a Line Break Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>During a detailed review of motor operated valves for periodic verification in response to Generic Letter 96-05, it was discovered that reactor water cleanup valve V-16-2 was being used to fill and vent the cleanup system while the reactor is at power and operating pressure. If V-16-2 is open and the downstream pipe were to break, V-16-2 would be required to close against normal reactor operating pressure. Delta pressure (delta p) calculations for V-16-2 did not address this event. Therefore, the valve was not set up to close against reactor pressure of 1020 psig. This oversight is attributed to personnel error in that the prior review missed the use of valve V-16-2 during power operation. V-16-2 was declared inoperable and deactivated in the closed position to prevent it from being opened with reactor pressure greater than 125 psig. AR engineers will be informed of this event and the importance of design verification through required reading of this LER.
2191997005 | Oyster Creek | 04/08/1997 | 05/08/1997 | 9705140159 | <strong>Standby Liquid Control System Sample Reporting Requirements Not Met Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1997 it was identified that the most recent Standby Liquid Control System (SLCS) sodium pentaborate solution Boron-10 (B-10) enrichment surveillance determining the B-10 enrichment solution results were not received within 30 days of sampling. Technical Specification Section 4.2.E.5 states, 'If not received within 30 days, notify NRC (within 7 days) of plans to obtain test results.' This notification was not made. The cause of this event was determined to be an inadequate procedure in that Technical Specification requirements were not included in permanent plant documents. The safety significance of this event is considered minimal. When the results were received, the B-10 enrichment atom percent was within specification. Therefore, the SLCS was capable of performing its intended function at all times. Corrective actions include revising appropriate plant documents to reflect the Technical Specification requirement.
2191997006 | Oyster Creek | 04/19/1997 | 05/19/1997 | 9705270205 | <strong>Reactor Shutdown Required by Control Rod 5% Scram Times due to Valve Diaphragms</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1997, control rod scram time testing was performed on a reference sample of seven control rods for Scram Solenoid Pilot Valve (SSPV) performance monitoring based on BWR Owners' Group recommendations. The tests revealed that the 5% scram insertion times had increased over previous tests, and the average 5% insertion time for these seven rods exceeded complete core average Technical Specification time limit. The reactor was shutdown to address the degraded performance. The apparent root cause of this event was the sticking of the Viton A diaphragms in the SSPVs. The safety significance of this event was determined to be minimal, because the small delay in 5% insertion time has a negligible effect on design basis accident and transient analyses. While the reactor was shutdown, the diaphragms for all SSPVs were replaced with a new Viton 515 A-B material designed to prevent the sticking experienced with Viton A. Subsequent scram time tests have shown a marked improvement in 5% insertion time. An evaluation will be performed to determine the need for a new test program on the SSPVs.
2191997007 | Oyster Creek | 05/31/1997 | 09/19/1997 | 9709300350 | <strong>Inadvertent Initiation of Diesel Generator 2 During Surveillance Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1997, while attempting to perform a post maintenance test to demonstrate operability of an emergency diesel generator (EDG) the wrong EDG was manually started. This report is being submitted voluntarily to document that occurrence. Technical Specifications require a daily operability test of the operable EDG when one EDG is out of service. Technical Specifications also require that when one EDG is inoperable none of the engineered safety features normally fed by the operational EDG may be out of service. Prior to the inadvertent start of the No. 2 EDG, all maintenance activities and load checks of the No 1 EDG had been successfully completed and it was awaiting final testing to demonstrate operability. Additionally, since the No. 2 EDG and all its associated engineered safety features were operable during the time of this occurrence, the safety significance of this event is considered minimal.
2191997008 | Oyster Creek | 06/27/1997 | 07/25/1997 | 9708050158 | <strong>Intermediate Range Monitor System Contacts in the Reactor Protection were not Tested by Procedure</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1997, at approximately 1100 hours, it was determined that certain IRM Upscale Scram and IRM Range 10 interlock relay contacts associated with MSL Low Pressure MSIV Closure were not functionally tested as required by Technical Specifications. All eight IRMs were declared inoperable. As the plant was in the "RUN" Mode neither of these RPS functions was required to be operable by Technical Specifications. The testing procedure was revised to require contact testing. Contact operability was verified and the IRMs were declared operable on July 7, 1997 at approximately 1500 hours. The root cause of this event was inadequate testing procedures. The safety consequence of this event is considered minimal. The IRM scram and associated interlock features were declared inoperable solely due to a inadequate surveillance. During past surveillance testing, each relay was verified to operate correctly with the exception of the identified contact(s), and subsequent revised testing verified the contacts did function properly.
2191997009 | Oyster Creek | 07/09/1997 | 08/08/1997 | 9708140209 | <strong>Radiation Monitor Setpoints Exceed Technical Specification Limit Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 9, 1997, during calibration of the reactor building ventilation exhaust radiation monitors, the trip setpoints of the monitors which initiate a reactor building ventilation isolation and start the standby gas treatment system were inappropriately adjusted to values higher than allowed by Technical Specifications. This condition existed for approximately 1.5 hours. The safety significance of this event is considered minimal because the reactor building isolation and standby gas treatment system initiation would still have occurred and offsite dose rates would still have been maintained well below 10 CFR 20 limits. The root cause of this event is personnel error. Corrective actions include resetting the monitors to the proper setpoint, verifying that other calibrations had been properly performed, self-checking training for instrument and controls technicians and evaluating procedure improvements and a setpoint change.
2191997010 | Oyster Creek | 08/01/1997 | 09/02/1997 | 9709090113 | <strong>Manual Reactor Scram, ESF Actuation and Design Deficiencies Noted As a Result of Generator Exciter PM</strong><br /><i>Abstract:&nbsp;</i>A manual scram was initiated in response to sparking in the main generator exciter commutator. The sparking was caused by a brush failure due to the use of incorrect parts. As a result of a low voltage condition, the emergency buses separated from off-site power and were subsequently energized by the emergency diesel generators. Several engineered safety features actuated. The two control rod drive pumps failed to start as designed. During a review of the transient, it was identified that the startup transformer voltage regulators were set to regulate voltage outside the plant's design basis as described in the degraded grid voltage study. A design defect in the control rod drive pump breaker control logic was also identified. Corrective actions include repair of the exciter, resetting the transformer voltage regulators and adding a time delay to the control rod drive pump start sequence.
2191997011 | Oyster Creek | 08/15/1997 | 09/12/1997 | 9709230005 | <strong>Isolation Relay Contacts in the Isolation Condenser System Were Not Testing by Procedure</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1997, at approximately 1100 hours, as part of the evaluation to address Generic Letter 96-01 "Testing of Safety Related Logic Circuits", it was determined that certain Isolation Condenser isolation relay contacts were not functionally tested as required by Technical Specifications. The Isolation Condensers were declared inoperable and a 30 hour shutdown action statement was initiated. The testing procedure was revised to incorporate the required contact testing. Contact operability was verified and the A Isolation Condenser was declared operable on August 16, 1997 at approximately 0140 hours. The 30 hour shutdown requirement was replaced by a seven day shutdown requirement. The B Isolation Condenser was subsequently tested and declared operable on August 16, 1997 at approximately 1300 hours and all shutdown requirements were exited. The root cause of this event was determined to be inadequate testing procedures. The safety consequence of this event is considered minimal. The A and B Isolation Condensers were declared inoperable solely due to an inadequate surveillance. During past surveillance testing, each relay was verified to operate correctly with the exception of the identified contact(s). Subsequent revised testing verified the contacts were operable.
2191997012 | Oyster Creek | 09/16/1997 | 10/15/1997 | 9710200242 | <strong>Setpoint Found to be Non-Conservative due to Failure to Include Possible Uncertainties</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1997, it was determined that the current procedural setpoints for the Reactor Building Ventilation and Reactor Building Operating Floor monitors were not set conservatively enough to preclude exceeding the Technical Specification Limits due to possible uncertainties. The root cause of this occurrence has been determined to be that the previous actuating setpoints of 13 mr/hr and 70 mr/hr apparently did not include adequate margin to compensate for uncertainties included in the current calculation. Corrective actions included declaring the monitors inoperable, manually initiating the Standby Gas Treatment System, and revising the procedural setpoints. A program to identify or develop the bases for safety related instrument setpoints, is presently underway. The safety significance of this event is considered minimal because even if the Standby Gas Treatment System did not initiate, the offsite doses would still have been maintained well below 10 CFR 20 and 10 CFR 100 limits.
2191997013 | Oyster Creek | 10/20/1997 | 11/19/1997 | 9712020163 | <strong>Reactor Building Ventilation Ductwork May Not Meet Its Seismic Design Basis Since Original Construction</strong><br /><i>Abstract:&nbsp;</i>The design of the reactor building ventilation system ductwork comprising the secondary containment boundary may not be in compliance with the requirements of its intended function. It is, however, installed in accordance with the original procurement specification for equipment installation. The functions of the ductwork are to provide a conduit for normal reactor building ventilation and remain intact when secondary containment integrity is required. The specific issue relates to the ductwork's ability to withstand the effects of a seismic event. An operability review in conjunction with a field walkdown was performed. The results of the operability review concluded that there is reasonable assurance that the ductwork will continue to perform its function following an operating basis seismic event. GPU Nuclear also received information from a seismic consultant that supported this conclusion. Seismic verification walkdowns are in progress to verify seismic adequacy of the existing installations while further reviews of design basis information are being conducted.
2191997014 | Oyster Creek | 10/21/1997 | 11/19/1997 | 9712020160 | <strong>Suppression Pool Bypass Path Created While Inerting/De- inerting Drywell and Torus Due To Inadequate Procedure Review</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1997, while reviewing industry events, it was discovered that a suppression pool bypass leak path existed during purging and venting of the primary containment. Two operating procedures allowed venting and purging of the torus and dry-well simultaneously. If a LOCA were to occur during this time, a pathway for steam to bypass the suppression pool was created. Calculations indicated that the allowable bypass area was exceeded but, in the unlikely event of a LOCA, the peak torus and dry-well pressure would not increase. The cause of this event was determined to be inadequate procedure review. Upon discovery, tags were hung in the control room to prevent operators from opening both torus and drywell purge or vent valves simultaneously. The operating procedures will be revised to preclude simultaneous opening of the purge and vent valves. In addition, the system performance team will consider the development of an interlock to prevent recurrence. The system performance team will also determine if other bypass paths exist. This situation will be incorporated into operator requalification training.
2191997015 | Oyster Creek | 12/04/1997 | 01/02/1998 | 9801130374 | <strong>Static Time Delay Units Not Mounted in Conformance with Seismic Qualification Criteria due to Improper Installation</strong><br /><i>Abstract:&nbsp;</i>On Dec. 4, 1997 it was discovered that some of the mounting screws were missing from a number of static time delay units (STDUs) in unit substation switchgear cubicles. Some of these cubicles are associated with safety related loads. This is contrary to the configuration on which their seismic qualification was based. This condition was caused by improper installation with contributing factors of panel configuration, lack of a questioning attitude, and lack of sensitivity to seismic mounting concerns. In the event of a seismic event, reliability of containment heat removal capability could have been reduced. Redundant components were available to accomplish the heat removal function and emergency operating procedures provide alternate methods even in the event redundant components were to fail as well. The STDUs have been properly mounted restoring operability to affected equipment. Additional information and guidance relating to seismic mounting requirements will be contained in future job orders (both preventative and corrective maintenance) and required reading will be assigned for appropriate personnel.
2191997016 | Oyster Creek | 12/12/1997 | 01/12/1998 | 9801220232 | <strong>Monitors May Not Have Operated For the Required Time due to an Inadequate Calculation</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1997, it was determined that an omission in a design basis calculation would have prevented the H sub 2 O sub 2 system from operating for the full 48 day post LOCA design interval if called upon. This is a condition outside of the design bases. The cause of the omission was a failure to allow for sufficient margin in the low pressure reagent gas setpoint to allow for increasing gas flow rates over the life of the analyzer. Corrective action was taken to increase the low pressure limit of the reagent gases and ensure that the installed gas bottles had sufficient pressure. This omission was discovered as part of a program to verify and evaluate existing calculations. The scope, determination, and implementation of this program are ongoing. The primary containment atmosphere is monitored and oxygen is maintained at a level which would preclude any hydrogen/oxygen reaction in a post LOCA environment.
2201997001 | Nine Mile Point 1 | 02/06/1997 | 03/10/1997 | 9703170139 | <strong>Pipe Supports Outside Seismic Design Basis Because of Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1997, with Nine Mile Point Unit 1 (NMP1) in the RUN mode and reactor thermal power at approximately 100 percent, Niagara Mohawk determined that 16 pipe supports in the Reactor Building Closed Loop Cooling System (RBCLC) inside the drywell did not meet the design basis criteria for seismic loads as descried in the Updated Final Safety Analysis Report (UFSAR). This deficiency was identified as a result of a design Analysis being performed as part of the corrective actions previously identified in voluntary Licensee Event Report (LER) 96-09, concerning potential overstressed pipe supports in RBCLC. The apparent cause of this event is a design deficiency resulting from the design methods used in the original design of RBCLC piping and supports. The RBCLC system has been determined to be operable. Engineering Analysis had demonstrated that the piping will remain intact and capable of performing its safety function after a design basis seismic event. The affected supports will be modified during the next refueling outage.
2201997002 | Nine Mile Point 1 | 03/13/1997 | 04/17/1997 | 9704290004 | <strong>Shroud Repair Anomalies</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1997, it was determined that one Core Shroud Repair Assembly was degraded. Subsequent inspections revealed that each Core Shroud Assembly had experienced some degradation. The cause of the degradation has been determined to be that assumptions used in the design did not appropriately account for installation tolerance and the potential for tie rod subcomponent damage due to this unanticipated movement. NMPC intends to modify and reinstall the Core Shroud Stabilizer Assembly, and to perform a re-inspection coincident with the core shroud vertical weld re-inspection schedule. NRC approval of the repair assembly modification is required prior to unit restart.
2201997003 | Nine Mile Point 1 | 04/03/1997 | 05/05/1997 | 9705140247 | <strong>Reactor Water Cleanup Auxiliary Pump Rooms Not Monitored By Thermal Sensors</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1997, Niagara Mohawk Power Corporation (NMPC) determined that thermal sensors used to detect line breaks were not appropriately located in the RWCU system auxiliary pump room as described in Section 10.B.3 of the Nine Mile Point Unit 1 (NMP1) Updated Safety Analysis Report (USAR). The cause of this event is that the original designers of the plant in the 1960s did not locate thermal sensors in the reactor water cleanup (RWCU) auxiliary pump room. To correct the deviation, thermal sensors have been installed in the RWCU system auxiliary pump room.
2201997004 | Nine Mile Point 1 | 05/13/1997 | 06/12/1997 | 9706250150 | <strong>10CFR50 Appendix R Section III J Lighting Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1997, Niagara Mohawk Power Corporation (NMPC) determined that Nine Mile Point Unit 1 (NMP1) was not in compliance with the requirements of 10CFR50 Appendix R, Section III.J. Deficiencies were identified during NMPC's evaluation of NRC Information Notice (IN) 95-36 "Potential Problems With Post-Fire Emergency Lights" The cause of this event has been determined to be ineffective change management in that the development of safe shutdown procedures and physical changes to the plant were not properly evaluated for compliance to 10CFR50 Appendix R, Section III.J requirements. Initial compensatory actions include utilization of hand held lights and installation of portable eight hour capacity lights in critical areas of the plant. Subsequently, installation of permanent eight hour capacity lights has begun.
2201997005 | Nine Mile Point 1 | 06/12/1997 | 07/14/1997 | 9707240111 | <strong>Potential Pressure Locking of Core Spray Valves During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1997, Niagara Mohawk Power Corporation (NMPC) determined that during surveillance testing of the core spray system containment isolation valves, a pressure locking condition could occur which would prevent the core spray system from performing its safety function. This discrepancy was discovered during NMPC's review of design documents for closure of the Nine Mile Point Unit 1 (NMP1) Generic Letter (GL) 89-10 Program. This reportable condition was caused by an original design deficiency in that the design did not consider this failure mode. Additionally, previous evaluations of pressure locking susceptibility performed in response to NRC Information Notice (IN) 92-26, "Pressure Locking of Motor Operated Flexible Wedge Gate Valves" and GL 95-07, "Pressure Locking and Thermal Binding of Safety Related Power Operated Gate Valves," failed to reconcile this design deficiency. Corrective actions included modification of the valves to preclude pressure locking.
2201997006 | Nine Mile Point 1 | 06/13/1997 | 07/14/1997 | 9707240089 | <strong>Technical Specification Required Shutdown Because of Loss of Drywell Floor Drain Leakage Monitoring Ability</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1997, at 0755 hours, with Nine Mile Point Unit 1 (NMP1) in the RUN mode and reactor thermal power at approximately 100 percent, Niagara Mohawk Power Corporation (NMPC) lost the ability to monitor the reactor coolant system leakage via the Drywell Floor Drain Monitoring System. This required entry into the action statement for Technical Specification (TS) 3.2.5, which required the reactor to be in cold shutdown within 24 hours. At 0718 hours on June 14, 1997, NMP1 entered the cold shutdown condition. The immediate cause of the loss of the ability to monitor the reactor coolant system leakage via the Drywell Floor Drain Monitoring System was the securing of the drywell floor drain outboard isolation valve in accordance with TS 3.3.4b after the inboard isolation valve was declared inoperable. NMPC repaired the inoperable inboard isolation valve and restarted NMP1 on June 20, 1997.
2201997007 | Nine Mile Point 1 | 08/15/1997 | 09/15/1997 | 9709240147 | <strong>Potential Control Room Emergency Ventilation System Operation Outside the Design Basis due to Inadequate Evaluation</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1997 at 1600 hours, the Nine Mile Point Unit 1 (NMP1) staff identified a reportable condition whereby the Control Room Emergency Ventilation (CREV) system would not have been able to perform its design function. Specifically, the Control Room Smoke Purge system has been operated at times when the CREV system was required to be operable. Per design, the Smoke Purge system does not have an automatic isolation feature. If the Smoke Purge system was in operation when an initiation of the CREV system occurred, the CREV system would not have been able to maintain the design requirements for Control Room habitability. The root cause of the event is inadequate evaluation (on two occasions) of the interface between the Smoke Purge system and the CREV system. The Control Room Smoke Purge system was operated for reasons other than smoke removal from a fire and operation in this manner was not considered for impact on Technical Specification (TS) operability of the CREV system. The implementation of the modification process failed to identify these deficiencies both in 1980 and again in 1984. The immediate corrective actions included placing administrative controls on the Smoke Purge system to limit its operation. The procedures controlling operation and testing of the system will be revised to restrict the operation of the system to its intended design function (smoke removal) and to ensure that the system is only tested when the CREV system is not required to be operable. In addition, selected modifications will be reviewed to determine if similar interface problems exist.
2201997008 | Nine Mile Point 1 | 08/28/1997 | 09/26/1997 | 9710030188 | <strong>Non Conservative APRM Gain Adjustments Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1997, with Nine Mile Point Unit 1 (NMP1) in Operational Condition (OC) 1 (Power Operation) and reactor thermal power at 100 percent, it was determined that NMP1 had operated in violation of Technical Specification (TS) 2.1.2a during previous startups and other power maneuvers. This violation occurred since Average Power Range Monitors (APRM) were allowed to be set to two percent lower than required by TS 2.1.2a, due to the improper application of TS Table 3/4.6.2a note m. The root cause of this event is inadequate technical review. No immediate corrective actions were required since NMP1 operating conditions requiring the APRM gain adjustment to satisfy TS 2.1.2a were not present at the time of discovery. Procedures N1-RESP-1, N1-REP-12, N1-REP-12A and N1-OP-43A were revised to be in compliance with TS.
2201997009 | Nine Mile Point 1 | 09/03/1997 | 10/03/1997 | 9710140233 | <strong>Technical Specification Violation Due to System Inoperability Caused by Leakage Through Drain Valves</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1997, during corrective maintenance on the channel 12 reactor water level reference leg back-fill system, a divergence between the channel 11 and channel 12 GEMAC narrow range level indicators was observed in the control room. The channel 12 instrumentation and the systems affected by it were declared inoperable, which resulted in multiple Technical Specification (TS) Limiting Conditions for Operation (LCO) entries. Troubleshooting revealed that the level divergence was due to water loss from the instrument column 12 reference leg through system drain valves that were not tightly closed. Since this condition has existed since startup from the last refueling outage in May 1997, the LCO action times for the affected systems were exceeded. The cause of this event was leakage through the instrument system drain valves. The exact cause of the leakage is unknown, but most likely is either inadequate force applied to tightly close the valves or valve degradation. When additional force was applied to the valves, the leakage stopped. The drain valves will be inspected to determine if any degradation exists and repairs will be completed, if required. Procedure changes will be implemented to heighten awareness of drain valve operation and leakage on instrumentation. A procedure will be developed to periodically check the instrumentation system for leakage. Training will be provided to Operations, Engineering and Technical Support personnel regarding this event.
2201997010 | Nine Mile Point 1 | 09/16/1997 | 01/30/1998 | 9802130023 | <strong>Technical Specification Required Shutdown Due to Emergency Cooling Condenser Tube Leak</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1997, Nine Mile Point Unit 1 (NMP1) personnel observed increased steaming from the Emergency Cooling (EC) Loop 12 vent to atmosphere. On September 12, 1997, operators at NMP1, based upon elevated EC loop temperatures and vent radiation monitor readings, isolated Loop 12 and entered Technical Specification (TS) 3.1.3.b. On September 15, 1997, NMP1 initiated a shutdown to inspect and test the EC condensers. Subsequently, it was determined that the EC repairs could not have been completed within the allowed TS Limiting Condition for Operation (LCO) time, and that the event was therefore reportable as a TS required shutdown. Inspection and testing revealed that tube cracking indications were present in all four EC condensers. The root cause of the EC condenser tube failures has been determined to be an original design deficiency that failed to preclude exposing the upper tubes to a continuous steam environment. This condition subsequently resulted in tube leakage due to thermal fatigue and transgranular stress corrosion. EC Loop 12 was manually isolated to secure the steaming from the loop vent to atmosphere and NMP1 was subsequently shutdown to determine the cause of the steaming and to affect repairs. The tube bundles for each of the EC condensers were replaced prior to returning NMP1 to service. In addition, a modification was made to the system to maintain water level above the tube bundles.
2201997011 | Nine Mile Point 1 | 09/30/1997 | 10/30/1997 | 9711060135 | <strong>Previous Plant Shutdown in Violation of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1997, Niagara Mohawk Power Corporation (NMPC) determined that on September 3, 1992, Nine Mile Point Unit 1 (NMP1) had placed the Mode Switch in REFUEL at temperatures in excess of 212 Degrees F, and on previous occasions were in violation of the Technical Specification (TS) Definition 1.1c, Refuel. For the period from initial operation of NMP1 through September 3, 1992, personnel inappropriately determined that placing the mode switch in REFUEL with all rods inserted to Position 00 was more appropriate than leaving the mode switch in STARTUP during the period of cool down to less than 212 Degrees F, and it avoided introducing an unnecessary scram from the SHUTDOWN position. The procedure was corrected prior to performing a normal shutdown on September 15, 1997.
2201997012 | Nine Mile Point 1 | 10/16/1997 | 11/14/1997 | 9711250140 | <strong>Additional 10CFR50 Appendix R Section III.J Lighting Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1997, Niagara Mohawk Power Corporation (NMPC) identified an area of Nine Mile Point Unit 1 (NMP1) which does not meet the requirements of 10CFR50 Appendix R Section III.J Emergency Lighting. This area was identified during a design bases review of the NMP1 Updated Final Safety Analysis Report (UFSAR) Section 10B. The cause of this event has been determined to be a cognitive personnel error which resulted in an analysis deficiency in Fire Protection Engineering Evaluation (FPEE) 1-90-014, Revision 1. Eight hour capacity lights will be installed prior to startup from the current forced outage.
2201997013 | Nine Mile Point 1 | 11/10/1997 | 12/10/1997 | 9712170187 | <strong>Engineered Safety Feature Actuation During Calibration Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1997, at approximately 1400 hours, with Nine Mile Point Unit 1 (NMP1) in cold shutdown, an isolation of the drywell vent and purge lines was initiated while performing a calibration of stack gas radiation monitor RN-10B. The calibration was being performed following troubleshooting and repairs to restore operability. A higher activity gamma source was incorrectly used for the calibration procedure, and when placed in the vicinity of the detector to be calibrated, the activity of this source was sensed by the detectors for both radiation monitors RN-10A and RN-10B, causing a hi-hi radiation alarm of both monitors. The hi-hi radiation signals resulted in an automatic isolation/Engineered Safety Feature (ESF) actuation of the drywell vent and purge valves. The root cause of the event was personnel error due to failure to properly self-check. The chemistry technician failed to ensure that he retrieved the correct radioactive source for the calibration procedure. The calibration procedure was immediately stopped. The cause of the ESF actuation was verified, the signal was reset and the drywell vent and purge valves were reopened. An additional pre-job brief was held with all the involved parties and the primary calibration was successfully completed with direct supervision. The chemistry technician involved received disciplinary action. This event will be reviewed with all NMP1 chemistry personnel.
2201997014 | Nine Mile Point 1 | 11/25/1997 | 02/06/1998 | 9802200351 | <strong>Vent and Purge System Isolation During Troubleshooting Due to Insufficient Precautions Applied</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1997, while performing troubleshooting on the Nine Mile Point Unit 1 (NMP1) stack gas radiation monitor (RAM-112-08A), an unexpected isolation of the containment vent and purge system was experienced. The design function of RAM-112-08A is to provide indication and alarm only, but due to troubleshooting activities and a system interaction due to an undetected equipment problem, an isolation occurred during troubleshooting efforts on the radiation monitor. The root cause of this event has been determined to be insufficient precautions applied during troubleshooting activities. A contributing cause was equipment degradation. The cause of the Engineered Safety Feature (ESF) actuation was verified, the signal was reset and the drywell vent and purge valves were reopened. The degraded power supply was replaced, and RAM-112-08A was tested and returned to service. The appropriate plant personnel who could encounter similar situations have been briefed on this event. Information about this event has been placed in work history to help ensure that future troubleshooting efforts incorporate adequate precautions to prevent adverse system interactions.
2371997001 | Dresden 2, Dresden 3 | 01/09/1997 | 04/11/1997 | 9704160366 | <strong>Primary Containment Electrical Penetrations Never Subjected to Type B Local Leak Rate Test Due to Break Down of the Modification Process</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At approximately 1300, on January 09, 1997, with Unit 2 operating at 100% power and Unit 3 shutdown for Forced Outage D3F23, a review of the UFSAR and Conax Buffalo electrical penetration assembly vendor manuals determined that there were two Primary Containment boundaries on Unit 2 and two boundaries on Unit 3 which had never been challenged by a Type B Local Leak Rate Test (LLRT). The cause for the omission of these four electrical penetrations from the LLRT program and its associated testing was due to a breakdown in the Modification process. Revisions were made to the applicable Primary Containment Leakage Rate Testing Program procedures to include these electrical penetrations as testable containment barriers and the LLRT basis will be updated. upon completion of procedure revisions, these four electrical penetrations were each given a Type B LLRT. Containment integrity has been intact as demonstrated by successful ILRTs performed at the end of numerous ILRT refuel outages. The safety significance concerning the omission of testing for these four electrical penetrations was minimal.
2371997002 | Dresden 2 | 01/09/1997 | 02/07/1997 | 9702130004 | <strong>Turbine First Stage Pressure Scram Bypass Switches Adjusted Outside Technical Specification Limits Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 09, 1997, Instrument Maintenance technicians performed a surveillance to calibrate the Unit 2 Turbine First Stage Pressure 45 percent Scram Bypass pressure switches. Errors in following the procedure resulted in as-found data being recorded incorrectly. Due to the nature of the errors (trip and reset data reversed), the switches were adjusted incorrectly to a setpoint which exceeded Tech Spec limits by approximately 1 to 2 percent. This condition existed for 4 days until discovered by a subsequent performance of the same surveillance due to a required Setpoint Change. Switches were immediately recalibrated to proper setpoints. During the 4 days the setpoints exceeded Tech Spec limits, a reactor scram would have occurred, but at a higher power than allowed by Tech Specs after a generator load reject or turbine trip. During this period, reactor power level was significantly greater than the trip setpoint, and had a turbine trip occurred, the Reactor Protection System would have performed as designed. Analysis of potential events requiring the trip indicate the safety significance of this event is minimal.
2371997003 | Dresden 2, Dresden 3 | 01/27/1997 | 07/11/1997 | 9707220172 | <strong>Containment Penetrations Outside Design Basis Due to Analysis of Thermally Induced Post-Accident Over- Pressurization</strong><br /><i>Abstract:&nbsp;</i>Between October of 1996 and January of 1997, systems that penetrate containment were reviewed to identify piping that is susceptible to the thermally induced pressurization issue identified in NRC Generic Letter 96-06. Based on the results of the review and subsequent operability determinations, on January 27, 1997 it was determined that the systems identified as susceptible to over-pressurization in post-accident conditions did not account for post-accident pressurization in their original design, and as a result were outside the design basis of the plant. Operability Assessments were performed to document the basis for continued operability of these affected penetrations and systems/components. The systems were determined to be operable but degraded. Permanent correction of the degraded condition will be accomplished by installing over pressure protection or by penetration specific analysis.
2371997004 | Dresden 2 | 02/08/1997 | 03/10/1997 | 9703180004 | <strong>Channel Checks for ATWS Level and Pressure Instruments Performed at Incorrect Frequency due to Personnel Error During the Procedure Review Cycle.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1430 on February 8, 1997, while performing a review of the computerized rounds, Appendix D, HVO Inside Round Logsheet, the program administrator identified that channel check frequencies for the Reactor Level and Pressure failed to meet the minimum frequency stated in the Upgraded Technical Specifications. Though this condition had existed since September 8, 1996, Technical Specification non-compliance did not occur until January 13, 1997, at which time Dresden fully implemented the Upgraded Technical Specifications. The cause of the event was determined to be personnel error in the preparation of the procedural change and during the Technical Review of the procedure revision paperwork. Corrective actions include counseling of all individuals involved with the Appendix D procedure revision, a thorough review of all Operator Rounds was performed finding no additional discrepancies and revision of Appendix D on February 8, 1997, correcting the deficiency.
2371997005 | Dresden 2 | 02/13/1997 | 03/13/1997 | 9703190124 | <strong>High Pressure Coolant Injection Low Flow Setpoint Found Outside Technical Specification Limit Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1997, at 1530 with Unit 2 in mode 1 (Run), while performing the scheduled quarterly Dresden Instrument Surveillance (DIS) 2300-02, High Pressure Coolant Injection Flow Calibration, the High Pressure Coolant Injection (HPCI) Low Flow Switch FS 2-2354, was identified with the trip setpoint below the Technical Specification limit. The cause for the Out-Of-Tolerance (OOT) is setpoint drift. The calibration frequency will be increased during the second quarter, 1997, to obtain additional trend data. The safety significance is minimal because the system would have operated as designed, providing 5600 gpm to the reactor vessel, and the pump's minimum flow requirements would have been satisfied during this system initiation.
2371997006 | Dresden 2, Dresden 3 | 02/26/1997 | 09/12/1997 | 9709170085 | <strong>SRO Absent From the Main Control Room Due to Loss of Focus on Interim Duties.</strong><br /><i>Abstract:&nbsp;</i>At approximately 1945 hours on February 26, 1997 while providing an interim relief for the Unit 3 Unit Supervisor in the Main Control Room, the OOS Supervisor became distracted from his interim duties, resulting in his exit from the Control Room to obtain additional technical documents. His absence was recognized by the Unit 2 Unit Supervisor, who immediately took action to correct the Technical Specification non-compliance. The Unit Supervisors short absence from the Control Room (approximately 6 minutes) had minimal affect on safety. Corrective actions include counseling of the individual and training on the Administrative Section (Section 6) of the Upgraded Technical Specifications. An additional corrective action was specified by the original LER to implement security badge egress control from the Main Control Room. This action was intended to prevent future violation through positive controls, but the complexity of the corrective action prevented timely implementation and consequently the event recurred. As a result, this action has been cancelled. This event was reportable per 10CFR50.73(a)(2)(i)(B), operation prohibited by Technical Specification.
2371997007 | Dresden 2, Dresden 3 | 02/26/1997 | 03/27/1997 | 9704020292 | <strong>LPCI Recirculation Loop Line Break Detection 900 psig Reactor Pressure Permissive Setpoint Set Outside Design Basis Limit Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>During the Dresden Station Key Parameter Screening Review effort, a discrepancy was identified relating to the LPCI loop selection initiation logic setpoint. The UFSAR identifies the design limit for this setpoint as </= 900 psig. Contrary to this, as a result of a personnel error that incorrectly established the design limit as a >/= value, the existing setpoint was calculated and set above the UFSAR limit. The LPCI loop selection logic ensures the LPCI injection flow is directed to an unbroken recirculation pump loop. With the current setting set nonconservative, this function was in question. Therefore, the LPCI injection subsystem was declared inoperable at 1920 hours on February 26, 1997 and a 7 day LCO was entered per Technical Specification 3.5.A.2.b. Immediate corrective action was initiated to revise the setpoint calculation and re-calibrate the pressure switches to be in compliance with the UFSAR limit. The system was restored to operability on March 03, 1997 at 0132 CST. Long term corrective action is in place to improve the quality of calculations performed for the Dresden station. This event was determined to be reportable pursuant to 10CFR50.73(a)(2)(ii)(B). The safety significance concerning the non-conservative setpoint was minimal, based upon completion of an analysis demonstrating that the loop select function would have functioned properly with the as-found setpoints.
2371997008 | Dresden 2, Dresden 3 | 04/10/1997 | 05/09/1997 | 9705140261 | <strong>Unit Shutdown due to Degradation of Auxiliary Switches in 4kV Circuit Breakers Caused by Design/Manufacturing Deficiency</strong><br /><i>Abstract:&nbsp;</i>At approximately 1940 hours on April 10, 1997, with Unit 2 in Mode 1, inspection of the Golden Gate 4kV feed breaker [EB] from Bus 23 to Bus 23-1 revealed that the breaker's Merlin Gerin auxiliary switch mounting plastic had broken, resulting in the switch being detached from its mounting plate. There was no immediate assurance that the switch would have operated properly if the breaker were to be cycled. Also, it was determined that the Merlin Gerin type auxiliary switch is susceptible to cracking of the switch mounting plastic. Cracking of the switch mounting plastic was viewed as a precursor to the switch completely breaking free from the mounting plate. Conservatively, all equipment utilizing the Golden Gate type breaker with a Merlin Gerin auxiliary switch were declared inoperable at 2112 on April 10, 1997. This rendered various systems inoperable, Containment Cooling Service Water (CCSW) [BO] being the most limiting. Shutdown of Unit 2 commenced at 2226 on April 10, 1997. Unit 3 was already in the refueling mode, Mode 5, for a scheduled refueling outage. The root cause of this event is design/manufacturing deficiency of the breaker auxiliary switch. Corrective actions include breaker auxiliary switch inspections, strapping the switch in place to add additional support, and to review the Part 21 for long term repair. This event was determined to be reportable pursuant to 10.CFR50.73(a)(2)(v) and (a)(2)(i)(a). The safety significance was determined to be minimal.
2371997009 | Dresden 2, Dresden 3 | 04/16/1997 | 05/15/1997 | 9705270019 | <strong>Source Range Monitor Surveillance Performed at Incorrect Frequency due to Human Error During Technical Specification Upgrade Project.</strong><br /><i>Abstract:&nbsp;</i>On 4/16/97, while performing a Technical Specification review for the 24 month fuel cycle project, a discrepancy was noted between the Source Range Monitoring System surveillance frequency and the Technical Specification requirement. It was determined that as a result of having the incorrect frequency within the computerized tracking network (Predefines), the Unit 2 Technical Specification surveillance frequency, as listed in Table 4.2.F-1, had been exceeded by thirty-nine days. The cause for the non-compliance was due to personnel performance errors within the surveillance frequency change approval process, which had amended the surveillance frequency of DIS 0700-10, SRM Rod Block Calibration, from quarterly to once every 18 months. As a result of the event, the station will revisit TSUP implementation and assure that the proper surveillance frequencies have been created to meet Tech Spec requirements and assure that the involved individuals understand their responsibilities during task performance. The safety significance of this event is considered minimal. This event is reportable per 10CFR50.73(a)(2)(i)(B), as operation prohibited by Technical Specification.
2371997010 | Dresden 2 | 07/28/1997 | 08/22/1997 | 9708270160 | <strong>Feedwater Transient results in Manual Reactor Scram due to Operating Team Knowledge Weakness and Operator Weakness while performing Manual Level Control.</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1997, with Unit 2 at full power, the 2B RFP recirc valve failed open and a recovery plan was created by the Operating Team to secure and isolate the failed valve. On July 28, 1997, the oncoming Operating Team reviewed Operating procedures and amended the recovery plan, without Management authorization, by allowing performance of the RFP changeover at a higher power than stated within the plan. This decision caused a higher than expected level increase on the start of the standby RFP and resulted in the Operator taking manual control of feedwater. The NSO failed to properly manipulate the feedwater controls and caused the trip of a RFP. A manual scram was initiated in accordance with conservative operating philosophy. The cause of the event was a performance error by the Operating Team. Corrective actions include counseling of involved operators in accordance with station policy and training to all operators on the event. This event is reportable per 10CFR50.73(a)(2) (iv), any event or condition that results in automatic or manual actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS). L:\8360\8301\237\180\97\010
2371997011 | Dresden 2, Dresden 3 | 04/30/1997 | 05/29/1997 | 9706050305 | <strong>Potential To Bypass Containment Pressure Suppression Due To Inadequacy Safety Evaluation and Review of Procedures</strong><br /><i>Abstract:&nbsp;</i>Dresden Design Engineering reviewed LaSalle LER 97-005 (Docket 05000373), dated March 24, 1997, regarding the potential loss of Standby Gas Treatment Systems and the Containment Pressure Suppression function following a Loss of Coolant Accident. Subsequent investigation determined that the only applicable concern was the potential to partially bypass the pressure suppression pool function if a LOCA should occur during the time when the drywell and suppression pool were interconnected by purging or venting operations. In resolving this issue, it was determined at 1200 on April 30 that this condition was reportable. A Four (4) hour phone call to the NRC was initiated under 10CFR50.72(b)(2)(i). The root causes of the event are 1) a failure in the original operating procedure for purging and its associated safety evaluation to address all interactions among the drywell and suppression chamber, and 2) failure to ensure that consistent operating alignment and philosophy were used in incorporating the design basis into operating procedure development. Corrective actions include revising station procedures to preclude the possibility of operation with a pressure suppression bypass flow path. The safety significance of this event is moderate. L:\8360\8301\249\180\97\011 05/28/97:1632
2371997012 | Dresden 2 | 05/20/1997 | 06/18/1997 | 9706250145 | <strong>Inadventant High Pressure Coolant Injection Isolation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1997 at approximately 0315, a High Pressure Coolant Injection (HPCI) Isolation occurred during the performance of Dresden Instrument Surveillance (DIS) 2300-03, High Pressure Coolant Injection Low Reactor Pressure isolation Channel Functional Test. The isolation was caused by an Instrument Maintenance (IM) 'B' technician connecting his digital multi-meter (DMM) across two terminals while in the resistance mode. The technician was assigned to verify a relay's change of state by measuring 125 Vdc across the terminals. The technician did not see the desired response for the test so he removed his test leads to perform a continuity check. After the satisfactory check of the leads he reconnected one lead and before connecting the second lead he noticed the DMM was still in the resistance/continuity mode. While On May 20, 1997 at approximately 0315, a High Pressure Coolant Injection (HPCI) Isolation occurred during the performance of Dresden Instrument Surveillance (DIS) 2300-03, High Pressure Coolant Injection Low Reactor Pressure isolation Channel Functional Test. The isolation was caused by an Instrument Maintenance (IM) 'B' technician connecting his digital multi-meter (DMM) across two terminals while in the resistance mode. The technician was assigned to verify a relay's change of state by measuring 125 Vdc across the terminals. The technician did not see the desired response for the test so he removed his test leads to changing modes of operation on the DMM, the second lead came into contact with the circuit being tested. This completed the electrical path to cause the HPCI isolation signal. The root cause of this event has been attributed to failure of the IMD technician to self-check while re-installing his test leads. The technician failed to ensure that his test leads were in a safe condition while changing the DMM modes of operation. Corrective actions include IMD establishing a Peer Check Program. This event is reportable pursuant to 10.CFR50.73(a)(2)(iv) and (a)(2)(v). The safety significance was determined to be minimal.
2371997013 | Dresden 2 | 06/06/1997 | 06/26/1997 | 9707090266 | <strong>HPCI System Declared Inoperable Due to Excessive Cycling of the Gland Seal Condenser Hotwell Drain Pump due to Pump Stop Level Switch Malfunction</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1997 at 0122 hours with Unit 2 in Mode 1(Run), while performing the scheduled quarterly Dresden Operability Surveillance (DOS) 2300-03, High Pressure Coolant Injection System Operability Verification, the High Pressure Coolant Injection (HPCI) Gland Seal Leak Off (GSLO) condenser hotwell drain pump began cycling on/off (excessively) on a 1 to 2 second interval. The cause for the excessive pump cycling is failure of the HPCI condenser hotwell pump level control switch 2-2300-LCS-1. The failed level switch was replaced. The high and low level switch/pump control, and level alarm switch operations were functionally verified. DOS 2300-03 was successfully performed. The safety significance of this event is minimal.
2371997014 | Dresden 2, Dresden 3 | 08/17/1997 | 09/12/1997 | 9709170089 | <strong>Inadvertent Exit From the Main Control Room due to SRO Loss of Focus Resulted in Inadequate Control Room Staffing</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1997, the Shift Manager provided the Unit 2 Unit Supervisor with an interim relief from the Control Room. When the Unit Supervisor returned to the Control Room from his break, he found that his interim relief had exited the Control Room resulting in a Technical Specification non-compliance for adequate Control Room Staffing. The duration of the non-compliance was verified to be one (1) minute in length, based on the elapsed time from the Shift Manager's exit until the return of the Unit Supervisor. The cause of the event was determined to be a Loss of Focus by the Shift Manager, evident by his failing to remember his interim relief responsibilities. Corrective actions include counseling of the individuals, Revision to station procedures (DAP 07-02) to formalize usage of badge clips to prevent inadvertent Control Room exit, elimination of the practice of allowing the Shift Manager to perform interim relief, and submittal of a supplemental LER to rescind corrective actions of LER 2-97-006. [illegible print]
2371997015 | Dresden 2 | 08/21/1997 | 09/15/1997 | 9709190225 | <strong>Operations fails to enter Drywell Radiation Monitor LCO due to inadequate Pre-job surveillance review.</strong><br /><i>Abstract:&nbsp;</i>On Aug 21, 1997, Operations performed a pre-task review of DIS 1600-16, Drywell High Radiation Monitor Group 2 Isolation Functional and Calibration Tests, identifying the need to enter Technical Specification TS 3.2.F. Accident Monitoring, during task performance. As a result of an inadequate review, Operations failed to identify that TS 3.2.A., Isolation Actuation, would need to be entered concurrently. After completion of the surveillance review, Operations granted approval for performance of DIS 1600-16. As Instrument Maintenance (IM) began calibration of the 2A Drywell High Radiation Monitor, Operations made a TS LCO entry under TS 3.2.F, missing the concurrent TS 3.2.A LCO. Later that day, IM suspended performance of the calibration. The following day, a new Operating Team performed a review of DIS 1600-16 in preparation for IMD to recommence performance of Radiation Monitor calibration, recognizing the previous failure to enter all appropriate TS LCOs. The cause of the event was determined to be error by the Unit Supervisor, who failed to perform an adequate pre-task review of DIS 1600-16, resulting in the failure to enter TS 3.2.A. Corrective actions include counseling of the individuals, review of all surveillances with a frequency of quarterly or greater to ensure Tech Specs for infrequently performed surveillances are pre-identified, and establishing an "apart in time" review process for Tech Spec surveillance LCO reviews to assure accuracy and independence of the review.
2371997016 | Dresden 2, Dresden 3 | 08/27/1997 | 09/23/1997 | 9709240236 | <strong>Autostart of the 2/3 Diesel Generator due to Operating Team Knowledge Deficiency.</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1997 at 1606, an unqualified toggle switch was found installed on the Unit 2/3 Emergency Diesel Generator (EDG)[EK] feeder breaker which supplies Unit 3 ESF Bus 33-1. Although the switch was designated as non-safety related, subsequent evaluation qualified the subject switch. Therefore, the non-qualified switch did not adversely affect the ability of the breaker to perform its intended function. In the interim, the EDG was declared inoperable until the breaker could be replaced and successful completion of operability testing was performed. The appropriate Technical Specification actions were taken upon discovery of this condition. Following installation of a replacement breaker, the 2/3 EDG was started for an operability run. A low idle start was to be performed per Dresden Operating Surveillance (DOS) 6600-01, Diesel Generator Surveillance Tests. The Nuclear Station Operator (NSO) started the EDG and allowed it to run at the low idle speed. After waiting 3 to 5 minutes, the High Voltage Operator (HVO) raised EDG speed locally. The 2/3 EDG tripped. The HVO reset the local annunciators, and depressed the 2/3 Diesel Engine Local Control Panel ALARM RESET pushbutton. The HVO believed the pushbutton would only reset the low cooling water pressure trip indicator. However, the pushbutton resets the sealed-in trip logic for the diesel, causing the EDG to restart because the EDG control switch was still in the "Start" position. This is an inadvertent ESF actuation. The cause of the event was determined to be a knowledge deficiency in the operation of the Diesel Engine Local Control Panel ALARM RESET pushbutton. Corrective actions include correction of the knowledge deficiencies and presentation of the event Lessons Learned to the other Operating Teams by the involved Operating Team.
2371997017 | Dresden 2, Dresden 3 | 11/26/1997 | 12/26/1997 | 9801050063 | <strong>Potential Vortex Formation in the CST to HPCI Suction Nozzle Due to Original Design Error</strong><br /><i>Abstract:&nbsp;</i>While assisting the Quad-Cities Station during an NRC inspection, Dresden engineering personnel became aware of a technical issue regarding vortexing at the High Pressure Coolant Injection (HPCI)/Reactor Core Isolation Cooling suction nozzle in the Condensate Storage Tank (CST). No previous calculations addressing vortexing at the HPCI suction nozzle on the CST had been performed for Dresden Station and the issue was judged applicable to Dresden Station. An operability determination found that significant amounts of air could be entrained into the HPCI suction piping before the CST low-low level would be reached and automatic transfer of the HPCI suction from the CST to the torus initiated. The Unit 2 and Unit 3 HPCI systems were declared inoperable and the applicable Technical Specification Limiting Condition for Operation was entered. Dresden has two CSTs and HPCI is generally aligned to one CST. Based on alignment of both CSTs to the HPCI systems and administratively maintaining water level in the CSTs and tori above low level alarm limits, it was determined that there was no line break accident scenario where the low-low CST level switches would be needed to initiate a transfer of the HPCI pump suction. For line breaks inside containment, automatic transfer of the HPCI pump suction from the CST to torus would be initiated by high level in the torus before the low-low CST level setpoint is reached. For line breaks outside of containment, the amount of water required for HPCI is small compared to the available inventory and no automatic transfer of the suction path is required. The primary root cause appears to be an original design error. The effect of vortexing on the useable CST volume was not considered in the original design of the HPCI system. Further evaluation will be performed to ensure that the HPCI suction path from the CSTs is automatically transferred to the torus prior to entraining significant amounts of air into the HPCI pump. No previous occurrences were identified. The safety consequences of a degraded HPCI system would have been minimal at the time of the event since the automatic depressurization system and other ECCS systems were available as a backup to the HPCI subsystem to mitigate the consequences of an accident. L:\8360\8301\237\180\97\017 12/26/97 1:10PM
2371997018 | Dresden 2 | 12/22/1997 | 07/06/1998 | 9807080096 | <strong>Unexpected High Pressure Coolant Injection System Supply Isolation During Testing Due to Spurious Actuation of the Isolation Circuit</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1997, at approximately 0303 hours, an unexpected Group IV (High Pressure Coolant Injection (HPCI)) Primary Containment Isolation signal was received while testing the HPCI Steam Line Low Pressure Isolation circuitry. Subsequent to the occurrence, a troubleshooting effort was initiated. However, no equipment faults were identified. Two relays which were suspected to have caused the isolation were replaced and successfully tested. A failure analysis was performed on the relays that were removed. The analysis showed that the relays were in acceptable physical condition and operated satisfactorily. The analysis did not confirm that the relays contributed to the cause of the HPCI isolation. A detailed calibration and acceptance test was performed on the multimeter that was used during the testing when the HPCI isolation occurred. The multimeter was within tolerance and passed the acceptance test, ruling out the possibility of a multimeter malfunction contributing to the HPCI isolation. The cause of this event is a spurious actuation of the HPCI low reactor pressure isolation circuit. The safety significance of this event is minimal due to other safety systems being available for operation. This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(iv) which requires the reporting of any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature.
2371997019 | Dresden 2 | 12/23/1997 | 01/22/1998 | 9801270112 | <strong>Spurious Local Power Range Monitor Spike Results In Full Reactor Scram Caused By Design/Manufacturing Deficiency And Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1997, at approximately 1141, during performance of Dresden Instrumentation Surveillance (DIS) 0500-01, Reactor Vessel High Pressure Scram Pressure Switch Calibration, an unexpected Reactor protection System (RPS) Channel A half scram was received from a spiking Local Power Range Monitor (LPRM). This in conjunction with the expected RPS Channel B half scram already received during DIS 0500-01, resulted in an unexpected full reactor scram. Following the reactor scram, a feedwater transient occurred which could have resulted in water entering the High Pressure Coolant Injection (HPCI) steam supply. However, the HPCI system was isolated at the time of occurrence. The root cause of the LPRM spike was a design/manufacturing deficiency of the LPRM detector and an inadequate review of a GE SIL which provided actions to reduce the probability of spurious LPRM spikes. The root cause of the feedwater transient was design deficiency of the feedwater control system [SJ]. The corrective actions include: possible expediting of the schedule to replace the LPRM detectors with the improved type, reevaluating the GE SIL, and modification of the feedwater control system. The overall safety significance of the is event was minimal.
2441997001 | Ginna | 01/31/1997 | 03/03/1997 | 9703110153 | <strong>Service Water Temperature Less Than Specified Value, Due to Non-Representative Method of Monitoring, Resulted in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1997, at approximately 1300 EST, the plant was in Mode 1 at approximately 100% steady state reactor power. Utilizing a hand-held temperature monitoring probe, it was discovered that the Service Water pump suction temperature (screenhouse bay temperature) was slightly less than 35 degrees F. Having this temperature less than 35 degrees F is a condition prohibited by the Ginna Station Improved Technical Specifications Bases, Section B 3.7.8. Immediate corrective action was taken to increase the water temperature in the screenhouse bay to greater than 35 degrees F, thus restoring compliance with the Improved Technical Specifications Bases. The cause was a non-representative method of monitoring screenhouse bay temperature. On February 11, 1997, at approximately 2230 EST, environmental restrictions limited the ability to increase the water temperature in the screenhouse bay. Temperature was slightly less than 35 degrees F. Corrective action was taken to increase the water temperature in the screenhouse bay while remaining within the limits of the environmental restrictions. Corrective action to prevent recurrence is outlined in Section V.B.
2441997002 | Ginna | 07/20/1997 | 08/19/1997 | 9708270015 | <strong>Loss of 34.5 KV Offsite Power Circuit 751, Due to External Cause, Results in Automatic Start of "B" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1997, at approximately 0043 EDST, the plant was in Mode 1 at approximately 100% steady state power. Power from Circuit 751 (34.5 KV offsite power source) was lost. This resulted in deenergization of 41 60 Volt bus 12B and "B" train 480 Volt safeguards buses 16 and 17. The "B" Emergency Diesel Generator (D/G) automatically started and reenergized buses 16 and 17 as per design. There was no change in reactor power or turbine load. Immediate corrective action was to perform the appropriate actions of Abnormal Procedure AP-ELEC.1 (Loss of 12A And/Or 12B Buses) to stabilize the plant and to verify that the "B" Emergency D/G had started and reenergized buses 16 and 17. The cause of the loss of power from Circuit 751 was determined to be a phase-to-phase fault caused by a raccoon. This fault caused the insulators on an offsite pole for Circuit 751 to fail. This event is NUREG-1022 Cause Code (C). Corrective action to prevent recurrence is outlined in Section V.B.
2441997003 | Ginna | 07/30/1997 | 09/29/1997 | 9710030201 | <strong>Bistable Instrument Setpoint (plus Instrument Uncertainty) Could Exceed Allowable Value, Causes a Condition Prohibited by Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1997, at approximately 1430 EDST, the plant was in Mode 1 at approximately 100% steady state reactor power. It was identified that the High Steam Flow Bistable Instrument Trip Setpoint plus the Instrument Uncertainty could exceed the "Allowable Value" listed in the Ginna Station Improved Technical Specifications. Immediate corrective action was to declare all four channels of High Steam Flow inoperable and enter Limiting Condition for Operation 3.0.3. When action was taken to place the affected bistable proving switches in the tripped position, the plant exited Limiting Condition for Operation 3.0.3. The cause of this condition was that the existing margin between the Trip Setpoint and the Allowable Value is insufficient to account for process and instrument uncertainties. Corrective action to prevent recurrence is outlined in Section V.B. Additional corrective actions are identified in this supplement.
2441997004 | Ginna | 10/24/1997 | 11/24/1997 | 9712030140 | <strong>Radiation Monitor Alarm, Due to Higher than Normal Radioactive Gas Concentration, Results in Containment Ventilation Isolation</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1997, at approximately 1919 EST, the plant was in Mode 6 with the reactor coolant system being maintained at a temperature of 110 degrees F and depressurized and vented. The plant was shut down for refueling. During activities associated with opening the primary sides of the steam generators, radioactive gas concentration increased within the containment. A containment ventilation isolation occurred when containment gas radiation monitor R-12 reached its high alarm setpoint. Immediate operator action was to perform the applicable actions of alarm response procedures. Corrective action to prevent recurrence is outlined in Section V.B.
2441997005 | Ginna | 10/31/1997 | 12/01/1997 | 9712050136 | <strong>Undetected Unblocking of Safety Injection Actuation Signal While at Low Pressure Condition, Due to Faulty Bistable, Resulted in Inadvertent Safety Injection Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1997, at approximately 1640 EST, the plant was in Mode 6 with the reactor coolant system being maintained at a temperature of 80 degrees F, and the reactor cavity filled to greater than 23 feet. The plant was shut down for refueling. An inadvertent automatic Safety Injection Actuation occurred. Immediate corrective action was to monitor the automatic start of engineered safety features components and secure unneeded equipment. The underlying cause of the inadvertent automatic Safety Injection Actuation was an undetected faulty bistable circuit board. During the performance of a periodic test, this faulty bistable caused the Safety Injection Actuation signal to be inadvertently unblocked with pressurizer pressure less than the setpoint for Safety Injection Actuation. Corrective action to preclude repetition is outlined in Section V.B.
2441997006 | Ginna | 11/03/1997 | 02/06/1998 | 9802170156 | <strong>Verification of Boron Concentration Not Performed Due to Misinterpretation of Event Sequence, Resulted in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1997, at approximately 1708 EST, the plant was in Mode 6, and refueling activities had been completed two days earlier. The reactor coolant system being maintained at a temperature of 75 degrees F, and the reactor cavity filled to greater than 23 feet. It was discovered that the nuclear instrumentation system audible count rate function was inoperable. Immediate action was to ensure future compliance to the Ginna Technical Specifications for loss of this function. This included verifying that the most recent boron concentration was within specified limits and formally tracking the time for future verification of boron concentration. Due to a misinterpretation of the event sequence, the verification of boron concentration may not have been performed within the time period specified by Ginna Technical Specifications Required Actions for the most limiting event sequence. Corrective action to prevent recurrence is outlined in Section V.B.
2441997007 | Ginna | 11/17/1997 | 02/06/1998 | 9802180030 | <strong>Reactor Trip Instrumentation Would Have Been in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1997, the plant was in Mode 3 with a reactor coolant system heatup in progress. One nuclear instrumentation system power range channel was removed from service in preparation for the beginning of Cycle 27 physics testing. The reactor engineer recognized that the neutron flux low range trip circuitry for this channel was not in the tripped condition, as required prior to entry into Mode 2. Since the plant was not in a mode where the power ranges are required to be operable, no immediate corrective action was required. Subsequent to the November 17 condition, research into the system design and operating history showed that, prior to 1988, the neutron flux high range trip circuitry was not routinely placed in the tripped condition during channel defeats. The underlying cause was technical inadequacies in procedures and design deficiency, in that Instrument and Control procedures utilized for channel defeat did not address the need for neutron flux low range trip circuitry to be in the tripped condition, and the original plant design required lifting leads to place the neutron flux high range trip circuitry in the tripped condition. While this condition is not reportable for the November 17, 1997, condition, this condition would have occurred during physics testing performed in the past, and was not recognized at those times. At those times, the plant would have been in a condition prohibited by the Technical Specifications. Corrective action to prevent recurrence is outlined in Section V.B.
2451997001 | Millstone 1 | 01/10/1997 | 02/10/1997 | 9702120389 | <strong>Liquid Radwaste Effluent Radiation Monitor Inoperable Due to Leaking Automatic Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1997, investigation of a related event identified that the effect of excessive liquid radwaste discharge isolation valve seat leakage on radwaste effluent line radiation monitor operability from November 28, 1991 until September 21, 1994 was not addressed. Since the liquid radwaste effluent radiation monitor is required by Technical Specifications (TS) to automatically terminate a release upon detection of excessive radiation, the monitor shuts these automatic isolation valves to accomplish its function. The liquid radwaste effluent radiation monitor could not terminate the release as required by TS because of the leaking valves, therefore, the monitor was inoperable from November 28, 1991 to September 21, 1994. One of the liquid radwaste discharge automatic isolation valves were repaired on September 16, 1994 and the other on September 21, 1994. Critical radwaste components will be identified and a preventative maintenance program to assure operability of these components will be implemented. The system design basis will be revised to identify these critical components and specify their design requirements. The Liquid Radwaste Discharge system lineup will be reviewed and the configuration and discharge procedures modified to ensure the system is operated within the design basis of the plant. The TS actions were applicable at all times liquid radwaste effluent line radiation monitor was inoperable. Since the required action statement for an inoperable radwaste effluent line radiation monitor were not performed, this event is reportable, pursuant to 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. There were no safety consequences
2451997002 | Millstone 1 | 01/14/1997 | 02/13/1997 | 9702200144 | <strong>Inadvertant Shutdown Cooling Isolation During System Removal from Services for Maintenance</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1997, at 0010 hours with the plant in cold shutdown condition, an inadvertent Group III (Shutdown Cooling) isolation occurred while removing the system from service for routine maintenance work on several primary containment isolation system (PCIS) logic system relays. The clearance (tagout) required fuses 595-716 and 595725 to be pulled de-energizing the relays to support the scheduled work. When the first fuse was pulled, valve 1-SD-1 (Shutdown Cooling Suction Valve) went closed due to the containment isolation signal caused by loss of power to the isolation relay logic power system. An immediate report was made on January 14, 1997, pursuant to 10CFR50.72(b)(2)(ii), “any event or condition that results in manual or automatic actuation of any engineered safety feature.” The cause of this event was an inadequacy in the preparation and review of the clearance that was required to perform maintenance on the isolation logic relays. Further corrective action is to revise the clearance (tagout) procedure and process to require two separate reviews of the clearance (tagout) procedure prior to release. Also, additional training will be provided in electrical schematic print reading to licensed personnel. No safety consequences resulted from this event. The core was off-loaded in the spent fuel pool with the fuel pool gates installed at the time of the event. Neither shutdown cooling or PCIS was required at the time.
2451997003 | Millstone 1 | 03/06/1997 | 04/07/1997 | 9704150254 | <strong>Service Water Effluent Not Monitored Per Requirements of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1997, a review of plant drawings revealed that the Service Water (SW) System in the Reactor Building has a potential unmonitored release path. At the time of discovery, the plant was in COLD SHUTDOWN, and SW flow to and from the Reactor Building was isolated for maintenance. Spent Fuel Pool cooling was being provided from the Turbine Building Closed Cooling Water (TBCCW) System. An unmonitored release could occur if, Reactor Building Closed Cooling Water (RBCCW) leaked into the SW while the SW continuous vent lines of the RBCCW heat exchanger(s) were in service. The continuous vent lines were installed under a plant design change. The cause of the unmonitored release path was an inadequate design change package. An inadequate review of the design change was performed during the approval process. This resulted in the plant failing to realize that a new discharge path was created. Northeast Nuclear Energy Company (NNECO) will revise procedures to ensure that Service Water effluent from the Reactor Building is operated within design basis and Technical Specifications. There were no safety consequences, since there were no releases that exceeded the release limit. During the period of time when the RBCCW continuous vents were in service, 1 987 to 1 989, the RBCCW system had detectable contamination levels. This contamination was from a Spent Fuel Pool heat exchanger tube leak. Contamination levels were kept low by a feed and bleed of the RBCCW system. Isotopic sample results for the RBCCW fluid showed that the concentration of radionuclides was maintained below the limits allowed for radioactivity in effluents to unrestricted areas as defined by 10CFR20. In addition, SW flow through the Reactor Building would have provided at least a 10 to 1 dilution for any RBCCW fluid that leaked into the SW system and was discharged through the continuous vents. Therefore, this event has no safety significance.
2451997004 | Millstone 1 | 01/27/1997 | 04/30/1997 | 9705060315 | <strong>RBCCW Containment Isolation Valve May Not Close Within Specified Time</strong><br /><i>Abstract:&nbsp;</i>On January 27, 1997, at 1200 hours, with the plant in COLD SHUTDOWN, a single failure vulnerability of Reactor Building Closed Cooling Water System (RBCCW) was identified. Containment Isolation Valve 1-RC-206 has an allowable closure time of 35 seconds per Technical Requirements Manual. The valve is powered from MCC-E3 which is connected to the Gas Turbine (GT) for its emergency power source. Following a Loss of Normal Power (LNP) event, AC power will not be restored to MCC-E3 for a maximum Technical Specification limit of 48 seconds. A time limit of 60 seconds is assumed in the offsite dose calculations to establish primary containment integrity. On a Loss of Coolant Accident (LOCA) with a LNP, a failure of DC operated valve 1-RC-207 will result in penetration X-24 taking longer than the assumed 60 seconds to completely isolate. Any post-LOCA gas escaping from primary containment through this penetration would be released into secondary containment. This leakage would be in addition to the 300.3 SCF per hour Appendix J leakage from the Drywell assumed in the off site dose calculations. Thus, this condition could exceed the existing calculated site boundary dose limits. The cause of this condition was the failure to adequately establish a design basis for RBCCW containment isolation. An engineering evaluation was performed that determined that the leakage from containment would be an additional volume of approximately 25.1 SCF from the post-LOCA containment atmosphere. The radiological impact of this additional leakage has been determined to be an unacceptable potential safety consequence due to limited margin to the design basis limits in areas related to control room habitability and EEQ integrated radiation doses.
2451997005 | Millstone 1 | 01/15/1997 | 04/30/1997 | 9705060297 | <strong>Radwaste Storage Building Exhaust Fan Discharges to Atmosphere Without Radiation Monitoring</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1997, with the plant in the COLD SHUTDOWN condition, it was discovered that the Radwaste Storage Building (RSB) vent exhaust fan HVE-14 discharges directly to the atmosphere without continuous radiation monitoring. On February 6, 1997, this event was determined to be reportable and a report was made pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition that is outside of the design basis of the plant. The HEPA filter for the exhaust fan has not been tested to verify the efficiency of the filter. The airborne activity in the RSB was exhausted directly without an operable HEPA filter. Operation of exhaust fan HVE-14 was prevented immediately upon discovery of the event. A review of a sample of the Health Physics airborne radioactivity surveys for the RSB has determined that there was no significant unmonitored release based on the low levels of airborne activity in the RSB. Prior to returning HVE-14 to service, the HEPA filter will be tested and a program for periodic testing of the filter will be established. The Design Change Manual will be reviewed to verify adequate design change controls for HVAC systems.
2451997006 | Millstone 1 | 01/31/1997 | 03/03/1997 | 9703060194 | <strong>Failure to Exert Best Efforts to Restore the Radwaste Effluent Line Radiation Monitor to Operable Status</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1997, with the plant in the Cold Shutdown condition, it was determined that “best efforts” were not being demonstrated to restore the Radwaste Effluent Line Radiation Monitor to an operable status. Technical Specification (TS) Section 3.8.A, Action 3 states, “exert best efforts to restore the inoperable monitor to OPERABLE status within 30 days and, if unsuccessful, explain in the next Annual Effluent Report why the inoperability was not corrected in a timely manner.” The Radwaste Effluent Line Radiation Monitor has remained inoperable since June 5, 1996, due to issues addressed in previous LERs: 96-043-00 on inadequate time response testing; 96-053-00 on inadequate source checks; and 96-065-00 and 97-001-00 on non-conservative setpoints due to draining the discharge piping. Since these conditions were not resolved using best efforts, as specified in TS, this event is reportable as a condition prohibited by the plant’s TS. The cause of this event was failure to provide clear management expectations of what constitutes “best efforts” and inadequate prioritization of work required to restore the Radwaste Effluent Line Radiation Monitor to an operable status. Corrective actions include providing guidance for TS “best efforts” and returning the Radwaste Effluent Line Radiation Monitor to an operable status. The safety significance of this event is low since required TS compensatory actions were in place the entire time. Therefore, no safety consequences resulted from this event.
2451997007 | Millstone 1 | 01/31/1997 | 03/31/1997 | 9704080356 | <strong>Flow-Biased High Flux Scram Is Not Single Failure Proof</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1997, at 0930, with the plant in COLD SHUTDOWN, it was discovered that the Average Power Range Monitor (APRM) Flow-Biased High Flux Reactor Scram is credited in establishing the initial conditions for limiting plant transients but is not redundant and not single failure proof. This event was immediately reported on January 31, 1997 pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition that is outside the design basis of the plant. There were no automatic or manually initiated safety system responses as a result of this event. The cause of this event is that the loss of stator cooling was not sufficiently analyzed, as a potential initiating event for a loss of feedwater heating event, due to programmatic weaknesses in ensuring adequate engineering review for purchased engineering activities. The safety significance of this event is that a single failure which disables the APRM Flow-Biased High Flux Reactor Scram results in the fuel thermal limits being exceeded during the transient. However, there were no safety consequences as a result of this event. The design will be enhanced to provide an appropriate protective system for this transient prior to startup for operating Cycle 16. Millstone Unit No. 1 is currently involved in a 10CFR50.54(f) design basis reconstitution effort that would identify past design basis inadequacies. The existing QA/QC and Engineering Standards will be reviewed to ensure that adequate review and processes are in place for in-house and purchased engineering activities prior to startup for operating Cycle 16.
2451997008 | Millstone 1 | 02/03/1997 | 03/03/1997 | 9703060126 | <strong>Failure To Verify Gas Turbine Generator Air Start Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1997, with the plant shutdown and the reactor in the COLD SHUTDOWN condition, a review of the Gas Turbine Generator (GTG) preoperational test has revealed that the test did demonstrate that the starting air receiver does contain sufficient inventory for three starts without recharging, however, the initial start was performed at 250 psig and the system pressure has since been maintained between 200 psig and 235 psig. Therefore, the starting air system has been operated outside the Plant Design Basis and is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(ii). There were no automatic nor manually initiated safety system responses as a result of this event. The cause of this event is the failure to properly identify and verify the design basis of the GTG air start subsystem and the corrective action is to establish the design basis, document it in the UFSAR and verify it by testing. There were no safety consequences as a result of this event. The safety significance of this event is low since the GTG air receiver has been demonstrated to contain sufficient inventory to provide at least one GTG start each month.
2451997009 | Millstone 1 | 02/12/1997 | 03/14/1997 | 9703190104 | <strong>Reactor Low-Low Level ECCS and Primary Containment Isolation Initiation Setpoints Not Conservative</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1997, with the plant in COLD SHUTDOWN, a review of a previously completed setpoint calculation from October 25, 1994, identified the reactor vessel low-low level Emergency Core Cooling System (ECCS) and Primary Containment Isolation System (PCIS) initiation setpoints were potentially non-conservatively set. A review of the instrumentation uncertainty associated with the low-low level ECCS and PCIS initiation functions revealed that the instrument uncertainty error is greater than the instrument trip setting band required by Technical Specifications (TS). Therefore, ECCS and PCIS initiation could occur beyond the required TS limits. This event was promptly reported on February 12, 1997, pursuant to 10CFR50.72(b)(2)(i) as an unanalyzed condition. The ECCS and PCIS low-low level initiation instrumentation was determined to be inoperable as a result of this discovery. The cause for exceeding TS limits is the use of an original setpoint methodology which did not explicitly evaluate individual contributors to the overall instrument uncertainty. There were no safety consequences as a result of this event. The TS will be changed or a new analysis will be performed to ensure that ECCS and PCIS actuation will occur consistent with the plant's design basis including consideration of instrument uncertainties. All calculations that have been completed as part of the Setpoint Verification Program will be reviewed to determine if other non-conservative setpoints exist.
2451997010 | Millstone 1 | 02/14/1997 | 03/17/1997 | 9703200148 | <strong>LLRT Test Pressure Less Than Accident Pressure</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1997, with the plant in COLD SHUTDOWN, a review determined that the Local Leak Rate Test (LLRT) pressure being used may be less than accident pressure. Design Basis Accident Pressure is 43 psig per Updated Final Safety Analysis Report, Section 6.2.1.1.1. Test pressure during the LLRT is also 43 psig. Use of LLRT test pressure equal to Design Basis Accident pressure fails to take into consideration pressure gauge inaccuracies and line losses due to flow through the test rig and flow meters. The test gauge was located at the inlet of the flow meters and as much as 200 feet of small diameter tubing was used to connect to the penetration. The failure to test at accident pressure invalidates past LLRTs and results in the inability to adequately demonstrate containment integrity. Containment integrity is required by Millstone Unit No. 1 Technical Specifications, Section 3.7.A.3, thus this event is reportable as a condition prohibited by the plant's Technical Specifications. The cause of this event is weaknesses in the management commitment to the Appendix J Program resulting in an inadequate technical review of the implementing procedures. There were no safety consequences as a result of this event. Procedural changes and changes to the test rig configuration are being undertaken to increase the LLRT pressure thus assuring a full Design Basis Accident Pressure is applied to the volume under test. A review of impacted test results will be undertaken and test results conservatively corrected.
2451997011 | Millstone 1 | 02/14/1997 | 03/17/1997 | 9703200163 | <strong>Exceeded Surveillance Test Interval for Containment Airlock</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1997, at 1300 hours, with the plant in COLD SHUTDOWN, it was discovered that the Technical Specification Surveillance Requirement 4.7.A.3.d, Containment Airlock Leakage Rate Test, had been exceeded. This surveillance did not conform to Appendix J requirements in that an additional 25% ('grace period') in the surveillance interval had been used. Most Technical Specification surveillance test intervals are allowed an additional 25% in the test interval, however, Appendix J tests frequencies do not have this provision. It was discovered that a test was performed on December 4, 1994, and the next test was not performed until July 3, 1995, for a total of seven months and one day between tests, thus exceeding the 6 month frequency for the test. The cause of this event is personnel error in that the surveillance was incorrectly scheduled. There were no safety consequences as a result of this event. Millstone Unit No. 1 is presently in a mode which does not require the Containment Airlock to be operable. The safety significance of this event is low since the Containment Air Lock integrity had been demonstrated by an adequate test. The corrective actions that have been completed include changes to the scheduling of the Containment Airlock Leakage Rate Test. Records will be reviewed for the past two cycles to verify that other Appendix J surveillances have not exceeded their interval.
2451997012 | Millstone 1 | 02/14/1997 | 03/17/1997 | 9703190081 | <strong>Seismic Deficiency in the Gas Turbine Generator Digital Control System</strong><br /><i>Abstract:&nbsp;</i>On February 14 1997, at 1400 hours, with the plant in COLD SHUTDOWN, a design deficiency was identified in the Gas Turbine Generator (GTG) digital control system which could have resulted in misoperation during a seismic event. The design deficiency was discovered during the implementation of the corrective actions from the USI A-46 seismic review of the GTG where the interface between control system input relays and the digital control system was being evaluated. The results of the evaluation indicate a potential for the digital control system to respond to relay contact chatter of durations less than 2mS which could render the GTG inoperable. This was immediately reported pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition that is outside of the plant's design basis. There were no automatic or manually initiated safety system responses as a result of this event. review during the installation of the digital control system in 1987. There were no safety consequences as a result of this event as the relay contacts have never been challenged by a seismic event. The safety significance is that with the GTG in this condition, a seismic event could occur that would cause a loss of normal power, and if concurrent with a single failure to the diesel generator, subject the unit to a Station Blackout (SBO) condition. The SBO condition has been previously analyzed and the safety significance of this event would be minimized as a result of Millstone Unit No. 1's ability to negotiate an SBO condition as documented in Standard Specification SP-EE-361 in response to 10CFR50.63. Corrective actions include implementing a physical modification to resolve this design deficiency prior
2451997013 | Millstone 1 | 02/17/1997 | 12/03/1998 | 9812090017 | <strong>Evaluation of Impact Load of the MP1 Refueling Platform Fuel Grapple Mast Over Spent Fuel Pool Racks and the Reactor Vessel Guide Plate</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1997, with the plant in COLD SHUTDOWN, it was discovered during a document review that the weight of the lower mast sections of the Refueling Platform fuel grapple were not added to the fuel assembly weight, to determine the total potential impact load for the design of the spent fuel pool storage racks. When moving fuel in the fuel pool, in the event of a single active failure of a hoist component, such as a cable break, could result in a dropped fuel assembly failing with portions of the mast onto fuel stored in the spent fuel storage racks or in an empty storage rack cell. In the course of reviewing potential interactions between the refueling mast and the spent fuel storage racks, it was also discovered on February 24, 1997, that a similar interaction may occur when the mast would be operated over the reactor vessel. In the event of a break in the hoist cable, the mast would not reach its full extension and consequently, a portion of the mast could remain attached to a dropped fuel assembly and strike the top of the fuel or the reactor vessel internals. These conditions were determined to be outside the design basis of the plant and reported on February 18, 1997, and February 25, 1997, in accordance with 10CFR50.72(b)(1)(ii)(B). The cause of the event has been determined to be the failure to maintain the design basis as stated in the Updated Final Safety Analysis Report (UFSAR) based on a revised analysis by General Electric (GE) in 1987. The revised analyses were subsequently performed for postulated drops over the fuel pool storage racks and reactor vessel core area. Changes were processed for incorporation of the revised analysis into the Millstone Unit No. 1 UFSAR.
2451997014 | Millstone 1 | 02/17/1997 | 02/27/1997 | 9709030368 | <strong>Certain Core Spray Components Not Included in the IST Program</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1997, with the plant in COLD SHUTDOWN and reactor defueled, a review performed on the Inservice Testing (IST) Program, as part of the 10 CFR 50.54(f) effort identified a historical IST Program deficiency. Core Spray valves 1-CS-13A/B were not included in the IST Program prior to 1 992. Additionally, on February 18, 1997, the same review identified that four Core Spray system check valves located on the keep-fill lines were not leak tested in the IST Program to support verification of the system's integrity as a closed system as credited in the 10CFR50 Appendix J program. On February 25, 1997, additional IST program deficiencies were identified. On July 30, 1997, several IST program deficiencies, which were identified during the 50.54(f) assessment of the IST program, were discovered as being omitted from the previous condition reporting process. The cause for this event is a lack of management commitment to support the IST Program by not allocating the resources to implement a successful [ST Program. No immediate action is required since the plant is in COLD SHUTDOWN and the reactor defueled. The IST Program manual already has been revised to include the core spray minimum flow line check valves. The IST surveillance deficiencies and other IST Program deficiencies will be corrected. NNECO will provide sufficient trained staffing to implement and manage the IST Program. NNECO will revise the IST Program Administrative Control Procedure based on the 10CFR50.54(f) findings. Any applicable corrective actions as a result of this review will be completed prior to startup for operating Cycle 16.
2451997015 | Millstone 1 | 03/21/1997 | 04/01/1997 | 9704290268 | <strong>Inadvertent Actuation of Group Six Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1997, at 1053 hours, with the plant in COLD SHUTDOWN and no fuel in the reactor, an inadvertent group six (containment ventilation) isolation occurred while maintenance cleaning and welding activities were being performed in areas local to the Containment High-Range Radiation Monitor detector RIT-1825 and its cables. This condition was reported on March 21, 1997, pursuant to 10 CFR 50.72(b)(2)(ii), 'any event or condition that results in manual or automatic actuation of any engineered safety feature.' There were no safety consequences as a result of this event. Primary containment was not required and there was no high radiation condition. There are no safety implications since this event does not impact any accident analysis. The cause of the event has been attributed to a noise spike generated from maintenance activities resulting in an inadvertent actuation via the Containment High-Range Radiation Monitor RIT-1825. Corrective actions include procedure revisions to bypass the group six isolation signal from both Containment High-Range Radiation Monitors, at the discretion of the Shift Manager, to preclude inadvertent high radiation alarms and actuations when work is being performed and primary containment is not required. Also, prior to startup for operating Cycle 16, testing will be performed to determine operability of the Containment High-Range Radiation Monitor.
2451997016 | Millstone 1 | 04/01/1997 | 05/01/1997 | 9705060117 | <strong>Loss of Secondary Containment During Purging/Venting Operations</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1997, at 1100 hours, with the plant in COLD SHUTDOWN condition, it was discovered that during vent/purge operations using the Standby Gas Treatment System (SGTS), the opening and closing sequence of the Atmospheric Control (AC) and the SGTS inlet valves (1-SG-1A/B) creates a temporary flow path between the Reactor Building and primary containment prior to isolation of the AC system. The flow escaping into the Reactor Building through this path during a Loss of Coolant Accident (LOCA) could be sufficient to lift the blow-out panels in the Reactor Building, especially if purging/venting was conducted with the 18' AC valves. Since the differential pressure (DP) in the Reactor Building would be at the 6 in Wg relief pressure of the panels, 10CFR100 limits would be exceeded before the SGTS could restore the -.25 in Wg DP and begin filtering the release. The potential safety consequences of this condition is a loss of safety function since without secondary containment, SGTS would be unable to mitigate the consequences of a LOCA. It should be noted that, Technical Specification 3.7.B.3.6 requires primary containment to be purged through SGTS whenever primary containment is required. The potential to pressurize the Reactor Building during vent/purge evolutions results from the fact that the design of the SGTS system did not consider a LOCA coincident with these operations. This event is considered outside the plant's original design basis.
2451997017 | Millstone 1 | 02/22/1997 | 03/24/1997 | 9704150082 | <strong>Failure To Meet Technical Specification 3.1.C. "Reactor Protection System Power Monitoring"</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1997, with the plant in cold shutdown (85 degrees Fahrenheit and 0 psig) it was determined that Technical Specification 3.1.C, 'Reactor Protection Power Monitoring,' was not complied with during battery maintenance and discharge testing. Battery maintenance or battery discharge testing removes one battery bus from service which removes the DC control power to one channel of the Reactor Protection Power Monitoring Electric Protection Assemblies (EPA's). In order to maintain control power to the EPA's powered from the out of service battery, jumpers were installed from the inservice battery to the EPA's so that the DC control power would be maintained. While in this configuration the EPA's were incorrectly declared operable and the Technical Specification Limiting Condition for Operation (LCO) requirements were not adhered to. The cause of this event is that personnel involved in the Jumper Device, Safety Evaluation, Procedure and Plant Operations Review Committee (PORC) review failed to recognize that the EPA's were not operable when DC control power was being received from the opposite battery bus with the normal DC control power out of service. No safety consequences resulted from this event, since both channels of the EPA's remained in service and would provide adequate protection of the RPS components. However, while in this configuration, the revised lineup was no longer single failure proof. OP 344A will be revised to delete the installation of the jumper and require that LCO 3.1.C.1 be entered if a battery is removed from service.
2451997018 | Millstone 1 | 02/24/1997 | 03/26/1997 | 9704020265 | <strong>Four MOVs May Not Fully Isolate Pipe Breaks</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1997, with the plant in COLD SHUTDOWN, a review of the as-left limit switch settings of valves that have a torque switch bypass feature indicated that four valves may not fully isolate a downstream pipe break. These four valves have a spring pack compensator which allows the stem to move upward during the closing valve stroke. This movement was not accounted for in determining the physical location on the valve seat where the valve disc would stop. The result is that the disc may not be covering the valve seats, thus not isolating the flow through the valve, before the bypass of the torque switch is electrically removed and the valve is assumed to stop. These valves (1-IC-1, 1-IC-4, 1-CU-2 and 1-CU-28) isolate the Isolation Condenser system and the Reactor Water Cleanup systems respectively. This condition was immediately reported as outside the design basis of the plant on February 24, 1997. The cause of the event is the lack of adequate design change process guidance and limited vendor and industry documentation availability. To prevent reoccurrence, a design change to compensate for the potential upward movement of the stemnut and stem during a high energy line break condition is required. This will include adjusting the close torque switch bypass percentage setting in the field. This corrective action will be completed prior to startup for operating Cycle 16.
2451997019 | Millstone 1 | 03/26/1997 | 04/25/1997 | 9704300194 | <strong>Liquid Discharge Without SW or Recirc Water Available</strong><br /><i>Abstract:&nbsp;</i>Millstone Unit One Technical Specification 3.8.A requires that the liquid radwaste effluent line radiation monitor setpoint be set in accordance with methods and parameters as described in the Offsite Dose Calculation Manual (ODCM). The ODCM specifies a fixed, default setpoint when liquid radwaste radioactivity concentration is below a certain level assuming a minimum dilution flow during discharge of 110,000 gpm. Contrary to this requirement the default setpoint has been used with dilution flows less than 110,000 gpm. There were no safety consequences for this event since the discharge procedures had administrative controls to ensure releases were below 10CFR20 limits. The safety significance of this event is the conduct of a liquid radwaste discharge with an incorrect setpoint for the existing plant conditions. The cause of this event was a failure to adequately implement ODCM requirements in a procedure. The radwaste discharge valve was tagged closed as a corrective action until changes to the operation's procedure SP 671.5 was completed. The chemistry procedure will be changed to a surveillance and will be revised to implement the assumptions and conditions from the ODCM concerning use of the liquid radwaste monitor default setpoint. The ODCM will be revised to address special conditions during shutdown when determining effluent monitor setpoints. The procedure controlling ODCM changes will be revised to require the Chemistry Manager to review and sign to ensure unit procedures reflect ODCM changes.
2451997020 | Millstone 1, Millstone 2, Millstone 3 | 02/27/1997 | 03/31/1997 | 9704080396 | <strong>Liquid Radwaste Effluent Monitor Functional Test Surveillance Not in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1997, at 1810 hours, with the plant in a Cold Shutdown condition, it was discovered that the downscale annunciator for the Millstone Unit 1 Liquid Radwaste Effluent Monitor was not adequately verified in accordance with Millstone Unit 1 Technical Specifications (TS). Functional testing for the downscale function is accomplished by using the drawer mode selector switch, which produces an Inop trip and Downscale/Inop annunciator when taken out of the operate position. However, it was determined that this method of testing does not fully check all components in the downscale trip circuitry. A review of similar type effluent monitors at Millstone Unit 1 revealed that the Service Water Effluent Line Radiation Monitor and Main Stack Noble Gas Activity Monitor also did not have the downscale annunciation adequately verified in accordance with TS. The Main Stack Noble Gas Activity Monitor is also in the TS of Millstone Unit 2 and 3. Therefore, the TS surveillance requirement for this monitor was not met for all three units. Millstone Unit 2 and 3 were also in Cold Shutdown at the time of discovery. Since TS surveillance requirements were not adequately performed, this event is reportable as any operation or condition prohibited by the plant's TS. The Main Stack Noble Gas Activity Monitor was declared inoperable, procedures were modified and it was tested in accordance with TS and declared operable. The other two monitors were already declared inoperable based on previous findings. Corrective action will be to revise surveillance procedures and perform tests which meet the TS surveillance requirements for these monitors. There were no safety consequences as a result of this event.
2451997021 | Millstone 1 | 02/28/1997 | 03/31/1997 | 9704090070 | <strong>Failure of 1-SG-1B to provide complete isolation of the SBGT system from RBVS</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1997, at 1000 hours, with the plant in the COLD SHUTDOWN condition, it was discovered that the Standby Gas Treatment System (SGTS) inlet isolation valve, 1-SG-1B, had a disc to shaft to actuator installed configuration such that the valve disc could not close the valve completely. Disassembly of the inlet valve revealed that the valve disc was installed such that the seating surface of the disc was oriented 180 degrees out from the design position. This orientation creates an approximately 1/4 inch annular gap between the disc and the seat which prevents complete isolation when the valve is closed. The SGTS inlet valves isolate SGTS from the Reactor Building ventilation system (RBVS) during normal plant operation while SGTS is used for containment venting and purging. These valves open on SGTS initiation and are designed to fail open. Technical Specification 3.7.B.3.6 requires primary containment to be vented through SGTS whenever primary containment is required. Since 1-SG-1B isolates SGTS from RBVS during vent and purge operations, the inability of this valve to fully seal could allow some of the primary containment gas to be drawn into the ventilation system and discharged out the stack, thus bypassing SGTS. This is reportable as an operation or condition prohibited by the plant's Technical Specifications. The causes of this event are: inadequate design review and installation; lack of a questioning attitude; inadequate procedural guidance; inadequate post maintenance testing. Regardless of the path, all releases are discharged via the monitored elevated stack. All releases have been well within 10CFR50, Appendix I, effluent ALARA guidelines. The safety function of 1-SG-1B is to open upon initiation of SBGT, it has been determined that the disc of 1-SG-1B being installed in this abnormal configuration would not have prevented it from performing it's safety function. Based on this and the fact that there has not been an unmonitored release, this event has no safety significance.
2451997022 | Millstone 1 | 03/15/1997 | 10/29/1997 | 9710310092 | <strong>Failure to Include Components in the ISI Program</strong><br /><i>Abstract:&nbsp;</i>On March 15, 1997, with the plant in COLD SHUTDOWN, during a comprehensive review of the Inservice Inspection (ISI) program, it was determined that the percentage requirements for ASME Code Category C-C components were not met for the first inspection period. Millstone Unit No. 1 is currently in the second inspection period. Additionally, on March 22, 1997, the same review of the ISI program identified that portions of 2" piping, Code Category B-J (Class 1 Piping), were incorrectly exempted using IWB-1220(a) of the ASME B&PV Code. The basis for exemption was applied solely based upon line size. Technical Specification 4.13, "Inservice Inspection," requires ASME Boiler and Pressure Vessel (B&PV) Code Section III, Class 1, Class 2 and Class 3 equivalent components to have ISI performed in accordance with Section Xi of the ASME B&PV Code as required by 10CFR50.55a(g). On October 1, 1997, while performing the committed system by system review additional deficiencies were identified in ASME Section XI Code Category C-B, Pressure Retaining Nozzle Welds in Vessels Class 2 components. The cause of this event was inattention to detail by the individual responsible for maintaining the ISI Program document in accordance with regulations. NNECO will provide the results of this event investigation to Engineering and reiterate the need for attention to detail in performance of assigned tasks. Other corrective actions include a revision of the ISI Program to incorporate all non-exempt components and their supports prior to startup for operating Cycle 16.
2451997023 | Millstone 1 | 04/09/1997 | 05/08/1997 | 9705150078 | <strong>Engineering Safety Features Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1997, at 0952 hours, with the plant in COLD SHUTDOWN, no fuel in the reactor, and the Fuel Pool Cooling system in service, an inadvertent Engineered Safeguards Feature (ESF) actuation occurred while testing was being conducted on a reactor vessel level indicating switch. The level switch was not properly isolated from the common sensing lines prior to valving in to a test set up, which resulted in a trip of the other level switches attached to the common sensing lines, and a subsequent ESF actuation. This actuation included the containment isolation group signals for Low and Low-Low Reactor water levels, which started the Gas Turbine Generator (GTG), and tripped the Emergency Service Water (ESW) pump which was supplying the Fuel Pool Cooling Heat Exchangers. The Fuel Pool Cooling temperatures increased no more than one degree during this event and there were no safety consequences as a result of this event. This condition was reported on April 9, 1997, pursuant to 10 CFR 50.72(b)(2)(ii), 'any event or condition that results in manual or automatic actuation of any engineered safety feature.' The immediate corrective actions were to stop all instrumentation and control work, restrict access to associated instrumentation racks, and to ensure any future instrumentation and control testing with the potential to cause an ESF actuation be conducted under direct monitoring by supervision until a personnel briefing is complete. A briefing will be conducted with Instrumentation and Control personnel to re-emphasize the expectations for the roles, responsibilities and behaviors during testing, including self checking and dual verification.
2451997024 | Millstone 1 | 04/09/1997 | 05/09/1997 | 9705130218 | <strong>Miscoordination of breakers causing loss of QA to non-QA isolation.</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1997, with the plant in COLD SHUTDOWN and fuel off-loaded, a review of a breaker panel design calculation identified several breaker to breaker coordination problems associated with the 125 VDC system. The loss of safety to non-safety isolation is due to the miscoordination between breakers 101B-29 (normal) or 101A-30 (emergency) and the other panel 11A-1 breakers. Also, 101A-31 (normal) or 101B-30 (emergency) and panel 11A-2 breakers do not coordinate. Both 125 VDC panels supply safety and non-safety related loads. The fault current due to failure of a non-safety related component on either bus would over trip the upstream safety related feeder breaker. This over trip event would prevent safety related loads on panels 11A-1 and 11A-2 from performing their safety related function. The potential safety significance of this condition is that the mis-coordination of breakers results in the loss of safety to non-safety isolation which could trip the panel supply breaker. The panels were evaluated to determine that 11A-1 and 11A-2 are functional for the current plant conditions. The panels will be reviewed and modified to eliminate the breaker to breaker mis-coordination. This event was reported pursuant to 10 CFR 50.72(b)(2)(i) as an unanalyzed condition that significantly compromises plant safety.
2451997025 | Millstone 1 | 04/24/1997 | 05/27/1997 | 9705290101 | <strong>Single Loop Jet Pump Baseline Data Collection Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1997, at 1625 hours, with the plant shutdown and the reactor in the COLD SHUTDOWN condition, it was discovered that the requirements outlined in Technical Specification Surveillance Requirement 4.6.G.3 were not being met. Technical Specification 4.6.G.3 requires acquiring the baseline data necessary to evaluate the conditions in Specification 4.6.G.1 and 4.6.G.2. When operating with one recirculation pump with the equalizer valves closed, Specification 4.6.G.2 requires checking jet pump differential pressures (dPs) are maintained within 10% of established patterns. The baseline data, required to evaluate the jet pump dPs during operation with one recirculation pump, has not been acquired each operating cycle as required by Specification 4.6.G.3. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specification. There were no safety consequences as a result of this event. In order to provide long term corrective action, specific to this issue, NNECO will submit to the NRC for approval, a revision to Technical Specification 3.6.G and Technical Specification Surveillance Requirement 4.6.G prior to startup for operating cycle 16. To ensure compliance with the Technical Specifications, a review of the Technical Specifications requirements will be performed to ensure procedures exist to adequately implement all requirements, prior to startup for operating cycle 16. A system to track licensing commitments to completion has already been established.
2451997026 | Millstone 1 | 04/14/1997 | 05/14/1997 | 9705220184 | <strong>Unqualified Coatings in the Torus</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1997, with the plant shut down and the reactor in the COLD SHUTDOWN condition, it was discovered based on a historical review that a significant amount of coating work inside the Millstone Unit 1 Torus may be unqualified. A number of different coating materials and systems have been used inside the Torus. The locations and extent of various coating systems is not clear. The potential safety consequence of this condition is that these coatings may not remain in place and intact after a loss of coolant accident (LOCA) and could compromise Engineered Core Cooling Systems (ECCS) recirculation flows. This unanalyzed condition was reported on April 16, 1997, pursuant to 10CFR50.72(b)(2)(i). An above waterline survey of the Torus will be performed to establish the present condition of the coating systems as applied based on sampling and testing to enable their precise or generic identification. The need for a hydrodynamic transport analysis will be evaluated to potentially determine the affect of delamination of coatings within the Torus on ECCS recirculation flows. The results of the survey will be used to determine the need for additional surveys and to evaluate the various coating materials and systems within the Torus. The results of the survey and the potential hydrodynamic analysis will be evaluated and, if required, sections of the Torus will be recoated.
2451997028 | Millstone 1 | 04/24/1997 | 05/27/1997 | 9706020298 | <strong>Identification of Unacceptable Failure Modes Of Safety Related Components Or Systems Resulting From Postulated Failures Of Non-Safety Related Components</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1997, at 1300 hours, with the plant in the COLD SHUTDOWN condition, an engineering review of a previously prepared Failure Modes and Effects Analysis determined that there existed several Non-QA components and circuits whose postulated failure could adversely affect the ability of safety related components or systems to perform their required safety functions. The following safety related components or systems were affected: Diesel Generator (DG), Gas Turbine Generator (GTG) and Feedwater Coolant Injection System (FWCI). This event was promptly reported on April 24, 1997, pursuant to 10CFR50.72(b)(2)(i), as an unanalyzed condition that seriously compromises plant safety. There were no actual safety consequences as a result of this event. A review of systems to identify and resolve design basis discrepancies is ongoing as part of the design basis verification program to address 10CFR50.54(f) concerns. The specific failure modes identified affecting the DG, GTG, FWCI will be corrected by plant changes or analysis. Engineering guidance delineating the detailed requirements for application of the single failure criterion will be prepared and training on the proper application of the single failure criterion will be conducted for personnel identified by the Manager, Design Engineering. All non-QA electrical interfaces with a safety system will be evaluated to assure that the ability of the safety systems to perform their required safety functions will not be affected.
2451997029 | Millstone 1 | 05/13/1997 | 06/12/1997 | 9706260036 | <strong>GL 96-01 Review Discovers Inadequate Surveillance Testing In Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1997, at 1030 hours, with the plant in Cold Shutdown, while performing a procedure review for Generic Letter (GL) 96-01 it was discovered that the Instrument Functional Test for the Reactor Building Ventilation and Refuel Floor High Radiation Monitor channels did not encompass the entire instrument channel. The Standby Gas Treatment system (SGTS) initiation relays, which drop out on a downscale trip of the radiation monitors, were not tested monthly per the Millstone Unit 1 Technical Specifications (TS). The downscale trip functions are part of the radiation monitor channels, which include these initiation relays. These relays are tested every refueling and not monthly. This condition is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by TS. The surveillance procedure was revised to ensure that the instrumentation channel was tested in accordance with the TS requirements. Subsequent performance of the surveillance procedure demonstrated satisfactory channel response, therefore no safety consequences or safety implications resulted from the event. Corrective action is to complete instrument control surveillance procedure reviews to identify any additional TS surveillances not properly performed.
2451997030 | Millstone 1, Millstone 2, Millstone 3 | 07/24/1997 | 08/25/1997 | 9708270370 | <strong>Stack Sampler Flowrate Setpoints</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1997, at 1050 hours, with the plant in COLD SHUTDOWN, while performing a self assessment on the station gaseous effluent monitoring program, it was discovered that the Unit 1 Stack Sampler Flowrate Calibration procedure included calibration tolerances for alarm setpoints which have resulted in "as left" settings that were not consistent with the Radiological Effluent Monitoring and Offsite Dose Calculation Manual (REMODCM). The Unit 1, 2, and 3 Technical Specifications (TS) require that the setpoints are determined in accordance with the methods and parameters described in the REMODCM. During periods that the settings were not consistent with the REMODCM the TS action statement was not entered. The cause of this condition was the failure to identify the inconsistency between the calibration procedure for the stack sampler flowrate monitor and the REMODCM during previous procedure reviews due to the inadequate procedure review process. The calibration procedure for stack sampler flowrate calibration has been revised to ensure the calibration tolerances are consistent with the REMODCM and the surveillance performed satisfactorily. Calibration procedures used to maintain setpoints in accordance with the methods and parameters of the REMODCM will be reviewed to ensure that the calibration tolerances are correct.
2451997031 | Millstone 1 | 07/30/1997 | 08/20/1997 | 9709030355 | <strong>Standby Liquid Control Pump Discharge Pressure Surveillance</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1997, at 1400 hours, with the plant in COLD SHUTDOWN, while performing a 50-54(f) design and licensing basis review of the Standby Liquid Control (SBLC) system, it was determined that the surveillance test for the SBLC pumps did not meet Technical Specification (TS) 4.4.A.1 requirements. The TS requires that the pumps must have a capacity of at least 40 gpm at a system head corresponding to a reactor vessel pressure of 1225 psig. The current test procedure requires a pressure of 1225 psig at the pump discharges. This acceptance criteria value for the pump discharge pressure does not consider the system line losses to the vessel, any differences in elevation between the SBLC pumps discharge pressure gauge and the vessel nozzle, or instrument inaccuracy. The cause of this condition was development of the surveillance procedure with incorrect acceptance criteria due to an inadequate procedure review process. Contributing causes to this event are the failure to identify this discrepancy in previous TS compliance reviews, and the inadequacy of the TS to capture plant operating requirements. The procedure acceptance criteria did not include the system pressure losses identified in the system design description. No immediate corrective actions were needed since the SBLC is not required to be in service. The system design basis will be reviewed to determine the correct pump discharge pressure acceptance criteria and the Standby Liquid Control system pumps will be tested using the revised procedure prior to operating cycle 16.
2451997032 | Millstone 1 | 07/31/1997 | 09/02/1997 | 9709080224 | <strong>Service Water Effluent Monitoring Composite Sampling</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1997, at 1500 hours, with the plant shutdown and the reactor in COLD SHUTDOWN, it was discovered that the sampling of the Service Water (SW) for radiological effluent monitoring had not been performed in accordance with the Radiological Effluent Monitoring and Offsite Dose Calculation Manual (REMODCM) as required by Technical Specification 4.8.C.1.1. The REMODCM specifies that the daily sample of the Reactor Building SW be composited proportionate to the flow rate for the weekly sample. During a self-assessment of activities for the REMODCM, it was discovered that the weekly composite was not being done proportionate to the SW flow rate. Equal aliquots were taken from each of the daily samples to produce the composite. The cause of this event is inadequate procedure guidance to ensure composited samples are prepared proportional to system flow rate due to a previously inadequate procedure review process. The sampling procedure has been revised to sample the SW proportional to the system flow rate. Other chemistry sampling procedures used to monitor effluents in accordance with the REMODCM will be reviewed to ensure the sampling methods are correct.
2451997033 | Millstone 1 | 08/01/1997 | 09/02/1997 | 9709080230 | <strong>Unmonitored Airborne Radioactivity Release Paths</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1997, at 1300 hours, with the plant in COLD SHUTDOWN, it was determined that several conditions existed on site which could create potential unmonitored airborne radioactivity release paths. As an example, roll-up doors in the turbine and solid radwaste buildings are opened at times without appropriate process controls in place to provide a method of monitoring the pathway for potential releases. Additionally, walkarounds have identified several structural openings in the turbine hall, and documentation indicating an airborne release evaluation is not apparent. The cause of this condition was the lack of an adequate monitoring program. The immediate corrective action was to place low volume air samplers at the areas in question. The work control administrative procedure has been revised with appropriate process controls in place to provide a method of monitoring of pathways for potential releases. Radiological assessments of these conditions will be performed and a structured monitoring program developed based on the assessment prior to startup from this refueling outage.
2451997034 | Millstone 1, Millstone 2 | 08/12/1997 | 09/11/1997 | 9709220022 | <strong>Unit 1 Switchgear Failure During Unit 2 High Energy Line Break</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1997, at 1500 hours, a deficiency was identified with the original assumptions for a postulated High Energy Line Break (HELB) in the Millstone Unit No. 2 Main Steam System. The Architect Engineering firm (A&E), Bechtel, performed the original analysis assuming that the limiting HELB occurred in a 12-inch steam line leading to the Main Turbine bypass valves. Postulated breaks downstream of the Main Turbine stop valves were not analyzed since it was assumed that the stop valves would rapidly close and terminate blowdown. This assumption was not conservative since there is a time delay before the stop valves receive a signal to close. The increase in time required for the valves to close results in more limiting breaks downstream of the stop valves which significantly increases calculated pressure in the Unit 2 Turbine Building. The door on the South side of the Unit No. 2 Turbine building could fail due to the higher pressure reached during the accident. This door leads to a corridor between the Unit 1 Turbine Building and the Unit 2 Turbine Building which could allow steam from the HELB to enter the switchgear room for the Unit 1 Emergency Onsite Power Supply System. The cause of this condition was an incorrect assumption for HELB analysis performed by the A&E, which was not identified during the original licensee review of the analysis. Engineering will evaluate the replacement of door 203-31-001 with a HELB door, the need for blowout panels in the Unit 2 Turbine Building external siding, and qualifying other paths and barriers between Unit 1 and Unit 2 prior to Unit 2 entering Mode 4. An adequacy review will be conducted of HELB barriers in Unit 1 for Unit 2 HELB events by March 1, 1998. A review of the Unit 1 HELB analysis will be conducted and the analysis revised as required for issues similar to those described in this LER by March 1, 1998.
2451997035 | Millstone 1 | 08/26/1997 | 09/25/1997 | 9709300286 | <strong>Emergency Core Cooling Subsystem Actuation Limiting Condition for Operation Not Met</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1997, at 1420 hours, with the reactor in the COLD SHUTDOWN condition, it was discovered during procedure reviews that the requirements for the minimum number of operable instrument channels per trip system for the Containment Spray 2/3 core height interlock as listed in Technical Specification (TS) 3.2.B, "Emergency Core Cooling Subsystem Actuation," were not met. Table 3.2.2 of this specification requires a minimum of 2 operable instrument channels per trip system for the 2/3 Core Height Containment Spray Interlock. The physical plant design is equipped with 1 level instrument in each of the two trip systems. Each trip system prevents the opening of the associated train of drywell and torus spray valves unless reactor vessel water level is equal to or greater than 2/3 core height. This event was caused by human error (technical oversight) when the interlock was added to the TS and adequate validation was not performed to ensure that the change was correct. A review will be performed to determine whether the containment spray interlock should be controlled in the plant TS. Depending on the outcome of that review, a TS change will be submitted, prior to startup for operating cycle 16, to either remove the interlock or ensure that it conforms to the plant design basis.
2451997036 | Millstone 1 | 09/29/1997 | 10/27/1997 | 9710290129 | <strong>Fire Pump Room Flooding Through Floor Drain During a Hurricane</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1997, with the plant in the COLD SHUTDOWN condition, through configuration management efforts ongoing in response to the 50.54f letter, it was determined that the fire pump house was vulnerable to flooding in a Postulated Maximum Hurricane (PMH) event. The Fire Water system provides makeup for the Isolation Condenser system during design basis flooding conditions. The flood protection actions to prevent flooding during a PMH are contained in Off Normal Procedure ONP-514A, "Natural Occurrences". This procedure outlines the requirements to plug floor drains and close flood gates 12 hours prior to the anticipated arrival of a hurricane. The building contains a total of three drains which provide the potential for flooding. Two of the three are traditional floor drains which are addressed by ONP-514A and plugged. The third drain path is a pressure relief fitting on the discharge of the relief valve from the Diesel Fire Pump which is not included in the procedure. The cause of this event was a weakness in the design change process in place in the early 80's which failed to identify this potential leakage path while modifying the building to provide flood protection. NNECO will evaluate the shutdown path for the PMH event, inspect the fire pump house to identify any additional leakage paths, and implement a plan to address the specific leakage path identified prior to restart from refueling outage 15.
2451997037 | Millstone 1 | 09/30/1997 | 10/30/1997 | 9711030018 | <strong>Unmonitored Release Path Due to Radioactive Ash in the House Heating Boiler</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1997, at 1500 hours, with the plant in COLD SHUTDOWN, the House heating boiler ash was found to be slightly contaminated. This condition was discovered during a count room screening for release of the boiler ash as a result of preparations to place the heating boiler in service for the winter. The contamination is the result of an initial contamination event during 1975 and additional tube leaks since that time. It is postulated that if the ash on the fire side of the boiler contains radioactive constituents, some of the particulate matter could be discharged through the boiler stack. Since the potential exists for some of the ash to be released as a result of normal operation, this condition should have been considered as a potential unmonitored release path since the boiler stack is not routinely sampled, and public dose as a result of this operation needed to be considered. A release of all of the activity in the ash would result in a dose in the range of 1E-05 millirems. This is below the 10CFR50, Appendix I limits. The cause of this condition was a failure to recognize this as an unmonitored release path for airborne effluents in accordance with the requirements of Technical Specification 4.8.D.4. The heating boiler was tagged out until a safety evaluation could be completed and the chemistry procedure revised to restrict boiler usage to contamination levels below 2E-05 uCi/ml. In addition potential unmonitored release pathways will be re-evaluated and the dose consequence of potential unmonitored releases will be incorporated in the annual effluent report.
2451997038 | Millstone 1 | 10/08/1997 | 11/05/1997 | 9711130393 | <strong>Reactor Building Roof Horizontal Shear Loads</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1997, at 1430 hours, with the plant in COLD SHUTDOWN, it was determined that the Reactor Building roof was not analyzed for the Millstone Unit No. 1 seismic Safe Shutdown Earthquake (SSE). The roof decking and welds to the roof steel were designed to transfer horizontal shear loads for the Operating Basis Earthquake (OBE). The existing welds are at their full capacity based on the OBE analysis, and the higher SSE loads have not been addressed. It is expected that the welds would exceed the code allowable stresses during the SSE loads. The function of the Reactor Building roof is to enclose the reactor and associated equipment and to provide secondary containment. The cause of this condition is failure to analyze the Reactor Building roof for the higher loads during a SSE due to a limited sampling method used during the assessment of the seismic capacity of the facility. Administrative controls are in place to prevent fuel movement until the Reactor Building roof has been qualified for the SSE. An analysis of the Reactor Building roof will be performed for the SSE loads and potential modifications made to the roof prior to startup from this refueling outage.
2451997039 | Millstone 1 | 10/31/1997 | 11/25/1997 | 9712010233 | <strong>Suppression Pool Bypass Path During Purge and Vent Operations</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1997, at 1020 hours, with the plant in COLD SHUTDOWN, it was discovered during a review of industry events that a valve alignment could exist during primary containment purging which would create a flow path that would allow the steam released during a Loss Of Coolant Accident (LOCA) to bypass the suppression pool if the inboard containment isolation valves fail to close. This bypass flow path could degrade the pressure suppression function of the suppression pool and possibly over-pressurize the containment. This valve alignment occurs when inerting or purging the drywell and suppression chamber simultaneously during plant startup or shutdown. The root cause was a design error, in that no interlock precluded the bypass flow path, nor did design output or the Updated Final Safety Analysis Report caution against this alignment. The operating procedures permitted simultaneous purging or inerting of the drywell and suppression chamber. Appropriate system operating procedures will be revised prior to startup from this outage to prohibit simultaneous opening of the drywell and suppression chamber inboard isolation atmospheric control valves whenever primary containment is required. A change to the UFSAR will be made to specify that the inboard isolation valves may not be operated in a manner that would provide a flow path that would bypass the suppression pool prior to startup from this outage. The potential for other lineups that may result in a similar bypass flow path Will be evaluated prior to startup from this outage.
2451997040 | Millstone 1 | 11/03/1997 | 12/03/1997 | 9712050067 | <strong>Missed Technical Specification Surveillances</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1997, at 0730 hours, with the plant in COLD SHUTDOWN, while performing procedure reviews during a Technical Specification review for Millstone Unit 1, it was discovered that the required monthly Instrument Checks were not performed for the Isolation Condenser Steam Line High Flow and Condensate Line High Flow Indicators as specified by Technical Specification (TS) Table 4.2.1. It was also discovered at 0930 hours on November 5, 1997, that the required monthly Instrument Checks were not performed for the Rod Block Monitor as specified by TS Table 4.2.1. Although Functional Tests of these instruments were performed on a monthly basis, as required by the TS, failure to perform the Instrument Checks constitute a missed surveillance with respect to compliance with the TS. The cause of this oversight was personal error when the procedures were developed, reviewed, and approved to implement Technical Specification required testing. Respective surveillance procedures will be revised to include the required Instrument Checks as specified in the Millstone Unit No. 1 TS and implemented prior to startup for operating cycle 16.
2471997001 | Indian Point 2 | 01/16/1997 | 02/18/1997 | ML10043107 | <strong>Automatic Start of the Auxiliary Feedwater Pumps and Steam Generator Blowdown Isolation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 16, 1997, with the unit operating at 100% power, the motor driven auxiliary feedwater pumps automatically started and the steam generator blowdown isolation valves automatically closed. At that time, Instrument and Control technicians were performing a reactor protection surveillance test. The test was stopped to investigate the cause of the above actuations. The test includes verification of the steam generator low level logic. Test switches are used to actuate the logic relays and to open the logic output circuit in order to preclude any equipment actuation during testing. Verification that the logic has been established is done by observing that approximately 125 VDC exists across the open logic output. A digital voltage meter is used to make this observation. The digital voltage meter was found to have the test leads inserted into the ammeter position input, instead of the voltmeter position input as required. The low impedance of the ammeter measuring circuit shorted out the open logic output circuit causing the actuating relays for the motor driven auxiliary feedwater pumps and steam generator blowdown isolation to operate. Following operator verification that the plant was stable, the auxiliary feedwater pumps were secured and returned to standby and steam generator blowdown was removed from isolation.
2471997002 | Indian Point 2 | 01/26/1997 | 02/25/1997 | ML10043111 | <strong>Reactor Trip due to Steam Generator Low Level</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1997, with reactor power at approximately 14 percent and a unit shutdown in progress, a manual turbine trip was initiated due to steam generator level variations. Feedwater regulating valves for 21, 22, 23, and 24 steam generators had been placed in manual prior to the trip due to inconsistent response experienced during the shutdown. Feedwater flow to the steam generators was being controlled primarily with 21 Main Boiler Feed Pump speed. 21 Main Boiler Feed Pump recirculation valve opened as designed on low flow, causing a reduction in feedwater to all steam generators. A manual turbine trip was initiated in accordance with management direction, which caused a further reduction in steam generator levels due to "shrink." The combined effect of reduced feedwater flow and "shrink" resulted in a low steam generator level reactor trip. All control rods fully inserted and the generator tripped 30 seconds following the turbine trip as designed. Following the reactor trip all safety-related equipment performed as required with the exception of the 21, 22, and 24 Main and 23 Low-flow Feedwater Regulating Valves which did not fully close, as required. A multi-discipline team was promptly assembled to investigate the cause of the Main and Low-flow Feedwater Regulator valve non-closures. The reactor was safely brought to hot shutdown conditions.
2471997003 | Indian Point 2 | 02/27/1997 | 03/31/1997 | ML10043108 | <strong>Plant Shutdown due to Excessive Leakage through Valve 838D</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1997, with the plant at hot shutdown and the reactor subcritical at zero percent power, the restrictions of Indian Point Unit No. 2 Technical Specification 3.1.F.2.b were triggered as a result of excessive seat leakage detected through RCS/RHR pressure isolation check valve 838D. Test data taken during the performance of test procedure PT-V16 determined that a leakage rate greater than that allowed by Technical Specification 3.1.F.2.b(1)(c) existed. Consequently, in accordance with the requirements of Technical Specification 3.1.F.2.b(2), an orderly plant shutdown was initiated and the reactor was safely brought to cold shutdown conditions.
2471997004 | Indian Point 2 | 03/05/1997 | 04/04/1997 | ML10043108 | <strong>Leak Testing of Reactor Coolant System at Normal Operating Pressure</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1997, during a plant outage, it was discovered that leak testing of the reactor coolant system, which is required by Technical Specification 4.3.a whenever the reactor coolant system is opened, was sometimes performed at the ASME Section XI requirement of normal operating pressure (2235 psig) as opposed to the test pressure required by Technical Specification 4.3.a (2335 psig). A review of plant maintenance records determined that, since 1993, there were three instances where the test should have been performed at the higher pressure. During this time period, there have been three successful performances of the reactor coolant system leak test at the required pressure (2335 psig). The reactor coolant system was last leak tested in March 1997 at the required pressure prior to the most recent return to service of the plant.
2471997005 | Indian Point 2 | 03/16/1997 | 04/15/1997 | ML10043108 | <strong>Unexpected Closure of Steam Generator Blowdown Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On March 16, 1997, with a unit power escalation in progress, an automatic closure of the steam generator blowdown isolation valves occurred as a result of a high alarm on the Steam generator radiation monitor R-49. The actuation of these isolation valves occurred due to a conservatively low alarm setpoint for radiation monitor R-49. The blowdown was re-established upon successful completion of steam generator leak identification procedure steps, in Abnormal Operating Instruction A 1.2, Steam Generator Tube Leak. Although the steam generator blowdown isolation valves are Automatic Containment Isolation Valves, which are Engineered Safety Feature (ESF) components, their closure in this case was in response to low level radioactivity in the steam generator blowdown stream and not a Containment Isolation ESF signal. The health and safety of the public were not adversely affected by this event since the activity released was significantly below the 10 CFR Part 20 limits.
2471997006 | Indian Point 2 | 03/20/1997 | 04/21/1997 | ML10043108 | <strong>Open Electric Penetration Area Door creates Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 20, 1997, with reactor power at 100 percent, non-operations personnel were transporting scaffolding materials through the pipe penetration area (PPA) to the electrical penetration area (EPA). A door between these two areas was held open longer than needed for personnel passage to facilitate the transfer of the scaffold material. This door is an environmental barrier intended to preclude postulated design basis accident harsh environments from entering the EPA. This area has not been evaluated or qualified for harsh environs per 10CFR50.49. The result of keeping the door to the EPA open longer than needed for personnel passage is the that the EPA becomes unanalyzed for that period of time. Nuclear Plant Operators (NPO's), as part of their routine inspections, check that the door remains in the closed position. This activity is procedurally required to be performed four times a day (approximately, every 6 hours). The door was immediately closed once discovered by a nuclear plant operator on routine tour of the plant. The plant remained in operation throughout this event.
2471997007 | Indian Point 2 | 04/02/1997 | 05/02/1997 | ML10043108 | <strong>Technical Specification 3.0.1 Entry</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 2, 1997, with the unit operating at 100% power, an unplanned entry into Technical Specification 3.0.1 took place due to equipment inoperability. Emergency Diesel Generator (EDG) 23 had been out of service for scheduled maintenance. EDG 21 was run to establish operability in accordance with Technical Specification 3.7.B.1 because an alarm switch had improperly actuated in the output breaker that was being used for EDG 23 on the previous day. Following the run of EDG 21, a control power fuse blew which rendered EDG 21 inoperable. Since EDG 23 was already out of service, the loss of EDG 21 resulted in the unplanned entry into Technical Specification 3.0.1. A failed jacket water pressure switch caused the EDG 21 control power fuse to blow. Within one hour of the entry into Technical Specification 3.0.1, a plant shutdown was commenced in accordance with Technical Specification 3.0.1. Approximately four hours later, the plant exited Technical Specification 3.0.1 when EDG 23 was returned to service (after the EDG 23 output breaker had been repaired and satisfactory operation was demonstrated). At this time the unit had already been reduced to approximately 42% power. Following operator verification that the plant was stable, power ascension to 100% was commenced. The failed jacket water pressure switch was replaced, and EDG 21 was subsequently returned to service.
2471997008 | Indian Point 2 | 04/24/1997 | 05/15/1998 | ML10043112 | <strong>Technical Specification 3.0.1 Entry</strong><br /><i>Abstract:&nbsp;</i>On April 24,1997, with the unit operating at 100% power, an unplanned entry into Technical Specification 3.0.1 took place due to equipment inoperability. Emergency Diesel Generator (EDG) 22 had tripped on overspeed during a monthly surveillance test. This placed the plant in a limiting condition of operation that required EDG 21 and 23 be run for operability. Following the operability run of EDG 23, a control power fuse blew which rendered EDG 23 inoperable. Since EDG 22 was already out of service, the loss of EDG 23 resulted in the unplanned entry into Technical Specification 3.0.1. A failed jacket water pressure switch caused the EDG 23 control power fuse to blow. Within one hour of the entry into Technical Specification 3.0.1, a plant shutdown was commenced in accordance with Technical Specification 3.0.1. Approximately six and one half hours later, the plant exited Technical Specification 3.0.1 when EDG 23 was returned to service following replacement of the jacket water pressure switch and a satisfactory operability determination. At this time the unit had been reduced to approximately 11% power. Following operator verification that the plant was stable, power ascension was commenced.
2471997009 | Indian Point 2 | 05/02/1997 | 06/02/1997 | ML10043109 | <strong>ESF Automatic Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>At 20:35 on May 2, 1997 with the reactor coolant system (RCS) temperature at 260 degrees Fahrenheit and RCS pressure at 378 PSIG during cooldown in preparation for the 1997 refueling outage, a station ventilation radiation monitor R-44 alarm was received at 3.47 E-5 [symbol omitted] Ci/cc, which resulted in an isolation of the vapor containment (VC) purge supply and exhaust valves and activation of the weld channel pressurization system (WCPS) to the VC purge valves. Although the VC purge supply and exhaust valves and the WCPS to the VC purge valves, are engineered safety feature (ESF) components, their closure was in response to low levels of radioactivity and not a containment isolation signal as a result of an ESF actuation.
2471997010 | Indian Point 2 | 05/01/1997 | 09/09/1997 | ML10043110 | <strong>Safety Injection Actuation While Testing Main Steam Safety Valves</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1997 at 00:01 the main generator at Indian Point Unit No. 2 was taken off line for the 1997 refueling outage. With the plant at hot shutdown and during the performance of test PT-R6, "Main Steam Safety Valve Setpoint Determination," one main steam safety valve, MS-46C, on the main steam line for steam generator 23, stuck open. This caused the initiation of a Safety Injection (SI) signal at 03:08:19 due to the differential pressure between one steam generator and two others. The SI signal generated a "stripping" signal to the 480 VAC buses and a start signal to the emergency diesel generators (EDGs). Loads "stripped" from the 480 VAC buses and the EDGs started as expected. The SI logic circuit then commenced to sequentially reload the buses. During the EDG load sequence, a motor-driven auxiliary feedwater pump (23AFWP) and containment fan cooler unit (25FCU) failed to start as required. In accordance with the emergency operating procedures (EOPs), operators manually started 23AFWP and 25FCU. At 03:21:51 the SI was reset in accordance with procedure. NRC approval for relief from the ASME Section XI testing requirements pertaining to the main steam safety valves was requested. Subsequent to receiving NRC verbal approval, the reactor was safely brought to cold shutdown conditions. During this event, the Isolation Valve Seal Water System (IVSWS) did not perform as described within the UFSAR. The health and safety of the public were not affected by this event.
2471997011 | Indian Point 2 | 05/01/1997 | 06/02/1997 | ML10043109 | <strong>ESF Automatic Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1997, with the unit at zero power, while preparing for steam generator safety valve testing prior to cooldown for the 1997 refueling outage, an automatic containment isolation valve closure occurred as a result of a high alarm on the steam generator blowdown radiation monitor R-49. The blowdown was re-established upon subsequent investigation based on successful completion of steam generator tube leak identification procedure steps of Abnormal Operating Instruction, A 1.2, Steam Generator Tube Leak. This isolation occurred due to a conservatively low alarm setpoint for the steam generator blowdown radiation monitor R-49 and the release, through the blowdown pathway, of low level radioactivity from the steam generators. Although these steam generator blowdown isolation valves are automatic containment isolation valves, which are Engineered Safety Feature (ESF) components, their closure was in response to low level radioactivity and not a containment isolation signal as a result of an ESF actuation.
2471997012 | Indian Point 2 | 05/09/1997 | 09/05/1998 | ML10043114 | <strong>IVSWS Leakage Greater Than Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>Surveillance tests of containment isolation valves were performed during the 1997 refueling outage, with containment integrity not required. The as-found leakage rate for valve FCV-625 sealed with water from the Isolation Valve Seal Water System exceeded the 14,700 cubic centimeters per hour leakage rate Technical Specification limit for containment isolation valves sealed by this system. This valve was repaired and tested prior to plant startup to ensure operability.
2471997013 | Indian Point 2 | 06/08/1997 | 08/04/1998 | ML10043113 | <strong>Plant Personnel Review of Test Data Received from an Offsite Test Laboratory</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1997, with the reactor at zero percent power and the plant in cold shutdown, it was determined that test data pertaining to the "as-found" lift set points for pressurizer safety valves did not meet the test acceptance criteria as required by Technical Specification 3. 1.A.3.c and American Society of Mechanical Engineers (ASME) Section XI, OM-1. An evaluation of the effect from "as-found" safety valve setpoints on various postulated accident response and outcomes has been completed, and indicates that the Updated Final Safety Analysis Report (UFSAR) analysis would remain bounding for the worst case safety valve setpoint of 2581 psig. During the 1995 Refueling Outage (RFO) a plant modification permanently removed the pressurizer enclosure roof. The temperature effect of removing the pressurizer enclosure roof combined with a subjective definition of "ambient temperature," per the requirement of recently implemented Section XI, OM-1, resulted in the 1995 temperature test criteria not being reflective of the as installed environment.
2471997014 | Indian Point 2 | 06/17/1997 | 07/17/1997 | ML10043109 | <strong>Non-compliance with Overpressure Protection System Technical Specification</strong><br /><i>Abstract:&nbsp;</i>Between approximately 0230 hours on June 14, 1997 and approximately 1655 hours on June 17, 1997, while the plant was at cold shutdown with reactor coolant system at atmospheric pressure and temperature at approximately 90F, pressurizer level was greater than 30 percent concurrent with an inoperable Overpressure Protection System (OPS). This is a condition prohibited by Technical Specifications. The non-compliant condition occurred in connection with a vacuum fill and vent evolution of the reactor coolant system and is attributable to inadequate procedural guidance, a scheduling deficiency, and inadequate operator knowledge of the OPS and applicable Technical Specifications. Upon discovery of the non-compliant condition, pressurizer level was reduced to 30 percent. The safety significance of this event is minimal as the reactor coolant system was not pressurized by any mechanism that the OPS protects against during the time the OPS was inoperable.
2471997015 | Indian Point 2 | 06/26/1997 | 07/28/1997 | ML10043116 | <strong>Valve 1863 Position Creates the Potential for the Plant to be Outside Design Basis.</strong><br /><i>Abstract:&nbsp;</i>During the 1997 refueling outage, Con Edison personnel recognized that a check-off list specified the closed, rather than the open, position for manual valve 1863, which is in a high-head recirculation alternative flow path described in the UFSAR. Valve 1863 must be opened to provide a flow path for core decay heat removal in the event of multiple active failures of safety related equipment or a passive failure of the suction piping to the safety injection pumps. Certain accident scenarios have the potential -or excessive post-accident radiation fields in the areas which provide access to the valve and at the location of the valve. This could render the flow path unavailable for use, if required, as the valve could not be accessed to be opened. The position of valve 1863 was changed to "open" prior to restart from the 1997 refueling outage. Further, a modification was completed on valve MOV-883 to address the concern of a single failure in an electrical system resulting in loss of capability to perform a safety function in accordance with Branch Technical Position EICSB 18. The Corrective Actions section identifies the completed, and ongoing activities. The currently ongoing corrective actions are scheduled for completion by March 1, 1999.
2471997016 | Indian Point 2 | 07/02/1997 | 08/01/1997 | ML10043110 | <strong>Auto-Start Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1997, with the unit at hot shutdown, 480V Bus 3A was inadvertently de-energized. This caused the three Emergency Diesel Generators (EDGs) to start and Auxiliary Feedwater Pump (AFP) 21, which was running at that time, to trip. At the time of this event, 480V Bus 3A was being supplied from 480V Bus 2A through a tie breaker. The normal supply breaker for Bus 3A was tagged out due to maintenance. The tie breaker between Buses 2A and 3A was erroneously tripped by a mechanic who was working on an adjacent breaker cubicle. Following the event, the tie breaker between Buses 2A and 3A was reclosed and Bus 3A was re-energized. AFP 21 was restarted and the EDGs were secured and returned to automatic status.
2471997017 | Indian Point 2 | 07/21/1997 | 06/24/1999 | ML10043118 | <strong>Review of monthly radiation monitor performance test data</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1997, with the unit at approximately 90 percent power, the results of a radiation monitoring system performance test were reviewed and determined to be unsatisfactory. The failure of performance test PT-M86 is attributed to a calibration constant being set incorrectly. The calibration constant is used to calculate the gaseous radioactivity in the in-service Large Gas Decay Tank that is then compared against the alarm set point. Evaluation of the results indicated that the calculated activity value of Large Gas Decay Tank gaseous monitor (R-50) activity was nonconservatively low. Once noticed, the calibration constant was restored to the proper value and, subsequently, the radiation monitor was declared operable.
2471997018 | Indian Point 2 | 07/26/1997 | 11/28/1997 | ML10043111 | <strong>Buchanan's Substation Ringbus Breaker Causes IP2 Turbine Overspeed Trip And Reactor Trip.</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1997, with the unit at 99.4 percent power, misoperation of a protective directional relay in transformer TA-5 at the Buchanan substation resulted in tripping the power transmission system load from the IP2 main generator. The load shed of the main generator's external loads caused the main turbine to trip on mechanical overspeed which in turn generated a reactor trip. The main generator electrical output to the unit auxiliary transformer increased in frequency due to the overspeed condition of the main turbine, which caused an increase in the rpm of all electrical pump motors connected to the unit auxiliary transformer at the time of the event. Approximately seven (7) seconds later an overcurrent condition on the unit auxiliary transformer tripped the electrical generator. The frequency mismatch at the time of transfer between the 6.9 kV buses powered by the unit auxiliary transformer and those powered by 138 kV supply to the station auxiliary transformer prevented automatic transfer of loads to the station auxiliary transformer. This caused loss of power to four (4) 6.9kv buses and their associated loads. Loss of power to the reactor coolant pumps (RCP's) brought the plant into a natural circulation cool down condition. The natural circulation condition lasted 40 minutes, after which a RCP was started and forced circulation was restored. Plant systems operated as designed.
2471997019 | Indian Point 2 | 07/31/1997 | 09/02/1997 | ML10043110 | <strong>Closure of steam generator blowdown isolation valves that also function as ESF automatic containment isolation valves</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1997, during a unit power escalation with power at approximately 92 percent, an automatic containment isolation valve closure occurred as a result of the high alarm setting being exceeded on the steam generator blowdown radiation monitor R-49. The blowdown was reestablished upon subsequent investigation based on successful completion of procedural guidance provided in System Operating Procedure (SOP) 12.3.2. This isolation occurred due to a conservatively low alarm setpoint for the steam generator blowdown radiation monitor R-49. Although these steam generator blowdown isolation valves are automatic containment isolation valves, which are Engineered Safety Feature (ESF) components, their closure was in response to low level radioactivity and not a containment isolation signal as a result of an ESF actuation.
2471997020 | Indian Point 2 | 08/06/1997 | 09/05/1997 | ML10043110 | <strong>Technical Specification 3.0.1 Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1997 at 1945 hours with the plant at 100% power, the Technical Specification 3.0.1 was entered pending an operability confirmation for the three pressurizer safety valves. Technical Specification 3.1.A.3.b requires that all three pressurizer code safety valves shall be operable whenever the reactor is critical. Additionally, Technical Specification 3.1.A.3.c requires the pressurizer code safety valve lift settings shall be 2485 psig with a +/- 1% allowance for error. Based on differences between recent temperature measurements made at power and temperatures previously used in valve testing the operability of the safeties was questioned. The unit was shutdown until the safety valve operability could be confirmed.
2471997021 | Indian Point 2 | 08/23/1997 | 10/31/1998 | ML10043116 | <strong>Reactor Trip Due to De-energization of 6.9 kV Breaker Logic Test Relay</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1997, with the unit operating at 100% power, a reactor trip occurred with all control rods fully inserting. This initiated a turbine trip, and the generator tripped 30 seconds following the reactor trip as designed. The cause of the reactor trip was traced to the de-energization of a logic relay which monitors the 6.9 kV breaker for Reactor Coolant Pump 23. There was no condition that would have required the breaker to open during this event, and the breaker did not open. The resistance across a relay contact in the coil circuit of the logic relay was found to vary with no observable plunger motion. The cause of this resistance variation was corrosion on the surfaces of the relay contacts. Such variation can cause intermittent interruption of the circuit. This is the most probable cause of the de-energization of this logic relay which in turn caused the reactor trip. All safety-related equipment performed as designed, and the reactor was safely brought to hot shutdown conditions.
2471997022 | Indian Point 2 | 10/28/1997 | 11/26/1997 | ML10043116 | <strong>Westinghouse Fuel Rod Internal Pressure/Oxidation Calculation</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, with the unit in cold shutdown mode, Westinghouse informed Con Edison, along with other utilities, of issues regarding fuel rod internal pressure (RIP), the status of the Westinghouse PAD code, and concerns with fuel rod design criteria. When initially notified, Con Edison was advised that Westinghouse could not preclude the possibility that plants with Zircaloy-4 clad integral burnable absorber fuel (IFBA) may be outside their design criteria due to fuel clad gap reopening, in that the 17 percent maximum cladding oxidation limit, as delineated in 10 CFR 50.46, may be exceeded. Since that time, and based on the LOCA analyses which have been performed to date by Westinghouse, an initial pre-transient 12 percent oxidation has been established as a screening criteria to permit assessment of plants regarding compliance with the 17 percent maximum cladding oxidation criterion of 10CFR 50.46. Based on the screening criteria, plants with IFBA rods in the first half of their operating cycle or returning from a refueling outage are determined to be in compliance due to either no gap reopening or low levels of pre-transient oxidation due to steady-state corrosion accumulation. Subsequent communication from Westinghouse indicates that a plant specific fuel rod performance assessment has been completed for Indian Point Unit 2 Cycle 14. Specifically, Westinghouse has informed us that the Indian Point Unit 2 Cycle 14 Reload Safety Evaluation (RSE) continues to remain valid through 23110 MWD/MTU.
2471997023 | Indian Point 2 | 10/29/1997 | 11/28/1997 | ML10043113 | <strong>Inadvertent Closure of Containment Isolation Valves During Maintenance</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1997, with the unit at cold shutdown, PCV-1228, an instrument air supply line isolation valve to containment, was inadvertently closed while Con Edison personnel were applying protection under a tagout in preparation for maintenance activities on valve PCV- 1229. The inadvertent closure of PCV-1228 occurred when the control fuses for valve PCV-1229 were removed in accordance with the tagout. As a result of the isolation of the instrument air supply, several containment isolation valves swapped to their fail-safe positions. Upon identification of the loss of instrument air to containment, the control fuses for valve PCV-1229 were reinstalled, restoring the instrument air supply to containment. All valves affected returned to their pre-event positions. The health and safety of the public were not affected by this event.
2471997024 | Indian Point 2 | 10/31/1997 | 10/09/1998 | ML10043115 | <strong>Westinghouse Model DB-50 Breaker Investigation</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1997, with the unit at cold shutdown while performing a comprehensive investigation of the Westinghouse Model DB-50 breakers, preliminary results of testing and inspection revealed two items affecting breaker performance that were voluntarily reported. These items included low trip bar forces and winding of the trip pan spring. The diagnostic testing that revealed these two items showed the critical nature of closing coil de-energization timing to breaker latching, the importance of trip bar forces, the possibilities of physical impairments of certain components, and the correlation of closing forces to certain gap adjustments. Other items affecting breaker performance were found from this testing. Also, a modification of the breaker closing coil auxiliary relays was made based on documentation on similar auxiliary relays in other Westinghouse breakers. A plan to test the DB-50 breakers using settings, adjustments, and modifications based on optimizing the items found during diagnostic testing was developed and implemented. Following satisfactory testing, DB-50 breakers were returned to service.
2471997025 | Indian Point 2 | 12/29/1997 | 01/28/1998 | ML10043111 | <strong>Inadequate Surveillance Requirements For Radioactive Liquid Effluent Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1997, while the plant was at 0% power in cold shutdown, Con Edison declared flow instrumentation associated with the liquid radwaste effluent and steam generator blowdown effluent lines to be inoperable. Indian Point Unit No. 2 Technical Specification Table 4.10-2, Items 3a and 3b requires that a channel functional test be performed at quarterly intervals for the liquid radwaste effluent line and steam generator blowdown effluent line flow instrumentation, respectively. A channel functional test is defined as the injection of a simulated signal into the channel to verify operability. A recent review of past records for these flow instruments revealed that the channel functional tests had not been performed in accordance with Technical Specification requirements. Upon discovery of this condition, new test procedures were developed and implemented to address the appropriate test methodology. The health and safety of the public were not effected by this event.
2491997001 | Dresden 3 | 02/09/1997 | 03/06/1997 | 9703120391 | <strong>High Pressure Coolant Injection Low Flow Setpoint Calibration Found Outside Technical Specification Limit Due to Inattention to Detail During the Recording and Review of Previous Calibration Data.</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1997, during the performance of Dresden Instrument Surveillance 2300-02, High Pressure Coolant Injection Flow Calibration, the low flow switch setpoint was found outside of technical specification limits. It was determined that during the previous calibration, the low flow switch was left outside of administrative limits due to inattention to detail on the part of the technicians in the data recording and supervisors reviewing the completed data. The individuals involved in this event were disciplined in accordance with Dresden Station Policy. The safety significance of this event is minimal because the low flow switch causes the minimum flow bypass valve to open on lowering pressure to ensure adequate recirculation flow through the pump and does not effect the ability of the High Pressure Coolant Injection System from performing its safety function.
2491997002 | Dresden 3 | 03/22/1997 | 04/21/1997 | 9704280012 | <strong>Licensed Operators Fail to Perform Tech Spec LCO Required Surveillance Due to Programmatic Failure in Task Methodology and Human Error.</strong><br /><i>Abstract:&nbsp;</i>On 3/23/97, while reviewing previous shifts log book entries, a Nuclear Station Operator recognized that DOS 0040-09, Unit 3 Operating Power Sources and Distribution, was not being performed every 8 hours while the Unit 3 Diesel Generator was declared inoperable, as required by Technical Specification 3.9.A.2.a. The Operating Surveillance was immediately performed to bring the station in compliance with the Tech Spec requirement, along with performance of the surveillance at a conservative frequency of every subsequent 6 hours to assure compliance. The primary cause of the event was determined to be human error, with a contributing cause in the methodology utilized by Operations to track existing active LCOs and Tech Spec action statements. As a result of the event, Operations will implement the shift turnover requirement for each Unit Supervisor to reference the original Tech Spec or DATR document for each active LCO, assuring that the supervisor clearly understands Tech Spec/DATR LCO, verifying that the appropriate LCO actions are being taken. This event is reportable per 10CFR50.73(a)(2)(i)(B), operation prohibited by Technical Specifications.
2491997003 | Dresden 3 | 06/19/1997 | 07/15/1997 | 9707220422 | <strong>HPCI System Declared Inoperable Due to Turbine Stop Valve Above Seat Drain Valves Leaking Steam.</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1997 at 0920 hours with Unit 3 in startup activities at 13% power, the Unit 3 HPCI turbine stop valve above seat drain valves AO3-2301-64 and AO3-2301-65 were leaking steam to the HPCI sump during performance of Dresden Operating Surveillance (DOS) 2300-03, High Pressure Coolant Injection System operability Verification. Steam began to fill the HPCI room and HPCI was subsequently secured. The seat loading for the 64 valve was below the minimum pressure range. This allowed the valve to lift during High Pressure Testing of HPCI. Also, the 65 valve was found with its actuator casing binding against the valve frame preventing the valve from fully seating. A procedure revision was made to a generic Copes-Vulcan procedure to include a gap clearance between the diaphragm case and valve frame. However, the specific procedure for the 65 valve was not changed. The root cause of this event is attributed to failure to identify all affected procedures when revising maintenance procedures for the 65 valve. The cause of the 64 valve improper loading could not be determined.
2491997004 | Dresden 3 | 03/29/1997 | 11/14/1997 | 9711210017 | <strong>Isolation Condenser Spurious Group V Isolation Due To Steam Flash In Condensate Return Line Due to Design/Installation Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1997, at approximately 0534, with Unit 3 in Mode 3, Shutdown for a refueling outage, a spurious Primary Containment Group V Isolation occurred after Operations Department performed a valve lineup in accordance with Dresden General Procedure (DGP) 02-03, "Reactor Scram" to secure the Isolation Condenser (ISCO)[BL] from Standby and prior to placing the Shutdown Cooling System (SDC) in service. The outboard ISCO reactor inlet isolation valve, 3-1301-3 went closed from the open position as designed. This was the only valve that moved during the isolation. All other ISCO isolation valves had already been closed in accordance with DGP 02-03. In addition, the Group V isolation signal [BD] could not be reset. The cause of the inability to reset the Group V isolation signal was an isolated case of a relay failure. The cause of the spurious Group V isolation is a design deficiency in the Group V isolation flow instrumentation. Corrective actions included: relay replacement, Operational enhancements and evaluation of a modification. The safety significance of this event was minimal.
2491997005 | Dresden 3 | 04/19/1997 | 07/01/1997 | 9707090392 | <strong>Preconditioning Stationary Battery Prior To Modified Performance Test Inconsistent with Technical Specification Bases Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 19, 1997, at approximately 0300, with all fuel removed from Unit 3 vessel for refueling outage (D3R14), Dresden maintenance and engineering personnel attempted a Modified Performance Test (MPT) on the Unit 3 250VDC battery to satisfy Technical Specification requirements. The test was performed after completion of maintenance which subsequently was determined to be preconditioning. Although the preconditioning was not sufficient to invalidate the MPT, it is inconsistent with the bases of the Technical Specifications. The cause of this event is personnel error. Corrective actions to be taken include procedure revisions, personnel training and personnel discipline. This event is being reported under 10CFR50.73(a)(2)(i)(b). The safety significance of this event was minimal.
2491997006 | Dresden 3 | 05/16/1997 | 06/13/1997 | 9706190285 | <strong>Preconditioning Stationary Battery Prior To Service Test Inconsistent With Design Bases Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1997, during review of a June 10, 1996, service discharge test performed on the Unit 3 125 volt dc Alternate Battery, it was determined that the test was performed following completion of maintenance and an equalization charge. The equalization charge and extent of maintenance were subsequently evaluated to be preconditioning. Although the battery service test results were acceptable, the indication of past maintenance practices was lost due to the preconditioning. Preconditioning is inconsistent with the design basis requirements as defined by UFSAR Section 8.3.2.2, which requires system battery test to be performed in accordance with IEEE-450 which further requires Service Tests to be performed with batteries in the "As Found" condition. The root cause of this event is personnel error in failure to identify "As Found" requirements during the Alternate Battery Service Test procedure development technical review. Corrective actions include procedure revisions and counseling with the individuals involved. This event is being reported under 10CFR50.73(a)(2)(ii). There was no safety significance associated with this event.
2491997007 | Dresden 3 | 05/21/1997 | 06/13/1997 | 9706190265 | <strong>Main Steam Safety Valve 3-0203-4G As Found Lift Setpoint Outside Tech Spec Limit Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1997, with Unit 3 in the Refuel mode with all fuel removed, during the performance of Dresden Maintenance Procedure (DMP) 0200-03, "Main Steam Safety Valve Pre-Maintenance Test", Main Steam [SB] Safety Valve 3-0203-4G (Serial Number BK 6526) opened at a conservative pressure outside of the Technical Specification 4.6.E limits of +/-1%. This failure was attributed to setpoint drift. The safety valve was replaced with a rebuilt safety valve. Valve disassembly and refurbishment is planned but has not been completed at this time. The safety significance of this event is minimal based on an evaluation which shows that with the valve setpoint in the "as found" condition, the reactor pressure safety limit would not have been exceeded during any design basis event. Previous occurrences of Main Steam Safety Valves testing outside the Technical Specification limits are listed in Section F.
2491997008 | Dresden 3 | 05/26/1997 | 06/24/1997 | 9707030108 | <strong>Inadvertent Unit 3 Scram While Shutdown During Performance of Instrument Surveillance Due To Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1997 at 1404 with Unit 3 in startup activities and fuel load in progress, the unit received a full reactor scram while Instrument Maintenance Department (IMD) was performing Dresden Instrument Surveillance (DIS) 0500-19, Reactor Protection System Logic System Functional Test. This first time test was being performed by one CST, two 'B' technicians and one contractor 'A' technician. An error was made by one of the 'B' technicians by re-positioning the mode switch for the wrong Average Power Range Monitor (APRM) channel. The technician had successfully completed four APRM channels with similar steps just prior to the error. The four APRMs previously completed were on the top bank of the cabinets while the one in error was on the bottom bank. The root cause of this event was a failure to self-check by the IMD 'B' technician. Corrective action involves establishing a Peer Check Program and training all IMD technicians on the STAR simulator. One previous event occurred on May 20, 1997 involving a IMD 'B' technician failing to check his meter prior to re-installation. The corrective actions for this event had not been implemented when the current event occurred. The safety significance of this event is minimal.
2491997009 | Dresden 3 | 09/05/1997 | 10/03/1997 | 9710080254 | <strong>HPCI System Declared Inoperable Following Gland Seal Leakoff Condenser Hotwell High Level Due to Drain Pump Stop Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On September 5, 1997, at 1438 with Unit 3 in Mode 1 (Run) while performing the quarterly High Pressure Coolant Injection (HPCI) system operability verification, the gland seal leak off (GSLO) condenser hotwell high level alarm was received while bringing the turbine up to full speed following the turbine warm up. The gland steam exhauster tripped off resulting in a GSLO condenser high pressure alarm. The HPCT turbine was manually tripped from the control room, the HPCI System was declared inoperable and the appropriate actions were taken. The cause of this event was the failure of the GSLO condenser drain pump low level stop switch to shut off the pump at the required low level. This led to cavitation/air entrainment in the pump suction and air accumulation in the discharge pressure regulating valve sensing line causing a reduction in the pump capacity. The GSLO condenser drain pump low level stop switch was replaced and the HPCI system was declared operable on September 8, 1997 at 0348 following a satisfactory operability surveillance. The safety significance of this event was minimal.
2491997010 | Dresden 3 | 09/09/1997 | 10/08/1997 | 9710140249 | <strong>High Pressure Coolant Injection Declared Inoperable Due to Turbine Interlock Dump Valve Being Out of Adjustment and Stuck in the Closed Position Induced by Normal Wear and Varnish Buildup</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1997, during a High Pressure Coolant Injection (HPCI) system walkdown by a Component Engineer, the interlock dump valve on the Unit 3 HPCI turbine was observed to be out of adjustment. Subsequent evaluation by the Component Engineer determined that this condition could negatively affect operation of the HPCI turbine. The HPCI System was declared inoperable at 1236 on September 9, 1997. The interlock dump valve was disassembled and inspected. The inspection revealed that the valve was out of adjustment and stuck in the closed position. The interlock dump valve was reassembled and adjusted utilizing the HPCI turbine oil system. Upon completion of the adjustment, the HPCI system operability surveillance was successfully performed on September 10, 1997, and the system declared operable at 2000. The valve being stuck is attributed to normal wear and varnish buildup. Since there is no record that maintenance was performed on the interlock dump valve, the out of adjustment appears to have been be an existing condition. There were no previous instances of interlock dump valve adjustment or sticking issues. The safety significance of this condition was minimal.
2491997011 | Dresden 3 | 10/28/1997 | 11/25/1997 | 9712010354 | <strong>SBLC was Inoperable from Suction Line Low Temperature Due to a Wiring Discrepancy in the Heat Trace Controller Circuit</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, with Unit 3 in mode 1, the Standby Liquid Control (SBLC) suction temperature fell below Technical Specification 4.4.A.1.c. minimum temperature limit of 83 degrees F and the SBLC system was declared inoperable. The heat trace controller was adjusted and temperature raised in the suction line to greater than 83 degrees F. An investigation revealed that a wiring discrepancy existed in the heat trace controller circuit. Two of the three heat trace circuits were crossed and wired to the wrong leg of heat tracing resulting in the heat trace controller from one section of pipe controlling another section. During the troubleshooting phase of this problem, the SBLC low suction temperature condition recurred on October 31, 1997 and the SBLC system was subsequently declared inoperable. System repairs were made to correct the cause of the suction piping low temperature heating problem. The primary cause of this event was determined to be improper wiring of the heat trace control circuitry due to indeterminate conditions. Contributing causes include: (1) Inadequate Post Maintenance Testing of heat tracing; and (2) A failure to implement setpoint changes to SBLC suction temperature switches in a timely manner following the change to upgraded Technical Specifications (TSUP). Corrective actions include establishing better Post Maintenance Testing instructions when work is performed on heat trace circuits, and completing the setpoint changes for SBLC suction line temperature switches for both Units. The safety significance of the event was determined to be minimal.
2491997012 | Dresden 3 | 11/01/1997 | 11/26/1997 | 9712010327 | <strong>Reactor Recirculation B Loop, High Pressure Flow Element Venturi Instrument Line Steam Leakage Results in Unit 3 Shutdown Due to Fatigue Failure Of Socket Welded Pipe Joint</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1997, at approximately 1130, during inspection of the Drywell for the source of a previously detected increase in unidentified leakage, a steam leak was discovered on a socket weld at a 1 inch tee fitting in the high pressure instrument line for the Reactor Recirculation (Recirc) pump Loop B Venturi flow element. The reactor was operating at approximately 39% power at the time of discovery. A Unit 3 shutdown was promptly performed in accordance with the pre-approved inspection plan, as required by Technical Specification 3.6.H for primary pressure boundary leakage. The cause of the event is attributed to fatigue failure of the subject socket weld. It is postulated that a flaw was present in the socket root weld which lead to a premature failure of the weld in the presence of vibration. Corrective actions include: failed weld was replaced, adjacent welds were non-destructive surface examined by penentrant testing with no indications found, and the instrument line piping analysis will be reviewed to determine if improvements should be made to reduce vibration in the line. The overall safety significance of the event was minimal.
2491997013 | Dresden 3 | 12/01/1997 | 06/19/1998 | 9806240286 | <strong>Torus Cooling Outboard Test Valve Would Not Close Resulting In Inoperable Low Pressure Coolant Injection System Due to Faulty Breaker Auxiliary Contact Switch</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1997, at approximately 1215, during performance of Dresden operating Surveillance (DOS) 1500-10, LPCI System Pump Operability Test With Torus Available and In-Service Test Program, the Torus Cooling Outboard Test valve, 3-1501-38B, could not be closed via its control switches. With the 3-1501-38B valve, and the Torus Cooling Inboard Test valve 3-1501-20B open, a flow path existed which could have diverted flow from the Reactor Vessel if initiation of the LPCI system, in response to a Design Basis accident, was required. The flow path is required to be isolated within 36 seconds. The 36-second isolation requirement is controlled administratively, by throttling open the 3-1501-38B valve no more than 36 seconds; thus, the valve will automatically close within 36 seconds upon a LPCI system initiation. Since the 3-1501-38B valve was inoperable, the 36 second isolation requirement could not be met. The LPCI system test line was then isolated using the 3-1501-20B valve. However, the 3-1501-20B valve stroke time exceeds the system design basis requirement to isolate the flow path (36 seconds) by 5 seconds. The root cause of the failure was the auxiliary contacts sticking open in the close circuit. Faulty auxiliary contacts on the valve breaker resulted in the valve not being able to close. Corrective actions included replacement of the faulty auxiliary contact switches. The safety significance of this event was minimal. No previous occurrences were identified.
2491997014 | Dresden 3 | 12/29/1997 | 01/28/1998 | 9802060072 | <strong>High Pressure Coolant Injection System Inoperable due to Gland Seal Leak Off Condenser Drain Pump Low Level Shut Off Switch Failure Caused by A Misaligned Switch Lever Arm</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1997, at approximately 0234 hours, following a manual start of the Unit 3 High Pressure Coolant Injection (HPCI) System gland seal leak off (GSLO) condenser drain pump, the drain pump failed to automatically shut off and the HPCI Gland Seal Condenser Hotwell Level HI/LO Alarm annunciated. Based on a review of available information, the operating shift concluded that HPCI was Operable. A subsequent Engineering Department walkdown during the following shift identified that the pump may be air bound. HPCI was declared inoperable at 1945 hours on December 29, 1997. The likely cause for failure of the GSLO condenser drain pump to shut off is a failure of the GSLO condenser drain pump low level stop switch in the closed position. Inspection of the pump stop level switch found that the lever arm to float shaft set screw was not tightly secured and that the lever arm to switch mechanical linkage was not properly aligned. The float shaft and lever arm alignment was adjusted and the set screw secured tightly. All four level switches were inspected and minor adjustments performed. The level switches were successfully functionally tested and HPCI declared operable on December 31, 1997 at 1721 hours. The cause for the loose set screw and misalignment was not determined. The drain pump stop level switch had been installed on September 7, 1997 following a previous level switch failure. The safety significance of this event is minimal due to other safety systems being available for operation. L:\8360\8301\249\180\97\014 1/28/98 1:39 PM
2501997001 | Turkey Point 3 | 01/18/1997 | 03/26/1997 | 9704010515 | <strong>MISSED SURVEILLANCE ON CONTROL ROD POSITION VERIFICATION DUE TO INOPERABLE ROD DEVIATION MONITOR</strong><br /><i>Abstract:&nbsp;</i>On 1/18/97, the Assistant Nuclear Plant Supervisor recognized that the Rod Deviation Monitor (RDM) was inoperable. An inoperable RDM requires that rod alignment be verified every 4 hours instead of every 12 hours. The 4-hour frequency was invoked immediately, and observed until the RDM was repaired. The RDM should have been declared inoperable in August, 1996, when Instrument and Control personnel (I&C) determined that the RDM would not be able to hold calibration sufficiently to pass successive surveillance tests. Instead, I&C removed the suspect circuit card and cleaned its connectors before taking as found data, in essence preconditioning the RDM. Operations personnel responsible for the rod alignment verification were not aware of the preconditioning, so the 4-hour frequency was not imposed. The cause of the inoperable RDM was a bad circuit common connection, now repaired. The cause of the missed surveillance was inadequate incorporation of management expectations into procedures. Since out of tolerance data for the RDM did not affect any protection system setpoints or acceptance criteria, reporting of the as found data to Operations was not required by procedure, and the I&C activity was not viewed as preconditioning. Maintenance personnel are being trained in preconditioning. Procedures will be revised to require appropriate notification for any important data found out of tolerance.
2501997002 | Turkey Point 3 | 03/03/1997 | 03/28/1997 | 9704080403 | <strong>Manual Reactor Trip Following a Rod Control Urgent Failure Alarm</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1997, Florida Power & Light Company's Turkey Point Unit 3 was subcritical in Mode 3 proceeding toward a shutdown to begin a refueling outage. At 0012 hours a Rod Control Urgent Failure alarm was received. Off Normal Operating Procedure 3-ONOP-028 "Reactor Control System Malfunction," was implemented to assure steady state conditions. After an attempt to troubleshoot, a reset of the alarm, and another attempt to move control rods, the reactor was manually tripped at 0041 hours. A post-trip review established that pertinent plant parameters responded as expected. Other than the manual reactor trip, there were no reactor protection system or engineered safety feature actuations. The cause of the urgent failure alarm was a phase failure detection on stationary A circuits of the 2BD rod control power cabinet. The NRC operations center was notified at 0124 in accordance with 10 CFR Section 50.72(b)(2)(ii), Reactor Protection System Actuation.
2501997003 | Turkey Point 3 | 04/10/1997 | 05/09/1997 | 9705190146 | <strong>Mode Change Without Meeting Requirements Of Technical Specification 3.0.4. Due To Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1997, operators realized that the Steam Generator Blowdown system interlock bypass (keylock) switches had been left in the DRAIN/FILL position. This position blocks automatic closure signals to blowdown isolation valves CV-3-6275 A, B, and C and blowdown sampling valves MOV-3-1425, 1426, and 1427, such that these valves are open and will not close automatically. Operators immediately placed all 3 keylock switches to OFF, thereby enabling the valves to respond to automatic closure signals. This error was caused by inadequate procedures and a knowledge level deficiency concerning the keylock switch position required for Mode 4. The inadequate procedures are being revised. A new procedure for switch and light verifications prior to mode changes is being generated. A Night Order was issued to inform Operations personnel that the S/G Blowdown keylock switches were left in DRAIN/FILL, which bypassed the automatic closure signals, during the MODE 5 to 4 change. All licensed operators will be trained on the correct position of these keylock switches for different operating modes.
2501997004 | Turkey Point 3 | 04/11/1997 | 05/09/1997 | 9705160224 | <strong>Auxiliary Feedwater Automatic Start Upon the Trip of all Main Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1997, Florida Power & Light Company's Turkey Point Unit 3 was in mode 3 proceeding toward a startup following a refueling outage. At 0503, while starting the 3B main feedwater pump (the 3A pump was off) the supply breaker failed to close. When the control switch was returned to the mid position, with no other main feedwater pump running, the logic for automatic auxiliary feedwater start was satisfied. expected. The auxiliary feedwater pumps were shutdown and returned to normal standby status at 0550. The cause of the start failure of 3B main feedwater pump was found to be a mispositioned valve closing the sensing line for a start permissive lube oil pressure switch, resulting in a supply breaker not closing. Therefore the 3B main feedwater pump did not start which caused an auxiliary feedwater start. The cause of the mispositioned valve is indeterminate. The NRC operations center was notified at 0832 in accordance with 10 CFR Section 50.72(b)(2)(ii), Engineered Safety Feature Actuation.
2501997005 | Turkey Point 3, Turkey Point 4 | 06/18/1997 | 07/14/1997 | 9707220413 | <strong>Reactor Coolant Pump Oil Collection System Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>During planning for a modification, Florida Power & Light Company determined that the design of the Reactor Coolant Pump (RCP) Oil Collection System does not capture leakage from all potential leakage sites. Specifically, the level switches, their associated piping flanges, the level sightglasses, and the lube oil cooler piping drain are not protected from being potential leakage sites, and are not provided with leakage collection. This condition places both Turkey Point units outside the design basis as stated in the Updated Final Safety Analysis Report. The original RCP Oil Collection System design did not consider these component parts to be potential leakage sources. The NRC's Safety Evaluation Report approving Turkey Point's Oil Collection System was received several months prior to the time that 10CFR50 Appendix R was issued. It appears that when Appendix R was issued, the design was not reconciled with respect to the exact wording of section III.O. The Oil Collection System will be modified to collect potential leakage from these points. In the interim, the Oil Collection System is considered operable.
2501997006 | Turkey Point 3, Turkey Point 4 | 07/22/1997 | 08/18/1997 | 9708220277 | <strong>Manual Reactor Trip Due To Failed Rod Control Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1997, Florida Power & Light's (FPL) Turkey Point Unit 3 was operating in Mode 1 at 100% power. At 12:42:51 hours, 12 control rods dropped into the core and the Reactor Control Operator (RCO) manually tripped the reactor at 12:42:57 hours. The 12 control rods dropped in the core due to a failure of the redundant pair of +24 Vdc rod control power supplies, PS1 and PS2, located in the 1AC power cabinet. Following the reactor trip, all safety related equipment functioned properly with one exception. The Train 1 Auxiliary Feedwater (AFW) flow control valve to Steam Generator (SG) "C", FCV-3-2818, would not fully close due to failure of its corresponding controller, HIC-3-1458A. The RCOs took manual action to isolate Train 1 AFW to the "C" SG. A post trip review established that the response of pertinent plant parameters was as expected. A total of 12 power supplies were replaced in the rod control logic and power cabinets. The remaining Unit 4 power supplies manufactured by the same vendor will be replaced during the next refueling outage.
2501997007 | Turkey Point 3 | 07/30/1997 | 06/15/1998 | 9806230040 | <strong>Automatic Reactor Trip due to Closure of the B Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1997, Florida Power & Light (FPL) Company's Turkey Point Unit 3 was operating in Mode 1 at 100% power. At 1506 hours, the 3B Main Steam Isolation Valve (MSIV) failed closed. The resultant level decrease in the 3B Steam Generator (SG) caused the reactor to trip automatically on low-low level in the 3B SG. All control rods fully inserted. A 3B steam line Main Steam Safety Valve (MSSV) opened then reseated as expected during the initial transient, as pressure in the 3B SG exceeded the MSSV setpoint pressure of 1085 psig. The A Auxiliary Feedwater (AFW) Pump tripped on overspeed during the event. Plant response was otherwise as expected. The cause of the MSIV closure was attributed to a failed BFD22S relay. The six relays on the 3A, 3B, and 3C MSIV's were replaced. The most probable cause of the A AFW pump overspeed trip was a spurious electronic overspeed signal caused by the A AFW pump tachometer module. A plant change was implemented to disable the electronic trip function of all three AFW pumps to enhance their reliability.
2501997008 | Turkey Point 3, Turkey Point 4 | 09/09/1997 | 10/08/1997 | 9710160056 | <strong>Containment Sump Debris Screens Outside Design Basis Due To Screen Damage</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1997, Turkey Point Unit 4 was in Mode 5 in preparation for a refueling. Inspection of the containment recirculation sumps revealed several gaps and a hole in the sump screens which were in excess of the design requirements. On September 11, a similar condition was found on Unit 3 while in Mode 1. The gaps would allow debris larger than 3/8 inch to enter the flow stream to the containment spray nozzles, during the recirculation phase following a loss of coolant accident. Therefore, the screen damage resulted in both units operating outside the design basis. The causes of this event were inadequate procedural guidance, and personnel error (utility non-licensed personnel). The Unit 3 screen was repaired on the spot. The Unit 4 screens have also been repaired. FPL is clarifying the containment recirculation sump screen design basis. Additional procedural guidance is being developed to verify containment recirculation sump screen design details. Discussion of the event will be incorporated into the continuing training program at Turkey Point.
2501997009 | Turkey Point 3 | 11/14/1997 | 03/24/1998 | 9803300354 | <strong>Console Switch Position Disabled Auxiliary Feedwater Auto Start Logic on 3B Steam Generator Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On 11/14/97, the Reactor Control Operator identified that the Control Room (CR) console switch for the 3B Steam Generator Feedwater Pump (SGFW) pump was not in the start position. The 3B SGFW pump had been locally started on 7/30/97, while Unit 3 was in Mode 3. Technical Specification (TS) Table 3.3-2, Item 6.e, requires Auxiliary Feedwater (AFW) actuation on trip of all main feedwater pumps breakers during Modes 1 and 2. Item 6.e of TS Table 3.3-2, was not met from 7/31/97 (when Unit 3 entered Mode 2), until 11/14/97 because the minimum operating channels requirement includes having each pump switch semaphore in the operating position (red flag). This AFW auto-start feature is an anticipatory AFW actuation for a Steam Generator Low-Low level. The AFW auto-start on SGFW pump trip was disabled only when SGFW pump 3A was not running during Modes 1 and 2. The 3A SGFW pump was not running from 0413 until 1845 on 7/31/97, and again from 1044 on 8/14/97, until 1010 on 8/15/97. At 1820 on 11/14/97, the CR console switch for the 3B SGFW pump was momentarily placed in the start position, restoring the AFW automatic start actuation circuit for the 3B SGFW pump. Procedure revisions to add local start requirements for the SGFW pump in Modes 3, 4, and 5, were reviewed to ensure they contain all necessary guidance. Operations verified that all CR switch semaphores match component indicating lights. A training brief was issued describing the event and its significance.
2511997001 | Turkey Point 4 | 03/27/1997 | 04/25/1997 | 9705020011 | <strong>Emergency Core Cooling System Recirculation Loop Leakage Found to be in a Condition Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1997, Florida Power & Light Company's Turkey Point Unit 4 was operating in Mode 1 at 100% power. At 1440 hours eastern standard time an engineering evaluation found leakage on the 4A high head safety injection pump casing joint to be outside the design basis for recirculation loop leakage. The cause was believed to be a leaking gasket. While torquing the casing bolts at the leak location, the leak increased significantly to a level determined to be outside allowable limits. With the static head of the refueling water storage tank, the estimated leakage was 38 liters per hour. The limit used was that which could cause exceeding the dose criteria of General Design Criterion 19 dose levels. The leak was repaired using injection sealant, and the pump was returned to operable status. On April 3, 1997, at 2030 hours, the 4A safety injection pump was discovered leaking at about 3.4 liters per hour while the pump was running. The pump casing gasket was replaced to return the pump to operability. The NRC operations center was notified after each event in accordance with 10 CFR Section 50.72(b)(1)(ii)(B), 'condition that is outside the design basis of the plant.' The April 3 event was retracted.
2511997002 | Turkey Point 4 | 04/23/1997 | 05/22/1997 | 9706030019 | <strong>Automatic Reactor Trip Due to Loss of External Load</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1997, Unit 4 tripped from 100% power. An I&C Specialist, working inside the back of the Main Control Board, apparently bumped a relay, causing a false Turbine Overspeed Protection signal. The signal caused turbine control valves to close (loss of load), and the reactor tripped on Over Temperature Delta-T. The root cause of the event was inadequate physical protection. The contact arm on this relay is not enclosed, and can be actuated with very slight force. Contributors were inadequate work controls and a loss of lighting inside the panel during the work. The work document did not indicate that the work had the potential to trip the unit. This relay and others like it will be evaluated to determine if they can be enclosed or relocated, to prevent inadvertent actuation. Until the evaluation is complete, Nuclear Plant Supervisor (NPS) permission is required to work inside this panel, and the NPS will brief the workers on the location and sensitivity of the relays. Administrative procedures governing the inadequate work controls will be revised to capture the lessons learned.
2541997001 | Quad Cities 1 | 01/07/1997 | 01/30/1997 | 9702100483 | <strong>Technical Specification required instrumentation readings were not completed within the required time frequency after changing from eight hour to twelve hour shifts because the consequences associated with changing shift duration were not adequately reviewed or assessed.</strong><br /><i>Abstract:&nbsp;</i>It was discovered on 011797, that on the 010797 day shift, with Unit One in Mode One at 100% power, some of the Technical Specification (TS) required, once per shift channel check readings were not completed within the required 12 hour time interval plus 25% maximum allowable extension. A review showed that approximately 18 hours elapsed between the recording of the night shift readings and the day shift readings. The cause of this event was a cognitive personnel error. The consequences associated with changing to twelve hour shifts were not adequately reviewed or assessed. The timeliness of taking readings was discussed prior to going on twelve hour shifts, but the TS requirements were not thoroughly reviewed by the procedure writer, reviewers or approver. On 010997, (prior to discovery of this incident) administrative controls were added to the daily surveillance procedure to ensure the TS surveillance interval is not exceeded. There was no safety significance to the station or the health and safety of the public as a result of this event. Each monitored parameter has four sensors to provide redundant protection. The readings were completed within approximately 18 hours of each other during consecutive twelve hour shifts and each of the readings were found within the Technical Specification limits.
2541997002 | Quad Cities 1, Quad Cities 2 | 01/27/1997 | 02/24/1997 | 9703050469 | <strong>Engineering Calculations performed in response to NRC Generic Letter 96-06 indicated that several isolable piping sections on each unit may experience stresses above UFSAR Allowables following a Loss of Coolant Accident due to inadequate original system design</strong><br /><i>Abstract:&nbsp;</i>On 012797, with both Units in Mode One at 100% power, it was determined that several isolable piping sections could experience stresses above Updated Final Safety Analysis Report Allowables due to Post-Loss of Coolant Accident thermal pressurization. In response to NRC Generic Letter 96-06, several calculations were performed to evaluate piping and containment penetrations for thermal overpressurization caused by a Main Steam Line Break (MSLB)/Loss of Coolant Accident (LOCA). These calculations identified five penetrations (per Unit) that could experience overpressurization under accident conditions. The affected piping systems include: Reactor Building Closed Cooling Water, Reactor Recirculation Sample lines, Residual Heat Removal, Reactor Water Clean-up, and Clean Demineralized Water. The affected piping sections were determined to be operable, but degraded. The cause of the event was inadequate original design. Based on the results of the operability assessment, there is minimal safety significance to the station or the health and safety of the public as a result of this event. The affected penetrations would maintain containment integrity following an accident. In the event of an accident, any radiological release would remain within analyzed limits. The corrective actions taken to resolve this issue are being developed and will be provided in a supplemental report.
2541997003 | Quad Cities 1 | 04/29/1997 | 05/29/1997 | 9706060056 | <strong>A visual examination, (VT-2) was not performed due to procedural deficiencies following a High Pressure Coolant Injection (HPCI) System valve replacement, as required by the American Society of Mechanical Engineers (ASME) Section XI and Technical Specification (TS) Section 4.0.E.</strong><br /><i>Abstract:&nbsp;</i>On 042997 at 1800 hours the Station identified a visual examination (VT-2) was not performed following a replacement of the 1-2301-45 valve in the High Pressure Coolant Injection (HPCI) System. This is contrary to the American Society of Mechanical Engineers (ASME) Section XI 1989 Edition, Subsection IWA, Paragraph IWA-5214 and Technical Specification (TS) Section 4.0.E. U-1 HPCI was subsequently declared inoperable at 1930 on 050197 following an operability screening of the event. The root cause of the event is inadequate procedures (QCAP 0307-20, QCAP 2200-04, and QCAP 2200-09), which failed to provide clear instructions for ensuring ASME Section XI Repair/Replacement (R/R) Program requirements are included in the Work Request packages, and also entered in the Post Maintenance Testing (PMT) matrix. Corrective actions included an immediate VT-2 examination of the 1-2301- 45 valve, a review of other R/R programs for similar occurrences, and the planned revision of the administrative procedures responsible for the generation of ASME Section XI R/R Programs, Work Requests and assignment of PMT requirements. The Safety Analysis concluded that despite the lack of a VT-2 examination, the health and safety of on-site personnel and the public was not affected. Although certified VT Examination personnel were not present during the initial HPCI Test and the ASME Code required VT-2 examination was not performed, the valve was verified to be leak tight by the HPCI system engineer. The valve would have been able to perform its function in case of an accident and subsequent HPCI initiation.
2541997004 | Quad Cities 1, Quad Cities 2 | 10/26/1996 | 03/20/1997 | 9703260326 | <strong>Residual Heat Removal Service Water Pumps in a Degraded Condition due to Inadequate Evaluation of Replacement Pump Casing Bolts</strong><br /><i>Abstract:&nbsp;</i>At 1450 hours on 102696, Unit One and Unit Two were operating at 100 percent and 55 percent power respectively, when the 1C and 2C Residual Heat Removal Service Water (RHRSW) pumps were declared inoperable due to unavailability of information concerning the acceptability of the pump casing bolting material. The pump casing bolting was replaced. The apparent cause of the event was a cognitive personnel error because the established procedure and checklist for performing the parts evaluation for the RHRSW pump casing bolting material was not followed. Subsequent evaluation of the questionable bolting material demonstrated that the material would have maintained pump casing integrity and would have ensured that the RHRSW pumps would have provided adequate flow through the RHR heat exchangers during accident conditions.
2541997005 | Quad Cities 1 | 03/19/1997 | 04/15/1997 | 9704220076 | <strong>The High Pressure Coolant Injection Subsystem was Made Inoperable to Protect Equipment Due to Uncertainties Related to an Abandoned Power Feed Cable, Which Had Been Inappropriately Abandoned.</strong><br /><i>Abstract:&nbsp;</i>The High Pressure Coolant Injection (HPCI) Subsystem was declared inoperable at 2200 hours on 031997 when the HPCI Gland Seal Condenser Exhauster (GSCE) control switch was placed in the pull-to-lock (PTL) control position by the Unit One Nuclear Station Operator. The GSCE was placed in PTL due to a concern with the power feed cable to the exhauster. Cable damage had been noted to a cable believed to provide power to the GSCE. At 2315 hours on 031997 it was determined that the damaged cable had been abandoned and the GSCE was placed back into the automatic control mode making the HPCI subsystem operable. An Emergency Notification System (ENS) call was made at 2346 hours due to the HPCI subsystem inoperability. The following actions contributed to this event: (1) The damaged cable had been improperly abandoned and (2) a previous Problem Identification Form (PIF) did not properly correct this problem. Corrective actions for this event include: (1) updating the plant design documents to properly reflect the status of this abandoned cable; (2) labeling this abandoned cable at each accessible location along its route and (3) reviewing and revising as necessary the Abandoned Equipment Procedure. There was no effect on the public or the control room personnel due to this event and the safety consequences were minimal.
2541997006 | Quad Cities 1, Quad Cities 2 | 03/27/1997 | 04/23/1997 | 9704290223 | <strong>A potential design basis fire could have caused multiple spurious operations of certain Reactor Water Cleanup System Valves, potentially allowing a loss of reactor coolant inventory in excess of design basis limits, due to inadequate procedural guidance.</strong><br /><i>Abstract:&nbsp;</i>On 032797, during a review of a Problem Identification Form (PIF) written on 022796, station personnel concluded that the PIF had been incorrectly dispositioned as non-reportable due to incomplete understanding of the Quad Cities Appendix R Safe Shutdown Analysis. On 022796, during a review of the Station's Appendix R Conformance Safe Shutdown Analysis (SSA), plant personnel discovered that the Reactor Water Cleanup (RWCU) system had been identified as a high/low pressure interface requiring isolation during certain design basis fires. However, no actions to isolate the RWCU system during a fire were included in the safe shutdown procedures due to a cognitive personnel error on the part of the procedure writer. Failure to properly isolate the RWCU system during a design basis fire could have prevented station operators from attaining safe shutdown prior to reactor level reaching the top of active fuel. The potential blowdown path was resolved by turning off the power feed breaker to the normally closed RWCU blowdown orifice bypass valve M01(2)-1201-76. All other high/low pressure interface paths were reviewed to ensure that each was resolved correctly. This event had the potential to pose a safety concern in the unlikely event of a design basis fire.
2541997007 | Quad Cities 1 | 03/31/1997 | 04/23/1997 | 9704290091 | <strong>Unit One Emergency Diesel Generator Inadvertent Start Due To A Personnel Error While Operating The Control Switch.</strong><br /><i>Abstract:&nbsp;</i>On 033197, at 1231 hours the Unit 1 Emergency Diesel Generator (DG) inadvertently started while the Unit 1 Nuclear Station Operator (NSO) was moving the three position control switch (C/S) from the AUTO (right) position to the STOP (center) position. The NSO turned the C/S to the left and at that time, personnel in the Unit 1 DG Room and the Control Room observed that the DG had started. The NSO immediately turned the C/S back to the AUTO position. Per Unit Supervisor direction, the NSO then placed the C/S to STOP and the Unit 1 DG was declared inoperable. The most probable cause of this event is personnel error by the NSO. The NSO was removed from all licensed duties until he has completed the remediation plan that was developed for him. The safety significance of this event was minimal. At no time during the event was the health and safety of the public or Control Room personnel jeopardized.
2541997008 | Quad Cities 1 | 04/02/1997 | 04/29/1997 | 9705070298 | <strong>High Pressure Coolant Injection Inoperable Due To Turning Gear Failure.</strong><br /><i>Abstract:&nbsp;</i>On 040297 at approximately 1700 hours the High Pressure Coolant Injection (HPCI)[BJ] Subsystem turbine was shutdown after quarterly flow rate testing. When the turbine came to rest the turning gear failed to automatically engage. After subsequent testing of the turning gear it was determined that there was a problem with the turning gear engage linkage and the Unit 1 HPCI system was declared inoperable at 2300 hours on 040297. Unit 1 entered a 14 day Limiting Condition for Operation per Technical Specification 3.5.A.3 Action 3. The turning gear engagement linkages were repaired on 040397 and the HPCI Subsystem was declared operable on 040497 after review of the cause of the failure. The failure was caused by improper adjustments to the turning gear engagement mechanism on 031397 while the reactor was shutdown. These adjustments were made at the direction of the system engineer who had an improper understanding of the turning gear mechanism. These adjustments were then improperly tested prior to start-up on 031797. Therefore the failure was not detected until the turbine run performed on 040297. There was no effect on the public or the control room personnel due to this event and the safety consequences were minimal. The person involved in providing the instructions for the turning gear adjustments has been counseled on his failure. The procedure used for testing the turning gear will be revised and appropriate turning gear adjustment instructions will be incorporated into the vendor manual.
2541997009 | Quad Cities 1, Quad Cities 2 | 05/04/1997 | 05/22/1997 | 9705280042 | <strong>Both Trains of Standby Gas Treatment Systems inoperable due to Operator fuse replacement error.</strong><br /><i>Abstract:&nbsp;</i>On 050497, at 2035 hours, Unit One was in Power Operation and Unit Two was shutdown and defueled. Operations made both trains of the Standby Gas Treatment System (SBGTS) inoperable for 40 minutes when the 1/2 B SBGTS Train Mode Selector Switch was placed in "OFF" in accordance with a surveillance procedure following the inadvertent installation of a blown fuse, which disabled the autostart capability of the A Train of SBGTS. The inoperability of the A train of SBGTS was identified when the A Train failed to start in the conduct of the procedure. Immediate actions were to enter a 1 hour Limiting Condition for Operation (LCO) because both trains of SBGTS were inoperable, stabilize plant conditions, replace the blown fuse, and reperform the applicable steps of the procedure to ensure the A Train of SBGTS would autostart. At 2115 hours the A Train was declared operable and Operations exited the 1 hour LCO. The root cause of this event is a cognitive personnel error by the Senior Reactor Operator (SRO) test director who did not adequately control a blown fuse and the new replacement fuse to ensure the new fuse was installed. Corrective actions were to counsel the-SRO test director and to conduct training on the event. The safety consequences of this event to on-site personnel and the general public were minimal. The B Train of SBGTS could have been manually started within 10 minutes in the event of a Loss Of Coolant Accident.
2541997010 | Quad Cities 1, Quad Cities 2 | 04/07/1997 | 05/02/1997 | 9705130382 | <strong>Train "B" of Control Room HVAC System Inoperable Due to Loss of Refrigerant.</strong><br /><i>Abstract:&nbsp;</i>On 040797, train “B” of the Control Room (CR) Heating, Ventilating, and Air Conditioning (HVAC) system was declared inoperable due to a loss of refrigerant. It was discovered that a fitting, on the refrigeration discharge line of the compressor, had a hairline split large enough to release most of the refrigerant charge. The fitting was replaced and the system was declared operable.
2541997011 | Quad Cities 1, Quad Cities 2 | 04/09/1997 | 04/30/1997 | 9705140175 | <strong>The Residual Heat Removal Service Water System was made inoperable due to uncertainties related to 4 KV Air Magne-Blast Horizontal Gas (AMHG) circuit breakers, which had experienced cracks in the auxiliary switches mounting channels.</strong><br /><i>Abstract:&nbsp;</i>The 4 Kilo Volt (KV) circuit breakers at buses 13, 14, 23 and 24 were declared inoperable on 040997 at 1330 hours due to cracks in 4 KV Air Magne-Blast Horizontal Gas (AMHG) circuit breaker auxiliary switches. The affected breakers included Residual Heat Removal (RHR) Service Water (SW) and offsite power distribution breakers. The apparent cause of the event was a improper manufacturer's switch mounting design. Unit one was shut down due to Technical Specification 3.8.A. Action 1.d for both RHR SW subsystems being declared inoperable. A design change has been completed to install a mounting strap around auxiliary switches for all affected Unit 14 KV breakers and the Unit 24 KV breaker which provide a path for backup power to Unit 1 from the Unit 2 Reserve Auxiliary Transformer. The same design will be completed for the remaining Unit 2 breakers prior to start up from Q2R14. The impact on Safety was minimal in that power would have always been available to Alternating Current (AC) powered Emergency Core Cooling (ECCS) Equipment from Diesel Generator Supplied 4 KV Essential Service buses 13-1, 14-1, 23-1 and 24-1.
2541997012 | Quad Cities 1, Quad Cities 2 | 04/10/1997 | 01/05/1998 | 9801140092 | <strong>Due to Design Related Cognitive Personnel Error, it is physically possible for the Unit 1 & 2 Refuel Bridge Monorail Auxiliary Hoists to perform core alterations without a Refuel Bridge Position Interlock actuation.</strong><br /><i>Abstract:&nbsp;</i>On 041097 at 1500 hours, during an evaluation, Design Engineering determined that it is physically possible for the Unit 1 & 2 Refuel Bridge Monorail Hoists to be over a portion of the core without the Refuel Bridge Position Interlock being actuated (contrary to design requirements). This was caused by a design program deficiency in which engineering personnel did not apply a sufficient degree of attention to re-positioning the Refuel Interlock Trip Plates and/or Interlock Limit Switches when the wider Refuel bridges were installed in 1986. Procedures were in-place to remove the Monorail Hoist from service and not perform the surveillance test for the hoist if it was not being used for core alterations. The site practice is to remove the monorail hoist from service prior to refueling operations. A potential inadvertent reactor criticality was still significantly limited by the procedures, work practices, and the nuclear characteristics of the core. The net effect of the event is that a slight increase in the probability of an inadvertent criticality existed which could have resulted in increased exposure to personnel on the Refuel floor.
2541997013 | Quad Cities 1 | 04/16/1997 | 05/08/1997 | 9705140186 | <strong>RCIC Area High Temperature Switch would not actuate due to excess sealing varnish applied by technician.</strong><br /><i>Abstract:&nbsp;</i>On 041697, at 0300 hours, Unit One (U1) was in Mode 4. Instrument technicians found the 1-1360-14D, Reactor Core Isolation Cooling (RCIC) High Temperature Switch, would not actuate as expected. Investigation identified excess sealing varnish around the temperature switch capillary plunger which bound the plunger to the housing preventing response. The root cause of this event is a personnel error by the technician who calibrated the 1-1360-14D temperature switch. The varnish was removed and the switch was calibrated and tested. Calibration and testing was performed on the U2 RCIC Area High temperature switches as well as the U1 and U2 High Pressure Coolant Injection (HPCI) Area High Temperature Switches and none were found degraded. The safety consequences of this event to on-site personnel and the general public were minimal. The 1-1360-14A/B/C temperature switches would have actuated to isolate the RCIC system had an actual high temperature condition occurred.
2541997014 | Quad Cities 1, Quad Cities 2 | 04/16/1997 | 05/15/1997 | 9705220493 | <strong>Target Rock Safety Relief Valves Removed From Unit 2 During Q2R13 and From Unit 1 During Q1R14 Did Not Receive As-Found Set Point Testing Within 12 Months Following Removal As Required By ASME/ANSI OM-1987 Part 1 Due To A Defective Procedure Which Did Not Provide Clear Guidance Of Test Requirements.</strong><br /><i>Abstract:&nbsp;</i>A Target Rock Safety Relief Valve (TRSRV), that was removed from the 2-0203-3A position during the Q2R13 refueling outage on 060195, had not been set pressure tested within 12 months. Also a TRSRV that was removed from the 1-0203-3A position during the Q1R14 refueling outage on 031596 had not been set pressure tested within 12 months. This is contrary to ASME/ANSI OM-1987, Part 1, Paragraph 1.3.3.1(c)(2) and Technical Specification (TS) Section 4.0.E. The root cause of the event is a Defective Procedure, which failed to provide clear instructions for ensuring prompt testing in the Target Rock Removal and Installation Procedure (QCMM 0203-31). Corrective actions include revising the maintenance procedure responsible for the removal of the TRSRV to ensure they are shipped to the testing facility in a timely manner and making improved use of the Nuclear Tracking System to verify the testing is performed within the required time frame. The Safety Analysis concluded that despite a small deviation above the TS set point tolerances, there would not have been a violation of reactor safety limits on maximum ASME overpressurization, Anticipated Transient Without Scram overpressurization, Reactor thermal limits (Minimum Critical Power Ratio), or Loss Of Coolant Accident fuel limits.
2541997015 | Quad Cities 1 | 04/18/1997 | 08/12/1997 | 9804160377 | <strong>The Electrical Protection Assembly failed due to aging and deterioration of the undervoltage release coil causing loss of power to the Reactor Protection Bus 1B</strong><br /><i>Abstract:&nbsp;</i>At approximately 0727 hours on 041897, the 1B Reactor Protection Bus (RPS) Bus Electrical Protection Assembly (EPA) Unit 1 1B-2 breaker tripped with no apparent TRIP signal causing a "B" channel Primary Containment Isolation (PCI) groups 2 & 3 actuation. A team was assembled to investigate this event, determine the root cause, and recommend corrective actions. An Emergency Notification System call was made at 0727 on 041897. Loss of the 1B RPS Bus caused a 1/2 scram and partial Primary Containment Isolation (PCI), Reactor Building Vents to isolate, Reactor Water Clean-up (RWCU) pumps to trip, and loss of shutdown cooling as designed. The cause of the EPA 1B-2 breaker tripping is the failure of the undervoltage release coil which is part of the molded case circuit breaker. Per an analysis performed by the Material Engineering Group (MEG) the undervoltage release coil had failed due to age degradation. This was an original equipment breaker. The breakers in Unit 1 EPAs 1A-1, 1A-2, 1AB-1, 1AB-2, 1B-1, and Unit 2 EPAs 2B-1, 2A-1, and 2AB-2 will be replaced with new 2-pole breakers. The breakers in Unit 1 EPA 1B-2, and Unit 2 EPAs 2A-2, 2B-2, and 2AB-1 are newer 2-pole breakers. The breaker in Unit 1 EPA1B-2 was replaced with a 2-pole breaker at this time. The failure of the RPS EPA breaker did not endanger the health and welfare of the public. The breaker failing caused the RPS bus to de-energize causing a partial PCI Group 2 and 3 initiation. The RPS system is designed to fail in a safe condition upon loss of power. The reactor temperature was monitored by Control Room personnel to verify that we did not exceed the Cold Shutdown limit of </= 212 degrees F. Operations has procedures in place to maintain the Reactor coolant temperature below 212 degrees F, as required by Technical Specifications Table 1-2, with the loss of the shutdown cooling mode of the RHR system.
2541997016 | Quad Cities 1 | 05/09/1997 | 09/03/1997 | 9709090222 | <strong>Diesel Generator Cooling Water Inservice Testing Requirements were not Completed When an Inaccurate Predefined Work Request Used for Scheduling was Implemented</strong><br /><i>Abstract:&nbsp;</i>On 050997 at 1220, Unit 1 was in Power Operation at 100 percent power when Operations performed the Unit 2 portions of QCOS 6600-08, "Quarterly 1/2 Diesel Generator Cooling Water (DGCW) To Unit 1 and Unit 2 ECCS (Emergency Core Cooling System) Room Coolers Flow Test" in accordance with a predefined Work Request (WR) for the activity. This quarterly surveillance was intended to be performed for both Units but the predefined WR for scheduling the activity only identified Unit 2. The predefined WR was inadequate when it was developed in 1996. The Inservice Testing (IST) program had not completed the surveillance in the second quarter of 1997 as it relied on the predefined WR for tracking. On 080797, the Unit 1 surveillance discrepancy was identified when the IST Coordinator was responding to questions from the shift concerning the third quarter testing and Operations successfully completed the Unit 1 portion of QCOS 6600-08 at 1519. The cause for this event was inadequate change management resulting in an inappropriately titled predefined WR. Corrective actions include completion of the Unit 1 portions of the testing, revising the predefined WR, and developing a new predefined WR for Unit 1. The safety significance of this event is minimal. The successful completion of the Unit 1 portion of QCOS 6600-08 on 080797 indicates the DGCW system was always capable of performing as designed.
2541997017 | Quad Cities 1 | 06/23/1997 | 08/12/1997 | 9708210040 | <strong>Unit 1 Entered a 12 Hour Hot Shutdown Limiting Condition for Operation Contrary to the Bases for Technical Specification 3.0.A due to Cognitive Personnel Errors When Scheduling Surveillances.</strong><br /><i>Abstract:&nbsp;</i>On 062397 at 2055, Unit 1 was in Power Operation at 100% power when a 12 hour Hot Shutdown Limiting Condition for Operation (LCO) was inappropriately entered for a total of 36 minutes when the High Pressure Coolant Injection (HPCI) system steam supply valves were closed for a scheduled Instrument Maintenance surveillance while the Low Pressure Coolant Injection (LPCI) system was inoperable. The crew identified and logged the entry into the 12 hour Hot Shutdown LCO with the understanding that the surveillance needed to be performed at that time. The surveillance was completed and the LCO was exited at 2131. On 062497 at approximately 1930, a similar Hot Shutdown LCO entry was scheduled and performed for a different HPCI surveillance with an entry of 56 minutes. The cause of this event is cognitive personnel errors by the Lead Unit Planner. The scheduling of these surveillances while LPCI was inoperable was unnecessary and nonconservative. Corrective actions include counseling, required reading, and procedure revisions. This LER is being submitted voluntarily. The safety significance of this event is minimal. While the scheduling of the 12 hour Hot Shutdown LCO entry was not conservative on these occasions, the entries were less than one hour in duration, and within the constraints of the design basis.
2541997018 | Quad Cities 1, Quad Cities 2 | 07/21/1997 | 08/20/1997 | 9708260004 | <strong>Surveillance was not Properly Performed due to Inadequate Procedure Development and Review During Implementation of Upgraded Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On 072197 at 1200, Unit 1 was in Power Operation at 100 percent power when a NRC resident inspector raised a question on the implementation of Technical Specification (TS) 4.8.A. It was determined that the Residual Heat Removal Service Water (RHRSW) valves associated with Residual Heat Removal (RHR) pumps oil and seal coolers were not included in the monthly valve lineup and were not locked, sealed or otherwise secured in position. At 1720, Operations verified the associated RHRSW valves were properly positioned in the plant. On 072497, a Senior Reactor Operator was tasked with reviewing all TS surveillance requirements to identify any other discrepancies. The TS Review also reviewed all Operations valve lineup TS surveillances for Safety Related systems using controlled drawings. On 080897 the TS review was completed and no other missed TS surveillance was identified. The cause for this deficiency was inadequate procedure development and review for the 092396 implementation of the upgraded TS. Corrective actions included a review of TS and valve lineup procedures, counseling, and lockwiring the affected RHRSW valves in the proper position. The safety significance of this event is minimal. The affected RHRSW valves were not required for a Loss of Coolant Accident.
2541997019 | Quad Cities 1, Quad Cities 2 | 08/08/1997 | 09/03/1997 | 9709090250 | <strong>Technical Specification 3.0.C Was Entered Because There Was No Limiting Condition for Operation Available For Secondary Containment When Both Doors For An Interlock Were Opened Simultaneously.</strong><br /><i>Abstract:&nbsp;</i>On 080897, Both Units were in Power Operation with Unit 1 at 100 percent power and Unit 2 at 65 percent power during the performance of a Secondary Containment isolation instrument surveillance. Both Units were in a Technical Specification (TS) 3.2.A Limiting Condition for Operation (LCO) action statement which requires establishing Secondary Containment integrity with the Standby Gas Treatment system operating. At 1055, two individuals were attempting to enter a Reactor Building interlock from opposite sides. Both individuals pressed the door opening buttons simultaneously and both interlock doors opened. Secondary Containment integrity requires that only one interlock door be open at any one time. The interlock doors automatically reclosed and the individuals involved immediately notified the Control Room. The cause of this event is the unlikely occurrence of individuals simultaneously actuating both interlock doors in a period when Secondary Containment was required by TS 3.2.A and there was no LCO available for Secondary Containment. Corrective actions include the automatic reclosing of the doors, verifying their proper operation, and implementing administrative controls or other measures to prevent recurrence for the interlocks in high traffic areas. The safety significance of this event is minimal. The interlock doors reclosed automatically. The Reactor Building differential pressure remained negative throughout the event preventing any unmonitored radioactive release which could impact site personnel or the health and safety of the public.
2541997020 | Quad Cities 1, Quad Cities 2 | 05/19/1997 | 06/18/1997 | 9706250201 | <strong>B-Train Control Room Ventilation Air Handling Unit breaker cycled and tripped During monthly test due to an undetermined cause.</strong><br /><i>Abstract:&nbsp;</i>On 051997, at 2254 hours, Unit One was in Power Operation and Unit Two was in Cold Shutdown. The B-Train Control Room (CR) Ventilation System became inoperable when an Air Handling Unit (AHU) breaker tripped when performing a monthly surveillance. During a procedural check of relay contacts, the CR operator attempted to start the AHU and the breaker cycled several times and tripped. Immediate actions were to exit the procedure, restart the A-Train CR Ventilation System, and enter a 30-day Limiting Condition for Operation (LCO). On 052997 at 0320 hours, Operations successfully completed the affected surveillance, the B-Train CR Ventilation system was declared operable, and Operations exited the 30-day LCO. The cause of this event could not be determined. Corrective actions were to conduct multiple tests to ensure the equipment would function as designed. The safety consequences of this event to on-site personnel and the general public were minimal. The affected system is not intended to mitigate dose to the general public, and the normal ventilation system was capable of mitigating dose to CR personnel.
2541997021 | Quad Cities 1, Quad Cities 2 | 08/26/1997 | 12/16/1997 | 9801020031 | <strong>The Cause of Discrepancies Found Between The Safe Shutdown (SSD) Procedures And The Fire Protection Report, Which Led To The Declaration That Nine SSD Paths Were Inoperable, Is Unknown At This Time.</strong><br /><i>Abstract:&nbsp;</i>On 082697, with Unit One (U-1) in Mode One at approximately 100% power, a review corrective actions for a problem identified through a self assessment was being performed. At 1100 it was discovered that the procedures for nine of the sixteen Quad Cities Safe Shutdown (SSD) paths did not contain adequate direction as required by the Fire Protection Report (FPR) for the tripping of breakers and the removal of breaker control circuit fuses for switchgear cubicles associated with non-SSD loads. Additionally, the procedures were found to conflict with the Fire Protection Report with regard to the availability of DC power for breaker control circuits. The root cause of this event was a lack of process for maintaining the accuracy and completeness of the SSD Analysis. The safety significance of this event was minimal. This event involves the capability to safely shutdown the reactor in the event of a severe fire. A probabilistic risk assessment for fire was performed to determine the integrated risk taking the effected SSD paths into account. Although the instantaneous risk while this SSD equipment was unavailable was about three times the base risk, the Station's projected integrated risk over a reactor year, including the time that these systems were inoperable, is not significantly higher than the base risk.
2541997022 | Quad Cities 1, Quad Cities 2 | 10/15/1997 | 11/12/1997 | 9711180274 | <strong>The Control Room Heating, Ventilation And Air Conditioning System Was Declared Inop Due To Inadequate Cooling Water Flow Which Was Caused By A System Perturbation.</strong><br /><i>Abstract:&nbsp;</i>On 101597, Unit One was operating at 100% power and Unit Two was in Cold Shutdown at 0% power. Operations personnel were performing surveillance procedure QCOS 5750-04, "Quarterly Testing of Control Room (CR) Heating, Ventilation, and Air Conditioning System Valves," when one of the Performance Acceptance Criteria (check valves full open) was not met. A flow rate of >/= 120 gallons per minute (gpm) through the water cooled condenser, as read on flow indicator FI 1/2-5795-342, verifies that check valves (1-5799-386 and 2-5799-386) have opened fully. The flow rate achieved was 115 gpm for both the Unit 1 and Unit 2 valves. Train "B" of the CR HVAC system was declared inoperable. Subsequent testing provided satisfactory results. The system was declared operable. The most probable cause of the low flow rate is the lifting of the Service Water System relief valve, as it is designed to do to, i.e., protect the HVAC condenser. Corrective actions include review and revision of the test procedure, and performance of a calculation to verify the validity of the 120 gpm requirement. There was no increased risk posed to the health and safety of onsite personnel or to the public as a result of this event.
2541997023 | Quad Cities 1 | 03/17/1997 | 11/25/1997 | 9712080146 | <strong>A Required Technical Specification (TS) Surveillance Was Not Performed Prior to Reactor Mode Change On Four Occasions Due To Inadequate Procedures Associated With Implementation Of The TS Upgrade Program</strong><br /><i>Abstract:&nbsp;</i>On four occasions between 031797 and 062297, pre-startup Average Power Range Monitors (APRM) downscale channel functional testing was not performed per TS requirements before entering Power Operations (Mode One) on Units One and Two. This resulted in the units being in a Limiting Condition for Operation (LCO) until weekly at-power surveillance verified the operability of the channel function. Shift personnel were not made aware of this lack of TS compliance until 102997. The root cause of this event is a cognitive personnel error due to a lack of information validation or verification by the Instrument Maintenance Department personnel responsible for implementing the Technical Specification Upgrade Project (TSUP). Procedure changes were not effectively validated for effect on TSUP and a new procedure that implemented the TS requirement was not properly integrated into existing startup checklists or the Electronic Work Control System. Corrective actions include incorporating new predefined surveillance work requests and revising station procedures to ensure the TS requirement is performed as specified. The safety significance to the health and safety of onsite personnel and to the public was minimal. Reactor Protective System (RPS) logic exists through the corresponding Intermediate Range Monitor (IRM) to provide a rod block and a trip signal as needed.
2541997024 | Quad Cities 1, Quad Cities 2 | 12/01/1997 | 12/22/1997 | 9801050293 | <strong>A Required 10CFR50.59 Summary Evaluation for a Change to the Updated Final Safety Analysis Report (UFSAR) was not Submitted to the NRC Due to an Administrative Oversight Error.</strong><br /><i>Abstract:&nbsp;</i>In mid-October, 1997, it was questioned that, during the preparation of the station 10CFR50.59 Safety Evaluation (SE) summary report, summaries of all SEs were not included. Subsequent to the issuance of the report on 103197, a review of all SEs not previously transmitted in 1995 and 1996 submittals was completed. The review revealed that between 1995 and 1996, the SE summaries that were not transmitted to the NRC had not identified any unreviewed safety questions or any changes to the facility as described in the UFSAR. On 120197, station personnel identified that SE 96-113, which did change the UFSAR, was not included in the summary SE report that was submitted to the NRC on 103197. The apparent cause of this error was an administrative oversight, in that the subject SE was inadvertently overlooked. Additionally and based upon industry feedback, an informed decision was made in 1995 to only send SEs to the NRC that involved facility changes, as described in the UFSAR. Corrective actions completed include a review of all SEs not submitted in the 1995 and 1996 summary reports and a pending action to submit all SEs not previously submitted. There is no resultant safety significance associated with these occurrences. This LER is being submitted voluntarily.
2541997025 | Quad Cities 1, Quad Cities 2 | 12/16/1996 | 12/05/1997 | 9712120256 | <strong>Units 1 And 2 Average Power Range Monitors (APRM) Flow Bias Were Not Calibrated To A Flow Signal Within The Required Interval Due To Inadequate Change Management When Implementing Upgraded Technical Specifications (TS). In Addition, This Calibration Was Not Performed Prior To Entering Power Operatio</strong><br /><i>Abstract:&nbsp;</i>On 121696 at 0445, Unit 1 was in Power Operation at 100 percent power when Unit 1 exceeded the allowed interval on a required weekly channel calibration "APRM Flow Biased Neutron Flux - High." On this occasion, Unit 1 was out of calibration for 19 consecutive days while in Power Operation. In addition, on 031797, the Station did not comply with TS 4.0.D when this same calibration had not been performed prior to a Unit 1 Mode change to Power Operation. On 062197, Unit 2 entered Power Operation and this calibration was not performed for Unit 2 prior to changing Mode. Unit 2 also exceeded the allowed interval as the calibration was not completed until 072297. On 100897, a Nuclear Engineer identified the calibration could be required prior to entering Power Operation following discussions with Nuclear Fuel Services and on 110797, the reportability was confirmed. The exceeded intervals and Mode change problems had separate causes. The cause of the calibrations exceeding the allowed interval was poor tracking of a known TS requirement due to inadequate change management during implementation of the upgraded TS. The cause of the Station not performing this calibration prior to entering the applicable Mode was that this TS requirement was not recognized due to a Station misinterpretation of the associated TS table notation. Corrective actions were to counsel personnel responsible for the change, conduct a trend investigation of TS noncompliance and revise procedures. The safety significance of this event is minimal as the applicable APRM signal does not affect the fuel safety analysis.
2541997026 | Quad Cities 1, Quad Cities 2 | 03/28/1997 | 02/02/1998 | 9802120298 | <strong>Technical Specification (TS) Required Instrument Channel Checks Were Not Documented Prior to Entering the Applicable Mode Due to Adequate Procedure Development and Review.</strong><br /><i>Abstract:&nbsp;</i>On 032897 at 1133, Unit 1 went from Cold Shutdown to Startup Mode and none of the Control Room (CR) readings for instrument channel checks applicable to Mode 2 were documented prior to changing Mode. These were in noncompliance with TS 4.0.D. On 060897 at 0542, this same noncompliance occurred when Unit 2 went from Cold Shutdown to Startup Mode. In addition, when further reviews were performed as initiated by revision 0 of this LER, channel checks required prior to entry into Hot Shutdown Mode and Primary Containment sump flowrate surveillances required for entry into Startup Mode were also found to have discrepancies. The root cause of these events was inadequate procedure development to ensure any instrumentation channel checks included in the CR readings or other required surveillances would be performed prior to entering the applicable Mode. Corrective actions were to revise procedures, counsel personnel, conduct a trend investigation of TS noncompliance, review TS sections to ensure surveillance requirements are implemented, including Mode change requirements, and to revise procedures. The safety significance of this event is minimal. When the channel checks and sump surveillances were performed there were no discrepancies identified, demonstrating the conditions were acceptable.
2541997027 | Quad Cities 1, Quad Cities 2 | 12/18/1997 | 01/16/1998 | 9801260484 | <strong>The Unit 1 and Unit 1/2 Emergency Diesel Generators (EDG) Were Simultaneously Inoperable While Unit 1 Was At Power Due To Time Delay Relay 2 Failing To Meet Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On 121897, Unit One (U-1) was in Mode One at approximately 99% power, with the U-1 Emergency Diesel Generator (EDG) Out-Of-Service (OOS) in day three of a seven day Limiting Condition for Operation (LCO) to perform periodic preventative maintenance. At 2125 the U-1/2 EDG Overcrank Time Delay (TD) 2 relay failed its acceptance criteria as identified in Diesel Generator Monthly Load Test. The U-1/2 EDG was declared inoperable when the TD2 relay was timed at 11.3 seconds when its acceptance criteria has been established at 15.0 to 16.5 seconds. The root cause of the this event appears to be time delay relay "drift" due to the lack of proper setup testing. The time delay relay appears to time out faster when operationally tested in the local control panel than what it was set at in the bench calibration phase. Results from the Materials Engineering Group (MEG) lab testing of the relay will be used in validating this data. The Unit 1/2 EDG TD2 relay was replaced and subsequently tested satisfactorily. The corrective actions include the calibration/check of EDG TD1 and TD2 relays every month under actual starting conditions, and an evaluation will be performed to determine the setpoint basis and if an alternate TD relay or setpoint adjustment is required for EDG TD1 and TD2 relays. Having 2 EDG's inoperable is a significant occurrence; however, the Safety Significance is considered minimal. The unit operators made preparation for an orderly shutdown in accordance with TS 3.9.A.6 which requires that one EDG be returned to operable within 2 hours or be shutdown within the next 12 hours. The TD2 relays were replaced on the 1/2 EDG in 1 hour and 15 minutes. (An additional 3 hours was needed to clear paperwork to declare the 1/2 D/G operable.) Unit 1 and Unit 2 SBO Diesels were available.
2541997029 | Quad Cities 1, Quad Cities 2 | 03/16/1997 | 01/09/1998 | 9801160051 | <strong>Units 1 and 2 Rod Block Monitor (RBM) Channel Functional Testing Was Not Accomplished Within 7 Days Prior To Startup As Required By The Technical Specification (TS) Individual Surveillance Requirement Due to Misinterpretation of TS and Inadequate Procedure Validation When Implementing Upgraded Techn</strong><br /><i>Abstract:&nbsp;</i>From 31697 to 62497, five reactor startups were performed without testing Rod Block Monitor Channels Prior-To-Startup as required by TSUP. Three of these events resulted in entering the operating mode requiring RBM operability without having verified operability of all RBM functional units. Root cause is personnel error during TSUP implementation involving interpretation of surveillance requirements, inadequate validation of the test procedure and failure to integrate the surveillance into startup checklists or Engineering Work Control System. Corrective actions will revise procedures and processes to ensure surveillance requirements met. The safety significance to health and safety of onsite personnel and to public was minimal. In considering safety significance, the pertinent scenario involves the unlikely condition of simultaneous failure of both RBM channels and subsequent withdraw of an incorrect control rod. With the Rod Worth Minimizer operable and a second person verifying control rod movements, chances of making a withdraw error are low. However, if it should happen, Unit 1 and 2 Operating Limit Minimum Critical Power Ratio is set sufficiently high such that if an unblocked rod withdrawal error had occurred, fuel or cladding damage would not occur.
2551997001 | Palisades | 01/06/1997 | 02/05/1997 | 9702120343 | <strong>Licensee Event Report 97-001, Violation Of Technical Specifications 3.1.3, T Sub Ave Less Than 525 Degrees F When Reactor Critical</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1997, at 1410, while synchronizing the Main Generator to the grid, T sub AVE dropped to approximately 524 degrees F. This temperature was below the minimum temperature for criticality, 525 degrees F, specified in Technical Specifications. T sub AVE Was below 525 degrees F for less than one minute. The event occurred because the control rod withdrawal rate to increase power was not sufficient to match the increase in steam demand. On January 6, 1997 at 1917, during a plant shutdown, T sub AvE dropped below 525 degrees F for six minutes. Reactor Engineering has determined that the reactor was subcritical by 0.3% [symbols omitted],; however, reactor power was greater than 10**-4% power, which is a violation of Technical Specifications. In both of these events the task planning was not comprehensive enough to prepare the operators to recognize and implement the necessary contingency and compensatory actions required for the plant and equipment responses that were actually experienced.
2551997002 | Palisades | 01/23/1997 | 02/21/1997 | 9703030529 | <strong>Licensee Event Report 97-002 - Failure To Meet Technical Specifications 4.5.2d(1)(B) For Testing Of The Emergency Escape Airlock</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1997, the plant was operating at 99.6% power. During the preparation of the Palisades Improved Technical Specifications, it was recognized that Palisades was not in compliance with the Technical Specification Surveillance requirement 4.5.2d(1)(b) for the emergency escape air lock. At 1528 on January 23, 1997, the emergency escape air lock was declared inoperable and Technical Specification 4.0.3 was entered due to the missed surveillance. At 1010 on January 24, 1997, the emergency escape air lock testing was completed and the emergency escape air lock was declared operable. This testing restored compliance with Technical Specifications.
2551997003 | Palisades | 11/01/1996 | 03/21/1997 | 9703270234 | <strong>Informational Licensee Event Report 97-003 - Potential for Steam Voiding and Water Hammer in Containment Air Cooler System, and for Overpressurization of Closed Piping Systems</strong><br /><i>Abstract:&nbsp;</i>The Palisades review of Generic Letter 96-06, has determined the following: 1. Water hammer could occur in the Service Water (SW) return piping downstream of the CACs (VHX-1, 2, & 3) which are in-service. 2. While CAC VHX-4 is isolated during a DBA, it was determined that a steam bubble could form. 3. The CACs (VHX-1, 2, & 3) were determined to be susceptible to short-term two-phase flow during a DBA. 4. Simplified, bounding analyses showed that the lines would remain operable. Detailed analyses are in progress to verify that FSAR design criteria are satisfied. Four piping lines were determined to be potentially susceptible to pressurization due to a containment temperature increase during an accident. These four piping lines are the clean waste receiver tank fill and drain lines (2 lines) and the reactor cavity fill and drain lines (2 lines). Analyses were not performed to predict pressures in the lines because the plant was in a refueling outage. Instead, modifications or procedure changes were completed before startup to eliminate the potential for overpressurization.
2551997004 | Palisades | 02/21/1997 | 03/24/1997 | 9704010031 | <strong>Trip Of High Pressure Safety Injection Pump While Filling Safety Injection Tank Resulting In Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1997, at 2004 hours, the plant was stable and operating at approximately 99.6% power. While supporting performance of Technical Specification (TS) sampling for safety injection tank (SIT) boron concentration, High Pressure Safety Injection Pump (HPSI) P-66A tripped due to a malfunctioning Y-phase time-overcurrent relay. This resulted in two emergency core cooling components (the safety injection tank and the HPSI pump) being inoperable, a condition prohibited by Technical Specifications (TS), and the plant entered Technical Specification 3.0.3. This event was very similar to the event that occurred on July 17, 1996 and reported in LER 96-010. Immediate investigation by Operations led to the resetting of the tripped relay by hand. The safety injection tank was refilled using P-66A, and TS 3.0.3 was exited. The plant was in the TS 3.0.3 action statement for approximately 32 minutes. The plant remained in a 24-hour action statement per TS 3.3.2 due to the inoperability of the HPSI pump, as the problem with the relay reset had not been resolved. The breaker relay was found to have a small metal particle lodged in its operating mechanism. The particle prevented proper reset of the breaker's Y-phase time over current relay induction disk after the P-66A motor start. After removal of the metal particle, the relay was tested and performed satisfactorily. The Y-phase time-overcurrent relay was cut out of service as permitted by plant design and the HPSI pump declared operable at 0043 hours on February 22, 1997, exiting TS 3.3.2. Subsequently, this relay was replaced with an identical model on February 25, 1997, with no further problems identified
2551997005 | Palisades | 12/20/1996 | 03/21/1997 | 9703270223 | <strong>Licensee Event Report 97-005 - Operation Of The Plant Outside The Design Basis Due To An Unacceptable Repair</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1996, at approximately 1800 with the plant in hot shutdown and the primary coolant system (PCS) at 2066 PSIA and 532 degrees F, both Main Steam Isolation Valves (MSIV), CV-0501 and CV-0510, were found leaking steam at the west stuffing box pipe plugs. power, temporary leak repairs were attempted, but could not be performed. On CV-0501, the drilling process penetrated the pressure boundary at an approximate depth of 1/8 inch. On CV-0510, the pipe plug threaded area leakage was unstable. Management decided to place the plant in cold shutdown for permanent repairs to the valves. Subsequently, inspection of the valves determined that unacceptable repairs had been made to the MSIV stuffing box pipe plugs which created the steam leaks. For CV-0501, the weld material over the hole in the pipe plug most likely violated the minimum wall requirements; however, this could not be validated. For CV-0510, the low pressure cast iron plug did not meet the forged steel high pressure requirements. These ASME Code violations are considered to have resulted in operation of the plant outside of the design basis. It should be noted that the steam leaks were from the treaded portions of the pipe plugs and not due to the failure of the pipe plugs themselves.
2551997006 | Palisades | 04/12/1997 | 05/12/1997 | 9705210029 | <strong>Licensee Event Report 97-006 - Overtime Exceeded For Radiation Protection Technicians</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1997, with the plant operating at 99.6% power, Operations personnel were discussing working hours with a Radiation Safety Technician and discovered three occasions in 1997 when the Overtime Limitations of Administrative Procedure 1.00 and Technical Specification 6.2.2.e.2 were exceeded. In each case, Radiation Safety Technicians who worked both days of the weekend, worked more than 24 hours in a 48-hour period. Subsequent evaluation discovered a total of seven occurrences in 1996 and 1997. These seven occurrences were determined to represent a significant administrative breakdown of the Overtime Limitations Policy and therefore reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant Technical Specifications. The Chemical & Radiological Services (C&RS) Scheduler took immediate action to ensure technicians were not scheduled for more than one weekend or holiday shift in any two day period. In addition, the Overtime Limitation responsibilities and expectations were communicated to all site and contractor supervisors. Future actions include: reinforcement of Overtime Limitation Program responsibilities to individuals, supervisors and contractors; clarification of the Administrative Procedure 1.00 Overtime Limitation Section; and a monthly audit of individual time sheets.
2551997007 | Palisades | 08/26/1997 | 09/24/1997 | 9709300385 | <strong>Licensee Event Report 97-007 - Inadequate Testing Of Diesel Generator Sequencer Control Relay Contacts</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1997, at approximately 1200 hours with the plant at 100% power, it was determined that contacts on the emergency diesel generator sequencer load control relays 106D-1/XL and 106D-2/XL (one contact per relay per diesel generator) were not adequately tested as part of the Technical Specification Test Program. The function of these contacts is to provide a block signal to the SIS-X relays. Failure of this contact to open following a safety injection system actuation signal, coincident with a loss of off-site power, would result in simultaneously loading all safety system loads onto the diesel generator as soon as the output breaker closed. This large load on the diesel generator would potentially result in the diesel generator breaker rapidly tripping on overcurrent. Based on failure to test these relay contacts in accordance with Technical Specification requirements, both diesel generators were declared inoperable. Testing of the subject relay contacts was successfully completed within the 24 hours allowed by T.S. 4.0.3. The controlling Technical Specification was exited and the equipment declared operable at approximately 2100 hours on August 26, 1997. Future Technical Specification testing will include testing of these relay contacts.
2551997008 | Palisades | 09/12/1997 | 10/10/1997 | 9710220082 | <strong>Licensee Event Report 97-008 - Spurious Valve Operation Could Result In Loss Of Shutdown Capabilities Per 10 CFR 50, Appendix R, Section III.L</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1997, at approximately 1330 hours, with Palisades operating at approximately 100% power, an Appendix R Program Engineering Analysis was discovered to have failed to properly evaluate the potential for spurious opening of Service Water (SW) cross-tie valves (CV-0879, CV-0880 and CV-0951). These three valves supply backup SW to cool Engineered Safeguards pump seals and bearings if a loss of Component Cooling Water (CCW) would occur. Specifically, a fire in one of several areas could result in a single spurious opening of any of these valves which could potentially result in a loss of CCW inventory to the lower pressure SW System. This condition was found during a planned review of Appendix R Program engineering analyses. This review determined the analysis contained errors which could potentially place the plant in a scenario which was not specifically addressed in the Appendix R program analyses. This event is reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the plant design basis. This Appendix R issue is reportable because the analysis failed to identify a condition which could potentially result in a loss of CCW inventory due to a fire in certain fire areas. This loss of CCW would jeopardize the ability to achieve the 10 CFR 50, Appendix R, Part III, L required plant conditions.
2551997009 | Palisades | 09/23/1997 | 10/23/1997 | 9710300112 | <strong>Licensee Event Report 97-009-Procedure Weakness In Implementing Appendix R Shutdown Methodology</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1997, at 1105 hours with the plant at approximately 100% power, it was recognized that an operator action to support an Appendix R program analysis had not been implemented in the appropriate Off-Normal Procedure (ONP). Specifically ONP 25.2, "Alternate Safe Shutdown Procedure" did not include the action to trip all four primary coolant pumps if the control room had to be evacuated. Instead, the procedure directed the control room operators to "...trip two primary coolant pumps and leave two operating ...". Once the control room is evacuated, no instrumentation is identified to provide the operational status of the primary coolant pumps or the status of the component cooling water to the primary coolant pump motor and seals. It has been identified that a fire-initiated hot short could cause one of the component cooling water containment isolation valves to spuriously close, isolating cooling flow to the primary coolant pumps. Palisades' primary coolant pump operation has not been analyzed for operation without seal or motor bearing cooling. The manufacturer indicates that no damage to the seal or pump motor will occur if operated without cooling for no more than ten minutes. ONP 25.2 has been revised to require tripping of all four primary coolant pumps when evacuating of the control room. Having not implemented the action to support the analysis is contrary to 10 CFR 50 Appendix R direction that during post fire shutdown,... the fission product barrier shall not be affected, i.e. there shall be no ...rupture of primary coolant boundary. This is reported as a condition outside of the plant's design basis.
2551997010 | Palisades | 09/30/1997 | 10/30/1997 | 9711050112 | <strong>Licensee Event Report 97-010-Inadequacy In Appendix R Analysis Results In A Condition Outside The Design Basis Of The Plant</strong><br /><i>Abstract:&nbsp;</i>A 10 CFR 50, Appendix R analysis concluded the simultaneous opening of two main steam line atmospheric steam dump valves (ASDVs) required termination of the steam generator blowdown by local manual actions within ten minutes. In the analysis, opening of two of the four main steam ASDVs occurred spuriously from a hot short. Recent reviews of the Appendix R analysis determined it should have accounted for all four main steam ASDVs and the turbine bypass valve (TBV) spuriously opening. A new evaluation indicates that local manual actions must be completed within six minutes to close the ASDVs in the event of the Appendix R fire scenario resulting in all four ASDVs and the TBV opening. A walk-through verification concluded that the ASDVs could be closed within six minutes. The procedure has been revised and operator training of the procedure revision has been completed. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the plant design basis. The earlier Appendix R analysis contained errors which could have potentially placed the plant in a scenario which was not addressed with approved procedures.
2551997011 | Palisades | 10/12/1997 | 10/29/1998 | 9811090137 | <strong>Starting Of Primary Coolant Pump With Steam Generator Temperatures Greater Than Cold Leg Temperatures</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1997, plant heatup from a short maintenance outage was in progress. At approximately 1926 hours with the plant at 250 psia and 130 degrees F, Primary Coolant Pump (PCP) P-50D was started. Immediately following the pump start, the Primary Coolant System (PCS) pressure started to rise. Anticipating the PCS pressure rise, operators took manual action and limited the pressure rise to approximately 280 psia. As a result, no Low Temperature Overpressure Protection (LTOP) actuation occurred since the LTOP setpoint at prevailing PCS temperature was approximately 310 psia. Because PCS pressure rose to this extent in a solid PCS, it was concluded that Technical Specification 3.1.1.h(2) had been violated. Technical Specification 3.1.1.h.(2) requires that forced circulation (starting of the first primary coolant pump) shall not be initiated unless"..the steam generator secondary temperature is less than or equal to T sub cold" to prevent an overpressurization of the PCS. From the amount of PCS pressure rise following start of the pump, it is apparent that the bulk steam generator secondary temperature could not have been less than T sub cold. The pressure transient was within design capabilities of the PCS and Shutdown Cooling System. The prevailing plant conditions and operating crew response associated with this event have been reviewed. The Standard Operating Procedure (SOP) used for starting the primary coolant pumps has been enhanced.
2551997012 | Palisades | 10/17/1997 | 01/26/1998 | 9802040056 | <strong>Control Rods Deenergized While In Power Operation</strong><br /><i>Abstract:&nbsp;</i>At 2102 hours on October 16, 1997, during power escalation to 85% power, it was noted that control rod #38 did not move as expected. The plant power escalation was ceased and the power level was held at 80% until the repairs to control rod #38 and repairs to a secondary side pump were completed. For personnel safety during repair, the control room personnel elected to remove rod drive power from all control rod drive mechanisms, thus rendering the control rods immovable from the control room. However, the ability to trip the control rods was retained. The control room personnel did not question the appropriateness of disabling a reactivity control system, did not recognize it was a procedure violation, and failed to realize that they had entered a Technical Specification LCO action statement. In addition, maintenance procedures were violated and the authorized scope of the maintenance work order was exceeded. Plant management did not initially identify the significance of this event. Later in the event, management initiated a multidisciplinary root cause analysis. The regulatory significance of this event stems from the simultaneous failure of multiple barriers, any one of which should have prevented this event. A multidiscipline root cause analysis team identified the causes for the event. Corrective actions are underway.
2551997013 | Palisades | 11/10/1997 | 04/15/1998 | 9804220224 | <strong>Supplement 1, "Violation Of Technical Specification 6.5.7 For Failure To Fully Test Valves"</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1997, the plant was operating at 99.6% power. During the evaluation of an NRC Architect-Engineering Design Inspection team request for information, it was determined the check valves (CK-ES3339 and CK-ES3340) in the minimum flow recirculation piping from the discharge of each High Pressure Safety Injection (HPSI) pump were not periodically tested to confirm their closure capability. It was concluded that this is contrary to the requirements of ASME XI and Technical Specification 6.5.7. A review of other check valves, control valves, and motor operated valves for similar testing discrepancies identified four additional instances where valves were not fully tested. These four instances are reported in this supplement. In each case, upon discovery, the equipment was either declared inoperable until testing was performed or determined to be operable per ASME Code or Technical Specifications requirements. All affected valves which were declared inoperable were subsequently tested and were declared operable based on the results, within the 24 hour period allowed by Technical Specification 4.0.3.
2591997001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 02/03/1997 | 03/05/1997 | 9703120079 | <strong>A potential overpressurization condition of a containment penetration pipe due to thermal expansion of entrapped water was identified.</strong><br /><i>Abstract:&nbsp;</i>On February 3, 1997, with Units 2 and 3 at approximately 29 percent and 83 percent power, respectively, and Unit 1 shutdown and defueled, a TVA engineering evaluation determined that during a design basis accident a pipe which penetrates the containment is susceptible to thermal overpressurization stresses resulting in pipe stresses in excess of BFN UFSAR allowable stresses. The cause of this condition results from a potentially filled and isolated pipe that penetrates the containment and is susceptible to thermal expansion during some design basis accident conditions. The corrective action to resolve this condition is to revise plant procedures to ensure that a sufficient quantity of water is drained from the affected pipe at the end of an outage. This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(ii)(B) as a condition outside design basis of the plant. No Previous LERs on similar events were identified.
2591997002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 03/14/1997 | 04/11/1997 | 9704150090 | <strong>Inadequate CREVS Surveillance Instruction Identified During Generic Letter 96-01 Review</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1997, at 1200 hours, a team performing reviews of Surveillance Instructions (SIs) in conjunction with Generic Letter 96-01, 'Testing of Safety-Related Logic Circuits,' determined that procedure 0-SI-4.2.G-2, 'Control Room Isolation and Pressurization Functional Test' did not fully test all relay logic combinations. Specifically, there was insufficient overlap in the SI section that tested the control bay damper isolation logic for the redundant vent solenoids. The SI was promptly revised to correct the deficiency and the applicable SI section successfully completed by 2300 hours the same day. A root cause analysis has determined that the procedure was incorrectly revised in 1993. The Generic Letter 96-01 review effort is continuing. In addition, System Engineering will conduct training on the specific circumstances which led to the deficient procedure.
2591997003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 08/12/1997 | 10/14/1997 | 9710220174 | <strong>Containment Pressure Could Exceed Design Containment Purging or Inerting if a Loss of Coolant Accident Occurs, Due to Unanalyzed Suppression Pool Bypass Path</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1997, during a review of industry reportable events, a valve alignment was identified which could, if a Primary Containment Isolation System (PCIS) Division I failure occurred, create a flow path that would allow the steam released during a loss of coolant accident (LOCA) to bypass the suppression pool, degrading the pressure suppression function of the containment. This valve alignment occurs when inerting or purging the drywell and suppression chamber simultaneously during plant startup and shutdown. A subsequent analysis of the design basis LOCA showed that peak containment pressure could exceed the maximum design pressure of 62 psig while in this configuration if Division I of the PCIS failed. If Division I of PCIS isolates as designed, containment design pressure would not be exceeded. Appropriate procedures have been changed to prohibit this alignment except during cold shutdown conditions. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(ii)(B) as any event or condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant.
2591997004 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 10/10/1997 | 11/07/1997 | 9711180007 | <strong>Residual Heat Removal Service Water Pump Limiting Condition for Operation is Non-Conservative</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1997, BFN engineering personnel identified an apparent inconsistency between the BFN FSAR and the plant Technical Specification 3.5.C, RHR (Residual Heat Removal) Service Water and Emergency Equipment Cooling Water (EECW) Systems, regarding the number of Residual Heat Removal Service Water (RHRSW) pumps required to remove heat from a unit following a design basis accident. The BFN FSAR states that two RHRSW pumps per unit are required to serve the core and containment cooling function following a design basis accident. There are eight pumps that can be aligned to RHRSW service. The current BFN Technical Specifications for the RHRSW system require a total of seven, five and four pumps to be operable and assigned to RHRSW service with three, two and one units fueled, respectively. Since two RHRSW pumps are supplied from emergency diesel generator A and two are supplied from emergency diesel generator B, then the potential exists for a single failure of diesel generator A or B to reduce the number of available RHRSW pumps to less than the number required by the FSAR for the case of two or three unit operation. Immediately upon the discovery of this condition, administrative controls were implemented to require two operable RHRSW pumps per unit. On October 10, 1997, after completing an analysis that confirmed the validity of the RHRSW pump requirements as stated in the FSAR, this condition was reported to NRC in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a event or condition that resulted in the nuclear plant being in a condition that was outside the design basis of the plant. A request for a change to Technical Specification 3.5.C will be submitted to the NRC to correct the non-conservatism.
2601997001 | Browns Ferry 2 | 04/24/1997 | 05/23/1997 | 9706040267 | <strong>Reactor Scram as a Result of Personnel Error During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1997, at 1814 Central Daylight Time (CDT), Unit 2 scrammed from full power due to a turbine trip caused by a high reactor water level trip signal. The main turbine and all three reactor feedwater pump turbines tripped when a high reactor water level trip signal was generated during the performance of 2-SI-4.2.B-ATU(C), Core and Containment Cooling Systems Analog Trip Unit Functional Test. The initiating high water level signal was caused by personnel error when a volt-ohm meter being used in the test was inadvertently connected across terminals of a companion Channel A relay instead of the intended Channel C relay. When Channel C was tripped per the test instruction with the meter connected to Channel A, the two out of two trip logic for high water level was completed. The Main Steam Isolation Valves (MSIV) subsequently closed from an unexpected high steam flow signal associated with the transient. The closure of the MSIVs in this event was an unexpected response to a turbine trip transient. The most probable cause of the high steam flow signal was instrumentation response to a steam line pressure wave and process noise from Main steam relief valve (MSRV) operation. Reactor water level decreased to -45 inches as a result of the loss of feedwater and the reactor pressure increase from the MSIV closure. Water level was restored and maintained by manual initiation of the Reactor Core Isolation Cooling System and automatic initiation of the High Pressure Coolant Injection System. The MSRVs functioned to control reactor pressure. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv), as any event or condition that resulted in manual or automatic actuation of any engineered safety feature including the reactor protection system. Corrective actions included personnel corrective action. TVA will place supplemental labels on individual relays. In addition, TVA will issue a design change to increase the response time for the main steam line high flow isolation function.
2601997002 | Browns Ferry 2, Browns Ferry 3 | 06/26/1997 | 07/25/1997 | 9708010256 | <strong>During Generic Letter 96-01 review, inadequate RHR surveillance instructions were discovered. These SIs resulted in not fully testing RHR TS logic circuits. Root cause was personnel error in that the SIs were not properly revised.</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1997, at 1330 hours, a team performing reviews of Surveillance Instructions (SIs) in conjunction with Generic Letter 96-01, "Testing of Safety-Related Logic Circuits," discovered that four SIs (Functional Testing of RHR Loop I and Loop II Valve Logic and Interlocks) did not fully test all relay logic combinations. Specifically, relay contacts for the reactor recirculation pump discharge isolation valve automatic closure logic were not tested. The root cause of this event was personnel error in that applicable SIs were not properly revised. This oversight occurred when the original SIs, which were performed during outages, were revised to allow the SIs to be performed while the units were in operation. These revisions occurred in June 1992 and September 1995 for Units 2 and 3, respectively. Corrective actions include: (1) Work Orders (WOs) were written to verify the relay contacts were operating properly. The WOs were successfully completed by 2253 hours and 2300 hours on the discovery date. (2) Applicable SIs will be revised prior to their next performance to ensure that the relay contacts are adequately tested. The review of SIs in response to Generic Letter (GL) 96-01 is complete. A previous LER (259/97002) identified a similar GL 96-01 oversight for the CREV system.
2601997003 | Browns Ferry 2 | 07/11/1997 | 08/07/1997 | 9708140241 | <strong>Field measurements of the HPCI Turbine speed indicated speed was lower than the speed displayed in Control Room. The cause was an improper evaluation of a valve leak which resulted in water intrusion into a unsealed junction box.</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1997, at 1910 hours, with Units 2 and 3 at 100 percent power, and Unit 1 defueled, it was determined that the HPCI turbine speed was lower than indicated. Specifically, during the performance of a surveillance instruction (SI) for testing the HPCI flow rate at normal reactor vessel pressure, field measurements of the HPCI turbine speed identified that the HPCI turbine speed was lower than the speed displayed in the Unit 2 Control Room. Since the HPCI turbine speed did not meet its SI acceptance criteria, HPCI was declared inoperable. The root cause of this faulty display was due to an improper evaluation of a valve leak. The valve leak resulted in water intrusion in an unsealed junction box causing grounds to some HPCI cables. HPCI was declared inoperable. The immediate corrective actions included troubleshooting and sealing of the junction box. Corrective actions to preclude recurrence will be to perform and document a walkdown of the HPCI, RCIC, and Reactor Feedwater Pump rooms where steam condensate could leak on junction boxes and to seal those conduit terminations deemed to be unacceptable. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(v) as any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems needed to mitigate the consequences of an accident. No previous LER was identified where HPCI turbine speed was affected by water intrusion.
2601997004 | Browns Ferry 2, Browns Ferry 3 | 09/09/1997 | 10/09/1997 | 9710210042 | <strong>Technical Specification (TS) surveillances were not performed During refueling outage timeframes. The root cause was a result of personnel error and not following procedure. This condition is prohibited by technical specifications.</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1997, at 1600 hours, Units 2 and 3 were approximately 100 and 95 percent power, respectively. Unit 1 was defueled. At that time, TVA determined that previous testing of snubbers had not been performed during refueling outage timeframes in accordance with Technical Specification (TS) requirements. On September 19, 1997, TVA identified another similar occurrence regarding testing of the suppression chamber to reactor building vacuum breakers. These vacuum breakers were also not being tested during refueling outage timeframes. These surveillances were being performed as pre-outage or routine activities. The root cause for not performing the TS surveillances within the correct timeframe was the ineffective control of outage schedules. Specifically, Work Control (WC) personnel were not properly instructed to ensure that TS surveillances were incorporated in refueling outage schedules. Additionally, a procedure was not followed in that a special surveillance schedule was not provided for all tests required to be completed during in refueling outages. The immediate corrective actions included placing these TS surveillances into the refueling outage schedules. Corrective action to preclude recurrence was a review of TS surveillances to ensure no other surveillances were missed being incorporated into refueling outage schedules. TVA will also provide guidance on job performance standards to WC personnel. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(i)(B) as any operation or condition prohibited by the plant's technical specifications. No previous LERs were identified where TS surveillances were not incorporated into an outage schedule.
2601997005 | Browns Ferry 2, Browns Ferry 1, Browns Ferry 3 | 10/12/1997 | 11/10/1997 | 9711180019 | <strong>ESF components were actuated as a result of an inadequate procedure. This is reportable due to ESF actuations in accordance With 10 CFR 50.73 (a)(2)(iv).</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1997, at approximately 0559 hours, Unit 2 was in cold shutdown in a refueling outage. Unit 3 was at 100 percent power. Unit 1 was defueled. At that time, a Unit 2 post modification test was being performed for a modification on the Unit 2 main steam relief valves. Instrumentation and Controls (I&C) personnel inadvertently made contact with two relay terminals simultaneously while attaching an alligator clip to one of the relay terminals. This initiated several engineered safety feature actuations. The root cause was a result of an inadequate procedure. Immediate corrective actions included: (1) CS pumps were secured and injection valves were closed, (2) refueling floor activities were stopped, (3) EDGs were secured and placed in standby, (4) alligator clips were removed, and the PMT was halted, and (5) PMT was revised and was successfully performed. Corrective actions to preclude recurrence include: (1) The Modification Test Program procedure will be revised, and (2) I&C personnel will review the problem evaluation report associated with this LER to sensitize personnel to the proper use of test clips. As a result of the ESF actuations, this report is submitted in accordance with 10 CFR 50.73 (a)(2)(iv) as a condition that resulted in the manual or automatic initiation of any ESF. There were several previous LERs (260/87006, 260/88018, 259/88019, 260/89005, 260/89020, 259/90008, 259/94001, 260/94012 and 259/95001) for jumper problems.
2601997006 | Browns Ferry 2 | 10/19/1997 | 11/18/1997 | 9711260239 | <strong>High Pressure Coolant Injection Inoperable As A Result Of HPCI Turbine Inlet Steam Line Drain Pot High Level</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1997, at 1629 hours CDT, TVA declared the Unit 2 High Pressure Coolant Injection (HPCI) system inoperable as a result of a HPCI turbine inlet steam line drain pot high level. As required by Technical Specifications (TS), TVA entered a seven day Limiting Condition For Operation (LCO) for an inoperable HPCI system. On October 21, 1997, at 0650 hours following successful completion of the cold start portion of Surveillance Instruction, HPCI Flow Rate Test At Normal RPV Pressure, the Unit 2 HPCI system was returned to standby readiness and declared operable. TVA's investigation into the cause of this event was inconclusive. As part of Unit 2 Cycle 9 Outage, TVA replaced the turbine steam supply valve, which is located downstream of the HPCI turbine inlet steam line drain pot, as well as the steam trap, and steam trap bypass valve, which are both located downstream of the HPCI turbine inlet steam line drain pot. During the replacement of the turbine steam supply valve the retaining welds were removed with an abrasive cutting tool. It is believed that during the removal operation fines may have entered the system. Corrective actions will include a review the maintenance and modification processes and procedural controls. If necessary, the controls will be modified. TVA intends to replace the Unit 3 HPCI turbine steam supply valve during the next scheduled Unit 3 refueling outage. The modification package that will replace the valve will provide instructions to ensure that the affected piping is inspected following the activity. TVA is providing this report in accordance with 10 CFR 50.73(a)(2)(v), as an event or condition that alone could have prevented the fulfillment of the safety function of a structure needed to mitigate the consequences of an accident.
2601997007 | Browns Ferry 2 | 10/28/1997 | 11/25/1997 | 9712020132 | <strong>Reactor Scram Resulting from Pressure Perturbation in the Electro-Hydraulic Control System Caused by Testing #1 Turbine Control Valve</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, at 1509 Central Standard Time (CST), Unit 2 automatically scrammed from approximately 70 percent power while cycling #1 Turbine Control Valve after repair. The scram resulted from an actuation of scram channel B1 caused by a pressure perturbation in the electro-hydraulic control (EHC) system at the turbine control valves. The pressure perturbation was induced by opening #1 turbine control valve. A half scram was previously present in RPS A due to cycling #1 control valve. Subsequent testing showed that the seal-in contact for one of the contactors in scram channel B1 (5A-K14B) exhibited chattering when subjected to reduced voltage. The scram contactor was replaced. Other corrective actions include procedure revisions to mitigate the consequences of pressure perturbation experienced while testing control valves, the installation of orifices in the EHC lines on the turbine control valves, and conducting a failure analysis of the RIPS contactor that was replaced. TVA is reporting this event in accordance with 10 CFR 50.73(a)(2)(iv), as an event that resulted in automatic actuation of an engineered safety feature including the reactor protection system.
2601997008 | Browns Ferry 2 | 11/04/1997 | 12/03/1997 | 9712110186 | <strong>Main Steam Safety/Relief Valves Exceeded the Technical Specifications Required Setpoint Limit as a Result of Pilot Valve Disc/Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1997, with Unit 2 at 100 percent power following the Unit 2 cycle 9 refueling outage, Unit 3 operating at 100 percent power, and Unit 1 shutdown and defueled, Wyle Laboratories notified TVA that 5 of the 13 Unit 2 main steam safety/relief valves (SRV) pilot cartridges removed during the Unit 2 cycle 9 refueling outage failed the setpoint tolerance bench tests. Wyle Laboratories' tests discovered that the SRVs' as-found setpoints were outside the TS setpoint tolerance of +/- 11 psi. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's technical specifications (TS). The cause was SRV pilot disc/seat bonding attributed to corrosion at the two-stage SRV pilot disc/seat interface. This resulted in drifting of the SRV setpoints. The Unit 2 SRV pilot cartridges were installed during the Unit 2 forced outage (October 29-November 3, 1996). Setpoint drift is a generic concern experienced by utilities using Target Rock Two-Stage SRVs (Model No. 7567F) in boiling water reactors and is being investigated by the Boiling Water Reactors Owners Group (BWROG) SRV Drift Fix Development Committee and the manufacturer. TVA will continue to participate in the BWROG's evaluation of the long-term solution for the SRV setpoint drift problem. During the Unit 2, cycle 9 outage, SRV pressure switches were installed to minimize the effects of setpoint drift. In addition, TVA will continue to evaluate other possible solutions. Previous LERs for failed SRV testing included: 260/87005, 259/88053, 260/93003, 260/95003, 260/96004, 260/96008, and 296/97003.
2611997001 | Robinson 2 | 01/10/1997 | 02/09/1997 | 9702110274 | <strong>Technical Specification Violation Due To Missed Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1997, H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100%. power. At 0149 hours Eastern Daylight Time, plant operators initiated a routine containment vessel pressure relief. At 0155 hours, operators discovered that a source check of the Radiation Monitoring System (RMS) radionoble gas monitor for the containment (i.e., monitor RMS-12) had not been performed as required by plant procedures and Technical Specifications (TS), and secured the pressure relief. Operators then performed the required source check of RMS-12, and the pressure relief was restarted at 0205 hours. This event was caused by personnel error. The operator conducting the pressure relief failed to fully review procedural requirements established to perform the containment pressure relief prior to commencing this evolution. The operator responsible for this error was counseled. This event had no adverse impact on plant or public safety since the release was continuously monitored by plant vent monitors RMS- 11, RMS-12, and RMS-14C. RMS-11 and RMS-12 would have isolated the release if an alarm had occurred. Technical Specification (TS) Section 4.19, 'Radioactive Effluent Instrumentation,' requires, in part, that radioactive gaseous effluent monitoring instrumentation channels be demonstrated operable by performance of a source check at the frequencies shown in TS Table 4.19-2, 'Radioactive Gaseous Effluent Monitoring Instrumentation Surveillance Requirements.' TS Table 4.19-2 requires that RMS-12 be source checked prior to each containment release. Since RMS-12 was not source checked prior to initiating the pressure relief, this condition constitutes a condition prohibited by TS. Accordingly, this report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B).
2611997002 | Robinson 2 | 01/10/1997 | 02/09/1997 | 9702200003 | <strong>Technical Specification Violation Due To Inadequate Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1997, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 operating at 100% power, plant Engineering personnel discovered that the containment personnel airlock had not been tested as required by the plant's Technical Specifications (TS) and 10 CFR 50, Appendix J, following startup from Refueling Outage 17. A modification implemented during Refueling Outage 17 modified the Penetration Pressurization System (PPS), which monitored containment leakage from the personnel airlock door seals, from a continuous monitoring system to an intermittent monitoring system. Personnel involved in preparing this modification failed to recognize that the continuous monitoring function of the PPS was an alternative accepted by the NRC to exempt the plant from the testing requirements of 10 CFR 50, Appendix J. Therefore, the basis for this accepted alternative was no longer valid. The subsequent failure to perform this test prior to establishing containment integrity created a condition that could have potentially allowed a containment leakage path to exist. A test of the containment personnel airlock was conducted on January 10, 1997, demonstrating that the airlock leakage rate was within the requirements of TS and 10 CFR 50, Appendix J. Procedures will be revised to specify that following opening of the containment airlock during periods when containment integrity is not required by the plant's TS, the airlock will be tested at the end of such periods in accordance with TS and 10 CFR 50, Appendix J. Expectations for Engineering personnel will be reinforced regarding the necessity for conducting a thorough review of the licensing basis when reviewing planned changes to plant systems and components. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(b) as a condition prohibited by the plant's TS.
2611997003 | Robinson 2 | 01/22/1997 | 02/21/1997 | 9702260380 | <strong>Condition Prohibited By Technical Specifications Due To Safeguards System Relay Replacement</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 22, 1997, the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 was operating at 100% power. A maintenance activity for replacement of a failed test relay in the Safeguards System required a jumper to be installed between the adjacent relays in the 'B' train of the Engineered Safety Function Actuation System (ESFAS). Since the jumper was not seismically qualified, credit could not be taken for operability of the 'B' train of ESFAS if a seismic event occurred during the relay replacement. A review of the HBRSEP seismic analysis concluded that the probability of a seismic event occurring during the period of time required for the repair was remote; however, if the jumper failed during the repair, the loss of a one train of some ESFAS functions may have occurred. Technical Specifications (TS) do not provide an action statement for inoperability of one train of ESFAS. Accordingly, TS Section 3.0, which requires the unit to be placed in hot shutdown within eight hours and in cold shutdown within the next thirty hours, was entered for the duration of the relay replacement work. This condition had negligible impact on plant safety. The relay replacement began at 1340 hours, and was completed at 1511 hours. TS Section 3.0 was exited accordingly. It should be noted that a TS change request which was previously submitted to the NRC to convert the current TS to the Improved Standard TS provides an action statement for one inoperable train of ESFAS. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
2611997005 | Robinson 2 | 04/22/1997 | 09/05/1997 | 9709170180 | <strong>Condition Outside Design Basis: Spent Fuel Shipping Cask Unreviewed Safety Question</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1997, with H. B. Robinson Steam Electric Plant (HBRSEP) 3 Unit No. 2, operating at 100% power, the results of an investigation revealed that certain spent fuel shipping cask handling activities had been conducted outside the design and licensing basis of the plant. Specifically, a IF-300 spent fuel shipping cask is configured for fuel loading by removing the cask valve box covers. The loaded cask is then lifted with a non single failure proof crane decontamination facility to the cask rail car, where the cask valve box covers are then installed. Lifting the cask with the non-single failure proof crane with the valve box covers removed is not covered by the shipping configuration drop analysis. An evaluation was completed that concludes this condition represents an unreviewed safety question. Accordingly, this report is being submitted in accordance with 10 CFR 50.73(a)(2)(ii) as a condition outside the design basis of the plant. There have been no significant adverse safety consequences associated with this condition. A postulated spent fuel shipping cask drop with the valve box covers removed could lead to an off-site release that exceeds the "no release" result of a cask drop specified in the licensing basis. However, results of the final evaluation, completed on July 14, 1997, concluded that the off-site doses resulting from a postulated cask drop with a less than fully ,secured cask are a small fraction of the 10 CFR 100 limits and the acceptance criteria in the Standard Review Plan. This condition was caused by inadequate evaluations for cask handling procedures. Personnel conducting these evaluations failed to identify the limitations of the drop analysis as it applied to cask handling operations, versus shipping configuration accident conditions. Procedures for spent fuel cask handling operations have been administratively placed on hold, pending resolution of this condition.
2611997006 | Robinson 2 | 05/21/1997 | 06/20/1997 | 9706260137 | <strong>CONDITION OUTSIDE DESIGN BASIS DUE TO DESIGN INSTALLATION ERROR: SAFETY INJECTION PUMP</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1997, with H. B. Robinson Steam Electric Plant, Unit No. 2 operating at 100% power, engineering personnel discovered that auto-start and manual start cables for Safety Injection (SI) Pump C were routed in the same cable tray stack as the auto-start cables for SI Pumps A, and B (when aligned in the safety Train A configuration), a condition outside of the design basis of the plant. A modification was implemented on May 25, 1997, that replaced the cables in new routes that achieved normal design basis separation. This condition was caused by an original plant design installation error. There have been no significant adverse safety consequences associated with this condition. The results of a review concluded that the cable routing error did not introduce a condition that had significant adverse safety consequences. A review of other SI pump cables was performed, and additional deviations to the redundant cable separation criteria that were identified were dispositioned. Current electrical installation practices provide conservative separation criteria that is based on the concepts of safety train separation. Additional emphasis will be placed on incorporating the review of electrical separation during appropriate engineering self-assessments. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i) as a condition that was outside the design basis of the plant.
2611997007 | Robinson 2 | 06/10/1997 | 04/16/1998 | 9804220111 | <strong>Condition Outside Design Basis Due To Inoperable Over Power Delta Temperature Channels</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1997, with the H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2 operating at 100% power, plant operators noted that the Reactor Protection System (RPS) Over Power Delta-Temperature (OPDT) channels were not responding properly, and at 1101 hours, declared the OPDT channels inoperable. The NRC Operations Center was notified of this condition at 1155 hours pursuant to 10 CFR 50.72(b)(1)(ii)(B). An investigation determined that the circuit for the OPDT summator in each of the three RPS loops was not properly calibrated. This event is attributed to inadequate programmatic controls which led to a personnel error. In 1979, personnel failed to specify the low limit setpoint for the summator on the data sheet used for the calibration. As a result, the OPDT channels were not calibrated using the proper setpoint. The safety significance of this event is minimal. Although the OPDT trip function is required by Technical Specifications, it is an additional trip which is available, and is not credited in the safety analyses. Procedure and calibration data sheet changes were implemented specifying the correct low limit setpoint, and the OPDT channels were re-calibrated and placed back in service on June 10, 1997. This event was reviewed by Maintenance Instrumentation and Control (I/C) craft personnel, Maintenance Unit I/C procedure writers, and Operations shift personnel. A review was performed to determine which summators in the RPS required high and low limits to be set, and calibration data sheets were reviewed and verified to ensure the limits are specified. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(ii) as a condition that was outside the design basis of the plant.
2611997008 | Robinson 2 | 06/27/1997 | 02/18/1998 | 9802240332 | <strong>Condition Outside Design Basis: Inadequate Safety Injection Pump Net Positive Suction Head</strong><br /><i>Abstract:&nbsp;</i>A review of calculations related to the available Net Positive Suction Head (NPSH) for the Safety Injection (SI) system determined that following a postulated large break Loss of Coolant Accident (LOCA), and assuming a single active failure of one SI pump, the remaining operating SI pump might not have sufficient NPSH under certain operating equipment configurations to respond to a design basis accident. The NRC Operations Center was notified of this condition on June 27, 1997, at 1152 hours. This condition was caused by personnel error. Personnel involved in a 1988 design change to the SI system did not adequately assess the impact of a single pump on SI system flow and pump NPSH requirements. Assuming a single failure, failure of the other SI pump could lead to increased fuel cladding temperatures and fuel damage during a LOCA, which could result in an increase in consequences beyond those considered in the current safety analysis. Therefore, during the period of inadequate available NPSH, the plant operated in a condition outside of the design basis. Modifications have been implemented to assure adequate NPSH is available to respond to a design basis event. ECCS flow modeling and calculations were completed on November 24, 1997, to document the capability of the ECCS system's pumps to perform their design functions. The SI system piping will be modified to gain additional NPSH margin during the next outage of sufficient duration, but prior to startup from Refueling Outage 18. Assessments of other systems will be conducted and will include evaluation of system modifications and related design calculations for potential inadequacies.
2611997009 | Robinson 2 | 07/02/1997 | 08/01/1997 | 9708060130 | <strong>Technical Specification Violation Due To Inadequate Surveillance Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1997, during a self-assessment, plant engineering personnel discovered that existing procedures for periodic testing of containment isolation valve leakage was not adequate because a proper vent path to measure leakage from the valves had not been established. A second valve subject to this condition was discovered on July 3, 1997. Valve RC-553 was declared inoperable at 0948 hours on July 2, 1997, and valve WD-1794 was declared inoperable at 1435 hours on July 3, 1997. The Technical Specifications (TS) action statement for inoperable containment isolation valves was entered, and the affected containment penetrations were isolated. A proper vent path for each valve was established, and a leakage test was subsequently performed. The test results concluded that the leakage rates for the valves were within specified acceptance criteria. This condition was caused by personnel error. Previous reviews of procedures failed to identify the proper vent path for these containment isolation valves. An assessment of the containment isolation valve leakage rate testing program was conducted, and no similar testing deficiencies were identified. This condition did not have a significant impact on plant safety, since subsequent testing confirmed that the leakage rates for the valves were within their acceptance limits. Therefore, these valves would have performed their safety function if an event where maintaining containment integrity would be required had occurred. Procedures will be revised to establish the proper testing configuration by October 15, 1997. Training will be conducted by October 15, 1997, to emphasize the need to conduct adequate technical reviews of procedure changes.
2611997010 | Robinson 2 | 08/20/1997 | 09/15/1997 | 9709190182 | <strong>Emergency Diesel Generator Inoperability Due To Mispositioned Output Breaker Control Switch</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1997, at approximately 1544 hours, plant operations personnel determined that the output breaker control switch for the "B" Emergency Diesel Generator (EDG-B) was in the tripped position. In the tripped position, the breaker would not be able to supply power to the associated emergency bus. The switch was immediately returned to the neutral position. During the time the EDG-B was considered inoperable, certain equipment in its redundant train did not meet the TS definition of OPERABILITY, a condition prohibited by TS. Operations personnel applied Technical Specifications (TS) Section 3.0 to this condition, which requires the plant to be placed in hot shutdown within eight hours and in cold shutdown within the next 30 hours. This condition also represents a condition that was outside the design basis of the plant. The NRC Operations Center was notified of this condition on August 20, 1997, at 1634 hours. Investigation of this event could not determine the specific cause of the switch mispositioning. A check of other selected switches in the plant was performed to verify they were in the correct position and to detect other evidence of tampering. A review of other switches outside the control room that could disable safety significant equipment without giving indication or annunciation in the control room will be completed, and a method will be provided for protecting and periodically checking the positions of these switches. Training will be provided to plant personnel on the switches outside the control room that could disable safety significant equipment without giving indication or annunciation in the control room. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition that was outside the design basis of the plant, and 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS.
2611997011 | Robinson 2 | 11/16/1997 | 09/23/1998 | 9809290052 | <strong>Reactor Trip Due to Condensate Pump "B" Shaft Failure</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1997, at 0133 hours, with H. B. Robinson Steam Electric Plant, Unit No. 2 at one hundred percent (100%) power, an automatic actuation of the Reactor Protection System (RPS) occurred causing an automatic reactor trip. The RPS actuation resulted from "C" Steam Generator (SG) low level coincident with feedwater flow less than steam flow. The cause of the reactor trip was reduced feedwater flow to the SG following the failure of the "B" condensate pump stub shaft. The unit was stabilized in MODE 3 using the Emergency Operating Procedures. The NRC Operations Center was notified of this event at 0353 hours on November 16, 1997, in accordance with 10 CFR 50.72(b)(2)(ii). Plant equipment operated as designed with the exception of the intermediate range neutron monitoring system, channel N-35, which prevented the source range neutron monitoring channels from automatically reenergizing and providing indication. A previous similar event occurred in 1991 when the "B" condensate pump stub shaft failed causing a reactor trip that was reported in LER 91-11. An investigation into the event reported in this LER has determined that the cause of the shaft failure was similar to the 1991 event. The cause of this event has been determined to be failure to adequately complete the corrective actions from the 1991 event. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in an automatic actuation of the reactor protection system.
2631997002 | Monticello | 01/16/1997 | 02/13/1997 | 9702190322 | <strong>No Licensed Senior Operator in the Control Room/Shift Supervisor's Office</strong><br /><i>Abstract:&nbsp;</i>While at 100% power, neither the duty shift manager nor the duty shift supervisor were present in the control room/shift supervisors office for approximately 10 seconds, The shift manager got too involved in responding to a question and forgot that the shift supervisor had left the control room/shift supervisors office. Soon after exiting the control room/shift supervisors office, the shift manager met the shift supervisor. They both immediately realized that there was no licensed senior operator in the control room/shift supervisors office. The shift supervisor and the shift manager returned to the control room/shift supervisors office. The operations supervisor discussed the event with the shift manager involved. An administrative system to help remind the shift supervisors and managers of this requirement is being evaluated.
2631997003 | Monticello | 01/28/1997 | 02/25/1997 | 9703040110 | <strong>Piping Between Double Containment Isolation Valves Could be Stressed Greater Than Code Allowables During Certain Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>During the assessment of Generic Letter 96-006, it was determined that during certain accidents several primary containment penetrations could exceed the allowable stresses specified in the Updated Safety Analysis Report. These design errors were made by the original architect engineer and not identified by subsequent plant reviews. Installation of a permanent pressure relieving device will be pursued for these penetrations.
2631997004 | Monticello | 02/20/1997 | 03/24/1997 | 9704010581 | <strong>Failure to Submit Relief Requests for Limited Inservice Inspection Examinations</strong><br /><i>Abstract:&nbsp;</i>Relief requests have not been submitted for limited inservice inspection examinations per the requirements of 10 CFR Part 50. In the past, inservice examinations have been done to the extent practical. 10 CFR Part 50, Section 50.55a(g) states for plants with construction permits prior to 1971 that examinations need to be performed "to the extent practical". Since Monticello's construction permit was dated prior to January 1, 1971, no relief requests were submitted if component design, geometry or materials of construction limited an examination. 10 CFR Part 50, Section 50-55a(g) had been miss-interpreted. Required relief requests will be submitted for all limited examinations that have been performed in the 3rd Ten Year Inservice Inspection Interval. Required relief requests will be submitted for all limited examinations performed in the future
2631997005 | Monticello | 04/08/1997 | 05/05/1997 | 9705120172 | <strong>Failure to Analyze Diesel Fuel Samples within the Technical Specification Required Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>A system engineer discovered that the monthly analysis of the diesel fuel was not being performed within the required time. Samples were taken monthly as required. Samples were then sent off site for analysis. The analysis results were returned to the system engineer regularly, in approximately 3 weeks. Surveillances are required to be completed within +/- 25% of the surveillance interval specified in the Technical Specifications. No time requirement had been associated with receiving and reviewing the sample analyses. The operability of the emergency diesel generators was never affected by this time delay, as all analyzed samples were acceptable. The surveillance procedure will be changed to specify the review of the required analysis results prior to the surveillance being considered complete.
2631997006 | Monticello | 04/08/1997 | 05/08/1997 | 9705150105 | <strong>Emergency Diesel Generators Started By Personnel Error During a Monthly Surveillance</strong><br /><i>Abstract:&nbsp;</i>Electrical maintenance personnel were performing the Monthly Degraded Safeguards Bus Voltage surveillance, when both Emergency Diesel Generators unexpectedly received a fast start signal and started. The control logic proceeded to transfer essential Bus 15 to the 11 Emergency Diesel Generator. Electrical maintenance personnel had been using a hand held meter to measure continuity. This meter acted as a jumper, causing the Emergency Diesel Generators to start and load the 11 Emergency Diesel Generator. The procedure has been modified.
2631997007 | Monticello | 04/15/1997 | 05/15/1997 | 9705210396 | <strong>Inadequate NPSH for the ECCS Pumps For Certain Single Failures During Loss of Coolant Events</strong><br /><i>Abstract:&nbsp;</i>After reviewing an LER from Quad Cities Nuclear Station, it was discovered that the net positive suction head available for the core spray pumps was less than required. Two issues were identified: increased head losses associated with the ECCS suction strainers and a more limiting net positive suction head case. These issues were determined to be applicable to Monticello. An operability evaluation determined that the pumps were still operable. Following evaluation of an additional issue, debris generation from the drywell piping insulation during post design basis loss of coolant accident conditions, the prudency of continued operations was questionable and the plant was brought to cold shutdown. The plant will remain there until new ECCS suction strainers are installed.
2631997008 | Monticello | 04/18/1997 | 05/19/1997 | 9705290023 | <strong>Inappropriate Use of the 25% Tolerance for Periodic Actions in Section 3 of the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>The performance of some periodic actions required by the Technical Specifications were in excess of that allowed by the Technical Specifications. A Technical Specification Interpretation had been written allowing a 25% tolerance on periodic actions required by Section 3 of the Technical Specifications. This was a logical extension of the application of the 25% tolerance allowed in Section 4, but a license amendment should have been requested. The Technical Specification Interpretation has been deleted and procedures changed. Personnel involved are aware of the error.
2631997009 | Monticello | 07/01/1997 | 07/23/1997 | 9708010020 | <strong>Partial Primary Containment Isolation Due to Voltage Transient During Severe Weather</strong><br /><i>Abstract:&nbsp;</i>During severe weather, a fault occurred on one of the 345 kV transmission lines coming into the Monticello substation. The plant electrical system experienced a voltage drop, causing the Reactor Protection System relays on one division to de-energize and re-energize. The momentary dropout of the Division "A" logic initiated the following actions: a half scram, a partial containment isolation (Partial Group II Isolation), a Reactor Building isolation, and the control room ventilation switched to the high radiation mode. Division "B" relays were not affected. Systems were restored to the conditions that existed prior to the event. The damaged 345 kV line is being repaired.
2631997010 | Monticello | 09/16/1997 | 10/16/1997 | 9710240095 | <strong>Failure to Include Some Support on the Reactor Head Line in the ISI Program in the 2nd 10 Year Interval Due to Inaccurate Drawings and Failure to Report This Event in a Timely Manner Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Seven piping supports on the Reactor Head Vent line were not included in the Inservice Inspection Program. The piping supports were not documented on the controlled drawings used to develop the Inservice Inspection Program. The omission of these supports in the Inservice Inspection program was not identified as a reportable item in a timely manner. The piping supports were inspected per the requirements of the ASME Section XI code and added to the Inservice Inspection program. The controlled drawings will be modified to include the supports. Piping covered by the Inservice Inspection Program and not evaluated in the response to NRC Bulletin 79-14 will be reviewed to ensure that all pipe supports are included in the Inservice Inspection program and are documented on controlled drawings. The personnel involved in the failure to report this event have been counseled on the importance of timely and accurate reportability determinations.
2631997011 | Monticello | 09/08/1997 | 10/16/1997 | 9710240109 | <strong>Error in Procedure Causes Failure to Transfer the HPCI and RCIC Suctions to the Suppression Pool After Making a Condensate Storage Tank Level Instrument Inoperable</strong><br /><i>Abstract:&nbsp;</i>Due to an error in a procedure used to remove a Condensate Storage Tank from service, the suction for HPCI (High Pressure Coolant Injection) and RCIC (Reactor Core Isolation Cooling) were not transferred from the Condensate Storage Tank to the suppression pool during maintenance on the Condensate Storage Tanks. Maintenance was planned to repair minor degradation of the Condensate Storage Tanks' internal coating. There are two Condensate Storage Tanks, #11 and #12. Each tank has a level column with one low level switch. Either switch sensing low level will transfer the suction of HPCI and RCIC from the Condensate Storage Tank to the suppression pool. Prior to coating replacement, a procedure was used to remove a Condensate Storage Tank from service which conflicted with the requirements of the Technical Specifications. This procedure directed operations personnel to make the level switch, associated with the tank to be recoated, inoperable. Under these conditions, the Technical Specifications require that the HPCI and RCIC suctions be transferred to the suppression pool. The procedure was in error as it did not direct operators to transfer the suctions to the suppression pool. The cause of the error in the procedure was improper implementation of a change to the Technical Specifications in 1986. The suctions for HPCI and RCIC were promptly aligned to the suppression pool upon discovery of the non-compliance with Technical Specifications. A temporary change was made to correct the procedural error. A permanent change will be made in the future. Other procedures involving the Condensate Storage Tank will be reviewed for similar errors. Improvements to the process for reviewing changes to the Technical Specifications will be considered.
2631997012 | Monticello | 09/26/1997 | 10/27/1998 | 9711040042 | <strong>Condensate Storage Tank Low Level Suction Transfer Setpoint Did Not Provide Sufficient Submergence As the Result of a Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>The Condensate Storage Tank low level setpoint was discovered to be inadequate since excessive air entrainment in the suction piping caused by vortexing could occur prior the HPCI and RCIC suctions transferring from the Condensate Storage Tanks to the suppression pool. Regulatory Guide 1.82, "Water Sources for Long-Term Recirculation Cooling following a Loss-of-Coolant-Accident", was conservatively used as a reference to determine the Condensate Storage Tank level required to prevent excessive air entrainment. The cause of this event is a design deficiency in the original Condensate Storage Tank low level setpoint. Level setpoints corresponding to higher tank levels have been determined and the level switches have been adjusted accordingly. A review of other suction sources for safety related pumps will be performed to assure that the effect of vortexing is properly addressed.
2631997013 | Monticello | 11/25/1997 | 12/22/1997 | 9801060259 | <strong>Manual Scram Inserted Due to Loss of Condenser Vacuum Caused by Electrical Fault Tripping Recombiners</strong><br /><i>Abstract:&nbsp;</i>Control room operators received alarms from the tripping of two 480V load center breakers. Each breaker fed one division of the Offgas Recombiners and the Offgas Compressors plus associated equipment. Loss of the Condenser Offgas System, specifically the recombiners, caused condenser vacuum to decrease. Control Room operators decreased reactor power to reduce the rate of loss of condenser vacuum. Engineering and operations personnel determined that the breakers had tripped on short circuit. Since it would not be possible to re-energize the offgas recombiners, condenser vacuum would continue to decrease. Control room operators conservatively manually scrammed the reactor (inserting the control rods). A cross-divisional cable fault caused the two 480V load center breakers to trip. Temporary cables were installed primarily above ground. The temporary cables feeding the Offgas Storage Building will be replaced with permanent underground cables. An evaluation of the action necessary to ensure the proper functioning of existing plant underground cables will be conducted.
2631997014 | Monticello | 12/19/1997 | 01/12/1998 | 9801220238 | <strong>Division II ADS Inhibit Switch Was Not Tested as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>A missed Technical Specification surveillance was discovered by a system engineer while addressing Generic Letter 96-01 (Testing of Safety-related Logic Circuits). During review of logic circuit surveillance tests, it was determined that the Division II ADS (Automatic Depressurization System) Inhibit Switch was not being tested. Technical Specification 4.5.A.4 requires that "ADS Inhibit Switch Operability" be performed "each operating cycle." Following issuance of the License Amendment which added this requirement, an existing surveillance test was changed to verify the operability of the switches. However, the change only tested the Division I ADS Inhibit Switch. This was a cognitive error by the preparer and the reviewer of the surveillance test. Following discovery of this problem, a temporary change was made to the surveillance test to verify the operability of the Division II ADS Inhibit Switch. A surveillance procedure will be written or revised to verify operability of the Division II ADS Inhibit Switch. Completion of the Generic Letter 96-01 logic testing reviews will identify any additional logic testing inadequacies.
2651997001 | Quad Cities 2 | 02/27/1997 | 07/17/1997 | 9707230128 | <strong>Instrument Maintenance Surveillance Caused HPCI Initiation Due To A Deficient Procedure.</strong><br /><i>Abstract:&nbsp;</i>At 0242 hours on 022797, with Unit Two in Mode One at approximately 95% power, the Instrument Maintenance (IM) Department was performing Quad Cities Instrument Maintenance Procedure (QCIPM) 0100-10 to test the High Pressure Coolant Injection (HPCI) initiation logic. During performance of the surveillance, the requirements for the HPCI logic initiation system were satisfied and HPCI initiated as designed. Control Room operators verified that the HPCI initiation was not required and tripped the turbine. The procedure directing this evolution did not include all prerequisite conditions and provided a false sense of security that it could be performed with HPCI operable. The root cause of this event was poor work practices (cognitive error) during the 1993 procedure rewrite project for conversion of existing procedures into a new format. The procedure writer and reviewer knew that the unit needed to be in the shutdown or refuel mode and included the words "Refuel Outage" in the title of the procedure. They did not include this information in the procedure's prerequisites section or impact statement. Additionally, there is a fundamental misunderstanding by first line supervisors in charge of work. They do not all realize that they must use some reference other than the procedure to validate that each action performed will provide the expected response. Corrective actions include revising the surveillance procedure, review the prerequisites of all IM procedures, communicate management's expectations for work supervisors to review additional references, and for procedure writers to include 10CFR50.59 safety screening/evaluation restrictions in procedure prerequisites. This LER is being supplemented to report the failure to comply with Technical Specification administrative Action Statement 3.5.7, submitting a Special 90 Day Report following the subject HPCI injection. The safety consequences of this event were minimal. There was no impact on Control Room personnel or the health and safety of the public.
2651997002 | Quad Cities 2 | 02/28/1997 | 11/18/1997 | 9712020147 | <strong>Unit 2 was shutdown, per the requirements of technical Specifications 3.5.A, and 3.6.F, because four Main Steam Relief Valve closure times did not meet Inservice Testing Program limits.</strong><br /><i>Abstract:&nbsp;</i>At 0500 on 022897, Unit Two was in Mode One at approximately 98% power and testing was being conducted in accordance with QCOS 0203-03, Main Steam Relief Valves Operability Test. During the testing, four Power Operated Relief Valves (PORVs) did not close within the limits specified by the Inservice Testing (IST) Program. All four valves were declared inoperable. At 0900 on 022897, a Unit 2 shutdown was initiated in accordance with the requirements of Technical Specifications (TS) 3.5.A and 3.6.F. At 0735 on 030197, the reactor was placed in Mode 4, COLD SHUTDOWN. Subsequent investigation determined that the IST baseline data and associated acceptance criteria had not been reevaluated when the method used to time the PORVs was revised. Evaluation of the PORV closing times utilizing the method originally used to establish the acceptance limits determined that the valve closure times were acceptable. The root cause of the event was the failure to recognize the impact that changing the timing methodology had on the IST acceptance criteria. The IST acceptance limits for these valves will be revised based on data obtained by the current valve timing methodology. This event did not adversely impact the health and safety of onsite personnel or the public. In addition, On 022897 Operations created a short term containment parallel vent path while Unit 2 was in Mode I when de-inerting the suppression chamber while the drywell vent valves remained open contrary to TS 3.7.K.3. The Unit 2 shutdown was also required by the primary containment integrity action statement.
2651997003 | Quad Cities 2 | 03/21/1997 | 01/20/1998 | 9802050214 | <strong>2B Core Spray Room Cooler Fouled Due To Hydrolyzing Debris</strong><br /><i>Abstract:&nbsp;</i>On 032197, significant fouling was discovered in the 2B Core Spray Room Cooler (CSRC) during the pre-cleaning inspection. This condition may have existed from June 1996. Recent modeling of the 2B Core Spray Room Coolers fouling condition determined that the room cooler flow would be calculated at 42.5 gpm. This flow is above the minimum design flow of 30 gpm. With this information, it can now be concluded that the 2B CSRC was operable from June 1996 until the refueling outage Q2R14. The apparent cause of the event was a failure to properly trend and analyze differential pressure and identify clogging of the 2B CSRC. Debris stirred up by hydrolyzing performed during Q2R13 on the EDG Cooling Water System was the source of the clog. Corrective actions completed include cleaning of the 2B CSRC and the other Unit 2 Emergency Core Cooling System (ECCS) Room Coolers. Unit 1 Room Coolers were cleaned less than a year ago. A new procedure will address future trending and analysis of room cooler dP and flow data. There were no safety consequences and no risk to Control Room personnel nor the health and safety of the public. This LER is being reported voluntarily. LER265\97\003R2.WPF
2651997004 | Quad Cities 2 | 05/09/1997 | 05/29/1997 | 9706100223 | <strong>Drywell Equipment Drain Sump and the Drywell Floor Drain Sump covers were constructed not in accordance with design drawings, due to an original construction error</strong><br /><i>Abstract:&nbsp;</i>Quad Cities Nuclear Station Unit Two was shutdown for refueling with no fuel in the reactor at the time of discovery for this event. Chemistry personnel were sampling the drywell sumps when they noticed that the sump covers appeared to be opposite to what they were expecting. Investigation proved that the Drywell Equipment Drain Sump and the Drywell Floor Drain Sump cover were not constructed per design drawings. This sump cover problem affects the accurate measurement of the Technical Specification for primary containment leakage. The plant was shutdown at the time of this event and there was no immediate consequences. The drywell sump covers construction error had no impact on the current operation of this or any other system. The apparent cause of this event was an error during plant construction. The actual root cause is unknown. The short term response to this event was to modify the Unit Two sump covers so that they now can meet Technical Specifications and to verify Unit One's sump covers by viewing them on video tape. The long term response is to visually verify the Unit One sump covers are installed as per design during the next refueling outage. There was no impact on health/safety of on-site personnel or to the public. The effect of wrong sump covers on identification of reactor coolant leakage was minimal.
2661997003 | Point Beach 1, Point Beach 2 | 01/09/1997 | 02/06/1997 | 9702110457 | <strong>Spare Containment Penetrations Not Leak Tested In Accordance With Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1997, while Point Beach Nuclear Plant (PBNP), Unit 1 was operating at 90 percent power and Unit 2 was shut down during its annual refueling outage, plant personnel determined that two containment penetrations (per unit) were not being tested in accordance with plant Technical Specifications. Evaluation of a September 16, 1996, Quality Assurance audit finding determined that Penetrations P-12B (both units) and P-30a (both units) made use of bolted flanges inside containment and isolation valves outside containment but were not Type B or C leak tested in accordance with 10 CFR 50, Appendix J. This failure to test penetrations P-12b and P-30a violated Technical Specifications Section 15.4.4, "Containment Tests," which required leak testing for all containment penetrations employing resilient seals, gaskets, or sealant compounds. These penetrations were subsequently tested with satisfactory results.
2661997004 | Point Beach 1, Point Beach 2 | 01/13/1997 | 02/12/1997 | 9702190327 | <strong>Potential Common Mode Failure In Vital DC Electrical System</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1997, with Unit 1 operating at 90% power and Unit 2 in a refueling shutdown condition, licensee engineers discovered the potential for a particular common mode failure in the Vital DC Electrical (VDC) System that could affect opposite trains of Unit 2 safeguards equipment. This flaw stems from the unreliability of VDC molded case circuit breakers (MCCBs) to trip in the magnetic-trip region and the lack of physical separation provided for non-safety-related circuits powered from VDC panels. For one postulated fault between two insulated conductors (fed from different VDC power panels), the calculated short circuit current exceeded the maximum operating limit of the thermal trip elements in the associated MCCBs. This would cause the associated upstream fuses to blow and deenergize opposite-train VDC panels; thereby disabling opposite-train safeguards equipment. The coincidental loss of opposite-train safeguards equipment is not analyzed in the FSAR. Subsequently, a similar common mode failure was identified for Unit 1. In each case, a non-safety related circuit was deenergized to isolate the potential fault.
2661997005 | Point Beach 1 | 01/16/1997 | 02/14/1997 | 9702260207 | <strong>1SI-852A Not Tested In Accordance With Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1997, while Point Beach Nuclear Plant (PBNP), Unit 1 was operating at 90 percent power, plant personnel determined that core deluge Valve 1SI-852A had not been tested in accordance with the Inservice Test Program as required by Technical Specification 15.4.5.II.A.1. Also since the valve was not stroke tested within 24 hours as stated in Specification 15.4.0.3 due to extended test preparation time, we were subsequently required to enter Specification 15.3.3.A.3.c. Specification 15.3.3.A.3.c allows any valve in the safety injection and residual heat removal systems, which is required to function during accident conditions, to be inoperable for up to 72 hours before placing the reactor in the hot shutdown condition. Valve 1SI-852A was stroke tested on January 17, 1997, and verified to be operable.
2661997006 | Point Beach 1, Point Beach 2 | 01/20/1997 | 02/19/1997 | 9702250235 | <strong>Potential Refueling Cavity Drain Failure Could Affect Accident Mitigation</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1997, with Unit 1 operating at 90% power and Unit 2 in a refueling shutdown condition, licensee engineers discovered a plant condition that could cause retention of a significant water inventory in the refueling cavity during a design basis loss of coolant accident (LOCA); thereby diverting water that is assumed to accumulate in the containment sump. The condition was discovered during review of 1983 modifications which installed a flapper valve and remote cable operator over the refueling cavity drain for Unit 1 and Unit 2. The modifications also removed the original cavity drain grate in each unit and reduced the size of the drain line to a 2-inch nozzle. The design was not evaluated for seismic considerations or the effects on the containment sump level. If the drain failed during a LOCA, as much as 46,000 gallons could be retained in the refueling cavity, which would invalidate the assumptions in the design basis accident analysis. To accommodate the potential loss of this sump water inventory, the emergency operating procedures were revised to ensure that a greater amount of water is transferred from refueling water storage tank to the containment during the LOCA recovery.
2661997007 | Point Beach 1, Point Beach 2 | 01/24/1997 | 02/21/1997 | 9702270242 | <strong>Potential Emergency Diesel Generator Overload Condition</strong><br /><i>Abstract:&nbsp;</i>On January 24, 1997, Point Beach Nuclear Plant (PBNP), Unit 1, was operating at 90 percent power and Unit 2 was shut down and defueled during its annual refueling outage. During evaluation of procedure reviews for performing high-head safety injection (HHSI) system fill and venting, plant personnel determined that the potential existed for an emergency diesel generator (EDG) overload condition. When one EDG is aligned to supply the safeguards buses for both units and a HHSI pump is operated on one unit, an opposite unit safety injection actuation and a total loss of off-site power would result in the starting of the opposite unit's HHSI pump. This would result in two HHSI pumps being powered by one EDG, which is outside the design basis of the plant and creates the potential for a EDG overload condition. Procedure changes are being implemented to prevent EDG overload when testing HHSI pumps when a EDG is being shared between units. A Unit 1 one-hour report and a Unit 2 four-hour report was provided to the NRC in accordance with 10 CFR 50.72. The NRC resident inspectors were also notified.
2661997008 | Point Beach 1, Point Beach 2 | 01/31/1997 | 03/03/1997 | 9703100017 | <strong>Non-Seismic Ductwork Located Above Safety-Related Equipment In Containment</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1997, with Unit 1 operating at 90% power and Unit 2 in a refueling shutdown condition, licensee engineers discovered a plant condition that could affect the operability of safety-related equipment inside the steam generator (SG) cubicles of containment. During a routine walkdown of Unit 2 containment, licensee engineers noted that SG channelhead ductwork located in the steam generator cubicles appeared to have insufficient support. Based on the general similarity of Unit 1 and Unit 2 designs, it was assumed that the Unit 1 configuration could also be inadequate. Unit 1 reactor power was reduced to three percent to allow access to the SG cubicles for inspection. The inspection indicated that the ductwork in the SG cubicles did not appear to be seismically supported in Unit 1. During the Unit 1 containment entry, some of the suspect ductwork was removed and the remaining ductwork was seismically restrained with a temporary modification. Seismic analyses are planned for Unit 1 and Unit 2. If necessary, modifications will be made to install supports or remove the ductwork such that the design and design documentation are restored to full compliance.
2661997009 | Point Beach 1, Point Beach 2 | 02/14/1997 | 03/17/1997 | 9703250061 | <strong>Potential for Safety Injection Failure During Filling of a Safety Injection Accumulator</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1997, with Unit 1 operating at 90% power and Unit 2 in a defueled condition, licensee engineers discovered a plant condition that could cause a potential for safety injection failure during filling of a safety injection accumulator. Condition report 97-0517 documents the discovery that the emergency core cooling system analysis does not include the effect of an open safety injection (SI) system accumulator fill valve. This condition could cause diversion of flow from the high head safety injection pump being used to fill the accumulator from the reactor coolant system into the accumulator that is being filled. The cause of this condition is considered to be due to a situation that was not adequately covered by the procedure. The procedure used for filling a safety injection accumulator has been changed to preclude the use of the Train B SI pump for filling an accumulator and to enter the applicable limiting condition for operation (LCO) for inoperability of the Train A SI pump while it is being used to fill any accumulator.
2661997011 | Point Beach 1, Point Beach 2 | 03/05/1997 | 04/03/1997 | 9704080339 | <strong>Containment Fan Cooler Accident Fans Not Tested In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a hot standby condition and Unit 2 was shut down during its annual refueling outage, plant personnel determined that the containment fan cooler accident fans were not being tested in accordance with plant Technical Specifications. During a review of administrative controls implementing Technical Specifications, it was identified that plant procedures may not adequately implement Specification 15.4.5.I.C.2, which requires containment fan cooler accident fans to be tested monthly to verify that the fans start and the running current is acceptable. Plant procedures only start fans that are not already running - fans that are already running are not stopped and then restarted. It was subsequently determined that this was a violation of Technical Specification 1.4.5.I.C.2. The fans were tested on March 5, 1997, and verified operable.
2661997012 | Point Beach 1, Point Beach 2 | 03/04/1997 | 04/02/1997 | 9704080391 | <strong>Diesel-Driven Fire Pump Day Tank Not Sampled In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1997, with Unit 1 in a hot standby condition (approximately 380 Degrees F, 1000 psig) and Unit 2 in a refueling shutdown condition, a licensee engineer discovered that a Technical Specification (TS) surveillance had not been routinely conducted. TS 15.4.15.A.1.d.2 requires a quarterly sample analysis of the diesel fuel for the diesel-driven fire pump (P-35B) engine. The programmatic review found that the TS test procedure (TS-80) for sampling fuel tanks did not include a requirement to sample diesel fuel day tank (T-30) for the diesel-driven fire pump (P-35B) engine. Within 2 hours of discovering this condition, the day tank was sampled and later, shipped for analysis. The appropriate TS action was taken for the missed surveillance. When the analysis results were not received within 24 hours, pump P-35B was declared out-of-service and the appropriate TS action was taken to test the other pump (P-35A). A requirement to sample day tank T-30 on a quarterly frequency is being added to test procedure TS-80.
2661997013 | Point Beach 1, Point Beach 2 | 03/04/1997 | 05/30/1997 | 9706050243 | <strong>Component Cooling Water System Not in Accordance With Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a hot standby condition and Unit 2 was shut down during its annual refueling outage, component cooling water (CCW) pump discharge cross-connect Valve CC-722B failed to open during valve manipulation tests. As a result, this valve was declared inoperable. PBNP FSAR Section 9.3 states that a cross-tie may be opened under abnormal conditions to allow unit-designated CCW pump(s) to supply the opposite unit. Since this cross-tie feature was not available due to the inoperability of Valve CC-722B, the plant was in a condition outside its design basis. An operability determination concluded that the Unit 1 CCW system was operable. A 4-hour report to the NRC was made under 10 CFR 50.72. The NRC resident inspectors were also notified.
2661997014 | Point Beach 1, Point Beach 2 | 03/21/1997 | 04/18/1997 | ML03087023 | <strong>Auxiliary Feedwater System Inoperability Due To Loss of Instrument Air</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1997, with Unit 1 in cold shutdown and Unit 2 in a defueled condition, licensee engineers discovered a condition that alone could have prevented the Auxiliary Feedwater (AFW) System from automatically performing its safety-related function during design basis accidents involving a loss of instrument air and reduced steam generator pressures. A loss of instrument air during the accident would cause both motor-driven AFW pump (MDAFWP) flow control valves to fail open. Without automatic flow control, the MDAFWPs' flowrate would be determined by steam generator pressure. If steam generator pressure is below the relief valve setpoints, which may occur for a low decay heat history, the pump motor breakers could trip on time-overcurrent. After discovery of these conditions, the AFW System was declared inoperable and the design was evaluated. The existing plant conditions did not require operability of the AFW system. The AFW system will be restored to operable status prior to establishing conditions that would require the system to be operable. The potential loss of both MDAFWPs during certain accidents has been attributed to a latent design characteristic of the original design of the AFW system.
2661997015 | Point Beach 1, Point Beach 2 | 03/24/1997 | 04/23/1997 | 9704290259 | <strong>Control Room Ventilation System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1997, with Unit 1 in cold shutdown and Unit 2 in a defueled condition, during inspection and repair of the control room ventilation system, a condition was discovered that could have prevented proper operation of the control room ventilation system. After discovery of these conditions, the control room ventilation system was declared inoperable and repairs were initiated. The existing plant conditions did not require operability of the control room ventilation system. It is expected that the control room ventilation system will be restored to operable status prior to establishing the conditions that would require the system to be operable. The failures of the backdraft damper and the vent duct access door have been attributed to original installation of the control room ventilation system. It has been judged that the control room dose consequences of these failures could have been mitigated. Offsite dose consequences were unaffected.
2661997016 | Point Beach 1, Point Beach 2 | 03/25/1997 | 04/24/1997 | 9704290158 | <strong>Steam Generator Level Logic Not Tested In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1997, Point Beach Nuclear Plant (PBNP) Unit 1 was in a hot standby condition and Unit 2 was shut down during its annual refueling outage. During a review of plant Technical Specifications (TS), plant engineers determined that the low-low steam generator level logic tests for both reactor trip and auxiliary feedwater (AFW) actuation were deferred as allowed by plant TS when the unit was in refueling shutdown and not performed until the plant was in a hot shutdown condition (Tavg>540F), contrary to TS 15.3.4.A.2 and its associated Limiting Condition for Operation (LCO). Technical Specification 15.3.4.A.2 requires essential AFW instrumentation to be operable when the reactor coolant system is heated above 350F. Specification 15.3.4.A.2 is more restrictive than TS Table 15.4.1-1, Item 8, which allows channel functional tests during refueling shutdown to be deferred until prior to reactor criticality. Applicable procedures will be revised to perform the required testing to ensure operability prior to exceeding 350F. The NRC resident inspectors were notified of this event.
2661997017 | Point Beach 1 | 05/08/1992 | 05/01/1997 | 9705070170 | <strong>Containment Third Door Blocked Open During Refueling Operations</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1997, during a review of condition reports relating to potential Technical specifications violations, it was discovered that a condition report was initiated on May 9, 1992, that described an event which had been screened as not being a Technical Specification violation. Accordingly, no 30-day licensee event report was submitted to the NRC. On on May 8, 1992, immediately following installation of the Unit 1 reactor vessel upper internals package, it was discovered that ramps used to transport equipment into and out of the containment blocked open the temporary third door on the upper personnel containment access. TS 15.3.8.1 requires that, "....a temporary third door on the outside of the personnel lock shall be in place whenever both doors in a personnel lock are open."
2661997018 | Point Beach 1, Point Beach 2 | 04/03/1997 | 05/05/1997 | 9705120341 | <strong>Potential Residual Heat Removal System Overpressure During Accidents</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1997, with Unit 1 in cold shutdown and Unit 2 in a defueled condition, licensee engineers discovered a potential for a section of the Residual Heat Removal (RHR) System inside containment to overpressurize during a design basis accident. The piping section is isolated by normally-closed RHR inlet isolation valves (RH-700 and RH-701), and is normally water-filled, but is not provided with relief valve protection. During a design basis accident which elevates containment temperature, the trapped fluid would be heated by the containment accident environment and could pressurize the isolated section. If unmitigated, the overpressure condition could lead to pipe rupture or valve damage, which would affect the capability of the RHR System to achieve and maintain cold shutdown if required later In the accident. This condition is a latent characteristic of the original RHR System design and is generic to both nuclear units. Prior to the startup of a nuclear unit, appropriate overpressure protection will be provided to that unit.
2661997019 | Point Beach 1, Point Beach 2 | 04/04/1997 | 05/02/1997 | 9705070094 | <strong>Residual Heat Removal Not Aligned In Accordance With Technical Specifications Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1997, Point Beach Nuclear Plant (PBNP) Unit 1 was in cold shutdown and Unit 2 was shut down during its annual refueling outage. During a review of NRC Inspection Report IR 96018, it was determined that PBNP had been operated during past refueling shutdown conditions with neither RHR normal decay heat removal loops in an operable status. Normal RHR decay heat removal takes suction from the 'A' RCS loop hot leg and returns to the 'B' RCS loop cold leg. However, during several occurrences, the RHR return was aligned to core deluge, potentially bypassing the reactor core. In the future, this method of utilizing the core deluge RHR line-up will be used only during conditions in which RHR is not required to be operable, or a Technical Specifications Change Request (TSCR) will be submitted to allow this line-up when RHR is required to be operable. A four-hour report was provided to the NRC in accordance with 10 CFR 50.72(b)(2)(i). The NRC resident inspectors were also notified of this event.
2661997021 | Point Beach 1, Point Beach 2 | 04/30/1997 | 05/30/1997 | 9706050221 | <strong>Spent Fuel Pool Cooling System Not In Accordance With Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in cold shutdown and Unit 2 was shut down and defueled during its ongoing refueling outage, two interfaces between seismic Class I and seismic Class II/III piping in the spent fuel pool cooling system were identified as being accomplished via normally open manual valves. This is contrary to the PBNP Final Safety Analysis Report (FSAR), Appendix A, which requires interfaces between Class I systems and lower class systems to be at a normally closed valve or a valve which is capable of remote operation from the control room. Since these manual boundary valves were maintained in the open position, the plant was in a condition outside its design basis. The valves were immediately closed and tagged shut. An operability determination concluded that the spent fuel pool cooling system is operable. A 4-hour report to the NRC was made under 10 CFR 50.72. The NRC resident inspectors were also notified.
2661997022 | Point Beach 1, Point Beach 2 | 05/07/1997 | 06/05/1997 | 9706110090 | <strong>Electrical Short Circuits During A Control Room Fire Could Affect Safe Shutdown Capability</strong><br /><i>Abstract:&nbsp;</i>May 7, 1997, with Unit 1 in cold shutdown and Unit 2 in a defueled condition, the licensee's Appendix R Rebaselining Project team discovered that a postulated Control Room fire may cause an electrical "hot short" that bypasses (i.e., disables) the limit or torque switches for certain motor-operated valves (MOVs) that are essential for achieving an Appendix R safe shutdown. Fifteen (15) MOVs may be affected by this "hot short" condition. The Auxiliary Feedwater System, Service Water System, Component Cooling Water System, and the Residual Heat Removal System are affected. Spurious operation of an MOV with a disabled limit switch could cause the valve operator to generate thrust and torque values which exceed the design limits of the valves; causing physical damage to the valve that precludes its manual-handwheel operation. The inability to operate these essential valves would affect the capability to achieve the Appendix R safe shutdown. This discovery was made by our Appendix R Rebaselining Project team during a review of NRC Information Notice IN 92-18. Modifications have been initiated to remedy the condition.
2661997023 | Point Beach 1, Point Beach 2 | 05/08/1997 | 06/05/1997 | 9706110083 | <strong>Noncompliant Emergency Lighting For Postulated Appendix R Fires</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1997, with Unit 1 in cold shutdown and Unit 2 in a defueled condition, the licensee's Appendix R Rebaselining Project team discovered that certain plant areas lacked adequate emergency lighting to demonstrate compliance with 10 CFR 50 Appendix R Section III.J requirements for 8-hour battery-powered lighting. This discovery was made during a review of Appendix R safe shutdown access/egress routes and locations of manual operations in the plant, in conjunction with a review of IN 95-036 "Potential Problems with Post Fire Emergency Lighting". Two of the five exterior buildings requiring access during certain fire scenarios lack the emergency lighting to comply with Section III.J. In addition, all of the access/egress routes to these buildings do not comply. The original plan for implementing Appendix R safe shutdown only provided for hand-held lighting to illuminate the two particular buildings and the access/egress routes. Corrective actions include revising the safe shutdown analysis, installing emergency lighting in the Service Water and Fire Pump House, and requesting an exemption to Appendix R Section III.J for emergency lighting along outdoor roadways to the support buildings.
2661997024 | Point Beach 1, Point Beach 2 | 05/01/1997 | 06/05/1997 | 9706160138 | <strong>Post Accident Sampling System Degradation</strong><br /><i>Abstract:&nbsp;</i>During reviews of the performance history for the Unit 2 containment atmosphere post-accident sampling system sample pump, it was determined that excessive leakage occurs at the leak test pressure of 15 psig. Evaluation of the leakage determined that the dose received by personnel obtaining a sample under worst case post-accident conditions would be in excess of the GDC 19 dose limits specified in NUREG 0737, Item II.B.3. This condition also applies to the Unit 1 sampling system. Additional design reviews of the containment atmosphere and reactor coolant post accident sampling systems also determined that in order to place the systems in service, instrument air, which may not be available post accident, would be required to be restored to containment. The containment atmosphere sample system will be upgraded to allow sampling at up to containment design pressure. Containment isolation provisions for the containment and reactor coolant sample systems are being evaluated.
2661997025 | Point Beach 1, Point Beach 2 | 05/20/1997 | 06/19/1997 | 9706270045 | <strong>Pressurizer Level Controlled Higher than Assumed in Accident Analysis</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a cold shutdown condition and Unit 2 was in a defueled condition, it was discovered that three Operating Procedures (OP) allow manual control of pressurizer level 10% higher than assumed in the PBNP FSAR section 14.2.5 rupture of steam pipe analysis assumption of 20%. This condition was discovered by Reactor Engineering personnel while reviewing operations and reactor engineering procedures in anticipation of the impending restart of Unit 2. These procedures were changed in the mid-1980's to allow manual control of pressurizer level at 30% in lieu of the automatic program level of 20% at zero power operation. This condition was caused by inappropriately changing the procedure without adequate consideration of potential affects on the PBNP accident analyses. The affected procedures will be revised prior to restart of Unit 2. It was determined that the consequences of the PBNP FSAR section 14.2.5 "Rupture of a Steam Pipe" analysis would not exceed 10 CFR 100 limits, even if some fuel damage could occur based on the use of a higher pressurizer level.
2661997026 | Point Beach 1, Point Beach 2 | 05/21/1997 | 06/19/1997 | 9706250078 | <strong>Technical Specification Violation of Operability Requirement for Main Steam Line Isolation</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1997, while PBNP Unit 1 was in a cold shutdown condition and Unit 2 was in a defueled condition, it was discovered that operability of the reactor coolant system average temperature instrumentation input to the main steam line isolation function was not being maintained in accordance with Technical Specification operability requirements. It has been concluded that the Technical Specification was violated each time either unit was above cold shutdown conditions with scaling resistors in place and the low reactor coolant system average temperature input to main steam line was not in the trip condition. This condition was caused by insufficient or inadequate consideration for operability of all required functions that rely on this input. The low reactor coolant system average temperature input to main steam line will be verified to be in the trip condition prior to leaving the cold shutdown condition when the scaling resistors are in place. It has been concluded that this situation did not diminish the safety of the public, plant personnel, or integrity of safety barriers in place at PBNP at any time.
2661997027 | Point Beach 1, Point Beach 2 | 05/21/1997 | 06/19/1997 | 9706270353 | <strong>NON-ENVIRONMENTALLY QUALIFIED MATERIAL IN CONTAINMENT HATCH APPLICATIONS</strong><br /><i>Abstract:&nbsp;</i>As a result of a review of operating experience information from another utility for applicability to the Point Beach Nuclear Plant, it was determined that the pressure equalizing valves in the containment personnel hatches utilized a Telfon material in various applications which is not qualified for the worst case post-accident radiation environment. In addition, packing material associated with a small window in the containment hatch doors is also believed to contain Telfon. Unit 1 is presently being maintained in cold shutdown. Unit 2 is presently being refueled. Under the present conditions, containment integrity is not required for either unit. The valves and windows will be replaced or modified to replace the Telfon with a suitable material prior to containment integrity being required.
2661997028 | Point Beach 1, Point Beach 2 | 08/29/1996 | 06/30/1997 | 9707080335 | <strong>Refueling Water Storage Tank Recirculation Piping Not In Compliance With Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1996, a condition was identified where the refueling water recirculation pump and its associated piping were aligned on a regular basis to perform RWST recirculation and purification. The interfaces between the seismic Class I RWST and the seismic Class III recirculation piping is accomplished via manually-operated valves. The PBNP FSAR requires interfaces between Class I systems and lower class systems to be at a normally closed valve or a valve which is capable of remote operation from the control room. Since these manual boundary valves were routinely maintained in the open position during recirculation/ purification activities, the plant was in a condition outside its design basis. The valves were immediately closed and tagged shut. An operability determination concluded that the RWST is operable. This condition was initially screened as not regulatory reportable based on Technical Specifications compliance. However, during evaluation of LER 266/97-021-00 on May 30, 1997, we determined that this condition was regulatory reportable based upon plant design basis non-compliance.
2661997029 | Point Beach 1, Point Beach 2 | 06/05/1997 | 07/07/1997 | 9707160022 | <strong>Safety Injection Accumulators Isolated During Plant Startup Procedure In Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>April 23, 1997, with Unit 1 in cold shutdown and Unit 2 in a defueled condition, a licensed operator discovered that an operating procedure allowed the isolation of Safety Injection (SI) accumulators during plant startup when primary pressure exceeded 1000 psig. This condition was in apparent violation of Technical Specification (TS) 15.3.3.A.1.h. On June 5, 1997, subsequent reviews confirmed that the procedure violated the Technical Specification and was reportable. The condition was first discovered during research for a major revision to Operating Procedure OP-1A, "Cold Shutdown to Low Power Operation". The failure to recognize the TS Limiting Condition of Operation (LCO) for the RCS leak test was the result of a non-conservative TS interpretation. The LCO was added in 1975 (TS Amendment 14), and at that time the plant startup procedures were not modified to accommodate the new requirement. Prior to the startup of either unit from their present outages, OP-1A will be revised to ensure that the SI accumulators are operable as required by TS 15.3.3.A.1.h.
2661997030 | Point Beach 1, Point Beach 2 | 06/11/1997 | 07/11/1997 | 9707150371 | <strong>Unanalyzed Service Water System Alignment</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a cold shutdown condition and Unit 2 was in a defueled condition, it was discovered that an actual alignment previously used does not conform with the assumed configuration used in the service water (SW) system hydraulic analyses. Specifically, service water was provided to a second component cooling water (CCW) heat exchanger during previous periods of higher than normal service water temperatures and for some changes in plant operating conditions. This alignment is not in conformance with current analyses that assume one CCW heat exchanger is being supplied with service water. This condition was caused by operation of the service water system in a condition that did not conform with the analyses for the service water system. In a letter dated June 25, 1997, Wisconsin Electric committed to operation of the service water system in accordance with analyses as implemented by approved procedures. Recent flow analyses show that minimal excess capacity exists in the service water system. Therefore, some safety equipment supplied by the service water system could receive less than desired flow for accident mitigation.
2661997031 | Point Beach 1, Point Beach 2 | 06/19/1997 | 07/21/1997 | ML03071041 | <strong>Nonconservative Setpoint For Auxiliary Feedwater Low Suction Pressure Trip</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1997, with Unit 1 in cold shutdown and Unit 2 in a refueling shutdown, the licensee's Design Basis team discovered that the auxiliary feedwater (AFW) pump low suction pressure trip setpoints may not ensure adequate suction pressure protection for the AFW pumps following a postulated seismic or tornado event. Portions of the AFW pump suction piping, including the condensate storage tank (CST), are not classified Seismic Class I and are not protected from tornado missiles. A postulated seismic or tornado event could cause a loss of offsite power, a loss of normal feedwater, and a break in the unqualified suction piping. At the postulated break locations, limited suction head will be provided to AFW pumps. If all pumps automatically start as designed, the suction piping could be swept of all water before the low suction pressure trip devices can secure the pumps; resulting in damage to the AFW pumps, and the potential loss of the secondary heat sink during the event. At the time of discovery, neither unit required the operability of the AFW System.
2661997032 | Point Beach 1, Point Beach 2 | 06/30/1997 | 07/30/1997 | 9708070144 | <strong>Inadequately Rated Electrical Buses Could Disable Switchgear And Cause Secondary Fires That Prevent Shutdown Per Appendix R.</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1997, with Unit 1 in cold shutdown and Unit 2 in a refueling shutdown, the licensee's Appendix R Rebaselining Team discovered that a previously-identified issue related to electrical switchgear ratings had implications on the plant capability to achieve a safe shutdown for Appendix R fire scenarios. A calculation concluded that for certain AC buses, the fault current for a postulated zero-impedance ("bolted") three phase fault may be larger than the current-interrupting capability of the equipment involved. The licensee evaluated the potential for a fire in one fire area to cause a bolted electrical fault that exceeded the interrupting capability of the associated switchgear. If the associated switchgear is located in a different fire area, the overcurrent condition of the switchgear could lead to another, secondary fire. The capability of the plant to achieve and maintain safe shutdown for fires in multiple fire areas has not been demonstrated. Calculations determined susceptible fire areas and electrical circuits. Compensatory measures were established to provide operability until full compliance is established.
2661997033 | Point Beach 1, Point Beach 2 | 06/30/1997 | 07/30/1997 | 9708060301 | <strong>Non-Exempt Power Cables Do not Meet Appendix R Separation Criteria</strong><br /><i>Abstract:&nbsp;</i>June 30, 1997, with Unit 1 in cold shutdown, the licensee's Appendix R Rebaselining Team discovered two power distribution cables located in the auxiliary feedwater (AFW) pump room that do not meet the requirements of 10 CFR 50 Appendix R, Section III.G.2, and are not specifically identified in the NRC-approved exemption to Appendix R. Specifically, these redundant safe shutdown cables associated with the AC power distribution system do not meet the requirement for 20' separation criterion with no intervening combustibles. Since the safe shutdown configuration described in the exemption does not include these cables, the capability to safely shutdown the plant for a fire in the AFW pump room is not adequately described in the plant licensing basis. An operability determination verified system operability pending restoration of the condition to full qualification. Compensatory fire watches have been established.
2661997034 | Point Beach 1, Point Beach 2 | 07/07/1997 | 08/05/1997 | 9708110188 | <strong>Unplanned Loss of Voltage on Train B Safeguards Buses</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a cold shutdown condition and Unit 2 was in a refueling shutdown condition, during loss of power testing, the emergency diesel generator, G-03, output breakers tripped open while it was supplying power to the Train B 4160 and 480 volt safeguards buses for both units. Affected equipment was restored based on guidance contained in the applicable abnormal operating procedures. Decay heat removal remained operating during the entire event because Train A was not affected within a short time, the Unit 1 and Unit 2 Train B safeguards buses were re-energized from off-site power. It was determined that the G-03 output breaker trip was caused by the "loss of field" trip signal when the emergency diesel generator was released from emergency run mode during test restoration. The "loss of field" output breaker trip is bypassed by an emergency run signal. Subsequent investigation revealed that the "loss of field" relay was not wired properly. The incorrect wiring was reworked and both Train B emergency diesel generators have been tested successfully.
2661997035 | Point Beach 1 | 05/16/1997 | 08/15/1997 | 9708220026 | <strong>Reactor Coolant Pump Rotor Stand Support Not Seismically Adequate</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1997, with Point Beach Nuclear Plant Unit 1 in a cold shutdown condition and Unit 2 in a refueling shutdown condition, the seismic adequacy of the support frame for the Unit 1 reactor coolant pump (RCP) rotor stand was questioned. On May 16, 1997, a calculation confirmed that the structure was not seismically adequate and would not meet design criteria if subjected to safe shutdown earthquake lateral loads. Failure of this support has the potential for dropping the RCP rotor stand onto the residual heat removal (RHR) or safety injection (SI) system piping. The rotor stand was not been known to have been used since initial plant construction. Subsequent to this determination, the Unit 1 RCP rotor stand was moved to a more secure location within the Unit 1 containment structure. The Unit 2 RCP rotor stand support was verified as being seismically adequate.
2661997036 | Point Beach 1, Point Beach 2 | 08/26/1997 | 09/25/1997 | ML03071043 | <strong>Potential Common Mode Failure in DC Power Supply Could Disable Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a cold shutdown condition and Unit 2 was operating at 100 percent power, licensee engineers discovered a potential common mode failure in the DC power supply system that could result in the loss of three auxiliary feedwater pumps during seismic or tornado events that cause the loss of the normal AFW suction source. The remaining AFW pump would not be capable of providing the feedwater flow rate that is assumed in the accident analysis for both units. The common mode failure is not a consequence of the postulated earthquake or tornado, but has been considered to be a single failure that should be considered during this design basis event. The common mode condition was created in a modification that assigned a common DC power supply to three (of four) AFW pump low suction pressure trip devices. Plant modifications will be performed to eliminate the potential common mode failure described herein.
2661997037 | Point Beach 1, Point Beach 2 | 09/03/1997 | 09/30/1997 | 9710070171 | <strong>Potential Failure of Emergency Diesel Generator Load Sequence</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a cold shutdown condition and Unit 2 was operating at 100 percent power, a condition was discovered in which the coincidental start of the Train A containment spray pump and the third Train A service water pump could cause the voltage on the 480 V system to drop sufficiently low to cause actuation of the 480 V undervoltage protection function. If this were to occur, 480 V load shedding would occur. This would cause the Train A residual heat removal pump, electric motor driven auxiliary feedwater pump, service water pumps, and containment spray pump to trip at about 25 seconds into the loading sequence. Only the Train A portion of the emergency power system is susceptible to this condition. Unit 2 was shutdown due to the conclusion by the Manager's Staff that the LCO would expire before the condition could be corrected. Cold shutdown was achieved at 1142 hours on September 8. A modification restored the operability of the EDG during load sequencing. Unit 2 was returned to criticality at 1810 hours on September 21, 1997.
2661997038 | Point Beach 1, Point Beach 2 | 09/26/1997 | 10/24/1997 | 9710290150 | <strong>Standby Emergency Power Inoperable In Excess of Technical Specifications Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>At about 0300 hours on September 3, 1997 emergency diesel generator (EDG) G-03 failed to start during a surveillance test. The inoperability of standby emergency power for 1A-06 placed Unit 2, which was operating at 100% power, in a 7-day limiting condition for operation (LCO) under the provisions of TS 15.3.7.B.1.g. Unit 1 was in cold shutdown, hence no LCO was applicable. At 0445 hours, EDG G-04, which is normally aligned as standby emergency power for 2A-06, was aligned to provide standby emergency power to both 1A-06 and 2A-06. This ended the 7-day LCO for Unit 2. Subsequent investigation of the G-03 failure concluded that the EDG had been inoperable since the previous shutdown of the EDG. The previous shutdown occurred on August 18, 1997 at about 0600 hours, when an operability test of G-03 was completed. The failure was caused by a failure in the engine governor for the EDG G-03. The governor was repaired and EDG G-03 was returned to service.
2661997040 | Point Beach 1 | 10/17/1997 | 11/21/1997 | 9711280294 | <strong>Potential Overstress of Seal Water Return Lines During Loss of Seal Coolant Events Such as Station Blackout or Appendix R Fires</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1997, Point Beach Nuclear Plant (PBNP) Unit 1 was in a cold shutdown condition and Unit 2 was operating at 100 percent power. Licensee engineers reviewing a vendor calculation for pressures and temperatures of reactor coolant pump seal water return lines, discovered that a potential existed for the Unit 1 lines to fail due to thermal stresses induced during a full loss of cooling to the reactor coolant pump seals. A formal thermal effects analysis had not been completed for this line in the past. The line will be modified to provide appropriate supports for the hypothesized scenarios. This condition was reported to the NRC in accordance with 10 CFR 50.72(b)(2)(i), "any event, found while the reactor is shut down, that, had it been found while the reactor was in operation, would have resulted in the nuclear power plant, including its principal safety barriers, being seriously degraded..."
2661997041 | Point Beach 1 | 10/23/1997 | 11/24/1997 | ML03071050 | <strong>Potential Common Mode Failure in Auxiliary Feedwater System Control Circuits</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was in a cold shutdown condition, licensee engineers discovered a potential common mode failure in the auxiliary feedwater (AFW) pump control circuits that could result in the loss of two auxiliary feedwater (AFW) pumps; 1P-29 and P-38A. The Final Safety Analysis Report provides for failure of only one AFW pump. The remaining AFW pump (P-38B) may not be capable of providing the feedwater flowrate that is assumed in the accident analyses. The postulated common mode failure to the adjacent cables is not a consequence of the accident, but has been considered to be a random, design basis single failure that should be considered. The common mode condition was created by a modification that installed a low suction pressure trip function on each AFW pump. Plant modifications will remedy the potential common mode failure described herein.
2661997042 | Point Beach 1 | 10/30/1997 | 12/01/1997 | 9712090155 | <strong>Failure to Perform Containment Personnel Air Lock Surveillance While Door Interlock is Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1996, Point Beach Nuclear Plant (PBNP) Unit 1 was operating at 100 percent power and Unit 2 was shut down for steam generator replacement. On that date the Unit 1 upper air lock inner door remote operator connecting gear was removed and subsequently not reinstalled as part of an interim repair. An investigation concluded that the interlocks were not affected by removal of the gear. On October 30, 1997, Routine Maintenance Procedure (RMP) 225 was performed to verify operation of the Unit 1 personnel air lock door interlocks as a prerequisite for placing the air lock back into operation. Operational verification of the inner door remote closure mechanism could not be completed. Therefore, the air lock interlocks were declared inoperable. A review of the requirements of the Technical Specification requirements for an inoperable air lock interlock revealed that the surveillance for the interlock (verifying a door locked each 31 days) had not been performed while the gear was removed and Unit 1 was operating.
2661997043 | Point Beach 1, Point Beach 2 | 11/15/1997 | 03/16/1998 | 9803300422 | <strong>Inadequate Technical Specification Surveillance of Reactor Trip System Interlocks</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1997, at about 1130 hours, with Unit 1 in cold shutdown and Unit 2 at about 47 percent power, the reactor protection circuits associated with reactor trip system interlocks were declared inoperable due to failure to meet the Technical Specification (TS) surveillance requirement for these circuits. Unit 2 entered an eight hour TS action statement to be in hot shutdown. Unit 2 was placed in hot shutdown at 1925 hours on November 15, 1997. The inadequate surveillance was discovered during reviews being performed in accordance with NRC Generic Letter 96-01. Testing of the Unit 1 circuitry was completed on November 21 and 25, 1997, prior to startup of that unit. Unit 2 testing will be completed prior to startup and a supplemental licensee event report will be provided to document that results of that testing and an assessment of the safety impacts based on the as-found condition of the associated circuitry. Based on successful completion of Unit 1 testing, it is judged that the Unit 1 circuitry was always operable.
2661997044 | Point Beach 1, Point Beach 2 | 12/16/1997 | 01/15/1998 | 9801230130 | <strong>Use of Dedicated Operators During Inservice Testing Of Containment Spray System Constituted An Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1997, while Point Beach Nuclear Plant (PBNP) Unit 1 was operating at 98 percent power and Unit 2 was in a cold shutdown condition, the licensee's system engineering group discovered that certain inservice test procedures employed "dedicated operators" to replace the automatic containment spray additive function. As written, these procedures rendered inoperable the automatic function which injects sodium hydroxide to both trains of containment spray during a design basis accident. After determining that the use of dedicated operators was not consistent with the guidance of NRC Information Notice (IN) 97-78, the licensee determined that both redundant trains of containment spray additive had been rendered inoperable during past performances of the test; an operation prohibited by Technical Specifications. The identified inservice test procedures have been revised such that dedicated operators will not be required. This condition was discovered during a review of IN 97-78.
2691997001 | Oconee 1, Oconee 2, Oconee 3 | 01/15/1997 | 02/17/1997 | 9702260063 | <strong>Technical Specification Not Met Due To Deficient Procedures</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On December 15, 1996, Units 1 and 2 were at cold shutdown and Unit 3 was in a refueling outage. A System Engineer was preparing a test procedure when he recognized that no administrative controls were in place to control the Low Pressure Injection outlet temperature above the minimum temperature (70 F) shown on the Technical Specification (TS) heatup and cooldown curves. Procedural guidance permitted operation at temperatures lower than the operating region defined by TS curves. On January 15, 1997, a past operability evaluation concluded that the minimum temperature shown on the curves is not a limiting value for flow into the reactor vessel. The evaluation indicated that the analyzed minimum temperatures are 40 F for Unit 1 and 2 and 50 F for Unit 3. The root cause of this event is deficient Written Communication; Technical Inaccuracies. Corrective actions included revising operations procedures to assure the current limits are met. Also, a revision to the TS is planned.
2691997002 | Oconee 1, Oconee 2, Oconee 3 | 01/24/1997 | 09/14/1998 | 9809180202 | <strong>Reactor Building Cooling Units Technically Inoperable Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>In response to NRC Generic Letter 96-06, Oconee Engineering has been performing conservative analyses to determine if the Low Pressure Service Water (LPSW) System piping which serves the Reactor Building Cooling Units (RBCU) may be susceptible to waterhammer. On 1/24/97, at 1426 hours, the NRC was notified per 10 CFR 50.72 because the analysis determined that, during certain design basis scenarios, waterhammers might occur in piping to the non-safety related auxiliary cooling units (ACUs). This might prevent the safety related RBCUs from performing their intended function. At that time, Units 1 and 2 were at Cold Shutdown and Unit 3 was in a refueling outage. On 2/20/97, revision 0 was submitted as a partial LER because more detailed analyses were still in progress. On 7/31/97, revision 1 was submitted to better describe the potential impact of water hammers in the ACUs. On 8/13/98, after further analysis identified some initial conditions that might result in severe waterhammer and breach LPSW piping serving the RBCUs, the NRC was again notified per 10 CFR 50.72. The root cause is deficient Design Analysis, Unanticipated interaction of systems. Corrective actions included initially isolating and draining the ACU piping, and revising operating procedures as required. This event is considered to be of no significance with respect to the health and safety of the public.
2691997003 | Oconee 1, Oconee 2, Oconee 3 | 03/17/1997 | 11/12/1997 | 9711170183 | <strong>Post LOCA Boron Dilution Design Bases Not Met Due To Deficient Design Analysis</strong><br /><i>Abstract:&nbsp;</i>While Oconee Units 1, 2, and 3 were in an extended outage, Engineering began an evaluation of Generic Letter 96-06. To eliminate present operability concerns related to thermal overpressurization in post-Loss of Coolant Accident (LOCA) boron dilution flow paths, procedures were revised to partially drain between valves LP-1 and LP-2 and between 3LP-103 and 3LP-104 during unit startup. On March 17, 1997, Units 1 and 2 were operating at 100 percent and Unit 3 was at 63 percent, an operability evaluation concluded that calculations could not prove that these valves could be opened post-LOCA with the lines full. Further engineering evaluation has revealed that the previous operability evaluation had conservatively neglected the impact of the holes drilled in the upstream disks of LP-1. The holes were drilled in LP-1 in April 1986, March 1985 and February 1987 on Units 1, 2, and 3, respectively. Therefore, the post-LOCA boron dilution flow path using LP-1 has been operable since the holes were drilled in the mid 1980s. However, this flow path is considered technically inoperable prior to the time the holes were drilled. The post-LOCA boron dilution flow paths using valves LP-103 and LP-104 were declared technically inoperable from the original installation until October, 1996 when the recent outages began. The root cause is a Deficient Design Analysis, unanticipated interaction of components. Additional corrective actions include developing and implementing future modifications.
2691997004 | Oconee 1, Oconee 2, Oconee 3 | 04/17/1997 | 05/15/1997 | 9705290263 | <strong>Low Temperature Overpressure Protection Path Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1997, a review was in progress of the Low Temperature Overpressure Protection (LTOP) portion of the Improved Technical Specification Conversion Project. During this review, it was determined that more than one High Pressure Injection (HPI) pump could be started during a LTOP event. On April 17, 1997, Units 1, 2, and 3 were at 100% full power. An Engineering analysis determined that the travel stops on valves 1, 2, and 3 HP-120 were not set to adequately restrict makeup flow with multiple HPI pumps running. This would have rendered one train of LTOP inoperable during periods when the Reactor Coolant System temperature was less than 325 degrees F and the required compensatory measures not taken. Duke's evaluation of this event is continuing and this report will be supplemented to address root cause and other LER content requirements.
2691997005 | Oconee 1, Oconee 2, Oconee 3 | 04/26/1997 | 05/27/1997 | 9706030116 | <strong>Low Pressure Service Water Piping Outside Design Basis For High Trajectory Turbine Missiles</strong><br /><i>Abstract:&nbsp;</i>The Oconee original design criteria, as stated in the Updated Final Safety Analysis Report (UFSAR), requires Engineered Safety (ES) Features to be protected from turbine generated missiles by means of shielding or separation. In addressing a concern found during the Service Water Upgrade Project, Oconee Engineering began a review in September 1996 to verify that the Low Pressure Service Water (LPSW) [EIIS:BI] system piping met the separation criteria for turbine missiles. on October 3, 1996, an evaluation determined that Low Trajectory missiles, thought to be most limiting, were not a concern. On April 26, 1997, Units 1 and 3 were at 100% full power and Unit 2 was at cold shutdown, when it was determined that portions of the LPSW system piping did not meet the Oconee separation criteria for High Trajectory Missiles. Separation was addressed by Engineering in the original design of ES systems, but these portions of LPSW piping do not have separation or documentation of adequate shielding from High Trajectory Missiles. The root cause of this event is Unknown. This event is not recurring and had no personnel injuries, exposures or releases of radiation. Corrective action included submitting an amendment to the UFSAR to allow for current industry and NRC guidance concerning vulnerable target area and probability of impact of a turbine missile without shielding or separation protection. This license amendment was approved by the NRC on May 16, 1997. When applying the NRC approved methodology, the LPSW system piping in question provides an acceptably low probability target. Therefore, the health and safety of the public was not impacted by this event.
2691997006 | Oconee 1, Oconee 2, Oconee 3 | 06/20/1997 | 07/21/1997 | 9707280243 | <strong>Voluntary LER on Problems During Electrical Tests: Loss of LEE, Failure of Keowee 1, and Loss of Keowee 1 Auxiliaries</strong><br /><i>Abstract:&nbsp;</i>On June 20, 1997, Oconee Unit 1 was at cold shutdown, Unit 2 was at 100% Full Power, and Unit 3 was at 13% Full Power. As part of a required test, the Lee Steam Station Switchyard was supplying power to Oconee Unit 1. At 1244 hours, a loss of the dedicated line from Lee resulted in a loss of power to Unit 1. Unit 1 automatically swapped to the Oconee switchyard and power was restored. Both Keowee Hydro (KH) Units (emergency generators) received a start signal, but KH-1 failed to energize the underground path. On June 23, 1997, the Lee test was repeated successfully. However, KH-1 lost auxiliary power during realignment. The loss of power from Lee resulted from inappropriate action. KH-1 failed to energize the underground path apparently due to failure of the field flash breaker to latch. The loss of auxiliary power was due to equipment failure and a deficient procedure. Corrective actions have addressed all these causes. This event did not impact the health and safety of the public. This is a voluntary report.
2691997007 | Oconee 1, Oconee 2, Oconee 3 | 06/24/1997 | 07/25/1997 | 9708040023 | <strong>Emergency Core Cooling System Technically Inoperable Due To An Inappropriate Action</strong><br /><i>Abstract:&nbsp;</i>On June 24, 1997, while Unit 1 was at cold shutdown, a routine walk down of the Reactor Building identified two sections of reactor coolant piping wrapped with blanket insulation that had potentially not been evaluated for use inside containment. A decision was made to inspect Unit 3 while power was at 15% and also to decrease power on Unit 2 from 100% to 15% for an inspection. Unit 3's inspection discovered two questionable pieces of blanket insulation and Unit 2's inspection discovered one piece. The questionable insulation was removed on all three units. No documentation could be found to show this insulation had been qualified or approved prior to use inside containment. Therefore, on June 25, 1997, Engineering concluded that past operability of the Reactor Building Emergency Sump may not be justified based on the unknown characteristics of the unapproved insulation. The Low Pressure Injection, High Pressure Injection, and Reactor Building Spray Systems might have been technically inoperable in the past. The root cause of this event is determined to be Inappropriate action, failure to adhere to directives. Planned corrective actions include increasing the awareness of engineering and maintenance personnel on the importance of utilizing the modification process when removing and replacing insulation in the Reactor Building.
2691997008 | Oconee 1 | 07/01/1997 | 09/24/1998 | 9810020431 | <strong>Manual Reactor Trip Due To Equipment Failure While Shut Down</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1997, Unit 1 was at hot shutdown (2180 Psig, 538F) with the Reactor Protective System (RPS) reset and Control Rod group 1 withdrawn 50%, per procedure. The 1A Main Feedwater Pump (MFDWP) was in operation. At approximately 0727 hours, alarms indicated the feedwater (FDW) system was swinging. The operators attempted to control FDW in manual, but the system did not respond as expected. At 0755:42 hours, the 1A MFDWP tripped on high discharge pressure. Per procedure, the operator manually tripped the RPS at 0755:47 hours. The group 1 control rods tripped into the core from their initial position at 50% withdrawn. An Anticipated Transient Without Scram (ATWS) mitigation system started the Emergency FDW pumps. The unit was stabilized on Emergency FDW. The reactor was sub-critical throughout the event. The root cause of this event is equipment failure of a circuit board in the 1A MFDWP Turbine control system. Corrective actions were to make temporary repairs pending receipt of a new circuit board. Further evaluations have indicated that the circuit board can be removed permanently. This event had no impact on safety.
2691997009 | Oconee 1, Oconee 3 | 10/10/1997 | 11/10/1997 | 9711140164 | <strong>Low Pressure Injection Flow Instrument Technical Specification Surveillance Interval Exceeded Due To Deficient Work Practices</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1997, Unit 1 was in a refueling outage, Unit 2 was at 1001 full power, and Unit 3 was at hot shutdown condition and preparing for startup. The Instrument and Control (I&C) section completed a review of Technical Specification (TS) instrument surveillances for Low Pressure Injection (LPI) flow transmitters. On October 10, 1997, it was discovered that when the surveillance was last performed in 1995, the Unit 1 and 3 LPI flow transmitters were omitted. The surveillance was immediately performed on Unit 3 since it was in a startup mode and Unit 1 was calibrated the next day. There were no deficiencies noted for the calibration of Unit 1 or 3 LPI flow transmitters. The root cause is Deficient Work Practices; Document Use Practices, Documents not followed correctly because the I&C personnel misinterpreted the work order task description. Corrective actions include calibrating the LPI flow transmitters, counseling personnel, and reviewing other Instrument procedures that satisfy TS surveillance criteria to determine if this event is an isolated case.
2691997010 | Oconee 1, Oconee 2, Oconee 3 | 12/10/1997 | 01/08/1998 | 9801160121 | <strong>Inadequate Analysis of ECCS Sump Inventory due to Inadequate Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1997, a Self-Initiated Technical Audit documented potentially non-conservative assumptions used in the calculation for the Reactor Building (RB) water level following a large break LOCA. The most significant issue was the modeling of water trapped in areas inside of the RB. After preliminary evaluation, a Systems Engineer concluded, on December 10, 1997, that inadequate NPSH might exist during long term Emergency Core Cooling System (ECCS) operation in the recirculation mode. At 1411 hours, Oconee made a 1 hour notification to the NRC per 10 CFR 50.72(b)(1)(ii)(B), to report that Unit 3 was potentially outside its design basis. At this time, Unit 1 was at cold shutdown and Unit 2 was at 100% but was considered less susceptible to the event. A flow restricting flange and 2 basket strainers were removed from the Reactor Vessel Cavity and Fuel Transfer Canal drain lines on each unit to provide additional NPSH margin to assure current operability. Subsequently, the completed evaluation concluded that the system had been operable on all Oconee units. Therefore, this is a Voluntary Report. The root cause of this event is Inadequate Design Analysis. A contributing deficiency was Inadequate Change Management.
2691997011 | Oconee 1 | 12/28/1997 | 01/27/1998 | 9802050218 | <strong>Steam Generator Leak Results in Technical Specification Unit Shutdown Due to Inadequate Process Control.</strong><br /><i>Abstract:&nbsp;</i>During power escalation testing following a Unit 1 refueling outage, alarms were received on the condensate air ejector off-gas radiation monitor. On December 28, 1997, sample results and calculations were initiated and confirmed. At 1507 hours, Unit 1 was operating at 54% full power when a shutdown was initiated as required by Technical Specifications (TS) due to a calculated 404 gallons per day steam generator leak. At 1532 hours, a one hour non emergency notification was made to the NRC per 10CFR50.72(b)(1) due to Unit shutdown per TS. Shutdown progressed normally and no safety system actuations occurred. Although several minor steam generator leaks were found, one leak was substantial and considered the primary contributor to the excessive leakage. The root cause was determined to be an inadequate process control for the installation of a remote welded plug. The leaks were repaired.
2701997001 | Oconee 2, Oconee 3 | 04/21/1997 | 05/21/1997 | 9705290213 | <strong>Unisolable Reactor Coolant Leak Due to Inadequate Surveillance Program</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1997, Unit 2 was at 100% Full Power(FP). At 2245 hours, Operators noted indications of a 2.5 gpm Reactor Coolant System (RCS) leak. The source could not be determined, so at 0352 hours on April 22, power reduction began. At 20%FP Operators could not identify the leak as isolable, so the decision was made to go to cold shutdown. At 1448 hours, the reactor was tripped by a planned test. At 1500 hours, a NOUE was declared when the leak exceeded 10 gpm. The NOUE was terminated at 2032 hours after the leak reduced below 10 gpm. The leak was found to be a crack at the safe end to pipe weld on the High Pressure Injection to RCS cold leg nozzle near Reactor Coolant Pump 2A1. The safe end and pipe were found to be cracked internally and the thermal sleeve was found to be loose and damaged. The failures were caused by thermal cycling fatigue. The root causes were determined to be failure to implement an effective HPI nozzle inspection program based on available industry recommendations and failure to effectively evaluate known problems and implement appropriate corrective actions. Corrective actions include repair of the nozzle components and establishing an effective program to inspect and support nozzles. Evaluation shows that the HPI line still had a factor of safety greater than 2 under design basis event loads. Prompt shutdown prevented the development of an unsafe condition.
2701997002 | Oconee 2 | 07/06/1997 | 08/05/1997 | 9708130067 | <strong>Grid Disturbance Results In Reactor Trip Due To Manufacturing Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1997 at 0652 hours, Oconee Unit 2 was operating at 100% full power when a system grid disturbance initiated a Generator protective relay actuation that resulted in all four reactor coolant pump/power monitor channels of the Reactor Protective System tripping. The operators placed the Unit in a stable, hot shutdown condition. The grid disturbance was created by a switching problem at Jocassee Hydro Station, located approximately 15 miles away from Oconee. The voltage regulator on Unit 2 did not respond as expected to the grid disturbance and maintain bus voltage within acceptable ranges. The root cause of this event is a manufacturing deficiency, inadequate installation instructions. Corrective action included calibration of the voltage regulator. This event is not considered to have an impact on the health and safety of the public.
2711997001 | Vermont Yankee | 02/07/1997 | 05/01/1997 | 9705070325 | <strong>Inadequate design evaluation allows plant operation under conditions where a single postulated electrical failure coincident with a LOCA could result in containment overpressure.</strong><br /><i>Abstract:&nbsp;</i>On 02/07/97 during an investigation for an unrelated issue, Vermont Yankee (VY) discovered the potential for a postulated electrical failure in the containment isolation control circuitry to challenge primary containment integrity. Plant design ensures that either the drywell vent and purge (VP) outboard isolation valves or the corresponding inboard isolation valves will close as designed given any postulated single failure. However it was recognized that the failure to close at least one of the inboard vent or purge isolation valves could challenge containment integrity. Were a Loss of Coolant Accident (LOCA) to occur, concurrent with the postulated single failure in the torus/drywell VP valve control circuitry, while containment inerting/deinerting was in progress, a flow path would be present which would allow a portion of the steam to bypass the available heat sink (suppression pool), potentially overpressurizing the containment pressure vessel. This flow path was possible because VY containment inerting procedures allowed simultaneous opening of the torus and drywell inboard VP paths while inerting and/or deinerting the containment. VY has established administrative controls to preclude simultaneously opening both the torus and drywell vent or purge paths during normal plant operation. The Root Cause of this condition is that the impact of these valves failing to close during a LOCA, was not correctly evaluated or understood. Because plant Technical Specifications only allow the high volume drywell and torus VP paths to be opened with the plant in cold shutdown (or for 24 hours after plant startup, or for the 24 hours preceding shutdown); the affected circuit is tested each operating cycle; and a LOCA must occur coincident with the electrical failure; the probability that the containment overpressurization could occur is exceedingly low. Therefore this event is not considered to have presented an increased threat to public health or safety.
2711997002 | Vermont Yankee | 02/21/1997 | 05/29/1997 | 9706050057 | <strong>Inadequate design allows VY Switchgear to be vulnerable to flooding During the Maximum Postulated Flood (MPC) conditions.</strong><br /><i>Abstract:&nbsp;</i>On 02/21/97 VY discovered the potential for water intrusion into the Vital Switchgear Rooms via underground conduits during Maximum Postulated Flood Conditions (MPC). Were the MPC to occur, switchgear providing electrical power to Division I and II safety systems would need to be de-energized, placing the plant in a vulnerable condition. This potential exists due to an inadequate initial plant design. Presently a Basis for Maintaining Operation (BMO) has been completed to support continued safe plant operation. In-place plant procedures require the Shift Supervisor to initiate plant shut down with flood waters approximately 10 feet below the level at which the switchgear rooms would be challenged should conditions continue to degrade. VY is installing high density silicone seals in conduits which otherwise allowed intrusion of external flood waters into the Switchgear Rooms. This will reduce water introduction into the Switchgear Rooms to an easily manageable rate. Procedures are being revised to specify additional actions to be implemented if a flood occurs. To date the maximum river level that has occurred at the site was an elevation of 231.4 ft. mean sea level (MSL). Because the probability of a MPC flood is extremely low, and the highest level achieved during a previous high water condition was 17.1 ft. below the elevation of concern; this event is not considered to have presented an increased threat to public health and safety.
2711997003 | Vermont Yankee | 03/05/1997 | 10/30/1997 | 9711070184 | <strong>Overpressure protection not provided for turbine building as described in the VY FSAR due to an unknown cause. The event investigation continues.</strong><br /><i>Abstract:&nbsp;</i>On 3/5/97, during investigation for a similar issue, it was discovered that the design for Turbine Building overpressure protection, described in the Vermont Yankee Final Safety Analysis Report, was never installed. The VY FSAR description of Turbine Building overpressure protection includes a 1000 sq. ft. blowout panel that would actuate at an internal pressure of 0.25 psi. No venting areas of this size have been found in the Turbine Building, and investigation to date has been unable to identify any other venting methods that may have beeR assumed, in lieu of the blowout panels, when the plant was constructed. The analysis for high energy line breaks (HELB) in the Turbine Building credits the blowout panel. Absent the blowout panel, the potential higher pressure raised concern for the structural capability of certain block walls and ductwork in the building. Analysis has been performed to assess the potential effects on safety related equipment and to justify continued operation. Where appropriate, compensatory measures are in place to reduce the areas potentially susceptible to an HELB absent the mitigating effects of the Turbine Building blowout panel. The affected ventilation system has been modified to prevent steam intrusion into the vital switchgear room in the event of an HELB. Blowout panels have been designed, and the design package is currently being reviewed. The devices, when installed, will provide overpressure protection for the Turbine Building and meet the intent of the original FSAR description. Because there has been no occurrence of an HELB in the turbine building during the plant's lifetime, and an accident of such magnitude is of extremely low probability (VY FSAR 14.4.3), this event is deemed to have presented no increased risk to the health and safety of the public.
2711997004 | Vermont Yankee | 03/07/1997 | 01/14/1998 | 9801220222 | <strong>Lack of Detailed Licensing Bases Document Relative to Internal Flood Protection Combined With Errors in Interpretation of Design Drawings Results in Configurations Inconsistent With Plant Design Bases for Flooding</strong><br /><i>Abstract:&nbsp;</i>On 3/7/97 through 5/20/97 deficiencies were identified during an internal flooding review by Vermont Yankee. The review identified that a failure in fire suppression water, and other non-seismic piping systems in areas adjacent to the switchgear rooms could potentially affect the vital switchgear. Additional investigation determined that similar potential flood sources with the capability of challenging redundant ESF's existed. Major failures in the affected lines have been estimated to produce flowrates of sufficient magnitude to challenge redundant safety systems within 20 minutes. The causes of this event included inadequate licensing bases documentation relative to internal flood protection requirements and incorrect interpretation of design drawings. Bases for Maintaining Operation (BMO's) were written which support continued safe plant operation in light of each postulated scenario. Administrative controls have been put in place to direct operators should any of the theorized flood conditions occur. A detailed report articulating the VY current licensing bases relative to internal flood protection attributes is currently under development. Because the postulated pipe failures, 1) would generally be slow in developing to a point where redundant safety significant SSC's could be challenged, 2) would generally actuate control room annunciators which would prompt an immediate investigation and appropriate mitigating actions, and, 3) the probability of such major failures occurring is very low, this event is not considered to have presented a significant increase in risk to public health and safety.
2711997005 | Vermont Yankee | 03/24/1997 | 09/05/1997 | 9709120240 | <strong>Inadequate design/operating license coordination allows plant configuration which could result in a loss of secondary containment integrity in the event of a LOCA coincident with containment inert/deinert operations.</strong><br /><i>Abstract:&nbsp;</i>On 03/24/97 during the review of a plant status report for an occurrence at another station, VY determined that a similar condition existed at VY. Specifically, the potential exists during primary containment inerting and deinerting operations at power to overpressurize the Standby Gas Treatment System filter train housings, should a major LOCA occur. While the SBGT system will isolate automatically from the primary containment on a LOCA signal, it was determined that the valve stroke times were such that the potential for system overpressurization existed. The potential overpressurization would challenge secondary containment in the event of a LOCA concurrent with containment inerting or deinerting activities. The potential for overpressurization existed because VY Technical Specifications and containment inerting procedures allowed inerting and/or deinerting the primary containment while at power. VY has established administrative controls to preclude the system alignment which creates the potential for overpressurizing the Standby Gas trains. On 4/24 and 5/1 2/97 there were recurrences of this event due to an inadequate disposition of the issue by VY. Further reporting on this issue is contained in VY LER 97-14, reported on 9/5/97. Because plant Technical Specifications only allow normal containment inerting and deinerting operations with the plant in cold shutdown (or for 24 hours after plant startup, or for the 24 hours preceding shutdown) and the postulated LOCA must occur coincident with an inerting or deinerting activity, the probability of the Standby Gas train overpressurization is exceedingly low. Therefore this event is not considered to have presented an increased threat to public health or safety.
2711997006 | Vermont Yankee | 03/26/1997 | 03/19/1998 | 9803260409 | <strong>Use of an inadequate design implementation document During initial plant construction results in the failure to maintain proper electrical separation of electrical cables.</strong><br /><i>Abstract:&nbsp;</i>On 3/26/97 during Appendix R program enhancement efforts, Vermont Yankee discovered an electrical cable installation in variance with the VY FSAR requirements for separation of electrical cables, Specifically, it was discovered that a non-safety lighting panel supply cable passed in proximity to both division I and division II Engineered Safety Feature actuating and power cables. This configuration conflicts with VY's single failure criteria for safety systems, creating a condition where a single failure of an active component (the safety-class circuit breaker providing protection for the non-safety lighting circuit) could challenge redundant ESF trains. This configuration has been in place since initial plant construction due to the use of an inadequate installation guideline. VY has rerouted the subject lighting cable to conform to the applicable separation criteria. Follow-up investigation has revealed similar cable routing non-conformances including a single electrical box which houses cable potentially affecting one Low Pressure Coolant Injection subsystem and a cable providing DC power to the High Pressure Coolant Injection system. VY has performed an extensive, systematic assessment of its cable routing. Cable separation non-conformances discovered have been evaluated for their safety implications. Compensatory measures and bases for maintaining operation were developed as necessary. The non-conforming cables are typically low-voltage signal/control cables and/or protected by multiple safety class protective devices. These devices provide highly reliable protection against faults which could reasonably be expected to challenge the cable insulation. Additionally, the cable mixing found was bounded by VY's current Appendix R analyses. Therefore this event is not considered to have presented an increased threat to public health or safety.
2711997007 | Vermont Yankee | 04/21/1997 | 05/21/1997 | 9705280382 | <strong>Inadvertent Primary Containment Isolation System Actuation Due To a Spurious Spike on a Reactor Building Vent Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>At 2143 hours on 04/21/97, with the reactor operating at 100% power, a Standby Gas Treatment System (SBGTS) initiation and Reactor Building Ventilation isolation occurred concurrent with a Primary Containment Isolation System (PCIS) Group III isolation. These isolations and the initiation of SBGTS were caused by a spike on the "B" Reactor Building Vent Radiation Monitor. <br /><br /> The cause of the event was a spurious electronic noise signal of a magnitude greater than the trip setpoint of the radiation monitor. <br /><br /> Corrective actions consisted of conducting a radiological survey in the area of the radiation monitor detector to determine if a valid signal had been received, and troubleshooting the radiation monitor circuitry. <br /><br /> There were no adverse implications to plant equipment or to the health and safety of the public because the isolation of the ventilation systems and SBGTS initiation are conservative system actuations with respect to protection of the public.
2711997008 | Vermont Yankee | 04/24/1997 | 05/23/1997 | 9705290004 | <strong>Plant scram due to procedural non-compliance and failure to perform self-verification During nuclear instrumentation calibration.</strong><br /><i>Abstract:&nbsp;</i>On 04/24/97 an Automatic Reactor Scram occurred as a result of personnel errors made during calibration of the Local Power Range Monitor (LPRM) detectors. Average Power Range Monitor (APRM) channels "A" and "D" were removed from service to block test signals to the Reactor Protection System (RPS). Failure to properly perform a procedural step resulted in the mode selector switches for APRM channels "A" and "D" remaining in the "Zero" vice "Operate" position. Following the calibration of the LPRM detectors, the procedure directed that the affected APRM output be adjusted to indicate core thermal power. Having omitted the restoration of the APRM mode switches the Reactor Engineer (RE) was unable to adjust APRM output. Without resolving this discrepancy, the RE proceeded with the testing activity. The RE then requested the Licensed Operator to restore APRM channels "A" and "D" to service. The rapidity with which the Licensed Operator restored both APRM channels to service did not allow for proper verification of system response. A reactor scram occurred and went to completion. The Operators followed plant procedures for a reactor scram and the plant was stablized. A post trip report and cause analysis were conducted. Lessons learned were presented to all Licensed Operators. The need for procedural compliance and communication of problems as they occur were reinforced to Site personnel. The quality and ownership of affected procedures are being reviewed and improvements are being made as necessary. This event is not considered to have presented an increased threat to public health or safety.
2711997009 | Vermont Yankee | 04/23/1997 | 05/21/1997 | 9705280388 | <strong>Lack of Specificity In Plant Technical Specifications results in operation of Plant Service Water Systems which was inconsistent with Prescribed Limiting Conditions for Operation and Testing Requirements.</strong><br /><i>Abstract:&nbsp;</i>On 04/23/97, during preparations for an upcoming engineering inspection, VY determined that past practices for declaring Station Service Water (SSW) subsystems inoperable were inadequate. It was determined that the SSW System is single failure vulnerable whenever a single SSW pump becomes inoperable. Historically VY had considered both subsystems operable unless two SSW pumps were inoperable. VY recently recognized that the loss of any single pump made the SSW system vulnerable to a single failure (loss or failure of an Emergency Diesel Generator) preventing the successful performance of the SSW system safety function. The apparent cause of this event is inadequate detail in the SSW Technical Specifications (TS's), in that neither the LCO, the TS surveillance requirements, nor the TS bases clearly described the specific operability requirements for system pumps. The SSW TS level of detail and specificity is not consistent with that of other similar VY safety systems. The proper interpretation of SSW system TS's has been communicated to the operating staff, and operating procedures have been corrected. An historical review of SSW material records (1990 to present) was performed, which determined that the system had only been operated on 2 occasions where the TS LCO limit of 15 days was exceeded. Material histories prior to 1990 lack sufficient detail for such as assessment. In each case a single pump was inoperable for approximately 18 days. In no case were two pumps inoperable simultaneously. Because the time frames for inoperable subsystems were very near the LCO limit, there was no indication of redundant component/subsystem unavailability, and there were procedures in place prescribing appropriate actions for the postulated event. This event is not considered to have presented an increased threat to public health or safety.
2711997010 | Vermont Yankee | 04/24/1997 | 05/21/1997 | 9705280395 | <strong>Individual Control Rod Drive Scram time greater than normal due to manufacturing defect in scram solenoid pilot head assembly.</strong><br /><i>Abstract:&nbsp;</i>On 04/24/97 while reviewing data after a reactor scram, it was determined that a single control rod (rod 06-11) exhibited a slower than normal scram time for the start of control rod motion. Although all control rod speeds during the plant trip met Technical Specification (TS) requirements, cause of the slower than normal rod speed was evaluated. While troubleshooting, it was determined that this rod was inoperable. During testing the rod failed to scram due to a Scram Solenoid Pilot Valve (SSPV) failure. The cause of the SSPV failure is attributed to inadequate Quality Control by the Manufacturer. A 10CFR21 Notification of potential defect has been issued by the vendor. Prior to failure, this SSPV and several others had exhibited a buzzing noise while energized. Following this event the noisy SSPV's were replaced or rebuilt, and scram testing was satisfactorily performed for all affected rods. Although Rod 06-11 was identified after the scram as having a longer than normal time, it was still acceptable to TS requirements and performed its intended function, meeting its safety design bases. VY also has in place Backup Scram Valves, and an Alternate Rod Insertion System with valves which are of a different design and manufacturer than the SSPV's. Therefore this event is considered not to have presented an increased threat to the public.
2711997011 | Vermont Yankee | 05/12/1997 | 06/11/1997 | 9706180260 | <strong>The Primary Containment Torus Was Not Inerted To Technical Specification Requirements Due To An Inadequate Procedure Which Resulted In An Insufficient Nitrogen Inerting Purge Flowrate.</strong><br /><i>Abstract:&nbsp;</i>At 0035 hours on 05/12/97, with the reactor operating at 100% power, while performing a containment oxygen (O2) concentration surveillance, it was discovered that containment torus O2 concentration did not meet the technical specification requirement. The cause of the event was inadequate procedural guidance which resulted in purging the torus with an insufficient nitrogen purge flowrate. Corrective actions consisted of checking for air in-leakage, obtaining grab samples, confirming the actual O2 concentration, and initiating a normal reactor shutdown in accordance with plant technical specifications (TS). Prior to completion of the shutdown, the containment was successfully inerted and the plant was returned to rated power operation. There was no increased threat to the health and safety of the public because the overall containment O2 concentration, considering the combination of both drywell and torus volumes, has been estimated as 4.6 %. This concentration would have eliminated any H2 combustion. Additionally, the time operated with the deficient inerted condition was very short (approximately 4 days), and there was no coolant leak during that time which would have required the torus pressure suppression chamber to perform its function.
2711997012 | Vermont Yankee | 05/02/1997 | 11/21/1997 | 9712020109 | <strong>Residual Heat Removal Service Water Flow Could Be Potentially Less than the Design Basis Flow due to Instrument Inaccuracies Not Being Included in Calibration and Operational Procedures</strong><br /><i>Abstract:&nbsp;</i>On 5/2/97 at 1300 hours, during the AE inspection preparation it was determined that the Residual Heat Removal (RHR) Service Water (SW) flow rate during a LOCA could potentially have been below the required design flow. The design flow of the RHRSW heat exchanger and required flow for a LOCA is 2700 Gallons Per Minute (GPM). Instrument accuracy for flow indication is +/- 150 GPM, which could have resulted in an actual RHRSW flow rate as low as 2550 GPM. This condition was evaluated and it was determined that the RHRSW system can meet its design cooling capacity at existing flow rates, provided that the plant is only operated if river water temperature is equal to or less than 70 degrees F. Additionally, if flow for the RHRSW system was 2850 GPM, with instrument inaccuracy in the conservative direction, it was determined that the remaining loads would still have the required amount of cooling with the river water temperature restriction in use. The root cause of this event is a management decision to accept existing setpoints as adequate, and only expend resources for applying standard setpoint methodologies to Environmentally Qualified (EQ) instruments and new instruments installed under a design change. Immediate corrective actions included the initiation of an Event Report to document the concern, notification of the Nuclear Regulatory Commission (NRC), the initiation of a Basis for Maintaining Operation (BMO) document and the establishment of a river water temperature administrative limit of 70 degrees F and a mandatory read and sign BMO training form for the Operations on-shift crews. Subsequent analysis has shown that the administrative river water temperature limit of 70 degrees F is unnecessary. The RHRSW System is capable of maintaining Torus temperatures less than 176 degrees F with a river temperature of 85 degrees F. The administrative temperature limit has been returned to the original 85 degrees F.
2711997013 | Vermont Yankee | 06/24/1997 | 07/21/1997 | 9707250082 | <strong>Unknown Cause(s) Result In Extended Actuation Times For Three-Out-Of-Four Safety Relief Valves.</strong><br /><i>Abstract:&nbsp;</i>On 06/24/97 a contracted test facility determined that a VY Main Steam (MS) System safety-relief valve (SRV) did not meet procedural requirements for valve actuation time. To meet In-Service Testing (IST), Final Safety Analysis, and Technical Specification requirements, VY removes its four SRV's each refueling outage, replaces them with properly tested valves, and bench-tests the removed valves. Testing of the three remaining relief valves (completed on 06/26) determined that, of the four valves removed and tested, three failed to meet valve actuation time requirements. Each failed valve actuated at the appropriate setpoint (pilot valve actuation), but an unknown cause(s) resulted in extended main valve actuation delay times. Investigations by both the contracted test facility and the valve manufacturer have failed to determine a cause. As the faulty valves are not installed in the plant, and there appears to be no industry or VY history of chronic problems with extended SRV delay times, this appears to be an isolated event and no formal corrective actions are planned at this time. The Nuclear System Pressure Relief System (NSPRS) as-found condition was compared to the system performance credited in the station analyses. A qualitative assessment of this comparison led to the determination that the conclusions of the subject analyses remained intact. Additionally, the as-found time delays would not have significantly affected the system's automatic depressurization or manual actuation functions, the NSPRS safety design bases would have been met. Therefore this event is not considered to have presented an increased risk to the health and safety of the public.
2711997014 | Vermont Yankee | 08/07/1997 | 03/19/1998 | 9803270022 | <strong>Lack of understanding of plant licensing and design bases results in an inadequate response to industry operating experience which allowed resumption of plant operations inconsistent with its design bases.</strong><br /><i>Abstract:&nbsp;</i>On 08/07/97, while preparing to update the docket relative to Vermont Yankee (VY) LER 97-05, it was determined that VY had inappropriately dispositioned the issue, which led to an event recurrence. On 03/24/97 VY had determined that the potential existed to overpressurize the Standby Gas Treatment System should a large break LOCA occur during primary containment inerting and deinerting operations at power. This could potentially challenge secondary containment. The potential for overpressurization existed because VY Technical Specifications (TS) and containment operating procedures allow inerting or deinerting the primary containment while at power. VY established controls prohibiting the cited system alignment. VY, after consultation with the NSSS Supplier, concluded that postulating the LOCA coincident with purge and vent operations at power was not consistent with its licensing bases due to its extremely low probability. Therefore, on 04/24/97 standard purge and vent operations were resumed. Following the resumption of normal purge and vent activities, VY management was made aware of licensing correspondence which commits VY to meeting 10CFR100 limits under the postulated conditions. This commitment had not been previously considered by the Plant Operations Review Committee due to a lack of understanding of plant licensing bases on the part of the personnel conducting the original investigation. Administrative controls prohibiting the vulnerable configuration were established. Because VY TS's only allow inerting and deinerting while in cold shutdown (or within 24 hours of a startup/shutdown) and the LOCA must occur coincident with inerting or deinerting activities, the probability of the SBGTS overpressurization is exceedingly low. Therefore this event did not present a significant increase in risk to the public.
2711997015 | Vermont Yankee | 08/27/1997 | 09/24/1997 | 9710010285 | <strong>Instrument Check not Completed in Accordance with Technical Specifications due to a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 8/27/97 during a project comparison between Vermont Yankee's current Technical Specifications (TS) and the Improved Technical Specifications, it was discovered that the required instrument check for the Recirculation Pump Trip (RPT) System is not performed in accordance with the TS definition of an instrument check. The Reactor High Pressure trip instrument loops provide no local or remote indication to facilitate an instrument check and the Reactor Low-Low Water Level trip only provides indication for two of the four level transmitters. The instrumentation loops that are currently used for the RPT were installed under an Engineering Design Change that was completed during the 1995 Refueling Outage. Prior to this installation, the previously installed instrumentation provided appropriate indication that allowed an instrument check. The root cause of this event is a personnel error in that there was a failure to identify all system requirements during the development of the design change that added new pressure and level instrumentation to the RPT System. Immediate corrective action included the submission of a plant event report to provide further investigation and a review by Design Engineering to determine if any amplifying information was available on the instrument check requirements. Further, the Electrical and Controls (E&C) Department began checking the transmitter's output, on a daily basis, by measuring and comparing their signals. Although the instrument checks could not have been previously completed, with the exception of two of the level transmitters, the subject pressure and level loop equipment were functionally tested and calibrated per TS. Since instrument checks on the transmitter output were proper, and Vermont Yankee has not experienced any events that required the use of the RPT system, there was no threat to the health and safety of the public from this event.
2711997016 | Vermont Yankee | 08/28/1997 | 09/24/1997 | 9710010300 | <strong>Missed Surveillance due to a Personnel Error as a result of an Inadequate Procedure Versus Technical Specifications Surveillance Evaluation</strong><br /><i>Abstract:&nbsp;</i>Between 8/28/97 and 9/10/97 as a result of a review conducted in accordance with Generic Letter 96-01, it was determined that a number of relay contacts in safety related logic circuits, the Primary Containment Isolation System (PCIS), the Automatic Depressurization System (ADS), the High Pressure Coolant Injection (HPCI) System and the Reactor Core Isolation Cooling (RCIC) System were not tested in accordance with Vermont Yankee's "Logic System Functional Test Methodology" or the Technical Specification (TS) definition of a Logic System Functional Test. This methodology requires individual relay contacts to be tested following a change of state to ensure that all components are operable per the design intent. Previous relay testing was conducted during Logic System Functional Testing, although the specific contacts in question were not tested in accordance with the approved methodology. The apparent cause of these events is attributable to a personnel error in that there was an inadequate, procedure versus TS surveillance requirement evaluation. A contributing cause was the misconception that the previous test method provided an adequate test without physical confirmation of contact movement. Corrective actions included immediate testing of the ADS, HPCI and RCIC contacts, closing and tagging the PCIS valves affected by the subject logic to ensure that they were not operated until the associated contacts were tested, and development of a test method to test contact position. Although the contacts of the subject logic circuits were not tested in accordance with the current testing methodology, the logic circuit relays were tested during Logic System Functional Testing. These relays are used throughout the industry, are safety class components, and have proven to be highly reliable. Therefore, there is reasonable assurance that the relays would operate as designed and would not cause any threat to the public health and safety.
2711997017 | Vermont Yankee | 09/02/1997 | 10/02/1997 | 9710080230 | <strong>An Equipment Malfunction Remaining Undetected by the Operating Crew Results in Plants in Operation in Excess of Rated Thermal Power</strong><br /><i>Abstract:&nbsp;</i>On 09/02/97 it was discovered that a malfunction in the plant process computer (PPC) data acquisition system (DAS) had resulted in reactor feedwater flow being under reported by about 0.75%. This resulted in thermal power, as determined by the PPC, indicating about 0.75% lower than it would otherwise have displayed. Routine control rod manipulations, preceded by slightly lowering reactor power via a reduction in reactor recirculation flow, effectively masked the error introduced by the PPC DAS. Although the operating crew recognized that the power reduction seemed slightly greater than anticipated for the recirculation flow adjustment, it was believed that the adjustment made had been slightly greater than intended. Following the control rod manipulation, core power was raised to approximately 100% as indicated by the PPC. The following day, a reactor engineer, while performing daily status checks, noted discrepancies meriting inquiry into core power indications. Power was reduced to approximately 98% as the investigation continued. That investigation discovered the DAS problem and the resultant power indication anomaly. Core thermal power as indicated by manual calculation was determined to be approximately 0.75% higher than indicated by the PPC. Thus indicating that thermal power, had been raised above the limit expressed in VY license condition 3.A following control rod manipulations. Plant processes are being reviewed to determine if there are opportunities available to enhance the operating crew's ability to detect subtle failures such as this. Because the PPC provides no safety function, and the safety significant protection systems were unaffected by the DAS perturbation, and the power level achieved during this event was fully bounded by plant analyses, this event did not present an increased threat to public health or safety.
2711997018 | Vermont Yankee | 09/18/1997 | 10/15/1997 | 9710220028 | <strong>Four Unused One Inch Containment Isolation Valves were Found Out of Position due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On 9/18/97 with the plant at 100% power while investigating the location of a spare drywell penetration connection, it was determined that four unused one-inch primary containment isolation valves were out of position. The valves were found in the open position and are required to be closed in accordance with the applicable valve lineup and Technical Specification requirements. These valves are on instrument connections that are no longer in use and are in series with an excess flow check valve, a closed instrument rack isolation valve, and a pipe cap such that primary containment was not breached. Immediate corrective actions included a verification of required valve position using the approved valve lineup list and applicable blueprint, and subsequent re-positioning the valves to the required closed position. The root cause investigation of this event is in progress. The Apparent Cause of this event is an inadequate reactor vessel hydrostatic test procedure that failed to specify a restoration valve lineup following a reactor vessel hydrostatic test. If the root cause investigation provides a cause different than the stated apparent cause, a supplemental License Event Report will be submitted. This event is not considered to have presented any threat to the public health and safety.
2711997019 | Vermont Yankee | 09/18/1997 | 10/16/1997 | 9710220034 | <strong>An Inadequate Hydraulic Calculation Performed in Support of a 1982 Fire Protection Sprinkler System Modification Allowed Degradation of Redundant Emergency Diesel Generator Manual Sprinkler Sub-systems</strong><br /><i>Abstract:&nbsp;</i>On 09/18/97, while evaluating Fire Suppression System code compliance, Vermont Yankee found that a change made to the fire suppression system had degraded the system such that required performance capabilities could not be demonstrated. The affected sprinkler system provides fire suppression capability in the Emergency Diesel Generator rooms (EDGRs). A 1982 modification rendered the system incapable of delivering 0.3 gpm per square foot of the protected area, a water density communicated to the NRC staff via a 1978 letter. While the water delivery capability of the current system has been assessed as comparable to systems designed for "ordinary [fire] hazards," the category ascribed to environments like electronic plants, automobile repair garages and paper mills; the 0.3 gpm cited implies that the system was to be treated as an "extra hazard" area. The system was therefore declared inoperable and compensatory measures were implemented per plant Technical Specifications (TS). Because TS require compensatory measures be implemented when the subject sub-systems are inoperable, and they have been in the described condition since 1982 this event is being reported as a condition prohibited by TS. As this condition was discovered while performing corrective actions to address similar conditions for another event, it is expected that those same corrective actions, combined with addressing the disparity between this system's current delivery capability and the committed flows, will adequately address this event. Because the fire suppression systems have no nuclear safety functions, and the EDGR sprinkler systems have consistently possessed significant fire suppression capabilities, this event did not pose an increased threat to the health and safety of the public.
2711997020 | Vermont Yankee | 10/30/1997 | 02/09/1998 | 9803170189 | <strong>An Inadequate Technical Justification for a Proposed Change to Plant Technical Specification Results in Operation Outside of the Bounds of Current Analyses Relative to Suppression Pool Temperature During LOCA.</strong><br /><i>Abstract:&nbsp;</i>On 10/30/97, while responding to concerns noted during an NRC architect engineer inspection of the facility, VY concluded that the plant having operated with a torus temperature greater than the initial temperature assumed in current analyses may have allowed conditions to occur which were subject to the reporting requirements of 10CFR50.72 and 10CFR50.73. No 10CFR50 Appendix B calculation exists which bounds the full range of suppression pool (torus) temperatures permitted by plant Technical Specifications (TS). The current containment response analysis assumes an initial pool temperature of 90 degrees Fahrenheit (F), while TS allows unlimited plant operations with torus temperatures as high as 100 F. Upon noting the lack of detail in the formal analysis used to justify the TS limit of 100 F, administrative limits were established prohibiting normal plant operation with torus temperature > 90 F. Preliminary calculations and evaluations performed as corrective actions for this event have led to a further reduction in allowed torus temperature (80 F maximum). The cause of the event was the inappropriate assignment of a technical review to a single work group which lacked the breadth of knowledge needed to address all of the implications of the change. Other causes included inadequate self-checking and a lack of procedural guidance. Procedures have since been improved, and VY has trained on the lessons learned from the event. VY is currently performing a reconstitution of the licensing basis for the maximum suppression pool temperature allowed. Because engineering evaluations performed since the discovery of the disparity indicate that conditions achieved would not have undermined the functionality of safety systems, this event did not present an increased risk to public health and safety.
2711997021 | Vermont Yankee | 10/09/1997 | 11/05/1997 | 9711170110 | <strong>Division SI Powered and SII Powered Cables Located in Same Manhole Contrary to FSAR Statement and Vermont Yankee Separation Criteria due to Inadequate Original Design Specifications</strong><br /><i>Abstract:&nbsp;</i>On 10/09/97, while operating at 100% power, it was determined that energized cables from one divisional raceway system traverse both Division SI and Division SII equipment. This is contrary to the Final Safety Analysis Report (FSAR) section 8.4.6.3 and the Vermont Yankee Cable Separation Specification VYS-027. The non-conforming cables supply the alternate feed from either Motor Control Center (MCC) 8C or 9C to Cooling Tower Fan CT 2-1 which is a part of Vermont Yankees Alternate Cooling System (ACS). The fan is normally fed from a Start-up transformer bus; however, if a loss of off-site power were to occur, the fan, which is fed from MCC SC and 9C, would ultimately be powered by the Emergency Diesel Generators (EDG). The non-conforming cables run in separate wireways from manhole 27, where they are spliced together, until they enter the wireway in the MCC's and consequently violate the separation criteria. The MCC breakers for the alternate supply, one normally open and the other normally closed, are key interlocked to prevent the closing of both breakers at the same time. The Apparent Cause of this event was due to the use of inadequate design specifications and installation procedures during initial plant construction. Immediate corrective action was taken to open the normally closed breaker and tag both breakers open. With the breakers open, the intent of the separation criteria is met. Although the original configuration violated the separation criteria, the alternate supply breakers to CT 2-1 would have provided the necessary breaker trip function to isolate any fault prior to the fault affecting either EDG. Additionally, operators have approximately two hours to establish the ACS following a loss of Service Water. This provides sufficient time to close the breaker for the fan. There was no threat to the health and safety of the public from this event.
2711997022 | Vermont Yankee | 11/15/1997 | 12/11/1997 | 9712170398 | <strong>Inadvertent Primary Containment Isolation System Actuation Due To a Spurious Spike on A Reactor Building Vent Radiation Monitor - Repeat Event.</strong><br /><i>Abstract:&nbsp;</i>At 0141 hours on 11/15/97, with the reactor operating at 97% of rated power, a Standby Gas Treatment System (SBGTS) initiation and Reactor Building Ventilation isolation occurred concurrent with a Primary Containment Isolation System (PCIS) Group III isolation. These isolations and the initiation of SBGTS were caused by a spike on the "B" Reactor Building Vent Radiation Monitor. The apparent cause of the event was a spurious electronic noise signal of a magnitude greater than the trip setpoint of the radiation monitor. Corrective actions included conducting a radiological survey in the area of the radiation monitor detector to determine if a valid signal had been received, and troubleshooting the radiation monitor circuitry. There were no adverse implications to plant equipment or to the health and safety of the public because the isolation of the containment purge, vent (EIIS = VB), air dilution and monitoring (EIIS = IK) systems, and SBGTS initiation are conservative system actuations with respect to protection of the public.
2711997023 | Vermont Yankee | 11/25/1997 | 12/23/1997 | 9801050010 | <strong>A Component Failure In The Main Generator Protection Circuitry Results In A Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1997 a plant trip occurred at Vermont Yankee. The cause of the trip was the failure of a protective device in the Main Generator protective circuitry. Errors made in the switchyard motor operated disconnect operating sequence, performed in support of transmission grid maintenance activities, resulted in a perturbation in the 345 kV transmission system, which in turn caused an initiation of an automatic reduction in steam admitted to the Main Generator turbine. The ramped power reduction should not have exceeded the approximate 0.1 seconds of the perturbation, resulting in minimal impact upon plant operation. However, a comparator/relay failure in the generator protection circuit prevented the circuit from responding to the resumption of normal comparator inputs, causing the automatic generator load reduction to continue. The operating crew performed the actions prescribed by plant procedures in response to the runback. The adequacy of those procedures are being verified. The automatic reduction in steam to the turbine results in a marked reduction in feedwater heating, and a resulting positive reactivity addition, ultimately leading to a flow-biased scram. The comparator initiated runback has since been removed from the circuit under the VY temporary modification process. Because the conditions which occurred in this event were bounded by the current analysis of record, and the analysis of record demonstrates that all safety design limits for abnormal operational transients were met, this event presented no increased risk to public health or safety.
2711997024 | Vermont Yankee | 12/16/1997 | 04/23/1998 | 9804300136 | <strong>Inadequate Analysis And Guidance Allows The Failure Of A Vertical Support Column Repair In The Plant Cooling Tower Which Rendered The Plant Alternate Cooling System Susceptible To A Seismic Induced Failure.</strong><br /><i>Abstract:&nbsp;</i>On 12/16/97, while performing a routine inspection of cooling tower structural components, VY discovered that a vertical support column in the safety class portion of the cooling tower had failed. The column (a safety class 4"x 4" wooden structural member) had apparently failed in the past and a repair had been completed. The cooling tower material records do not describe any details regarding the repair. The cause for the failed member is a combination of inadequate analysis of, and guidance for, the application of construction techniques for the splicing of vertical support members in repair efforts. The alternate cooling system having been declared inoperable to support the inspection, remained in the inoperable status until the broken column was replaced. During subsequent maintenance efforts a second column was found to be inoperable. It too has been replaced. The appropriate guidance for the application of the splicing technique will be developed. Recently improved cooling tower inspection methodologies will continue. Current VY design requirements for structural loading of the safety class portion of the cooling tower requires that the system be demonstrated capable of performing under the combined effects of design snow loading, maximum cooling water inventory, and a design basis seismic event. Because the structural load combination which must be postulated to preclude the cooling tower's ability to perform as designed is highly unlikely, this event is not considered to have presented a significant increase in risk to public health and safety.
2721997001 | Salem 1, Salem 2 | 01/17/1997 | 12/24/1998 | 9901060113 | <strong>Failure To Perform Technical Specifications Surveillance Of Component Cooling Water System Check Valves</strong><br /><i>Abstract:&nbsp;</i>This supplemental LER reports a TS non-compliance identified during a review of the Salem Inservice Test program (IST). On February 15, 1997 a review of the Salem IST program determined that the IST surveillance of Component Cooling Water system check valves CC195 and CC210 was not performed as required. CC195 and CC210, which serve as a part of the ASME Class 3 boundary, were exempted from IST program testing in 1991 under the provision that they remain isolated by closure of manual valves CC145 and CC146. Contrary to the requirements of the IST program, changes were made to the required positions of CC145 and CC146 that permitted at least one of these two manual isolation valves to remain open during plant operation. Because these changes were made without consideration of IST program requirements, reverse flow testing of CC195 and CC210 to verify the integrity of the ASME Class 3 boundary was not performed. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications. Specifically, the requirements of TS 4.0.5 regarding in-service inspection and testing of ASME Code Class 1, 2, and 3 components. The cause of this event was a lack of programmatic interface between the IST program personnel and Operations department personnel responsible for programs used to control system configuration. To prevent recurrence, procedural controls will be implemented to inform IST program personnel of changes to normal valve positions before those changes are implemented so that adjustments to the IST program can be made when warranted to comply with TS 4.0.5.
2721997002 | Salem 1, Salem 2 | 02/10/1997 | 03/12/1997 | 9703180208 | <strong>Chilled Water System Single Failure Vulnerabilities</strong><br /><i>Abstract:&nbsp;</i>Recent re-evaluation of the Chilled Water System has determined that to provide the design support function and assume a single failure, three chillers and two chilled water pumps are required to be operable for each Salem unit. With less than this configuration, the Chilled Water System may not be able to perform its design support function and withstand a single failure. In the past, the plant has operated with less than three chillers or two chilled water pumps. <br /><br /> The cause of this occurrence is that at the time of the original plant design, the ability to withstand a single failure with a component out of service for maintenance, was not recognized as a design input. Because the system did not have specific Technical Specifications associated with it, the impact of having components out of service was not recognized. Corrective actions include submission of a License Change request and an Operability Determination addressing the actions to be taken if less than three chillers or two chilled water pumps are operable. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B), any condition that resulted in the nuclear plant being outside the design basis of the plant.
2721997003 | Salem 1, Salem 2 | 01/31/1997 | 03/03/1997 | 9703110126 | <strong>Non-Conservative Single Failure Assumption - Postulated Loss of Service Water System</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During the development of a Failure Modes and Effects Analysis, in support of NRC Generic Letter 96-06, 'Assurance of Equipment Operability and Containment' for the Service Water System (SWS), a SWS alignment that is more hydraulically challenging than previously analyzed was discovered. The previous alignment assumed, during a Loss of Coolant Accident, a single failure of the Component Cooling Water (CCW) heat exchanger valve, and resulted in three SW pumps supplying flow to two full open CCW Heat Exchangers, five Component Fan Cooling Units (CFCU), and three Emergency Diesel Generators (EDGs). The new more limiting alignment assumes a single failure of a 125 Vdc channel, and results in two SWS pumps being in a runout condition, that could cause insufficient SWS flow rates. The cause of this occurrence was the hydraulic impact of a modification was not considered. Corrective actions include modifications to restore the system hydraulics and reviews of the modification process. This LER is being submitted pursuant to 10CFR50.73.(a)(2)(ii), any condition that was outside the design bases of the plant.
2721997004 | Salem 1, Salem 2 | 02/21/1997 | 03/21/1997 | 9703280229 | <strong>Inadequate Surveillance Testing of Molded Case Circuit Breakers.</strong><br /><i>Abstract:&nbsp;</i>During NRC inspection activities, an inadequate performance of a surveillance requirement was identified. Technical Specification (TS) Surveillance Requirement 4.8.3.1.a.2 requires that ten percent of each type of all required containment penetration conductor overcurrent protection devices (e.g., circuit breakers) required to provide thermal protection of a penetration be verified operable every 18 months. In addition, TS 4.8.3.1.b requires each required overcurrent protection device be inspected and have the manufacturer's preventative maintenance performed once per 60 months. Contrary to these requirements an adequate verification of the required overcurrent protection devices was not performed. Certain elements of the protective devices were not verified, because an acceptance criterion was not specified in the procedure. The protection devices were adequately tested, and the test procedures were clarified to better define the TS requirements. <br /><br /> This event is being submitted pursuant to 10 CFR 50.73(2)(i)(B), any operation or condition prohibited by TS.
2721997005 | Salem 1, Salem 2 | 06/25/1997 | 07/25/1997 | 9708040138 | <strong>Radioactive Liquid Effluent Samples Not Analyzed Within Required Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>During the review of a Technical Specification (TS) surveillance work order on June 26, 1997, for the performance of gross alpha analysis on a composite liquid sample in accordance with TS 3.11.1.1 Table 4.11-1, Operations Department personnel questioned Chemistry personnel on whether the completion date of the analysis was meeting the surveillance requirements of the TS. Subsequently, a determination was made that the required surveillance interval for the analysis of the composite sample was not being satisfied. <br /><br /> The cause of this event is attributed to an incorrect interpretation of the TS surveillance requirements by Chemistry personnel. A review of similar TS surveillances was performed which identified a similar reportable occurrence for quarterly liquid composite sampling analysis for Sr-89, Sr-90 and Fe-55, monthly gaseous composite sample analysis for gross alpha and quarterly gaseous composite sample analysis for Sr-89, and Sr-90. Surveillance testing work order completion dates will be or have been revised to ensure compliance with the TS surveillance interval and training will be provided to the Chemistry Supervisors. <br /><br /> This event is being reported in accordance with 10 CFR 50.73 (a) (2) (i) (B), any condition prohibited by the plant's Technical Specifications.
2721997006 | Salem 1, Salem 2 | 03/12/1997 | 04/08/1997 | 9704150046 | <strong>Inadequate Technical Specification Required Surveillance Test for Pressurizer Overpressure Protection System</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1997, a review of the Salem Unit 2 Pressurizer Overpressure Protection System (POPS) logic determined that relays that are part of the logic for opening the Power Operated Relief Valves (PORV) were not tested and calibrated as required by Technical Specifications (TS) 4.4.10.3.1.a and 4.4.10.3.1.b. The POPS Channel Functional Test and Channel Calibration have been inadequate since at least 1985. A new procedure has been written and successfully completed to verify that the omitted relays actuate the PORV for Salem Unit 2. Testing is not required on Salem Unit 1 in the present defueled condition. Salem Unit 1 POPS will be adequately tested prior to being required. <br /><br /> The cause of this occurrence is attributed to a lack of adequate controls for the development and maintenance of Technical Specification surveillance procedures. Corrective actions include revision of procedures, initiation of new procedures and continuation of the TSSIP project. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721997007 | Salem 1 | 06/30/1997 | 07/29/1997 | 9708060039 | <strong>Failure to Perform Independent Verification for Radioactive Release Lineup Required by Technical Specification 3.3.3.8</strong><br /><i>Abstract:&nbsp;</i>On 6/30/97, radioactive liquid waste was released from the 11 Chemical and Volume Control System Monitoring Tank without performing an independent verification for a portion of the discharge line valving as required by Technical Specification 3.3.3.8. The independent verification was required since the Waste Disposal System Liquid Effluent Radiation Monitor (1R18) was inoperable. <br /><br /> The Control Room Supervisor (CRS) inadvertently marked a procedure step requiring independent verification of a portion of the discharge lineup as "N/A" and as a result the required independent verification was not performed. The root cause of this event was personnel error as a result of inattention to detail and lack of self verification by the CRS. The CRS was held accountable for his actions and the Operations Manager will conduct detailed discussions of this event with the operating crews during Licensed operator training, emphasizing Management expectations on the use of self-verification and minimization of distractions. <br /><br /> This event is being reported in accordance with 10 CFR 50.73 (a) (2) (i) (B), any condition prohibited by the plant's Technical Specifications.
2721997008 | Salem 1, Salem 2 | 03/21/1997 | 04/21/1997 | 9704290077 | <strong>Inadequate Surveillance Testing of PORV Accumulators and Check Valves</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1997 Station personnel determined that the testing performed on the Power Operated Relief Valve (PORV) accumulator solenoid valves and check valves did not provide full stroke testing as required by Technical Specification 4.4.3.1.b for Unit 2 and 4.4.5.1.b for Unit 1. This condition has existed since implementation of Technical Specification amendment 150/130 which was approved on April 7, 1994. Further review determined that testing pursuant to Specification 4.0.5 was not adequately performed for these valves since at least 1990 when the valves were required to be added to the IST program in accordance with Generic Letter 90-06. <br /><br /> The cause of this occurrence is attributed to a lack of adequate controls for the development and maintenance of Technical Specification surveillance procedures. This weakness was previously identified in LER 311195-008-00. Further, the inadequate IST testing was caused by personnel error in the classification of the components. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications
2721997009 | Salem 1, Salem 2 | 04/18/1997 | 06/27/1997 | 9707090070 | <strong>Past Operation of the Emergency Core Cooling System Outside of Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>As a result of an NRC Special Inspection 311/97-11, several issues concerning past operation of the Salem Emergency Core Cooling System were identified. On April 18, 1997, a determination was made that prior to March 1996, Salem Generating Station was operated in the past in a condition that was outside the design basis of the plant due to the following reasons: 1) excessive Residual Heat Removal (RHR) system flows during the recirculation mode of Loss of Coolant Accident (LOCA) mitigation, and 2) the inability to ensure the successful completion of the switchover from the injection mode of LOCA mitigation to the recirculation mode without the possibility of interrupting ECCS pump flow to the core since the installation of the semiautomatic switchover modification in 1989. <br /><br /> The root cause evaluation for the introduction of the USQs into the design and licensing basis identified the following causes: 1) failure to address all accident scenarios that could affect the assumptions made, and 2) failure to adequately review the licensing and design bases for the semi-automatic swapover. <br /><br /> These issues are reportable under 10CFR50.73(a)(2)(ii)(B) and 10CFR50.73(a)(2)(v).
2721997010 | Salem 1, Salem 2 | 12/19/1994 | 09/28/1998 | 9810070166 | <strong>Past Operation of the Emergency Diesel Generators in a degraded but operable condition.</strong><br /><i>Abstract:&nbsp;</i>During performance of 18-month surveillance testing of the Emergency Diesel Generators (EDGs) in December of 1994, the output breaker for the 2C EDG closed prior to the generator achieving 90% of nominal bus voltage. Public Service Electric & Gas (PSE&G) investigation into this event concluded that the cause of the 2C EDG breaker closing early is attributed to an improperly set voltage-sensing relay. The slow generator voltage rise was due to a broken voltage regulator. PSE&G also concluded that the rate of rise of the EDG voltage during the test provided reasonable assurance that the EDG would have been able to carry the design basis loads without stalling. Thus the equipment required to mitigate the consequences of a DBA accident would have performed their safety function. Corrective actions taken were installing new EDG output breaker voltage closing permissive relays and the replacement of the 2C EDG voltage regulator. <br /><br /> This event is being reported in a voluntary basis.
2721997011 | Salem 1, Salem 2 | 11/19/1997 | 12/19/1997 | 9801050381 | <strong>Failure to Test Isolation of Steam Generator Blowdown and Sampling System on the Automatic Start of the Auxiliary Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1997, the Salem Technical Specification Surveillance Improvement Project (TSSIP) identified that the Steam Generator blowdown isolation valves (GB4 valves) and the Steam Generator blowdown sampling isolation valves (SS94 valves) were not being functionally tested to verify that these valves would isolate on an automatic start of the Auxiliary Feedwater (AFW) pumps. This concern was identified following a review of the applicable drawings and surveillance test procedures in accordance with the guidelines of NRC Generic Letter (GL) 96-01. Isolation of these valves is assumed to occur in the evaluation of the Loss of Normal Feedwater accident. <br /><br /> The cause of this occurrence has been attributed to the inadequate incorporation of design basis accident mitigation features into plant testing procedures. The evaluation of surveillance test procedures in accordance with the guidelines of GL 96-01 is continuing and will be completed by December 31, 1997. <br /><br /> This event is reportable under 10 CFR 50.73(a)(2)(ii)(A) for the past operation of Salem in an unanalyzed condition that significantly compromised plant safety.
2721997012 | Salem 1, Salem 2 | 07/09/1997 | 08/12/1997 | 9708190034 | <strong>Missed Technical Specification Surveillance For Average Temperature and Main Turbine First Stage Pressure (PT505/506) Channel Check</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1997 a review of the Salem Unit 2 operating logs identified that channel checks of the Loop Average Temperature channels had not been performed as required by Technical Specifications 4.0.4 and 4.3.2.1.1. In addition, a similar review performed on July 17, 1997 identified that channel checks of the Turbine First Stage Pressure channels had not been performed as required by Technical Specifications 4.0.4 and 4.3.2.1.1. <br /><br /> This occurrence is attributed to misjudgment by the Control Room Operators and Supervisors caused by misinterpretation of information provided in the operating logs. Corrective actions include changes to the operating logs and communication of requirements for the performance of Technical Specification channel checks. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721997013 | Salem 1, Salem 2 | 07/02/1997 | 12/19/1997 | 9801020108 | <strong>Failure To Meet Technical Specification 3.8.1.1 Action B</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1997, the 2A Emergency Diesel Generator (EDG) was tested in accordance with surveillance test procedure, S2.OP-ST.DG-0001, 2A Diesel Generator Surveillance Test. The test was completed satisfactorily, and the EDG was declared operable at 0545. However, the test equipment was intentionally left in place to support additional EDG testing scheduled for later that day. The second test did not occur for approximately 9 hours later, and during this period the 2A EDG was thought to be in an Operable status. On October, 2, 1997, an engineering evaluation determined that the EDG should have been declared inoperable with the test instrumentation connected. <br /><br /> The reason for this occurrence is attributed to personnel error. <br /><br /> Corrective actions taken included; appropriate disciplinary action was taken with involved personnel, procedures were changed, the test equipment was removed. <br /><br /> The failure to perform this surveillance is reportable in accordance with 10CFR50.73(a)(2)(i)(B).
2751997001 | Diablo Canyon 1, Diablo Canyon 2 | 01/31/1997 | 03/03/1997 | 9703110082 | <strong>The Component Cooling Water System Has Operated With Procedural Guidance That Permitted Operation in a Condition Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 31, 1997, at 1130 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the component cooling water (CCW) and auxiliary saltwater (ASW) systems have operated with procedural guidance that permitted, following a loss of coolant accident and the loss of power on either Vital Bus F or G, operation in a condition outside the design basis of the plant. A 1-hour, non-emergency report was made to the NRC at 1220 PST, in accordance with 10 CFR 50.72 (b)(1)(ii)(B). <br /><br /> The cause of the event is unknown, but it occurred during the original design of the plant. The cause is attributed to incomplete or incorrect application of the single failure criteria design requirement to ASW and CCW systems operation during post-accident split train, hot leg recirculation. <br /><br /> Emergency Operating Procedure E-1.4, "Transfer To Hot Leg Recirculation," has been revised to no longer require immediate separation of the ASW and CCW systems into separate trains after the transfer to hot leg recirculation. The decision to separate has been transferred to the Technical Support Center, where a decision will be made after an evaluation of plant conditions. This action precludes placing the plant into a configuration where this vulnerability would be created without a thorough assessment being performed.
2751997002 | Diablo Canyon 1, Diablo Canyon 2 | 02/26/1997 | 03/28/1997 | 9704080091 | <strong>Refueling Water Storage Tank Outside Design Basis Due to Insufficient Water Margin At Completion of Switchover to Cold Leg Recirculation Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1997, at 1530 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined previous revisions of Emergency Operating Procedure (EOP) E-1.3, 'Transfer to Cold Leg Recirculation,' could have resulted in the plant being outside its licensing basis. At the completion of switchover to cold leg recirculation, the procedure would have left a remaining usable volume in the refueling water storage tank (RWST) less than the licensing basis margin of 32,500 gallons. A 1-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B) as a condition outside the design basis of the plant. <br /><br /> This event was discovered by PG&E engineering personnel during the review of Final Safety Analysis Report (FSAR) Update Table 6.3-5, following questions by NRC resident inspectors. <br /><br /> The root cause of this event was personnel error (cognitive). Personnel who prepared the original FSAR made nonconservative assumptions in calculating pump flow rates for the sequence of events following a loss-of-coolant-accident. <br /><br /> PG&E has approved a change request for the FSAR Update and has revised EOP E-1.3 and Administrative Procedure OP1.DC11, "Conduct of Operations - Abnormal Plant Conditions." These corrective actions will provide assurance of maintaining the licensing basis RWST volume margin.
2751997003 | Diablo Canyon 1, Diablo Canyon 2 | 03/05/1997 | 04/04/1997 | 9704150233 | <strong>Reactor Vessel Level Instrumentation System Outside Design Basis Due to Personnel Error and Inadequate Vendor Communication</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1997, at 1302 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the reactor vessel level instrumentation systems (RVLIS) for both units were inoperable due to failure to perform normalization of input parameters following each refueling outage. This vendor basis requirement had not been previously identified or performed; therefore, the system has operated outside design basis requirements. A 1-hour, non-emergency report was made to the NRC at 1316 PST, in accordance with 10 CFR 50.72 (b)(1)(ii)(B). <br /><br /> On March 5, 1997, following performance of the revised surveillance test procedure for RVLIS dynamic range indication, Trains A and B were returned to operable status. <br /><br /> The cause of this event was utility personnel error, knowledge exceeded, and inadequate vendor communication. The RVLIS System Manual did not provide clear documentation of required periodic normalization of RVLIS dynamic range indication to assure continued operability. <br /><br /> Corrective actions include a review of instrumentation and control systems that were installed late in the construction period that may not have had completed vendor manual information. The systems identified that require review are the core exit temperature monitoring system, the subcooled margin monitor, and anticipated transient without scram system. Since current design processes and criteria preclude recurrence of similar events, PG&E determined that no additional corrective actions are necessary.
2751997004 | Diablo Canyon 1 | 02/27/1997 | 05/20/1997 | ML09153019 | <strong>Technical Specification 3.7.1.2, Not Met Due to Paint Applied to Auxiliary Feedwater Pump Turbine Governor Linkage Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1997, at approximately 1000 PST, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the limiting condition for operation for Technical Specification 3.7.1.2, "Plant Systems - Auxiliary Feedwater System," was exceeded when turbine-driven Auxiliary Feedwater (AFW) Pump 1-1 was inoperable, due to application of paint to the turbine governor linkage, for greater than 72 hours. On February 28, 1997, at 1136 PST, AFW Pump 1-1 was conservatively declared inoperable when the condition was discovered. The paint was removed from the governor interfaces, the parts were lubricated, and a test run of the pump was completed satisfactorily. At 1659 PST, AFW Pump 1-1 was declared operable. <br /><br /> The cause of this event was personnel error (non-cognitive), in that inadequate work instructions were provided to the PG&E painter. <br /><br /> Corrective actions include. (1) reviewing work controls necessary for working on safety-related equipment with Paint Department personnel, and (2) procedure changes to require providing appropriate levels of guidance to personnel assigned to plan or perform coating activities on safety-related equipment. <br /><br /> This revision is submitted to correct the year listed in Section II.E. from 1996 to 1997.
2751997005 | Diablo Canyon 1, Diablo Canyon 2 | 03/14/1997 | 09/02/1997 | 9709090148 | <strong>Residual Heat Removal System Outside Design Basis Due to Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1997, at 1601 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the residual heat removal (RHR) system had operated in a condition that was outside the design basis of the plant. Administrative controls did not require sufficient refueling water storage tank (RWST) level channels to meet the single active failure criteria and ensure adequate availability of the automatic tripping function for the RHR pumps during transfer to recirculation. A 1-hour, non-emergency report was made to the NRC at 1648 PST, in accordance with 10 CFR 50.72 (b)(1)(ii)(B). The 1-hour, non-emergency report was updated on March 19, 1997, at 1300 PST, to report an additional scenario that could prevent the automatic start or cause the premature tripping of the RHR pumps. <br /><br /> PG&E attributes the inadequate administrative controls to personnel failing to consider the consequences of an RWST level channel failure concurrent with another level channel in test or maintenance on the functioning of the RHR system when a third level channel was added to the design in 1974. <br /><br /> A license amendment request was submitted to include all three RWST channels in the technical specification (TS). Until the TS change is issued, administrative controls have been implemented.
2751997006 | Diablo Canyon 1, Diablo Canyon 2 | 04/28/1997 | 05/28/1997 | 9706040327 | <strong>Reactor Coolant Pump Lube Oil Collection System Outside Design Bases Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1997, at 1627 PDT, with Unit 1 in Mode 6 (Refueling with the reactor vessel defueled) for a refueling outage, and Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that Units 1 and 2 reactor coolant pump (RCP) lube oil collection systems do not meet the requirements of 10 CFR 50.48 and 10 CFR 50, Appendix R. A 1-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B) on April 28, 1997, at 1634 PDT. The 1-hour, non-emergency report identified lift oil pump tubing that was unshielded on Units 1 and 2. It was also determined that some drip pans of the RCP lube oil collection system were missing or damaged on Unit 1. Based on a review of inspections, photographs, and video tapes, the drip pans in Unit 2 were evaluated to be acceptable. <br /><br /> Due to the lack of documentation and the amount of time that has passed since the instrument tubing was routed outside the shielding, a definitive root cause could not be established. The cause is presumed to be personnel error (non-cognitive), knowledge exceeded on the part of the individuals who performed and approved the tubing modification. <br /><br /> Unit 1 RCP lube oil collection system modifications have been completed. Unit 2 modifications will be completed during the next Unit 2 forced outage or refueling outage, whichever occurs first. An inspection of the RCP lube oil collection system will be required coming out of each refueling outage to verify that proper configuration is maintained.
2751997007 | Diablo Canyon 1 | 05/06/1997 | 05/28/1997 | 9706040347 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1997, and May 9, 1997, with Unit 1 in Mode 6 (Refueling), analysis of eddy current testing on Steam Generators (AB)(SG) 1-2 and 1-1, respectively, indicated that greater than 1 percent of the total tubes inspected in each SG were defective. On May 6, 1997, at 1656 PDT, and on May 9, 1997, at 1711 PDT, PG&E made 4-hour, non-emergency reports to the NRC pursuant to 10 CFR 50.72(b)(2)(iii)(C), to report this condition as required by Technical Specification Table 4.4-2. <br /><br /> The majority of the tube defects are attributed to primary water stress corrosion cracking and outer diameter stress corrosion cracking at hot leg tube support plate intersections. <br /><br /> PG&E has plugged all defective tubes identified during the current refueling outage. All defective tubes met the criteria of Regulatory Guide 1.121 for structural integrity at the end of Unit 1, Cycle 8. PG&E maintains a comprehensive program to minimize SG tube degradation.
2751997008 | Diablo Canyon 1, Diablo Canyon 2 | 10/20/1994 | 08/21/1997 | 9708260164 | <strong>Technical Specification 4.5.3.2 Not Met Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>not met on October 20, 1994, during the Unit 2 sixth refueling outage, when the manual discharge valves for the safety injection pumps were closed and caution tagged instead of being closed with a seal applied. Similar alignments may have been performed during other tests in other outages. <br /><br /> The event was caused by inadequate corrective actions for a previous nonconforming condition. The actions did not assure that all affected procedures were changed and maintained to meet the TS requirement. <br /><br /> Information will be provided in a design criteria memorandum that will identify the valves to be sealed and/or controls to be used when TS 4.1.2.3.2, 4.1.2.4.2, and 4.5.3.2 apply. Procedures will be reviewed and revised as necessary to assure compliance with TS surveillance requirements.
2751997009 | Diablo Canyon 1 | 05/08/1997 | 06/06/1997 | 9706110050 | <strong>Unplanned Start and Load of Diesel Generator 1-1 (ESF Actuation) Due to Personnel Error and Inadequate Work Controls</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1997, at 0917 PDT, with Unit 1 shut down and defueled, Diesel Generator (DG) 1-1 started and loaded due to an invalid undervoltage signal after a lead was inappropriately removed from the 27HHB2 relay circuit by maintenance personnel. A 4-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(ii) on May 8, 1997, at 1120 PDT. <br /><br /> On May 8, 1997, at 1328 PDT, DG 1-1 was separated from vital Bus H, shut down, and returned to the automatic mode of operation. <br /><br /> The event was caused by personnel error. Plant personnel did not recognize that the clearance for the 52HH12 cubicle was inadequate to cover the scope of work. After the clearance was authorized, maintenance personnel, as directed by their work package, removed a lead from the 27HHB2 undervoltage relay circuit causing vital Bus H to autotransfer to DG 1-1. <br /><br /> Groups responsible for the work will review the causes, corrective actions, and lessons learned. In addition, component information about the unique component cooling water cubicle design will be developed for use in the work control process. This information will alert those planning and scheduling work that the cubicle also contains electrical components for the bus which may require additional planning, work, and clearance controls.
2751997010 | Diablo Canyon 1 | 05/20/1997 | 11/07/1997 | 9711180080 | <strong>Unplanned Start of Diesel Generator 1-1 Due to a 4160 V Bus H Startup Feeder Phase Potential Transformer Opened Fuse</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1997, at 2131 PDT, with Unit 1 in Mode 5 (Cold Shutdown), Diesel Generator (DG) 1-1 automatically started due to an under voltage relay actuation after a fuse opened on the primary side of the 4160 V Bus H startup feeder potential transformer (PT). This event constitutes an engineered safety features actuation. A 4-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(ii) on May 21, 1997, at 0021 PDT. <br /><br /> On May 20, 1997, at 2144 PDT, DG 1-1 was shut down and returned to the automatic mode of operation. <br /><br /> Based on available evidence, the most likely cause of failure was accumulated fuse element degradation due to current surges on the fuse over the life of the plant. The degraded fuse would have experienced higher element temperatures due to an increased resistance in the fuse element, which over time could cause the fuse to fail. <br /><br /> The maintenance program which monitors fuse continuity will be revised to include resistance checks of fuses. Primary side PT fuses were replaced on the vital busses for the Unit 1 startup and auxiliary transformer feeders. The fuses on the primary side of the Unit 2 startup and auxiliary power potential transformers will be checked and replaced, as necessary. Additionally, operators have reviewed the lessons learned from this event.
2751997011 | Diablo Canyon 1, Diablo Canyon 2 | 07/03/1997 | 12/23/1997 | 9801020066 | <strong>Auxiliary Saltwater Systems Outside Design Basis for Flooding Because of Inadequate Corrective Actions Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1997, at 1608 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, and Unit 2 in Mode 3 (Hot Standby), PG&E determined that inoperable check valves in the drain lines for the auxiliary saltwater pump (ASWP) vaults could cause the auxiliary saltwater systems to be outside their design basis. A 1-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B). <br /><br /> At the request of the NRC Senior Resident Inspector, PG&E reviewed past valve inspection results and determined that the valves were inoperable on a number of occasions. <br /><br /> This review also identified that, on August 9, 1991, with Units 1 and 2 in Mode 1 at 100 percent power, PG&E failed to report that Technical Specification 3.7.4.1 was not met for approximately 24 hours when the check valves were concurrently removed from both ASWP vault drain lines on Unit 1 for inspection and maintenance. <br /><br /> The root cause was inadequate corrective actions due to personnel error (cognitive). Personnel performing maintenance activities did not fully understand the role of the check valves in supporting Technical Specification operability of the ASWPs. <br /><br /> Corrective actions include placing the valves in maintenance rule goal setting, increasing the frequency of inspections, revising work orders to flush the lines with valves removed, and protecting the drain lines from the entry of debris.
2751997012 | Diablo Canyon 1 | 07/15/1997 | 08/14/1997 | 9708210403 | <strong>Technical Specification 3.7.3.1 and 4.0.5 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1997, at 2244 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the requirements of Technical Specifications (TS) 3.7.3.1 and 4.0.5 were not met for Component Cooling Water Pump (CCWP) 1-3 due to inadequate inservice testing (IST). <br /><br /> On July 15, 1997, engineering determined that the pump surveillance had been performed using an inadequate test procedure. The test procedure for the CCWPs did not comply with TS 4.0.5 and ASME Operations and Maintenance (OM) Part 6 requirements as clarified by NUREG-1482. <br /><br /> The procedure discrepancy had been identified on May 22, 1997. PG&E decided to revise the CCWP test procedures to include the more restrictive Code criteria prior to the next required test interval. However, PG&E IST personnel failed to complete the procedure revisions prior to the next test performance. Required test dates were incorrectly calculated by the responsible personnel scheduling the procedure revisions. <br /><br /> The surveillance test procedures for the CCWPs were revised to comply with OM Part 6, prior to the next required surveillance test. An independent assessment of the IST Program will be performed to ensure that all required relief requests have been submitted for compliance to the ASME Code and NUREG-1482. PG&E intends to submit a relief request to allow using pump reference curves for the CCWP testing.
2751997013 | Diablo Canyon 1, Diablo Canyon 2 | 07/25/1997 | 04/10/1998 | 9804140055 | <strong>Technical Specification 3.6.1.1 Not Met Due to Misinterpretation of Containment Isolation Valve Surveillance Requirements for Certain Test, Vent, and Drain Valve</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1984, and on July 19, 1985, respectively, Technical Specification (TS) 3.6.1.1, "Containment Integrity," was not met when Units 1 and 2 entered Mode 4 (Hot Shutdown) during plant heatup. Certain containment penetration test, vent, and drain valves were not periodically surveilled in accordance with TS 4.6.1.1.a. "Containment Integrity." <br /><br /> On July 9, 1997, an NRC inspector questioned if Instrumentation Root Valve SI-1-8964 was included in the 31 day surveillance required by TS 4.6.1.1.a. for containment isolation valves (CIVs). PG&E verified that this valve was not included. On July 25, 1997, NRC staff indicated all test, vent, and drain valves between penetration inner and outer CIVs should be included in the surveillance requirements. On August 28, 1997, during a prudent action inspection, a threaded plug was discovered to be missing from many of the manifolds used in the steam generator level and flow transmitters. On March 18, 1998, it was determined that test connections at the personnel airlock should also be surveilled. <br /><br /> This event was caused by a misinterpretation of TS 4.6.1.1.a. by PG&E non-licensed personnel. Reviews and inspections were completed for all containment penetrations required to be closed during accident conditions to ensure TS 4.6.1.1.a. requirements are met. Surveillance procedures have been revised to include the additional CIVs.
2751997014 | Diablo Canyon 1 | 07/17/1997 | 08/18/1997 | 9708250150 | <strong>Technical Specification 3.8.1.1, Action b., Not Met Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1997, at 1338 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.8.1.1, Action b., allowed action time was exceeded. This TS requires a conditional surveillance of the offsite power sources be performed within 1 hour, and at least once per 8 hours thereafter, when a diesel generator is inoperable. <br /><br /> On July 17, 1997, at 0538 PDT, plant operators satisfactorily performed the initial 1 hour conditional surveillance. <br /><br /> On July 17, 1997, at 1605 PDT, plant operations personnel satisfactorily performed the 8 hour offsite power conditional surveillance following identification of the missed surveillance by the shift forman (SFM) at 1600 PDT. <br /><br /> The cause of this event was personnel error (cognitive) by a utility shift technical advisor (STA) and a utility licensed SFM, in that they failed to ensure proper performance of the conditional surveillance. A contributory cause was personnel error (cognitive) by utility licensed plant operators in that they failed to perform the assigned surveillance within the required time. Corrective action for this event include disciplinary action for the SFM and STA. Additionally, the plant operators involved have been given coaching and counseling regarding the need for attention to detail regarding conditional surveillances. PG&E has also provided additional timing devices for conditional surveillance tracking in the control room.
2751997016 | Diablo Canyon 1, Diablo Canyon 2 | 09/12/1997 | 12/15/1997 | 9712220123 | <strong>Technical Specification 3.3.1 not met Following Inadequate Surveillance Testing of Reactor Trip Interlock Due to Inadequate Vendor Design Information Discovered as a Result of Generic Letter 96-01</strong><br /><i>Abstract:&nbsp;</i>In 1984 and 1985, Technical Specifications (TS) 3.3.1 and 3.3.2 were not met when Units 1 and 2, respectively, began power operations. On September 12, 1997, PG&E identified that the P-8 interlock was not verified during the solid state protection system (SSPS) semiautomatic test. On November 14, 1997, PG&E identified that three additional functions, P-10 interlock (low setpoint power range neutron flux), P-14 interlock (feedwater isolation), and safety injection feedwater isolation functions, had also not been verified. <br /><br /> TS requirements were not met because the cabinets supplied by Westinghouse did not provide the wiring to the semi-automatic tester to test the P-8 inhibit function. For the additional three functions, the SSPS automatic tester did not verify each memory input to all affected individual universal logic cards. <br /><br /> The P-8 condition was identified by a utility engineer during a review of surveillance tests for compliance with the guidelines set forth in NRC Generic Letter 96-01. The lack of verification for the three additional functions was identified during communications with another utility. <br /><br /> The test procedures were revised and performed to check the affected interlock functions. The final safety analysis report will be reviewed and revised as required. PG&E will continue to check testing of safety-related logic circuitry.
2751997017 | Diablo Canyon 1, Diablo Canyon 2 | 10/23/1997 | 11/24/1997 | 9712030281 | <strong>Technical Specification 4.5.2.b.1 Not Met Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1997, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, PG&E identified that Technical Specification (TS) 4.5.2.b.1 had not been met for past operation. This TS requires verification that the emergency core cooling system (ECCS) piping is full of water by venting the ECCS pump casings and accessible discharge piping high points. Since prior to initial plant operation, Surveillance Test Procedure (STP) M-89, "ECCS System Venting," exempted venting the ECCS pump casings if a pump was in operation. On October 23, 1997, during a review of the past 2 years of test data, PG&E identified that adequate venting had not been performed for past operation only. On November 4, 1997, PG&E discovered that STP M-89 did not identify two accessible high point vents on normally isolated hot leg safety injection lines. The cause of this event was personnel error (cognitive) in that utility personnel failed to ensure the surveillance procedure was in strict compliance with TS. STP M-89 has been revised to require venting the ECCS pump casings and accessible discharge piping high points as required by the TS. STP M-89 has been satisfactorily performed for both Units 1 and 2.
2751997018 | Diablo Canyon 1, Diablo Canyon 2 | 10/22/1997 | 11/21/1997 | 9712030253 | <strong>AMSAC System Outside Design Basis Due to Incorrect C-20 Permissive Setpoint</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1997, at 1500 PDT, with Units 1 and 2 in Mode 1 (Power Operation), at 100 percent power, PG&E determined that the anticipated transient without scram mitigating system actuation circuitry (AMSAC) had been originally installed with a C-20 permissive setpoint that was outside design basis. The C-20 permissive had been set at 40 percent turbine power instead of 40 percent reactor thermal power as stated in the current licensing basis. A-1 hour non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B) at 1520 PDT. This condition existed because PG&E personnel were unaware of a conflict between the actual C-20 setpoint and the setpoint stated in the licensing basis. The C-20 permissive was adjusted to the equivalent of 40 percent reactor thermal power. Design documents were revised accordingly. The administrative procedure regarding incoming regulatory correspondence will be revised to require a review of safety evaluation reports for consistency with information provided by PG&E.
2771997001 | Peach Bottom 2, Peach Bottom 3 | 03/18/1997 | 04/16/1997 | 9704250161 | <strong>Technical Specification Violation Due to Non-Conservative Average Power Range Monitor Flow Bias Scram Setpoints for Single Loop Operation</strong><br /><i>Abstract:&nbsp;</i>On 03/18/97, based on the review of past single loop operations in 1992, it was determined that the Average Power Range Monitors (APRM) Flow Biased scram setpoints were non-conservative for single loop operations. Procedural enhancements have been made to ensure that single loop flow conditions are appropriately accommodated in the APRM flow biased setpoints. The cause of this event was that non-conservative single loop APRM flow biased setpoints were in effect due to incorrect implementation of the calculated single loop setpoints. A Shift Update Notice was issued to ensure that all shifts are notified of this situation. Furthermore, the pertinent information from this event will be provided to the appropriate station engineering personnel to emphasize the importance of ensuring accurate incorporation of setpoints into procedures. No actual safety consequences occurred as a result of this event. No previous similar events were identified.
2771997002 | Peach Bottom 2, Peach Bottom 3 | 03/26/1997 | 04/24/1997 | 9704290295 | <strong>Technical Specification violation as a result of Reactor Operation slightly in excess of Licensed Thermal Power</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1997, Engineering Personnel determined that Unit 2 and Unit 3 had operated marginally above 100% of licensed Core Thermal Power (CTP) (i.e., 3458 Megawatts thermal power (MWt)). Specifically, it was determined that due to an inaccurate calculated recirculation (recirc) pump heat addition to the reactor coolant used in the CTP calculation, licensed thermal power may have been exceeded by a maximum of 1.5 megawatts thermal. Additionally, it appears this inaccuracy was a result of the original recirc system design and therefore could have resulted in operation marginally in excess of 100% licensed power at various times since 1974. The cause of the event was a failure to take into account the effect of the instrument characteristics of the recirc pump motor waft transducer on the recirc pump heat addition calculation. No actual safety consequences occurred as a result of this event. The CTP calculation program was modified to compensate for this error. A team will be formed to perform a broad review of every aspect of the CTP calculation. Two previous similar LERs were identified.
2771997003 | Peach Bottom 2 | 06/01/1997 | 06/27/1997 | 9707090253 | <strong>High Pressure Coolant Injection Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1997, it was identified that the High Pressure Coolant Injection (HPCI) Steam Leak monitoring element was indicating higher than the other temperature elements in that group. This condition requires, per the Technical Specifications (Tech Spec), that the instrument channel associated with the TE be placed in the tripped condition. This action was to be accomplished in accordance with General Procedure (GP)-25 Appendix 10. At 1301 hours, during the performance of GP-25, a common power wire lug at a terminal connection was momentarily removed during jumper-installation. This action resulted in the opening of two HPCI Torus Suction Valves and the annunciation of system alarms. The issue was caused by the lifting of a common power wire lug in the HPCI electrical power logic as part of the GP-25 activity. The momentary lifting of the lug at terminal strip disrupted the daisy chain power supply which caused a portion of the HPCI logic power circuitry to de-energize. This occurred because a metal C-jumper, which was under the wire lug, was not seen by the GP-25 performers. Following identification of the event, the HPCI system was restored to its operable condition. The lessons learned from this event has been provided to the appropriate operations personnel and operational training enhancements will be initiated. No previous similar events have been identified.
2771997004 | Peach Bottom 2, Peach Bottom 3 | 07/10/1997 | 07/31/1997 | 9708110054 | <strong>Non-Compliance with Technical Specifications when Tech Spec Action Times were exceeded</strong><br /><i>Abstract:&nbsp;</i>On 07/10/97, the Plant Reactor Operator (PRO) observed the Main Control Room Emergency Ventilation (MCREV) Radiation Monitor Division I alarm cleared when the Main Stack Low Flow alarm was reset. The alarm was annunciated when the "A" channel of MCREV Radiation Monitor was removed from service for repair and testing on 07/09/97 in accordance with GP-25 Appendix 13. The PRO realized that the MCREV Radiation Monitor alarm should not have cleared and immediately notified Control Room Supervision. An investigation was performed which determined that the radiation monitor had been turned "ON" at the local key-lock switch which negated the trip inserted per GP-25 Appendix 13. The inadvertent removal of the trip resulted in the non-compliance to the Tech Spec Action Time allowed by Tech Spec 3.3.7.1. The cause of this event was that the procedural control was not adequate to ensure the radiation monitor would be maintained in the trip condition. Following discovery of this event, GP-25 Appendix 13 was temporarily changed to trip the channel using a jumper. A revision was made to GP-25 Appendix 13 & 14 to require jumper installation in the future versus the use of the keylock switches to trip the MCREV Radiation Monitors. A review of the other GP-25 Appendices was made which ensured that no other similar conditions existed. The pertinent information associated with this event is being provided to all Operations shift teams. No previous LERs were identified.
2771997005 | Peach Bottom 2, Peach Bottom 3 | 08/08/1997 | 09/08/1997 | 9709120085 | <strong>Technical Specification Non-Compliance associated with Rod Block Contact Testing</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1997 it was determined that a non-compliance with the original Custom Technical Specifications (Tech Specs) existed from late 1989 until the time that Improved Tech Specs was implemented in January of 1996. It was determined that no Surveillance Test (ST) functionally tested two Rod Withdraw Block logic channel relay contacts. Following discovery of this condition, interim procedure changes were made and testing was completed that ensured the relay contacts were functional on both units. The cause of this event was an ST revision in October of 1989 which attempted to consolidate the testing of the Rod Block logic from two instrument panels to one instrument panel. This revision inadvertently removed the testing of Rod Withdraw Block channel relay contacts. An evaluation will be performed to determine appropriate procedural revisions to test this relay's contacts. Generic implications are being addressed per an ongoing logic circuit review project under Generic Letter 96-01. Additional corrective actions will be evaluated pending the results of the evaluation. No previous similar LERs were identified.
2771997006 | Peach Bottom 2, Peach Bottom 3 | 09/23/1997 | 10/21/1997 | 9710290055 | <strong>Diesel Generator Auto Start During 4-kV Relay Testing</strong><br /><i>Abstract:&nbsp;</i>On 09/23/97, during performance of a test to calibrate Unit 3 E-43 4-kV electrical bus overcurrent relays, one of the relays tripped which resulted in a trip and lockout of the E-43 bus. The E-4 Diesel Generator (D/G) auto-started due to the dead bus condition, but did not re-energize the bus due to the bus lockout, as designed. Technicians involved in the testing notified the Main Control Room operators of the inadvertent trip of the relay and operations personnel re-energized the bus and load center before the plant was adversely impacted. The cause of this event was personnel error with contributing factors of a relay cover interference and an inadequate procedure. During re-installation of the relay cover, the relay reset lever bar bumped the relay internals which resulted in an inadvertent actuation of the relay. The test procedure did not contain precautions regarding the potential consequences of mishandling the relay cover during test performance. If an accident had occurred with the E-43 bus de-energized, sufficient AC power and equipment were still available to ensure safe shutdown of the plant. The appropriate I&C procedures will be revised to include precautions related to the potential consequences of mishandling relay covers. The appropriate maintenance and I&C pre-job briefing sheets were revised to include a review of the appropriate self check techniques. A review of the relay cover design will also be performed.
2771997008 | Peach Bottom 2, Peach Bottom 3 | 07/05/1994 | 11/26/1997 | 9712050149 | <strong>Logic System Functional Testing procedures did not contain all of the required testing per Technical Specification Surveillance requirements.</strong><br /><i>Abstract:&nbsp;</i>On October 30 and October 31, 1997 respectively, the engineering review performed in response to NRC GL 96-01 identified two (2) issues involving contacts within the standby gas treatment (SBGT) and residual heat removal (RHR) systems logic channel that were not tested in the existing surveillance testing and preventive maintenance programs for Peach Bottom Atomic Power Station (PBAPS) as required by the Technical Specifications (TS). The untested SBGT system contacts were associated with initiation of the heaters for each train of the SBGT system. The RHR system testing deficiency was associated with an insufficient method of verifying contact state associated with the reactor low pressure relays. This RHR condition was common for each train of RHR for Unit 2 and Unit 3. Corrective actions to compensate for the untested logic were taken in accordance with Technical Specification Surveillance Requirement (SR) 3.0.3. All of the deficient contacts were tested and operated correctly. The TS SR had not been met since the original Surveillance Requirement for testing these contacts was not met, resulting in operation prohibited by TS. The actual and potential consequences from these conditions were minimal. Inadequate review of the logic circuits during the procedure development and subsequent reviews resulted in the incorrect procedures. The review of the safety-related logic channels as stipulated in the response to GL 96-01 has been completed for Unit 2 and Unit 3. No additional TS deficiencies were identified. The appropriate procedures will be revised prior to the next performance.
2771997009 | Peach Bottom 2, Peach Bottom 3 | 11/09/1997 | 06/10/1998 | 9806220337 | <strong>Unit 2 Reactor Scram resulting from a generator lockout condition & subsequent turbine trip Failure of the 2A Reactor Feedpump turbine to trip on demand During recovery activities.</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1997, with unit 2 at 100 percent power, a generator lockout and subsequent turbine trip occurred that resulted in a reactor scram. The turbine trip caused an expected high reactor pressure condition resulting in a main steam relief valve lifting and Alternate Rod Insertion (ARI) to initiation. The generator lockout resulted from problems caused during activities that swapped the 2AD003 battery charger from charger #1 to charger #2 when an equipment operator failed to appropriately follow procedure. No safety consequences occurred as a result of the scram and all safety systems were available. Corrective actions for the personnel error/procedure non-compliance were taken by the Senior Manager of Operations and reinforced with operations shift personnel. Additionally, during post-scram recovery activities, the 2A reactor feedpump turbine (RFPT) failed to trip on demand from the control room and at the local trip station. Corrective actions for the RFPT included repair, reinstallation and testing of the trip device, and an on-going analysis of the anomalies associated with the trip oil system.
2771997010 | Peach Bottom 2 | 12/29/1997 | 06/10/1998 | 9806220356 | <strong>Failure of the 2A reactor feedpump turbine to trip.</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1997, the 2A RFPT was being removed from service during reactor power reduction to support a planned maintenance outage. At this time, the 2A Reactor Feedpump Turbine (RFPT) failed to trip when the Reactor Operator (RO) pushed the control room 2A RFPT trip pushbutton. During the time frame of developing the troubleshooting plan, the 2A RFPT did trip when it received an actual reactor high level signal. Further investigation proved that the 2A RFPT does trip when a trip signal is sustained for greater then one second. The condition where a delayed trip of up to ten seconds to occur was evaluated within the non-conformance process and was deemed to be acceptable. Corrective actions for the 2A RFPT included repair, reinstallation, and testing of the electrical trip solenoid and associated mechanical devices. Additionally, inspection of the 2B and 2C RFPTs and the unit 3 RFPTs found that no similar problems or anomalies with delayed trip functions existed. This report is a revision to the original submittal and is being submitted voluntarily.
2781997001 | Peach Bottom 3 | 10/22/1995 | 02/19/1997 | 9702240466 | <strong>Thermal Power Exceed 100 Percent Due to Out of Tolerance Test Equipment</strong><br /><i>Abstract:&nbsp;</i>On 1/21/97, at 1450 hours, it was determined that the plant thermal power level exceeded 100 percent by approximately 0.6 percent due to four feedwater temperature instruments being non-conservatively recalibrated on 6/13/95. These instruments provide input into the overall core thermal power calculation. Once identified, operating personnel promptly reduced reactor power. The non-conservative calibration of the instruments was due to the use of out-of-tolerance test equipment. When the out-of-tolerance test equipment was reported to station personnel in July 1996, no recalibrations were performed. This was due to a lack of specific information available to the reviewer concerning the function of the feedwater temperature instruments. Subsequent investigation has revealed that the test equipment had a history of internal component failures although the failures were on different components within the test equipment. A contributing cause involved not acting on the fact that all instruments were recalibrated on 6/13/95. use. Surveillance procedures for feedwater temperature instruments and other similar instruments used in the thermal power calculation will be reviewed and revised as necessary. Appropriate personnel involved with the review of out-of-tolerance reports for test apparatus were informed of this event. Personnel involved with the review of completed surveillances will be informed of this event. The programs for reviewing test equipment failure trends and test equipment out-of-tolerance reports will be reviewed. There were no previous similar events identified.
2781997002 | Peach Bottom 3 | 03/09/1997 | 04/07/1997 | 9704150258 | <strong>Manual Scram Due to a Loss of Forced Reactor Core Circulation at Power as a Result of a 13kv Feeder Breaker Auxiliary Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On 3/9/97, at 0600 hours, the 3B reactor recirculation pump unexpectedly tripped when the Unit 3 main turbine was manually tripped at 14 percent power. The main turbine was tripped during preparations to enter the drywell with the unit in single-loop operation. An auxiliary switch in the #4 13kv feeder breaker failed to change state after a manual bus transfer. This switch verifies the 13kv transfer from the main generator output to off-site sources for the 3B reactor recirculation pump motor logic. Without this transfer verification the 3B reactor recirculation pump motor breaker tripped when the main turbine was manually tripped and the generator locked-out. The unit was manually scrammed, in accordance with procedure, due to the loss of all forced core circulation at power. Examination of the auxiliary switch revealed internal binding due to a buildup of a dirt-like substance on various shaft pieces and contacts. The switch assembly was cleaned, lubricated and exercised until it functioned properly, then reinstalled. A failure analysis will be performed to further pinpoint the failure mechanism and any generic implications. No previous similar events have been identified.
2781997003 | Peach Bottom 3 | 04/04/1997 | 05/14/1997 | 9705220426 | <strong>Technical Specification Non Compliance due to Loss of 3C Reactor Feed Pump High Water Level Trip</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1997 the 3C Reactor Feedwater Pump (RFP) High Water Level Trip function was declared inoperable upon discovery of a blown fuse in the pump control circuit. The high water level trip function is required by Technical Specification 3.3.2.2 and requires restoration within 2 hours. The loss of the trip function was traced to simultaneous DC electrical grounds in the 3B Control Rod Drive (CRD) pump 4 kv breaker charging motor and the 3C RFP vacuum trip cabinet. The delay in entering the Tech Spec action was caused by not correlating an indicating light problem to inoperability of the 3C RFP High Water Level trip. The fuse was replaced, restoring the high level trip function, and both DC grounds were eliminated by replacing the CRD pump breaker and bypassing the ground from the limit switch in the vacuum trip cabinet. Appropriate corrective action will be developed to improve recognition of the loss of the high water level trip function. There were no actual safety consequences and no previous similar events have been identified.
2801997001 | Surry 1 | 01/23/1997 | 06/10/1997 | 9706180217 | <strong>Shutdown Due to Steam Drain Line Weld Leak</strong><br /><i>Abstract:&nbsp;</i>At 1850 hours on January 23, 1997, with Unit 1 and Unit 2 both at 100% power, a Service Building Operator performing routine activities in the Unit 1 Main Steam Valve House discovered a small steam leak in the steam drain piping on the "B" main steam line. Unit 1 was shutdown in accordance with the requirements of Technical Specification 4.15.C.1. While performing normal shutdown procedures, both source range nuclear instruments failed to indicate source range counts, and operator action to manually trip the turbine from the main control room failed to result in a turbine trip. The turbine was tripped locally at the governor pedestal using the manual trip lever. While shutdown, both source range detectors were replaced, tested and the nuclear instruments were returned to service. The turbine trip actuation circuitry was inspected and tested satisfactorily. The leak was repaired, inspected, and tested prior to returning the Unit to power operation. The health and safety of the public were not affected by this event. A radiological release did not occur. This event was caused by a pin hole leak in a 1 1/2 inch diameter weld. This report is being made pursuant to 10CFR50.73 (a)(2)(i)(A), for any nuclear plant shutdown required by the plant's Technical Specifications.
2801997002 | Surry 1, Surry 2 | 01/16/1997 | 04/08/1997 | 9704150060 | <strong>One Train of Auxiliary Ventilation System Inoperable Outside of TS</strong><br /><i>Abstract:&nbsp;</i>On January 9, 1997, with Unit 1 and Unit 2 at 100% power, a 7 day Limiting Condition of Operation (LCO) was entered at 0508 hours for auxiliary ventilation system filter exhaust fan 01-VS-F-58B maintenance. On January 10, 1997, the actuator for 1-VS-MOD-58B was replaced with a rebuilt actuator and the linkage was adjusted. Following completion of the specified testing, the fan was declared operable on January 15, 1997. On January 16, 1997 reverse rotation of 1-VS-F-58B was observed. The fan was declared inoperable and 1-VS-MOD-58B was adjusted, eliminating the reverse rotation of the 58B fan. The fan was declared operable at 1257 hours on January 16, 1997. On February 7, 1997, it was determined that the misalignment of 1-VS-MOD-58B, which had existed on January 15,1997, rendered the fan inoperable and that the 7 day LCO that was entered on January 9, 1997 for maintenance should not have been exited until full damper closure was properly verified. This occurred 7 hours 49 minutes after the expiration of the 7 day LCO, exceeding the 6 hour requirement of TS 3.22 requiring the units to be in Hot Shutdown. The auxiliary ventilation system was capable of performing its safety function during this event. Therefore, the health and safety of the public were not affected. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) for operating in a condition prohibited by TS.
2801997003 | Surry 1, Surry 2 | 02/19/1997 | 03/19/1997 | 9703260334 | <strong>Loss of Pressurizer Heaters Results in Manual U1 Trip and U2 ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>At 2040 hours on February 19, 1997, with Unit 1 at 100 percent power and Unit 2 at Hot Shutdown, a Technical Specification 3.12.F.2 two hour Limiting Condition of Operation was entered due to Reactor Coolant System (RCS) pressure being less than 2205 psig. An Abnormal Procedure was entered in response to the decreasing RCS pressure. At 2052 hours, a Unit 1 shutdown was commenced. At 2259 hours, a manual reactor trip was initiated due to a continuing decrease in RCS pressure. Upon receipt of the reactor trip signal, the Reactor Protection System actuated and functioned as designed, and all control rods inserted into the core. Station operating personnel acted promptly to place the plant in a safe, hot shutdown condition in accordance with the proper procedures. The shutdown margin was calculated and the critical safety function status trees were monitored to verify that the unit conditions were acceptable. Plant response was as expected and the unit stabilized at hot shutdown. No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. A detailed Reactor Trip Report and a Root Cause Evaluation is being performed for this event. The cause of the trip was inability to maintain RCS pressure due to loss of the Group C pressuizer proportional heaters due to failure of the Robicon controller unit. Additional approved recommendations from the Root Cause Evaluation will be implemented. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv) and 10 CFR 50.73(a)(2)(i).
2801997004 | Surry 1 | 03/17/1997 | 04/15/1997 | 9704220103 | <strong>Main Steam Safety Valve As Found Setpoint Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1997, with Unit 1 in Cold Shutdown, setpoint testing of Unit 1 Main Steam Safety (MSSVs) revealed that the lift setting for one MSSV was outside the As Found setpoint tolerance (+/- 3%) that is allowed by Technical Specification (TS) 3.6.A. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for conditions prohibited by TS 3.6.A, 3.6.B.3. <br /><br /> The safety valves were sent to Wyle Laboratories for testing to ensure conformance with TS requirements. The As Found setpoint for one MSSV was found to be outside TS tolerance. <br /><br /> The safety valve was repaired, adjusted, and tested to be within the correct As Left setpoint tolerance (+/- 1 %) allowed by TS. <br /><br /> This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. The health and safety of the public were not affected at any time during this event.
2801997005 | Surry 1 | 05/02/1997 | 05/28/1997 | 9706040089 | <strong>Unit 1 Power Range Nuclear Instrumentation Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1997, with Unit 1 at approximately 30% power, Operations Periodic Test procedure 1-OPT-RX-004, "Reactor Power Calorimetric Using Feed Flow with P-250 Out of Service (Manual)," was completed at 23:20 and the power range nuclear instrumentation (PRNI) channels were adjusted to correspond with the calculated reactor power value of 37.9%. On May 3, 1997, the Shift Technical Advisor discovered an error in the manual reactor power calorimetric that was performed on the previous day. As a result of the error, the calculated reactor power value was approximately 10% higher than the actual value. At 12:52, the PRNI channels were declared inoperable because the channels had been adjusted based on the erroneous reactor power calorimetric. Technical Specification (TS) 3.0.1, requiring the unit to be in Hot Shutdown within six hours, was entered. The PRNI channels were properly adjusted and TS 3.0.1 was exited on May 3, 1997 at 14:49. The event occurred as a result of personnel errors. The personnel who were directly involved in this event were counseled. The safety functions of the PRNI channels were not adversely affected by this event and the health and safety of the public were not affected at any time. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
2801997006 | Surry 1 | 03/20/1997 | 04/18/1997 | 9704230266 | <strong>Loss of Refueling Integrity Due to Inadequate Containment Closure Process.</strong><br /><i>Abstract:&nbsp;</i>At 1206 hours on March 20, 1997, with Unit 1 in refueling shutdown and fuel movement underway, and Unit 2 at 100% power, a management walkdown of selected refueling containment integrity penetrations questioned the adequacy of the main steam safety valve inlet pipe flange cover installation. Investigation by a maintenance team determined that the flange cover on main steam safety valve, 1-MS-SV-103C, had a gap of approximately one-eighth inch. Technical Specification 3.10.A.1, regarding refueling operations, requires penetrations which provide a direct path from containment atmosphere to the outside atmosphere to be closed by a valve, blind flange, or equivalent. Since refueling containment integrity was not satisfied, fuel movement was stopped in accordance with the action requirements of Technical Specification 3.10.B. A containment integrity verification plan was developed and implemented. Additional containment integrity issues were identified, corrected and evaluated. The health and safety of the public were not affected by this event. A fuel handling accident or radiological release did not occur. This event was caused by inadequate refueling containment closure process and verification. A Root Cause Evaluation i underway. This report is being made pursuant to 10CFR50.73(a)(2)(i)(B) for any operation or condition prohibited by Technical Specifications.
2801997007 | Surry 1, Surry 2 | 09/30/1997 | 10/30/1997 | 9711050098 | <strong>Outside Appendix R Design Basis Due to Vital Bus Isolation Issue</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1997, it was identified that during an earlier time frame Surry Units 1 and 2 had been outside the Appendix R design basis due to a 120 VAC vital bus isolation issue. From July 1988 on Unit 1 and September 1989 on Unit 2 when Appendix R isolation switches were removed until August 1997 when the procedures containing interim compensatory measures were revised, Operations did not have adequate procedural direction necessary to ensure isolation of the required power supplies and/or replacement of UPS fuses. Without proper isolation, power to the Appendix R panels may not have been available, thereby placing Surry Units 1 and 2 outside the Appendix R design basis during this period. Therefore, this report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(ii)(B). When it was determined that Surry was outside the Appendix R design basis, appropriate compensatory measures had already been defined and put into place. This condition resulted in no significant safety consequences or implications, and the health and safety of the public were not affected at any time.
2801997008 | Surry 1, Surry 2 | 10/11/1997 | 11/07/1997 | 9711120275 | <strong>Invalid Actuation of Engineered Safety Features Due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1997, with Unit 2 at Refueling Shutdown, an inadvertent actuation of the Unit 2 "B" train of the High-Consequence Limiting Safeguards (Hi-CLS) system occurred at 14:22 during the replacement of electrical relay 2-CLS-RLY-1B12. As designed, the Hi-CLS signal initiated a Unit 2 "B" train Safety Injection (SI) system actuation. Plant systems and components responded to the Hi-CLS and SI signals, as designed. After verifying that the Hi-CLS signal was not valid, the affected systems were restored to their pre-event configuration. A Root Cause Evaluation concluded that this event was caused by personnel errors. To prevent recurrence, training will be conducted to discuss the lessons learned. The event did not affect Unit 2 reactor core cooling, or result in any radiological releases or personnel injuries. Although the engineered safety feature actuations were invalid, the CLS and Si systems were not completely removed from service. Therefore, the NRC was notified pursuant to 10 CFR 50.72 (b)(2)(ii) on October 11, 1997, at 16:39. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv).
2801997009 | Surry 1, Surry 2 | 10/14/1997 | 01/13/1998 | 9801210219 | <strong>Intake Canal Level Probes Inoperable Due to Marine Growth</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1997, Unit 1 was operating at 100% power with Unit 2 at Refueling Shutdown. Intake canal level instrument Channel III was declared inoperable at 10:17 to allow testing of intake canal level probe 2-CW-LE-202. The as-found response time of 2-CW-LE-202 was greater than the acceptance limit. The probe was cleaned by divers, tested satisfactorily, and Channel III was returned to operable status. Channel IV was declared inoperable at 17:13 to allow canal level probe 2-CW-LE-203 to be tested. The as-found response time of 2-CW-LE-203 was also greater than the acceptance limit. The probe was cleaned by divers, tested satisfactorily, and Channel IV was returned to operable status. Based on the conclusion that the 2-CW-LE-202 and 2-CW-LE-203 testing failures resulted from a common cause marine biofouling, Channels I and II were declared inoperable and an LCO was entered in accordance with TS 3.0.1. Intake canal level probes 1-CW-LE-102 and 1-CW-LE-103 were cleaned by divers, tested satisfactorily, and Channels I and II were returned to operable status. The TS 3.0.1 LCO was exited at 20:10. A Category 1 RCE was performed and determined that the failure to adequately maintain the intake canal level probes resulted in marine biofouling, which prevented the probes from achieving the required response time. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(vii)(D).
2801997010 | Surry 1 | 10/28/1997 | 11/25/1997 | 9712020172 | <strong>Missed Fire Protection Surveillance Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 2145 hours on October 28, 1997, with Unit 1 at 100% power and Unit 2 in Intermediate Shutdown following refueling, it was discovered that the 31 day surveillance periodic test (PT) used to determine the diesel driven fire pump 1-FP-P-2 operable was not completed within the time required by technical specifications. The cause for this event was cognitive personnel error. Fire pump 1-FP-P-2 was declared inoperable, and since recirculation valve 1-FP-36 was open, the motor driven fire pump 1-FP-P-1 was also declared inoperable. A 24 hour clock was entered to close valve 1-FP-36 and a 7 day clock was entered to test the diesel driven fire pump. Valve 1-FP-36 was closed and the motor driven fire pump was declared operable. Procedure 0-OPT-FP-009 was satisfactorily completed and fire pump 1-FP-P-2 was declared operable at 2334 hours on October 28, 1997. The individual involved was disciplined. As an enhancement, an additional administrative barrier has been implemented that compares the completed PT procedures with the PT work schedule. No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited b the plant's technical specifications.
2801997011 | Surry 1 | 10/30/1997 | 11/26/1997 | 9712020116 | <strong>Improper Bypass Breaker Testing Due to Inadequate Definition of In Service</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1997, with Unit 1 at 100% power and Unit 2 reactor critical with low power testing in progress, it was determined that the periodic test (PT) procedures for testing the reactor trip bypass breakers did not test the manual undervoltage trip prior to placing the breaker in service. Testing of the undervoltage trip had previously been conducted with the reactor trip bypass breakers racked into the connect position. Therefore, the breakers were actually in service at the time of the testing. The event was caused by a misinterpretation of the term "in-service" and how it applied to the bypass breakers. The TS requirements were not properly incorporated into PT procedures when they were revised. The PT procedures have been corrected and the bypass breakers have been satisfactorily tested. <br /><br /> No conditions adverse to safety resulted from this event and the health and safety of the public were not affected because testing of the reactor trip bypass breakers took place immediately after closing the bypass breakers and before the reactor trip breakers were open for testing. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
2801997012 | Surry 1, Surry 2 | 10/28/1997 | 01/13/1998 | 9801210215 | <strong>EQ Unanalyzed Condition/Outside App. R. Design Basis Due to Unlatched Doors</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1997, tripping of two breakers in a security distribution panel resulted in loss of power to security systems, as well as loss of power to the latching mechanism on several doors, causing the doors to become unlatched. The affected doors have security, EQ, and/or fire protection functions. At the time of occurrence, Unit 1 was at 100% power and Unit 2 was at intermediate shutdown in the process of starting up following completion of a scheduled refueling. Compensatory measures were implemented, as required, including security provisions. It was determined that having multiple EQ doors in an unlatched condition simultaneously resulted in an unanalyzed condition because the defined allowed breach times for the EQ doors assume no simultaneous EQ door breaches. It was also concluded that fire doors being unlatched resulted in being outside the Appendix R design basis because the unlatched doors may not have prevented the spread of a fire from one fire area to others. A design change to revise the power failure mode on the affected doors from energized-to-latch to energized-to-unlatch has been implemented. This report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(A) [unanalyzed condition] and 10CFR50.73(a)(2)(ii)(B) [outside design basis]. Upon further review, it was determined that a previous situation also resulted in an EQ unanalyzed condition; therefore, this LER supplement is being submitted pursuant to 10CFR50.73(a)(2)(ii)(A).
2811997001 | Surry 2 | 02/18/1997 | 03/19/1997 | 9703260311 | <strong>Manual Reactor Trip and ESF Actuation Due to Loss of EHC Control Power</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1997, at 1449 hours, with Unit 2 operating at 100% reactor power, a loss of turbine Electro-Hydralic Control (EHC) control power caused the turbine governor valves to close. The reactor was manually tripped at 1450 hours. The Reactor Protection System actuated and functioned as designed, and all control rods inserted into the core. Three Individual Rod Position Indicators (IRPI) were observed between 10 and 15 steps. The Turbine Driven Auxiliary Feedwater Pump (TDAFWP) started and operated as designed, however, a second start was initiated and the pump tripped on overspeed. The most probable cause of the loss of EHC control power was a momentary short that lead to an over-voltage condition and tripped two redundant +15 VDC power supplies. An automatic turbine trip should have been initiated by the loss of EHC control power, but did not occur. The lack of a turbine trip was due to a faulty relay card. The power supplies and relay card were replaced. Two IRPIs were recalibrated and the calibration on the remaining IRPI verified with recent data. Emergency procedures were revised to reduce the possibility of a re-start signal until the TDAFWP governor reset. No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
2811997002 | Surry 2 | 07/13/1997 | 12/10/1997 | 9712180399 | <strong>Main Steam High Range Radiation Monitor Inoperable Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1997, with Unit 2 at approximately 100% power, the control room annunciator, 2-RMA-A-7, for the main steam line effluent high range radiation monitors alarmed. Control room operators responded to the alarm in accordance with Annunciator Response Procedure 2-RMA-A-7, "UNIT 2 MN STM ABC RAID MON ALERT/HI," and determined that the "B" main steam line effluent high range radiation monitor, 2-MS-RM-225, was not functioning properly. The monitor was declared inoperable at 07:42 and the preplanned alternate method of monitoring was initiated in accordance with Technical Specifications (TS) Table 3.7-6. An extensive investigation was performed during the subsequent three week period. Based on the results of the investigation, Instrumentation and Controls personnel concluded that the detector for 2-MS-RM-225 did not function properly at the ambient temperature of the detector enclosure. A temporary blower was installed on August 19, 1997, to reduce the ambient temperature of the detector enclosure. 2-MS-RM-225 was tested satisfactorily and returned to service on August 31, 1997, at 17:20. This Special Report is being submitted in accordance with TS Table 3.7-6 because 2-MS-RM-225 was not returned to an operable status within seven days.
2811997003 | Surry 2 | 10/14/1997 | 11/13/1997 | 9711180287 | <strong>Main Steam Safety Valves As Found Setpoint Found Out Of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1997 and October 17, 1997, with Unit 2 in Refueling Shutdown, setpoint testing of Unit 2 Main Steam Safety (MSSVs) revealed that the lift setting for two MSSVs were outside the As Found setpoint tolerance (+/- 3%) that is allowed by Technical Specification (TS) 3.6.A. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for conditions prohibited by TS 3.6.A, 3.6.B.3. The safety valves were sent to Wyle Laboratories for testing to ensure conformance with TS requirements. The As Found setpoint for two MSSVs were found to be outside TS tolerance. The safety valves was repaired, adjusted, and tested to be within the correct As Left setpoint tolerance (+/- 1%) allowed by TS. This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. The health and safety of the public were not affected at any time during this event.
2811997004 | Surry 2 | 12/02/1997 | 12/31/1997 | 9801080116 | <strong>Invalid MSTV Indication In Manual Reactor Trip With ESF Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1997, at 0930 hours, Surry Unit 2 was manually tripped from 100% reactor power when the Main Steam Trip Valve (MSTV) Closed annunciator was received and MSTV A position lights indicated intermediate position. The manual reactor trip was initiated to minimize a unit transient for a MSTV closure event. Automatic actuations occurred as expected. Six Individual Rod Position Indicators (IRPI) initially indicated between 10 and 20 steps and all eventually drifted to less than 10 steps. It was later determined that MSTV A was full open and no signals were present for the valve to close. <br /><br /> The cause of the event was movement of the MSTV A open limit switch arm from its full open position. The limit switch arm and valve position arm were determined to have marginal overlap. Work activity in the area may have caused the repositioning of the limit switch. The position of the switch was subsequently adjusted to provide sufficient overlap. <br /><br /> Prior to returning to 100% reactor power, the Turbine Driven Auxiliary Feedwater (TDAFW) pump turbine tripped on overspeed during routine testing. The governor was replaced and a root cause evaluation was initiated to determine the cause for the overspeed trip. <br /><br /> No conditions adverse to safety resulted from this event and the health and safety of the public were not affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv).
2821997001 | Prairie Island 1, Prairie Island 2 | 01/08/1997 | 02/07/1997 | 9702130255 | <strong>Auxiliary Building Crane Protective Features Defeated by Wiring Errors</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1997 it was determined that the 125 ton Auxiliary Building Crane had been used to handle a spent fuel cask while two protective features had been defeated by wiring errors. A new radio control transmitter had been procured and placed in service. The controller has critical and non-critical positions which are chosen by the crane operator. The new controller was wired differently than the old one and choosing the critical position actually put the controller in the non-critical position. When this was done, the main hoist drum overspeed protection was defeated as was the spent fuel pool roof slot limit switch. However, some overspeed protection remained functional, roof slot alignment lights were functional, and the crane still met the single failure proof criteria. <br /><br /> The controllers are being made to agree with one another and procedures are being changed to provide additional assurance that the controller is in the correct position.
2821997002 | Prairie Island 1, Prairie Island 2 | 02/19/1997 | 03/21/1997 | 9703280352 | <strong>Failure to Submit Relief Requests for Limited Inservice Inspection Examinations</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. An Inspector from NRC Region III, while performing an inspection regarding the augmented reactor vessel examinations required by 10CFR50.55a(g)(6)(ii)(A), noticed that the reactor beltline welds had 100% coverage and the nozzle to vessel welds did not. The inspector asked if relief had been requested for the nozzle to vessel welds since the coverage was limited. Subsequent discussions revealed that we had differing understandings of 10CFR50.55a(g) regarding the need for relief requests for a plant whose construction permit was issued prior to January 1, 1971. We had not submitted any relief requests for examinations where they were limited by geometry or other component interferences. On February 19, 1997 we agreed to comply with the NRC interpretation of the regulation. This placed earlier examinations outside of the Technical Specifications requirements for compliance with 10CFR50.55a(g). <br /><br /> The corrective actions include submitting relief requests for all Section XI Interval 3 examinations where the coverage is limited, including those examinations already completed. <br /><br /> Since the examinations were limited by the design of the plant, the regulations allow impracticality to be the basis for relief, and the examinations were performed to the extent practical, it is expected that the relief requests will be approved following submittal.
2821997003 | Prairie Island 1, Prairie Island 2 | 03/25/1997 | 04/23/1997 | 9705060067 | <strong>Discovery that the Auxiliary Feedwater Pumps will Trip on Low Steam Generator Pressure During a Complete Loss of Feedwater ATWS Event</strong><br /><i>Abstract:&nbsp;</i>During preparation of a safety evaluation to justify changing the setpoints for the low discharge pressure switches for runout protection of the auxiliary feedwater pumps, a scenario was discovered where the auxiliary feedwater system would not be capable of performing as assumed in the ATWS analysis as described in the plant Updated Safety Analysis Report (USAR). For two specific ATWS events (loss of offsite power and complete loss of feedwater), both auxiliary feedwater pumps could cease operating early in the transient and not be available unless the operator(s) took action to restore them. The ATWS analysis in the USAR assumes that both auxiliary feedwater pumps are operating throughout the event. This loss of the AFW pumps during either a loss of offsite power or a complete loss of feedwater ATWS event is not within the plant's current licensing basis. An operability evaluation was performed, with the support of Westinghouse, and it was concluded that the auxiliary feedwater system, as currently configured, is capable of mitigating the complete loss of feedwater and loss of offsite power ATWS events. Long term corrective actions to resolve the discrepancy between the performance capability of the Prairie Island auxiliary feedwater system and the assumptions in the ATWS analysis are being actively investigated.
2821997004 | Prairie Island 1, Prairie Island 2 | 04/04/1997 | 05/05/1997 | 9705120193 | <strong>AMSAC Actuation Blocking Setpoint Inadvertently Set Non- conservatively High</strong><br /><i>Abstract:&nbsp;</i>During review of system documentation by the System Engineer, it was determined that the AMSAC C-20 Permissive Setpoint was non-conservative with respect to the USAR value. As stated in USAR section 7.11, the C-20 permissive arms AMSAC when turbine load is greater than 40% power. It was determined that the actual setpoint used by AMSAC corresponded to a turbine (reactor) power of approximately 48% power. This is non-conservative to the USAR requirement of 40% power. This condition has apparently existed since original installation of the AMSAC systems in 1989/90. <br /><br /> The AMSAC timer function (Variable Actuation Delay of 27.5 to 225 seconds) was also found to have the incorrect setpoints. The effect on the time delay was to shift the setpoint line described in USAR Fig. 7.11-2 towards the maximum time delay curve and actually exceeded the maximum time delay curve between approximately 46% and 55% power. <br /><br /> The cause of the event was the assumption that First Stage Turbine impulse pressure was linear from 0% to 100% turbine load when, in fact, it is non-linear less than 10% turbine load.The AMSAC setpoints were revised within approximately 24 hours of discovery. Other setpoints that could have been mis-set by a similar error were reviewed for problems.
2821997005 | Prairie Island 1, Prairie Island 2 | 04/08/1997 | 05/08/1997 | 9705140174 | <strong>Surveillance Interval Discrepancies with Diesel Fuel Oil Sample Analyses</strong><br /><i>Abstract:&nbsp;</i>A system engineer discovered that the monthly analysis of the diesel fuel was not being performed within the required time. Samples were taken monthly as required. Samples were then sent off site for analysis. The analysis results were returned to the system engineer regularly, in approximately 3 weeks. Surveillances are required to be completed within +/- 25% of the surveillance interval specified in the Technical Specifications. No time requirement had been associated with receiving and reviewing the sample analyses. The operability of the emergency diesel generators was never affected by this time delay, as all analyzed samples were acceptable. The surveillance procedure will be changed to specify the completion of the required analysis prior to the surveillance being considered complete.
2821997006 | Prairie Island 1, Prairie Island 2 | 04/11/1997 | 05/12/1997 | 9705190041 | <strong>Discovery of Logic Error in Control Room Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1997 a condition was identified that is considered outside the 1967 proposed GDC Criterion 20 requirements for protection against single failures. Specifically, a design deficiency exists which could result in the failure to automatically isolate control room outside air supply upon detection of high radiation levels (for conditions where a safety injection would not be required) in the control room. Control room outside air supply isolation logic may be inadequate to assure that control room habitability is not adversely impacted during a radiological release event with a concurrent single failure of the control room radiation monitors. This deficiency has existed since the beginning of plant operation. <br /><br /> Corrective action has been taken to ensure the outside air supply to the control room is isolated prior to conducting any plant operations which may result in a radiological release with the potential to exceed control room allowable doses. A design change to modify the logic to make the high radiation actuation logic meet the single failure criterion is being developed.
2821997007 | Prairie Island 1, Prairie Island 2 | 04/29/1997 | 06/30/1997 | 9707090036 | <strong>Both Trains of Spent Fuel Pool Special Ventilation Inoperable While Handling Load over Spent Fuel</strong><br /><i>Abstract:&nbsp;</i>On April 29, 1997 Prairie Island plant management, while reviewing the implications of a Quality Services Report, determined that when fuel handling operations have been in progress in the Spent Fuel Pool, both trains of the Spent Fuel Special Ventilation System have been momentarily out-of service whenever plant personnel opened one of the personnel doors to gain entry into the spent fuel pool enclosure. Both trains of Spent Fuel Pool Special Ventilation are out-of-service when a door is opened. This condition is in violation of Technical Specification 3.8.D.3 which states: ". . . suspend all fuel handling operations and crane operations with loads over spent fuel (inside the spent fuel pool enclosure)" when both trains are out-of-service. The last occurrence of this condition took place at approximately 1630 on February 6, 1997 while Unit 2 was in refueling mode and refueling operations was nearing completion. The ventilation system returned to service almost immediately when the door automatically shut behind the personnel. No other equipment was out-of-service or faulted during the event and no operator action was taken as personnel were not aware the action constituted a violation. Procedure changes will be put in place that will require that all (except personnel) doors be closed when handling fuel or crane operations with loads over spent fuel prior to the next movement of loads or fuel in the enclosure.
2821997008 | Prairie Island 1 | 06/02/1997 | 07/02/1997 | 9707090141 | <strong>Unit 1 Reactor Trip Caused by Electrical Ground in Rod Control System</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1997, Prairie Island Unit 1 was at steady-state, 100% power with the Rod Control System in automatic. At approximately 11:10 AM, Unit 1 control room operators received a "Rod Control System Non-Urgent Failure Alarm" followed seconds later by a "Rod Control System Urgent Failure Alarm". Approximately thirty seconds later, Unit 1 tripped from 100% power on a Negative Flux Rate Trip generated by Power Range Nuclear Instrumentation. The plant response to the reactor trip was as expected, except that following the trip, leakage past the normally closed Feedwater Regulation Bypass Valve to 11 Steam Generator (11 FRBV) resulted in a faster than expected cooldown rate. Operators took manual actions to stop the cooldown. A short to ground was found in the (+) stationary gripper coil wire in a Control Rod Drive Mechanism (CRDM) cable. The cause of the shorted cable has been initially attributed to foreign material within the cable connector during original manufacture of cable assemblies. Corrective actions are being taken to ensure the cause of the failure is thoroughly understood and any actions necessary to prevent recurrence are identified. The CRDM cables on Unit 2 will be meggared during the next Unit 2 refueling outage.
2821997009 | Prairie Island 1 | 06/05/1997 | 07/07/1997 | 9707140103 | <strong>Unavoidable Momentary Non-compliance with Technical Specification Requirements Which Do Not Provide a Time Interval to Establish Different Plant Equipment Configurations Upon Moving into Different Plant Conditions</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1997, Unit 1 was sub-critical and cooling down to cold shutdown to repair a control rod drive cable assembly. The unit had tripped on June 2 following the failure of this cable assembly. While cooling down, the reactor coolant system (RCS) temperature was lowered below 200 degrees F to achieve cold shutdown. Technical Specification 3.3.A.4 requires that both safety injection pump control switches in the control room shall be in pullout whenever RCS temperature is at or less than 200 degrees F and Technical Specification 3.3.A.1 requires that one safety injection pump be OPERABLE whenever the RCS temperature is greater than 200 degrees F and less than 310 degrees F. If the switch is placed in pullout just prior to reaching 200 degrees F, the unit doesn't meet the requirements to have one pump operable above 200 degrees F. If the pump switch is placed in pullout just after reaching 200 degrees F, then the unit doesn't meet the requirements to have both pumps in pullout for that brief period of time. Since the pump was placed in pullout when the unit was above 200 degrees F, the unit entered Technical Specification 3.0.C (the "motherhood clause") because there is no action statement to follow when above 200 degrees F and both pumps are inoperable. <br /><br /> When the unit was heated up on June 14, 1997 following the repair to the control rod cable assembly, it was heated up above 200 degrees F before one safety injection pump control switch was placed in auto. Briefly then, the unit was again in a condition where both pumps were inoperable while he RCS temperature was above 200 degrees F. <br /><br /> The corrective action is to submit a License Amendment Request to fix the Technical Specification requirements.
2821997010 | Prairie Island 1, Prairie Island 2 | 06/16/1997 | 07/16/1997 | 9707240051 | <strong>Failure to Evaluate the Condition of a Residual Heat Removal Pump When the Vibration Level During a Surveillance Test Was Recorded at the Alert Value</strong><br /><i>Abstract:&nbsp;</i>During June 1997, while Unit 1 was in a cold shutdown condition, a Quality Assurance audit of the ASME Section XI Inservice Testing Program uncovered some inconsistencies regarding acceptance criteria in Revision 7 of Surveillance Procedure SP 1092B "Safety Injection Check Valve Test (Head Off) Part B: RWST To RHR Flow Path Verification." This procedure was performed on January 13, 1996 during a refueling outage and its purpose was to provide new ASME Section XI baseline flow and vibration levels for 11 and 12 Residual Heat Removal (RHR) pumps. The procedure stated that no acceptance criteria applied and that the results would be evaluated by the system engineer. However, even for baselining purposes the vibration acceptance criteria should have been specified in the surveillance procedure (per the ASME requirements). During performance of the test, a vibration level in the alert range for 12 RHR Pump was recorded (the procedure did not specify what the alert range was) and was not subsequently evaluated. <br /><br /> Following discovery of this failure to evaluate, a similar test was performed and other test results were reviewed. It was concluded that the pump was operable and not degraded throughout the time period in question. <br /><br /> Corrective actions to prevent recurrence are aimed at improving system engineers' knowledge of the Inservice Testing program requirements and to improve turnovers of system responsibilities between system engineers.
2821997011 | Prairie Island 1, Prairie Island 2 | 10/03/1997 | 10/31/1997 | 9711120176 | <strong>Failure to test the low pressure auto-start function of 121 motor-driven cooling water pump and inadequate separation between Trains A and B low pressure auto-start switches</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1997, Unit 1 was in coastdown at 94% power and Unit 2 was at 100% power. As part of investigations under way per Generic Letter 96-01, it was determined that the low pressure auto-start of No. 121 Motor-Driven Cooling Water Pump was not being tested as required. Plant walkdowns and analysis also revealed that inadequate electrical separation exists between the No. 121 Motor-Driven Cooling Water Pump low header pressure switch and the No. 12 Diesel-Driven Cooling Water Pump low header pressure switch.
2821997012 | Prairie Island 1, Prairie Island 2 | 10/09/1997 | 11/07/1997 | 9711170058 | <strong>Chemical and Volume Control System Malfunction Unanalyzed for Boron Dilution During Shutdown Modes of Operation.</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1997, Unit 1 was in coastdown at 89% power and Unit 2 was at 100% power. As part of the USAR review and update project, the engineering staff identified that operation of the plant during hot or cold shutdown with the shutdown margin required by Technical Specifications would not provide the time identified in the USAR for operator action to mitigate an inadvertent boron dilution. The engineering staff also identified a potential boron dilution accident not described in the USAR resulting from RHR directly injecting to the vessel without adequate mixing. <br /><br /> Procedures have been modified to maintain increased shutdown margin during hot and cold shutdown. Procedures are being reviewed to identify activities with RHR direct vessel injection and to appropriately modify these activates. <br /><br /> This event will be analyzed and any necessary revision to the Technical Specifications will be submitted.
2821997013 | Prairie Island 1 | 10/18/1997 | 11/17/1997 | 9711280150 | <strong>Inoperability of Auxiliary Feedwater and Entry Into Tech Spec 3.0.C Due to Auxiliary Feedwater Manual Start During Planned and Orderly Shutdowm.</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1997, Unit 1 was in Mode 3 as part of a planned and orderly shutdown for a scheduled refueling outage. As per procedure, the 12 Auxiliary Feedwater (AFW) pump selector switch was placed in MANUAL and the 12 AFW pump was started to provide feedwater to the steam generators for reactor decay heat removal. After starting the 12 AFW pump, the selector switch for the 12 AFW pump was placed in SHUTDOWN AUTO. <br /><br /> The time the 12 AFW pump selector switch was maintained in MANUAL rendered the 12 AFW pump INOPERABLE. Because Technical Specification 3.4.13.2 did not contain any action statements applicable to Mode 3, Technical Specification 3.0.C was entered. A License Amendment Request will be prepared and submitted to clarify the OPERABILITY in Technical Specifications of the Auxiliary Feedwater system during plant evolutions.
2821997014 | Prairie Island 1, Prairie Island 2 | 10/28/1997 | 11/24/1997 | 9712080069 | <strong>Maintenance Shop Fire in the Service Building</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, Unit 1 was in Mode 6 and Unit 2 was in Mode 1 at 100% power. At 0845 hours the Control Room was informed of a fire in the Maintenance Shop located on the 735' elevation of the Service Building. The fire brigade was dispatched at 0846 hours and an evacuation of the turbine building was declared at 0850 hours. <br /><br /> An air filtration unit attached to a welding and cutting table in the shop had a small fire smoldering in its lower hopper which was being fanned by the open station air supply to the unit. At 0904 hours the station air supply to the unit was identified and isolated. The dense smoke from the unit subsided and the small smoldering fire was extinguished. <br /><br /> The evacuation was lifted at 0936 hours and by 1016 hours all fire protection and detection systems were returned to normal. Twelve employees exposed to smoke were treated onsite and released to return to work.
2821997015 | Prairie Island 1, Prairie Island 2 | 11/03/1997 | 12/03/1997 | 9712090084 | <strong>Both Trains of Control Room Special Ventilation System Simultaneously Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1997 events were identified which previously had resulted in the inoperability of both trains of control room ventilation. Inoperability of both trains of control room ventilation is a condition prohibited by Technical Specifications. These events had occurred during previous performances of a monthly surveillance, in which the outside air supply dampers to the control room ventilation system were opened. Some of these dampers would not have closed on a safety injection signal or high radiation in the control room. These dampers must close in order for the system to be on 100% recirculation, which is the initial post-accident configuration. Because operation with outside air supply dampers open after an accident could have resulted in a condition where neither train may have had the capacity to maintain control room operator doses below GDC 19 criteria, both trains of control room ventilation should have been considered inoperable.
2821997016 | Prairie Island 1, Prairie Island 2 | 11/19/1997 | 12/19/1997 | 9712290080 | <strong>Reactor Coolant Pump Lube Oil Lift Pump Oil Leak Collection System Design Not in Compliance with 10 CFR 50 Appendix R Section III.O)</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1997, Unit 1 was in Mode 6 and Unit 2 was in Mode 1 at 100% power, when a preliminary conclusion based on engineering judgment was made that the lube oil collection systems installed on the Unit 1 Reactor Coolant Pumps (RCP) did not fully comply with the prescriptive requirements of 10 CFR 50 Appendix R Section III.O. <br /><br /> A potential pressurized leakage site from the oil lift pump and associated piping for 11 RCP and 12 RCP would not be captured by the collection pans of the installed RCP lube oil collection system. <br /><br /> Before restarting Unit 1, a seismically qualified splash shield was installed over the oil lift pump and piping to divert any potential leakage to the collection pan directly below the pump. <br /><br /> At the next refueling outage for Unit 2 (or mid-cycle if conditions permit), a seismically qualified splash shield will be installed over each RCP oil lift pump and piping to divert any leakage to the collection pan directly below the pump.
2821997017 | Prairie Island 1 | 12/06/1997 | 01/05/1998 | 9801130147 | <strong>Separation of Pressurizer Level Indication Channels Not in Compliance with 10 CFR 50 Appendix R Section III.G.2</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1997, Unit 1 was in Mode 5 after completing a scheduled refueling outage. A meeting of the plant Operations Committee (OC) was held that afternoon to evaluate the reportability of issues associated with a modification package presented for OC review that morning. This modification package was for the installation of a noncombustible radiant heat shield around cabling to pressurizer level transmitter 1LT-433, where it is within 20 ft of cabling to pressurizer level transmitter 1LT-426. After reviewing the available material and questioning the involved staff, it was concluded that the condition of cabling to 1LT-433 and 1LT-426 did not satisfy the separation criteria of 10CFR50 Appendix R Section III.G.2. Notification was made pursuant to the requirements of 10CFR50.72(b)(1)(ii) for the plant being in a condition that is outside its design basis. <br /><br /> A noncombustible radiant energy shield has been installed over the cabling associated with transmitter 1LT-433 where it is within 20 ft of cabling associated with transmitter 1LT-426.
2821997018 | Prairie Island 1, Prairie Island 2 | 12/07/1997 | 01/06/1998 | 9801130383 | <strong>Failure to Test the Auto-Start Feature of the Control Room Ventilation System Air Handlers due to Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 7, 1997, Unit 2 was operating at 100% power and Unit 1 was shutdown for refueling. As part of investigations underway per Generic Letter 96-01, it was determined that the 121/122 Control Room Air Handler "Auto-Start" from its associated 121/122 Control Room Cleanup Fan is required to be surveillance tested by Technical Specifications but was not. <br /><br /> The auto-start feature had not been formally tested due to oversight during original surveillance development. This oversight was discovered during the review being performed in response to Generic Letter 96-01, "Testing of Safety-Related Logic Circuits." At the time of discovery, the autostart function of the 121/122 Control Room Air Handler had been demonstrated functional within the most recent required surveillance interval. The testing requirements are being incorporated into an existing surveillance procedure.
2851997001 | Fort Calhoun | 01/22/1997 | 02/21/1997 | 9702260367 | <strong>Main Steam Outside of Design Basis Due to an Error in Safety Valve Analysis</strong><br /><i>Abstract:&nbsp;</i>Following the report by Millstone Unit 2 of a problem with the calculation of Main Steam Safety Valve (MSSV) setpoints on September 3, 1996, Fort Calhoun Station (FCS) began an investigation to determine if similar issues applied. It has been determined that on only one occasion, over the life of the plant, have the number of inoperable MSSVs exceeded the design basis as recalculated due to this incident. discovered that the pressure drop to the MSSVs was not being taken into account. <br /><br /> The root cause of this event was an inadequate vendor review of a CESEC code modeling. When the code modeling was originally developed, the analysis methodology should have accounted for piping pressure losses associated with flow. CESEC does not have the capability for directly modeling pressure drop in the piping. Therefore, the potential existed for pressure to exceed the code allowed during a single Main Steam (MS) isolation valve closure event. <br /><br /> OPPD has performed the necessary analysis to update the design basis of the plant to account for the error discover and reported in this LER. Guidance has been provided to the operating staff to ensure that the design basis is maintained. A revision to the FCS Technical Specifications will be submitted to appropriately reflect the new design basis.
2851997002 | Fort Calhoun | 04/14/1997 | 05/14/1997 | 9705200250 | <strong>Charging Pump Outside Technical Specification for Alternate Shutdown Panel</strong><br /><i>Abstract:&nbsp;</i>Due to questions by the plant Operations Staff, Licensing was requested to determine if a Technical Specification (TS) (2.15(4) or (5)) seven day LCO should be entered if charging pump CH-1B is inoperable, since its control circuit is on the Alternate Shutdown Panel (ASP). Licensing determined that the specification should apply. A review indicated that during 1991 with the plant in Mode 1, CH-1B had been out of service for 10 days 17.5 hours. This violated the intent of TS 2.15(4) for CH-1B. On April 14, 1997, the Plant Review Committee (PRC) determined that this event was prohibited by the plant TS. <br /><br /> The root causes for this problem were: (1) ineffective communication between the Omaha Public Power District (OPPD) and the NRC regarding Amendment 125 to plant TS 2.15, and (2) lack of adequate management review to ensure that the wording of TS 2.15(4) would meet the intent of the requests of the NRC. <br /><br /> Guidance has been provided to the operating staff to ensure the intent of the TS is met until a revision to the TS can be processed.
2851997003 | Fort Calhoun | 04/21/1997 | 05/20/1997 | 9705230301 | <strong>Manual Reactor Trip Due to a Steam Line Rupture</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1997 at 2023 with the plant operating at 100% power, a section of the high pressure turbine fourth stage extraction steam line ruptured at a large radius elbow (sweep) resulting in the Control Room Operators manually tripping the reactor. Although several secondary systems housed in the Turbine Building were damaged, safety related systems functioned as required, and the reactor was safely shutdown. There were no personnel injuries resulting from this event. <br /><br /> Preliminary information suggests that the physical cause of the steam extraction line rupture was Flow-Accelerated Corrosion (FAC). It was determined that over-reliance was placed on one factor, that typically wear rates for sweeps are low, consequently omitting the failed site from previous inspections. Consideration of other factors (e.g., industry experience/industry practice) could have resulted in selection of the failed site for inspection. <br /><br /> Corrective actions include replacing the affected piping and inspecting and replacing additional piping as needed. Long term corrective actions include completing the failure analysis of the affected pipe and upgrading the erosion corrosion program.
2851997004 | Fort Calhoun | 05/05/1997 | 08/13/1997 | 9708200071 | <strong>Diesel Generator Outside of Design Basis due to a Violation of Appendix R</strong><br /><i>Abstract:&nbsp;</i>During an April 1997 review of the equipment credited for Control Room/Cable Spreading Room fire safe shutdown, it was determined that the Diesel Generator No. 2 (DG-2) speed sensing circuit's analog output was not capable of being isolated from the Control Room/Cable Spreading Room. A fire in the Control Room could have caused a short circuit of the tachometer or applied 120 VAC or 130 VDC voltage across the speed sensing switch tachometer loop output terminals, which could have damaged the speed switch built-in power supply. In addition to providing output to the tachometer circuit, the speed sensing switch also provides power to four set-point relays. Three of these four relays function to prevent the secondary air start motor from engaging if the engine exceeds 40 rpm, disengage the air start motors and open the DG-2 outside air dampers at 100 rpm, and flash the generator field at 750 rpm. Since the speed sensing switch has a common built-in power supply for the tachometer circuit as well as for the set-point relays, its damage could have resulted in not only the tachometer circuit becoming inoperable, but also could have deenergized or rendered the set-point relay circuits inoperable. This could have adversely affected the operation of the DG-2. The issue does not involve any common mode failure, only DG-2 is credited for meeting the Appendix R requirements.
2851997005 | Fort Calhoun | 05/30/1997 | 06/27/1997 | 9707090068 | <strong>Improper Entry into a High Radiation Area</strong><br /><i>Abstract:&nbsp;</i>At approximately 1500 on May 30, 1997, with Fort Calhoun Station operating in Mode 1 with a power ascension in progress. An equipment operator entered a High Radiation Area (HRA) without an integrating alarming dosimeter. This is a violation of Technical Specification 5.11.1. Technical Specification 5.11.1 provides for HRA access controls which are approved alternatives to the requirements of 10 CFR 20.1601(a). This event was caused by a lack of self-checking and inattention to detail on the part of the individual involved. Corrective actions include, discussion of this event with plant staff and disciplinary action taken against the individual involved.
2851997006 | Fort Calhoun | 06/06/1997 | 07/07/1997 | 9707110368 | <strong>Loss of All Fire Suppression Due to Inoperability of Fire Pumps</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1997 with the motor driven fire pump (FP-1A) inoperable, the blocking device used to prevent a start signal from the FP-1A control circuit to the diesel driven fire pump (FP-1B) moved out of position. As a result the diesel driven fire pump received a start signal. It failed to start due to sand in the pump. Pump FP-1B was declared inoperable at 1840 on June 6, 1997. With no fire suppression water systems operable, Standing Order SO-G-103 "Fire Protection Operability Criteria and Surveillance Requirements" requires that a backup fire suppression water system be established within 24 hours and the NRC be notified by an LER. Continuous fire watches were posted in the required areas of the plant. The fire main was aligned to the Water Plant for part of the time both pumps were inoperable. This source could have supplied water for manual fire suppression. Additionally, FP-1A was capable of being aligned to the fire main in a short period of time. This report is being submitted as required by plant procedure SO-G-103.<br /><br /> The inoperability of the fire pumps was due to an atypical set of operating circumstances and some problems with river sanding. <br /><br /> Plant procedures are being modified as needed to prevent a repeat of this event.
2851997007 | Fort Calhoun | 06/14/1997 | 07/11/1997 | 9707150262 | <strong>Failure to Satisfy Surveillance Requirement for Reactor Coolant flow</strong><br /><i>Abstract:&nbsp;</i>At 1850 on June 14, 1997, during the performance of OP-ST-SHIFT-0001, "Operations Technical Specification Required Shift Surveillance," it was discovered that the readings for Reactor Coolant System (RCS) flow voltages had not been recorded for the 1300 performance that day. The last recorded entry for RCS flow voltages was at 0658 on June 14, 1997. With a Technical Specification (TS) required frequency of shiftly, defined as every 8 hours, the TS required frequency had been exceeded. The Shift Technical Advisor (STA) and the Shift Supervisor (SS) reviewed the results of the 1300 performance of OP-ST-SHIFT-0001, and neither detected the missed readings, but signed the surveillance test review sheet signifying that the results were satisfactory. <br /><br /> The root causes for this event were the lack of self-checking by the Control Room operator taking the OP-ST-SHIFT-0001 readings and the inadequate reviews performed by both the STA and SS. <br /><br /> Corrective actions include re-emphasizing the need for adequate self-checking on logs and accurate review of documents to all operators and instituting the use of data loggers in the control room.
2851997008 | Fort Calhoun | 06/16/1997 | 07/16/1997 | 9707220411 | <strong>Improper Shift Staffing Due to Inadequate Control of Respirator Spectacle Kits</strong><br /><i>Abstract:&nbsp;</i>During a plant tour with an NRC Inspector on May 6, 1997, a station manager discovered that certain Licensed Operators (LO) did not have prescription respiratory glasses available to be used in response to an emergency if Self Contained Breathing Apparatus (SCBA) respirators were needed. A number of Fort Calhoun Station (FCS) LO are required by their individual licenses to wear glasses when operating plant equipment. <br /><br /> The root cause of this event is that the program for obtaining and maintaining the corrective lenses did not have appropriate administrative processes to ensure compliance with 10 CFR requirements. Additionally, individuals have not been accountable for obtaining and maintaining the spectacle kits if they needed them. A contributing cause of this violation is that the reduced use of respirators for routine work diminished the attention to the respiratory program and the need to maintain the spectacle kits. <br /><br /> LO who are regularly assigned to control room operations that require corrective lenses have either contacts or respirator spectacle kits available. The FCS Safety Manual was revised to add specific guidance for obtaining corrective lenses for respirators.
2851997009 | Fort Calhoun | 06/19/1997 | 07/21/1997 | 9707280279 | <strong>Potential Loss of Remote Shutdown Capability Due to Fire Induced Damage</strong><br /><i>Abstract:&nbsp;</i>Condition Report 199700679 was written to address a concern raised regarding Control Room evacuation due to a fire in the Cable Spreading Room. Procedure AOP-06, "Fire Emergency," did not provide adequate guidance to Control Room operating personnel as to when the Control Room should be evacuated due to a Cable Spreading Room fire. The decision to evacuate was left to the judgement of the Shift Supervisor (SS). The time when postulated spurious operation of valves could occur is dependent on the ability of the associated control cable to withstand the fire. Waiting too long to evacuate may have impacted the operability of equipment needed for a safe shutdown. <br /><br /> The root cause of this event is that the basis for evacuating the Control Room was not completely addressed in any design documents. <br /><br /> AOP-6 and other appropriate documentation have been updated to define the time for Control Room evacuation. The need for modifications is being reviewed to strengthen the Appendix R design of the plant.
2851997010 | Fort Calhoun | 07/31/1997 | 09/02/1997 | 9709080234 | <strong>Violation of Technical Specifications While Moving Spent Fuel in the Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1997, with the plant operating in mode 1 at 100% power, a Control Element Assembly (CEA) locking clip became disengaged from its fuel assembly during a fuel movement in the Spent Fuel Pool (SFP). Although the CEA was still inserted in the fuel assembly, this assembly is required by Technical Specification (TS) 2.8(11) to be mechanically coupled to a CEA for storage in Region 2 of the SFP. This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B) due to a condition prohibited by the plant's TS. <br /><br /> The root cause of this event was determined to be the inadequate design of the CEA locking clip. Failure to control the design and installation of the locking clip under the formal design process was identified as a contributing cause. <br /><br /> Corrective actions include moving the affected assembly to Region 1 of the spent fuel pool where it meets all TS fuel storage requirements without having the locking clip installed. The remaining four assemblies which require a CEA locking clip will be placed into Region 1 of the SFP. Storage of these assemblies in Region 1 does not require a CEA locking clip. The affected fuel assemblies will be administratively controlled to prevent a re-occurrence of this event.
2851997011 | Fort Calhoun | 08/19/1997 | 09/19/1997 | 9709240161 | <strong>Violation of Technical Specifications Due to Inoperability of a Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1997, with the plant operating at 100% power, RM-064 was declared inoperable due to slight leakage past isolation valve HCV-922. The basis for the inoperability determination was that leakage past the seat of HCV-922 would mix with the sample flow from HCV-921 and therefore RM-064 would not provide accurate information for determining dose rates if a tube rupture occurred in RC-2A. On August 19, 1997 it was noted that there was a difference in operability calls between the 1997 event and a similar event in 1996. As a result of this review it was determined that the condition noted in 1996 was a violation of Technical Specification 2.21 Table 2-10 and was therefore reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The root cause of this event was determined to be a lack of depth in evaluation/review by station personnel. <br /><br /> Operating Instruction, OI-RM-1, "Radiation Monitoring," and other appropriate procedures (such as surveillances) will be revised to require that if either HCV-921 or HCV-922 leak by that RM-064 must be declared inoperable.
2851997012 | Fort Calhoun | 08/21/1997 | 09/22/1997 | 9709260271 | <strong>Inadvertent Isolation of All Containment Spray Due to Operator Error</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1997, with the Fort Calhoun Station operating at 100 percent power, a Licensed Operator (LO) unknowingly rendered all Containment Spray (CS) inoperable for approximately 12 hours. The LO was performing a Technical Specification quarterly surveillance and post maintenance test. During the performance of the test he misunderstood the directions of the test procedure and took the hand control switches for valves HCV-344 and 345, the CS header isolation valves, to the "OVERRIDE" position. This position prevents these valves from automatically opening. <br /><br /> The reasons for this event can be traced to four causes. First is the skill based slip of the operator performing the surveillance and the other on-shift operators to make the mental connection that the CS system was disabled. Second was failure to fully implement self-checking. Third was communication with respect to annunciators as they alarmed and turnover of annunciator and plant status to the oncoming crew. Finally, fourth is inadequate corrective action to prevent recurrence and inadequate management oversight and observation on corrective action effectiveness and improvement. <br /><br /> When discovered, immediate action was taken to restore the valves to an operable condition. Additionally, administrative and procedural actions are being taken to minimize the potential for recurrence of this type of event.
2851997013 | Fort Calhoun | 08/26/1997 | 09/25/1997 | 9709300022 | <strong>Voluntary Entry into the General Shutdown Technical Specification Action Statement</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1997, at 2134 Central Daylight Time (CDT), the Fort Calhoun Station (FCS) entered Technical Specification (TS) 2.0.1 "Motherhood" to facilitate repair to a plant inverter. <br /><br /> The general shutdown specification (TS 2.0.1) was entered as part of the repair process for the switch that had failed causing the "A" Inverter to be declared inoperable. <br /><br /> The inverter switch was successfully replaced and tested satisfactorily. The plant shutdown was terminated and a power ascension was started. The plant was returned to full power.
2851997015 | Fort Calhoun | 10/17/1997 | 11/17/1997 | 9711210268 | <strong>Unanalyzed Condition for the Station Batteries</strong><br /><i>Abstract:&nbsp;</i>During a review of the Direct Current (DC) Distribution System described in the Updated Safety Analysis Report (USAR), a discrepancy regarding the operation of the station batteries without battery charger operation in the event of a Design Basis Accident (DBA) was identified. No analysis exists to support the Fort Calhoun Station (FCS) USAR battery capacity requirements without a charger during a DBA. There is an analysis of the 8-hour battery capacity for the Station Blackout (SBO) scenario. The station batteries are considered operable based on the similarities in DC loads needed to operate in response to the DBA and SBO scenarios and minimizing DC loads if a battery charger is lost. <br /><br /> It has been concluded that the root cause of the plant being in an unanalyzed condition is the lack of a detailed plant design calculation and/or analysis to provide the supporting information related to the eight-hour capacity requirement for the station batteries in the event of a DBA without battery charger operation. <br /><br /> The USAR verification project that discovered this issue is continuing. The approach of this USAR review will help ensure that other errors like this will be caught and corrected. A calculation is being developed to support the USAR requirement for the station batteries.
2851997016 | Fort Calhoun | 10/29/1997 | 11/26/1997 | 9712030224 | <strong>Nuclear Fuel Potentially Outside of the Manufacturer's Fuel Design Criteria</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, Westinghouse informed Fort Calhoun Station (FCS) of issues regarding fuel rod internal pressure, the status of the PAD code (a Westinghouse fuel performance code), and concerns with the fuel rod design criteria. When initially notified, FCS was advised that Westinghouse could not preclude the possibility of plants with Integral Fuel Burnable Absorber (IFBA) fuel being outside their fuel design criteria due to fuel clad gap reopening, and that the 17 percent maximum cladding oxidation limit, as delineated in 10CFR50.46, may be exceeded. Since that time, and based on the LOCA analyses which have been performed to date by Westinghouse, an initial pre-transient 12 percent oxidation has been established as a screening criteria to permit assessment of plants regarding compliance with the 17 percent maximum cladding oxidation criterion of 10CFR50.46. OPPD was informed by Westinghouse that FCS will not exceed the 12 percent oxidation criteria prior to the end of the current operating cycle. FCS had previously planned on replacing Westinghouse Zirc-4 fuel with either Westinghouse ZIRLO fuel or non-Westinghouse fuel during the 1998 refueling outage. This fuel replacement will help resolve this issue.
2851997017 | Fort Calhoun | 11/07/1997 | 03/20/1998 | 9803260113 | <strong>Low Pressure Safety Injection in an Unanalyzed Condition Due to Potential for Voiding</strong><br /><i>Abstract:&nbsp;</i>While reviewing recent industry operating experience on the potential for nitrogen voiding in safety injection systems, the Omaha Public Power District (OPPD) determined that a similar condition may exist for the Fort Calhoun Power Station (FCS). An engineering susceptibility evaluation was performed for the FCS which indicated that the Low Pressure Safety Injection (LPSI) and High Pressure Safety Injection (HPSI) systems at FCS have the potential for water hammer should nitrogen voiding occur in the systems. The evaluation indicates that several supports would have reaction loads exceeding design allowables for the LPSI system from water hammer if voiding existed. <br /><br /> Based on previous SI tank leakage and potential for low header pressure, the SI system may have voided and been in an unanalyzed condition in the past. No comparable voiding has occurred in the HPSI system. Based on a review of design documents it has been inferred that the plant's architect engineer did not consider water hammer in the piping and support design. <br /><br /> OPPD will modify the system to install vents at appropriate locations. System performance will be monitored to determine the effectiveness of this solution.
2861997001 | Indian Point 3 | 01/02/1997 | 01/31/1997 | ML10049108 | <strong>Inadvertent Actuation of the 32 Auxiliary Boiler Feedwater Pump After Closing the 31 Emergency Diesel Generator Manual Output Breaker Switch During Testing</strong><br /><i>Abstract:&nbsp;</i>On January 2, 1997, with the plant at approximately 97 percent power and normal temperature and pressure, a Control Room (CR) operator observed that a normally alarmed condition for the turbine driven Auxiliary Boiler Feedwater (ABFW) pump 32, cleared and that the pump was in operation. A 'Non-Safety Injection (SI) Blackout Logic Defeated' alarm was expected as a result of a test being performed on the 31 Emergency Diesel Generator (EDG), which closed the manual output breaker switch to tie the 31 EDG to 480 Volt Bus 2A/3A. The clearing of the alarm for the ABFW pump was not expected. Operators determined that there were no plant conditions requiring operation of the 32 ABFW pump, and shutdown the pump. The event was recognized as a repeat of an event with EDG 32 reported in LER 96-015. Investigations determined that the auto start circuitry for the 32 ABFW pump actuated and sealed-in because a slip contact for the 31 EDG manual output breaker switch did not close when manipulated by an operator. The probable cause was a mechanical problem with a slip contact in the 31 EDG manual output breaker control switch resulting in a failure of the 'Non-SI Blackout Logic Defeated' circuitry to makeup, allowing the 'Non-SI Blackout Bus 3A circuitry to makeup and actuate the auto start circuit when the 31 EDG switchgear tied to 480 Volt Bus 2A/3A. Corrective actions included assessments that determined that the 32 ABFW pump was operable, functional testing of the 31 EDG, performance of an operability check on EDG 32 and EDG 33, and procedure revisions to alert operators of a possible auto start of the ABFW pump when testing the EDGs. The manual output breaker switch for EDGs 31, 32, 33 will be replaced in Refueling Outage 9 and testing/failure analysis performed to determine the specific cause. This event had no effect on the health and safety of the public.
2861997002 | Indian Point 3 | 01/23/1997 | 02/21/1997 | ML10049109 | <strong>CIVs for the Hydrogen Monitoring System were Open During Testing but Not Listed in the Tech Spec Table of Non- Automatic Valves Open Continuously or Intermittently Due to Personnel Error: A Condition Prohibited by Tech Specs.</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1997, with the plant at hot shutdown, engineering identified that the control circuitry for the containment isolation valves of the two hydrogen monitor unit's sample lines did not meet single failure criteria. The Engineered Safety System (ESS) relays that provide the containment Phase A isolation signals to the containment isolation valves (both inboard and outboard) for the sample lines for each hydrogen monitor unit are powered from only one safety related power source. The configuration ensures, assuming a single failure and manual isolation of WCCPPS, the capability to monitor the post-accident containment atmosphere in accordance with Regulatory Guide 1.97. A postulated accident and single failure during testing does not ensure automatic containment isolation, but remote manual isolation from the control room is maintained. Further evaluation determined this configuration met design regulatory requirements. The condition is being reported because CIVs, that were not listed in the Technical Specification (TS) table of valves as 'allowed' to be open continuously or intermittently, were opened during periodic testing. Failure to meet the containment integrity requirements of the TS is considered a condition prohibited by TS. The cause of the condition was personnel error that failed to incorporate the replacement valves on TS Table 3.6-1 in an amendment which reflected replacement of the original manual valves with solenoid operated valves. Corrective actions include an amendment to TS to provide the proper valve listing, FSAR changes, and an interim action to allow testing only if entering an LCO action statement for containment integrity when the hydrogen monitor isolation valves are open. This event had no effect on the health and safety of the public.
2861997003 | Indian Point 3 | 03/13/1997 | 08/15/1997 | ML10049115 | <strong>Discovery of a Design Deficiency in the DC Power System That Causes Inadequate Emergency Power Due to a Postulated Single Failure During Use of a Backup Battery Charger Resulting in the Plant Being Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 13, 1997, with the plant at 100 percent power and normal temperature and pressure, operations reported the plant outside design basis as a result of an engineering determination that there was a design deficiency in the 125 volt DC Electrical Distribution System (EDS) power supplies due to an inability of the system to meet single failure criteria during use of a backup battery charger (BC). The reported condition existed periodically since a design modification added a backup battery charger (BC-35) to the 125 volt DC EDS and powered it from a 480 volt AC bus that is supplied from one of three Emergency Diesel Generators (EDG-33). When BC-35 is used in lieu of a normal charger to sustain the DC power supply supporting one of the other two EDGs, a Loss of Offsite Power or Safety Injection and a postulated single failure to EDG-33, or its associated bus/power circuit could result in loss of two BCs. Subsequent battery depletion could result in loss of one of the two remaining EDGs. The potential loss of two of three EDGs places the plant outside its design basis. The event was caused by the original classification of BC-31, 32, 33 as non-seismic which was relied upon for the modification to add BC-35 and resulted in no consideration of cross-tie effects. Further review determined that the non-safety classified BC's perform a safety function. The cause of classifying the BC's originally as non-seismic was the unavailability of qualified BCs, but the failure to adequately justify their classification could not be determined. Corrective actions include an evaluation to document the BC's design basis, re-classification of BCs 31, 32, 33, 35 as Seismic Class I/QA Category I, revision of procedures, and issuance of a temporary modification for limited use of BC-35. This event had no significant effect on the health and safety of the public.
2861997004 | Indian Point 3 | 04/25/1997 | 05/27/1997 | ML10049111 | <strong>The Fuel Storage Building Emergency Ventilation System Was Inoperable During Movement of the Cask Crane Over the Spent Fuel Pit Due To Failure To Perform All Required Testing; A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1997, with the plant at 100 percent power and normal temperature and pressure, Operations concluded the Fuel Storage Building (FSB) Emergency Ventilation System (EVS) was inoperable because all testing required by Technical Specifications (TS) 4.5.A.6.c was not performed. On April 17, 1997, as a result of a chemical release during roof repair, the TS for the FSB EVS was entered and the charcoal absorber filter (HECA) tested. The particulate (HEPA) filters were not tested because only the HECA was considered to be potentially affected by a chemical release. After successful testing of only the HECA, the FSB EVS was declared operable on April 19, 1997, and cask crane was allowed to be moved over the spent fuel pit. The NRC questioned the operability of the FSB EVS on April 24, 1997, after observing that all the testing identified in the TS was not performed. After further evaluation, operations concluded that all TS required testing should have been performed and declared the FSB EVS inoperable. TS requires the FSBEVS to be operable whenever irradiated fuel is being handled or the spent fuel cask or cask crane is moved over the spent fuel pit. Because the FSB EVS was not tested in accordance with the TS and subsequently considered to be inoperable during the time the cask crane was allowed to be moved over the spent fuel pit, a condition prohibited by TS existed. The cause was personnel error due to failure to follow the wording in the TS. Corrective actions include performing a complete test of the filter system, issuing a shift order notifying operators of the requirements of the TS, instruct licensed operators on use of TS section 4, and changes to applicable test procedures. This event had no affect on the health and safety of the public.
2861997005 | Indian Point 3 | 05/14/1997 | 06/06/1997 | ML10049112 | <strong>Manual Reactor Trip Initiated Due to Overpower Delta T Channel Signal and Turbine Runback</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1997, with the plant at approximately 74%, reactor operators initiated a manual reactor trip in response to a turbine runback. The runback was due to an Overpower Delta-T Channel Signal in one of the four loops. Control Room indications did not indicate that the setpoint was exceeded, but the bistable alarm light was illuminated. The plant was stabilized at hot shutdown and subsequent decisions were made to proceed to cold shutdown for early commencement of a scheduled refueling outage. All safety related and major plant equipment involved in the trip operated as expected. Operators and plant personnel responded in an appropriate manner using conservative decision making, good communication and direction, and proper procedure adherence. Corrective actions included the performance of a post trip evaluation in accordance Administrative Procedures. I&C Engineering is performing an Equipment Failure Evaluation (EFE) to determine the actual cause of the overpower delta-T runback signal. This event did not affect the health and safety of the public.
2861997006 | Indian Point 3 | 05/08/1997 | 06/06/1997 | ML10049112 | <strong>Plant Outside Design Basis Due to Error In Original Design That Did Not Identify RWST Purification Loop Isolation Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1997, with the plant at 95 percent power, Engineering determined that the plant had been operated outside the design basis in the past when the Refueling Water Storage Tank (RWST) was aligned to the non-seismic purification loop of the Spent Fuel Pit Cooling Loop because design requirements for isolation had not been identified and proceduralized. A failure of the purification loop pressure boundary, without proper provisions for isolation, would affect the RWST inventory available for the safety injection system. The event was due to personnel error during the original design process. The corrective action was to establish administrative controls to require a trained person at isolation valves AC-727A and AC-727B during operation of the RWST purification loop while above cold shutdown to assure the system is isolated following an earthquake, safety injection or as required by the control room. The feasibility of plant modifications is being assessed. An extent of condition review is underway. There was no significant effect on public health and safety.
2861997007 | Indian Point 3 | 05/20/1997 | 06/19/1997 | ML10049112 | <strong>Past Operation of the Service Water Discharge Throttle Valves SWN 35-1 And SWN 35-2, May Have Placed the Plant Outside Design Basis due to Human Error.</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1997, with the plant in a cold shutdown condition, NYPA determined that the sequence of emergency operating procedure (EOP) steps to re-position the service water discharge throttle valves on the component cooling heat exchangers had potentially placed the plant outside its design basis. The EOP may not have ensured the design basis accident minimum service water flow requirements were met. During a postulated loss of coolant accident and prior to going on recirculation these manual valves needed to be repositioned open to a predetermined throttled position to provide sufficient heat removal capability. During normal operation these valves were throttled below the prescribed setting to maintain component cooling water temperature within the normal operating range due to seasonal river water temperature conditions. The cause was human error during the revision of the EOPs and non-formal implementation of design basis information. An operability determination established the minimum required throttle positions for fifty degree river water and this requirement was implemented until the current outage started. Service water and component cooling water EOP steps have been verified to comply with design. Additional review of EOPs may be required and this will be identified prior to plant startup. A procedure change will be issued to include the operational limits required to ensure the design is maintained. This event had no affect on the health and safety of the public because, based on preliminary engineering evaluation, the associated components are believed to be able to perform their function during the postulated event.
2861997008 | Indian Point 3 | 06/16/1997 | 07/16/1997 | ML10049113 | <strong>Automatic Actuation of Emergency Diesel Generators Following a Loss of Offsite Power Due to a Personnel Error that Inadvertently Grounded the Feed to the Station Auxiliary Transformer</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1997, at approximately 1020 hours, with the plant shutdown for a refueling outage, Indian Point 3 lost offsite power from 138KV feeder 33332 that was supplying plant loads from the Station Auxiliary Transformer (SAT). The loss of power initiated an automatic start of Emergency Diesel Generators (EDG) 32 and 33. EDG 31 was out of service for maintenance. EDG 32 and EDG 33 automatically started and closed on their safeguards 480 volt buses 6A and 5A. The assigned loads for bus 6A would not automatically sequence or allow remote manual loading due to a blown fuse in the undervoltage protection circuitry. Reactor core cooling was being provided by a Residual Heat Removal (RHR) pump until power was lost. Spent fuel pool cooling was restored at approximately 1055 hours after its power supply was reset. offsite power was available from one of two 13.8Kv feeders. Power was restored to 6.9Kv bus 6 from the 13.8Kv feeder system at approximately 1058 hours. RHR pump 31 started to restore forced core cooling at approximately 1103 hours. Restoration of the 138 Kv system to buses 5A and 6A was completed at 1344 hours. Offsite power was lost for approximately 43 minutes. Loss of feeder 33332 was a result of efforts in the Buchanan substation to apply a ground for scheduled maintenance. A Consolidated Edison Company substation operator mistakenly applied the wrong ground switch, shorting the 138Kv feed that supplies power to the SAT. The cause of the power loss was personnel error due to a failure to follow an approved procedure and perform self checking. Corrective actions included counseling of yard operators on procedure adherence/self checking, assessing the adequacy of coordinating offsite switching activities, and implementing an action plan for correcting deficiencies discovered during event recovery. There was no effect on public health and safety.
2861997009 | Indian Point 3 | 06/18/1997 | 07/18/1997 | ML10049114 | <strong>Automatic Actuation of an Emergency Diesel Generator Following a Loss of Normal Power Feed to a Safeguards Bus</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1997, at approximately 0156 hours, with the plant in a refueling condition and no core alterations in progress, Indian Point 3 lost the normal feed to 480 volt bus 6A when its feed breaker opened. Offsite power was being supplied to 480 volt safeguard bus 6A through feed breaker 52-6A from 6.9 Kv bus 6. The undervoltage condition on bus 6A initiated an automatic start of Emergency Diesel Generator (EDG) 32. EDG 32 automatically started and re-energized bus 6A. Component Cooling Water (CCW) pump 33 and Service Water (SW) pump 36 were shed from their assigned bus 6A on undervoltage, sequenced back onto the bus and re-started by a Non-SI Blackout logic signal. The 32 CCW pump powered from a redundant 480 volt bus automatically started on low pressure. Residual Heat Removal cooling and spent fuel pool cooling remained operating during this event. Restoration of the normal power feed to bus 6A was completed at approximately 0243 hours. The specific cause could not be determined but the most likely cause was personnel error. The job supervisor was counseled, procedures controlling work were reviewed and will be enhanced with appropriate information to limit trip hazards. There was no effect on public health and safety.
2861997010 | Indian Point 3 | 06/18/1997 | 10/14/1997 | ML10049120 | <strong>Less than the required number of Emergency Diesel Generators were Operable Due to Loss of Ventilation resulting from an Inadvertent Operation of a Carbon Dioxide Systems; A Condition Prohibited By Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1997 at approximately 0845 hours with the plant in cold shutdown and the 31 Emergency Diesel Generator (EDG) inoperable for maintenance, Operations concluded 32 Emergency Diesel Generator (EDG) was inoperable. This resulted in less than the required number of EDGs operable; a condition prohibited by Technical Specifications. The inoperability of 32 EDG was based on the loss of 32 EDG room ventilation. The loss of 32 EDG room ventilation was caused by inadvertent operation of the carbon dioxide (CO2) system provided for 32 EDG room. This did not result in a CO2 discharge. Lack of ventilation could have allowed the temperature to exceed design temperature in 32 EDG room if 32 EDG had started. 32 EDG would have operated reliably until room temperature exceeded equipment qualification temperature of 126 degrees Fahrenheit. EDG combustion air is supplied by a snorkel to ensure continued operation of the EDGs with a fire in the associated diesel room. Subsequent investigation determined that all three EDGs could be susceptible to a similar failure due to inadvertent operation of a similar relay in each of the other EDG CO2 panels during an earthquake. A four hour report was made to the NRC pursuant to 10 CFR 50.72 (b)(2)(iii)(A) at 2212 hours on July 2, 1997. The cause of this failure was personal error due to inadequate failure and effects analysis for the 1980 modification that installed the CO2 system. Corrective actions included restoration of 32 EDG room ventilation to establish operability of 32 EDG. Further corrective actions included isolation of power to the CO2 actuation circuitry that initiates isolation of the EDG ventilation systems, isolation of CO2 supply and posting of continuous fire watch personnel in accordance with the fire protection Operational Specifications. This event had no effect on the health and safety of the public.
2861997011 | Indian Point 3 | 06/27/1997 | 09/24/1997 | ML10049117 | <strong>Incomplete Testing of Safety-Related Logic Circuits Fails to Fully Demonstrate Technical Specification Requirements; A condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1997 with the plant shutdown for a refueling outage, the Independent Safety Engineering Group determined that no surveillance test verifies that the feeder breaker for Motor Control Center 210 (MCC 210) is automatically stripped from the emergency safeguards bus by a safety injection /undervoltage signal as required by Technical Specification 4.6.A.3. This deficiency was identified as part of the Authority's drawing-to-procedure comparison review performed in accordance with Generic Letter 96-01. The MCC 210 feeder breaker was removed from service until testing on August 17, 1997 demonstrated proper operation of the affected contact in the load shedding circuit. <br /><br /> As part of this same review, during July 1997, the Authority identified six additional surveillance test deficiencies involving Technical Specification testing requirements. Four of these deficiencies are related to EDG load shedding / load sequencing logic, one involves start up of the Auxiliary Boiler Feed Pump, and one is for an ESF actuation signal to a containment isolation valve. The surveillance test procedures were revised and logic circuit testing was completed during August 1997, prior to start up from the refueling outage. There was no affect on public health and safety because testing with the revised procedures demonstrated that the logic circuits were working as designed. Additional corrective actions are planned to provide training to personnel responsible for the preparation and revision of surveillance procedures that test safety-related logic circuits.
2861997012 | Indian Point 3 | 06/30/1997 | 07/30/1997 | ML10049115 | <strong>A Common Condition Causing Multiple Core Exit Thermocouples to be Inoperable During Postulated Accident Conditions Due to Moisture Intrusion, an Original Manufacturer Defect</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1997, the unit was in cold shutdown due to a refueling outage and the core was off loaded to the spent fuel pool. It was determined that all twenty (20) safety-related core exit thermocouples may have been inoperable during postulated accident conditions because of an original manufacturing defect that results in moisture intrusion. The in-core thermocouples in question are original plant equipment and the exact time of the moisture intrusion condition is unknown. A meggar insulation resistance (IR) measurement on all Regulatory Guide 1.97 qualified thermocouples indicated that all of these thermocouples failed to meet the IR requirements. Upgrades or replacement of incore thermocouples were accomplished to return to twenty (20) Regulatory Guide 1.97 qualified thermocouples. It is believed that this event had no significant effect on the health and safety of the public.
2861997013 | Indian Point 3 | 07/21/1997 | 03/10/1998 | ML10049124 | <strong>Operation of 2 High Head Safety Injection Pumps, a Condition Prohibited by Technical Specification, Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1997, at approximately 1742 hours, while the plant was in the refueling mode, Operations concluded that the Indian Point 3 Technical Specification (TS) had been violated on or about June 1, 1992 when a test operated two high head safety injection pumps. TS 3.3.A.8 requires no more than one safety injection pump to be energized and aligned to feed the Reactor Coolant System (RCS) when the RCS cold leg temperature is at or below 332 degrees F. The probable cause was personnel error, a failure to identify the non compliance with the TS in the preparation and review of the test, with a misleading Technical Specification Interpretation (TSI) as a contributing factor. The corrective action includes past efforts to upgrade procedural preparation guidelines, upgrades to the engineering process, revisions to the test to allow one pump operating, withdrawal of the misleading TSI, a review and scheduled withdrawal of other TSIs, an upgrade to the TSI guidelines, and a proposed TS change to allow the testing currently prohibited. There was no safety significance since the test required the reactor head to be off, a condition during which the RCS could not be overpressurized.
2861997014 | Indian Point 3 | 08/05/1997 | 08/28/1997 | ML10049116 | <strong>Lack of Weld Channel and Containment Penetration Pressurization System Air Supply to Airlock Shaft Seals, Equalizing Ball Valve Flanged Joints and Containment Penetration Welds, a Condition Prohibited by Tech Specs Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This Licensee Event Report (LER) describes events pertaining to the lack of Weld Channel and Containment Penetration Pressurization System (WCCPPS) air supply to the 80' and 95' airlock shaft seals, equalizing ball valve flanged joints and containment penetration welds. At the time of discovery of these events, the plant was in cold shutdown condition due to a refueling outage. On August 5, 1997, at approximately 1852 hours, during installation of the 80' airlock shaft seal upgrade, it was discovered that the weld channel port to the existing door mechanism shaft seal had been blocked by the seal housing flange gasket. This condition prevented weld channel supply to the airlock door shaft seal. On 8/7/97, at approximately 1655 hours, the Authority discovered that the 3/4" pipe associated with 80' inner door seal pressure gauges PI-1434 A & B that directly penetrates the 80' airlock inner bulk head did not have WCCPPS air supplied to the containment boundary weld. It was also discovered that the equalizing ball valve flanged joints had no WCCPPS supply. An extent of condition review indicated that the same discrepancies existed on the 95' airlock. Corrective actions have been completed that ensure supply of WCCPPS air to the 80' and 951 airlock shaft seals, equalizing ball valve flanged joints and containment penetration welds. The purpose of WCCPPS is to prevent potential leakage of the Vapor Containment air to the surrounding environment and eliminate offsite doses in the event of a design basis accident. However, without WCCPPS, offsite doses would still be within the limits of 10 CFR Part 100. The cause of these events was personnel error. Repairs were made to correct these deficiencies. These events had no effect on the health and safety of the public.
2861997015 | Indian Point 3 | 08/01/1997 | 08/29/1997 | ML10049116 | <strong>Two Emergency Diesel Generators Inoperable During Refueling as a Result of the Loss of a Diesel's Room Ventilation During Maintenance on Another Diesel; A Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1997, at approximately 1005 hours, with the plant in a refueling condition and no core alterations in progress, Operations declared the 31 Emergency Diesel Generator (EDG) inoperable after the NRC resident inspector observed the 31 EDG Building ventilation damper open but no fan operating. An investigation discovered the 314 exhaust fan motor operating, the fan inoperable, and the ventilation damper for fan 314 open (the exhaust damper is interlocked with its fan motor). The redundant EDG 31 ventilation fan 315 was made inoperable by this failure mode because the flow path would be short circuited (fan 315 would pull air through damper 314 rather than through the EDG room). The plant was in a condition prohibited by Technical Specification 3.7 (EDG 32 was out of service for maintenance making 2 EDGs inoperable) from 1005 hours until ventilation was restored at about 1015 hours. The preliminary cause of the failure is a gap between fan shaft and it's bearing. Corrective actions included closure of the damper for fan 314, a preliminary equipment failure evaluation (EFE) by Maintenance identified upgrades to the installation procedure which were completed, fan 314 repairs, the other fans were disassembled and inspected, an EFE will be completed. Further corrective actions will be performed as necessary. A supplemental LER will be issued if the results of the EFE differ significantly. This event had no effect on the health and safety of the public.
2861997016 | Indian Point 3 | 08/06/1997 | 09/08/1997 | ML10049116 | <strong>Two Emergency Diesel Generators Rendered Inoperable by Engineered Safety Feature Logic Circuit Surveillance Testing; A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Safety Injection Test 3PT-R003C is conducted at a refueling frequency with the plant at cold shutdown conditions to verify that the safety injection system logic circuits perform as designed in accordance with Technical Specification 4.5.A.1.a. A portion of the test involves verifying logic circuits associated with operation of the Emergency Diesel Generators (EDG) in response to the test safety injection signal. This LER describes two cases in which performance of this test rendered two EDGs inoperable, which is a condition prohibited by Technical Specification 3.7.F.4. The first case occurred during tests performed prior to Refueling Outage 9 (RO9) and involves interrupting power to EDG support components for two EDGs at the same time. This condition was identified and corrected by a procedure revision prior to performing the test on August 8, 1997 for RO9. The second case occurred during the performance of the test on August 8, 1997 and involved tripping of the EDG lockout relay for two EDGs at the same time. The EDG lockout relays were reset within approximately five minutes and a procedure change was processed to prevent recurrence. There was no affect on public health and safety for either case because there was no actual loss of offsite power during these tests.
2861997017 | Indian Point 3 | 08/13/1997 | 09/12/1997 | ML10049117 | <strong>The Reactor Coolant System Over-Pressurization Protection System was Inoperable Due to Inadequate Procedure; A Condition Prohibited by Technical Specifcations</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1997, at approximately 1420 hours, with the plant in the cold shutdown condition, NYPA determined that two of three pressure inputs to the Over-Pressurization Protection System (OPS) circuitry were isolated, thereby making OPS inoperable. This is a condition prohibited by Technical Specification 3.1.A.8. A four hour report was made to the NRC pursuant to 10 CFR 50.72 (b) (2) (iii), at 2056 hours, on August 13, 1997. <br /><br /> The cause of the event was that the procedural requirements lacked specifics for verifying OPS operability prior to entering a plant condition that required OPS to be operable. Contributing causes were the failure of the appropriate personnel to recognize the isolation of the OPS pressure transmitters when two Protective Tagging Orders were applied and inadequate review of deviations from the Reactor Coolant System (RCS) system check off list. <br /><br /> Immediate corrective actions included depressurization of the RCS, securing the inservice charging pump and establishing a vent path by opening the Power Operated Relief Valves (PORVs). Further corrective actions will be to provide specific procedural requirements for verifying OPS operability prior to entering a plant condition that requires OPS. <br /><br /> This event had no effect on the health and safety of the public.
2861997018 | Indian Point 3 | 08/18/1997 | 09/17/1997 | ML10049117 | <strong>Containment Isolation Valve AC-751B Held Open During Plant Operation; A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Surveillance test 3PT-Q36 was performed on 7/24/97 with the plant in cold shutdown during Refueling Outage 9. The purpose of this,evolution in part, was to test component cooling water (CCW) check valve AC-751B, a containment isolation valve that is missile protected and a closed loop inside containment. Data obtained from this test indicated that valve AC-751B was not closing. This was documented in DER 97-1826. A review of this event o August 18, 1997 determined that due to the check valve not closing, containment integrity was not as defined in Technical Specations. Disassembly of the valve identified a 1/8 inch layer of corrosion in the valve body caused by a galvanic cell formed when the valve became stuck in the open position. This was documented in DER 97-1845. Engineering review determined that the cause of AC- 751B sticking open was wear of the mechanical travel stop, allowing the valve to open farther than normal, causing the valve to become jammed in the valve body in the open position. Corrective actions included removal of the corrosion from inside the valve and machining of the valve disk to preclude recurrence of jamming. This event had no effect on the public health and safety.
2861997019 | Indian Point 3 | 08/28/1997 | 09/25/1997 | ML10049118 | <strong>Steam Driven Auxiliary Feedwater Pump Full Flow testing Inadequate Due To Improper Procedure Change In 1978, A Condition Prohibited By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1997, the unit was in cold shutdown for a refueling outage. Engineering determined that the Technical Specification required- auxiliary feedwater pump full flow testing criteria was inadequate for the turbine driven pump. The flow rate acceptance criteria needed to be higher when considering the delay for control room operator action to speed-up the turbine driven pump and open its discharge valves during a postulated loss of normal feedwater transient. The safety evaluation report and final safety analysis report credit the auxiliary feedwater system as having pumps driven by diverse principles. The accident analysis assumed the flow rate of only one of two fully automatic motor driven pumps to mitigate design basis accidents. Therefore, redundancy to the extent of the required flow rate and the power supply to their motors can be assured with the two fully automatic motor driven pumps without crediting the semi-automatic turbine driven pump. An analysis and reasonable assurance of safety were performed to establish new testing and operating criterion to meet the license condition for diversity. A full flow test was performed satisfactorily with the new criteria. Emergency operating procedures were revised to assure the appropriate operator actions for the steam driven pump if a failure were to occur that rendered the two motor driven pumps inoperable during a postulated loss of feedwater transient. This event had no effect on the health and safety of the public.
2861997020 | Indian Point 3 | 09/03/1997 | 10/03/1997 | ML10049118 | <strong>Plant Outside Design Basis Due To Error In Original Plant Design Probably Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1997, with the plant in hot shutdown, the Independent Safety Engineering Group determined that the main boiler feed pump motor operated discharge valves would not close upon receipt of a feedwater isolation or safety injection signal if they were opening. These discharge valves have been opened in the past while starting up and following repairs while the plant was in a condition where the valves were credited for mitigation of a feedwater addition accident or a steam pipe rupture. The discharge valves, manufactured by Crane-Teledyne, have an "RY" relay circuit which is operated by the valve closed torque switch and valve open limit switch. The "RY" relay circuit is designed so that the valve closed torque switch (actuated when the valve is torqued shut) deenergizes the valve closing circuit and blocks reenergization until the valve reaches the full open position. If a feedwater isolation or safety injection signal is received while the valve is in an intermediate position, during the opening stroke, the valve will stop opening and reclosure is prevented. The cause is probably personnel error in original plant design. Administrative controls are in place to assure feedwater isolation, considering a single failure, when the valves are opened during startup. These administrative controls will be maintained until Engineering has assessed and completed corrective action. This event had no significant effect on the public health and safety.
2861997021 | Indian Point 3 | 09/06/1997 | 06/09/1998 | ML10049127 | <strong>One Train of Engineered Safeguards Logic out-of-service; A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1997, with the plant in hot shutdown (Reactor Coolant System temperature and pressure at 547 degrees F and 2235 psi, respectively), the Engineered Safeguards Features (ESF) relay logic system Train A was deenergized after evaluating alternative approaches for replacing a defective relay in the ESF cabinet. Because the Indian Point 3 Technical Specification does not have an action statement which addresses an ESF instrumentation train out-of-service, the actions of specification 3.0 were applied. Administrative Procedure, AP-21.9 was followed to implement a 13-hour time limit for reducing Reactor Coolant System temperature to below 350 degrees F. The defective relay was replaced and the Train A ESF relay logic system was returned to service in approximately 3 hours, at which time the requirements of specification 3.0 no longer applied. This report is being made because NUREG 1022 states that entry into Standard Technical Specification 3.0.3 or its equivalent for any reason or justification is reportable. The New York Power Authority has initiated action to revise the Indian Point 3 Technical Specification to identify the required actions for an ESF relay logic train being out-of-service. There was no affect on the health and safety of the public because the redundant ESF Train B was in service during the 3 hours that Train A was deenergized for the relay replacement.
2861997022 | Indian Point 3 | 09/11/1997 | 10/06/1997 | ML10049118 | <strong>Two Safety Injection Pumps Inoperable During a Design Basis Event May Have Placed the Plant Outside Design Basis Due to Inadequate Procedural Instructions</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1997, at approximately 1634 hours, with the plant at 30 percent power and normal temperature and pressure, NYPA determined that inadequate Emergency Operating Procedure (EOP) instructions could have caused two motor driven High Head Safety Injection (HHSI) pumps to operate without flow during the transfer to hot leg recirculation following a postulated Loss of Coolant Accident. <br /><br /> Containment Isolation Valves on the discharge header for the HHSI pumps are re-positioned to the closed position in accordance with EOP ES-1.3 when the HHSI system is not in operation. EOP ES-1.4, for re-aligning the plant for hot leg recirculation, did not account for this prior re-positioning. This could have resulted in the HHSI pumps being operated in a dead-headed configuration. <br /><br /> The cause was an inadequate procedure review attributed to the lack of instructions in the EOP review process and ineffective verification and validation when the requirements were added to the EOP ES-1.3 on June 12, 1989. <br /><br /> ES-1.4 was revised on August 25, 1997 to require the HHSI valves to be opened. A review of other safety related pump operation in the EOPs determined that isolation of non-automatic valves would not impact a system operation. <br /><br /> This event did not cause a significant increase in risk to the public health and safety.
2861997023 | Indian Point 3 | 09/09/1997 | 10/09/1997 | ML10049119 | <strong>Manual ESF Actuation of Auxiliary Feedwater Pumps due to Main Boiler Feedwater Pumps Tripping</strong><br /><i>Abstract:&nbsp;</i>During plant startup on September 9, 1997, with the plant at approximately 3-4 percent reactor power, both Main Boiler Feedwater Pumps (MBFP) trip alarms were received in the Control Room. The Operators manually started the Auxiliary Feedwater Pumps (AFWP), thereby initiating a manual ESF actuation prior to the automatic response. All safety related and major plant equipment involved in the trip operated as expected. The reason for the concurrent trip of both pumps is due to a high discharge pressure on the common line for both MBFPs caused by the increased speed of 32 MBFP. The cause of the event is believed to be a failure of the manual control station for the MBFP No. 32. Corrective actions included removing the controller and testing the output. The output was found to be stable. However it was determined that when the "T" handle was manually moved left or right it did not return to its center position smoothly. This can best be described as a slight drag compounded by a weak spring in the "T" handle switch. The controller was replaced by a new controller. MBFP No. 32 and the replaced controller were operating satisfactorily. Plant startup continued after the controller was replaced. This event did not affect the health and safety of the public.
2861997024 | Indian Point 3 | 09/10/1997 | 10/09/1997 | ML10049119 | <strong>Reactor Trip Due to a Turbine Trip as a Result of a Personnel Error During Turbine Generator Mechanical Trip Testing</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1997, with the reactor power at approximately 7 percent, a reactor trip (RT) occurred as a result of a turbine trip (TT) during a turbine generator (TG) trip test. During performance of a TG test, operators closed the switch stabs to the TT solenoids with the TT relays in the tripped condition. This operation re-instated the trips into the TT logic and initiated a TT. Reactor power (RP) was below the permissive P-10 actuation level and permissive P-7 was active. Operators knew that prior to the test one of the two inputs for the trip logic for actuating P-10 was active [Power Range (PR) channel]. The P-7 permissive includes a bypass of the TT signal to the reactor protection system which is activated with input from P-10. A RT occurred because another PR channel actuated and made up the trip logic, thereby defeating the P-7 bypass. The cause of the RT was an error in the test procedure which did not require the TT relays to be reset prior to reinstating these trips into the TT logic, and failure of operators to detect a change in permissive status (P-10/P-7 reset). The procedure error was introduced as a result of inadequate review of changes incorporated into the procedure. A contributing cause was failure to perform self checking during procedure use. Corrective actions include revision of the test procedure, verified operability and calibration of permissive bistables and indicators, review and validation of recently revised operating tests/procedures needed to be performed for startup which may cause a transient, and briefed the operating crew on STAR principles. An analysis will be performed on cause of the procedure and operator error. There was no effect on public health and safety.
2861997025 | Indian Point 3 | 09/15/1997 | 10/15/1997 | ML10049119 | <strong>Automatic Reactor Trip due to a High Resistance Contact on a Reactor Protection Relay While Testing An Analog Channel</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1997 the plant was operating at approximately thirty percent reactor power. At 1623 hours, the plant experienced an inadvertent automatic reactor trip when the logic for two out of four channels for low pressurizer pressure was completed. One channel was placed in trip as per procedure in order perform instrument channel testing in accordance with Technical Specifications. At that time, the logic relay for another channel was already effectively tripped due to a high resistance contact causing an insufficient voltage being applied to the corresponding reactor trip relay. After the trip, the relay with the high resistance contact was replaced. Voltage drops across contacts on reactor protection relays were measured, relay contacts were cleaned and found to be acceptable. Review of the plant trip identified that other protective equipment responded as designed after the trip. Corrective action to preclude future similar events will be developed by engineering to include a preventative maintenance program for reactor protective relays. The event had no affect on the health and safety of the public.
2861997026 | Indian Point 3 | 10/01/1997 | 10/30/1997 | 9711130230 | <strong>Individual was Granted Unescorted Access Based on Falsified Pre-employment Screening Records</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1997, at approximately 0945 hours, the access control Supervisor was advised by another utility that a contractor who had recently worked at Indian Point 3 had previously tested positive during a Fitness For Duty (FFD) test. The individual had unescorted access from May 13, 1997 to August 14, 1997. Investigation of his pre-employment screening records identified that he falsified information regarding a previous positive FFD test. Security concluded that authorization for unescorted access would have been denied had the Authority known of the contractor's background. Based on this information and guidance of Generic Letter 91-03, at approximately 1001 hours, the Authority determined the event was reportable, and made a one hour report to the NRC at approximately 1052 hours. The cause of the event was that the individual falsified personal background information required for unescorted access. Corrective actions included review of his background information, notification of the event to previous nuclear plants he worked at, assessment of the work he performed, updating of plant access records assessment of the completeness of the initial background investigation, notification to the individual that his access is now denied, and notification to the background investigator of a failure to perform an additional inquiry required by contract. This event did not constitute a risk to the health and safety of the public.
2861997027 | Indian Point 3 | 10/22/1997 | 11/21/1997 | ML10049121 | <strong>Two Boric Acid Flow Paths Out-of-Service Without an Allowed Outage Time; A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1997, at approximately 1510 hours with the plant operating at 100% power, a body-to-bonnet leak of approximately one-quarter to one-half gallon per minute was observed in a Boric Acid Filter Bypass stop valve. A catch containment was established and the leakage was monitored while corrective maintenance options were evaluated. On October 22, at approximately 1300 hours, various valves were closed and both boric acid transfer pumps (BATP) were isolated to establish the isolation boundary for the valve repair. The isolation rendered both BATPs and both boric acid flow paths inoperable, which are conditions prohibited by Indian Point 3 Technical Specifications 3.2.B.2 and 3.2.B.4. Since there was no allowed outage time specified, the Indian Point 3 equivalent of Standard Technical Specification 3.0.3 was applied, which is a reportable condition as stated in NUREG 1022. Repairs were completed and the BATPs and associated flow paths were returned to service at approximately 1500 hours on October 22, eliminating the need for a plant shutdown. <br /><br /> The cause of the event was that the action statements in Technical Specification Section 3.2.C do not provide Allowed Outage Times for each corresponding Limiting Condition for Operation in Section 3.2.B. The Authority will submit an Application for Amendment to propose improvements to this section of the Technical Specifications. There was no significant effect on the health and safety of the public because the repair duration was short (approximately 2 hours) and the Refueling Water Storage Tank remained available as an alternate source of boric acid solution during this period.
2861997028 | Indian Point 3 | 10/23/1997 | 11/21/1997 | ML10049120 | <strong>The Safety Injection System Was Aligned for Testing Contrary to The Technical Specification Due to Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1997, the plant was operating at 100% power. On that day, a system engineer reviewing operator logs discovered that on September 4, 1997, while the reactor was in hot shutdown condition, Operations had aligned a safety injection system valve contrary to the technical specifications for fifty minutes to perform post maintenance testing. A historical review for similar conditions identified that the same type of test was performed in 1995. During the testing performed on September 4, 1997, Operations entered a second safety injection system limiting condition for operation action statement; entering two action statements is contrary to the technical specifications. The event was caused by personnel error and inattention to detail in that licensed operators misapplied the technical specifications when aligning the system. Contributing to the cause was an inappropriate test method. Corrective actions include providing the lessons learned from this event to licensed operators. Operations procedures and initial licensed operator training will be enhanced. Engineering will determine an appropriate test method for these types of valves. This event did not affect the health and safety of the public due to the shutdown condition of the reactor and the short duration of the activities.
2861997029 | Indian Point 3 | 10/28/1997 | 11/25/1997 | ML10049121 | <strong>Plant Potentially Outside Design Basis due to New Information Indicating Some Fuel Rods May Have the Pellet to Clad Gap Reopen Causing the Clad Oxidation Limit to be Exceeded</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, while operating at 100 percent power, New York Power Authority (NYPA) reported a condition potentially outside the plant's design basis based on preliminary information provided by Westinghouse. Westinghouse sent NYPA information indicating that analysis made using the licensed PAD code (revised to correct recent discrepancies, new corrosion data and conservative assumptions on other parameters) indicated that the internal pressure criterion would not be met for high burnup (i.e., 40,000 MWD/MTU) integral fuel burnable absorber (IFBA) fuel rods. The increased pressure could cause the fuel rod pellet-to-clad gap to reopen, which would allow the 17 percent clad oxidation limit of 10CFR50.46 to be exceeded for design basis accident conditions. IP3 subsequently determined that no IFBA fuel rod would exceed a burnup of 40,000 MWD/MTU until about July 4, 1998. If Industry information submitted to the NRC does not resolve this issue for Indian Point 3, NYPA will supplement LER 97-029 to identify the results of plant specific corrective action. There were no significant effects on public health and safety due to this event since no fuel rod has exceeded the burnup limits that Westinghouse identified. Westinghouse has generically concluded that exceeding the fuel rod pellet-to-clad gap would not prevent safe shutdown, cause a loss of coolable geometry or cause dose criteria for postulated accidents to be exceeded.
2861997030 | Indian Point 3 | 11/07/1997 | 12/05/1997 | ML10049122 | <strong>Plant Outside Licensing Design Basis Due To AMSAC Automatic Arming/Disarming At Greater Than 40 Percent Reactor Core Power</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1997, while operating at 100 percent power, the New York Power Authority (NYPA) reported that the Indian Point 3 (IP3) plant was outside it's design basis because the ATWS Mitigating System Actuation Circuitry (AMSAC) automatically arms at 40 percent turbine impulse pressure rather than 40 percent reactor core power. AMSAC was declared inoperable and an administrative limiting condition for operation action statement was entered. The cause is personnel error that led to an inconsistency in the topical report between the specified requirement for the AMSAC setpoint and the analytical basis. NYPA performed a reasonable assurance of safety that found that the AMSAC is capable of performing its design function at the current setpoint. NYPA is assessing what the proper permanent corrective action should be. There were no effects on public health and safety due to the deviation from the AMSAC setpoint requirement since AMSAC would have performed its intended design function.
2861997031 | Indian Point 3 | 12/12/1997 | 07/31/1998 | ML10049128 | <strong>Plant Outside of Design Basis Involving Single Failure Criteria for the Auxiliary Feedwater System, Due to Error in Original Design</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1997, with the plant operating at 100% power, Engineering determined that the plant might have been outside of its design basis during past operation. A design configuration was discovered in which, for a specific and limited set of plant conditions, the Auxiliary Feedwater (AFW) System would not meet single failure criteria. The design configuration is that certain AFW System controls associated with two motor-driven pumps are powered from the same instrument bus. The specific condition required is a safety injection signal or loss of offsite power at the same time that Instrument Bus 33 is connected to its backup power supply. The result is the tripping of both motor-driven pump motors due to flow runout, so that a single failure of the remaining turbine-driven pump would prevent the AFW system from performing its design function. <br /><br /> The cause of the event could not be definitively determined because the design configuration was present at initial plant startup. A probable cause is that design personnel did not recognize that certain controls for the motor-driven pumps were required to prevent flow runout and thereby protect the pump motor from tripping on excess current. Corrective actions were taken to modify the design configuration. The event did not affect the health and safety of the public because the actual length of time when plant conditions were subject to the single failure was minimal.
2861997032 | Indian Point 3 | 12/18/1997 | 05/28/1998 | ML10049126 | <strong>480 Volt Bus Inoperable Due to a Failure of the 32 Residual Heat Removal Pump Circuit Breaker to Open; A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1997, with reactor power at 100 percent, a plant shutdown was initiated in accordance with the Technical Specifications (TS). Following a surveillance test, the breaker used to power the 32 Residual Heat Removal (RHR) pump could not be opened. Operations concluded that the breaker was not capable of opening and shedding the 32 RHR pump from its associated safety bus following a safety injection or undervoltage signal, therefore, the safety bus could be rendered inoperable. Because the TS do not provide an allowed outage time for an inoperable safety bus, the plant was brought to hot shutdown. On December 22, during testing of additional breakers, another breaker was determined to be potentially degraded. Engineering determined that other breakers could be subject to failure and result in overload of the three emergency diesel generators (EDG). Operations declared the three EDGs inoperable and brought the plant to cold shutdown. The cause of the breaker failure was lack of lubrication at key pivot connections in the breaker mechanism. The missing lubrication was due to a lack of knowledge by the breaker overhaul vendor. A contributing cause was a unique combination of wear, tolerances and adjustments of breaker parts that permitted linkages within the breaker to overtravel to a position where small changes in frictional forces affected the breaker trip capability. Corrective actions include; breaker replacement, testing of like breakers, equipment failure evaluation, development of a process to test/inspect overhauled breakers, and expedite the PM for the vendor overhauled breakers. This report is also a 10 CFR Part 21 notification. There was no effect on public health and safety.
2871997001 | Oconee 3 | 03/20/1997 | 04/17/1997 | 9704290300 | <strong>Control Rod Drive System Short Circuit Results In A Reactor Trip Due To A Manufacturing Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1997, Unit 3 was operating at 73% full power, following a refueling outage. Maintenance and Operations personnel were performing a monthly 'Control Rod Drive Breaker Trip and Event Recorder Timing Test.' At approximately 0913 hours, while testing one breaker, the Reactor tripped due to an electrical short in the redundant Control Rod Drive trip confirm breaker circuitry. The trip response was routine with no significant occurrences. The unit was stabilized at Hot Shutdown conditions. The root cause of the event is a manufacturing fabrication deficiency. Corrective actions include repairing the electrical short and revising the CRD breaker trip time test procedure.
2871997002 | Oconee 3 | 04/02/1997 | 06/02/1997 | 9706110117 | <strong>Reactor Building Cooling Units Technically Inoperable To A Manufacturing Deficiency</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1997, while reviewing previously identified problems on Unit 3's Reactor Building Cooling Units (RBCU) fan motor circuits, it was recognized that a potential past operability concern existed. Potentially underrated fuses had been replaced with fuses of a higher rating on June 21, 1995. On May 1, 1997, with Unit 3 operating at 100% full power, an Engineering evaluation concluded that the Unit 3 RBCUs were technically past inoperable, prior to June 1995, because the fuses in the primary circuit of Unit 3's RBCUs control power transformer were underrated. This might have prevented the RBCUs from re-starting during a LOCA/LOOP upon receipt of an Engineered Safeguard signal. The root cause is Manufacturing Deficiency, functional design deficiency, electrical. Corrective actions included replacing all three units' RBCU fuses.
2871997003 | Oconee 3 | 05/03/1997 | 06/02/1997 | 9706110014 | <strong>High Pressure Injection System Inoperable Due to Design Deficiency and Improper Work Practices</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1997, Unit 3 was being shutdown to verify the integrity of the High Pressure Injection (HPI) System nozzles. Unit 3 was at approximately 240 degrees and 270 psig with a Low Pressure Injection pump and a Reactor Coolant Pump in operation. At approximately 0915 hours, the 3A and 3B HPI pumps were damaged due to operation with an inadequate suction source. Both Letdown Storage Tank (LDST) level instruments erroneously indicated level was 55.9 inches for about one hour and forty five minutes prior to the damage to the HPI pumps. However, at the time of the failure, the tank was essentially empty. Subsequent investigation determined the reference leg of the LDST level to be partially drained. The Operators responded to the event and placed the unit in a stable condition. On May 5, 1997, an Engineering evaluation determined that the inaccurate level made the HPI system inoperable at some point between February 22, 1997 and May 3, 1997. This is significant because operation in this condition is outside the design bases of the HPI System. The root cause is a combination of a design weakness of a common reference leg for the LDST level instruments and a leaking instrument fitting due to an inadequate work practice. A contributing cause was the failure to adequately apply available operating experience. Corrective actions include a modification of the LDST level instruments.
2871997004 | Oconee 3 | 10/29/1997 | 11/25/1997 | 9712030017 | <strong>Deficient Procedure Results In A Missed Technical Specification Surveillance Check</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1997, Unit 3 was operating at 100 % full power. As a result of a training package that was issued earlier, Operations shift personnel raised questions in regard to the Periodic Instrument Surveillance procedure. Operations staff personnel reviewed the questions and discovered that one Technical Specification surveillance check had not been performed on Unit 3 since the March 1997 startup. The associated procedure step requires a daily check between the Operator Aid Computer (OAC) subcooling margin and the Inadequate Core Cooling Monitor subcooling margin. The OAC was removed from service prior to startup due to the calculations for the subcooling margin being non-conservative. The cause of this event is Deficient Written Communications; Content, Omission of relevant information. Corrective actions included Engineering developing an alternate method to perform the surveillance check with the OAC out of service. The Periodic Instrument Surveillance procedures for Unit 2 and Unit 3 were revised to reference the associated Technical Specification surveillances.
2891997001 | Three Mile Island 1 | 01/17/1997 | 02/17/1997 | 9702250333 | <strong>Potential Overpressurization Of Piping Between Closed Reactor Building Isolation Valves Due To Inadequate Design Code Guidance</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1997, during a review of piping systems that penetrate containment as requested by Generic Letter (GL) 96-06, 'Assurance of Equipment Operability and Containment Integrity During Design-Basis Accident Conditions,' GPU Nuclear determined that most of the el even (11) affected piping segments could be stressed beyond the piping design code (B31.1-1967) allowable stresses during a design-basis accident. This condition was found to be reportable in accordance with 10CFR50.73(a)(2)(ii)(B) as a condition in which the plant was found to be outside of its design basis. The analysis modeled the effects on internal fluid and piping in response to an external ambient temperature increase. The results revealed that although the piping did not meet the design requirements, the postulated stresses did not exceed ASME Section III, Appendix F criteria for piping. Therefore containment integrity would be maintained during an accident. Using the guidance in NUREG/CR-5455, 'Development of the NRC's Human Performance Investigation Process (HPIP),' the root cause was found to be that the applicable design standards were 'less than adequate - confusing or incomplete.' Operability determinations were performed and further evaluations are ongoing to determine the need for modifications or procedural revisions. There were no adverse safety consequences or safety implications that resulted from d the event did not affect the health and safety of the public.
2891997002 | Three Mile Island 1 | 01/29/1997 | 02/28/1997 | 9703070047 | <strong>Potential Inability of the Startup Feedwater Block Valves to Fully Close Following a Main Steam Line Break Due To MOV Program Weaknesses</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1997, GPU Nuclear reviewed the operability of Feedwater Startup Block Valves, FW-V92 A/B. Improvements to the GL 89-10 program had led to more conservative assumptions being used in the valve thrust calculations. The new assumptions increased the calculated thrust requirements for the valves. Although calculations were not yet design verified,' there was reason to believe the valves may not close fully during a Main Steam Line Break (MSLB). FW-V92A/B are required to close by a signal from the Heat Sink Protection System (HSPS) when Once Through Steam Generator (OTSG) pressure decreases to less than 600 psig. Technical Specification 3.5.1.9 requires HSPS operability when the reactor is critical and establishes a 72 hour allowable outage time with a single train inoperable. With FW-V92A/B inoperable for greater than 72 hours, this condition is an event which is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition in which the plant was-not in compliance with its Technical Specifications. The torque switch settings for FW/V92A/B were increased to ensure full valve closure during a MSLB. The root cause was weakness of the Motor Operated Valve (MOV) Program. All valves in the GL 89-10 MOV program are being reevaluated using justifiable and conservative assumptions. The safety consequences associated with this event were minimal.
2891997003 | Three Mile Island 1 | 02/24/1997 | 09/01/1997 | 9710070328 | <strong>Potential Overpressurization Of Makeup Pump Suction Piping Due To Inadequate Test And Operating Procedures</strong><br /><i>Abstract:&nbsp;</i>On February 24, 1997, GPU Nuclear determined that suction piping for Make Up pumps A & C may have been stressed beyond the piping design code (B31.1-1967) allowable stresses during ES Testing and could be similarly overstressed during system response to a design-basis accident. This condition was found to be reportable in accordance with 10CFR 50.73(a)(2)(ii)(B) as a condition in which the plant was found to be outside of its design basis. An analysis of the effect of the overpressure condition on the piping and components was performed. The results revealed that although the piping and components may not have met the design requirements, the postulated stresses did not exceed ASME Section III, Appendix F criteria. Therefore system integrity would be maintained. <br /><br /> Using the guidance in NUREG/CR-5455, Development of the NRCs Human Performance Investigation Process (HPIP), the root cause was found to be "standards, policies, or administrative controls (SPAC) Less than adequate - technical errors". <br /><br /> The system was determined to be operable and procedure changes will be implemented prior to startup from the 12R outage to prevent future occurrence. There were no adverse safety consequences or safety implications that resulted from this event, and the event did not affect the health and safety of the public.
2891997004 | Three Mile Island 1 | 02/28/1997 | 04/04/1997 | 9704100171 | <strong>Auxiliary and Fuel Handling Building Ventilation System Declared Inoperable Due To Questions on Quality Classification</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1997, GPU Nuclear declared the Auxiliary & Fuel Handling Building Ventilation system (AFHBVS) inoperable due to quality classification concerns. The AFHBVS continues to meet its surveillance requirements and its filter efficiency and flow requirements and thus remains in operation. The cause of this event is related to wording in the Technical Specification Bases and the Final Safety Analysis Report (FSAR) that implies quality requirements that are not supported by the system design. <br /><br /> A Safety Evaluation will be completed by August 15, 1997, to support any documentation changes needed to clarify the existing Technical Specification Bases and FSAR in regards to the AFHBVS. <br /><br /> This event is not reportable under the criteria of 50.72 or 50.73. However, a voluntary LER is being submitted to document this condition. This LER is also being submitted in accordance with Technical Specification 3.15.3.3.b, which requires a special report if the Auxiliary & Fuel Handling Ventilation system is inoperable longer than seven days. <br /><br /> There were no adverse safety consequences or safety implications that resulted from this event, and the event did not affect the health and safety of the public.
2891997005 | Three Mile Island 1 | 04/10/1997 | 05/12/1997 | 9705200332 | <strong>Containment Purge Motor Operated Valves Found to Have Inadequate Closing Torque due to Deficient Design Analysis</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1997 the motor-operated Reactor Building Purge valves (AH-V-1B/C) were declared inoperable when it was determined using draft calculations that the motor operator torque was not adequate to fully seat the valves during a LOCA with degraded grid voltage. In accordance with Technical Specification (TS) 3.6.8.1 the redundant air-operated valves (AH-V-1A/D) were verified closed and operable. Subsequent to the event, valve specific test data for the actual seating torque has been located and is being analyzed for applicability. The root cause of the event was deficient design analysis. Purging the Reactor Building at power in the past with this condition is reportable in accordance with 10CFR50.72(b)(1)(ii)(B) and 50.73(a)(2)(ii)(B) as a condition outside of the design basis. If a single failure of either pneumatically operated purge valve were to occur along with a Loss of Coolant Accident and degraded grid conditions, containment integrity could not be assured if the motor-operated valves were unable to fully seat and seal tightly.
2891997006 | Three Mile Island 1 | 04/24/1997 | 05/23/1997 | 9706030161 | <strong>Reactor Building Fan Motor's Unqualified Cable Termination due to Incorrect Engineering Guidance</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1997 following a review of the motor cable termination repair on the Reactor Building Air Recirculation & Cooling Unit AH-E-1A, GPU Nuclear concluded that the power lead connections on the redundant components, AH-E-1B and AH-E-1C, did not satisfy environmental qualification requirements for exposure to a post-LOCA harsh environment. As a result of the inadequate environmental qualification configuration, the AH-E-1B and AH-E-1C fans were considered inoperable. The root cause of the event was identified as personnel error. During a cable modification in 1986, engineering provided improper guidance and documentation for the heat shrink installation at the motors' terminations. As a result, the connection did not satisfy environmental qualification criteria and was not sealed against impact from a harsh environment. The event was reported to the NRC via the ENS and actions were initiated to provide an environmentally qualifiable covering over the exposed metal surfaces of the connection. The event is being reported per 10 CFR 50.73(a)(2)(v).
2891997007 | Three Mile Island 1 | 06/21/1997 | 07/21/1997 | 9707310052 | <strong>Generator Output Breaker Failure Resulting In A Loss Of Offsite Power And Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1997 at approximately 1214, while the plant was operating at 100% power, TMI-1 experienced a loss of off site power (LOOP) due to the failure of both generator output breakers located in the site's 230KV substation. The fault detected on the #4 bus (230KV) resulted in the opening of the parallel breaker which suffered a re-strike and caused a fault on the alternate #8 bus. The two faults resulted in breaker action which isolated power to the station and resulted in the LOOP. The LOOP resulted in immediate reactor and turbine trips. Both emergency diesel generators started and loaded on to their respective safeguards buses as designed. Without balance of plant power, the condensate, feed, circulating water and main condenser vacuum pumps were not operable. The once through steam generators were fed through the Emergency Feedwater System via two electric pumps powered by the engineered safeguards buses and a steam driven pump. Heat was removed via the steam generator atmospheric dump valves. Loss of station power also deenergized the reactor coolant pumps which forced the plant into a natural circulation mode. Natural circulation flow was achieved within 19 minutes of the trip. Offsite power was restored within 90 minutes. Systems were restored to enable cooling via the main condenser and subsequent restart of the reactor coolant pumps. The failed breakers were replaced with new ABB model 242 PMG 3000 amp breakers. The plant was back on line at 0202 on June 29, 1997. <br /><br /> The root cause of the plant trip and LOOP was the failure of generator breaker GB-1-02 and the re-strike which occurred during the opening of the parallel breaker caused a fault on the alternate #8 bus in the plant 230KV switch-yard. The fault in the "B" phase of GB-1-02 breaker caused severe overheating and ejection of the bushing and conductor from the breaker. <br /><br /> The event is being reported per 10 CFR 50.73(a)(2)(iv)
2891997008 | Three Mile Island 1 | 06/21/1997 | 07/21/1997 | 9707300084 | <strong>Control Rod Trip Insertion Times Exceed TS Section 4.7.1.1 Limits</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1997 at approximately 1214, while the plant was operating at 100% power, TMI-1 experienced a loss of off site power due to the failure of both generator output breakers located in the site's 230KV substation. As a result of the event, which is being reported via LER 97-007, the power to the control rod drive mechanisms was lost and the reactor tripped. The plant computer captured times associated with each control rod reaching the 25% zone reference as the reactor trip occurred. The computer data was used to calculate control rod trip insertion times which were subsequently evaluated. It became apparent upon review of the evaluation results that more than one control rod was inoperable based on their failure to satisfy the requirement Technical Specification 4.7.1.1 to insert from the fully withdrawn position to 3/4 insertion within 1.66 seconds. Initially, three control rods were reported to the NRC as being inoperable. Subsequent to that report, one additional control rod was determined to exceed the 1.66 second trip insertion time limit and was reported during a followup call. <br /><br /> The root cause of the control rod trip insertion times exceeding the Technical Specification limit is a hydraulically induced effect resulting from reduced clearances in the old style control rod drive thermal barriers due to the presence of deposits on the internal check valves and between the thermal barrier bushing and the leadscrew. GPU Nuclear will continue current reactor plant chemistry controls and extended rod exercises as well as complete the replacement of all remaining old style thermal barriers with modified thermal barrier design prior to startup from the 13R outage. <br /><br /> The event is being reported per 10 CFR 50.73(a)(2)(i)(B) and (a)(2)(ii)(B).
2891997009 | Three Mile Island 1 | 07/25/1997 | 08/25/1997 | 9709020257 | <strong>Engineering Analysis Of The Loss Of 'A' Train Dc Power With A Loss Of Offsite Power And A Loss Of Coolant Accident</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1997, as a result of reviewing a plant event reported to the NRC by the Crystal River Unit 3, GPU Nuclear personnel determined that a similar condition existed at TMI-1. <br /><br /> It was identified that a loss of 'A' station DC distribution and a concurrent loss of offSite power would affect both trains of Engineered Safety Features (ESF) equipment. As expected, the 'A' train of ESF equipment would be made inoperable by this event due to the loss 'A' train AC and DC power. In addition, 'B' Train Engineered Safeguards Actuation System (ESAS) would actuate with inability to bypass the "B" train of ESAS. If this failure were to occur concurrently with a large break loss of coolant accident, no procedural guidance was available to operators to allow them to bypass ESAS and take control of components as required to throttle reactor building spray flow and complete switchover to the reactor building sump. The inability to bypass "B" train of ESAS upon loss of power on "A" Train results from a design arrangement in which three analog channels fan out to two trains of logic. Two of the analog channels are powered from "A" Train power. This design has existed since initial plant operation. <br /><br /> The root cause of the condition was determined to be a failure of the plant's designers to properly consider the bypass of Train B of ESAS on a loss of offsite power and a loss of 'A' DC. Procedure changes were implemented which restored the ability to control the 'B' Train ES components. <br /><br /> The condition was reported per 10 CFR 50.72(b)(2)(iii).
2891997010 | Three Mile Island 1 | 10/12/1997 | 11/12/1997 | 9711180205 | <strong>Pilot Operated Relief Valve (PORV) Inoperability Due To Being Mis-Wired and Failure to Perform Post-Maintenance Test (PMT) Following Replacement During 11R Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On October 13, 1997, GPU Nuclear (GPUN) Inc. determined that the Pilot Operated Relief Valve (PORV) installed during the 11R refueling outage was not capable of being opened during the operating cycle prior to refueling outage 12R. GPUN reached this conclusion on the basis of post-maintenance testing of the PORV replacement installed during the 12R outage and from observation of lead landings on the valve removed from service. <br /><br /> This condition was found to be reportable in accordance with 10CFR50.73 (a) (2) (i) (B) as a condition which is prohibited by the plant Technical Specifications, in that Inservice Testing (IST) required by ASME code and the TMI Inservice Inspection Program was not properly conducted on the PORV following its replacement during 11R, and which if conducted properly would have led to the early discovery of its inability to be cycled. <br /><br /> The root cause of the event was identified as personnel error. During the valve reinstallation in 11R, the power supply leads to the PORV solenoid were improperly terminated; and the error went undiscovered because of a failure to perform the required PMT on the valve following its installation pursuant to Technical Specification 4.2.2. <br /><br /> There were no adverse safety consequences or safety implications resulting from this event, and the event did not affect the health and safety of the public.
2931997001 | Pilgrim | 01/20/1997 | 02/14/1997 | 9702260176 | <strong>Very Small Quantity of Unaccountable Special Nuclear Material</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1997, the NRC Operations Center was notified that a very small quantity of special nuclear material (SNM) contained in sealed devices could not be accounted for. The discovery was the result of reconciling a 1996 baseline inventory of portable devices containing SNM. <br /><br /> The most probable cause was less than effective methods for control and accounting of devices containing less than one gram of SNM in the 1975 - 1987 time frame. The previous (1987) baseline inventory of portable devices containing SNM relied on a review of documentation for items located in the spent fuel pool or installed in the reactor, and piece counts of portable devices located in other plant areas. The method used for the 1996 baseline inventory was a piece part count of portable devices containing SNM including the devices in the spent fuel pool. <br /><br /> Corrective actions taken in 1987 included revision of the procedure governing the control and accounting of SNM to include devices containing less than one gram of SNM. Corrective actions taken in 1996 included revision of the procedure governing the control and accounting of SNM including the transfer of SNM, revision of maintenance procedures that involve SNM, training on SNM, and the establishment of a new baseline inventory of portable devices containing SNM. <br /><br /> The devices containing the SNM that could not be accounted for were most probably shipped to a licensed disposal facility and pose or posed no threat to national defense or public health and safety.
2931997002 | Pilgrim | 02/06/1997 | 03/10/1997 | 9703190094 | <strong>Steam Jet Air Ejector Sampling Not Performed in Accordance with Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1997, it was determined that a certain sampling and analysis since 1990 was not consistent with Technical Specifications. Specifically, Technical Specification 3/4.8.G.1 requires an isotopic analysis of representative sample taken at the off-gas system steam jet air ejector (SJAE). This analysis is performed to ensure that the gross radioactivity release rate of noble gases will not exceed 500,000 uCi/sec. Although samples were taken during this time period, they were taken at the augmented off-gas system recombiner outlet (RCO), rather than at the SJAE as specified by the Technical Specification. <br /><br /> The cause was an improper conclusion contained in the response to a request for licensing interpretation in 1990. The response did not fully identify the requirements of Technical Specification Section 3/4.8.G.1.a The response to the ESR indicated a Technical Specification change was not necessary in order to change sample locations. Based on the licensing response, the chemistry department revised the applicable procedure and commenced sampling at the RCO. <br /><br /> Immediate corrective action has been taken to resume sampling as required by Technical Specification Section 3/4.8.G.1. A change to the Technical Specification will be submitted to allow sampling at either location, depending on plant conditions. This condition posed no threat to public health and safety.
2931997003 | Pilgrim | 02/15/1997 | 07/18/1997 | 9707280076 | <strong>Manual Scram due to Increasing Reactor Water Level During Power Reduction for Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1997, at 0038 hours, a manual scram was initiated at approximately 20 percent reactor power. The scram was intentionally initiated as a result of increasing reactor water level experienced while reducing power for the scheduled 1997 refueling outage. The scram resulted in the insertion of the control rods, transfer of the source of power to the auxiliary power distribution system, and trip of the turbine-generator. <br /><br /> The direct cause was greater than normal feedwater flow past the nonsafety-related feedwater system train 'A' and 'B' regulating valves at low steaming rates. Degradation of the actuator of FV-642A in conjunction with the inability of the valve's plug to travel to its lower seat was the primary root cause of the event. Corrective action taken included disassembly and repair of FV-642A and its actuator and positioner. The positioner of FV-642B was repaired and calibrated. The preventive maintenance program was modified for the train 'A' and 'B' regulating valves and startup feedwater regulating valve. <br /><br /> The scram was initiated when the reactor mode selector switch was moved from the RUN position to the SHUTDOWN position. The reactor vessel pressure was 954 psig with the reactor water temperature at the saturation temperature for the reactor pressure. The event posed no threat to public health and safety.
2931997004 | Pilgrim | 03/07/1997 | 04/14/1998 | 9804200480 | <strong>Loss of Preferred Off-Site Power and Oil Spill Due to Main Transformer Fault While Shut Down</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1997, at 1449 hours, an automatic start of the 'B' train emergency diesel generator and an actuation of the secondary containment isolation control system and a portion of the primary containment isolation control system occurred while shutdown during the 1997 refueling outage. The event was the result of an electrical fault in the main transformer that was energizing the unit auxiliary transformer and related 4.16 Kv electrical power distribution system at the time of the event. The fault also resulted in a significant leak of main transformer insulating oil into the area of the transformer and adjacent turbine building. The diesel generator loaded onto its bus, and the containment isolation systems actuated as designed for the conditions existing at the time of the event. <br /><br /> The failure of the main transformer was most likely caused by either a degraded winding condition or static electrification. Corrective action involved replacing the main transformer, updating the fire hazards analysis report, installing berms in the oil spill area, and replacing a portion of degraded feeder cables. The event occurred with the reactor mode selector switch in the REFUEL position. The reactor vessel was completely de-fueled, and no reactor fuel movement was in progress. The event posed no threat to public health and safety.
2931997005 | Pilgrim | 03/08/1997 | 05/15/1997 | 9705230003 | <strong>Limiting Condition for Instrumentation which Provides Surveillance Information - Turbine Building Effluent Monitoring</strong><br /><i>Abstract:&nbsp;</i>Section 3.2.F of the Pilgrim Nuclear Power Station (PNPS) technical specifications establishes the Limiting Condition for Operation (LCO) for instrumentation that provides surveillance information. Table 3.2.F requires, as a minimum, one (1) operable instrument channel for the turbine building vent. It also identifies RI-1001-610 and RR-1001-608 as the required surveillance instrumentation for the turbine building vent. Note seven(7) for Table 3.2.F contains the governing action statement; it reads as follows: <br /><br /> (7) With less than the minimum number of operable instrument channels, restore the inoperable channels to operable status within 7 days or prepare and submit a special report to the Commission within 14 days of the event outlining the action taken, the cause of the inoperability and the plans and schedule for restoring the channels to operable status. <br /><br /> Contrary to the requirements of Section 3.2.F of the PNPS technical specifications , the turbine building effluent monitoring instrumentation was inoperable for a period of time in excess of seven (7) days and special report was not submitted to the Commission within 14 days of the time the instrument was made inoperable. The plant was shutdown for refueling when the monitoring instrumentation was made inoperable. The condition posed no threat to public health and safety because the potential for an uncontrolled release of radioactive material through the turbine building vent did not exist. This report constitutes the special report required by section 3.21 of the PNPS technical specifications.
2931997006 | Pilgrim | 03/21/1997 | 04/22/1997 | 9704290096 | <strong>Inadvertent Group 3 Isolation While Trouble Shooting a 125vDC Ground on the "A" Battery</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1997, motor operated valve 1001-50 closed while trouble shooting a ground on the 125v 'A' battery. The 'B' residual heat removal (RHR) pump tripped as a result of the valve closure and a partial unplanned group 3 containment isolation occurred. <br /><br /> RHR train 'B' was in the shutdown cooling mode of operation with the 'B' RHR pump in service at the time of the event. The isolation occurred as a result of a 'relay race' when circuit breaker D4-8 was cycled (opened and closed) as part of the trouble shooting effort. The circuit in question functioned as designed, the motor operated valve isolated when the circuit breaker was closed. No component or system failures contributed to the event. <br /><br /> The following corrective actions were taken: <br /> Electrical prints were reviewed and it was verified that the logic worked as designed. <br /> Group 3 isolation was reset per procedure 2.2.125 <br /> Shutdown cooling was restored per procedure 2.2.19. <br /> A precautionary statement was added to procedure 2.2.14 to preclude recurrence. <br /> Operations and maintenance crews were briefed.
2931997007 | Pilgrim | 04/01/1997 | 05/01/1997 | 9705130019 | <strong>Safeguards Buses De-Energized and Losses of Off-Site Power During Severe Storm While Shut Down</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1997, both 120 volt safeguards buses de-energized on two occasions, and subsequently, a loss of preferred off-site power (345 Kv) followed later by a loss of secondary off-site power (23 Kv) occurred while the emergency diesel generators were in operation during a severe storm (blizzard). An Unusual Event was declared at 0349 hours and was terminated at 2347 hours by which time the secondary and preferred off-site power sources were re-energized. <br /><br /> The cause of the de-energizing of the safeguards buses was brief, severe 345 Kv transmission system undervoltage transients that resulted in automatic shut downs of the voltage regulating transformers (480/120 volt) that power the safeguards buses. The transformers' purchase specification did not address and the manufacturer and supplier documentation did not identify an automatic shut down feature if input voltage was less than 384 volts (greater than zero volts). The separate losses of the off-site power sources were caused by the effects of the storm. <br /><br /> Corrective action taken included the replacement of the microprocessor control units installed in the voltage regulating transformers. <br /><br /> The events occurred while in cold shut down. The reactor mode selector switch was in the REFUEL position. The events posed no threat to public health and safety.
2931997008 | Pilgrim | 03/12/1997 | 04/24/1997 | 9704290280 | <strong>Setpoint of Target Rock Relief Valve Pilot Assembly Out of Tolerance During Testing</strong><br /><i>Abstract:&nbsp;</i>On April 14, 19 97, a reportability evaluation concluded that the initial popping pressu re (1152 psig) of a pilot valve previously installed in one of four two-s tage main steam relief valve was greater than the technical specificatio n limit of 1126 psig including tolerance was reportable. The discovery w as made as a result of a routine surveillance test of the pilot valv e at the Wyle test facility on March 12, 1997. <br /><br /> The caus e is believed to be setpoint drift. Minor steam leakage experie nced during the initial popping pressure test run may have contri buted to the setpoint drift. The pilot valve exhibited no leakage while it was installed in the relief valve. Corrective action taken incl uded disassembly, inspection, and rework by Target Rock Corporation per sonnel. The pilot valve exhibited no abnormal conditions during in spection. The pilot valve will be tested as part of routine c ertification testing. <br /><br /> The discovery occurred while in cold shut down during the 1997 refueling outage. The reactor mode selector switch was in the REFUEL position. The initial popping pressure posed no threat to public health and safety.
2931997009 | Pilgrim | 04/17/1997 | 05/19/1997 | 9706020251 | <strong>RCIC System Inoperable Due to Turbine Overspeed Trip During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1997, at 1315 hours, the reactor core isolation cooling (RCIC) system became inoperable, and a 14 day Technical Specification 3.5.D.2 limiting condition for operation (LCO) was entered. The system became inoperable because of a mechanical overspeed trip of the RCIC turbine that occurred during a surveillance test of the RCIC system. The test was conducted during startup from the 1997 refueling outage. <br /><br /> The cause was a gear change in the motor operator of the RCIC system flow test valve. The gear change was made during the refueling outage and affected the time used to position (open) the flow test valve before the RCIC turbine-pump is started for the test. Applicable RCIC system procedures were not identified as impacted by the gear change. Corrective action taken included a change in the surveillance procedure. The change increased the time, from approximately three seconds to approximately five seconds, used to position the flow test valve for the test. The RCIC system was tested with satisfactory results, and the LCO was terminated on April 18, 1997. Corrective action planned includes reviewing RCIC system procedures for potential revision and including this report in the engineering support training program. <br /><br /> The event occurred during startup from the 1997 refueling outage. The reactor mode selector switch was in the RUN position, and reactor power was 16 percent. The reactor vessel pressure was approximately 955 psig with the reactor water temperature at the saturation temperature for the pressure. The event posed no threat to public health and safety.
2931997010 | Pilgrim | 04/20/1997 | 05/21/1998 | 9806020159 | <strong>Postulated Pipe Break Pressure Relieving Pressure Relieving Pathway Boundary Door Found Open During Power Operation</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1997, at 1230 hours, a normally-closed, locked door that forms part of the pressure relieving boundary for a postulated high pressure coolant injection (HPCI) system turbine steam supply pipe break in the HPCI turbine-pump room was found open. Upon discovery, the door was immediately closed, latched, and subsequently locked. The as-found condition of the door was such that it was not blocked open or otherwise prevented from closing or being closed. <br /><br /> The apparent cause of the door being open when it was required to be closed was human performance in that the door was not closed and locked after a maintenance activity that was performed during the 1997 refueling outage. The door was removed as part of the maintenance activity. Corrective action taken included a thorough walkdown of the plant configuration for a pipe break in the HPCI compartment. A multi-discipline team was formed to conduct a root cause analysis and identify corrective actions for problems involving control of subcompartment boundaries that are modeled in the analyses performed for high energy pipe breaks outside primary containment. This report will be updated after the root cause analysis is completed. <br /><br /> The discovery occurred during reactor power operation with the reactor mode selector switch in the RUN position with the reactor power at 19 percent. The reactor pressure was approximately 950 psig with the reactor water at the saturation temperature for that pressure. The condition posed no threat to public health and safety.
2931997011 | Pilgrim | 07/01/1997 | 12/30/1997 | 9801070019 | <strong>Service Water System Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>The Pilgrim Station design basis includes a requirement for redundant and independent salt service water (SSW) system trains such that no single active failure can prevent the SSW system from fulfilling its safety objective (i.e., to provide cooling water to the reactor building closed cooling water (RBCCW) system). The design basis of the SSW system also includes the requirement for the normally cross-connected SSW trains be automatically isolated upon loss of the preferred AC power source. During a Service Water Operational Performance Inspection (SWOPI) follow-up NRC inspection, a single failure vulnerability was identified which placed the unit in a condition thought to be outside the design basis. Specifically, a single failure of a 125 vdc battery, under certain conditions, would compromise the redundancy and independence of the SSW system and potentially lead to a SSW pump cavitation condition. <br /><br /> It was determined that a single failure of a 125 vdc battery might defeat the SSW loop independence and redundancy if the SSW swing pump was selected for dedication to the opposite safety train and a loss of off-site power occurred. Such a DC failure would disable the associated diesel generator and one of the SSW discharge header division valves. As a result, the SSW loops would remain cross-connected, and one SSW pump would supply both loops of SSW for a short time, potentially in a cavitating condition. <br /><br /> A temporary modification was implemented that required closing one of the division valves in the common SSW discharge header to effect redundant and independent cooling water loops and to preclude the potential pump cavitation condition. The condition posed no threat to public health and safety.
2931997012 | Pilgrim | 07/29/1997 | 05/19/1998 | 9805270054 | <strong>Failure of Relay to Energize During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1997, at about 1100 hours, the control relay that initiates a portion of the pipe break detection circuit in the residual heat removal (RHR) system channel 'B' circuitry did not energize as expected during a logic system functional test. The RHR low pressure coolant injection (LPCI) mode was declared inoperable and a seven day limiting condition for operation (LCO) was entered in accordance with technical specifications. The relay did not energize because of the failure (to close) of two paired contacts of the RHR channel 'B' high drywell pressure trip relay, a type HFA relay. The root cause of the failure of relay 10A-K10B contacts 9-10 to close was incorrect setting of contacts. This condition was attributed to personnel exhibiting overconfidence with skills obtained from previous successful HFA alignments and a lack of need for concern when checking spare relays. Immediate corrective action consisted of replacing and retesting the relay on July 30, 1997, and terminating the LCO at 1525 hours which had been entered for the isolation and replacement of the relay. Additional corrective actions include revising the procedure used for testing HFA relays and developing training for E-Lab engineers and/or electricians. The event occurred during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The reactor pressure was approximately 1035 psig with the reactor water at the saturation temperature. The problem posed no threat to public health and safety.
2931997014 | Pilgrim | 08/25/1997 | 12/15/1997 | 9712230103 | <strong>Transmitters Not Calibrated in Accordance With the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1997, during the nuclear operations supervisor's (NOS's) review of a request by the instrument and control (I&C) department to perform surveillance 8.M.2-8.4, calibration of the drywell high pressure analog trip system transmitters PT-1001-89A and C, the NOS noted that the Technical Specification Table 4.2.B Note (7) had not been met. Note (7) requires the transmitters to be calibrated during refueling outages. These transmitters had not been calibrated during refueling outage No. 11. Additional review determined surveillance 8.M.2-8.4, calibration of drywell high pressure analog trip system transmitters PT-512 A and B, surveillance 8.M.2-8.5, calibration of turbine first stage pressure analog trip system transmitters PT-504A,B,C, and D, and main steam line pressure low transmitters PT-261-30A,B,C, and D had also been performed on-line. Technical Specification Tables 4.2.B, 4.1.2 and 4.2.A, Note (7) also required these transmitters to be calibrated during refueling outages. The calibration of the transmitters had been removed from the refuel outage schedule and rescheduled for on-line work to allow more time to perform emergent outage work. An evaluation by the I&C department concluded the transmitters could be safely calibrated on-line. Action was taken to calibrate the transmitters. The transmitters were calibrated with satisfactory as-found results prior to the expiration of the surveillance interval (24 months plus 25 percent grace period). The cause was due to an incorrect interpretation of the surveillance requirements by the plant personnel who performed the review and approval of the transfer to on-line performance. The master surveillance tracking system nodes associated with the analog trip transmitters identified in this report have been revised to be consistent with the technical specification tables. At the time of discovery, the plant was operating at approximately 100 percent power with the mode switch in the RUN position. The reactor vessel pressure was at approximately 1035 psig with the reactor water at the saturation temperature for vessel pressure. This event posed no threat to public health and safety.
2931997015 | Pilgrim | 11/04/1997 | 06/01/1998 | 9806100185 | <strong>SSW Pumps Overload Settings too Low for Single SSW Pump Operation with Degraded Voltage</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1997, while reviewing the results of recent off-site performance testing of the bowl assembly of a salt service water (SSW) pump, it was identified that with a single pump operating and supplying one cooling loop, the pump's brake horsepower will approach 113 HP. The current drawn by the pump motor at this load, in particular under a conservative assumption of ten percent decrease in motor terminal voltage, could have resulted in an overload (OL) relay trip with the (then) existing trip setting of 100 percent of the pump motor thermal OL relay. Both containment cooling system loops were declared inoperable and a twenty-four hour cold shutdown limiting condition for operation (LCO) was entered in accordance with Technical Specifications at 1940 hours on November 4, 1997. The root cause of the condition involving the SSW pumps is attributed to a variation in SSW pump BHP characteristics due to the Original Equipment Manufacturer (OEM) for these pumps being changed from Goulds Pumps to Johnston Pump. Immediate corrective action taken consisted of sequentially removing the SSW pumps from service and resetting the OL relay for each service water pump motor to 115 percent. Prior to declaring the SSW pumps operable, each OL relay was tested satisfactorily. The LCO was terminated at 0300 hours on November 5, 1997. The condition was discovered during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The reactor vessel pressure was about 1035 psig with the reactor water at the saturation temperature for that pressure. The condition posed no threat to public health and safety.
2931997016 | Pilgrim | 11/05/1997 | 06/19/1998 | 9806250204 | <strong>Recirculation System Loop 'B' Pump Trip due to Surveillance Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1997, at 1810 hours, an unplanned closing of the recirculation system loop 'B' pump discharge valve occurred during the performance of a surveillance of the emergency diesel generator (EDG) 'B' initiation circuitry. The closing of the valve resulted in the automatic trip of the recirculation system loop 'B' motor-generator (MG) set and pump, consequent decrease in reactor core flow and reactor power, and reactor operation in the caution zone of the reactor core power - flow map. Licensed operator response included the insertion of control rods to achieve reactor operation at less than the 100 percent load line. The root cause of the event was an inadequacy in the test procedure being performed in that the procedure did not include guidance regarding how long the logic reset switch was to be depressed for a reset of the logic circuitry. The EDG 'B' surveillance procedure, being performed at the time of the event, will be revised to include the status of additional relays prior to resetting the circuitry. All logic system functional test procedures will be reviewed for similar improvement. <br /><br /> The event occurred during power operation while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor vessel water at the saturation temperature for that pressure. The event posed no threat to public health and safety
2931997017 | Pilgrim | 11/04/1997 | 12/18/1998 | 9812290153 | <strong>Past Operation with Service Water Temperatures Greater than Design due to Licensing Basis Ambiguity</strong><br /><i>Abstract:&nbsp;</i>During certain periods of past operation, the inlet seawater temperature of the open loop, safety-related salt service water (SSW) system was greater than 65 degrees F. The 65 degree F parameter is significant because, prior to the issuance of license amendment 173 on July 3, 1997, 65 degrees F was assumed in safety-related heat removal analyses described in the updated final safety analysis report (UFSAR). <br /><br /> The cause of operating with seawater/SSW inlet temperatures greater than 65 degrees F was ambiguity in the licensing basis. Actions taken included the issuance of a safety evaluation, and a license amendment request. UFSAR changes identified in the safety evaluation were included in the 1996 update of the UFSAR. Subsequently, license amendment 173 authorized plant operation with seawater temperatures to 75 degrees F. This report is submitted as part of corrective actions identified in response to NRC findings contained in Inspection Report 97-05. Broader corrective action planned regarding licensing basis ambiguity will be tracked as part of the commitments made during an enforcement conference held on November 21, 1997. <br /><br /> The condition occurred while operating at various power levels and included 100 percent reactor power operation. The condition posed no threat to public health and safety.
2931997018 | Pilgrim | 11/04/1997 | 12/04/1997 | 9712090137 | <strong>Plant Operation Outside of Environmental Qualification Envelope due to Nonconservative Drywell Temperature Profile</strong><br /><i>Abstract:&nbsp;</i>The drywell temperature analysis of record (1987) was nonconservative until 1996 due to a NSSS supplier computer modeling error. The computer modeling error involved certain small steamline breaks and an incorrect assumption that drywell temperature would be equal to the reactor vessel temperature. Subsequently, a new NSSS supplier analysis predicted a higher drywell temperature profile than the analysis of record. An immediate evaluation of the environmental qualification of all affected safety-related equipment inside the drywell determined that all equipment was qualified except the position indicators of five containment isolation valves which were subsequently verified qualified through retesting. A new NSSS supplier analysis has been accepted and the environmental specification revised to incorporate the new drywell temperature profile. A more conservative containment analysis has been mandated by License Amendment 173. <br /><br /> All input values and assumptions are being approved by BECo prior to acceptance of the analysis. <br /><br /> This report was submitted following reassessment of reportability as a result of NRC Inspection 97-05.
2931997019 | Pilgrim | 11/04/1997 | 12/04/1997 | 9712090072 | <strong>Analysis Assumption to Close Valves Supplying Cooling Water to Non-Essential Heat Loads Not Transferred Into Procedure</strong><br /><i>Abstract:&nbsp;</i>During past periods of reactor operation when the reactor building closed cooling water (RBCCW) system was required to be operable, actions to close RBCCW valves that supply cooling water to non-essential heat loads were not contained in a written procedure(s). Specifically, the closure of RBCCW system valves to isolate non-essential loads during design basis loss of coolant accident conditions was not translated into a procedure(s), contrary to the updated FSAR. The cause was inadequate design control in that the action to isolate RBCCW flow to non-essential heat loads during accident conditions was not translated into a procedure. Corrective actions taken included performing a safety evaluation and revising a procedure to include the action, and initiating calculations to demonstrate adequate RBCCW flow will be supplied to all safety-related heat loads when the non-essential RBCCW heat loads are not isolated. This report is submitted as a result of findings stemming from NRC Inspection Report 97-05. Broader corrective actions to be taken will be tracked as part of commitments made at an enforcement conference held on November 21, 1997. The condition existed since initial plant startup. During that time, reactor operation occurred at various reactor power levels including 100 percent.
2931997020 | Pilgrim | 11/04/1997 | 12/04/1997 | 9712090204 | <strong>RHR Operating Procedure Did Not Reflect Analysis</strong><br /><i>Abstract:&nbsp;</i>During past periods of reactor operation when the RHR system was required to be operable, Pilgrim Station operated outside the design basis because procedures to establish an RHR flow-rate that did not comport with the analysis of record or the design-basis as described in the UFSAR. Specifically, containment heat removal during a design-basis loss of coolant accident with a flow-rate as low as 4800 gpm in procedures was less than the 5100 GPM established in the analysis of record (UFSAR Chapter 14 and calculation M-664). <br /><br /> The cause was inadequate translation of analysis parameters to operating procedure parameters. Corrective actions taken included performing a safety evaluation and revising the RHR operating procedures to reflect the UFSAR Chapter 14 and calculation M-664. Broader corrective action will be separately tracked as part of commitments made at an enforcement conference held on November 21, 1997. This report is submitted as a result of findings stemming from NRC Inspection Report 97-05. <br /><br /> The condition could have existed since initial plant startup. During that time, reactor operation occurred at various reactor power levels including 100 percent.
2931997021 | Pilgrim | 11/04/1997 | 12/04/1997 | 9712090114 | <strong>Emergency Diesel Generator Ambient Air Temperature</strong><br /><i>Abstract:&nbsp;</i>During past periods of reactor operation when the emergency diesel generators (EDGs) were required to be operable, Pilgrim Station operated outside the design as described in FSAR Table 10.9-2 because ambient air temperatures experienced during certain periods were greater than the 88 degrees F shown on the table. <br /><br /> The cause has been attributed to ambiguity in the FSAR; the 88 degree value is believed to be a nominal design parameter and not a design limit but the FSAR is not clear on this point. Since the system sections of the FSAR only describe the safety design basis and the safety design objectives, not the bounding parameters for analysis, it is difficult to objectively determine which parameters constitute the design basis as defined in 10CFR50.2 and which provide design information. <br /><br /> Broad corrective action includes a design basis recapture project and upgrading the FSAR to clearly describe design basis information. These commitments will be tracked as part of the commitments made at an enforcement conference held on November 21, 1997. This report was submitted as a result of findings contained in NRC Inspection Report 97-05. This condition has occurred during certain summer periods since initial plant startup. During those periods, reactor operation occurred at various power levels including 100 percent.
2931997022 | Pilgrim | 10/28/1997 | 11/28/1997 | 9712090049 | <strong>Temporary Power Cables and Extension Cords Draped or Tie Wrapped to Class 1E Conduits In The Reactor Building In Violation of Electrical Separation Criteria.</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, during a plant walkdown, temporary power cables and extension cords were found draped or tie wrapped to class 1E conduits in the reactor building in violation of electrical separation criteria. Examples included cables off a power pack for torus temporary lighting, extension cords off a power pack for the steam tunnel, and an extension cord plugged into an outlet for use in the reactor water cleanup system pump room (cord was not energized at the time of the walk down) The plant walkdown was prompted by a recent nuclear network message involving a similar problem at another power plant. Immediate corrective action was taken to remove and reroute extension cords or deenergize and red tag the applicable power packs. Temporary lighting in the torus room will remain deenergized until an engineering evaluation has been performed to determine acceptable electrical separation. A policy statement will be issued to station personnel regarding the use of temporary power cables and extension cords. The procedure that governs the control temporary power, does not provide guidance regarding electrical separation with respect to the use of temporary power cables and extension cords. Procedure 3.M.3-36, "Control of Temporary Power," will be revised to incorporate required separation criteria guidance. This condition posed no significant threat to the public health and safety.
2931997023 | Pilgrim | 10/31/1997 | 05/21/1998 | 9806010396 | <strong>Both Radwaste Building Trucklock Doors Closed Resulting in a Configuration Inconsistent with Tornado Depressurization Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1997, at about 1230 hours, PNPS engineers discovered the Radwaste Building in a configuration not considered in the Updated FSAR or tornado depressurization analysis. Thus, a design basis tornado could have affected the availability of Class 1 equipment stored or housed in (and adjacent to) the Radwaste Building. The tornado depressurization analysis assumes the truck doors (a single set) to the Radwaste Building will fail at a differential pressure of 0.5 psi. Engineers discovered two complete door assemblies installed in the doorway, both in the closed position. As a result of the discovery, one of the doors was tagged open. <br /><br /> The cause was inadequate control of the subcompartment barriers. Immediate corrective actions included opening and tagging one of the doors. Longer term corrective actions include implementing a formal program to control subcompartment barriers and removing the outer doors to restore the building to its original configuration. <br /><br /> The condition was discovered during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The condition posed no threat to public health and safety.
2931997024 | Pilgrim | 10/23/1997 | 11/24/1997 | 9712030016 | <strong>Plant Valve Configuration for Inerting Primary Containment was outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>Abstract On October 23, 1997, during a review of the primary containment atmosphere control system as a result of a General Electric (GE) notification of a potential 10CFR21 issue regarding suppression pool (torus) bypass leakage, one potential bypass flow path was identified through which the drywell air space could communicate with the torus air space. The potential for this event existed while in the valve line up for inerting the primary containment because a single failure could occur that causes valves AO-5035A and PCIS AO-5036A to fail open on a primary containment isolation signal. These valves share a common actuating relay, RPWA1 and relay contact 1-2, that provide the primary containment isolation system signal to these valves. If the plant was in the process of changing from torus to drywell inerting and a LOCA event occurred, a single failure of relay RPWA1 to deenergize or the single failure of relay RPWA1 contact 1-2, to open would prevent AO-5035A and AO-5036A from closing, resulting in a steam bypass path from the drywell to the torus air space without passing through the torus downcomers. <br /><br /> This operating configuration was determined to be outside the design basis of the of the plant. Immediate action was taken to establish administrative controls that preclude entry into the inerting portion of Pilgrim Nuclear Power Station Procedure 2.2.70, "Primary Containment Atmosphere Control System." Procedure 2.2.70, will be revised to eliminate this vulnerability. This event posed no significant threat to the public health and safety.
2931997025 | Pilgrim | 11/23/1997 | 08/19/1998 | 9808240198 | <strong>Completion of a Required Shutdown due to Two Inoperable Main Steam Isolation Valves (MSIVs)</strong><br /><i>Abstract:&nbsp;</i>On November 23, 1997, at 2215 hours, a Technical Specification (TS) required shutdown was completed because two main steam isolation valves (MSIVs) in separate main steam lines were inoperable. During the subsequent cooldown, the reactor vessel flange temperature could not be monitored/logged as required by TS. <br /><br /> The root cause of the failure of the two MSIVs to close was main closure spring relaxation. Corrective action taken included replacement of some closing springs and overhaul of actuators. Corrective action planned includes replacement of closing springs on the remaining MSIVs, evaluation of alternate spring designs, and revision of maintenance procedures. The root cause of the failure of the vessel flange thermocouples could not be conclusively determined. Corrective action planned includes restoring the reactor vessel flange thermocouples and improving how they are maintained. <br /><br /> The event occurred while operating at 50 percent reactor power with the reactor mode switch in the RUN position. The reactor vessel pressure was approximately 972 psig with the reactor water at the saturation temperature for that pressure. The event posed no threat to public health and safety.
2931997026 | Pilgrim | 12/06/1997 | 01/05/1998 | 9801130243 | <strong>Automatic Scram Due to High Reactor Water Level During Power Ascension</strong><br /><i>Abstract:&nbsp;</i>On December 6, 1997, at 0907 hours, an automatic scram occurred at approximately 75 percent reactor power. The scram was initiated as a result of a turbine trip due to high reactor water level (>45 inches) experienced during power ascension following an outage. The turbine trip/reactor scram resulted in the insertion of the control rods and transfer of power to the startup transformer. <br /><br /> The cause of the scram was the failure of the "A" feedwater regulating valve (FRV) in the full open position due to the misalignment of the valve clip inside the pilot valve assembly of the positioner. Corrective action taken included replacing the valve positioner and performing calibration adjustments. <br /><br /> The scram occurred while the reactor mode selector switch was in the RUN position. The reactor vessel pressure was approximately 1004 psig with the reactor water temperature at the saturation temperature for the reactor pressure. The event posed no threat to public health and safety.
2931997027 | Pilgrim | 11/28/1997 | 12/29/1997 | 9801070189 | <strong>Emergency Diesel Generator Winter Ambient Temperature</strong><br /><i>Abstract:&nbsp;</i>During past periods of reactor operation, when the emergency diesel generators (EDGs) were required to be operable, Pilgrim Station operated outside the design as described in FSAR Table 10.9-1 for the diesel generator room heating and ventilation because room air temperatures experienced during certain periods were less than the 60 degrees F shown on the table. <br /><br /> The cause has been attributed to ambiguity in the FSAR. Because the system sections of the FSAR describe the safety design basis and the safety design objectives, not the bounding parameters for analysis, it is difficult to objectively determine which parameters constitute the design basis, as defined in 10CFR50.2, and which provide design information. <br /><br /> Compensatory measures will be instituted when the diesel generators are not running and the room air temperature is below 60 degrees F. Broad corrective action includes a design basis recapture project and upgrading the FSAR to clearly describe design basis information. An analysis to determine the design temperature limits for the diesels will be performed in conjunction with the design basis reconstitution project. <br /><br /> This condition has occurred during certain winter periods since initial plant startup. During those periods, reactor operation occurred at various power levels including 100 percent.
2931997028 | Pilgrim | 12/17/1997 | 01/16/1998 | 9801210090 | <strong>LER 97-028-00, Intake Structure in a Configuration Inconsistent with Tornado Depressurization Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1997, at 1708 hours, PNPS personnel informed the NRC that the tornado depressurization analysis did not consider all of the depressurization pathways in the intake structure. Thus, a design basis tornado could have affected the availability of Class 1 equipment stored or housed in the intake structure. The station tornado procedure requires operators to secure open all intake structure doors, thereby creating large openings not considered in the tornado depressurization analysis. <br /><br /> The cause was inadequate control of the tornado barriers. Operations declared the intake structure operable based on an engineering evaluation (EE 97-068) that showed the additional vent paths, not considered in the tornado analysis, are insignificant compared to other larger openings already considered in the analysis. Long term corrective actions include resolving the inconsistencies between the tornado depressurization analysis for the intake structure and the station tornado procedure. PNPS also plans to implement a formal program to control compartment barriers. <br /><br /> The condition was discovered during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The condition posed no threat to public health and safety.
2931997029 | Pilgrim | 12/16/1997 | 01/09/1998 | 9801210192 | <strong>Shutdown Cooling (SDC) Suction Valves Vulnerable to Damage from Potential Failure Mode Involving Hot Shorts</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1997, while reviewing the results of a previous reportability evaluation (August, 1997), the determination was made that the SDC suction isolation valves were vulnerable to mechanical damage from a potential failure mode involving hot shorts and that this condition was outside the design basis of the plant. The condition could have caused a spurious operation of these MOVs during a control room or cable spreading room fire, resulting in damage to either of these valves such that the SDC mode of the RHR system would not be available to support the safe cooldown of the plant. The cause of this condition is attributed to the failure to recognize the new failure mode discussed in NRC IN 92-18. Immediate corrective action consisted of implementing a temporary modification on August 21, 1997, when the condition was originally discovered. The temporary modification deenergized both valves by opening their respective breakers which removes the potential failure mode for a postulated hot short damaging either valve. Long term corrective action will consist of either converting the temporary modification to a permanent change or developing another design change to modify the control circuits for these MOVs. The condition was discovered during power operation while at 100 percent reactor power. The reactor mode selector switch was in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water at the saturation temperature for that pressure. The condition posed no threat to public health and safety.
2931997030 | Pilgrim | 12/24/1997 | 01/23/1998 | 9802040120 | <strong>Missapplication of FSAR Drywell Free Volume</strong><br /><i>Abstract:&nbsp;</i>On December 24, 1997, a discrepancy was identified between FSAR Table 5.2.1 which identifies the approximate drywell free volume to be 147,000 cubic feet and draft engineering calculations which indicate the actual free volume to be approximately 137,000 cubic feet. The 147,000 cubic feet drywell free volume value was used as a design input for a variety of design basis calculations and analyses. <br /><br /> The inappropriate use of FSAR Table 5.2.1 drywell free volume value in design basis calculations and analyses appears to have resulted from incomplete understanding and validation of its basis. Corrective action taken included reviewing affected calculations and verifying operability. Corrective action planned includes revising the FSAR Table 5.2.1 to clarify the drywell free volume value and completion of drywell volume calculations. <br /><br /> The condition was identified while at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the reactor water temperature at the saturation temperature for the reactor pressure. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B). The condition posed no threat to public health and safety.
2951997001 | Zion 1, Zion 2 | 01/10/1997 | 11/07/1997 | 9711200226 | <strong>Recirculation Sump Cover Plate Holes Were Not Installed at Original Construction</strong><br /><i>Abstract:&nbsp;</i>On 1-10-97 while in mode 5, during a dimensional verification for a pending modification, it was noted that two 1" holes were not in the Unit 2 containment recirculation sump cover plate as detailed on a plant structural drawing. At approximately 0700 on January 11, 1997 inspection of the Unit 1 sump cover plate verified that the holes on that plate were missing also. Because adequate venting capability of the sump could not be proven, the operating department declared both Residual Heat Removal (RHR) [BP] Pumps inoperable, entered Technical Specification 3.8.3 and placed Unit 1 on a 4 hour limiting condition for operation (LCO). The sump covers on both units were removed, holes were drilled and the covers replaced. Upon completion of this work the RHR Pumps were declared operable. <br /><br /> The holes are believed to have been missed because of an original plant construction installation error. The investigation could not determine why the holes were missing. <br /><br /> An evaluation has been performed to show there was ample time for operators to align alternate water sources to the Refueling Water Storage Tank (RWST). Therefore the safety significance of this event is minimal.
2951997002 | Zion 1, Zion 2 | 01/17/1997 | 02/18/1997 | 9702270260 | <strong>Containment Isolation Valves Not Tested Prior To Leaving Cold Shutdown. This Was Caused By Management Deficiencies In The Technical Specification Implementation Process. This Event Resulted In Minimal Safety Impact.</strong><br /><i>Abstract:&nbsp;</i>In January 1997 it was identified that in previous outages some PTs which contain containment isolation valves (CIV) were scheduled for performance after entering Mode 4. Zion Technical Specification (TS) 3.9.3.A/4.0.5 requires that CIVs be operable prior to entering Mode 4. Amendment 129/118 and Amendment 136/125 implemented TS 4.0.5 which changed the required mode of testing for CIVs. The components in question, which are required during accident conditions, are in systems which fulfill multiple functions (e.g, ECCS and Containment Isolation). <br /><br /> The cause of this event was inadequate review and implementation of procedures associated with Amendment 129/118 and Amendment 136/125. The process that controls License Amendment changes does not provide for independent review. As a result a single error or erroneous conclusion caused the implementation process to fail. <br /><br /> Although the following valves were not tested prior to entry into Mode 4 in previous outages, they were tested satisfactorily prior to entry into Mode 1. Therefore, the satisfactory testing prior to Mode 1 gave assurance these valves were operable during operation, and gives reasonable assurance these valves were operable prior to entering Mode 4. Thus, the safety impact was minimal. <br /><br /> The corrective actions are: 1) Unit 2 containment isolation valves will be verified tested prior to Unit 2 entering Mode 4 from Z2R14. associated procedures or create new procedures to ensure that CIVs are tested prior to entering the required mode of applicability. 3) Zion Station IST Group is continuing a review of the IST program to ensure all requirements are met. 4) Zion Station will modify the Technical Specification Amendment implementation process to include a required independent verification.
2951997003 | Zion 1, Zion 2 | 01/17/1997 | 02/18/1997 | 9702270298 | <strong>Non-Compliance with Emergency Diesel Generator Technical Specifications Due To Programmatic Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On 17-JAN-97, while reviewing a report of operating experience from another facility, Zion personnel determined that Emergency Diesel Generator (EDG) tests completed in the previous refueling outages on both units did not meet the Technical Specification Surveillance Requirement 4.15.1.B.3.f. The performed tests incorrectly specified that the EDGs would be loaded to at least 4,000 Kilowatts (N), and the EDGs were run at loads up to 4,180 kW. The Technical Specification requirement specified a range of FOG loads as follows: "...greater than or equal to 3,600 kW and less than or equal to 4,000 KW." The event did not adversely impact safety at the facility nor of the public. The event was caused by insufficient barriers in the Technical Specification implementation process to prevent a single error from causing the process to fail. Zion Station has corrected the deficient procedures and completed testing on the operating unit. In addition, Zion Station will examine the Technical Specification Amendment implementation process, with particular emphasis on document review and preparation practices, and the Station will implement appropriate corrective actions.
2951997004 | Zion 1 | 02/21/1997 | 03/20/1998 | 9803240356 | <strong>Reactor Shutdown Per LCO 3.6.1 Due To One Inoperable Containment Spray Pump.</strong><br /><i>Abstract:&nbsp;</i>On 2/11/97, Zion Station Unit 1 was at 42% power, at stable operations. The 1C diesel-driven Containment Spray (CS) [BE] pump was placed out of service for planned maintenance. On 2/19/97 at 1020, the ACE CS pump was declared inoperable after failing a periodic test. Unit 1 subsequently entered Technical Specification Limiting Condition for Operation (LCO) 3.6.1.C which allows 48 hours for repairs or commence shutdown. The immediate cause was a plugged fuel strainer from the pump's fuel oil day tank [DC]. During subsequent testing the ACE CS pump experienced a 10 to 20 second delay prior to starting. The immediate cause was a degraded starting solenoid. Both starting solenoids were immediately replaced. On 2/21/97 at 1358, the ACE CS pump was successfully tested operable; however, post-test lineup verifications could not be completed within the required LCO time. Unit 1 was shutdown in compliance with LCO 3.6.1.D. <br /><br /> The diesel fuel day tanks were cleaned to prevent recurrence of the fuel system failure. The starting solenoids were placed on a 3-year starting replacement frequency to prevent recurrence of the starting solenoid failure. <br /><br /> The safety significance of this event was minimal. <br /><br /> On 2/13/98, Zion Station certified its shutdown status by letter to the Nuclear Regulatory Commission. As a consequence of this activity, the Containment Spray system is not expected to be required for use at any time in the future
2951997005 | Zion 1 | 02/21/1997 | 03/02/1998 | 9803050444 | <strong>Supplement to Unapproved Mode Change with Technical Specification Required Equipment Inoperable.</strong><br /><i>Abstract:&nbsp;</i>During a Technical Specification (TS) required plant shutdown, a reactor operator attempted to reduce power to the Point of Adding Heat (POAH) by continuously inserting the control rods until the power level specified in-the shutdown procedure was reached. When the operator stopped rod insertion, power continued to decrease below the POAH. This resulted in a mode change to Mode 3 -(Hot Shutdown TS Definition is K/K). The operator then withdrew rods approximately 80 steps over the next two minutes in an attempt to correct the subsequent power under shoot and resulted in an unapproved Mode change. The core remained subcritical by about -0.48-06 DELTA K/K as a result of the final rod moves prior to a manual scram being inserted. This supplement to LER 97-005 contains 1) The final root causes of this event supplied from an Independent Investigation. 2) Identification of all equipment inoperable at the time of the event. 3) A Safety Analysis for the inoperable equipment at the time of the event. 4) A detailed Reactivity Event Safety Analysis supplied from the Independent Investigation. 5) Long term corrective actions based on the results of the Corporate Investigation.
2951997006 | Zion 1, Zion 2 | 02/22/1997 | 03/26/1997 | 9704010108 | <strong>Zion Station Exceeded A Limiting Condition For Operation Due To Inadequate Procedure Controls</strong><br /><i>Abstract:&nbsp;</i>On Saturday 22-FEB-97, the Unit Supervisor (US) approved and at 1310 the operators began to install an Out Of Service (OOS) request in conjunction with a Work Request (WR) that had been prepared to repair the instrument sensing line manifold for the Loop A Reactor Coolant System (RCS) flow detector (1FI-414). The WR was included in the forced outage schedule for unit 1. The forced outage began at 1415 hours on 21-FEB-97 when unit 1 entered MODE 3 (HOT SHUTDOWN). The valve manipulations specified by the DOS checklist rendered 3 of 3 Loop A RCS flow instruments INOPERABLE. Technical Specification 3.1 'Reactor Protection Instrumentation and Logic,' requires the RCS flow instruments to be OPERABLE in MODES 1,2,3,4 and 7. The Technical Specification allows for less than 1 flow instrument operable up to 8 hours if the failed channels are placed in the tripped mode. If these conditions are not met, the unit is to be in HOT SHUTDOWN within 24 hours and in COLD SHUTDOWN within the following 24 hours. Although the original failed instrument (1FI-414) had been placed in the tripped mode, the additional instruments that became inoperable as a result of the OOS valve manipulations were not placed in the tripped mode until Monday; 24-FEB-97 at 1330 hours. This event was caused by inadequate procedures and inadequate verification practices. This event did not impact plant, personnel nor public safety because the reactor was maintained in the HOT SHUTDOWN MODE with reactor trip breakers open throughout the event and ended with the unit in COLD SHUTDOWN. Corrective actions for this event include issuance of a Standing Order to require review of Technical Specifications during DOS procedure implementation, revising appropriate procedures to require Technical Specification review in verifying compliance during maintenance, and training for appropriate personnel.
2951997007 | Zion 1, Zion 2 | 03/11/1997 | 04/10/1997 | 9704160044 | <strong>System Auxiliary Transformer Trip Caused By Spurious Operation of the Sudden Pressure Relay with Minimal Impact to the Plant</strong><br /><i>Abstract:&nbsp;</i>At 1554 on March 11, 1997, during rounds, an operator opened the local System Auxiliary Transformer (SAT) panel. While leaning gainst the open panel to tap the oil temperature gauge mounted above the panel, he heard a click. The SAT deluge activated to spray water on the SAT, the SAT tripped, and Unit 1 experienced an undervoltage condition on the safeguard buses. The loads on the safeguard buses were stripped, the Emergency Diesel Generators (EDG) started, and essential loads were sequenced onto the safeguard buses. This event is reportable per 10CFR 50.73(a)(2)(iv). The sudden pressure lockout relay and associated auxiliary relay were found tripped which indicated the SAT sudden pressure relay (SPR) circuitry had energized. Testing confirmed that the SAT had not experienced a sudden pressure event and the sudden pressure circuit was operating properly. Operator error was ruled out. The EDG safe shutdown timer was found not to have fully reset automatically and was reset manually. The safety significance of these events were minimal as safety related equipment actuated as designed and the timer reset failure does not affect EDG operation. <br /><br /> The cause of the SAT trip could not be conclusively determined. The most probable cause is spurious operation of the SAT SPR. Spurious operation of SPRs has been experienced both within ComEd and the utility industry. Corrective actions taken: 1) the SAT was tested for damage, and none was found, 2) the SPR was replaced with a newer, more reliable model and tested satisfactorily after installation, 3) the faulty sudden pressure relay was sent to a lab for analysis, 4) the Unit 2 SAT SPRs will be replaced, 5) Operator actions near electrical panels were addressed, and 6) repairs to the safe shutdown timer are scheduled.
2951997008 | Zion 1, Zion 2 | 03/21/1997 | 04/21/1997 | 9704280005 | <strong>Air Filters Containing Aluminum Inadvertently Installed in Containment, Caused By Faulty Parts Selection Process, Resulting In Exceeding The Design Basis.</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1997, while investigating applicability of a vendor notification letter, Station Maintenance Engineering discovered High Efficiency Particulate Air (HEPA) filters containing aluminum were installed in unit 1 and 2 reactor containment buildings. The surface area of aluminum installed as a result of these HEPA filters exceeded the 915 square foot limit established by the Updated Final Safety Analysis (UFSAR). This condition can cause excessive Hydrogen gas concentrations during the Design Basis Loss of Coolant Accident (LOCA) as a result of the reaction between the aluminum and the sodium hydroxide solution in the containment spray fluid. The originally installed HEPA filters were certified by the manufacturer on 16-OCT-73 to comply with the non-aluminum requirement of the design specification. The original filters were in place in the Containment Charcoal Filter Units (CCFU), two in unit 1 and two in unit 2, until replaced as corrective work to address decreasing filter efficiencies. The plant's four CCFU HEPA filters were replaced in the period between April, 1992 and January, 1994. This event was caused by failure to verify the parts were correct. Public safety was not adversely affected during this period. The assessment of safety consequences shows the lower flammability limit for hydrogen would not have been reached within 30 days of the LOCA, and venting the containment to alleviate excess hydrogen would not have been necessary. Therefore, 10CFR100 limits would not have been impacted due to this event. Corrective actions for this event are removing or replacing the aluminum containing HEPA filters, strengthening standards and control of part specification practices in work package preparation, and training appropriate personnel.
2951997009 | Zion 1, Zion 2 | 01/14/1997 | 05/14/1997 | 9705200417 | <strong>1FCV-CS0002 was inoperable between January 15, 1997, and February 8, 1997, because of failing to verify that the acceptance criteria for the return to service of 1FCV- CS0002 was met.</strong><br /><i>Abstract:&nbsp;</i>Operating personnel failed to meet Technical Specification(TS) 4.0.5 "Inservice Inspection Surveillance Requirements." During his review of PT-6B-ST "Containment Spray B Pump Tests and Checks." a Unit Supervisor (US) misinterpreted the partially performed Technical Staff Group Procedure (TSGP) TSGP-31, "Setting minimum flow stops for FCV-CS0001, 2. 3" as meeting the operability requirements of 1FCV-CS0002. The US assumed that TSGP-31 had been completely performed, but did not review TSGP31. Therefore 1CFV-CS0002 was inoperable between January 15 and February 8, 1997. On February 8, 1997, 1FCV-CS0002 was successfully "Fail Open" proven operable. Although not correctly documented, the valve was operated during the performance of TSGP-31 sufficiently to provide assurance that following maintenance to the valve, it would fail open. When first reviewed, it was considered that operability of the 1FCV-CS0002 had been shown during the maintenance activity and this event was not reportable. Upon further evaluation, it was determined on April 14, 1997, that because PT-6B-ST was not performed on 1FCV-CS0002, TS 4.0.5 requirements were violated. The Cause of this event is the practice which allows a single License Shift Supervisor to determine what sections of a prescribed Post Maintenance Test will be performed. A contributing cause of this event was the Unit Supervisor failing to verify that the acceptance criteria for the return to service of 1FCV-CS0002 was met. Corrective actions include 1) Unit Supervisor has been counselled. 2) This event will be covered in Licensed Operator current events training. 3) Deletion of a sections of prescribed Maintenance Test will require concurrence of two License Shift Supervisors.
2951997010 | Zion 1, Zion 2 | 04/04/1997 | 05/05/1997 | 9705080273 | <strong>Missed Radiation area surveys because of inadequate Technical Specification review: no impact</strong><br /><i>Abstract:&nbsp;</i>At 0350 hours on April 4, 1997, Area radiation monitor ORE-0006 'Primary Sample Room Area Monitor' failed. The Unit Supervisor(US) reviewed the Technical Specifications(TS), Zion Operational Determination Manual (ZODM) Process Radiation (PR) section, and Zion Radiation Protection(ZRP) ZRP 5820-12 'Out of Service Surveillance for Radiation Monitors.' On April 6. 1997, the same US who was on shift on April 4. reviewed the TS and this time noticed TS 3.14-1 table reference to OR0006. The consequences of the event are two missed area surveys to meet the TS requirements for a failed radiation detector. The causes of this event are I)a cognitive error by the US in his review of the TS: 2)no confirming review required or performed by either the Shift Engineer(SE) or Nuclear Station Operator(NSO); Less than adequate questioning attitude by any subsequent reviewers. A contributing factor in this event was an error in the ZRP 5820-12. Corrective Actions: 1)US, SE and NSO have been counseled. 2)ZRP 5820-12 has been corrected. 3)The US has presented this event at a Licensed Shift Supervisor meeting to ensure awareness and emphasize lessons learned. 4)The US will modify procedures to require a confirming review be performed by the NSO. 5)Operating Training Department will determine the type of training required as a result of this LER and the resultant procedure changes and incorporate lessons learned into the Licensed Operator Training.
2951997011 | Zion 1, Zion 2 | 04/23/1997 | 12/18/1997 | 9803050452 | <strong>Main Steam Instruments Declared Inoperable Due To Calculation Error with Minimal Safety Impact</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1997, the Main Steam Line pressure transmitters were declared inoperable. The pressure transmitter instrument setpoints were based on a loop accuracy calculation that did not utilize the correct cable lengths or take into account the elevated temperature resulting from a Main Steam Line Break (MSLB). Use of the proper (longer) cable lengths and elevated temperature introduces inaccuracies into the instrument loops because of increased leakage currents from the instrument cables that could prevent the performance of safety functions. <br /><br /> The safety significance of this issue is minimal because there are other devices that perform the same protective functions and indications. <br /><br /> The root cause of the event is management deficiency since ComEd exercised inadequate control over contractor prepared calculations in 1991. Contributing to the event, the ComEd EQ group failed to transmit the necessary information to the affected groups as required by procedure. <br /><br /> The corrective actions are to revise the instrument loop insulation resistance (IR) calculations, replace the Fischer Porter pressure transmitters, assess the need to perform a modification to upgrade the instrument cables, and conduct training to emphasize the necessity for interdisciplinary review. LER 1-97-020 resulted from the performance of corrective actions for this LER. Additional corrective actions are discussed in LER 1-97-020.
2951997012 | Zion 1, Zion 2 | 04/23/1997 | 05/23/1997 | 9706020157 | <strong>Inappropriate Test Criteria for Hydrogen Recombiner Because of Interpretation of Tech Specs with Minimal Impact on Plant</strong><br /><i>Abstract:&nbsp;</i>Technical specification #4.8.8.A requires readiness testing of the hydrogen recombiner in accordance with the manufacturer's recommended tests. The plant testing procedures did not include the manufacturer's acceptance criteria for testing. Because the station tests contained acceptance criteria which were less restrictive, the specification requirements were not met. However, the testing performed was sufficient to confirm that the hydrogen recombiner would function as required to mitigate the effects of an accident. Though the specific root cause of the event could not be determined, the apparent cause of the event was a low standard for documentation of changes to vendor information and for explicit Technical Specification compliance at Zion Station which assumed the Technical Specifications could be interpreted rather than followed explicitly. There was minimal safety significance to this event. <br /><br /> Corrective actions include: 1) changing the high level and low level test criteria to conform to the manufacturer's recommendations, 2) updating of the on-site vendor manual to reflect new vendor recommendations. 3) the results of the 1995 Technical Specification compliance self assessment will be reviewed to ensure that other findings have been appropriately addressed.
2951997013 | Zion 1 | 04/12/1997 | 06/02/1997 | 9706060205 | <strong>VT-3 Inspection Requirements of Relief Request CR-13 for Reactor Head Bolting Were Not Performed</strong><br /><i>Abstract:&nbsp;</i>Although this report is not required per 10CFR56.73 it is being submitted voluntarily. <br /><br /> Technical Specification Section 4.0.5.a requires that inservice inspection (ISI) of ASME Class 1, 2 and 3 components shall be performed in accordance with Section XI of the ASME Boiler and Pressure Vessel Code, except where specific written relief has been granted by the Commission pursuant to 10 CFR 50.55a (g)(6)(i). Written relief from the ASME Section XI, 1989 Edition Code Requirement of IWA-5242(a), for the inspection of bolted connections on systems containing boric acid was granted by the NRC in the form of Relief Request CR-13. However, the Relief Request CR-13 alternative examination visual examination (VT-3) of the reactor head bolting with the insulation removed and the system depressurized each outage prior to dismantling of the head was not performed. A review of past refueling outages inspections revealed that this VT-3 alternative examination required by Relief Request inspections CR-13 had not been performed during this current ISI Interval, nor had the inspection designated by the Code been performed. <br /><br /> The cause of this event is the failure to revise the ISI database after the Safety Evaluation Report (SER) was received from the NRC approving the use of the CR-13 relief request. This failure of revising the ISI database resulted because there was no process which took this type of information and incorporated it into program documents. By rot having this process in place, it was possible to miss an item such as this inspection requirement identified in relief request CR-13. <br /><br /> VT-1, VT-3 and UT inspectors of the Unit 1 Reactor Head Bolting after detensioning was completed for the current outage. In addition, a review of previous outages visual, surface and volumetric inspections performed during the Third ISI Interval was also completed. These additional inspections and reviews concluded that no degradation including degradation due to boric acid of the Reactor Head Bolting had occurred. Consequently, there was no safety impact due to the missed VT-3 inspections.
2951997014 | Zion 1, Zion 2 | 05/02/1997 | 05/30/1997 | 9706060121 | <strong>Missed Technical Specification Surveillances (TS) on Radiation Monitors because of interpretation of TS, with the minimal plant impact.</strong><br /><i>Abstract:&nbsp;</i>During a "Readiness for Restart" review of procedure ZRP 5820-12, "Out of Service Surveillance for Radiation Monitors." it was determined that Technical Specification (TS) 3.14 surveillance requirements for an inoperable radiation monitor 1(2)RT-PR15 had not been met. Seven radiation monitors provide noble gas inputs to 1(2)RT-PR15 that would be indicative of a reactor coolant system (RCS) leak. Inoperability of 1(2)RT-PR15 requires that "...a grab sample analysis at least once per shift" be performed. The surveillance, as implemented by procedure, non-conservatively required a grab sample selectively, such that grab samples would be taken only for certain input failures, instead of any input failure. <br /><br /> The root cause of this event was a technical interpretation that kept 1(2)RT-PR15 operable when its non-TS feeds were inoperable, rather than compliance to TS 3.14 as written. Corrective Actions are to revise station procedures to ensure TS compliance and to provide appropriate training on the procedure revisions. <br /><br /> 1(2)RT-PR15 has no automatic actuation, and is not associated with the control/quantification of plant effluents. The areas monitored by 1(2)RT-PR15 are monitored by other noble gas radiation monitors within the plant. consequently the safety significance was minimal. ZLER\971702.ler(1)
2951997015 | Zion 1, Zion 2 | 07/24/1997 | 03/04/1998 | 9803110147 | <strong>Unit 1 Emergency Diesel Generators and Unit 2 Residual Heat Removal System Inoperable and Inadvertent ESF Actuation While Performing Technical Specification Related Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 7/24/97 at 1709, while performing Technical Staff Surveillance (TSS) 3.8.1.10-1, "Loss of Offsite Power Testing of Diesel Generators During Refueling for Unit 1, "on the 1A emergency diesel generator (EDG) [EK], an individual inadvertently manipulated a test switch out of sequence. This resulted in an inadvertent actuation of various Engineered Safety Features (ESF) equipment. On 7/25/97 at 2359, the 0 EDG was declared inoperable when exceeding the critical date for the same TSS referenced above. At the time that the 0 EDG was declared inoperable, the 1B EDG was out of service for scheduled maintenance and the IA EDG was inoperable because of exceeding the critical date for the same TSS. Because all three Unit 1 EDGs were inoperable, all Unit 1 service water (SW)[BI] pumps and component cooling pumps (CC)[CC] were considered to be inoperable. With the 0 EDG inoperable, the 1A SW pump could not be considered operable. Therefore, the Units may not have been within their design basis requirements for single active failure of a SW pump or associated EDG. <br /><br /> The cause of the event is engineering management did not have clear expectations on completion of surveillance testing prior to the due date nor provided an adequate accountability system. The Nuclear Safety significance was minimal since the bus never de-energized and all equipment auto started as designed. Equipment, while administratively out of service, was still available. The 0 EDG was tested and declared operable on 07/26/97. The 1A EDG was tested and declared operable on 07/29/97.
2951997016 | Zion 1, Zion 2 | 08/15/1997 | 04/10/1998 | 9804160278 | <strong>Failure to recognize 125 VDC Buses Inoperable on August 15, 1997 due to DC cross-tie</strong><br /><i>Abstract:&nbsp;</i>On August 15, 1997, Station Battery DC bus 111 was being supplied from DC bus 211 through a cross-tie connection. Battery 111 was removed for discharge testing. When DC buses are cross-tied and a battery is removed (for testing), the associated DC buses are inoperable. Operations was not aware that DC buses 111 and 211 were inoperable. At approximately 12:15 pm on August 15, the DC System Engineer became aware that Bus 111 had not been declared inoperable. Operations was informed that DC bus 111 was inoperable and PIF Z1997-01241 was written. DC buses 111 and 211 were cross-tied on August 11. The buses had been inoperable since that time. <br /><br /> The root cause of the event is that System Engineering did not appropriately address operability in the revised battery test procedure and the system operating procedure. In addition, the Engineers did not verbally communicate the operability ramifications of the cross-tie calculation to Operations. Corrective actions include document revisions and training.
2951997017 | Zion 1, Zion 2 | 08/06/1997 | 04/10/1998 | 9804160297 | <strong>Missed Technical Specification Surveillance on Containment Isolation Valve Operability After Maintenance</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1997, while performing corrective actions #5 and #8 to LER 96-008, it was determined that five manually-operated Containment Isolation Valves (CIVs) did not meet Technical Specification (T.S.) 4.9.3.A.1. T.S.4.9.3.A.1 requires each CIV to be demonstrated operable prior to returning the valve to service after maintenance. At this time Zion Station Unit 2 was n cold shutdown at 0% power. Zion station Unit 1 was defueled. These five manually-operated valves were added to UFSAR Table 6.2-4 in July, 1993, identifying them as CIVs. The test used to stroke manually-operated CIVs is Periodic Test (PT)-306, Manual Containment Isolation Valves Cycle Test. PT-306 was not revised to include these valves when the UFSAR change was submitted. These valves were returned-to-service after maintenance without demonstrating operability. <br /><br /> An investigation was performed to determine the root cause of this event. Two LERs were written as a result of two similar events (LER 95-012 and 96-008). Those LERs along with other associated information were reviewed. It was determined that the procedure screening process that was used at the time the UFSAR update was made was inadequate. <br /><br /> The safety significance of this event was minimal. Containment isolation capability existed and manual isolation valves were capable of performing their intended isolation function.
2951997018 | Zion 1, Zion 2 | 08/06/1997 | 04/10/1998 | 9804160314 | <strong>Failure to recognize 125 vdc buses inoperable During unit cross-ties prior to September 1996 calculation.</strong><br /><i>Abstract:&nbsp;</i>Since original start-up Zion. has cross-tied 125 VDC buses to accommodate battery and charges testing and equalization charging without restricting loads on the bus. In 1996. detailed battery calculations were performed to model the cross-tie configurations. During cross-tying of buses. it was determined that a bus with d disconnected battery could not fulfill its design basis requirements. <br /><br /> The root cause was an inadequate Technical Specification review process. The Nuclear, Safety significance is dependent upon the plant configuration and equipment out-of-service at the time the cross-tie was used. A Safety analysis performed indicates that the risk imposed by cross-tying buses is minimal due to the station's three division design. Corrective actions include document revisions and training.
2951997019 | Zion 1, Zion 2 | 08/19/1997 | 09/18/1997 | 9709240292 | <strong>Failure to Test Safety Related Logic Circuits Required by Technical Specifications Due Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1997 while performing a review of plant surveillance test procedures in accordance with GL96-01, it was discovered that the logic testing for plant permissive P-10 did not provide sufficient logic combinations to independently verify each contact would operate properly when required. The condition is considered to be a failure to fully comply with the Surveillance Requirements of Technical Specifications (TS) as they relate to these specific logic functions. The safety significance of the specific examples reported in this LER is minimal. However, the overall significance is indeterminate since the GL 96-01 review has not yet been completed. <br /><br /> The affected procedures will be revised and the logic testing performed prior to unit restart.
2951997020 | Zion 1, Zion 2 | 09/08/1997 | 10/08/1997 | 9710100300 | <strong>Main Steam Instrument Cabling Routed Through Main Steam Tunnels In Contradiction To UFSAR.</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1997 a review of Safety Evaluation (97-472) and Appendix 3A of the UFSAR, "Analysis of the Effects of a Main Steam or Feedwater Pipe Break Outside the Containment" identified an apparent discrepancy between the as-built plant conditions and the assumptions made in the UFSAR analysis. UFSAR Appendix 3A states that all electrical cabling associated with the nuclear safety related (autoclose) operation of the Main Steam Isolation Valves (MSIVs) are routed outside the steam tunnel but, in fact, the cables for the main steam pressure transmitters are routed inside the tunnel. These transmitters initiate a close signal to the MSIV when high main steam flow exists. Low-low RCS temperature concurrent with high main steam flow will also close the MSIVs for this design basis steamline break outside containment. <br /><br /> The UFSAR is not clearly worded regarding which safety related cables may run through the main steam (MS) tunnel. Consequently there is an incomplete description of the assumptions used for the Zion Design Basis and for UFSAR Appendix 3A. The root cause investigation is continuing and further contributing causal factors and corrective actions will be included in the supplemental report which will follow this initial report. <br /><br /> Immediate actions were to review the as-built configuration against design basis events, supported functions and post accident monitoring. Preliminary results of this review show the ability of the MSIVs to autoclose after the Appendix 3A event is not compromised. But it is not conclusive regarding other safety related cabling in the area of concern.
2951997021 | Zion 1, Zion 2 | 09/19/1997 | 12/23/1997 | 9712300397 | <strong>Nuclear Instrumentation System Power Range Rate Trip Setpoints set outside of Technical Specifications due to incorrect interpretations</strong><br /><i>Abstract:&nbsp;</i>On 9/19/97, during an historical review of completed surveillances it was determined that a Nuclear Instrumentation System [JD] (NIS) Power Range Rate Trip Setpoint was left at a setting greater than the Technical Specification (TS) limit. On 7/2/92, the power range nuclear instrumentation procedures for Unit 1 were revised to incorporate the changes resulting from the installation of the Westinghouse Eagle 21 Reactor Protection System. On 2/1/93, similar changes were made to Unit 2 surveillances. The revision to the related procedures changed the setpoint tolerances from 5% to 5% plus 1% minis 0%. This change would allow an instrument technician to leave the setpoint for this instrumentation as high as 6%. The TS limit is 5%. During the period between 7/24/95 and 7/15/97, the discrepancy between the implementing procedures and the TS limit was identified as a potential discrepancy an 3 different occasions. However. because in each instance the TS were misinterpreted, this discrepancy was not dispositioned properly. The cause of this event is due to a misinterpretation of the "++" note in the TS Table 3.1-1. <br /><br /> Unit 2 related procedures were revised on 8/14/97. Unit 1 related procedures will be revised prior to refueling. <br /><br /> The NIS Positive/Negative Flux Rate Trip setpoint remained within all Zion Nuclear Steam Supply System (NSSS) setpoint evaluation and UFSAR assumptions, such that this event did not result in any adverse safety significance.
2951997022 | Zion 1, Zion 2 | 10/22/1997 | 08/28/1998 | 9809040093 | <strong>Non-Safety Heating System Affects Control Room Habitability</strong><br /><i>Abstract:&nbsp;</i>This supplemental LER documents that conditions originally reported have been determined not to constitute a reportable occurrence. <br /><br /> The station originally determined that a non-safety related heating system was necessary to keep the Control Room habitable during an accident. Also, an unacceptable Administrative Limiting Condition for Operation (LCO) had been inappropriately applied to ensure that the Control Room remains habitable following a combined Loss of Offsite Power and Loss of Coolant Accident (LOOP/LOCA). It was believed the potential existed for areas adjacent to the Control Room to affect adversely the ability of the Control Room ventilation system to maintain a positive pressure during these accidents. <br /><br /> Testing has since been performed to verify that the Control Room would remain habitable and, therefore, no condition existed which would have prevented the fulfillment of a safety function.
2951997023 | Zion 1, Zion 2 | 11/07/1990 | 12/10/1997 | 9712170198 | <strong>Auxiliary Building Ventilation Does not Conform to the UFSAR Due to an Analysis Deficiency</strong><br /><i>Abstract:&nbsp;</i>During review of the operator actions to align the Auxiliary Building Ventilation System during the transfer to cold leg recirculation phase of a LOCA, it was discovered that placing handswitch 0HS-AV95 in the "cubicle mode" does not also align the exhaust air flow from the pipe tunnels through charcoal filters. Because the Class I pipe tunnel and the Fuel Building exhaust air flow dampers react to the radiation monitors. there will be a time delay between the radiation detection in the pipe tunnel and damper repositioning to direct the air flow through the charcoal filters. This time delay will result in a "puff" of air unfiltered by charcoal to atmosphere. The radiation release described in the UFSAR for Control Room Habitability did not consider this unfiltered release. The off-site dose analysis for the general radiation release also did not consider this unfiltered release. The cause of the event is an original analysis error. The safety significance of this event is minimal with regard to the affect on Control Room Habitability and off-site dose release. <br /><br /> A modification is being performed to assume all required ventilation is filtered through charcoal when done so manually.
2951997024 | Zion 1, Zion 2 | 11/13/1997 | 12/12/1997 | 9712180056 | <strong>Missed Technical Specification Surveillance for Pressurizer Pressure Instrument Channel</strong><br /><i>Abstract:&nbsp;</i>Zion Technical Specification Table 4.4-1 for Engineered Safeguards [JE] require the performance of a quarterly channel functional test for the low pressurizer pressure actuation channel. Zion Technical Specifications define a channel functional test as "the injection of simulated signal(s) into the channel as close to the primary sensor(s) as practicable to verify operability, including all channel outputs, as appropriate." <br /><br /> On November 13, 1997, System Engineering performed a review of Westinghouse's Nuclear Safety Advisory Letter, NSAL-97-011, entitled 7-11 Surveillance Testing." The review revealed inadequate testing of pressurizer pressure channel as required by Zion Technical Specification Table 4.4-1. The circuit continuity between the output of Eagle 21 process protection system [JC] and the coil of logic relay for pressurizer pressure "B" bistable was never tested and resulted in a missed Technical Specification required surveillance. <br /><br /> The cause of this event was procedural inadequacy of the pressurizer pressure functional test. Corrective actions include revising the appropriate procedures, testing the pressurizer pressure "B" bistable prior to mode change, reviewing other procedures to ensure other Eagle 21 circuits are properly tested, and informing other Eagle 21 users about the situation.
2951997025 | Zion 1, Zion 2 | 11/24/1997 | 12/19/1997 | 9712310027 | <strong>Visual Inspection of Reactor Cavity Area Not Performed per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1997, during discussions about reactor cavity area inspections, it was determined that Technical Staff Surveillance (TSS) 15.6.21, "Visual Leak Examination of Class 1 Components (Reactor Coolant System Leak Test)" did not include the reactor cavity (Incore penetration) area to be inspected as required in Section XI, IWB-5220, from 1991 to present, due to the area being identified as an inaccessible area. It was subsequently determined that the reactor cavity area is accessible for a VT-2 inspection during Mode 3. <br /><br /> The cause of the event was that an inadequate review of the TSS 15.6.21 procedure was performed in 1991. The safety significance of not performing the VT-2 in the reactor cavity during start-up, following refueling outages since 1991, is considered minimal. <br /><br /> Corrective actions include revising TSS 15.6.21 to include a requirement to have future changes to the procedure include a Lead ISI Engineer review, to add VT-2 inspections of the reactor cavity area for both units and to perform the VT-2 inspection on Unit 1 and Unit 2 reactor cavity areas prior to unit restart.
2951997026 | Zion 1, Zion 2 | 12/09/1997 | 01/08/1998 | 9801130046 | <strong>Unit 1 1B Diesel Generator And 1C Service Water Pump Became Inoperable Due To A Missed ESF Load Shed Verification Surveillance As The Result Of A Scheduling Error And Caused A Technical Specification Violation On Unit 2.</strong><br /><i>Abstract:&nbsp;</i>On 12-09-97 at 1015, while performing a review of the Improved Technical Specifications (ITS), it was discovered that a missed surveillance on Unit 1 vital Bus 149/139 occurred, due to the failure to complete the surveillance testing identified in Performance Test PT-431, "480 V ESF BUS LOAD SHED RELAY TEST". Surveillance procedure PT-431 demonstrates the operability of load shed relays LSX and LSX1 on the electrical loads associated with vital 480 volt Bus 139. On 12-09-97 at 1016, the electrical loads on Bus 139 that had not previously had their load shed feature tested, were placed in the pull-to-lock position, and a 24-hour Limiting Condition of Operation was entered. The required test, PT-431, was completed and the 24-hour LCO was exited on 12-09-97 at 1729. This event also affected Unit 2. since the Service Water System is operated as a shared system for both units. This event placed the 1C Service Water pump in an inoperable condition and resulted in a Technical Specification violation regarding the number of cooling water sources available for decay heat removal in Unit 2. The Nuclear Safety significance associated with this event was minimal since the 1B EDG, if called upon to sequence loads during an automatic start, would have been able to carry the additional load. The cause of this event is improper specification of the modes of applicability for PT-431 during initial creation. Corrective actions include completion of PT-431, changing the modes of applicability for PT-431 in the electronic work control system to include modes 1, 2, 3, 4, 5, 6 & Defueled, and review of modes of applicability for surveillance requirements.
2961997001 | Browns Ferry 3 | 03/05/1997 | 04/04/1997 | 9704150185 | <strong>Loss of Offsite Power on Unit 3 During Refueling Outage Resulting From a Shorted Component</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1997, at 1040 hours Central Standard Time, (CST) Unit 3 received engineered safety feature system actuations due to a loss of offsite power. The loss of power was the result of the loss of both the Athens and Trinity 161 KV power lines. Emergency Diesel Generators 3A, 3C, and 3D automatically started and tied to their respective shutdown boards. At 1122 hours CST, BFN declared a Notification of Unusual Event (NUE) for Unit 3 due to a loss of offsite power greater than 15 minutes and notified NRC in accordance with 10 CFR 50.72(a)(3). At 1136 hours CST, following the restoration of the offsite power to Unit 3, BFN terminated the NUE, and in accordance with 10 CFR 50.72 (c)(1)(iii) notified NRC. The root cause of this event was the sensitivity of the auxiliary tripping relays. TVA has replaced the relays involved in the event with less sensitive relays. TVA is currently replacing other Westinghouse AR type relays in similar applications with less sensitive relays. This event is being reported accordance with 10 CFR 50.73 (a)(2)(iv), as any event or condition that resulted in manual or automatic actuation of any engineered safety feature including the reactor protection system.
2961997002 | Browns Ferry 3 | 04/10/1997 | 05/08/1997 | 9705190199 | <strong>Unit 3 HPCI system unexpectedly isolated resulting in an ESF by the actuation of the isolation logic. The cause of this event was personnel error.</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1997, Unit 3 and Unit 2 were operating at 100 percent power, and Unit 1 was shutdown and defueled. While performing a surveillance instruction for the functional testing of the Unit 3 HPCI steam supply low pressure switches, a volt-ohm meter (VOM) was inadvertently placed across a wrong pressure switch contacts. When the pressure switch under test actuated, the VOM completed a HPCI isolation logic circuit causing the actuation of the logic circuitry. As a result of this configuration, HPCI was declared inoperable since it could not perform its intended function. The cause of this event was personnel error as a result of mispositioning a volt-ohm meter lead due to a lack of self checking and second party verification. Corrective actions included personnel corrective actions and training of personnel involved to heighten their awareness of the consequences of this event. <br /><br /> This report is being submitted in accordance with 10 CFR 50.73 (a)(2)(iv) as an event or condition that resulted the automatic actuation of an Engineered Safety Feature. Additionally, this event is also reportable in accordance with 10 CFR 50.73(a)(2)(v) as an event or condition that alone could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident. Three previous LERs (259/95001, 296/95005, and 296/95004) on similar events were identified.
2961997003 | Browns Ferry 3 | 03/14/1997 | 04/09/1997 | 9704150127 | <strong>Main Steam Safety/Relief Valves Exceeded the Technical Specifications Required Setpoint Limit as a Result of Disc/Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1997, with Unit 3 in a refueling outage, Units 2 operating at 100 percent power, and Unit 1 shutdown and defueled, Wyle Laboratories notified TVA that 11 of the 13 Unit 3 main steam safety/relief valves (SRV) pilot cartridges failed setpoint tolerance bench tests. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's technical specifications (TS). <br /><br /> Testing by Wyle Laboratories discovered that the SRVs' as found setpoints were outside the TS setpoint tolerance of +/- 11 psi. The cause was attributed to corrosion bonding of the SRV pilot disc/seat interface resulting in drifting of the SRV setpoints. The Unit 3 SRVs were installed during the Unit 3, cycle 6 refueling outage. Setpoint drift is a generic concern experienced by utilities using Target Rock Two-Stage SRVs (Model No. 7567F) in boiling water reactors and is being investigated by the Boiling Water Reactors Owners Group (BWROG) SRV Drift Fix Development Committee and the manufacturer. TVA will continue to participate in the BWROG's evaluation of the long-term solution for the SRV setpoint drift problem. In addition, TVA will evaluate other possible solutions including use of pressure switch actuated SRVs.
2961997004 | Browns Ferry 3 | 04/14/1997 | 05/14/1997 | 9705210262 | <strong>Unplanned Manual Start of an Emergency Diesel Generator During a Scheduled Redundant Start Test</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1997, at 1142 hours Central Daylight Time (CDT), an unexpected Engineered Safety Feature actuation occurred when Emergency Diesel Generator (EDG) 3D was inadvertently manually started. During the scheduled performance of the Diesel Generator 3C Redundant Start Test, EDG 3D was manually started from the Unit 3 Main Control Room. EDG 3D was returned to the pre-event configuration by 1153 CDT. The root cause of the event was personnel error. During the performance of the redundant start test, the operator was requested to start EDG 3C; however, the individual started EDG 3D. The operator failed to properly utilize touch STA**2R (Stop, Think, Ask, Act, and Review) verification process during the test. Personnel corrective actions were administered to the individual. A briefing on the event was provided to appropriate plant personnel. The briefing package was reviewed with the shift crews. Personnel activities will be evaluated to ensure management expectations for use of touch STA**2R verification process are met. TVA is providing this report in accordance with 10 CFR 50.73 (a)(2)(iv), as any event or condition that resulted in manual or automatic actuation of any engineered safety feature, including the reactor protection system.
2961997005 | Browns Ferry 3 | 08/24/1997 | 10/03/1997 | 9710100204 | <strong>When a valve was malfunctioning, an LCO was not entered. The root cause for this event was that Operations crew lacked a questioning attitude and mindset. This LCO oversight is prohibited by technical specifications.</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1997, at 1945 hours, Units 2 and 3 were approximately 100 and 96 percent power, respectively. Unit 1 was defueled. At that time, a primary containment isolation valve failed to close. Although a relay in its circuit was replaced five (5) days earlier, the replacement did not resolve the valve problem. Specifically, during the performance of a surveillance instruction (SI) for testing the containment atmosphere dilution system valve operability, the primary containment isolation flow control valve failed to close. However, the limiting condition for operation (LCO) was not entered as required by the plant's technical specifications (TS). On September 5, 1997, after a review of these events, it was determined that an LCO should have been entered. The root cause for not entering an LCO was that the Operations crew lacked a questioning attitude. Senior Reactor Operators developed a mindset regarding the failure mechanism and did not full assess new information for the effect on technical specifications. The immediate corrective actions included replacement of the solenoid valve. Corrective actions to preclude recurrence include the counseling of the involved Senior Reactor Operators. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(i)(B) as any operation or condition prohibited by the plant's technical specifications. No previous LERs were identified where BFN personnel failed to enter an LCO.
2981997001 | Cooper Station | 01/30/1997 | 02/18/1997 | 9702260446 | <strong>Six Containment Penetrations Susceptible to Thermally Induced Overpressurization</strong><br /><i>Abstract:&nbsp;</i>While performing engineering evaluations in response to NRC Generic Letter 96-06, it was determined that six containment penetrations are susceptible to thermally induced overpressurization during certain design basis accidents. At 1340 hours on January 30, 1997, it was determined that this situation was reportable as a condition outside design basis. <br /><br /> The apparent cause for this condition is the failure to recognize and address the potential failure modes described in Generic Letter 96-06 during original plant design and construction (NUREG 1022, Appendix B, Cause Code B). An evaluation of the structural integrity of the bounding configuration demonstrates that continued operability is assured for all six penetrations. Evaluation of the six affected penetrations to quantify the impact and required corrective actions is continuing. Corrective actions planned or taken to resolve this issue will be communicated to the NRC in follow up response to Generic Letter 96-06.
2981997002 | Cooper Station | 04/09/1997 | 05/09/1997 | 9705150066 | <strong>Safety Relief Valves Found Outside Technical Specification Limiting Safety System Setting</strong><br /><i>Abstract:&nbsp;</i>While in cold shutdown for the current refueling outage (RE17), eight Safety Relief Valves (SRVs) were removed and sent to the Wyle testing facility in Banning, California for testing in accordance with CNS Technical Specifications (TS). In the period between April 9-13, 1997, all eight of the SRV lift pressures were found higher than the TS Limiting Safety System Settings tolerance of +/- 11 psi, (1%). <br /><br /> The cause of the SRV setpoint drift is attributed to corrosion bonding of the pilot disc to the pilot seat, (NUREG 1022, Appendix B, Cause Code B - Design, Manufacturing, Construction/Installation). CNS installed the Boiling Water Reactor Owners Group (BWROG) recommended Platinum-Stellite pilot disc in four SRVs during 1994. Test results for RE16 showed promising performance improvements after nine months of service. Performance data for the Platinum-Stellite disc has been extrapolated to indicate that the SRVs should remain within the Proposed CNS Improved Technical Specification (ITS) setpoint limits (+/- 3%) for an operating cycle of no more than ten and one half (10.5) months. CNS will continue to monitor industry efforts to resolve the corrosion bonding issue and implement appropriate maintenance and/or modification activities during a mid-cycle outage. ensures the valves will be in service for no longer than ten and one half (10.5) months. <br /><br /> In addition, three Safety Valves (SVs) were also tested at the same facility in accordance with CNS TS. In the period between April 9-11, 1997, two of the SV lift pressures were found to be lower, and the remaining SV lift pressure was found to be higher than TS Limiting Safety System Setting tolerance of +/- 13 psi, (1 %). <br /><br /> Failure of the Safety Valves to meet a +/- 1 % tolerance appears to be a result of the tolerance being too restrictive, (NUREG 1022, Appendix B, Cause Code B - Design, Manufacturing, Construction/installation). Past performance indicates that the repeatability of the lift pressure set spring is within the Proposed CNS ITS tolerance of +/- 3%. The SVs are considered to be functioning as de si gned. The only previous failure of a SV which experienced a setpoint drift above the +/- 13 psi (1 %) tolerance, was determined by the manufacturer to be indicative of normal valve performance.
2981997003 | Cooper Station | 04/23/1997 | 07/23/1997 | 9707310082 | <strong>Primary Containment Vent and Purge System; Simultaneous Opening of Inlet Purge and Outlet Exhaust Lines</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1997, during the review of Procedure 2.2.60, Revision 55, it was determined that this procedure provided steps that could lead licensed operators to open both the Drywell and Torus 24" inlet purge lines and outlet exhaust lines simultaneously, during a plant condition where reactor water temperature is above 212 degrees Fahrenheit (F) The issue was discovered during an internal Operating Experience Review of INPO Topics 6649, 6815, and 6855. During the processing of the Problem Identification Report (No. CAQ 97-0780), which documents the procedural concern, it was determined that the subject 24" inlet purge lines and outlet exhaust lines had been simultaneously opened on March 28 and March 29, 1997. <br /><br /> It was determined that during the shutdown for Refueling Outage 17 (RFO-17), both 24" inlet purge lines and both 24" outlet exhaust lines were left open simultaneously from 1641 to 2104 on March 28, 1997. On March 29, 1997, all four 24" lines were open again from 0436 until 1528. From March 28, 1997 at 1641 to the time which the average coolant temperature was reduced to below 212 degrees F (which occurred March 29, 1997 at 1828), both of the 24" inlet purge lines remained open. This resulted in a violation of Technical Specification (TS) 3.7.A.2.b until 1828 on March 29, 1997 (when the TS was no longer applicable). This condition was caused by a violation of Procedure 2.2.60, which resulted in a violation of TS 3.7.A.2.b. This TS allows only one 24" inlet purge line and one 24" outlet exhaust line be opened simultaneously when the reactor water temperature is above 212 degrees F. The cause classification for this condition is Personnel Error (NUREG 1022, Appendix B, Cause Code A). The results of the completed investigation associated with this event are consistent with the results provided in LER 97-003-00. <br /><br /> Corrective actions taken include the revision of CNS Procedure 2.2.60, the issuance of a Night Order to all Shift Licensed Operators discussing the meaning and limitations of TS 3.7.A.2.b, and the initiation of a Training Work Request to ensure that the full meaning and limitations of TS 3.7.A.2.b is addressed in Licensed Operator Initial and Requalification Training.
2981997004 | Cooper Station | 05/06/1997 | 07/14/1997 | 9707210039 | <strong>Reactor Trip Signal, ESF Actuation, and Loss of Shutdown Cooling During Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>At 2248 CDT on May 6, 1997, while in a cold shutdown condition for a refueling outage, a reactor vessel low water level signal was received while restoring instruments to service after backfilling a common reference leg for Reactor Vessel Water Level Instrumentation. The low level signal resulted in a full scram and Group 2 (Primary Containment), Group 3 (Reactor Water Cleanup), and Group 6 (Secondary Containment and Standby Gas Treatment) isolations. The Group 2 isolation resulted in a loss of Shutdown Cooling. At 0041 CDT on May 7, 1997, the reactor trip signal was reset, at 0109, the Group 2, 3 and 6 isolations were reset, and at 0144, Shutdown Cooling was restored after a rise in reactor water temperature from 104 to 123 degrees Fahrenheit. This corresponds to a rate of 6 degrees per hour. The estimated time to boiling at the beginning of the event was 17 hours. The water level at the time of the event was approximately 185 inches which is between the main steam lines and the vessel flange. <br /><br /> The erroneous low water level signal was the result of air being introduced into the instrument variable leg by the air loading on the floodup instrumentation. Corrective actions were taken to flush the instrument legs to remove the entrained air and restore the instruments to proper operation. During the flushing process a second low level scram signal was received at a time of 0051. The second scram signal during flushing operations was expected to occur. When the instruments were returned to service, shutdown cooling was restored. <br /><br /> The circumstances regarding this event have been discussed with Instrument and Control (I & C) personnel during a shop seminar in which the problems associated with this event were identified. The procedures governing this evolution have been revised to specifically alert the I & C technicians to avoid the situation encountered during this event.
2981997005 | Cooper Station | 05/07/1997 | 06/05/1997 | 9706100338 | <strong>Inadvertent Start of Diesel Generator 1 While Performing Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1997, with the Unit in the cold shutdown condition, Diesel Generator Number 1 started while the test set-up section for Surveillance Procedure 6.1DG.302, "Undervoltage Logic Functional, Load Shedding, and Sequential Loading Test (Division (Div.) 1)" was being performed. The action being carried out at the time of the inadvertent start of the Diesel Generator (DG) was the installation of a temporary jumper. The slow start of the DG was caused by inadvertent contact between two terminals. The Control Room Operators verified that there were no initiation signals present. Operators secured the Diesel Generator and verified that the logic functioned as expected. The critical bus which was energized by the startup transformer was not affected by the DG start. <br /><br /> Subsequent investigations revealed that the cause of this event was due to human factors deficiencies in the procedure. Although this procedure had been used successfully in the past, a different type of jumper which has larger jaws was being utilized. The larger jaw design requires greater care when installation is being performed in a congested area. A contributing cause of the event was the failure of the personnel performing the jumper installation to exercise the appropriate level of caution. <br /><br /> Activities have been initiated to evaluate the procedure and the associated Div. II procedure for improved human factors. In addition, a briefing has been performed with the electrical shop personnel dealing with this issue and the importance of performing maintenance correctly.
2981997006 | Cooper Station | 05/09/1997 | 06/09/1997 | 9706180485 | <strong>Failure to Perform ECCS Surveillance Within Required Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>On 5/9/97, while in a refueling outage, twenty-three (23) instrument surveillances supporting Emergency Core Cooling Systems (ECCS) were discovered to have exceeded their allowable Technical Specifications (TS) functional check requirement. Immediate actions were taken to complete the missed surveillances in support of ECCS operability. This situation occurred because of failure to identify ECCS instrumentation surveillance requirements during refueling operations. When routine surveillances are canceled during system inoperability, rescheduling is based on directly referring to TS for system operability requirements. This reliance on an individual's interpretation and comprehensive knowledge of TS is a programmatic weakness. Accordingly, this situation is designated Cause Code E, Management/Quality Assurance Deficiency (NUREG 1022, Appendix B). To prevent recurrence, a formally approved process will be developed to ensure surveillances are performed in support of all conditions of TS system operability.
2981997007 | Cooper Station | 06/14/1997 | 07/14/1997 | 9707210044 | <strong>Opening of a Torus to Drywell Vacuum Breaker</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1997, at 0918, while inerting the Primary Containment, one of the twelve Torus to Drywell Vacuum Breakers, PC-AOV-NRV25, opened. The Primary Containment was being inerted in accordance with the standard operating procedure. The Torus was being inerted first with the 24 inch purge inlet being used for purging and the 2 inch bypass around the outboard 24 inch vent valve, being used for venting. Due to the difference in the flow capacities of these paths, the Torus was slightly pressurized with respect to the Drywell thereby causing the vacuum breaker to come off its closed seat to relieve the pressure difference. <br /><br /> Once alerted to this condition, the control room operator lowered the nitrogen flow rate and the vacuum breaker fully reclosed at 0925 as the pressure difference between the Torus and the Drywell equalized. <br /><br /> Opening of a Torus to Drywell vacuum breaker is a possibility when the Primary Containment is being inerted, however, Procedure 2.2.60 which governs this evolution, did not contain either guidance appropriate to preclude this occurrence nor any note to alert the operator to the possibility. Thus, the cause of this event is procedural inadequacy. <br /><br /> Procedure 2.2.60 has been revised to provide the option of using the 24 inch vent valve for Containment inerting when using the Standby Gas Treatment (SGT) system. A note has been added to Procedure 2.2.60 to alert the operator to the possibility of a Torus to Drywell vacuum breaker opening during Containment inerting when using the SGT system. Procedure 2.2.60 will be evaluated to determine if the potential for challenging the Torus to Drywell vacuum breakers can be further reduced. <br /><br /> This event has minimal safety significance since the PC-AOV-NRV25 valve functioned as designed and the other Engineered Safety Features (ESF) systems remained capable of fulfilling their safety function.
2981997008 | Cooper Station | 06/14/1997 | 07/14/1997 | 9707180025 | <strong>Technical Specification 3.7.A.5.d Time Limit Exceeded</strong><br /><i>Abstract:&nbsp;</i>At 1950 on June 13, 1997, with plant power reduced to approximately 15%, CNS began to de-inert Primary Containment in preparation to make a Drywell entry to repair leaking feedwater vent valves. Technical Specification 3.7.A.5 Limiting Condition for Operation (LCO) was entered at 2129 when oxygen concentration exceeded 4% by volume. Technical Specifications require the oxygen concentration to be reduced to less that 4% by volume within a twenty-four hour period or the reactor must be in a cold shutdown condition. To avoid inducing a plant thermal transient and the potential challenge of plant safety systems associated with a plant shutdown, a decision was made to remain at approximately 15% power until oxygen concentration was reduced to less than 4%. A formal request for Enforcement Discretion was made by letter on June 14,1997. Oxygen concentration was reduced to less than 4% by volume and the LCO was exited at 2359 on June 14, 1997. <br /><br /> A decision to request Enforcement Discretion from the requirements of Technical Specification 3.7.A.5 was made in order to avoid inducing a plant thermal cycle and potential challenges to plant safety systems. A contributing factor in making the decision was to not place undue pressure on plant operators while performing this infrequent evolution. A contributing cause to the time required to re-inert was a procedural inadequacy which prohibited the rapid inerting of Containment from this plant condition. <br /><br /> There is a low safety significance associated with operation at reduced power levels when Oxygen concentrations exceed 4% by volume. This condition is bounded by both NUREG-1433, "Standard Technical Specifications, General Electric Plants, BWR/4," and the CNS Improved Technical Specifications (ITS) submittal dated March 27, 1997. <br /><br /> CNS has submitted ITS which eliminates the subject LCO. In addition, a revision to Operating Procedure 2.2.60 has been made to appropriately provide for utilizing a larger vent path to more rapidly inert Containment.
2981997009 | Cooper Station | 07/13/1997 | 10/03/1997 | 9710100218 | <strong>Inadvertent Reactor Protection System (RPS) Half Trip</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1997, at 1718 the Reactor Protection System (RPS) "A" Bus was lost due to a failure of Electrical Protection Assembly (EPA) 1A2. The loss of "A" RPS Bus caused an "A" RPS trip, "A" Groups 1, 2, 3, and 7 actuation and an "A" and 'B" Group 6 actuation. These group isolations resulted in various Primary Containment (PC) and Secondary Containment (SC) valves closing since the logic is configured such that certain PC and SC isolation valves will close on a half RPS actuation. This constituted an unplanned ESF actuation and was reported as a four hour non-emergency report. <br /><br /> The "A" RPS bus was transferred to an alternate power source and the equipment and systems, affected by the half trip, were restored to their normal configuration by 1800 on July 13, 1997, except for the Augmented Off Gas (AOG) system. The AOG remained secured for a reason unrelated to the loss of the "A" RPS Bus. The bus failure was determined to be caused by a defective card in the EPA. This equipment has been replaced, however, the "A" RPS bus remained powered from the alternate power source until July 29, 1997 when the transfer was accomplished. The defective card will be sent to General Electric for determination of the failure and repair.
2981997010 | Cooper Station | 07/13/1997 | 07/16/1998 | 9807290234 | <strong>Standby Gas Treatment Inoperability Due to a Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1997, at 1054, a design deficiency was discovered wherein during a Design Basis Accident (DBA) concurrent with a Loss Of Offsite Power (LOOP), the Standby Gas Treatment (SGT) system would not have been capable of fulfilling its function. This was discovered when a half group 2 isolation isolated the steam supply to the Augmented Off Gas (AOG) system (Ref. LER 97-009). Subsequent to this AOG isolation, about 5200 gallons of water were pumped from the Z sump. The Hi-Hi-Hi sump level alarm was not annunciated, indicating that the pump was able to maintain the water level in the sump within normal levels. <br /><br /> The safety function of the Z sump is to maintain the water level in the sump below the level where it could back into the SGT system discharge line and adversely affect SGT operation. Since the Hi-Hi-Hi sump level alarm is below the bottom of the SGT discharge lines operability of the SGT system was maintained throughout the event. Subsequent investigations revealed the design deficiency described above. Since the Z sump pumps are not required to be provided with essential onsite power until several hours after event initiation, the Z sump could have been sufficiently flooded to have prevented SGT operation. <br /><br /> On 7/16/97 at 1054, a one hour notification was made as a condition outside design basis. On 7/21/97 surveillance procedure 6.SUMP.101 was performed, with AOG in service, to demonstrate operability of the Z sump. This procedure injects demineralized water into the 48" holdup line drain line which would then flow to the sump to verify pump and level switch operation. Water was injected into the drain line for about 30 minutes (about 750 gallons) without any water entering the sump as evidenced by the fact that neither of the pumps started nor did the Hi-Hi-Hi level alarm annunciate. The AOG system was secured and subsequently about 1 000 gallons of water was pumped from the sump. A one hour notification was made as a condition outside design basis. On August 30, 1997, the AOG system was returned to service without affecting the operability of the SGT system.
2981997011 | Cooper Station | 07/29/1997 | 08/28/1997 | 9709040256 | <strong>Forced Shutdown Due to Inoperable Torus to Drywell Vacuum Breaker</strong><br /><i>Abstract:&nbsp;</i>At 0210 on July 29, 1997, during the performance of a monthly surveillance test positive closed indication for one of twelve Torus to Drywell vacuum breakers was not received. A follow up surveillance test was initiated to determine if the vacuum breaker was closed and Primary Containment was operable. This surveillance was unable to demonstrate the vacuum breaker was closed. At 0835, CNS declared Primary Containment inoperable and initiated plant shutdown in accordance with Technical Specification (TS) 1.0.J. <br /><br /> Initial inspection of the vacuum breakers indicated that all twelve of the vacuum breakers were in the closed position but four of the twelve vacuum breakers were leaking in areas where the seat gasket had been compressed by the gasket retaining ring. Investigation also noted that the testing method to establish the drywell to suppression chamber leakage during power operation differs from the testing method used when containment is not required. <br /><br /> There was a minimal safety significance associated with this event. If a small break Loss of Coolant Accident (LOCA) had occurred, the rapid increase in drywell pressure would have quickly overcome the minor seat leakage of the four vacuum breakers and fully seated the valves. The small break LOCA bounds the Design Basis Accident cases, therefore Primary Containment would have remained functional during all accident conditions. <br /><br /> The twelve vacuum breakers have been refurbished. The gasket retaining rings were straightened, gaskets replaced, and the pallets, closure magnets, and indicating micro switches were adjusted as necessary. The vacuum breakers were satisfactorily tested prior to returning the plant to service.
2981997012 | Cooper Station | 08/04/1997 | 09/08/1997 | 9709110173 | <strong>Suppression Pool Design Basis and Technical Specification Maximum Water Volume Exceeded</strong><br /><i>Abstract:&nbsp;</i>On 8/4/97 at approximately 0338, after completion of a quarterly High Pressure Coolant Injection (HPCI) surveillance, it was discovered that the suppression pool level had risen to nearly 3 inches above normal water level. This exceeded the Technical Specification (TS) 3.7.A.1.b maximum water volume of 91,100 cubic feet (i.e., 2 inches above normal water level). This TS limit is also a design basis limit. This situation occurred because of inadequate operations crew supervisory oversight. The suppression pool level was not adequately monitored and controlled to prevent the level from exceeding the TS and design basis limit. Contributing factors to this situation included: failure of an operator to perform the actions required by an annunciator response procedure; an inadequate HPCI surveillance procedure that did not provide preventive measures to ensure the suppression pool level did not exceed the TS limit; an inadequate annunciator response procedure that did not provide instructions to restore the level below the alarm point and preclude exceeding the TS limit; and Operations crew supervision's decision to proceed with the HPCI surveillance because it had been delayed twice in the shift. <br /><br /> Corrective actions taken were: 1) lowered the suppression pool volume to below the TS limit; 2) issued Operations Night Orders to ensure the suppression pool level is maintained below alarm levels and alarm response procedures are followed; 3) revised the HPCI surveillance procedures to ensure that the initial level is sufficiently low so that the final level does not exceed the alarm level; and 4) revised the suppression pool high level annunciator procedure to provide direction for restoring level to below the alarm point and to indicate the level corresponding to the TS volume limit. <br /><br /> In addition, Priority 1 and 2 alarm response procedures were reviewed for similar inadequacies and found to have adequate instructions. To prevent recurrence, a formally approved Crew Improvement Plan will be implemented and Operations crews will be trained in the lessons learned from this situation.
2981997013 | Cooper Station | 08/07/1996 | 10/30/1997 | 9711040224 | <strong>Plant Outside of Design Basis Due To Inadequate Scram Discharge Volume Modification</strong><br /><i>Abstract:&nbsp;</i>Station Design Change MDC 81-010-1, "Scram Discharge Volume Modification," installed a second Scram Discharge Instrument Volume (SDIV) and associated vent and drain piping in response to IEB 80-17, "Failure of Control Rods to Insert During a Scram at a BWR." This modification failed to meet the requirements of Safety Criterion 2 (Single Failure) of the "Generic Safety Evaluation Report, BWR Scram Discharge System" issued in December 1980. Cooper Nuclear Station (CNS) was in normal power operation at approximately 100 percent power in August 1996 when this condition was discovered. The cause of this event is unknown. An inadequate design review or a misinterpretation of evaluations performed to justify continued operation prior to implementation of the modification may have caused this condition. CNS implemented modification MP96-121, "SDIV Second Auto Isolation Drain and Vent Valves," in May of 1997 which brought the SDIV drain line isolation into compliance with the design requirements of the Generic Safety Evaluation Report for BWR Scram Discharge Systems.
2981997014 | Cooper Station | 11/08/1997 | 12/12/1997 | 9712230280 | <strong>Station Modification Creates Potential Inability to Mitigate Accident Consequences</strong><br /><i>Abstract:&nbsp;</i>On November 3, 1997, during activities to evaluate Reactor Equipment Cooling (REC) system integrity, three manual sample valves to the REC filter demineralizer skid located on a header which supplies cooling flow to non-critical loads, were determined to have a normally open position to permit continuous sampling of the REC system chemistry. The resultant REC system inventory loss of approximately 228 gallons per day, combined with the loss of non-essential make-up water, could have affected the ability of the REC system to meet its design basis function. This condition was determined to be reportable on November 8, 1997, <br /><br /> The cause of this event is attributed to a failure to fully understand the design basis functions of the REC system which resulted in an inadequate design review and 10CFR50.59 Safety Evaluation of the Design Change that installed the filter demineralizer skid. <br /><br /> Immediate action was taken to close the three sample valves.
2981997016 | Cooper Station | 12/10/1996 | 12/31/1997 | 9801060340 | <strong>Incorrect Technical Specification Interpretation of results in Diesel Generator Test not meeting Minimum Time Requirements</strong><br /><i>Abstract:&nbsp;</i>It was discovered on December 1, 1997, that a Cooper Nuclear Station Technical Specification (TS) Surveillance Requirement (SR) had not been appropriately implemented on December 10, 1996. TS SR 4.5.F.1.d requires the redundant operable diesel generator (DG) be demonstrated operable by a run time of greater than or equal to two hours following the declaration of an inoperable DG. On December 10, 1996, DG-1 was ran for a period of one hour and nine minutes. <br /><br /> Immediate corrective actions consisted of putting the applicable surveillance procedures on administrative hold to ensure that these procedures are not used inappropriately. These procedures were subsequently revised to be clear as to their applicability.
2981997017 | Cooper Station | 07/24/1996 | 12/31/1997 | 9801070013 | <strong>Inadequate Original Design Places Plant Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1997, a subsequent review of an issue identified in July 1996, was determined to be reportable as a condition that was outside the design basis of the plant. On July 24, 1996, during activities to close a Design Basis Open Item, the motors and operators for the Residual Heat Removal (RHR) system heat exchanger vent valves (RHR-MOT-MO166A/B and RHR-MO-MO166A/B) were identified as having a non-essential safety classification. In addition, it was determined that the inboard isolation valves (RHR-MOV-MO167A/B) were powered from the same source and there was not an automatic closure signal supplied to the valves from the Primary Containment Isolation System (PCIS). Therefore, these valves did not meet the applicable Primary Containment isolation requirements. <br /><br /> The apparent cause of this condition is attributed to an inadequate original design which failed to consider the Primary Containment isolation requirements and electrical separation requirements associated with these valves. A contributing factor was the decision, during the development of the Environmental Qualification program, to not include the components in the program. <br /><br /> The outboard valves were de-energized in the closed position in July 1996.
2981997018 | Cooper Station | 12/15/1997 | 01/08/1998 | 9801160018 | <strong>High Pressure Coolant Injection System Isolation During Surveillance Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>At 2116 hours on December 15, 1997, a High Pressure Coolant Injection (HPCI) system isolation (Group 4) occurred due to a personnel error. During routine surveillance testing of the HPCI Steam Line Space Temperature Switches, a non-licensed station operator placed the incorrect test switch in the test position. A Group 4 isolation occurred, isolating the HPCI system, on an invalid steam line space temperature signal. At the time of the isolation, the plant was at full power, steady state operation. <br /><br /> Immediate corrective actions were taken to verify the cause of the Group 4 isolation and to return the HPCI system to an operable status. During the subsequent investigation, it was determined that the event was caused by inadequate self checking on the part of the non-licensed station operator responsible for positioning the test switches. The station operator involved has been temporarily removed from watch standing duties pending development and approval of an individual corrective action plan by Operations management.
2981997019 | Cooper Station | 12/22/1997 | 01/21/1998 | 9802020039 | <strong>Incorrect Mind Set and Scheduling Process results in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1997, two reactor water sample valves, located in series, were opened on two occasions prohibited by Cooper Nuclear Station Technical Specifications (TS). These valves serve as primary containment isolation valves. The cause of this TS violation was a failure in the work scheduling process which led to an incorrect mind set of the Shift Supervisors. <br /><br /> Corrective actions include the development of TS case studies to be presented at SS meetings, and modification of the scheduling process to account for inoperable equipment.
3011997001 | Point Beach 2 | 01/07/1997 | 02/06/1997 | 9702110462 | <strong>Containment Liner Clearance Not In Accordance With Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On January 7, 1997, while Point Beach Nuclear Plant (PBNP) Unit 2 was shut down and defueled during its annual refueling outage, plant personnel identified one location where the clearance between internal Unit 2 containment structures and the containment liner was not in accordance with the plant design basis. 2, plant personnel noted that the Unit 2 'A' containment accident fan platform was in contact with the containment liner located opposite to an indicated void between the containment liner and concrete containment structure. This configuration could have resulted in a containment breach during a safe shutdown earthquake which is contrary to the plant design basis. The Unit 2 containment structure was immediately declared inoperable. Plant engineers walked down the remainder of the Unit 2 containment and documented eight additional locations of concern. The Unit 1 containment was also inspected, and although several areas of concern were identified, further evaluations determined the Unit 1 containment to be operable.
3011997002 | Point Beach 2 | 04/15/1997 | 05/14/1997 | 9705220451 | <strong>Potential Reactor Coolant System Branch Connection Stresses Beyond Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1997, with Unit 1 in cold shutdown and Unit 2 in a defueled condition, pipe stress calculations indicated that the Unit 2 Reactor Coolant System (RCS) Loop "B" RTD (resistance temperature detector) branch connection to the top of the RCS hot leg piping could be stressed in excess of the design basis code allowable limits. The calculated stresses did not exceed the interim operability limits described by the licensing basis; therefore, the piping is considered operable. Evaluation of similar piping in Unit 2 Loop "A" and in Unit 1 did not identify stresses in excess of code allowables. The potential stress problem was identified during an engineering consultant's programmatic review of Point Beach safety-related tubing. This calculated stress condition may have been inherent to the original design, but should have been identified and remedied when the configuration was analyzed in 1987. Those calculations applied RCS thermal/seismic anchor movements in the wrong direction, which provided non-conservative results. Support modifications are planned to restore the stresses to within their design basis limits.
3011997003 | Point Beach 2 | 06/22/1997 | 07/11/1997 | 9707150358 | <strong>Technical Specifications Violation: Reactor Vessel Head Installed Without An Operable Pressurizer Safety Valve</strong><br /><i>Abstract:&nbsp;</i>On June 22, 1997, with Unit 2 in refueling shutdown, during the tensioning of the studs for the reactor vessel head, it was recognized that the reactor vessel head was installed without an operable pressurizer safety valve. The pressurizer safety valves were not installed. The pressurizer safety valves had been previously removed during the Unit 2 refueling outage and had not yet been re-installed. This condition is a violation of Technical Specification 15.3.1.A.4.a which states, "At least one pressurizer safety valve shall be operable whenever the reactor head is on. The reactor vessel head was installed on June 19, 1997, at 2223 hours. At 1525 hours on June 23, 1997, pressurizer code safety valve, 2RC-434, was returned to service which established compliance with the requirements of Technical Specification 15.3.1.A.4.a. This event was caused by incorrect Technical Specifications. This Technical Specification violation did not diminish the safety of the public, plant personnel, or integrity of safety barriers in place at PBNP at any time.
3011997004 | Point Beach 2 | 07/29/1997 | 08/28/1997 | 9709040164 | <strong>Residual Heat Removal Loop Inoperable Due To Component Cooling Water Leak</strong><br /><i>Abstract:&nbsp;</i>At 1058 on July 29, 1997, while Point Beach Nuclear Plant, Unit 2, was in a refueling shutdown with reactor coolant system temperature at approximately 100 degrees F, a component cooling water (CCW) leak was identified on the Unit 2 CCW piping for residual heat removal (RHR) heat exchanger, 2HX-11D. Plant operators isolated CCW to 2HX-11B, and at 1110 declared the associated RHR loop inoperable. The decision to place the plant in this configuration resulted in a violation of Technical Specification 15.3.1.A.3.b which requires both RHR loops to be operable when reactor coolant system (RCS) temperature is less than 140 degrees F. The piping was subsequently repaired and the RHR loop was declared operable at 0930 on July 31, 1997.
3011997005 | Point Beach 2 | 08/06/1997 | 08/28/1997 | 9709040162 | <strong>Residual Heat Removal (RHR) Loop Inoperable Due To RHR Pump Seal Leak</strong><br /><i>Abstract:&nbsp;</i>On August 3, 1997, with Unit 2 in cold shutdown for refueling outage, plant personnel identified abnormal seal leakage from the Loop "A" residual heat removal pump (RHR), 2P-10A. At 0950 hours on August 6, 1997, the RHR pump was declared inoperable based on the excessive seal leak rate. The inoperability of the "A" RHR loop under these conditions was prohibited by the Technical Specifications because the reactor coolant system temperature was less than 140 degrees F. Technical Specification 15.3.1.A.3.b requires two RHR loops to be operable with reactor coolant system temperature less than 140 degrees F. At 1557 hours, Technical Specifications compliance was reestablished based on RCS temperature > 140 degrees F, both reactor coolant loops and steam generators operable, and the "B" RHR loop operable. By 1110 hours on August 10, 1997, all repairs and post-maintenance testing of the Loop "A" RHR pump were complete and the pump was declared operable.
3021997001 | Crystal River 3 | 01/28/1997 | 02/27/1997 | 9703040258 | <strong>Ineffective Change Management Results in Unrecognized NPSH Issue Affecting Emergency Feedwater Availability</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). Discussions with NRC inspection personnel identified that FPC had not explicitly reported a condition that existed prior to May, 1996 involving inadequate net positive suction head (NPSH) affecting one of the two Emergency Feedwater Pumps (EFP). On a loss of 'B' DC power, the turbine-driven pump's (EFP-2) flow control valves would remain fully open and EFP-2 would start in a maximum flow condition resulting in cavitation from inadequate NPSH which could lead to pump failure. In addition to an Emergency Diesel Generator load management concern, the postulated loss of 'B' DC power single failure coincident with a Small Break Loss of Coolant Accident and Loss of Offsite Power, a low probability event, could have resulted in two situations in which emergency feedwater may not have been available to perform its intended safety and accident mitigation functions. These include a design feature which trips the motor driven pump, EFP-1 at a Reactor Coolant System pressure of 500 pounds per square inch gauge, and a point in time at which EFP-1 would need to be secured in order to load the Low Pressure Injection pump onto the EDG in order to provide adequate NPSH to the High Pressure Injection pump. As a result, CR-3 was in an unanalyzed condition which could have rendered the emergency feedwater system incapable of fulfilling its intended safety and accident mitigation functions. <br /><br /> The cause of this event was ineffective configuration change management. Corrective Actions include a power upgrade of the 'A' EDG, EFW system modifications to eliminate NPSH concerns, and a failure modes and effects analysis.
3021997002 | Crystal River 3 | 01/29/1997 | 06/17/1997 | 9706270135 | <strong>Out-Of-Calibration Fuel Storage Pool Water Level Transmitters Invalidate Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC discovered the fuel storage pool (FSP) [DA] water level transmitters [LT] SF-1-LT1 and SF-1-LT2 were overdue for calibration and therefore, out-of-service. FPC determined this was a condition prohibited by Technical Specifications (TS). TS surveillance requirement (SR) 3.7.13, verification of the FSP water level during the time period of irradiated fuel movement, was performed using out-of-calibration transmitters, therefore, invalidating the FSP water level surveillance recordings. The causes for this event were determined to be a lack of commitment to, and management oversight of the Preventive Maintenance Program; weaknesses in the Preventive Maintenance (PM) Program; weakness in the corrective action program; and failure to formally train Operations personnel on changes to the PM Program. A measuring device was physically placed into the FSP to determine the FSP water level. The measuring device will be used to monitor the FSP water level until the level transmitters are declared operable and placed back into service. Procedures will be revised to enhance the PM program and to include verification of calibration for instruments required for TS surveillances.
3021997003 | Crystal River 3 | 01/31/1997 | 08/14/1997 | 9708190181 | <strong>Personnel Error Causes Testing Deficiencies Resulting in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC personnel were performing a comparison of schematic diagrams against plant surveillance procedures in response to Generic Letter (GL) 96-01, "Testing of Safety Related Logic Circuits." Testing deficiencies were identified to be violations of Technical Specification Surveillance Requirements. Separate deficiencies were identified on January 31, 1997, February 11, 1997, March 17, 1997, April 28, 1997, May 21 through 23, 1997, and June 3, 1997. FPC has completed the review as requested in GL 96-01. The testing deficiencies did not compromise the health and safety of the general public. The cause was cognitive human error based on personnel not fully identifying all components and contacts that should be tested. Corrective actions include procedure revisions, surveillance testing, and completion of the reviews requested by GL 96-01. Actions to Prevent Recurrence include revisions to administrative procedures and training. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) for operation or condition prohibited by the plant's Technical Specifications.
3021997004 | Crystal River 3 | 02/07/1997 | 07/25/1997 | 9707300107 | <strong>Thermal Relief Vales inside the Containment Do Not Meet the Requirements for Design Basis Accidents</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC performed a design review of the Nuclear Service Closed Cycle Cooling Water (SW) and Industrial Cooling Water (CI) systems in accordance with Generic Letter 96-06. Based on the review, FPC determined the selection of the thermal relief valves did not take into consideration the back pressure inside the reactor building (RB) during main steam line break (MSLB) and loss of coolant accident (LOCA) conditions. The engineering evaluation concluded that the containment integrity was not adversely affected due to the relief valves in the SW and CI systems. The conditions inside the RB during a MSLB and LOCA were not adequately considered during the selection of the thermal relief valves due to personnel error. No immediate corrective actions were necessary because CR-3 was in MODE 5. FPC will issue a Modification Approval Record (MAR) to replace the existing thermal relief valves and reinstall the inappropriately removed relief valves in the SW and CI systems inside the RB by November 20, 1997. Nuclear Engineering Procedure NEP-213, "Design Analysis Calculations," has been revised to include a requirement for a review of the design by the system engineer, plant operations, and other organizations, as applicable. No other LERs have been issued related to thermal relief valves in the SW and CI systems.
3021997005 | Crystal River 3 | 02/14/1997 | 03/17/1997 | 9703210110 | <strong>Unanalyzed Condition Regarding Small Break LOCA Mitigation Caused by Misunderstanding Reliance on Emergency Feedwater</strong><br /><i>Abstract:&nbsp;</i>Florida Power Corporation's Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) on February 14, 1997. A team studying Emergency Diesel Generator (EDG) capacity and Emergency Feedwater (EFW) system dependency issues discovered an unanalyzed condition involving a Small Break Loss of Coolant Accident (SBLOCA) in the reactor coolant cold leg discharge piping line coincident with a Loss of Offsite Power (LOOP) and single failure of the turbine-driven Emergency Feedwater Pump, EFP-2. CR-3 has two limitations related to EDG load margin concerns which trip the motor-driven emergency feedwater pump, EFP-1. EFP-1 is automatically tripped when the Reactor Coolant System (RCS) depressurizes to 500 pounds per square inch gauge (psig). Also, EFP-1 may be manually tripped when the Low Pressure Injection (LPI) pumps would need to be loaded onto the EDG in order to take suction from the Reactor Building Sump to provide adequate net positive suction head (NPSH) to the High Pressure Injection (HPI) pumps upon depletion of inventory from the normal source. For a certain range of small breaks, the RCS may repressurizes For an unisolable cold leg pump discharge line break or an isolable broken HPI line that may not be identified, if emergency feedwater is lost early in the transient, there may be inadequate HPI flow to the core, even with two HPI pumps operating. With a combination of insufficient HPI injection and no EFW, 10 CFR 50.46 requirements may not be met. The cause of this condition was a misunderstanding of the reliance on emergency feedwater for SBLOCA mitigation. Action will include an upgrade of the EDGs and development of accident mitigation strategies to ensure EFW remains available and operator guidance exists for HPI flow management with or without EFW.
3021997006 | Crystal River 3 | 02/19/1997 | 03/20/1997 | 9703260137 | <strong>Surveillance Testing Results in Reduction of Emergency Diesel Generator Rating Limit Due to Inadequate Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). At that time FPC performed an assessment of the surveillance procedures performed during the most recent refueling outage utilized to verify Emergency Diesel Generator (EDG) maximum load capacity. This review concluded that the tests, performed in April, 1996 may not have satisfied Improved Technical Specification Surveillance Requirement SR 3.8.1.11 and may also have subjected both EDGs to run time in the 30 minute rating (>3250 kW). The cause of this event was that the procedure did not account for instrument uncertainties in acceptance criteria. Corrective actions include evaluation of instrument uncertainties and procedure revisions.
3021997007 | Crystal River 3 | 03/06/1997 | 07/18/1997 | 9707230124 | <strong>Building Temperature Variations Larger Than Assumed Resulting In Unknown Instrument Uncertainties</strong><br /><i>Abstract:&nbsp;</i>On, March 6, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC made a four hour report to the NRC in accordance with 10 CFR 50.72(b)(2)(i), as being in an unanalyzed condition (Reference Event Number 31903). On February 13, 1997, FPC discovered the temperatures in the plant are not being maintained in accordance with the Environmental & Seismic Qualification Program Manual (ESQPM). On March 6, 1997, after an engineering evaluation, FPC declared CR-3 was in an unanalyzed condition because the instrument uncertainties were unknown due to inadequate temperature controls and may effect the setpoints for safety related instrumentation. If actual temperature variations were greater than those used in the development of these calculations, instrument calibrations and equipment performance could potentially be adversely impacted. A lack of commitment to configuration management resulted in controls and procedural guidance being insufficient to ensure ambient temperatures were maintained within the required temperature ranges in the buildings. Procedural guidance to ensure engineering requirements specified in the calculations and implementing procedures receive adequate review by implementing organizations, is scheduled to be completed by October 15, 1997. Nuclear Engineering Procedure NEP-213, was revised to require a review of the FSAR, Enhanced Design Basis Document and Improved Technical Specifications as part of the calculation approval.
3021997008 | Crystal River 3 | 03/07/1997 | 04/07/1997 | 9704160033 | <strong>Discovery of Original Design Configuration Resulting in Unanalyzed Condition Regarding High Pressure Injection Pump Recirculation Leading to Possible Pump Failure and Dose Consequences</strong><br /><i>Abstract:&nbsp;</i>On March 7, 1997, Crystal River Unit 3 (CR-3) was in COLD SHUTDOWN. A review was completed which determined that a condition previously identified in October, 1996 as a restart issue had not been adequately reviewed and evaluated for reportability. This resulted in the discovery that the plant had been in an unanalyzed condition during a Small Break Loss of Coolant Accident (SBLOCA) that could result in transfer of contaminated water from the Reactor Building sump to the Auxiliary Building via the Makeup Tank resulting in dose rate increases. In addition, another scenario could result in a failure to establish High Pressure Injection (HPI) pump recirculation which could lead to HPI pump failure. This condition was reported as a 4-hour report at 1748 hours in accordance with 10 CFR 50.72(b)(2)(i). <br /><br /> The scenario of concern occurs during certain SBLOCAs after regaining subcooling margin (SCM). The cause of the event was design error in that CR-3's original design did not adequately consider the full range of break sizes and did not address a very small break LOCA that would result in a requirement to throttle HPI to the point where minimum flow recirculation is required. CR-3 will remain shut down until this and other design margin deficiencies are resolved. A plant modification will ensure recirculation capability to the makeup pumps will be provided to assure adequate pump protection and prevent overflow of the makeup tank.
3021997009 | Crystal River 3 | 03/19/1997 | 06/27/1997 | 9707090144 | <strong>Inadequate Design Resulted in Reactor Coolant Pump Lubricating Oil Collection System Being Outside the Requirements of 10 CFR 50, Appendix R</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5, (COLD SHUTDOWN). As a result of a walkdown of the Reactor Coolant Pump [AB, P] (RCP) Motors [AB, MO] performed as part of the system readiness review, FPC identified several leakage sites in the RCP motor lubricating oil system that were outside the boundary of the oil collection system [LM] (LOC) and therefore, not in compliance with the requirements of 10CFR50, Appendix R, Section III.O. This condition is outside the design basis of the plant. The cause of potential leakage sites outside the LOC was an inadequate design of the LOC system due to programmatic deficiencies and lack of attention to detail. RCP motor lubricating oil system piping components located outside the oil collection system are a potential fire hazard associated with uncontained RCP motor lubricating oil. FPC performed a walkdown of five RCP motors (four installed and one in storage) to identify potential lubricating oil system leakage sites on the RCP motors that are outside the lube oil collection system. Potential leakage sites determined to be outside of the LOC system, for the installed RCP motors, will be in compliance with 10CFR50, Appendix R, Section 111.0 by November 26, 1997. There have been three previous reportable events involving the RCP motor LOC system at CR-3.
3021997010 | Crystal River 3 | 03/27/1997 | 05/20/1997 | 9705290298 | <strong>HVAC Was Not Considered For Manual Operation Of Safe-Shutdown Equipment In Post-Fire Conditions Resulting In Non-Compliance of 10CFR50, Appendix R</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1997 Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). A Precursor Card was generated by FPC questioning the habitability of areas in the plant that contain safe-shutdown equipment in post-fire conditions. On April 21, 1997, after the review of the CR-3 Appendix R Fire Study and the Fire Study supporting documents, FPC discovered that heating, ventilation, and air conditioning (HVAC) consideration in support of post-fire manual actuation of safe-shutdown equipment has not been specifically evaluated and documented in the Fire Study. This condition was evaluated by FPC on April 21, 1997, and was determined to be reportable pursuant to 10CFR50.73(a)(2)(ii)(B). The CR-3 Appendix R Fire Study did not take into account the loss of ventilation for the manual operation of post-fire safe shutdown equipment. FPC will perform calculations and/or revise the procedures necessary to manually operate equipment for post-fire safe shutdown for elevated temperature environment. The action plan identified in Problem Report PR 96-0401 will be annotated to identify the above condition, during the complete review of the post-fire shutdown analysis, as a corrective action step. PR 96-0401 will be utilized to evaluate and track concerns and initiate corrective actions for the CR-3 Appendix R program.
3021997011 | Crystal River 3 | 05/29/1997 | 06/27/1997 | 9707090085 | <strong>Potential design basis Condition from Pressure Locking of Emergency Feedwater Isolation Valves Caused by Insufficient Oversight/Review of Calculations</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1997, Florida Power Corporation's Crystal River Unit 3 was in MODE 5 (COLD SHUTDOWN). A reportability determination was made based on a condition previously discovered on March 15, 1997 during the system readiness review of the Emergency Feedwater System (EFW). A re-evaluation of EFW isolation valves EFV-32 and EFV-33 determined they are potentially susceptible to pressure locking during a very specific set of conditions in which a steam environment is caused by a pipe break and the valves cannot reopen after they close on a steam generator [AB,SG] overfill signal. If pressure locking did occur, EFW would not be able to provide a continuous emergency supply to the steam generators, possibly placing the plant in a condition outside its design basis. This condition was caused by an inadequate calculation prepared to assess the potential for occurrence of pressure locking and thermal binding (PLTB). The planned installation of cavitating venturis in the EFW pump discharge lines will reduce the maximum flow rate and increase the time to overfill the steam generators. EFV-32 and EFV-33 will be modified or replaced prior to plant restart. The PLTB calculation will be reviewed by October 26, 1997. The procedure for preparation of calculations has been revised to ensure system engineers and plant operations review assumptions and results.
3021997012 | Crystal River 3 | 05/31/1997 | 06/26/1997 | 9707030281 | <strong>Portions of Industrial Cooling System Not Designed to Applicable Code Resulting in Operation Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC engineering personnel were performing an assessment of containment integrity. During the review, FPC determined that a portion of the industrial cooling (CI) piping system, located within the reactor building (RB), failed to meet the Engineered Safeguards (ES) requirements applicable to a closed piping system. At the time the deficiency was identified, a reportability evaluation was conducted, which concluded that this deficiency comprised a condition outside the design basis of CR-3. Currently, there is minimal safety significance associated with the present condition, since with the plant in MODE 5, containment isolation valve operability is not required. The cause of this event was a design error by the engineering organization. Corrective actions include the upgrading of the associated piping, supports and coolers inside containment to meet safety classification and seismic requirements. Similar events were reported in LERs 88-016, 89-012, and 95-025.
3021997013 | Crystal River 3 | 05/30/1997 | 06/26/1997 | 9707030035 | <strong>Emergency Diesel Generator Room Could Exceed Maximum Design Temperature During Operation Due to Inadequate Room Cooling</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5, COLD SHUTDOWN. A reportability determination was made based on a condition previously discovered on February 1, 1997, during a functional test on the emergency diesel generators (EDG). FPC determined a potential exists for the EDG rooms to exceed the design basis temperature of 120 degrees F, when the outside air temperature is 95 degrees F, or greater. Exceeding the 120 degrees F temperature limit in the EDG rooms would result in CR-3 being in a condition outside the design basis. The 120 degrees F limit is to provide an acceptable environment for the electrical equipment in the EDG room. The electrical component temperatures were recorded and evaluated during the functional tests. FPC concluded the components will perform their required function in the increased temperature environment and the EDGs will perform their intended function. There is no impact to the general public health and safety. Inadequate EDG room cooling resulted in a potential to exceed the design basis temperature limits. FPC will improve cooling air flow to the EDG rooms during EDG operation to maintain the temperature at or below 120 degrees F by December 1, 1997.
3021997014 | Crystal River 3 | 06/11/1997 | 07/11/1997 | 9707180034 | <strong>Due To Engineering Design Errors, Reactors Building Penetrations Do Not Meet Applicable Codes Resulting In A Condition Outside The Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) when the evaluation of a suspected design basis issue concluded that the issue represented a condition outside FPC's design basis. FPC personnel were performing a review of reactor building penetrations as a corrective action to resolve penetration surveillance concerns documented in LER 50-302/96-018-01. During the review, FPC determined that a portion of the Reactor Building Pressure Sensing & Testing, Spent Fuel Cooling, and Nitrogen, Hydrogen & Carbon Dioxide Systems may not be adequately designed and/or tested to ensure post accident reactor building integrity. A subsequent evaluation of the suspected design basis issues concluded that the deficiencies constituted conditions outside the design basis for CR-3. Currently, there is minimal safety significance since containment isolation valve operability is not required in MODE 5. The cause of this event was a design error by the engineering organization during plant construction. Corrective actions include a review of other reactor building penetrations for similar conditions and the implementation of appropriate actions (modifications, analyses, and/or testing) to ensure that reactor building penetrations meet the design bases for CR-3. Similar events were reported in LER 50-302/96-018-01 and LER 50-302/97-012-00.
3021997015 | Crystal River 3 | 06/12/1997 | 09/18/1997 | 9709220137 | <strong>Non-Conservative Differential Pressure Rating For Letdown Line Inboard Containment Isolation Valves Prohibiting Safety Function Performance</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During a review of the differential pressure calculation for the Letdown Line [CB] Inboard Containment Isolation Valves, FPC discovered that the evaluation of the maximum differential pressure (dP) that these valves could be subject to is in error. These valves are rated to close against a maximum dP of 1800 pounds per square inch (psi), but could be subjected to a dP in excess of 2000 psi in the event of a letdown line rupture downstream of outboard containment isolation valve (MUV-49), concurrent with a failure of MUV-49 to close and operator action in accordance with Emergency Operating Procedure (EOP) 3. Upon further evaluation, on August 19, 1997, FPC discovered that outboard containment isolation valve MUV-49 would not be capable of closing if subjected to 2000 psi dP. Isolation at Penetration 333 requires either MUV-49 or MUV-40/41/505 to close. The cause of this event was the use of inappropriate assumptions in the calculation for the determination of maximum valve dP. In accordance with 10 CFR 50.72(b)(2)(i), a Four Hour Non-Emergency Notification was made on this issue (Event # 32472). A Modification Approval Record (MAR) is being developed to install a new inboard containment isolation valve prior to restart of CR-3. In addition, the air operator on MUV-49 will be modified to allow closure against the predicted dP.
3021997016 | Crystal River 3 | 06/13/1997 | 07/11/1997 | 9707170158 | <strong>Due To Engineering Error, Omissions In Reactor Building Coating Calculations Result in CR-3 Being In An Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) when the evaluation of a suspected design basis issue concluded that CR-3 was in an unanalyzed condition. Specifically, FPC engineering personnel had questioned the coating used on Core Flood Tanks CFT-1A and CFT-1B. The existing coatings were not approved for use in the reactor building. Additionally, the coatings were not identified in the calculations addressing reactor building coating failures. Personnel resolving the coatings issue subsequently identified three open south "D" wall penetrations which provided open debris transport paths that were not accounted for in the reactor building coating failure calculations. The latter condition was the subject of a four-hour notification to the NRC on June 19, 1997. Currently, there is minimal safety significance since Emergency Core Cooling System train (Reactor Building Emergency Sumps) operability is not required in MODE 5. The cause of this event was cognitive engineering error during the development and review of engineering calculations that evaluate reactor building coating failures. Corrective actions include correcting the specific deficiencies and performing reviews to ensure that coatings are qualified and open debris transport paths have been identified inside the reactor building. No similar events have been reported.
3021997017 | Crystal River 3 | 06/21/1997 | 07/21/1997 | 9707280273 | <strong>Personnel Error Caused Inadequate Electrical Separation of the High Pressure Flow Indicators</strong><br /><i>Abstract:&nbsp;</i>On June 21, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). On May 1, 1997, while performing a modification in the main control board, FPC personnel noticed that electrical separation material previously installed was different than that being currently installed. On June 21, 1997, FPC concluded the material previously installed (Nextel) was incorrect. The material was used to sleeve cables for electrical separation during the installation of a modification to the HPI Flow Indicators. The modification to the HPI flow indicators was performed during the tenth refueling outage (11 OR), spring 1996. Electrical separation ensures a failure in one cable will not disable other related trains or systems. The HPI flow indicators assist the reactor operators in isolating a faulted HPI line during certain design basis accidents. Personnel error during the installation resulted in the incorrect material being used for electrical separation. A walkdown of other areas is scheduled to be completed by September 15, 1997, to identify areas where Nextel may have been used. <br /><br /> Two other LERs were issued by FPC concerning electrical separation.
3021997018 | Crystal River 3 | 07/02/1997 | 07/26/1997 | 9708010241 | <strong>A High Energy Line Break In The Intermediate Building Could Result In Loss of Chilled Water To The Control Complex Ventilation System Due To Design Error</strong><br /><i>Abstract:&nbsp;</i>At 1949, on July 2, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) when an issue was determined to be reportable under 10CFR50.72(b)(2)(i) (Event No. 32580) and 10CFR50.73(a)(2)(ii)(A). In 1990, FPC became aware of the potential for losing both control complex chillers following a high energy line break (HELB) in the Intermediate Building (IB). FPC implemented a Modification Approval Record (MAR) installing a manual valve for isolating the Chilled Water System from the IB. The 10CFR50.59 evaluation for the MAR considered failure of the operating chiller and a single active failure being the standby chiller. The evaluation inappropriately took credit for the nonsafety-related Appendix R chiller and a temporary chiller for concluding that an unreviewed safety question did not exist. Prior NRC approval was not requested. The cause for the initial condition was design error during construction. The cause for the current condition was an inadequate 10CFR50.59 evaluation. A loss of control complex cooling could affect the control complex habitability envelope and allow temperatures in vital areas to exceed limits for ensuring continued operation of electrical equipment. Currently, minimal safety significance is associated with the existing condition. A HELB is not credible in MODE 5. Corrective actions include re-evaluating a HELB in the Intermediate Building, continuing the System Readiness Review program, and the recent 10CFR50.59 program enhancements.
3021997019 | Crystal River 3 | 07/03/1997 | 12/18/1997 | 9712230275 | <strong>Elevated EDG Supply Air Temperatures Due to EDG Radiator Discharge Air Recirculation Effect</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). As part of the effort to support the power upgrade modifications of the Emergency Diesel Generators (EDG), testing of EDG-1A identified elevated EDG radiator, control and engine room air temperatures. This increase is due to a portion of the radiator discharge air released to atmosphere from the roof of each EDG building being recirculated back into the EDG radiator room. The recirculated air can cause the supply air to the EDG rooms to be increased 10 to 15 degrees Fahrenheit (F), depending on wind conditions, above the design basis outside air temperature of 95 degrees F. Analysis of EDG capability at these temperatures identified that EDG-1A&B are in a degraded condition. A reportability determination was made on July 3, 1997, and in accordance with 10 CFR 50.72(b)(2)(i) and (b)(2)(iii)(D), a Four Hour Non-Emergency Notification was made regarding this issue (Event Number 32589). Failure to identify this effect was due to a design oversight during initial plant design. A modification to reduce the recirculation of the radiator discharge air is being developed. Implementation and testing will be completed by February 28, 1998. Previous Licensee Event Report (LER) 97-013, dated June 26, 1997 identified a potential for temperatures in the EDG engine rooms to exceed their design basis temperature of 120 degrees F when outside air temperature was 95 degrees F or greater. The results of LER 97-013 are affected by this current LER.
3021997020 | Crystal River 3 | 07/18/1997 | 08/18/1997 | 9708220282 | <strong>Misinterpretation Leads To Noncompliance With Technical Specification Criteria Involving Past In-Place Filter Testing</strong><br /><i>Abstract:&nbsp;</i>On July 18, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) when FPC identified a condition reportable under 10CFR50.73(a)(2)(i)(B). LER 50-302/96- 016-00 identified the failure of the Control Room Emergency Ventilation System (CREVS) in-place testing of the high efficiency particulate air (HEPA) filters and charcoal adsorber bank filters to meet Improved Technical Specification (ITS) surveillance requirement acceptance criteria. An extent of condition review for that LER revealed that in-place testing of the HEPA filters and charcoal adsorber bank filters for the Reactor Building Purge, Auxiliary Building Ventilation Exhaust System and CREVS did not meet pre-ITS acceptance criteria. The cause for this condition was cognitive personnel error. To resolve the identified concerns, the Ventilation Filter Test Program will be revised to specify the correct in-place surveillance requirement acceptance criteria for the Reactor Building Purge and Auxiliary Building Ventilation Exhaust System HEPA filters and charcoal adsorber bank filters.
3021997021 | Crystal River 3 | 07/21/1997 | 11/04/1997 | 9711060015 | <strong>Loss Of "A" Battery Leads To The Inability To Bypass ES Actuation Signals As A Result Of Inadequate System Knowledge</strong><br /><i>Abstract:&nbsp;</i>This LER is being supplemented to revise the corrective actions. On July 21, 1997 Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During the Class 1E Electrical Direct Current (DC) Failure Modes and Effects Analysis (FMEA) review, FPC identified that during a loss of offsite power (LOOP) coincident with loss of the train "A" 250 volt (V) battery prior to starting the Emergency Diesel Generator (EGDG) 1A, the ability to bypass the "B" Engineering Safeguards (ES) train actuation signals is lost. A four hour report was made to the NRC pursuant to 10CFR50.72(b)(2)(i) (Event Number 32659). When the "A" battery is inoperable and EGDG-1A does not start, train "A" ES components do not operate. During a LOOP event, coincident with the loss of "A" 250V battery and EGDG-1A, power to the "A" and "C" inverters is lost (Vital Bus "A" and "C"). Loss of the train "A" 250V battery will also prevent ES analog channel 1 and channel 2 Trip Bistables from being bypassed after actuation. Therefore, ES actuation signals for train "B" components remain actuated. The apparent cause is an inadequate FMEA for the original plant design. This cause resulted in inadequate procedures and training on event recovery. FPC will install a new relay with contacts in parallel to the existing bypass permissive bistable contacts and the bypass permissive indication light contacts for "B" train, channel 1, HPI and LPI.
3021997022 | Crystal River 3 | 07/21/1997 | 08/27/1997 | 9709040062 | <strong>Calculation Errors Associated With Control Complex Habitability Envelope Unfiltered Air Inleakage Could Allow Operator Dose Limits To Be Exceeded</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) when the cumulative effect of several recently discovered deficiencies was determined to be reportable under 10CFR50.73(a)(2)(ii)(B). Design deficiencies associated with past modifications to the Control Complex Habitability Envelope (CCHE) and Control Room Emergency Ventilation System (CREVS) could have the combined effect of allowing post-accident doses to Control Room operators to exceed allowable limits. Minimal effect exists for the current condition. CREVS is only required to be operable in MODES 1-4 and during irradiated fuel movement. Deficiencies were caused by design engineering process weaknesses. Current engineering processes contain adequate guidance to prevent recurrence. Improved Technical Specification (ITS) 5.6.2.12.c CREVS charcoal adsorber laboratory test requirements for humidity will be amended or a calculation will be performed to support the 70% humidity test requirement. New calculations for Control Room operator dose and design of CREVS will be developed. Physical modifications and testing will be implemented. Similar events were reported in LERs 50-302/96-016-00 and 50-302/97-020-00.
3021997023 | Crystal River 3 | 07/30/1997 | 08/25/1997 | 9709020269 | <strong>Design Engineering Process Allows Installation Of Vital Bus Inverters Containing An Unanalyzed Trip Circuit</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) when a design basis deviation was determined to be reportable under 10CFR50.72(b)(2)(i) and 10CFR50.73(a)(2)(ii)(A). At 1015, on July 30, 1997, FPC completed the four-hour notification (Event No. 32699) required by 10CFR50.72.(b)(2)(i). FPC personnel discovered a trip coil in the control circuitry for vital bus inverters VBIT-1A/1C direct current (DC) input breakers that was not analyzed when their replacement was implemented during Refueling Outage 10. The batteries, in combination with the inverters, are designed to provide an uninterruptible source of power to support the Station Blackout requirement for CR-3. The inverter DC input breaker low voltage trip circuit could interrupt this source of power prematurely. The cause for this condition was a weakness in the engineering process for component procurement. The inverter design will be reviewed. The inverters will be modified, as appropriate. Nuclear Engineering Procedures will be revised to provide guidance for ensuring correct design requirements are reflected in component procurement documents. No similar LERs were identified.
3021997024 | Crystal River 3 | 07/31/1997 | 08/27/1997 | 9709040039 | <strong>Feedwater Valves Do Not Meet The Requirements For Main Steam Line Or Feedwater Line Break Event Mitigation Due To Inadequate Design and Calculation Errors</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). On June 13, 1997, while performing the System Readiness Review (SRR) for the Feedwater System (FW), FPC identified a condition whereby the differential pressure (dP) across feedwater suction valves FWV-14/15 could prevent the valves from closing in response to a signal from the Emergency Feedwater Initiation and Control System (EFIC)[JB]. Upon completion of an evaluation on July 31, 1997, FPC determined this was a condition outside of the design basis. A Steam Line Break (SLB) or Feedwater Line Break (FWLB) is not a credible event while in MODE 5, therefore no immediate actions are necessary. These deficiencies were caused by inadequate design and calculation errors. The reanalysis of the Final Safety Analysis Report (FSAR) Chapter 14 SLB will be completed by September 30, 1997. A modification to upgrade the actuators on feedwater suction valves FWV-14 and FWV-1 5 is scheduled to be completed by November 20, 1997. The Final Safety Analysis Report (FSAR) will be updated by November 30, 1997 to reflect the new analysis, which will include conservative assumptions for Moderator Temperature Coefficient (MTC), High Pressure Injection (HPI) and slower closure times for low load block valves FWV-31 and FWV-32. These corrective actions are included in the FPC Restart Plan. Incorrect design assumptions have been identified and described in LERs 50-302/97-015-00, 89-033, 89-013, and 87-007.
3021997025 | Crystal River 3 | 08/12/1997 | 12/22/1998 | 9812300223 | <strong>Non-conservative Assumptions Resulted in the Service Water Temperature Being Outside of the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC determined the analysis supporting the increase of the ultimate heat sink (UHS) design basis temperature from 85 degrees Fahrenheit (F) to 95 degrees F contained non- conservative assumptions which could have resulted in the Nuclear Services Closed Cycle Cooling (SW) system exceeding its peak design basis temperature of 110 degrees F. FPC implemented a modification to limit the start of the Reactor Building Cooling Units to one on an Engineered Safeguards Actuation Signal to reduce the amount of heat rejected to the SW system following a Loss Of Coolant Accident. This modification ensured that the SW system was within the design basis with a maximum UHS temperature of 95 degrees F. <br /><br /> The cause of the non-conservative assumptions was personnel error. Improvements to the processes that govern design calculations have been implemented. FPC previously reported two other events regarding incorrect design assumptions in the SW system.
3021997026 | Crystal River 3 | 08/14/1997 | 09/13/1997 | 9709160229 | <strong>Failure to Perform a Field Validation Resulted in a Deviation to 10CFR50 Appendix R Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). As part of the corrective action to LER 50-302/96-001-00, "10CFR50 Appendix R Fire Study Review and Drawing Validation," which is on ongoing, FPC discovered a conduit containing control circuitry for components necessary for safe shutdown not protected from the effects of a design basis fire. Air Handling Fan AHF-54B is used to supply cooling to the Emergency Feedwater Initiation and Control (EFIC) room for safe shutdown operation. A design basis fire could fail control power resulting in a loss of chilled water to AHF-54B and cause a loss of cooling for the EFIC Rooms. The apparent cause of the failure to protect the control power conduit with a one hour fire barrier was inadequate incorporation of the Appendix R Fire Study requirements into the Modification Approval Record (MAR) creation process. FPC will either reroute the affected conductors for the above control circuits to eliminate this condition or protect the conduit with an acceptable one hour fire barrier by December 15, 1997.
3021997027 | Crystal River 3 | 07/07/1997 | 10/03/1997 | 9710080253 | <strong>Failure To Add Antifreeze To The Diesel Generator Coolant Radiators May Render Emergency Diesel Generator Inoperable During Sub-Freezing Temperatures</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While performing a review of the Emergency Diesel Generators (EGDG) [EK] upgrade modification, FPC engineering personnel discovered antifreeze was not used in the Diesel Generator Coolant (DJ) [LB] System to prevent freezing when the ambient temperature is below 35 degrees Fahrenheit (F). FPC submitted a 10CFR50.72 report on July 7, 1997 (Event Number 32596). On August 29, 1997, FPC personnel discovered that a written report had not been submitted to the NRC within 30 days of discovery as required by 10CFR50.73. Isolated freezing of the radiator coolant in the radiator could cause a rupture of the radiator coil and loss of coolant. Also, freezing within the radiator core could result in reduced flow due to the blockage thereby causing the coolant pumps to be dead headed. The cause of the event was cognitive personnel error. FPC is replacing the radiators for EGDG-1A and 1B and will add antifreeze to the DJ system by November 30, 1997 to eliminate the potential for freezing. FPC has reported one other LER regarding failure to pursue vendor recommendations, 50-302/90-002-01.
3021997028 | Crystal River 3 | 09/02/1997 | 10/02/1997 | 9710060266 | <strong>Flow Element Accuracy Uncertainty May be Greater Than Assumed Due to a Design Error</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During an extent of condition review for a previously identified concern regarding the Nuclear Services and Decay Heat Seawater (RW) system flow elements, FPC discovered that the flow elements [FI] in the Nuclear Services Closed Cycle Cooling Water (SW) [CC] and Decay Heat Closed Cycle Cooling (DC) [CC] Systems were not installed as recommended by the manufacturer. Based on their current configuration, the accuracy of the flow elements is uncertain because the flow elements have not been tested in their present configuration. The flow measurement error is considered in system hydraulic calculations which establish IST surveillance acceptance criteria for pumps and valves. If accuracy uncertainty is greater than assumed, the surveillance acceptance criteria cannot be established. Therefore, performance data cannot be compared with design margin limits to show that the SW and DC pumps have satisfied the intent of the surveillance test. Straight pipe run lengths were not considered during the initial installation of the flow elements due to an oversight by the design engineers. FPC will test the existing flow elements in a similar configuration to determine their accuracy by October 31, 1997. If test results are unfavorable, FPC will replace or relocate the existing flow elements by November 30, 1997.
3021997029 | Crystal River 3 | 09/17/1997 | 10/14/1997 | 9710200018 | <strong>Failure to Perform a Field Validation Resulted in a Deviation of 10CFR50 Appendix R Requirements</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During the ongoing 10CFR50 Appendix R Fire Study Review and Drawing Validation as part of the corrective action and extent of condition review for LER 50-302/96001-00, FPC discovered cables used to select the power source for a motor control cabinet (MCC) [MCC] were not protected from the effects of a postulated Appendix R fire. A postulated Appendix R fire in Fire Area CC-124-111 could result in a loss of power to Pressurizer Relief Isolation Valve RCV-11 and Makeup Gear Oil pump MUP-4B, while a fire in Fire Area CC-134-118A could result in the loss of power to Makeup Valve MUV-27 and MUP-4B. Each of these components have been identified in the CR-3 Fire Study as necessary for safe shutdown. A field validation of the Appendix R Fire Study was not performed, resulting in a failure to ensure components necessary for safe shutdown were protected from the effects of a postulated Appendix R fire. FPC will protect the affected circuits to preclude the loss of MCC-3AB in Fire Areas CC-124-111 and CC-134-118A by December 15, 1997. Also, the Appendix R design drawings and Fire Study will be revised to reflect the modified field condition by March 31, 1998.
3021997030 | Crystal River 3 | 09/23/1997 | 10/21/1997 | 9710240162 | <strong>Installation Error Results In a Containment Isolation Check Valve Disk Sticking in the Open Postion</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While performing a scheduled ASME Section XI internal inspection of feedwater valve FWV-46, FPC personnel discovered the check valve disc stuck in the open position. This condition was caused by missing hinge and retaining pins on one side of the check valve disc. FWV-46 is a containment isolation valve and is designed to close when feedwater flow is not being supplied to Reactor Coolant Steam Generator (RCSG) 1B. Loss of containment isolation valve function during operation is considered to be reportable under 10CFR50.73(a)(2)(ii). This condition could contribute to post-accident offsite dose consequences during a Steam Generator Tube Rupture accident. The cause for this condition was cognitive personnel error. In 1989, a tack weld was not correctly placed to prevent one of the retaining pins from backing out of its position. Containment isolation valves are not required to be operable in MODE 5. No immediate actions were required. FPC has located and retrieved the missing hinge and retainer pins. FWV-46 will be repaired. Safety related Crane tilting disc check valves requiring the same retainer pin tack welding will be inspected and repaired, if necessary. Maintenance Procedure MP-120 will be revised. Two previous similar LERs have been identified.
3021997031 | Crystal River 3 | 09/26/1997 | 01/15/1998 | 9801200151 | <strong>Inadequate Cable Sizing Due to Nonconservative De-rating Factors Could Reduce the Cable Remaining Qualified Life</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While performing a review of the preliminary electrical cable operability evaluation, FPC discovered three cable trays where the cables may have experienced temperatures in excess of the cable insulation temperature rating. Also, on October 9, 1997, FPC found the cables for the Reactor Building Cooler Air Handling Fans AHF-1A, 1B, and 1C were inadequately sized for the current load during operation of the fans. The cable sizing was based on de-rating factors and anticipated electrical current loads. Based on the results of the evaluation, FPC determined this is a condition outside of the design basis of CR-3. This report is being submitted pursuant to 10CFR50.73(a)(iii)(B). The preliminary result of the testing indicates that there is no measurable degradation in the cables previously identified. A nonconservative de-rating factor for TSI Thermo-Lag was used to determine cable ampacity sizing. Based on the results of the testing and evaluation, FPC concluded that the cables identified in this LER will not exceed the remaining qualified life through the next refueling outage and will not exceed the cable insulation temperature rating. Conservative cable ampacity correction factors have been included in the cable selection criteria for CR-3, "Cable Ampacity Sizing," Revision 2.
3021997032 | Crystal River 3 | 04/06/1997 | 11/05/1997 | 9711070032 | <strong>Inadequate Electrical Isolation on a Safety Related Power Supply Due to a Design Error</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While performing a review of the CR-3 electrical systems, FPC discovered a discrepancy where a non-safety related solenoid valve was receiving power from a safety related distribution panel without the appropriate electrical separation or isolation. After completing an engineering evaluation, on October 8, 1997, FPC determined that this condition was contrary to the CR-3 design basis. FPC determined that electrical isolation was not provided between the safety related indication and the non-safety related circuit for solenoid valve RW-63-SV. Solenoid valve RW-63-SV, which is powered from Vital Bus Distribution Panel VBDP-4, breaker 8, is used to test the emergency Nuclear Services Seawater Pump RWP-2B. The loss of solenoid valve RW-63-SV would not affect the ability to start and run RWP-2B because the circuit is only used for pump testing. This discrepancy was caused by an incorrect interpretation of the electrical separation design criteria specified in IEEE 279-1968 and IEEE 308-1969 (Proposed) during initial construction of CR-3. CR-3's current electrical separation design criteria clearly defines requirements for the isolation of safety and non-safety related electrical components. An isolation device will be installed or the solenoid valve will be replaced with a safety related solenoid valve prior to MODE 4.
3021997033 | Crystal River 3 | 08/07/1997 | 11/10/1997 | 9711140055 | <strong>Loss of Control Complex Ventilation System Due to Electro Thermo Link and Fusible Link Fire Damper Automatic Closure</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During the ongoing 10CFR50 Appendix R Fire Study Review, FPC discovered that automatic closure of Electro Thermo Link (ETL) and Fusible Link (FL) fire dampers located in the Control Complex Ventilation System ductwork was not evaluated in the Appendix R Fire Study. Specifically, the effects of fire induced damper closure on Appendix R safe shutdown equipment room temperatures were not evaluated. Control circuitry for ETL fire dampers located in the Control Complex Ventilation System common ductwork were reviewed. Results indicated that the ETL fire dampers controlled by High Temperature Switches located in the Control Complex are susceptible to hot short conditions causing damper closure. Preliminary time versus temperature heatup curves for Appendix R safe shutdown equipment rooms were developed. The curves indicated that a loss of ventilation results in room temperatures exceeding the current design temperature limit of 104 degrees Fahrenheit. On October 10, 1997, FPC determined this condition to be outside CR-3's design basis. The CR-3 Fire Study did not consider the effect of hot shorts causing ETL fire damper closure. This spurious closure isolates Control Complex ventilation to Appendix R safe shutdown equipment. The appropriate procedures will be revised to include operator actions to reestablish ventilation in affected rooms. The Fire Study will be revised to include effects of ETL and FL fire damper closure and additional operator actions as required.
3021997034 | Crystal River 3 | 10/08/1997 | 11/06/1997 | 9711130200 | <strong>Nonconservative Assumption In Breaker Setpoint Calculations Could Prevent Stating Of Motor Operated Equipment</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While performing an investigation into the recent spurious trip of a nonsafety-related molded case circuit breaker (MCCB), FPC personnel determined setpoint calculations for safety-related MCCBs with adjustable instantaneous trip settings do not provide adequate allowance for breaker tolerances and for greater than nominal voltages at motor terminals. The potential for unexpected tripping of safety related MCCBs is being reported under 10CFR50.73(a)(2)(ii)(B). This condition could affect the ability of safety-related equipment to mitigate the consequences of design basis accidents. However, most MCCBs have a long history of operating without spurious tripping. The cause for this condition was a nonconservative assumption in MCCB setpoint calculations. FPC will recalculate trip settings for safety-related MCCBs with adjustable instantaneous trip settings. Necessary changes will be implemented prior to MODE 4 entry. By January 31, 1998, the Electrical Design Criteria document will be revised to reflect the methodology for determining the instantaneous trip setting and the revised lower limit setting multiplier for MCCBs. Nonconservative assumptions have been reported in LERs 97-024-00, 97-01 5-01, and 89-033-01.
3021997035 | Crystal River 3 | 10/16/1997 | 11/13/1997 | 9711170029 | <strong>A Design Error Resulted in the Inability to Provide Reactor Coolant System Inventory Makeup During a Postulated Appendix R Event</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During the ongoing 10CFR50 Appendix R Fire Study Review, Drawing and Procedure Validation, FPC discovered that the power supplies used to power the Makeup and Purification System High Pressure Injection (HPI) valves and normal inventory makeup valves were not protected from the effects of a postulated Appendix R fire in the Main Control Room (MCR) or Cable Spreading Room (CSR). As a result, components necessary to maintain safe shutdown may not have been available following an Appendix R fire. Manual action could have been taken by the operators to restore flow for inventory makeup. Therefore, the postulated Appendix R fire would not have increased the risk to the health and safety of the public.. Appendix R requirements associated with the operation of the Makeup valves were not adequately considered during the design of the Remote Shutdown Panel. FPC will provide an alternate means of restoring power to the HPI valves. Subsequent to the installation of the Remote Shutdown Panel, Nuclear Engineering Procedures (NEPs) have been revised by FPC to improve the design process and verification of designs.
3021997036 | Crystal River 3 | 10/24/1997 | 11/21/1997 | 9711260037 | <strong>Thermal Overload Relays in Manual Reset Position Resulted in Operation Outside of the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During a walkdown of the High Pressure Injection (HPI) system, FPC discovered that the overload relays for the Makeup and Purification (MU) System HPI valves, MUV-23, MUV-24, MUV-25, and MUV-26, were not in the automatic reset mode of operation. The CR-3 Final Safety Analysis Report (FSAR) states "Automatic overload reset is provided." The risk to the public health and safety was not significantly increased because the overload relays set in the manual position did not affect the normal operation of the MUVs. The requirement for the Emergency Core Cooling System (ECCS) Motor Operated Valves (MOVs) to have automatic reset capability was not included in the development of the modification. FPC will review and reset, as necessary, the ECCS MOV overload relays to assure the correct setting is used. This action will be completed under the CR-3 12 week rolling work schedule process. The Nuclear Engineering Procedures (NEPs) were revised to enhance the development and verification of designs. FPC has reported two previous LERs regarding thermal overload relay settings.
3021997037 | Crystal River 3 | 10/24/1997 | 11/21/1997 | 9711260071 | <strong>Containment Integrity Cannot be Proven Following Calibration of Building Spray (BS) Pressure Switches and Transmitters</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During a review of Surveillance Procedure SP-132, "Engineered Safeguards Channel Calibration" and SP-162, "Post Accident Monitoring Instrumentation Channel Calibration," FPC discovered that following calibration, the Reactor Building Spray System (BS) pressure switches (PS) and BS pressure transmitters (PT) were not adequately leak tested in accordance with 10 CFR 50, Appendix J. The BS PS/PTs were not tested at a pressure equal to or greater than the analyzed peak Design Basis Accident (DBA) pressure for containment. During performance of PS/PT calibration, the 1/4 inch instrument lines are removed from the PS/PTs. Because these instrument lines penetrate containment, removal of a component in that line could result in a breach in containment. The RB pressure sensing instrument lines affect containment integrity for Reactor Building (RB) penetrations 319, 426, 429, and 442. FPC failed to recognize that the RB PS/PT penetrations required post-maintenance leak testing at peak DBA containment pressure. FPC also failed to recognize the potential containment breach caused by removal of the instrument lines. This condition has existed since original plant construction. Upgrade of the affected RB instrument penetrations to permit appropriate testing is being implemented prior to restart. LER 97-014-00 and 96-018-01 document previous examples of inadequate containment penetration testing.
3021997038 | Crystal River 3 | 03/17/1997 | 08/13/1999 | 9908230113 | <strong>An Engineering Oversight Resulted in Operation Outside of the Design Basis for the Waste Disposal System</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While performing a system readiness review of the Radioactive Waste Disposal (WD) System, FPC identified that the WD system liquid outlet piping did not meet the Seismic Class I requirements. The Final Safety Analysis Report (FSAR), Section 5.1.1.1 (i), specifies the WD system liquid outlet piping is required to be Seismic Class 1. On April 7, 1997, FPC engineering prepared an evaluation using Regulatory Guide 1.143 as a basis for acceptance and concluded the WD system liquid outlet piping was not outside of the design basis. On October 24, 1997, FPC re-reviewed the engineering evaluation and determined the evaluation was invalid because Regulatory Guide 1.143 was not part of the licensing basis and is not applicable to CR-3. Therefore, WD system liquid outlet piping is outside of the design basis. Any postulated liquid leaks from the non-seismic liquid outlet piping would be contained in either the Auxiliary Building or the Reactor Building. The discrepancy between the FSAR and the as-built condition was due to engineering oversight. FPC has concluded that the WD system is operable and capable of performing its intended safety function during a seismic event. The WD system outlet piping has either been upgraded to Seismic Class I or the FSAR has been revised, as appropriate.
3021997039 | Crystal River 3 | 06/02/1997 | 12/03/1997 | 9712080131 | <strong>Unqualified Material Left In Reactor Building During Construction Could Affect Post-LOCA Cooldown Capability</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While evaluating the existence of polystyrene found permanently installed inside the Reactor Building, FPC personnel determined the material was not analyzed for impact on post-LOCA (Loss of Coolant Accident) cooldown. At 1454 hours, on November 8, 1997, a four-hour notification (Event No. 33239) was made in accordance with 10CFR50.72(b)(2)(i). This report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(A). Dislodged polystyrene could interfere with post-LOCA recirculation flow by obstructing the sump screens and/or entering the recirculation flow stream, adversely affecting the ability to mitigate the consequences of a LOCA. The cause for the presence of polystyrene in the Reactor Building is cognitive personnel error during construction of CR-3. FPC personnel walked down the Reactor Building and concluded polystyrene was not permanently installed anywhere else within the Reactor Building, other than between the incore pit/letdown cooler structure and the Reactor Building liner. Prior to entering MODE 4, the permanently installed polystyrene will either be removed from the Reactor Building or analyzed for impact on post-LOCA cooldown. Current CR-3 procedures would identify and control polystyrene brought into the Reactor Building as a transient combustible. No previous similar events have been reported by FPC.
3021997040 | Crystal River 3 | 01/08/1997 | 12/04/1997 | 9712080123 | <strong>Inadequate Engineering Documentation for Safety-Related Large Bore Piping Analysis and Pipe Supports</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC personnel determined a current issue would be of generic interest and should be reported as a voluntary LER. The issue is inadequate engineering documentation for safety related large bore piping analysis and pipe supports. In 1996, FPC chartered an independent reviewer to evaluate the adequacy of existing documentation to support current licensing and design basis of large bore piping and associated supports. The assessment identified discrepancies. Assessment results were documented and evaluated. FPC determined the individual and cumulative effect of the discrepancies did not result in structures, systems or components being rendered incapable of performing their safety function. The cause for inadequate original calculations was cognitive personnel error. The cause for not maintaining calculations was a process weakness. FPC plans to perform a comprehensive and rigorous inspection, revalidation and/or requalification of safety-related large bore piping and pipe supports. The program will take approximately 4-6 years (2-3 fuel cycles) to implement. Previous similar events have been reported.
3021997041 | Crystal River 3 | 11/10/1997 | 12/10/1997 | 9712120099 | <strong>Control Complex Chiller May Be Rendered Unavailable Due to a Design Error</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC discovered a condition where the Control Complex Chilled Water System and Control Room Emergency Ventilation System (CREVS) fans could be unavailable for a time greater than assumed in the calculation for the Control Complex transient temperature response. The calculation assumes the CREVS fans will be started within 30 minutes and the Control Complex Chilled Water System will be started and remain in service within 90 minutes after the event. This was discovered during the validation of an Emergency Operating Procedure (EOP) for a Small Break Loss of Coolant Accident (SBLOCA) concurrent with a Loss of Offsite Power (LOOP) and a single failure. This condition was determined to be reportable pursuant to 10CFR50.73(a)(2)(ii)(B), as a condition outside of CR-3's design basis. If the CREVS fans and Control Complex Chilled Water System are not started within the required time frames, the rated ambient temperature of Control Complex equipment that is relied upon to remain functional could be exceeded during and following a design basis event. The apparent cause of this event was a design error in a pre-1987 modification for upgrading the Control Complex Chilled Water System to safety-related. A modification to remove the subsequent Engineered Safeguards (ES) actuation load shedding by deleting the Undervoltage/ES Lockout Relay output contacts from the control circuits will be implemented prior to the restart of CR-3.
3021997042 | Crystal River 3 | 07/30/1997 | 06/15/1998 | 9806190155 | <strong>Inadequate Engineering Evaluation Results in Loss Of Diverse Reactor Coolant System Leak Detection Capability</strong><br /><i>Abstract:&nbsp;</i>On November 25 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While validating a calculation performed for FPC to establish the sensitivity of the Reactor Coolant System (RCS) leak detection channel, FPC personnel determined that the gaseous radioactivity monitor RM-A6 was not capable of detecting a one gallon per minute (gpm) RCS leak within one hour. This represents a condition prohibited by the CR-3 Improved Technical Specifications (ITS) and is reportable in accordance with 10CFR50.73(a)(2)(i)(B). The containment sump monitor was operable and provided one means of detecting a one gpm RCS leak within one hour. The cause for failing to have diverse monitoring devices available is personnel error. RCS leakage detection instrumentation is not required to be operable in MODE 5. No immediate corrective actions were necessary. A new RM-A6 particulate radioactivity monitor has been installed. The RM-A6 gaseous radioactivity monitor (the third diverse RCS leak detection method) has been entered into the Operations Equipment Out of Service log. FPC will submit a License Amendment Request by September 30, 1998, to reflect the limitations of the gaseous radioactivity monitor to detect RCS leakage. Current Nuclear Engineering Procedures ensure design-related activities performed for CR-3 are controlled and verified. No previous similar events have been reported.
3021997043 | Crystal River 3 | 12/08/1997 | 01/06/1998 | 9801090232 | <strong>A Deficiency in the Electrical Design Criteria Resulted in the Control Complex Chiller Motor Trip Set point Set Below the Full Load Ampere Setting</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC was performing a review of an electrical calculation and discovered the trip set points for the Control Complex Chiller (CHHE) Motor overloads were set below the vendor recommended set point. The low set point could cause the CHHEs to trip, resulting in insufficient cooling for the Control Complex during a design basis accident. If the CHHEs were to trip, temperatures could exceed the rated ambient temperature for the Control Complex equipment necessary to mitigate the consequences of the accident. The low set points of the CHHE motor overloads were incorrect since the initial installation. FPC will reset the motor overload set points to the vendor recommended value prior to entering MODE 4. Procedures will be revised to assure periodic surveillance of the motor overloads is performed.
3021997044 | Crystal River 3 | 12/09/1997 | 01/05/1998 | 9801090115 | <strong>Breaker Trip Setpoint Could Result in Deenergizing Safety-Related Equipment Due To Inadequate Design Criteria</strong><br /><i>Abstract:&nbsp;</i>On December 9, 1997, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). During an evaluation of 480 volt switchgear breakers that supply power to Engineered Safeguards (ES) Motor Control Centers (MCCs), FPC discovered that the long-time overcurrent trip setpoint for the feeder breaker (number 3351) to ES MCC 3A2 was set too low. During design bases accident conditions involving an ES actuation with off-site power available, the steady state current on ES MCC 3A2 could be above the potential trip range for the breaker long-time overcurrent trip setpoint. Loss of ES MCC 3A2 does not affect components powered from remaining Train A ES MCCs 3A1 or 3A3. Also, redundant components supplied by Train B ES MCCs 3B1, 3B2, and 3B2 remain operational. The cause for the incorrect long-time overcurrent trip setpoint was inadequate setpoint criteria. Prior to entering MODE 4, FPC will reset the long-time overcurrent trip setpoint for breaker number 3351 and implement administrative controls to prevent simultaneous loading of the two largest nonsafety-related loads onto ES MCC 3A2. The Electrical Design Criteria for CR-3 will be revised by April 15, 1998, to include criteria for determining the long-time overcurrent trip setpoint for 480 volt switchgear breakers. FPC has submitted one recent LER associated with incorrect breaker setpoints.
3021997045 | Crystal River 3 | 12/05/1997 | 12/31/1997 | 9801060075 | <strong>Containment Isolation Valves Not Seismically Qualified Due to an Installation Error</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). While performing a walkdown in preparation for maintenance work on the Chemical Addition (CA) System, FPC personnel discovered two valves in the CA System that did not meet the Seismic Class I qualification requirement. Outside Containment isolation valves CAV-6 and CAV-7 actuators were not restrained as originally designed. In the event of a postulated seismic event, the 0.375 inch tubing connected to CAV-6 and CAV-7 creates the potential for a Containment breach pathway to the adjacent Auxiliary Building. The supports for the valve actuators were to be installed during the original construction of CR-3. The specified supports did not fit the actuators. FPC has installed the necessary supports to return the valves to Seismic Class I. This error occurred during the original construction of CR-3. The current installation and modification controls in place at CR-3 would prevent this type of error from recurring. FPC has submitted two previous LERs regarding equipment not installed and four LERs regarding components which did not meet the Seismic Classification criteria.
3021997046 | Crystal River 3 | 12/20/1997 | 01/16/1998 | 9801210095 | <strong>A Design Error Resulted in a Potential for the Emergency Diesel Generator to be Unavailable Following a Postulated Appendix R Event</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1997, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN). FPC discovered circuits required for the operation of the Emergency Diesel Generator (EDG) exciters were not protected from the effects of a postulated Appendix R fire in the Main Control Room (MCR) or the Cable Spreading Room (CSR). As a result, components necessary to achieve and maintain safe shutdown of the plant may not have been available following an Appendix R fire. In the event of the postulated Appendix R fire, the EDGs may not have been readily available to respond to a loss of offsite power, as required by the Appendix R safe shutdown analysis. The apparent cause of this event was an engineering oversight and an incorrect assumption when developing the CR-3 Appendix R Fire Study in 1985. FPC has installed isolation fuses in the identified circuits. The design drawings and the Fire Study will be revised to reflect the vendor and block drawings by March 31, 1998. Since the initial development of the CR-3 Appendix R Fire Study in 1985, FPC has improved the process of design validation. FPC has previously submitted six LERs regarding misinterpretation of drawings, engineering oversight or information not correctly translated onto drawings.
3041997001 | Zion 2, Zion 1 | 09/02/1997 | 10/02/1997 | 9710060466 | <strong>Unit 2 Instrument Bus Perturbation caused by a short circuit occurring During 2C Accumulator Level Transmitter Modification installation resulted in Engineer Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1997, at approximately 1430 Instrument Maintenance Technicians were performing work instructions which included the installation and removal of temporary jumpers so that power would not be interrupted for Steam Generator Level indication. The technician donned safety gloves and proceeded to install the first jumper. As the second jumper was being placed onto terminal screw, the first jumper was knocked off the terminal causing a short. A voltage perturbation occurred on Instrument Bus 212. As a result, Eagle Rack 8, 9, & 10 Bistables tripped, 0B & 0C CC pumps auto-started, letdown isolated, N42 positive & negative flux rate tripped, 2FCV-PR24B auto-closed & 2RI-PR03 went into HI alarm. All systems functioned as designed and no abnormalities were noted. Upon examination of the terminal block an arc strike was evident indicating the first jumper hit the terminal screw below it and caused the voltage perturbation. <br /><br /> The cause of this event was that the policy/guidelines on the use of personnel protection equipment and jumper type were general in scope and lacked sufficient details for work to be performed. Corrective actions include the development of a policy for the proper use of protective gear, equipment and tools in areas that require a higher level of manual dexterity and provide training to appropriate departments. No previous events of this type were identified. g:\zler\297001.ler
3041997002 | Zion 2, Zion 1 | 10/12/1997 | 11/11/1997 | 9711140157 | <strong>Inadvertent Isolation of Service Water Cooling to 28 Diesel Generator During System Alignment</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1997, at 1515, the Operating Department was performing System Operating Instruction (SOI)-61F, Splitting Service Water Header for Maintenance, on the normally cross-tied Unit 1/Unit 2 Service Water (SW)[BI] system. At 1554, while SOI-61F was being performed, Periodic Test (PT)-11E-0, 0 Diesel Generator (DG)[EK] Cylinder Liner Test, was started on 0 DG. The combination of actions from these two procedures resulted in five of the six SW pumps being inoperable. <br /><br /> The cause of the event is that Shift Management did not ensure all operability requirements were met prior to the performance of SOI-61F and PT-11E-0. There was a lack of communication between Unit 1 and Unit 2 Shift Supervisors, and SOI-61F did not contain a step to verify that the Unit 2 DG cross-tie valves were open because of inadequate procedure preparation. <br /><br /> The safety significance of this event is minimal. Corrective actions include restoring the required number of SW pumps, revising SOI-61F to reflect the need to verify the DG cross-tie valve positions, and increasing the awareness of the operations personnel regarding the need to keep a broad perspective on the impact that evolutions will have on other plant systems.
3041997003 | Zion 2 | 10/14/1997 | 11/13/1997 | 9711190156 | <strong>Unit 2 Residual Heat Removal System Declared Inoperable Because Only One Component Cooling Pump was Operable</strong><br /><i>Abstract:&nbsp;</i>At 1619 hours on 10/14/97, the 0B Component Cooling [CC] (CC) Pump was declared inoperable due to excessive oil leakage coming from the outboard oil bulb. At 1653 hours on 10/14/97, 1B Emergency Diesel Generator (EDG)[EK] failed to start during the performance of Periodic Test (PT)-11-DG1B, the 1B Diesel Generator Loading Test, because a control air line to the 1B EDG air start distributor had separated. This rendered 0C CC Pump inoperable leaving only the 0A CC Pump operable. With only one CC pump operable, both trains of the Residual Heat Removal (RHR)[BP] system were declared inoperable. <br /><br /> At 0253 hours on 10/15/97, the 0B CC Pump was declared operable, following completion of repairs. As a result, both the CC System and the Unit 2 RHR system were declared operable. At 0022 hours on 10/17/97, 1B EDG was successfully tested and declared operable. The cause of 0B CC Pump being declared inoperable was an oil leak from the oil bulb. <br /><br /> The cause of the 1B EDG failure was a broken 1/2" pipe nipple due to high cycle fatigue. Corrective actions include fixing the oil leak on the 0B CC Pump and repairing the 1B EDG control air line. <br /><br /> There were no actions in progress that would have reduced the Reactor Coolant System (RCS)[AB] boron concentration and there was at least 100 degrees F of RCS subcooling available. Therefore, the health and safety of the public was not compromised.
3041997004 | Zion 2, Zion 1 | 10/15/1997 | 11/14/1997 | 9711170187 | <strong>Small Bore Containment Penetration Line Inadequately Supported Since Plant Construction</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1997, while performing an engineering review, a 3/4" Reactor Coolant Drain Tank line (2DT0403/4"), exiting the Unit 2 Reactor Containment through penetration P-30 was found unsupported outside the Reactor Containment [NH] Building. The investigation concluded that the support was not installed due to inadvertent omission by the field engineer or installer during plant construction. The line has been verified to be intact b Non Destructive Examination (NDE), and there are no adverse safety consequences to the public as a result of this event. The line was declared inoperable upon completing a review that found the line to be permanently deformed and overstressed. <br /><br /> Prior to Unit 2 start-up, a design change will be installed to provide proper support for line 2DT040-3/4", and other lines that may be identified during walkdowns to verify the extent of the condition. Prior to Unit 1 start-up walkdowns will be performed, and similar defects that may be identified on Unit 1 will be corrected.
3041997005 | Zion 2 | 10/24/1997 | 11/21/1997 | 9711260215 | <strong>Missed Technical Specification Surveillance Failure to Test one 2A Safety Injection Pump Suction Valve in the Prescribed Periodicity</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1997, during the performance of a Quality and Safety Assessment (QSA) In Service Testing (IST) Audit, it was discovered that the suction valve for the 2A safety injection (SI)[BQ] pump, 2MOV-SIB923A, was not stroke tested as required by Technical Specification 4.0.5. Technical Specification 4.0.2 allows a 25% grace period for the surveillance test. The valve was tested on December 14, 1995, and it should have been tested before April 8, 1996, but it was not. <br /><br /> The cause of this event was that the program to ensure the Technical Specification IST requirements for each component are met in every circumstance (mode change. post maintenance testing, return to service testing, periodic testing) is inadequate. The program does not verify that all the IST requirements which reside in various test procedures are satisfied. <br /><br /> The missed surveillance for 2MOV-SI8923A did not impact the health and safety of the public nor the plant since the safety injection function was still available. Corrective actions include creating a second check review of periodicity requirements, ensuring review of IST surveillances prior to the critical date, sending completed test procedures to IST group for review prior to the critical date, and pursuing acquiring a scheduling/monitoring tool to keep track of IST surveillances.
3041997006 | Zion 2, Zion 1 | 10/28/1997 | 11/26/1997 | 9712010069 | <strong>Potential to Exceed 10 CFR 50.46 Emergency Core Cooling System Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>Westinghouse informed ComEd on October 28, 1997, of issues regarding fuel rod internal pressure, the status of the Performance Analysis and Design (PAD) code, and concerns with fuel design bases and 10CFR50.46 criteria for Braidwood, Byron, and Zion Stations. Westinghouse could not preclude the possibility that the Integral Fuel Burnable Absorber fuel may be outside of the fuel design basis due to fuel clad gap re-opening and the 17% maximum cladding oxidation limit may be exceeded. <br /><br /> An initial 12% oxidation level was established as a screening criterion to permit assessment regarding compliance with the 17% maximum cladding oxidation criteria. Westinghouse stated that plants potentially may have fuel rod gap re-opening, but those which have cladding oxidation of less than 12% are in compliance. <br /><br /> Westinghouse developed a plan to resolve the concerns in three steps: Review and improvement of analytical models; Gather additional data; and Perform plant specific assessments. Zion Station will monitor and evaluate the data received from Westinghouse and will summit a supplement to this LER based on the assessment content. <br /><br /> The fuel rod design has the potential for the nuclear fuel being outside the design basis and is being reported pursuant to 10CFR50.73(a)(2)(ii).
3041997007 | Zion 2, Zion 1 | 10/30/1997 | 12/01/1997 | 9712040010 | <strong>Failure to Maintain the Required Number of Service Water Pumps Operable</strong><br /><i>Abstract:&nbsp;</i>Prior to conducting maintenance on the common service water (SW)[BI] system with that system in an unusual, split-header configuration, station personnel revised the system operating instructions to ensure Unit 2 SW pump operability in the event of a dual unit loss of off-site power during this infrequent evolution. Specifically, the revisions were intended to ensure the 0 emergency diesel generator (DG)[EK] would lock onto the Unit 2 Emergency Safety Feature (ESF) bus 247 instead of the Unit 1 ESF bus 147. Following the maintenance and the return of the SW system to the normal cross-tied configuration, an operator, while reviewing an associated procedure identified a technical error that prevented the 0 DG from serving as an emergency power source for the 2A SW pump in the event of a dual unit loss of off-site power. As a result, the 2A SW pump was not operable and there were an insufficient number of operable SW pumps for 18 hours. The cause was that several management personnel failed to adhere to the requirements for reviewers to use the applicable drawings when reviewing procedures. A contributing cause was a procedure writing process that did not require procedure writers to use the applicable drawings when revising or drafting new instructions. Corrective actions include attaching the applicable drawings to the revised/new procedure, requiring reviewers and writers to document that they have used the applicable drawings and counseling the reviewers. This event is reportable pursuant to the requirements of 10CFR50,73(a)(2)(v)(B).
3041997008 | Zion 2 | 11/22/1997 | 12/22/1997 | 9712300329 | <strong>Safety Related Snubber Not in Snubber Program and Subsequently Not Inspected Per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>While performing the Technical Specification Surveillance, TSS 15.6.48 (Safety Related Hydraulic and Mechanical Inaccessible Snubber Visual Inspection walk-down) on November 22, 1997, a Grinnell hydraulic snubber (VC208-S6) not included in the snubber inspection program was identified on line, 2VC037-2". This 2 inch line is the discharge of the Charging Pump (VC) supply to the No. 1 seal on the 2C Reactor Coolant Pump. The cause of the event is unknown. The line associated with this particular snubber was not part of the IE Bulletin 79-14 walk-downs which is believed to helped validate the basis for the safety related snubber surveillance. A review of the IEB 79-14 walk-downs were performed and it identified that the line in question was not walked down along with 11 other piping subsystems which were identified as inaccessible. <br /><br /> The safety significance of this event was minimal, because the snubber was subsequently successfully tested. Corrective actions include adding the snubber to the 18 month surveillance and perform the necessary walk-downs on the accessible subsystems for both Units 1 and 2 for those subsystems that were originally not walked down during the IEB Bulletin 79-14 Program. Additionally, the IEB 79-14 isometrics will be reviewed against the snubber surveillance procedure to identify discrepancies.
3041997009 | Zion 2 | 12/02/1997 | 12/22/1997 | 9712310062 | <strong>Inadvertent Engineered Safeguards Feature Actuation During Testing</strong><br /><i>Abstract:&nbsp;</i>During performance of Periodic Test (PT) 10-3 "Containment Isolation Phase B Testing" on Dec. 2, 1997, test relay SIX1-AX did not unlatch as required during restoration of PT 10-3. An inadvertent Engineered Safeguards actuation signal was sent to several components. The 2A Service Water pump started and 2B Steam Generator Isolation Valve 2MOV-FW0016 went closed. All other Safeguards Equipment associated with this relay were either Out Of Service (OOS) or running. During troubleshooting it was discovered that relay SIX1-AX had been miswired. <br /><br /> The cause of this event was a failure to follow procedures. On 10/04/97, during replacement of test relay SIX1-AX by Electrical Maintenance personnel. both the electrician performing the work, and the electrician performing the second verification used the HFA Relay Data Sheet in Electrical Maintenance Procedure E005-2, HFA Relay Inspection and Adjustment to disconnect relay SIX1-AX, but they did not use it to reconnect the relay. <br /><br /> Corrective actions include correctly wiring test relay SIX1-AX, counselling the individuals involved, holding a tailgate session with the entire Electrical Maintenance Department, management verification for reterminations for a period of time, and revising Electrical Maintenance procedures to require verifications be performed apart in time.
3051997001 | Kewaunee | 01/31/1997 | 03/03/1997 | ML11188055 | <strong>NRC Inspection Identifies Two Potential Unreviewed Safety Questions and One Potential Inadequate TS</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1997, during an exit for a safety system operational performance inspection (SSOPI) of Kewaunee's auxiliary feedwater (AFW)[BA] and residual heat removal (RHR)[BP] systems, a Nuclear Regulatory Commission (NRC) inspection team presented their preliminary findings. They identified two potential unreviewed safety questions (USQs) and one potential inadequate Technical Specification associated with the Kewaunee Plant. The inspectors identified potential concerns with: 1) the low discharge pressure trip of the AFW pumps, 2) the minimum required flow for the AFW system, and 3) the required level in the condensate storage tanks (CSTs). <br /><br /> Wisconsin Public Service Corporation (WPSC) has reviewed these concerns. Our review has determined there are weaknesses in the design basis documentation and administrative controls of the AFW system and CSTs. <br /><br /> Our review also determined that the concerns raised during the inspection, as we understand them, do not represent USQs nor did they result in a violation of the Technical Specifications. <br /><br /> To address these concerns WPSC will be: 1) reviewing and revising the Updated Safety Analysis Report (USAR) and the TS basis to accurately reflect the design basis of the AFW system, 2) revising the administrative controls for the CST.
3051997002 | Kewaunee | 02/05/1997 | 10/24/1997 | ML11188059 | <strong>Potential Defect in the Process Used to Perform a Laser Welded Repair of Previously Sleeved Steam Generator Tubes</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1997, with the plant in a cold shutdown condition, plant management determined that there was a potential defect in the process used to laser weld repair a number of previously sleeved steam generator (SG) tubes during the on-going refueling outage. The refueling outage started on September 21, 1996, and was extended until June 12, 1997, due to the number of parent tube indications found in Westinghouse mechanical hybrid expansion joint (HEJ) sleeves. <br /><br /> During a test with the secondary side of the SGs pressurized to approximately 100 psi, a number of the laser weld repaired HEJ sleeved tubes were found to be leaking. Six (6) of the repaired HEJs were removed to perform laboratory evaluation to determine the root cause of the weld failures. This evaluation concluded that the welds mechanically sheared due to unevenly distributed stresses during the post-weld stress relief process. All the laser weld repaired joints were re-inspected and all tubes with unacceptable welds were either plugged or repaired prior to placing the SGs back into service. This LER was originally submitted in accordance with 10 CFR 50.73 (a)(2)(ii) as a potential degradation of a principal safety barrier found while the plant was shutdown; however since the defective welds were never placed in service this LER is being submitted as information only.
3051997003 | Kewaunee | 03/10/1997 | 04/09/1997 | ML11188056 | <strong>Plant Operation Outside of Test Specs with Reactor Vessel Level Indication Out of Service</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1997, with the plant in refueling shutdown, a design error was identified in one of the subsystems of the Inadequate Core Cooling Monitoring System (ICCMS), the Reactor Vessel Level Indicating System (RVLIS). As a result the RVLIS is incapable of performing its intended function over its required span. The cause of this event is failure to properly implement changes to the design as refinements were made in the early phases of the project prior to installation. <br /><br /> This condition has existed since the system was installed in 1986. Kewaunee Technical Specifications (TS) require the RVLIS to be operable when above the hot shutdown operating mode. Therefore, the plant was operated in violation of the TS since the system was installed. <br /><br /> Currently, Kewaunee is in an extended outage completing steam generator repairs. The RVLIS system is not required during this plant mode. Prior to the reactor being made critical following the current outage, a software change will be implemented to correct the system. <br /><br /> The ICCMS was designed by Wisconsin Public Service and built by Combustion Engineering (CE). The Kewaunee system does not use the standard CE ICCMS software used at other nuclear power plants.
3051997004 | Kewaunee | 04/09/1997 | 08/07/1997 | ML11188058 | <strong>Unanalyzed Condition Exists During Safety Injection Accumulator Filling Operations</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1997, with the plant in refueling shutdown mode, it was discovered that, if an accident requiring Safety Injection (SI) were to occur during the filling operation of either SI accumulator, the amount of water injected into the reactor coolant system will be reduced by the amount of water being diverted into an accumulator. This potentially affects SI system accident analysis assumptions and results, and when using single failure criteria, the operating SI pump may exceed the design runout flow limit.<br /><br /> This issue has existed since initial plant startup. The effect that the accumulator filling operation had on the operability of the SI system during an accident was probably not considered at that time because of the infrequent occurrence and the short duration of the fill operation. Short term corrective action (current operating cycle only) is to use an alternate, throttled path from the SI pumps to fill the accumulators. Long term corrective actions will be implemented following further investigation.
3051997005 | Kewaunee | 04/16/1997 | 05/16/1997 | ML11188057 | <strong>Design Review of Auxiliary Feedwater System Identifies Inconsistencies with Main Steam Line Break and ATWS Analyses</strong><br /><i>Abstract:&nbsp;</i>A review of the auxiliary feedwater (AFW) system's design identified inconsistencies between actual system design and that assumed by analysis. Specifically, system resistance curves developed to respond to I.E. Bulletin 80-04 overestimated system resistance. Furthermore, the analysis of a main steam line break assumed the turbine driven pump would maintain full speed throughout the event. However, during some main steam line breaks, there may be insufficient steam generator (SG) pressure to maintain the turbine driven pump at full speed. The generic analysis of an anticipated transient without scram (ATWS) assumes that AFW pumps will be available throughout the event without operator intervention. Kewaunee's system would require operator action to prevent the pumps from tripping on low discharge pressure during an ATWS. <br /><br /> Due to the significant time between the original analyses and the date the discrepancies were identified, the cause of the event can not be conclusively determined. <br /><br /> Corrective actions include testing the pumps, evaluating the test results and analysis results to assure compliance with our license, and re-evaluating the ATWS event.
3051997006 | Kewaunee | 06/04/1997 | 07/03/1997 | ML11188057 | <strong>Missed Shift Surveillance Due to Ineffective Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1997, with the plant in Refueling shutdown, Surveillance Procedure (SP) 87-149, "Daily Instrument Channel Checks - Shutdown," was inadvertently not performed on the day shift. SP87-149 is required to be performed every 12 hours when the plant is in Cold Shutdown or Refueling Shutdown. <br /><br /> The root cause of this event was determined to be inadequate administrative control. The operations crew failed to realize that SP87-149 was not performed during their shift and there was no administrative control in place to ensure the SP was performed in the required time period. <br /><br /> This report will be required reading for the operations staff to remind each staff member of the importance of completing the required surveillance within the required time. Since this is a repeat occurrence, an evaluation will also be performed to determine further corrective actions to prevent a recurrence.
3051997007 | Kewaunee | 06/06/1997 | 07/07/1997 | ML11188057 | <strong>Reactor Vessel Level Indication System Level Error Due To Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1997, with the plant in refueling shutdown, a design deficiency was discovered in the Kewaunee reactor vessel level indication system (RVLIS). The deficiency was discovered while resolving a previously identified software error in the system. The deficiency results in the potential for a non-conservative indicated level error; indicated level may be as much as ten percent higher than actual level. This potential condition has existed since the system was installed in 1986. <br /><br /> Kewaunee is unable to determine if the level error actually exists without draining the reactor coolant system (RCS). Additionally, we are unable to assure that the condition will not occur during normal plant operation even if it could be proven that the condition was not created during RCS filling. The phenomenon which causes the potential for the level error and the inability to provide assurance that the condition will not occur during plant operation may be of generic interest. <br /><br /> An operability determination has been made assuming the condition occurs and the worst case level error exists. Administrative corrective actions have been implemented to address the potential offset in indicated level. The corrective actions will remain in place until the deficiency can be resolved during the next scheduled refueling shutdown in the fall of 1998.
3051997008 | Kewaunee | 06/03/1997 | 04/15/1998 | 9804210353 | <strong>Target Rock Solenoid Valve Test Failure Under Differential Pressure Conditions (Voluntary LER)</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1997, while in refueling shutdown, one of the reactor coolant system (RCS) vent valves failed to open. During filling and venting operations, when the control switch for the RCS vent to containment valve was positioned to open, the valve remained closed. At the time, the RCS pressure was approximately 50 psig. The valve had been previously cycled a number of times earlier in the refueling outage when the RCS pressure was essentially 0 psig. The valve which failed to open is a Target Rock, dual pilot operated, solenoid valve, Model 80B. <br /><br /> The valve design is such that it should operate with or without differential pressure (dP). However, during the filling and venting operation, the valve did not open when a 50 pound dP was applied. Subsequent investigation revealed a light accumulation of sediment on the valve internal surfaces, which is suspected to have impeded valve operation. <br /><br /> Surveillance testing in accordance with plant Technical Specifications for this system is normally performed at 0 psig RCS pressure. However, based upon the failure identified, testing at zero dP is not sufficient to demonstrate satisfactory valve performance. This event is being reported voluntarily to inform the industry of the potential for inadequate testing for those licensees with similar valve design and test conditions.
3051997009 | Kewaunee | 10/08/1997 | 11/06/1997 | ML11188059 | <strong>Portion of ESF Actuation Circuit Not Tested per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1997, while the plant was operating at fun power, a portion of the actuation circuitry for both trains of the containment fancoil units' emergency discharge dampers was identified as not being tested in accordance with Technical Specifications (TS) surveillance requirements. An evaluation of this condition found that a functional test of a slave relay in the circuit was not being performed periodically. The last functional test was performed when the relay was replaced in 1992. This condition was found during Kewaunee's efforts in response to Generic Letter (GL) 96-01, "Testing of Safety Related Logic Circuitry." <br /><br /> Subsequent to identifying the testing deficiency, functional tests of the affected portions of the actuation circuitry were performed. Testing was completed on October 12, 1997. These tests confirmed that the actuation circuitry not previously tested performs its safety related function. <br /><br /> Revisions to existing test procedures will be implemented to conduct periodic tests which will ensure future TS compliance.
3061997001 | Prairie Island 2, Prairie Island 1 | 02/07/1997 | 03/17/1997 | 9703250236 | <strong>Transporting a Heavy Load over Irradiated Fuel or Safe Shutdown Equipment without Establishing the Required Conditions</strong><br /><i>Abstract:&nbsp;</i>On 2/4/97, it was determined that 22 Reactor Coolant Pump upper bracket and rotor (heavy load - 21 tons) was moved over irradiated fuel on 2/3/97, without a specific load handling procedure defining the safe load path and without containment isolated. The movement of this heavy load in containment did not follow the reactor building safe load path requirements stated in Operations Manual Section D58, Control of Heavy Loads. D58 states that 'With the reactor head removed, loads greater than 2100 lb. SHALL NOT be moved within 15 horizontal feet of the irradiated fuel without specific written procedures per step 5.3.5' and containment isolation requirements satisfied. Neither of these provisions were satisfied. Following this event two subsequent heavy load lifts were recognized as not meeting the intent to control heavy load lifts where safe shutdown equipment could be affected. <br /><br /> Corrective actions, taken and planned, address issues raised by this event. These issues include: procedure compliance, adequacy of the heavy loads program, human factors considerations of the implementing procedures, and training and qualifications of the individuals with responsibilities for implementation of the program features.
3061997002 | Prairie Island 2 | 03/18/1997 | 04/17/1997 | 9704220158 | <strong>SI Discharge Valves to the RCS Cold Legs Closed When RCS above Cold Shutdown Because of Administrative Error</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1997, Unit 2 was above cold shutdown, with the reactor coolant system (RCS) at approximately 335 degrees F and 360 psig, during startup evolution from a refueling outage. Following an outage, each safeguards accumulator (tank containing borated water pressurized with nitrogen that provides a passive means of injecting into the RCS in the event that the RCS pressure drops below the pressure of the accumulator) needs to be filled. In order to accomplish this, a safety injection pump is normally used to deliver water to an accumulator through the accumulator fill line (see Figure 1); during the filling, the valves to the RCS cold legs, 8801A and 8801B, must be closed to prevent flow to the RCS when RCS pressure is below shutoff head of the safety injection pump. This evolution is normally done prior to heating the RCS above 200 degrees F. Because of plant conditions, the fill was delayed until after heatup to above 330 degrees F. When the fill was performed, the isolation valves for the safety injection to the cold legs were closed to prevent injection to the RCS. However, these valves are required to be locked open when above 200 degrees F, by Technical Specifications. <br /><br /> The decision was made to allow these valves to be closed for the filling operation because it could be accomplished in less than one hour and the 'motherhood clause' was entered which gave one hour before a shutdown would be required. The operations staff did not realize that the 'motherhood clause' was not intended to be entered voluntarily like a limiting condition for operation action statement. <br /><br /> Corrective actions include training on the intent of the 'motherhood clause' to the operations staff.
3061997003 | Prairie Island 2 | 05/17/1997 | 06/16/1997 | 9706230411 | <strong>Auto-start of 22 Turbine Driven Auxiliary Feedwater Pump on Undervoltage Signal and Entry into TS 3.0.C for the Inoperability of Reactor Coolant Pumps When Buses 21 and 22 Were De-energized</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1997, Unit 2 was brought to a planned hot shutdown condition to perform valve maintenance in the 22 reactor coolant pump (RCP) containment vault. The operators were reestablishing the substation electrical configuration when the operator observed electrical arcing at the 2RSX B Disconnect Switch. The disconnect switch was inspected and determined to be questionable. The 2RSX B disconnect switch provides power to the plant 4.16kV buses 21 and 22 and is the only normal power supply at shutdown for buses 21 and 22. Buses 21 and 22 are the power supplies for 21 and 22 RCPs. It was decided that it would be prudent to stop 21 and 22 RCPs in a timely manner to preclude a possible failure of the disconnect switch. The concern was that the disconnect could fail and cause single phase operation of the loads (RCPs). 22 RCP was shutdown (21 RCP was already shutdown) at 1200 to reduce the electrical loading on the disconnect switch. Although this was prudent, it meant an entry into Technical Specification 3.0.C, the "motherhood clause," which is reportable. <br /><br /> When both buses 21 and 22 were de-energized, 22 Turbine-Driven Auxiliary Feedwater Pump automatically started on an undervoltage signal. The 22 Turbine Driven Auxiliary Feedwater Pump control switch was placed in manual and the pump was stopped. The switching procedure was completed at approximately 1230, 21 RCP restarted at 1235, and 22 RCP restarted at 1244.
3061997004 | Prairie Island 2 | 09/26/1997 | 10/27/1997 | 9710310179 | <strong>Plant Shutdown due to Greater Than Allowable Leakage from the Maintenance Airlock per Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>The Unit 2 Maintenance Airlock volumetric test exceeded the TS-4.4 required containment leakage rate test program limit for airlock leakage. Repairs were not completed until a unit shutdown was necessary. Leakage occurred through the operating mechanism shaft seals. The airlock volumetric test method actually yields results that are the summation of the leakage across both airlock door boundaries. The airlock volumetric test pressurizes the space between the doors. However, during an accident situation the actual airlock leakage would be the lesser of the individual door leakages. As-found shaft seal test results indicate the interior door was below the leakage limit. After reducing these shaft seal leakages, the airlock volumetric test results were 196 SCC/min versus the 12,900 SCC/min limit. In addition to the immediate repairs, the airlock test procedure will be changed to require complete inspection of the entire airlock pressure boundary before the leakage is assigned to one door.
3061997005 | Prairie Island 2 | 11/17/1997 | 12/17/1997 | 9712230066 | <strong>Sudden Pressure Lockout of No. 10 Transformer Resulting in Auto Load Rejection/Restoration on Safety Related Bus</strong><br /><i>Abstract:&nbsp;</i>On Monday, November 17, 1997, at 12:04 with Unit 2 in Mode 1 at 100% power, the Prairie Island No. 10 Transformer (10 Transformer), locked out on Sudden Pressure. The 4.16 KV Safeguards Bus 26, which was being supplied by 10 Transformer via 13.8 KV Bus CT12, automatically transferred to its 2RY Transformer source by Bus Sequencer actuation. All automatic switching occurred as expected without any equipment malfunctions. The NSP transmission system experienced no other transients or perturbations.<br /><br /> A Limiting Condition for Operation was entered at 12:04 per TS 3.7.B.2 due to the loss of one of the two required paths from the grid to the unit 4 KV safeguards distribution system. The LCO was exited at 15:15 after the CT12 Source to Bus 26 was restored by energizing it from 4.16 KV Bus CT11 via Breaker CTBT112. <br /><br /> The 10 Transformer locked out from an apparent sudden pressure. There is no indication of the source of the sudden pressure event. Testing and inspection concluded that there is no significant damage to the transformer. The 10 Transformer Sudden Pressure Relay, 63T10, was replaced as precautionary measure.
3091997001 | Maine Yankee | 01/09/1997 | 02/18/1997 | 9702240413 | <strong>CABLE SEPARATION II</strong><br /><i>Abstract:&nbsp;</i>During the week of January 9, 1996, while the plant was in the cold shutdown mode of operation, Maine Yankee engineers discovered additional cable separation issues. One (1) of these issues was determined to be an original construction issue, while others involve various components affected by the design modification process. These concerns were discovered as a result of the on-going reviews of cable separation issues identified in LER 96-038. <br /><br /> The conditions that were determined to be outside of Maine Yankee's cable separation criteria include the following: power cables were found encroaching different tray sections; cables from different vital buses and channels were found routed together or in the wrong tray sections; numerous cables of different trains or channels do not meet original separation criteria as a result of tray configurations at transition points such as risers and T's. <br /><br /> The discrepancies discovered during reviews have been or are in the process of being corrected or addressed. Some of the cables have been wrapped, separated, or re-routed in the correct section. Cable separation design and walkdown teams are in the process of identifying further actions or engineering justifications for various conditions. Plant management is assessing long term actions to address causal factors identified by Plant Root Cause Evaluation #214, 'Root Cause Investigation of Cable Separation Problems at Maine Yankee Atomic Power Co.'
3091997002 | Maine Yankee | 01/10/1997 | 02/10/1997 | 9702180241 | <strong>PCC/SCC Vacuum Relief Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1997, Maine Yankee engineers discovered that the Component Cooling Water (CCW) Surge Tank Vacuum Breakers were not included in the In-Service Testing (IST) Program. The two (2) Vacuum Breaker Valves (PCC-S-328 and SCC-S-394), by not being part of the IST Program, have not received appropriate surveillance and testing as required by code. This condition does not meet the requirements of Technical Specification 4.7 and is considered outside of the Maine Yankee Licensing Basis. The basis for this determination is further detailed in Design Discrepancy Evaluation 97-001. <br /><br /> Upon notification of the condition, the Maine Yankee Control Room declared the valves operable after demonstrating operability. Short term contingency plans were developed by Operations to provide a continuous vent to the surge tanks on those occasions when the tank relief lines are isolated for RMS signal testing. The valves are currently in the process of being replaced by new vacuum breaker valves. The new valves will be included in the IST Program and tested accordingly.
3091997003 | Maine Yankee | 01/17/1997 | 02/18/1997 | 9702240389 | <strong>Leaking Fuel Pins Identified in Westinghouse Fuel</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1997, Maine Yankee was in a Refueling Shutdown Condition with fuel sipping in progress. <br /><br /> As a result of fuel sipping 9 leaking fuel assemblies were identified. Follow up ultrasonic testing of these assemblies identified a total of 76 leaking pins. All of the assemblies with leaking pins were manufactured by Westinghouse and were loaded into the core during the 1995 refueling outage. As a result of visual inspections of leaking assemblies, the failure mechanism has been determined to be caused by grid-pin fretting at the mid-bundle grids. <br /><br /> Current plans are to replace all installed Westinghouse fuel assemblies with a fuel design not susceptible to the grid-pin fretting failure mechanism.
3091997004 | Maine Yankee | 01/22/1997 | 02/24/1997 | 9703040300 | <strong>RCS Loop Fill Header MOV Overpressure</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1997 Maine Yankee was in a Cold Shutdown condition. While conducting a review of plant design in response to a design deficiency identified in LER-96-022, Containment Primary Component Cooling Piping Design Inadequacy Due to Lack of Thermal Relief Valves, and subsequent Nuclear Regulatory Commission Generic Letter 96-06, Assurance Of Equipment Operability And Containment Integrity During Design-basis Accident Conditions, engineers noted that under post LOCA conditions, sections of piping associated with the Reactor Coolant Loop Fill Header could become pressurized in excess of design pressure due to thermal expansion of fluid trapped in the header. <br /><br /> As the conditions postulated to cause over pressurization only exist post LOCA, and the plant is currently in a Refueling shutdown condition, no immediate corrective/compensatory action is required. Relief valve protection will be installed in the header prior to plant startup.
3091997005 | Maine Yankee | 02/18/1997 | 03/20/1997 | 9703260077 | <strong>Potential Freezing Conditions in the Circulating Water Pump House</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1997, the Maine Yankee Control Room was notified by engineering that in the event of a Loss of Offsite Power or a ventilation fan malfunction, freezing conditions could be created in the Circulating Water Pump House which could adversely affect Service Water Pump Components. This concern resulted from the follow-on reviews generated by the "Maine Yankee Atomic Power Station Safety System Support Ventilation Systems Assessment Report" dated December 20, 1996. In the event of a Loss of Offsite Power, Pump House heating would be lost and the building ventilation dampers would fail open. This could create potentially freezing conditions for Service Water Pump components. In the event of a fan malfunction, discharge air flow would increase and also create potentially freezing conditions for Service Water pump components. Immediate corrective actions include the use of temporary heaters in the Pump House, increased equipment monitoring, and de-energized fans and closed dampers during cold weather operations. Long term actions will include an evaluation to consider design changes to preclude unacceptable air temperatures in the Pump House.
3091997006 | Maine Yankee | 02/26/1997 | 03/28/1997 | 9704090162 | <strong>Propane Tank Improperly Stored Near Pump House.</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1997, the plant was in the Refueling Operations Mode. In response to a question raised by the NRC Senior Resident, site Security personnel notified the Control Room that a 1000 gallon propane tank was found in close proximity to safety related components in the Circulating Water Pump House. The Control Room notified engineering personnel and plant management. Immediate actions were taken to empty the propane tank. <br /><br /> Further review revealed that the tank was installed as part of a heating system for the new outage cafeteria building that was installed in the protected yard. installed without an approved work order, adequate engineering review, or adequate safety analysis. <br /><br /> Long term corrective actions include an evaluation of the potential affects of a 1000 gallon propane explosion on nearby safety related components. Project approval training needs will be evaluated to ensure future modifications of this nature receive the appropriate level of engineering review.
3091997007 | Maine Yankee | 03/13/1997 | 04/14/1997 | 9704210013 | <strong>No Radiation Protection Technician On Site for greater than two hours</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 13, 1997, at 0230, with the plant in the refueling shutdown mode, the only Maine Yankee (MY) individual qualified in radiation protection (RP) procedures, left the site due to illness. The Technical Specifications requires one qualified RP technication on site with fuel in the reactor. Allowance is made for accomodating unexpected absence, such as this illness, provided immediate action is taken to restore the staffing position within two hours. The RP supervisor was aware that the MY RP technician had left the site and that the technical specification requirement must be met. The RP supervisor was unaware that the other MY RP technicians were not qualified, was engaged in other activities requiring immediate attention, and did not assess the situation completely. This requirement is stated in the MY RP administrative procedure. The next shift arrived at 0530 with a qualified MY RP technician on site. <br /><br /> The corrective actions were: (1) Performed a formal root cause evaluation, (2) Reviewed previous work schedules since January 1, 1997 to assure that no other similar event had occurred, (3) Identify the qualified MY RP technician on the weekly schedule and in the logbook, and (4) Reinforce training on procedural adherence and the technical specification requirements.
3091997008 | Maine Yankee | 04/11/1997 | 05/09/1997 | 9705150173 | <strong>Inservice Inspection and Testing Deficiencies that Affect Operability</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1997, with the unit in the Refueling Operations Condition, the Engineering Programs Department (EPD) notified the Control Room of Inservice Inspection and Testing (IST) Program deficiencies. These deficiencies involved valves that affected the operability of systems required for refueling and were discovered during an EPD self-assessment of the IST Program. <br /><br /> The valves were in the Primary Component C ooling (PCC), Secondary Component Cooling (SCC), Residual Heat Removal (RHR), Diesel Generator MG), and Service Water (SW) systems. Except as noted, the valves had been tested in other programs but not formally tested IAW Technical Specification 4.7 (INSERVICE INSPECTION AND TESTING OF SAFETY CLASS COMPONENTS). <br /><br /> Operability Determinations and Engineering evaluations were performed on the affected systems. Baseline testing of some valves was performed. Other valves had been recently tested and met IST Program requirements. The remaining valves were either placed in their safe position or their operability was determined to be not applicable for existing plant conditions. <br /><br /> The following corrective actions were identified: EPD will complete the self-assessment of the IST Program, Operability Determinations were performed and required systems were returned to Operable Status. Identified valves will be tested as required prior to plant heat-up. Procedures will be revised to include the valves in the IST Program.
3091997009 | Maine Yankee | 05/01/1997 | 06/18/1997 | 9706250010 | <strong>Design Basis Issue for High Energy Line Break in the Turbine Building</strong><br /><i>Abstract:&nbsp;</i>Revision 1 to LER 97-009 is a major rewrite with significant changes from the original LER. To improve readability change bars have not been included. <br /><br /> On May 1, through May 21, 1997, Maine Yankee was in the Refueling Shutdown Condition. During the review of Maine Yankee's Individual Plant Evaluation for External Event (IPEEE) a scenario that could be more limiting than the design basis High Energy Line Break (HELB) in the Turbine Building was identified. Analyses of a broader spectrum of line breaks were initiated. Initial assessment of the preliminary HELB profiles identified components in the Component Cooling Water and Feedwater Systems that were not qualified for the harsh environment predicted by the analyses. On May 19, 1997, following further review of Maine Yankee's High Energy Line Break licensing basis it was recognized that certain plant modifications installed after 1973, did not correctly account for licensing basis requirements for a postulated High Energy Line Break in the Main Steam Valve House (MSVH). Safe Shutdown Equipment potentially impacted by this oversight include the following: EFW System, Secondary Component Cooling Water System, Emergency Diesel Generator, DWST Level Alarms, and RG 1.97 Steam Generator Pressure instruments. On May 21, 1997, HELB related deficiencies associated with possible ruptures in Steam Generator Blowdown and Letdown System piping were identified in the Primary Auxiliary Building. <br /><br /> Additional analyses of postulated ruptures on high energy lines in the Turbine Building, MSVH and PAB continues. Potential corrective actions being considered include: replacement, modification, or relocation of components not qualified for a HELB, and continued evaluations for possible modifications to the Turbine Building, MSVH and PAB that would mitigate the consequences of a design basis HELB in these areas.
3091997010 | Maine Yankee | 05/09/1997 | 06/09/1997 | 9706160094 | <strong>Steam Generator Tube Deficiencies Issues</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1997, Maine Yankee was in the Refueling Shutdown Condition. Maine Yankee was performing examinations of its Steam Generators (SG) during the refueling outage, including a 100% examination of all the tubes in all three Steam Generators. At 1740 on May 9, 1997, Engineering reported that greater than 1% of the total tube population were determined to be defective. In accordance with requirements of Maine Yankee Technical Specifications, a four hour report was made to the NRC. <br /><br /> Tubes representative of those containing the largest detected defects were selected to undergo in-situ hydro testing. On May 21, 1997, one tube in #3 Steam Generator leaked at a pressure lower than that required by Reg. Guide 1.121 criteria. <br /><br /> All of the other initially tested tubes satisfied the Reg. Guide 1.121 leak criteria. The sample size for testing was expanded to include tubes whose Eddy Current Test characteristics were close to that of the failed tube. All of the additional tubes tested met the Reg. Guide 1.121 leak criteria. <br /><br /> Causal factors of the events include: Primary and Secondary Water Stress Corrosion Cracking, pitting, Intergranular Attack, and that bobbin flaw signals are difficult to detect at dented egg crates. <br /><br /> Corrective actions include: plus point exams of all dented intersections in egg crate supports 1 through 6, plug all detected cracks and plug volumetric indications equal to or greater than 40% through-wall and those which have grown.
3111997001 | Salem 2 | 01/15/1997 | 02/13/1997 | 9702200174 | <strong>Inadequate Surveillance for PORV Accumulator Discharge Check Valves</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1997 a review determined that the surveillance of the Salem Unit 2 check valves for the pressurizer over-pressure system had not been performed correctly in December 1994 and in January 1997. The testing was being performed with a reduced differential pressure rather than the maximum differential pressure as required by the ASME code. In accordance with the provisions of Technical Specification 4.0.3, a correct surveillance was completed on January 16, 1997. The Salem Unit 1 surveillance for the check valves was performed correctly in the past and was not affected by this occurrence. <br /><br /> The cause of this occurrence was the failure of the procedure writers and reviewers to identify that the procedure testing method did not meet the requirements of the ASME code. Corrective actions include a satisfactory retest of the valves and a procedure revision. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111997002 | Salem 2, Salem 1 | 02/13/1997 | 03/17/1997 | 9703240138 | <strong>Non-Seismically Qualified Pressure Switches In Auxiliary Building Ventilation</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1997 an investigation raised questions regarding qualifications of components in the Auxiliary Building Ventilation system. Subsequent investigation revealed that four pressure switches on Salem Unit 2 could not be verified as seismically qualified. In addition, one of the four pressure switches was found to have its sensing lines reversed. The pressure switches were replaced in 1986 with non-qualified pressure switches. The sensing lines for the one pressure switch were reversed in 1978 as part of a design change. Three seismically qualified switches have been re-installed and the sensing lines restored to the correct configuration. The fourth switch will be replaced prior to Unit 2 entry into Mode 4. In addition, walk downs confirmed that other similar sensing lines were installed correctly. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A), the plant was in an unanalyzed condition that significantly compromised plant safety.
3111997003 | Salem 2, Salem 1 | 03/19/1997 | 04/18/1997 | 9704280002 | <strong>Excessive Debris in the Unit 2 Containment</strong><br /><i>Abstract:&nbsp;</i>During the cleanup of the Salem Unit 2 Containment Building many examples of poor housekeeping were found. As an example, an estimated 300 to 400 pounds of excess debris was found. While no specific transport analysis was performed, it is postulated that the debris could find its way to the containment sumps, and affect the performance of pumps that use the containment sumps as a supply of water. <br /><br /> The cause of this event, is poor enforcement and lack of management expectations over the life of the plant, coupled with poor worker practices. The debris was removed from the containment building, and corrective action work requests were written for those housekeeping items that could not be readily corrected. Management has reiterated its expectation that all debris and material left over after completion of work activities be removed, when the job is completed. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(ii) any condition that resulted in the nuclear power plant being outside the design bases of the plant.
3111997004 | Salem 2, Salem 1 | 04/08/1997 | 10/30/1998 | 9811030207 | <strong>Failure to Comply With TS Action Statement, Diesel Generator Start, and Inadequate Surveillance Testing.</strong><br /><i>Abstract:&nbsp;</i>At 1306 April 8, 1997, station personnel discovered that the 2A and 2C AC electrical bus trains were inoperable for longer than allowed by TS 3.8.2.2. The operating shift initiated actions to establish Containment Integrity as required by TS 3.8.2.2, and restored the 2C AC electrical bus train to operable. TS 3.8.2.2 was exited at 1600 on April 8, 1997. Further, during investigation of the occurrence two additional reportable issues were identified. The 2A DG started unexpectedly and ran for approximately 2 hours, and the Surveillance Test for TS 4.8.2.2 was discovered to be inadequate. <br /><br /> The cause of the TS 3.8.2.2 violation is attributed to inadequate tracking of inoperable equipment by shift personnel. Corrective actions include a review of the TS Action Tracking Log for improvements, and a review of this event with Operations personnel for lessons learned. The cause of the 2A DG start has not been determined. The cause of the inadequate Surveillance Test is attributed to inadequate controls over maintenance of TS surveillance procedures This condition was previously identified and described in LER 311/95-008. Corrective actions include procedure revisions to ensure TS 4.8.2.2 is properly addressed. This supplemental LER reports that a manufacturer's evaluation of the Safeguards Equipment Controller (SEC) did not identify the cause for the unexpected start of the 2A DG. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications, and 10 CFR 50.73(a)(2)(iv), any condition that results in an Engineered Safety Feature actuation.
3111997005 | Salem 2, Salem 1 | 04/30/1997 | 05/30/1997 | 9706090332 | <strong>Pressurizer Overpressure Protection System Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1997, a review of the Unit 2 control room narrative logs identified that from 0531 on March 23, 1997 until 2148 on March 27, 1997 the Reactor Coolant System (RCS) remained pressurized with a channel of the Pressurizer Overpressure Protection System (POPS) inoperable. The POPS was inoperable for 112 hours and 17 minutes because the 2A 115 volt Vital Instrument Bus was aligned to its AC line regulator, and both POPS channels were being powered from the same DC Bus. At the time the transfer occurred, RCS temperature was 105 degrees F, and RCS pressure was 150 psig. This is a violation of Technical Specification 3.4.10.3 which requires that both channels of POPS be operable or the RCS be vented when RCS temperature is less than 312 degrees F. The cause of this occurrence is attributed to inadequate procedural guidance resulting from an inadequate implementation process in 1980 for license changes. This process has changed significantly since 1980. <br /><br /> Corrective actions include revision of the procedures for 115 volt Vital Instrument Bus and 125 VDC Bus operations to address POPS operability concerns when an instrument Bus is transferred from its normal alignment or 125 VDC loads are transferred to an alternate source. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications. It is likely that similar violations have occurred in the past at Unit 1 or Unit 2.
3111997006 | Salem 2 | 04/04/1997 | 05/05/1997 | 9705140299 | <strong>Seismic Adequacy of the Service Water Header Invalidated.</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1997, the seismic adequacy of the 21 Service Water (SW) header was determined to be invalid. A modification to the header was being performed, and piping was connected to the 21 SW header without the proper pipe hangers being installed. <br /><br /> This occurrence was caused by unclear work instructions. This condition existed for a limited period of time (approximately one week) during which no seismic activity was experienced. The condition was limited to only the 21 SW header. The newly installed piping was disconnected from the 21 SW header. The work instructions were changed to clarify the requirements for connecting the new piping to the SW system. The piping has been re-installed correctly. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii), any condition outside of the plant's design bases.
3111997007 | Salem 2 | 06/23/1997 | 07/23/1997 | 9707300043 | <strong>Missed 4.0.5 Testing of Check Valves 2CC195 and 2CC210</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1997, the Technical Specification (TS) 4.0.5 Inservice Inspection (ISI) requirement to perform radiography of check valves 2CC195 and 2CC210 every 92 days was determined to have been missed. As a result of the missed surveillance, one loop of the component cooling water was declared inoperable until the surveillance testing (radiography) was completed. Since the missed surveillance test exceeded the surveillance test interval, the 25% extension allowed by TS 4.0.2, and the Limiting Condition for Operation (LCO) statement time, this event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as, "any condition prohibited by the plant's Technical Specifications." <br /><br /> The cause of this occurrence is attributed to personnel error. The recurring task for performing the next 92 day surveillance was not generated prior to the expiration of the surveillance test interval. The check valves were subsequently tested and determined to be in their proper position. The personnel involved in this event have received appropriate disciplinary actions.
3111997008 | Salem 2, Salem 1 | 07/15/1997 | 08/14/1997 | 9708210055 | <strong>Failure to Enter Action Statement for having Both Radiation Monitors in the Same Control Room Air Intake Duct Inoperable</strong><br /><i>Abstract:&nbsp;</i>As a result of channel checks of the Control Room radiation monitors on July 13, 1997, Operators determined that one of two radiation monitor channels in the Unit 2 outside air intake duct was inoperable and entered Unit 2 Technical Specification 3.3.3.1 Action b.27 for the seven day action statement. On July 15, 1997, troubleshooting on the other Unit 2 intake radiation monitor channel rendered that channel inoperable. The Control Room Supervisor failed to identify that troubleshooting this channel would make both Unit 2 air intake radiation monitor channels inoperable and thus failed to enter the appropriate Technical Specification action statement. <br /><br /> This event is attributed to misjudgment by the Control Room Supervisor caused by a failure to validate and verify the impact of the troubleshooting work package. Personnel involved with the occurrence were held accountable for their actions and the Operations Manager will discuss this event with the operating crews during Licensed Operator requalification training, emphasizing proper work planning methods and the use of the Technical Specification Action Statement Log. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(i)(B) as, "any condition prohibited by the plant's Technical Specifications."
3111997009 | Salem 2 | 07/11/1997 | 08/07/1997 | 9708200050 | <strong>Failure to Stroke Pump Discharge Valves for Potential Pressure Locking Concern</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.6.2.1, which requires both Containment Spray (CS) systems to be operable in Modes 1 through 4, was not satisfied from June 15, 1997 to July 14, 1997. The CS pump discharge valves (21CS2 & 22CS2) were identified as susceptible to pressure locking in PSE&G's response to Generic Letter 95-07. To address pressure locking concerns, the CS2 valves are required to be stroked following operation of the associated CS pump. on July 11, 1997, it was identified that procedure S2.OP-IO.ZZ-0002, "Cold Shutdown to Hot Standby," directed functional testing of the CS pumps without subsequently stroking the 21CS2 and 22CS2. Further review determined that the CS pumps were functionally tested on June 14, 1997 in accordance with this procedure while in Mode 5. Valves 21CS2 and 22CS2 were not stroked open and closed prior to June 15, 1997 when Salem Unit 2 entered Mode 4. The cause of this occurrence is attributed to personnel error in that personnel failed to perform an adequate review to identify all instances in which the Containment Spray pumps were operated. Corrective actions include procedure revisions to address the additional instances of Containment Spray pump operation. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications, and 10 CFR 50.73 (a)(2)(ii)(B) a condition that was outside the design basis of the plant.
3111997011 | Salem 2, Salem 1 | 09/02/1997 | 10/01/1997 | 9710090022 | <strong>Improper Scheduling of Staggered Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1997, station personnel discovered that the Solid State Protection System (SSPS) P4 permissive and undervoltage (UV) reactor trip breaker functional testing was not being performed on staggered surveillance test basis as required by Technical Specification (TS) 4.3.1.1. A review of other staggered surveillance testing also identified that the Auxiliary Feedwater (AFW) pump staggered testing required by TS 4.7.1.2 was not properly scheduled. <br /><br /> The cause of the failure to comply with TS 4.3.1.1 and TS 4.7.1.2 staggered testing requirements is attributed to personnel error. The responsible personnel for scheduling staggered surveillance testing did not comply with the requirements of administrative procedure NC.NA-AP.ZZ-0012(Q), "Technical Specifications Surveillance Program." <br /><br /> Personnel involved in the scheduling of the SSPS and AFW pump staggered surveillance testing have been held accountable in accordance with PSE&G's disciplinary policies. Additional training will be provided to personnel responsible for scheduling surveillance testing. <br /><br /> This event is reportable under 10CFR50.73(a)(2)(i)(B) as, "any condition prohibited by the plant's Technical Specifications."
3111997012 | Salem 2 | 09/07/1997 | 10/03/1997 | 9710150004 | <strong>Entry Into Technical Specification 3.0.3 Due to the Inoperability of Two Overtemperature-Differential Temperature (OTDT) Channels.</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1997 Reactor Coolant Loop 24 Overtemperature Differential Temperature (OTDT) was declared inoperable due to differential temperature being lower than acceptable. Loop 23 protection circuit was already inoperable in support of ongoing maintenance work. Thus two channels of OTDT were inoperable, requiring entry into Technical Specification 3.0.3 at 0750. The maintenance work was terminated, Loop 23 OTDT was returned to an operable state and Technical Specification 3.0.3 was exited at 0840. The unacceptable differential temperature was caused by a change in 24 Loop hot leg temperature (T-hot) streaming profile from the previous cycle, and the conservatively set NIS indication. The expected differential temperature was based on last cycle's streaming profile (the only information available) which caused the differential temperature to appear low. Corrective action included a check of the instrumentation calibration, collection of data to determine the new streaming profile and resealing of Loop 24 instrumentation to reflect the current cycle streaming profile. <br /><br /> This event is reportable per 10CFR50.73 (a)(2)(i)(B), a condition prohibited by the plant's Technical Specifications.
3111997013 | Salem 2 | 09/02/1997 | 10/02/1997 | 9710100130 | <strong>Unplanned Entry into 3.0.3 Due To Two Inoperable Pressurizer Level Channels</strong><br /><i>Abstract:&nbsp;</i>At the time of occurrence Salem Unit 2 was in Mode 1 at 39% Reactor Power. On August 29, 1997, Salem Unit 2 pressurizer level channel III exceeded the level deviation between channels and was declared inoperable. Channel III was placed in a tripped condition in accordance with Technical Specifications. On September 2, 1997, Maintenance personnel prepared to isolate channel III at the root valve to support troubleshooting. Root valve 2PS9 was shut at 0548 hours and immediately pressurizer level channel I failed low. Since channel I was selected as a controlling channel, pressurizer heaters tripped off, letdown isolation valves closed and maximum charging flow was initiated. TS 3.0.3 was entered for two inoperable pressurizer level channels (I & III). The pressurizer heaters were restored and valve 2PS9 was reopened within approximately 3 minutes. Following a satisfactory channel check, channel I was restored and TS 3.0.3 exited at 0554 hours. Subsequent investigation identified an error in the controlled drawing used to identify the root valve. Corrective actions include revision of drawings to remove this error. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications.
3111997014 | Salem 2 | 10/02/1997 | 10/31/1997 | 9711170131 | <strong>Manual Reactor Trip From 100% Power Following Loss of Both Operating Steam Generator Feed Pumps</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1997 Salem Unit 2 was manually tripped from 100% power following the loss of both operating Steam Generator Feed Pumps (SGFP). The event was caused by a failed analog circuit card in the Westrac Data Acquisition System (DAS). The DAS is a temporary system that was connected to the Advanced Digital Feedwater Control System (ADFCS) to monitor ADFCS performance in support of modification acceptance testing. The component failure produced a false signal in the ADFCS representative of low feedwater header pressure. The differential between this signal and main steam header pressure is compared to a programmed differential pressure set point to determine SGFP speed. In response to this condition, SGFP speed increased, raising feedwater flow to 120% of the full flow value. This reduced SGFP suction pressure to the SGFP Low Suction Pressure trip setpoint, tripping both operating SGFPs. Operations personnel promptly responded to this condition by manually tripping the reactor. Following the event, the DAS was disconnected from the ADFCS.
3111997016 | Salem 2, Salem 1 | 09/09/1997 | 11/21/1997 | 9712010348 | <strong>Loss of Fire Protection Water to the Salem Unit 1 and 2 Auxiliary Building and Containments</strong><br /><i>Abstract:&nbsp;</i>At 2210 hrs on September 16, 1997, a Unit 1 Nuclear Control Operator (NCO) identified that the fire protection water for Salem Units 1 and 2 Auxiliary Buildings and Containment was isolated. Fire protection water for these areas is supplied via valves 1FP186 and 1FP187, which were found closed. While the exact cause of the valves being mispositoned could not be determined, the valves were most probably misaligned during relamping activities on September 9, 1997. The cause of the condition going unidentified is attributed to human error due to inattention to detail by the NCO and the Loss Prevention Operators during subsequent panel reviews. Fire protection personnel were promptly notified, and the valves were opened at 2237 hrs. <br /><br /> Pursuant to License Conditions 2.C.(10) and 2.I of the Unit 2 Facility Operating License, a 24 hour report and a follow-up Special Report were made to the NRC on September 17 and September 30, 1997, respectively. <br /><br /> This Special Report is being made in accordance with Technical Specification Section 6.9.3, and supplements the September 30, and October 15 1997 Special Reports.
3111997017 | Salem 2, Salem 1 | 12/12/1997 | 01/12/1998 | 9801210258 | <strong>Failure to Comply With Technical Specification Action Statement 3.7.10.a.1</strong><br /><i>Abstract:&nbsp;</i>At 2220 on December 12, 1997, while reviewing plant conditions in preparation for troubleshooting activities to determine the reason that the 23 chiller was inoperable, the Unit 2 Control Room Operator recognized that non-essential heat loads for the chilled water system were not isolated in accordance with Technical Specification Action Statement (TSAS) 3.7.10.a.1. Upon the identification that the non-essential loads were not isolated, the Operator isolated the non-essential loads to comply with TSAS 3.7.10.a.1. <br /><br /> The cause of this event is attributed to inadequate configuration control tracking by the Control Room personnel. The Control Room personnel failed to update the TRIS database and failed to tag the control room switches due to a misunderstanding of the requirements of procedure SC.OP-AP.ZZ-0103 (Q), "Component Configuration Control." Control Room personnel involved with this event were held accountable for their inappropriate actions in accordance with PSE&G policies. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3111997018 | Salem 2, Salem 1 | 11/25/1997 | 12/25/1997 | 9801210136 | <strong>Inadequate Technical Specification Testing - Main Steam Isolation Valve Hydraulic Unit Override Contacts</strong><br /><i>Abstract:&nbsp;</i>In December 1995, a Technical Specification Surveillance Improvement Project (TSSIP) was initiated for Salem Units 1 and 2. The scope and content of the TSSIP program was described previously in LER 311/95-008-00. This Technical Specification (TS) non-compliance was identified by the TSSIP project review team.<br /><br /> This LER documents a TS requirement non-compliance involving the failure to properly implement TS 4.7.1.5, demonstration of the operability of the Main Steam Isolation Valves (MSIV). Specifically, the TS surveillance procedure to verify the operability of the MSIV did not adequately test the MSIV hydraulic override feature. This feature interrupts hydraulic operation of the MSIV to allow valve closure in the event of an Engineered Safety Features Actuation System (ESFAS) Main Steam Isolation signal. Additionally, during the time that the MSIV hydraulic override feature was not being adequately tested, two or more MSIVs were (have been) operated simultaneously, placing the plant in Limiting Condition for operation 3.0.3 without the knowledge of the operators. <br /><br /> The cause of this occurrence has been attributed to a lack of adequate controls and understanding of the development and maintenance of Technical Specification surveillance procedures. This weakness was previously identified in LER 311/95-008 and LER 272/96-005 and its supplements. These events are reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3131997001 | Arkansas 1 | 04/08/1997 | 03/18/1998 | 9803240310 | <strong>Inconsistencies Between Once Through Steam Generator Tube Destructive Examination Results and Intergranular Attach Flaw Sizing Qualification Data Caused The Possibility That Tubes Were Left In Service With Flaws Exceeding The Technical Specification Limi</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1997, ANO-1 discovered that inconsistencies between destructive examination results of three Once Through Steam Generator (OTSG) pulled tubes and field eddy current sizing of intergranular attack (IGA) flaws in the upper tubesheets created the possibility that tubes had been left in service during a refueling outage in the fall of 1996 with defects exceeding the through-wall limit contained in Technical Specifications (TS). The sizing technique had been qualified in accordance with EPRI guidelines. Technical Specification 3.0.3 was entered, with actions delayed per 4.0.3, until enforcement discretion was obtained from the NRC. A request for an exigent TS change was submitted to allow operation for the remainder of the current cycle with IGA flaws in the upper tubesheet exceeding the TS limit. The TS change was issued as Amendment No. 189 on May 7, 1997. ANO has not been able to determine a root cause for this condition, but several potential contributing causes have been identified. Tubes that could remain in service with flaws in excess of the limit were determined not to represent a structural or leakage concern.
3131997002 | Arkansas 1, Arkansas 2 | 04/18/1997 | 05/19/1997 | 9705280011 | <strong>Reactor Operations Did Not Have Required Corrective Eyewear For Use With Self Contained Breathing Apparatus Readily Available Due To Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1997, ANO Operations personnel conducted an assessment which concluded that several operators from both ANO-1 and ANO-2 who are required to wear corrective eyewear did not have ready access to the appropriate eyewear for use with self contained breathing apparatus (SCBA). Since ANO's annunciator response procedures require operators to don SCBA within two minutes under certain conditions, the unavailability of SCBA eyewear for those individuals potentially compromised their ability to perform required watchstanding duties. The assessment also identified that several operators did not have current respirator qualification. Although these individuals had been previously respirator qualified, they had not maintained the administrative requirements for continued qualification. The root cause of this condition was inadequate procedural guidance. operations procedures did not contain requirements for watchstanders to maintain corrective eyewear for SCBA use readily available or to maintain respirator qualification. Immediate corrective actions were to ensure that all watchstanders obtained required SCBA corrective eyewear and renewed respirator qualification, if necessary. Appropriate procedure changes and training will be completed by August 5, 1997.
3131997003 | Arkansas 1 | 07/08/1997 | 08/07/1997 | 9708140112 | <strong>Inadvertent Automatic Actuation of the Emergency Feedwater System Resulting from a Lightning-Induced Trip of Two Emergency Feedwater Initiation and Control System Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1997, at approximately 1251, an inadvertent automatic actuation of the Emergency Feedwater (EFW) system occurred. At the time of the event, Reactor Protection System (RPS) testing was in progress and, as part of the test, Emergency Feedwater Initiation and Control (EFIC) system channel "A" was placed in Maintenance Bypass and a loss of main feedwater pumps signal was inserted in that channel. While in this configuration, the +/-15 vdc and the +28 vdc power supplies for EFIC channel "D" deenergized as a result of a lightning strike near the plant, resulting in a "Channel D in Bypass" signal being sent to the other EFIC channels. Since the EFIC system logic allows only one channel to be in Maintenance Bypass, it automatically removed channel "A" from bypass. The loss of channel "D" combined with the actuation signal in channel "A" satisfied the EFW actuation logic and EFW pump P-7B started. P-7A was out of service for maintenance and did not start. P-7B was secured after verifying the absence of conditions warranting EFW actuation. RPS testing was secured and all trips associated with the surveillance were reset. Applicable portions of EFIC surveillances were performed prior to returning the EFW and EFIC systems to operable status. The cause of this event was attributed to a lightning strike on or near the Reactor Building which caused the EFIC power supplies to trip on overvoltage. The EFIC system wiring and the Lightning Protection System will be evaluated for potential enhancements.
3131997004 | Arkansas 1 | 10/21/1997 | 11/20/1997 | 9711260112 | <strong>Two Remotely Operated Reactor Building Isolation Valves Not Tested As Required Due To A Misinterpretation Of Technical Specifications Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1997, during a review associated with an upgrade to the Inservice Testing Program, it was identified that two remotely operated Reactor Building (RB) isolation valves were not being stroke tested quarterly as required. Technical Specifications (TS) require that every three months remotely operated RB isolation valves shall be stroked to the position required to fulfill their safety function unless such operation is not practical during operation. SV-1440 and SV-1443 are Post-Accident Sampling System isolation valves for the RB sump. These remotely operated solenoid valves do not receive an Engineered Safeguards (ES) signal, are normally closed, and are operated infrequently. There were no procedural controls in place to ensure that they were stroke tested quarterly. The root cause of this condition was determined to be a misinterpretation of the testing requirements of TS. Plant personnel interpreted the intent of the applicable specification to require testing only those valves which receive an ES signal. Although not consistent with the wording of the TS, this interpretation is consistent with ASME requirements and Revised Standard Technical Specifications. The valves were successfully stroked and will be added to the appropriate surveillance procedure. Reviews will be conducted to identify any additional valves that need to be added to the surveillance program.
3131997005 | Arkansas 1 | 10/22/1997 | 11/20/1997 | 9711260117 | <strong>Surveillance Testing Did Not Verify That A Valve Would Close Upon Receiving An Engineered Safeguards Signal To Isolate Auxiliary Cooling Water From Service Water With All Combinations Of Service Water Pumps In Operation Due To A Deficient Testing Procedure</strong><br /><i>Abstract:&nbsp;</i>During a Quality Assurance audit of surveillance testing, ANO-1 discovered that testing of the circuitry for the valve that isolates the Auxiliary Cooling Water system from the Service Water (SW) system had not verified that the valve would close upon receipt of an Engineered Safeguards signal if "B" SW pump was running. operability had been verified for other SW pump combinations. At the time the condition was discovered, "B" SW pump was not operating. Testing was conducted in accordance with a special work plan and verified that the valve was operable. The root cause was attributed to a deficient test procedure. The test method had remained unchanged since procedure development in 1973. A review of similar circuits was in progress in accordance with NRC Generic Letter 96-01, but circuitry for this isolation valve had not yet been reviewed. Corrective actions for a similar condition reported in Licensee Event Report 50-313/94-003-01 resulted in a review of a 25 percent sample of similar components that did not include this valve. Completion of the GL 96-01 review is expected to identify any similar conditions. The test procedure will be revised before its next scheduled performance.
3151997001 | Cook 1 | 01/12/1997 | 02/11/1997 | 9702200157 | <strong>Technical Specification 3.03 Entered On Loss of Four Loop Injection Capability Due to Incorrect Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1997, with Unit 1 in Mode 1 at 99.8 percent Rated Thermal Power, the Safety Injection (SI) pump discharge cross-tie train "B" shutoff valve was closed to support filling the SI system accumulators. The East and West Residual Heat Removal (RHR) pump discharge cross-fie valves were already closed at this time. With the unit in this configuration, all four loop injection was lost and Technical Specification 3.0.3 was entered. This condition existed for approximately one minute. The event was terminated when the RHR cross-tie valves were opened per procedure.<br /><br />The problem was discovered on January 16, 1997 during a subsequent simulator training scenario on four loop injection where it was determined that procedure steps had been incorrectly sequenced. A one hour notification was made in accordance with 10 CFR 50.72(b)(1)(ii)(B), as a condition outside of the design basis, at 1653 hours on the same day. This event was a result of incorrect procedural guidance. The affected procedures were corrected to direct the proper sequence for operation of the SI pump and RHR pump discharge cross-be valves. Other actions were taken to ensure that source documentation, performance of 10CFR50.59 reviews and functional reviews are properly performed. <br /><br />This event was evaluated against the analyses for large break LOCA, small break LOCA, and containment, and found to have no safety significance.
3151997002 | Cook 1 | 01/28/1997 | 07/01/1997 | 9707090394 | <strong>LER Retraction - Stresses for Piping Found to Exceed Allowable Values During Postulated Design Basis Accident due to Inadequate Analysis during Original Design</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1997, with Unit 1 at 96.6 percent Rated Thermal Power and Unit 2 at 100 percent Rated Thermal Power, initial analyses performed in response to Generic Letter (GL) 96-06 on thermal over pressurization were completed. At that time, it was determined that the reactor coolant pump seal water return line, the reactor coolant sample lines, and the accumulator sample line could potentially over pressurize during a design basis accident; thus, in accordance with 10 CFR 50.72(b)(1)(II)(B), this condition was reported. As outlined in our 120 day response to GL 96-06, supplemental analyses were completed to determine the internal pressure and the resultant wall stresses in each of the aforementioned lines following a design basis accident. Those analyses concluded that the fluid lines in question would not over pressurize and that the pipe wall stresses would remain within the design limits under all conditions. For these reasons, the Licensee Event Report (LER) previously submitted on February 26, 1997, as LER 315/97-002-00 is being retracted.
3151997003 | Cook 1, Cook 2 | 02/05/1997 | 03/31/1997 | 9704070093 | <strong>Condition Outside the Design Basis Due to Potential Safety Injection Pump Runout</strong><br /><i>Abstract:&nbsp;</i>On February 5, 1997, with Unit 1 at 96.7 percent Rated Thermal Power and Unit 2 at 99.8 percent Rated Thermal Power, preliminary information was received from Westinghouse that indicated that the Safety Injection pumps could potentially experience runout conditions if the accumulator fill line were open during a large break LOCA demand. An ENS notification was made under 10CFR50.72(b)(1)(ii)(B), to report a condition outside the design basis at that time. <br /><br /> Cook Technical Specification 4.5.2.h states that total Safety Injection system flow shall not exceed 700 gpm with a single pump running and the minimum flow valve open. If only one safety Injection pump is providing flow to all four injection lines while the accumulator fill line is fully open and the minimum flow valve is open, which may occur during the injection phase of a large break LOCA towards the end of blowdown, the runout limit may be exceeded. By letter dated February 21, 1997, Westinghouse has confirmed, by model, that the pumps will run out to between 708 and 720 gpm, dependent on initial conditions. <br /><br /> The flowpath created by opening the accumulator fill line had not been previously identified as affecting the emergency core cooling system analysis and therefore had not been adequately addressed in the analysis. <br /><br /> This event was evaluated against the analyses for large break LOCA, small break LOCA, containment and the sump recirculation flow requirements, and found to have no safety significance.
3151997004 | Cook 1 | 02/28/1997 | 04/02/1997 | 9704090128 | <strong>Main Steam Valve Exceeds Allowable Lift Setpoint Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On February 28,1997 with Unit 1 in Model at 55 percent Rated Thermal Power, one Main Steam Safety Valve (MSSV) was found to exceed its allowable setpoint as defined in Technical Specification 3.7.1.1. 1-SV-2A-3 was found to lift at 1112 psig, 5 psi above the maximum allowed by the Technical Specification. <br /><br /> This event is therefore reportable under the provisions of 10CFR50.73(a)(2)(i)(B), as operation prohibited by plant Technical Specifications. The cause of the event is attributed to setpoint drift. The valve was removed and disassembled for inspection. The inspection did not reveal any evidence of a different cause. The setpoint for the valve was adjusted to within Technical Specification limits prior to completion of testing. <br /><br /> The Steam Generator system has a total of 20 MSSVs, with 5 valves per Steam Generator. Even though the setpoint for one valve was out of tolerance, the valve was capable of fully opening, and the overpressure protection capability was maintained. safety of the public.
3151997005 | Cook 1 | 03/13/1997 | 10/23/1997 | 9710300123 | <strong>Reactor Coolant Pump Fire Protection Inoperable For Extended Period Without Compensatory Actions Due to Improperly Fabricated Gasket In Spay Header Line</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1997, with Unit 1 in cold shutdown, it was discovered that gaskets in the Fire Protection water spray system for the #13 Reactor Coolant Pump (RCP) had not been properly fabricated prior to installation during the 1995 refueling outage. The improper configuration of the gaskets rendered the Fire Protection system for the #13 RCP inoperable from the time of installation, without compensatory actions being taken. This event is reportable under 10CFR50.73(a)(2)(i)(B), as operation prohibited by Technical Specifications. Although the Fire Protection requirements were removed from the Technical Specifications in March of 1996, at the time the gaskets were installed the Fire Protection Technical Specifications were still in effect. <br /><br /> The root cause of this event is personnel error. The personnel involved did not properly incorporate into their actions the information contained in the Job Order Activity regarding fabrication of the gaskets, and did not perform an adequate part serviceability inspection. To restore the system to operable status, the old gasket material was removed and new gaskets were installed. Pre-fabricated gaskets will be stocked to prevent this from occurring in the future. <br /><br /> This condition has been evaluated, and it has been concluded that the defense-in-depth fire protection for this area adequately protected the fire safety of the plant. Therefore, this event did not constitute a significant hazard to the health and safety of the public.
3151997006 | Cook 1, Cook 2 | 03/27/1997 | 05/30/1997 | 9706050294 | <strong>Equipment in Containment Rendered Inoperable Due to Cracked Floodup Tubes</strong><br /><i>Abstract:&nbsp;</i>This LER revision is being submitted to provide additional information regarding the safety significance and the root cause determination for cracked floodup tubes (FUTS) found in Cook Units 1 and 2. <br /><br /> During an inspection of floodup tubes for moisture intrusion, 3 FUTS with thru wall defects were identified. As a result, proactive measures were taken to inspect the remaining Unit 1 FUTS. This resulted in the identification of six additional thru wall defects in Unit 1. As a result, Unit 2 FUTs were inspected, and 2 cracked tubes were found. Of the 11 total damaged tubes, Unit 1 contained 7 FUTS and Unit 2 contained 1 FUT with an associated circuit that is needed for accident mitigation or post accident monitoring. On March 23 the Unit 2 condition was reported under 10CFR50.72(b)(1)(ii). On March 27 Unit 1 condition was reported under 10CFR50.72(b)(2)(i). ENS notifications were made for both. <br /><br /> The damage has been attributed to work practices that resulted in two different types of failures--material stress cracks and random arc strikes, most probably early in plant life. All damaged Unit 1 EQ FUTS have been replaced and both Unit 2 tubes have been replaced. To prevent the cracks due to installation practices from reoccurring, the Cook Plant FUT Installation Work Instructions will be modified to contain additional guidance. Welding practices have been sufficiently enhanced since the early portion of the plant life to preclude arc strikes on FUTS. Inspections of the FUTS for damage will also be performed at the beginning and the end of the refueling outages until assurance is reached that no further problems were found. <br /><br /> Postulated failures that could result from the cracked floodup tubes were evaluated and found not to present a significant risk wi regard to the protection of the public health and safety.
3151997007 | Cook 1 | 04/05/1997 | 02/13/1998 | 9802270048 | <strong>Technical Specification Surveillance Requirement 4.7.2.1 Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1997, it was determined that the Unit 1 Steam Generator (SG) pressure indications in the control room had been isolated since March 29, 1997. Personnel had been using these indications to verify compliance with Technical Specification Surveillance 4.7.2.1. This Technical Specification requires that the pressure in both the primary and secondary side of the SGs be verified as less than 200 psig once per hour when either the primary or secondary coolant in the SG is less than 70 degrees Fahrenheit (degrees F). As the surveillance requirements were not met, this event is reportable under 10CFR50.73(a)(2)(i)(B), as operation prohibited by Technical Specifications. <br /><br /> The root cause of this event was deficient procedures used in the processes of isolating the SGs to establish refueling containment integrity and initiate the Technical Specification surveillance. To prevent recurrence, the SG isolation methodology contained in the refueling integrity surveillance has been revised, as has the daily surveillance for verification of SG pressures. The daily surveillance now verifies that the SG secondary side pressure instruments are unisolated and available prior to utilization in the surveillance. <br /><br /> During the time period the instrument was isolated, it has been determined that at no time was the SG pressure greater than 200 psig concurrent with either the primary or secondary temperature being less than 70 degrees F; therefore, this event had no safety significance.
3151997008 | Cook 1 | 04/04/1997 | 05/05/1997 | 9705080291 | <strong>Cycle 15 Operation of Steam Generators Outside Technical Specification Tube Degradation Acceptance Criteria Due to Inadequate Analysis of Eddy Current Data</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1997, with Unit 1 in Mode 6, it was determined that a number of the hot leg tubesheet region Steam Generator (SG) tubes with indications had been placed back into service at the end of the 1995 Cycle 15 refueling outage after performing SG tube inspections and tube repairs. During the 1997 inspection a large number of tubes in the hot leg tubesheet region of each SG were identified as degraded. Re-analysis of the Cecco-5 probe data from the previous SG inspection of the largest tubesheet crevice indications determined that these indications were also present in 1995, implying that tubes with defects had been placed back in service, and not repaired in accordance with Technical Specification 4.4.5.4.a.6 and 4.4.5.4.b. In accordance with 10CFR50.73 (a)(2)(i)(B), this event is reportable as operation prohibited by the plant's Technical Specifications. <br /><br /> The cause of this event is attributed to inadequate analysis of the Cecco-5 eddy current data in 1995. For the 1997 outage, EPRI qualified bobbin coil and rotating coil inspection techniques and an EPRI qualified data analyst were used. For future inspections, use of a qualified process with better data analysis capability, use of highly trained and qualified analysts, and independent data review is expected to significantly minimize or preclude occurrence of a similar event. <br /><br /> Eddy current tube inspections and a bounding tube pressure test program at the end of Cycle 15 determined that the tubes with the largest defects met the draft RegGuide 1.121 for leakage at Main Seam Line break conditions and for burst at 3 times the normal operating pressure differential. Therefore, there was no hazard to the health and safety of the public during Cycle 15.
3151997009 | Cook 1, Cook 2 | 04/15/1997 | 05/15/1997 | 9705220415 | <strong>Radiation Monitor Particulate Channels Inoperable Due to Use of Incorrect Calibration Constant</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1997, it was discovered that the calibration constant for the particulate channels of the Eberline radiation monitors were incorrect. A calibration constant value of 1.17E-05 [Symbol omitted]Ci/cpm had been used instead of the correct value of 4.66 E-05 [Symbol omitted]Ci/cpm. The calibration constant for the Eberline particulate channel is based on what is referred to as the "divide by circuitry". The "divide by circuitry" converts detector pulses to units of activity. A channel's calibration constant is adjusted depending on which "divide by circuitry" is used. When the procedure was developed in 1990 for making the "divide by circuitry" adjustment it was incorrect. The cause for this event is personnel error. <br /><br /> This event is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the power plant being in a condition that was outside the design basis of the plant, 10 CFR 50.73(a)(2)(v)(C) as a condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material, and 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's technical specifications. <br /><br /> Immediately upon confirming the error, the technical specification action statement for those channels with technical specifications were entered, the parameter file log sheets were revised to the correct value of 4.66 E-05 [Symbol omitted]Ci/cpm, and the channel parameter files were revised to reflect the new calibration constant. Based on current requirements for the review and verification of information, no further actions are being taken. Additionally, based on other required monitors being operable and the ability to use the trending function of the particulate monitors this event did not represent a significant risk to the health and safety of the public.
3151997010 | Cook 1, Cook 2 | 08/08/1997 | 12/31/1997 | 9801070234 | <strong>Unit Operation with Lake Temperature In Excess of Design Basis Value Results in Condition Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1997, with Units 1 and 2 at 100 percent Rated Thermal Power, as a result of questions posed by the NRC AE Design Inspection team, it was determined that both units had operated outside the design basis of 76 Degrees Fahrenheit for lake water temperature. An ENS notification was made at 0934 hours the same day under under 10CFR50.72(b)(1)(ii)(B), as a condition outside the design basis. This report is made in accordance with 10CFR50.73(a)(2)(ii), as a condition outside the design basis, and an unanalyzed condition. <br /><br /> The root cause of this event was the failure to recognize a UFSAR value as a design basis parameter and to recognize interrelationships between a UFSAR value and other design aspects. Process changes have been implemented which require that changes to design basis information be handled via the design change process, a corporate directive and policy were written to provide direction on design basis, and additional training on design basis has been provided to those employees involved in handling such information. Restrictions have been placed on plant operation such that the plant will not be operated with lake water temperatures above 76 Degrees Fahrenheit. This restriction will remain in effect until all analyses and 10CFR50.59 safety evaluations are complete. <br /><br /> Analysis of this event has been performed, taking into account the effects of the elevated service water temperature on the safety related systems to which it provides cooling. It has been determined that the event did not result in any threat to the health or safety of the public.
3151997014 | Cook 1, Cook 2 | 08/29/1997 | 12/31/1997 | 9801070226 | <strong>Potential for Operation in Unanalyzed Condition Due to Postulated Elevated Control Room Temperatures</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1997, with Units 1 and 2 at 100 percent Rated Thermal Power, as a result of questions posed by the NRC AE Design Inspection team, it was determined that during August, 1987, both units operated in an unanalyzed condition for Control Room equipment operability due to postulated high room temperatures. An ENS notification was made on August 29, 1997 at 1412 hours EDT under the provisions of 10CFR50.72(b)(1)(ii)(A), for any condition during operation that results in the plant being in an unanalyzed condition. This LER is therefore submitted in accordance with 10CFR50.73(a)(2)(ii)(A). This LER is directly related to, and can be considered a sub-issue to, the condition reported in LER 315/97-010-02. <br /><br /> The root cause of this condition was the failure to realize the interrelationship between a UFSAR value and other design aspects. Process changes have been implemented which require that changes to design basis information be handled via the design change process, A corporate directive and policy were written to provide direction on design basis, and additional training on design basis has been provided to those employees involved in handling such information. Restrictions have been placed on plant operation such that the plant will not be operated with lake water temperatures above 76 Degrees Fahrenheit. This restriction will remain in effect until all analyses and 10CFR50.59 safety evaluations are complete. <br /><br /> Analysis of this event has been performed, taking into account the potential effects of elevated temperature on the Control Room equipment. It has been determined that the event did not result in any threat to the health or safety of the public.
3151997015 | Cook 1 | 09/02/1997 | 11/03/1997 | 9711100082 | <strong>LER Retraction: 609' Drumming Room Does Not Meet Waste Handling and Storage Requirements</strong><br /><i>Abstract:&nbsp;</i>This submittal is to retract the interim licensee event report (LER) 315/97-015-00 submitted on 10/02/97. The interim LER reported that the 609' drumming room did not meet the final safety analysis report (FSAR) criterion for the monitoring of fuel and waste storage from Section 11.3 of the FSAR. On October 1, 1997, following further review of FSAR Section 11.3, it was determined that the basis of the requirements applied to radioactive waste treatment areas. Treatment of waste is to ensure that the requirements in 10 CFR 61.56, such as providing structural stability and eliminating liquids to less than 1%, are met. At Cook Nuclear Plant, only one area of the plant is used for radioactive waste treatment, and that is the 587' drumming room. The 609' drumming room is used for waste handling and storage, that is, segregation by-hand of dry active waste and storage, not treatment. Based on the October 1, 1997 review the condition reported on September 2, 1997 and described in the interim LER is being retracted.
3151997016 | Cook 1, Cook 2 | 09/12/1997 | 11/14/1997 | 9711200167 | <strong>Operation of the Residual Heat Removal System Contrary to the UFSAR Could Result in a Condition That Would Prevent the Fulfillment of the Safety Function of a System</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1997, with Units 1 and 2 in Mode 5, it was discovered that current operating procedures for the Residual Heat Removal (RHR) System did not prevent the operation of both RHR pumps when the Reactor Coolant System (RCS) is open to atmosphere. This is contrary to Updated Final Safety Analysis Report (UFSAR) Section 9.3.3 which states, "Only one residual heat removal (RHR) pump will be operated when the reactor coolant system is open to the atmosphere to prevent damaging both pumps in the unlikely event that suction should be lost". This event is being reported in accordance with 10 CFR 50.73 (a)(2)(v) as a condition that potentially could have prevented the fulfillment of the safety function of a structure or system. <br /><br /> The cause of not including all of the UFSAR requirements into the RHR procedure could not be determined. Inadequate understanding of the UFSAR and inadequate safety screenings prevented this issue from being identified sooner. All applicable procedures have been revised to include the restriction that only one RHR pump be operated when the RCS is open to atmosphere. <br /><br /> Based on vendor manual information for the pump and additional information from the UFSAR, if the RCS level is greater than half loop, then the pump suction lines are completely filled, with enough Net Positive Suction Head to preclude the formation of air pockets and enough level exists above the suction source to prevent vortexing. Therefore, this condition had no significant safety consequences for the plant or the health and safety of the public.
3151997017 | Cook 1 | 09/08/1997 | 08/17/2001 | ML01234012 | <strong>Condition Outside Design Basis Results in Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1997, at 2000 hours, with Unit 1 at 74 percent Rated Thermal Power, it was discovered that under certain scenarios the volume of water resident in the active sump of the containment would not have been adequate to support Jong term Emergency Core Cooling System (EGGS) or Containment Spray (CTS) pump operation during the recirculation phase of a loss-of-coolant accident (LOCA). <br /><br /> This was determined to be reportable under 10CFR50.72(b)(1)(ii)(B), as a condition outside the design basis. A Technical Specification required shutdown was undertaken, and was reported under 10CFR50.72(b)(1)(i)(A). An LER was submitted in accordance with 10CFR50.73(a)(2)(ii) and 10CFR50.73(a)(2)(i)(A). On September 10, 1997 Unit 1 entered Mode 5, cold shutdown. <br /><br /> The root cause of this event was determined to be a breakdown in the design control process. This process breakdown resulted in engineering reviews that did not evaluate the impact of flow diversions into the inactive sump volumes of the containment. <br /><br /> This revision incorporates information from the root cause investigation and replaces Licensee Event Report (LER) 50-31511997-017-01 in its entirety.
3151997018 | Cook 1, Cook 2 | 09/05/1997 | 11/14/1997 | 9711200179 | <strong>Failure to Maintain 1/4 Inch Particulate Retention Requirement for the Containment Recirculation Sump Results in a Condition Outside the Design Bases</strong><br /><i>Abstract:&nbsp;</i>While reviewing findings relative to containment recirculation sump modifications and requirements, the containment system engineer identified a historical problem on Unit 1 and Unit 2 recirculation sumps from 1978 until 1996 in Unit 2 and 1997 in Unit 1. In 1978 five 3/4 inch diameter holes were installed in the upper roof of the recirculation sump under design change 12-RFC-2361. Under the same design change, the 1/4 inch particle retention boundary was moved from the lower chamber of the recirculation sump back to the recirculation sump inlet area. When this 1/4 inch retention element was moved several sump inlet locations, including the five holes, were left unprotected for 1/4 inch particle retention. The NRC was notified of this event on September 5, 1997 at 0921 hours. The NRC notification was made under 10 CFR 50.72 (b)(1)(ii)(B) as a condition outside the design basis of the plant. This event is being reported under 10 CFR 50.73(a)(2)(ii) as a condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. <br /><br /> The cause for this event was that the design change that moved the 1/4 inch particle retention boundary was not technically complete in that it did not address the 1/4 inch particle retention requirement during design and/or installation. <br /><br /> Based on the low probability of material entering the sump and an analysis of material which had the highest probability of entering the sump, it was concluded that the containment recirculation sump could have performed its intended function with the identified deficiencies. Therefore, this event did not present a risk to the health and safety of the public.
3151997019 | Cook 1, Cook 2 | 09/11/1997 | 11/17/1997 | 9711250109 | <strong>Operation Contrary to the Design Bases with Residual Heat Removal Suction Valves Automatic Closure Interlock Defeated In Modes 4 and 5</strong><br /><i>Abstract:&nbsp;</i>In September 1997, during the NRC Architect and Engineering Design Inspection, a discrepancy was identified between the Updated Final Safety Analysis Report (UFSAR) and an Operations department procedure. The procedure also conflicted with Technical Specification (T/S) requirements. This condition was reported as a notification under 10 CFR 50.72(b)(2)(i), for an unanalyzed condition on September 11, 1997, and as a condition outside the design basis of the plant. This update is submitted to provide the cause and safety significance of the event. <br /><br /> The event has been attributed to an inadequate safety review performed at the time the procedure change was made in 1980. Additionally, a procedure change was used to effectively accomplish a design change to the plant, further reducing the chances, under the processes in existence at that time, of identifying the impact on the design basis. A T/S amendment has been formally requested to remove the surveillance related to automatic valve closure. The change was requested on September 19, 1997, via our letter designated AEP:NRC:1278. A design change will also be processed to document the change appropriately under our design change process. <br /><br /> The procedure steps involved were intended to prevent inadvertent auto-closure of the valves which would result in a loss of Residual Heat Removal (RHR) suction during shutdown cooling operation. The procedure accomplishes this by removing power from the valves when the valves are opened to the Reactor Coolant System (RCS). The RCS and the RHR systems were protected from over-pressurization by the Low Temperature Over-Pressure Protection (LTOP) equipment, at all times that the original RHR suction valve interlock was designed to protect the RHR system. Therefore, this condition did not significantly impact the health or safety of the public or pose a threat to plant safety.
3151997021 | Cook 1, Cook 2 | 09/10/1997 | 11/14/1997 | 9711190306 | <strong>Potential Loss of All Medium and High Head Injection Due to Single Failure Could Result in a Condition That Would Prevent the Fulfillment of the Safety Function of a System</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1997, with Units 1 and 2 in Mode 5, it was determined that a single active failure during an accident while performing switchover of the Emergency Core Cooling System (ECCS) pumps from the Refueling Water Storage Tank (RWST) to the recirculation sump could result in loss of all high and medium head injection. This was determined to be reportable as an unanalyzed condition under 10CFR50.72(b)(2)(i), and as a condition that could have prevented the fulfillment of a safety function under 10CFR50.72(b)(2)(iii). An ENS notification was made at 1919 hours the same day. This report is submitted in accordance with 10CFR50.73(a)(2)(ii) and (a)(2)(v). <br /><br /> The root cause of this event was personnel error. Significant improvements have been made to the review process for Emergency Operating Procedures (EOPs) since 1992 when the error occurred. Contributing to this event was the failure to recognize that the definition of a single active failure included failure of a pump to run once it had already started. The EOP which sequences the steps for switchover has been revised to preclude the situation where a single active failure would cause redundant equipment from being impacted. A formal policy and a directive on design bases and single failure criteria have been developed. The directive provides specific direction on the definition and use of the single failure criteria. <br /><br /> A Probabilistic Risk Assessment was performed to determine the failure probability of an RHR pump to continue to run. The failure probability did not result in a noticeable increase in core damage frequency. This condition was therefore concluded to have a low safety significance, and not to represent a threat to the health or safety of the public.
3151997022 | Cook 1, Cook 2 | 09/11/1997 | 10/31/1997 | 9711050221 | <strong>Failure to Comply with USAS B31.1 Power Piping Code Due to Oversight in Valve Control Requirements Results in Condition That Could Have Prevented the Fulfillment of a Safety Function of a System</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1997, with Units 1 and 2 in cold shutdown, it was determined that conditions had not been properly established in the Component Cooling Water (CCW) system to meet plant piping design code requirements. It was determined that this event was reportable under 10 CFR 50.72(b)(2)(iii)(C) and (D), as a condition that alone could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material and mitigate the consequences of an accident. An ENS notification was made at 1956 hours on September 11, 1997. An interim LER was submitted on October 13, 1997 under 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). <br /><br /> The piping design code at the Cook Plant is USAS B31.1 Power Piping Code, 1967 edition. Code requirement B31.1 states that an intercepting stop valve cannot be located between the source of pressure and the pressure relief device credited for protecting the pipe. Contrary to the code requirement there were manual valves between the Reactor Coolant Pump (RCP) thermal barrier cooling coil and the safety relief valve on the CCW surge tank that were not controlled in accordance with or exempted from USAS B31.1, 1967 edition. <br /><br /> To correct this condition the intercepting stop valves have been place under procedural control such that the valves are sealed open during system operation, thus ensuring the safety valve on the CCW Surge Tank will provide over pressure protection for the CCW System Piping during a rupture of an RCP thermal barrier cooling coil. Based on normal system operation and controls, this event was determined to have negligible safety impact.
3151997023 | Cook 1, Cook 2 | 09/16/1997 | 11/14/1997 | 9711180190 | <strong>Design Change Introduces Possibility of Single Failure Which Could Result in Loss of Both Trains of ESF Ventilation Due to Failure to Identify Adverse Impact During Design Review</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1997, with Units 1 and 2 in Mode 5, it was determined that a design change to the bypass dampers for the Engineered Safeguards Features (ESF) ventilation system installed between December 1996, and August, 1997 introduced the possibility of a single failure which could result in the loss of both trains of the ESF ventilation system. The loss of the 85 psig air header without concurrent loss of the 20 psig air header would result in the ESF ventilation trains being unable to meet their design function. On September 16, 1997, this event was reported via ENS under 10CFR50.72(b)(2)(i), as an event found while the reactor was shutdown that resulted in an unanalyzed condition. This LER is therefore submitted in accordance with 10CFR50.73(a)(2)(ii), as an event found while the reactor was shutdown that resulted in an unanalyzed condition, and a condition outside the design bases. <br /><br /> The root cause of the event is the failure of the design change process to identify the potential adverse impact on the ESF ventilation system created by the modification of the control air supply to the bypass dampers. Installation of a supply to the inlet damper actuators from the 85 psig header via a pressure reducing valve was completed on November 5, 1997. This modification placed both the inlet and bypass dampers on the same supply header. The Design Change Reference Guide will be revised to explicitly require the consideration of the effects of a proposed change of the air system on a "header by header" basis and the analysis of individual source failures. <br /><br /> Based on the low probability of the series of events necessary to prevent the ESF ventilation trains from performing their design functions, and the Probabilistic Risk Assessment results, it has been concluded that this condition had low safety significance, and did not endanger the health or safety of the public at any time.
3151997024 | Cook 1, Cook 2 | 09/17/1997 | 04/30/1998 | 9805050318 | <strong>Material Discovered in Containment Degrades Containment Recirculation Sump and Results in Condition Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1997, a fibrous material, known as Fiberfrax, was identified in an electrical cable tray inside the Unit 2 containment. An investigation was initiated to determine the scope and magnitude of this condition. On September 17, 1997, with Units 1 and 2 in cold shutdown, it was determined that Fiberfrax was present in both containments in enough quantity to potentially cause excessive blockage of the containment recirculation sump screen during the recirculation phase of a Loss of Coolant Accident and render the sump inoperable. An ENS notification was made at 1629 hours on September 17, 1997, under 10CFR50.72(b)(2)(i), as a condition which was found while the reactor was shutdown, which if it had been found while the reactor was operating, would have resulted in the nuclear power plant being outside the design basis. As part of the investigation, reviews were conducted of industry information related to containment sump strainer blockage, and plant insulation specifications. Walkdowns were conducted of both containments and other potential material threats to blockage of the recirculation sump were identified and dispositioned. <br /><br /> The root cause of this condition has been attributed to inadequate specifications and procedures which did not preclude or strictly control these types of materials. The materials have either been removed from the containments, or have been evaluated and determined to not constitute a substantial threat to the recirculation sump. Additionally, the condition of containment coatings was reviewed and repair of some coatings has been undertaken. Specifications and procedures are being revised and /or developed to preclude or strictly control materials inside containment which could block the recirculation sump. <br /><br /> Analysis using models for debris generation and transport has been completed. The results of that analysis will be provided to the NRC separately as it contains proprietary information. it is expected that the information will be provided to the NRC prior to, or at, the May 20, 1998, enforcement conference.
3151997025 | Cook 1 | 09/23/1997 | 10/23/1997 | 9710290113 | <strong>Unexpected ESF Actuation During Filling of Steam Generators for Wet Lay-up</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1997, at 1510 hours with Unit 1 in Mode 5 at approximately 140 degrees Fahrenheit and 290 psig, an unplanned ESF actuation occurred. An ENS notification was made per paragraph 10CFR50.72(b)(2)(ii) at 1739 hours on September 23, 1997. This event is reportable in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in the automatic actuation of Engineered Safety Features (ESF). <br /><br /> While filling the Unit 1 Steam Generators (SG) to place them in wet lay-up, a low low level alarm was received on two out of four SGs. This low level made up the logic to start the Turbine Driven Auxiliary Feedwater Pump (TDAFP) and open the associated feedwater valves. <br /><br /> The cause of the actuation was a small expected oscillation in the SG levels during the filling operation, which, combined with the 1% deadband of the associated bistables, resulted in the ESF actuation. This situation will be corrected by increasing the deadband on the low low level bistable from 1% to 3%. <br /><br /> The event has been evaluated and determined to have no safety significance, nor did it pose a threat to the health or safety of the public.
3151997026 | Cook 1, Cook 2 | 09/25/1997 | 11/17/1997 | 9712010357 | <strong>Potential for Overpressurization of the Control Air Headers Determined to be Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1997, with Units 1 and 2 in Mode 5, it was recognized that due to a lack of overpressure protection on the 85, 50, or 20 psig control air headers, if an air regulator failed open resulting in an overpressurization of a control air header, there was the potential for common mode failure of both trains of safety related equipment. The potential for this event was reported in accordance with 10 CFR 50.72(b)(2)(i) as a condition which was found while the reactor was shutdown, which if found while the reactor was operating, would have resulted in the nuclear plant being in an unanalyzed condition. <br /><br /> The lack of overpressure protection on the control air headers due to a regulator failing open was not identified as a mechanism that could overpressurize the low pressure headers. As a result, single failure of a non-safety related component affecting both trains of safety related equipment was not identified. Redundant safety related relief valves have been installed on the 20, 50, and 85 psig control air headers. In addition, the current design change process addresses the requirement to ensure that single failure criteria has been met. <br /><br /> An evaluation was performed to determine what the effect of an overpressurization of the control air headers would have been. This evaluation determined that there would have been no significant effects for the 85 and 50 psig headers. Overpressurization of the 20 psig header could have resulted in the degradation of the RHR system and the partial opening of the unit 2 Steam Generator (SG) Power Operated Relief Valves (PORVs) for the duration of the overpressure event. Due to a single failure being identified that could have potentially resulted in the degradation of both trains of RHR this event may have been significant.
3151997027 | Cook 1, Cook 2 | 10/28/1997 | 01/16/1998 | 9801230308 | <strong>Westinghouse Integral Fuel Burnable Absorber (IFBA) Fuel Rods</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, with Unit 1 in Mode 5 and Unit 2 in Mode 6, it was determined that both units had the potential to be outside of their design basis and possibly in non-compliance with 10 CFR 50.46(b)(2). This is a generic issue applicable to Westinghouse fuel rods containing integral fuel burnable absorber (IFBA). It was determined that this was reportable under 10CFR50.72(b)(2)(i) as an event found during shutdown that potentially resulted in a degraded principle safety barrier and an ENS notification was made at 1830 hours on October 28, 1997. An interim LER was submitted on November 24, 1997. This LER is being submitted under 10CFR50.73(a)(2)(ii)(B) as a condition potentially outside of the design basis of the plant. <br /><br /> The licensee was informed by Westinghouse, on October 28, 1997, that in the process of developing new fuel rod cladding corrosion and rod internal pressure models it was determined that these new models showed a decrease in rod internal pressure margin. This decrease in margin has the potential to place plants in a condition that is outside of their design basis with respect to pellet-to-clad gap re-opening. Additionally, should pellet-to-clad gap re-opening occur there is a potential for certain plants to possibly be in non-compliance with the 17 percent oxidation criteria of 10CFR50.46. <br /><br /> Subsequent calculations have shown compliance with 10CFR50.46 for the current operating cycles, Unit 1 Cycle 16 and Unit 2 Cycle 12. Additional calculations show that Unit 1 will be within its design basis with respect to pellet-to-clad gap re-opening throughout Cycle 16 and Unit 2 will be within its design basis for a minimum of 10,680 MWD/MTU (approximately 257 EFPD) for Cycle 12. For the possible operation outside the design basis for Unit 2 Cycle 12 a justification for continued operation has been included in the Reload Safety Evaluation for Unit 2 Cycle 12 which covers operation to the end of the cycle.
3151997028 | Cook 1, Cook 2 | 11/07/1997 | 12/08/1997 | 9712120367 | <strong>Failure to Comply with 10CFR50, Appendix R Requirements Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>10 CFR 50, Appendix R, Section III G.2.(b) requires a twenty foot separation between trains with no intervening combustible materials with fire detection and suppression installed. At Cook Nuclear Plant, fire stops were being used to prevent the possible spread of fire across the twenty foot separation space at two locations in the Auxiliary Building (el. 587' and 609') where there are intervening combustibles (open cable trays) inside the twenty foot separation space. However, an exemption to 10 CFR 50, Appendix R, Section III G.2.(b) had not been requested. <br /><br /> Our configuration had been described to the NRC in submittals dating back to 1983. However, the deviation from Appendix R described above was not specifically noted in applicable Appendix R SERs. On May 21, 1997, we submitted a letter to the NRC which responded to NRC questions dated March 26, 1997, regarding this configuration, and provided our basis for why we did not believe an exemption to Appendix R was necessary. During a conversation with the NRR staff on November 6, 1997, we were informed that a specific exemption to Appendix R is required for this deviation or the intervening combustibles must be eliminated. <br /><br /> Because our configuration differs from the requirements of 10 CFR 50, Appendix R, Section III G.2.(b), it is being reported as a condition outside the plant's design bases. Generic Letter (GL) 92-08 indicated that Thermo-Lag was a combustible material. The fire watch established for these locations, as a result of GL 92-08, was released on December 30, 1996, after the Thermo-Lag wrap had been removed. The Appendix R Safe Shutdown revalidation effort evaluated the use of fire stops again. A fire watch was re-established on January 24, 1997. The fire watches will remain in place until resolution of this issue is obtained.
3161997001 | Cook 2 | 03/11/1997 | 04/10/1997 | 9704160170 | <strong>Unit Trip Due to Low Level Coincident with Steam Flow/Feed Flow Mismatch Due to Controller Failure</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1997 at 1056 hours with Unit 2 at 100 percent Rated Thermal Power, an automatic reactor trip signal was initiated by the Reactor Protection System (RPS). The trip signal resulted from a #21 Steam Generator (SG) low level coincident with a Steam Flow/Feed Flow mismatch. An unplanned ESF actuation consisting of a second automatic start of the Turbine Driven Auxiliary Feedwater Pump (TDAFP) also occurred. This event is reportable in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in the automatic actuation of Engineered Safety Features (ESF), including the Reactor Protection System (RPS). <br /><br /> This event was caused by the failure of the controller for 2-FRV-210, due to static discharge. The controller for 2-FRV-210, a Taylor MOD 30, was replaced with a newly configured controller. Corrective Actions were completed for all Unit 2 Taylor controllers prior to restart. <br /><br /> No safety systems were out of service prior to the trip. After the reactor trip, all safety systems operated as designed. Normal off-site power was available and an automatic transfer to this source occurred after the Main Generator trip. This event was determined to have no safety significance, and to have no potential or actual effect on the health and safety of the public.
3161997002 | Cook 2 | 05/08/1997 | 06/09/1997 | 9706170121 | <strong>Unit Shutdown in Accordance with Technical Specifications for Electrical Power Systems - AC Sources</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1997, at 1509 hours, Unit 2 commenced a shutdown in accordance with Technical Specification 3.8.1.1 for Electrical Power Systems - AC Sources. This shutdown resulted from the inability to return the 2 AB Emergency Diesel Generator (EDG) to service within the 72 hours allowed by the Technical Specification LCO, due to a failed voltage regulator. A conservative decision was made to suspend EDG troubleshooting and to commence the shutdown at hour 60 of the LCO to ensure adequate time for an orderly, controlled shutdown to take place. EDG troubleshooting was restarted once the unit was placed in Mode 5. This report is made in accordance with 10CFR50.73(a)(2)(i)(A), which requires an LER to be submitted upon completion of a Technical Specification shutdown. <br /><br /> The root cause of this event is personnel error. The personnel performing the work on the 2 AB EDG voltage regulator failed to properly tighten the electrical connections (screws) to the circuit boards, and did not recheck the electrical connections prior to calling the work complete. Appropriate administrative actions have been taken with the individuals involved. Actions are being taken to prevent recurrence by strengthening the self checking program and strengthening the understanding of the responsibilities of members of multi-person work teams. <br /><br /> At the time of the event all other safety related equipment was operable, except for a train associated containment air recirculation fan that was removed for planned work. The shutdown was completed without incident. This event has been evaluated and determined to have no safety significance.
3161997003 | Cook 2 | 08/26/1997 | 01/23/1998 | 9801290073 | <strong>Performance of Dual Train Component Cooling Water Outage During Unit 2 1996 Refueling Outage Resulted in Condition Outside Plant's Design Basis</strong><br /><i>Abstract:&nbsp;</i>During the Unit 2 1996 refueling outage a dual train component cooling water (CCW) outage was scheduled and performed. In performance of the dual train CCW outage, manual operator actions were credited for restoration of the Unit 2 spent fuel pool (SFP) cooling system, should the Unit 1 SFP cooling train become unavailable, to maintain the SFP within its design basis. Following evaluation of the shutdown risk review performed at the time, the crediting of these manual actions was not adequate and created the possibility of an unreviewed safety question. Based on this, it was determined that this event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B), as a condition that was outside the design basis of the plant. <br /><br /> The Unit 2 1996 refueling outage planning and scheduling review activity performed in accordance with plant procedures, overlooked the reviews necessary to fully credit operator actions and the performance of an unreviewed safety question determination to support the manual actions. The outage review process has been revised to preclude recurrence. <br /><br /> The contingency actions for recovering spent fuel pool cooling during the Unit 2 1996 refueling outage were such that the plant was capable of restoring Unit 2 CCW within 1.5 hours, assuming no errors or environmental affects. Greater than 3 hours was available before threatening the SFP design basis. The actual dual train CCW outage configuration existed for only 8 hours and 1 minute. In addition, draining of the CCW system did not occur, thus ensuring an uncomplicated restoration. Based on this, there was no risk to the health and safety of the public.
3161997004 | Cook 2 | 08/26/1997 | 01/22/1998 | 9801280276 | <strong>LER Retraction - Analysis Demonstrates Design Basis Impact of Inadequate Refueling Outage Safety Evaluation was Negligible</strong><br /><i>Abstract:&nbsp;</i>The basis for this revision is to provide additional information relative to the retraction of this report. On August 26, 1997, with Unit 2 at 100 percent Rated Thermal Power, it was determined that the unit had potentially operated outside the design basis during the Unit 2 1996 refueling outage relative to the spent fuel pool (SFP) heat exchanger's component cooling water (CCW) inlet design temperature. It was determined that this event was reportable under 10 CFR 50.72(b)(1)(ii)(B) as a condition outside the design basis, and an ENS notification was made at 1533 hours on August 26, 1997. An interim LER was submitted pursuant to 10 CFR 50.73(a)(2)(ii) as a condition outside the design basis on September 22, 1997. As a result of the subsequent investigation and analysis into this event, it has been concluded that the unreviewed safety question determination performed in support of the Unit 2 1996 refueling outage full core offload was conservative with respect to the required core offload period; however, the SFP temperature limit could not be demonstrated at the maximum design CCW temperature. Subsequent analysis using a more realistic core offload period has demonstrated that the SFP design requirement would have been met at a maximum CCW temperature of 95 degrees Fahrenheit noted in the UFSAR. Based on this, the LER Retraction 316/97-004-01. submitted on November 17, 1997, is being revised to reflect this additional information. The analysis to support this LER revision is HI-971612, "Thermal Hydraulic Analysis for D.C. Cook 1997 Refueling Outages", Revision 0. This analysis bounded the Unit 2 1996 refueling outage conditions and demonstrated that the design basis was maintained.
3161997005 | Cook 2 | 09/08/1997 | 08/17/2001 | ML01235018 | <strong>Condition Outside Design Basis Results in Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1997, at 2000 hours, with Unit 2 at 96 percent Rated Thermal Power, it was discovered that under certain scenarios the volume of water resident in the active sump of the containment would not have been adequate to support long term Emergency Core Cooling System (ECCS) or Containment Spray (CTS) pump operation during the recirculation phase of a loss-of-coolant-accident (LOCA). <br /><br /> This event was determined to be reportable under 10CFR50.72(b)(1)(ii)(B), as a condition outside the design basis. A Technical Specification required shutdown was undertaken, and was reported under 10CFR50.72(b)(1)(i)(A), An LER was submitted in accordance with 10CFR50.73(a)(2)(ii) and 10CFR50.73(a)(2)(i)(A). On September 10, 1997 Unit 2 entered Mode 5, cold shutdown. <br /><br /> The root cause of this event was determined to be a breakdown in the design control process. This process breakdown resulted in engineering reviews that did not evaluate the impact of flow diversions into the inactive sump volumes of the containment. <br /><br /> This revision incorporates information from the root cause investigation and replaces Licensee Event Report (LER) 50- 316/11997-002-01 in its entirety.
3161997006 | Cook 2 | 10/10/1997 | 11/10/1997 | 9711140190 | <strong>Equipment in Containment Rendered Inoperable Due to Faulted Floodup Tubes</strong><br /><i>Abstract:&nbsp;</i>Following a discovery of damaged floodup tubes in March of 1997 (LER 97-006-01), Donald C. Cook Plant personnel committed to perform inspections of floodup tubes during subsequent refueling outages. An inspection of unit 2 floodup tubes conducted during its current refueling outage identified three tubes containing cables connected to safety related components with through wall holes caused by welding activities. On October 10, 1997, the condition was reported under 10CFR50.72 (b)(2)(i). The damage has been attributed to arcing due to welding activity. The time at which the damage occurred cannot be positively determined, but it is believed to have occurred during recent welding activities near the damaged floodup tubes. The damaged tubes will be replaced, and enhancements made to the welding work process will preclude future arcing damage due to welding. Additionally, inspection of the floodup tubes for damage at the beginning and end of refueling outages will be performed. Additionally, for an operating unit, floodup tubes in the vicinity of any hot work performed in the annulus will be inspected daily. Postulated failures that could result from the cracked floodup tubes were evaluated and found not to present a significant risk with regard to the protection of the public health and safety.
3161997007 | Cook 2 | 10/14/1997 | 01/16/1998 | 9801230332 | <strong>Contract Worker Received Exposure in Excess of 10CFR20.2202 Limits</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1997, with Unit 2 in Mode 5, a contract worker (see attachment 1) who alarmed a foot monitor upon exiting the Unit 2 containment was discovered to have "hot particles" in his right shoe. Results of the immediate investigation revealed that when the worker reported for work at Cook he reported having experienced an uptake of mixed fission and activation products at a previous work site, which was confirmed by spectral whole body count. The particles were collected from the worker's shoe and analyzed for activity, which showed primary isotopic activity of Zr-5 and Nb-95. An initial dose estimate for the contract worker is 50.7 rem SDE-ME. A voluntary 24 hour ENS notification was made at 1600 hours EDT on October 15, 1997, under the requirements of 10CFR20.2202, for a shallow dose equivalent to the skin or extremities exceeding 50 rems. An interim LER was submitted on November 14, 1997. This LER is submitted in accordance with 10CFR20.2203(a)(1). Since the contamination did not occur at Cook, the cause could not be determined. It is suspected that the contamination occurred on or before August 13, 1997 and was most likely due to management methods used to control refueling activities. In order to respond to a positive indication of contamination on incoming workers, inprocessing will include two spectral whole body counts if the person alarms a whole body monitoring device. The first will be done in street clothes and the second will be performed in modesty or paper garments to determine if the contamination is internal or external. This exposure did not represent a safety significant event for the Cook Plant. The worker experienced no outward physical effect to his foot. Surveys were performed of the motels where the worker had stayed, his home, and personal effects. None of the surveys provided any positive identification of radioactive contamination. Therefore, the general public was not endangered by this contamination event.
3161997008 | Cook 2 | 10/24/1997 | 11/24/1997 | 9712020137 | <strong>ESF Actuation Due to Failure of Train A Upper Containment Area Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1997 at 0008 hours with Unit 2 in Mode 6, Refueling, an unplanned ESF actuation occurred. A high radiation alarm and high fail signal were generated by the Train A Upper Containment Area Radiation Monitor due to equipment failure. The high radiation alarm resulted in a Containment Ventilation Isolation. The associated isolation valves closed as designed. This event is reportable in accordance with 10 CFR 50.73 (a) (2) (iv) as an event that resulted in the automatic actuation of Engineered Safety Features (ESF). An ENS notification was made per paragraph 10 CFR 50.72 (b) (2) (ii) at 0256 hours on October 24, 1997. <br /><br /> The Train A Upper Containment Area Radiation Monitor generated a high radiation alarm and high fail signal. The reason for the malfunction was caused by the failure of the monitor's detector. The components that could have caused or contributed to the failure have been replaced. The channel was tested and returned to service the same day. <br /><br /> The high radiation alarm was due to component failure. A high radiation condition. implied by this alarm, did not exist. This event posed no threat to the health and safety of the public.
3161997009 | Cook 2 | 11/26/1997 | 12/24/1997 | 9801020028 | <strong>Blockage of Containment Air Recirculation Inlet Line Results in Condition Outside Design Bases</strong><br /><i>Abstract:&nbsp;</i>During a foreign material exclusion inspection conducted on November 26, 1997, one of two Train B inlet lines for the hydrogen removal and air recirculation from the Unit 2 number 2 and 3 Steam Generator enclosures was found to have been blocked by concrete. The condition was reported under the provisions of 10CFR50.72(b)(2)(i) on November 30, 1997. <br /><br /> The blockage occurred during the Unit 2 Steam Generator replacement in 1988. During this time, portions of the Steam Generator enclosure structure were removed to allow access to the Steam Generators. Following the replacement, the structures were reconstructed. It is believed that the concrete entered the line during the repair of the structure. The blockage has been removed, and procedures will be implemented to preclude future blockages of these lines. <br /><br /> An evaluation of the impact of the blockage has concluded that there would have been adequate flow through the Steam Generator enclosure to preclude excessive accumulation of hydrogen. Thus, the condition did not present a significant risk to the health and safety of the public.
3161997010 | Cook 2, Cook 1 | 12/10/1997 | 02/13/1998 | 9802190221 | <strong>Use of Teflon Packing on Containment Airlock Door Interlock Shaft Results in Potentially Degraded Condition</strong><br /><i>Abstract:&nbsp;</i>During periodic maintenance of the Unit 2 upper containment airlock, the seal for the inner bulkhead interlock shaft was found to consist of Teflon packing rings rather than the specified EPDM elastomer. As Teflon degrades when exposed to the high radiation levels that could exist inside the containment following a postulated loss of coolant accident, a leakage path from the containment into the airlock compartment could have been opened. This condition was reported via ENS at 1726 hours EST the same day in accordance with 10CFR50.72(b)(2)(i), as a degraded condition discovered while the reactor was shutdown. <br /><br /> The cause of the event was unclear written work instructions which resulted in incomplete performance of the shaft seal replacement. <br /><br /> An evaluation of the impact of the use of Teflon seals in the inner bulkhead interlock shaft concluded that although there could have been increased leakage into the airlock following a postulated LOCA, the outer airlock bulkhead, and its associated sealed door provided a barrier to excessive radioactive material releases. Thus, the condition did not present a significant risk to the health and safety of the public.
3171997001 | Calvert Cliffs 1, Calvert Cliffs 2 | 01/10/1997 | 02/10/1997 | 9702130029 | <strong>Spent Fuel Moved with Ventilation System Inoperable and Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On Friday, January 10, 1997, it was discovered that air from the Spent Fuel Pool (SFP) area was leaking out into the Auxiliary Building while fuel was being moved in the SFP. This condition was outside the design basis of the plant. Subsequent investigation found that the Surveillance Test Procedure performed every 18 months to demonstrate operability of the SFP ventilation system had not been performed since September of 1994. <br /><br /> Fuel movement has been suspended until appropriate procedures are changed to ensure that the SFP ventilation system operates at a negative pressure versus surrounding areas, including the Auxiliary Building. <br /><br /> A Root Cause Analysis is being performed to determine casual factors and generic implications for this event. <br /><br /> Additional actions will be reported in a supplement to this report.
3171997002 | Calvert Cliffs 1, Calvert Cliffs 2 | 02/20/1997 | 03/24/1997 | 9703280416 | <strong>Misread Technical Specification Requirements Results in an Inadequate Test</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1997 personnel at Calvert Cliffs determined that the Technical Specification (TS) surveillance tests for the emergency diesel generators were not adequate to meet the requirements of TS 4.8.1.1.2.d.3.c. This TS Surveillance Requirement requires verification that the automatically bypassed diesel trips are automatically bypassed on a safety injection actuation signal (SIAS) in conjunction with a simulated loss of offsite power. Past tests verified that these trips were bypassed on a SIAS only. At the time, Units 1 and 2 were operating at 100 percent and 98 percent rated thermal power, respectively. All of the emergency diesel generators were declared inoperable and testing was completed in the time frames allowed by the TS. <br /><br /> The cause of the inadequate surveillance test procedures was the lack of strict adherence to the wording of the plants TS requirements. The wording of the TS and TS Bases combined with the description in the Updated Final Safety Analysis Report led us to believe that the automatically bypassed diesel trips only needed to be tested in conjunction with a SIAS.
3171997003 | Calvert Cliffs 1, Calvert Cliffs 2 | 04/24/1997 | 05/23/1997 | 9706020099 | <strong>Fuel Moved in Spent Fuel Pool Without Charcoal Filters in Service</strong><br /><i>Abstract:&nbsp;</i>On Thursday, April 24, 1997, fuel was moved in the Spent Fuel Pool without the charcoal adsorber banks being in service. This placed the plant outside its design basis. <br /><br /> An ongoing Root Cause Analysis has thus far identified as primary causal factors for this event personnel error on the part of the Spent Fuel Handling Machine operator and poor communications between him and the Control Room Operator. Contributing to this event was unclear procedural guidance. Additional contributing causes are being evaluated. <br /><br /> Upon discovery, fuel movement was suspended until all appropriate personnel could be trained and procedures revised. An effort is underway to identify and address potential similar problems. A Root Cause investigation is currently ongoing. If any additional causes or corrective actions are identified, they will be detailed in a supplement to this report.
3171997004 | Calvert Cliffs 1 | 06/02/1997 | 07/02/1997 | 9707090148 | <strong>Trip Bypasses Not Removed Above 15 Percent Power</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1997, it was discovered that the Reactor Protective Instrumentation Axial Flux Offset trip bypass and Loss of Load trip bypass were not automatically removed when thermal power, as indicated by Delta-T power, was increased above 15 percent. This condition is not allowed by Technical Specification 3.3.1.1. The plant was in Mode 1 at approximately 17 percent Rated Thermal Power. The cause of this event was a failure to recognize that the potential difference between nuclear instrument and Delta-T indicated power could prevent compliance with the literal reading of plant Technical Specifications. Plant procedures will be revised to require adjustment of the nuclear instruments prior to increasing power above 15 percent thermal power during reactor startup, and prior to decreasing power below 15 percent thermal power during reactor shutdown.
3171997005 | Calvert Cliffs 1 | 05/29/1997 | 06/30/1997 | 9707070337 | <strong>Reactor Coolant System Leak Due to Failed Compression Fitting</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1997 at 1620, Calvert Cliffs Unit 1 experienced a Reactor Coolant System leak of approximately 8-10 gallons per minute while operating at 100 percent power. Operators implemented Abnormal operating Procedure-2A, declared an Unusual Event, and commenced a rapid unit downpower. The leakage source was a failed 3/4 inch compression fitting in an instrument line from the pressurizer vapor space. The leak was isolated at 1930. By 1935 the plant was in Hot Standby. <br /><br /> The cause of the compression fitting failure was improper assembly. It's ferrule was insufficiently compressed due to insufficient nut advancement. <br /><br /> Inspections of critical compression fittings in both Calvert Cliffs units was expeditiously completed. Other compression fittings will be evaluated and addressed during scheduled system maintenance. Additional corrective actions will be implemented based on the results of an ongoing root cause analysis.
3171997006 | Calvert Cliffs 1, Calvert Cliffs 2 | 07/22/1997 | 08/21/1997 | 9708270011 | <strong>Cable Spreading Room Halon System Out-of-Service - Missed Action Statement</strong><br /><i>Abstract:&nbsp;</i>On Tuesday July 22, 1997, Calvert Cliffs Units 1 and 2 were in mode 1 at 100 percent power and normal operating temperature and pressure at the time of the event. At approximately 0615 am, the No. 11 Control Room Heating, Ventilation, and Air Conditioning was declared out-of-service for scheduled maintenance. The tagging boundary for the maintenance activity also caused the Cable Spreading Room Halon System to become inoperable. The Cable Spreading Room Halon System was not declared out-of-service and was returned to service after approximately 35 hours. During this 35 hour period the associated Technical Specification action requirements were not implemented for the out- of-service Halon System. The root cause of this event was personnel error on the part of the Operator. <br /><br /> Operations personnel have been reminded of the possibility of inoperable dampers affecting Halon System operability. The Operators involved in this event have also been counseled. Additional corrective actions may be implemented based on a root cause analysis being conducted.
3171997007 | Calvert Cliffs 1 | 10/29/1997 | 12/01/1997 | 9712040194 | <strong>Combined Surveillance Test Interval Exceeded</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1997, during the performance of a self-assessment of the recently completed Unit 1 Surveillance Test Procedure M-663-1, "Containment Tendon Surveillance," it was identified that the three previous similar Unit 1 Surveillance Test Procedures were not completed within 3.25 times the surveillance interval, as required by the applicable requirement of Technical Specification 4.0.2. The 3.2.5 requirement was removed from Technical Specification 4.0.2 in January 1991. The cause of the event was excessive use of the 25 percent grace period allowed for completion of the surveillance. This event did not result in any significant safety consequences. Corrective action includes procedural revision to require management approval if a significant amount of the surveillance grace period will be exceeded for those surveillances with a periodicity exceeding six months.
3171997008 | Calvert Cliffs 1 | 10/17/1997 | 11/12/1997 | 9711180262 | <strong>Two Reactor Protective Systme Channels Out of Service During Test</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1997, at approximately 1015 hours, an "NI channel inoperable" alarm was noticed on the Unit 1 Reactor Protective System Channel D Wide Range Nuclear Instrument. At the time Channel C was bypassed for performance of a Technical Specification required channel calibration procedure. With both channels potentially inoperable, operations declared a limiting condition for operation could not be met and entered Technical Specification 3.0.3. Operators then requested the Instrument Maintenance Technicians back out of the calibration procedure. At approximately 1026 hours the same day, the "inoperable" alarm cleared on its own and operations exited Technical Specifications 3.0.3, but continued with the restoration of Channel C. <br /><br /> Subsequent testing to determine the cause of the spurious "inoperable, light was inconclusive. A complete root cause analysis is being performed to ensure the problem does not recur.
3171997009 | Calvert Cliffs 1 | 10/24/1997 | 11/20/1997 | 9711250364 | <strong>Automatic Reactor Trip Due to Condenser Vacuum Breaker Opening</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1997 at 0917 a.m., Calvert Cliffs Unit 1 automatically tripped on low condenser vacuum when the condenser vacuum breaker unexpectedly opened. The plant was brought to a safe shutdown condition. This event resulted in no significant consequences to the health and safety of the public. At the time of the event, Unit 1 was operating at 100 percent power. <br /><br /> The cause of this event was a failure to properly terminate an electrical lead on the condenser vacuum breaker handswitch during prior handswitch maintenance. The Plant General Manager formed a Significant Incident Finding Team to investigate. Over 200 similar connections were inspected for a similar deficiency. Additional corrective actions will be taken once the results of the Significant Incident Finding Team investigation are finalized.
3171997010 | Calvert Cliffs 1 | 12/10/1997 | 01/29/1999 | 9902030242 | <strong>Action Time Exceeded Due to Failed Diesel Generator Governor</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1997 at approximately 2355, Unit 1 No. 1B Emergency Diesel Generator failed to start during performance of a routine surveillance test. Operators entered Technical Specification 3.8.1.1, Action b. The cause of No. 1B Emergency Diesel Generator failing to start was the governor. A stainless steel strand in the governor's shutdown solenoid valve prevented it from operating properly. The stainless steel strand was most likely introduced into the governor from stainless steel tubing installed between the governor and the governor booster. A review determined there was no history of similar governor failures involving stainless steel foreign material in governor hydraulic boundaries. We concluded that a similar governor failure in the Nos. 1A, 2A, 2B, or 0C Diesel Generators is highly unlikely. To prevent similar events, we will incorporate governor tubing precautions in the Fairbanks Morse vendor technical manual.
3181997001 | Calvert Cliffs 2, Calvert Cliffs 1 | 04/01/1997 | 04/30/1997 | 9705060140 | <strong>Refueling Machine Overload Protective Circuitry Inoperable</strong><br /><i>Abstract:&nbsp;</i>On Tuesday April 1, 1997, Calvert Cliffs Unit 2 was in Mode 6 with the Reactor Coolant System at approximately 88 degrees Fahrenheit. During a review of the operation of the refueling machine, it was determined that its overload protection circuit was bypassed during approximately 7 inches of vertical travel of the fuel assemblies. The bypassed region is after the fuel assemblies are withdrawn from the core region. This condition did not meet the requirements of the plant's Technical Specifications. At the time of discovery, no core alterations or fuel movements were in progress. A modification was put in place to restore the refueling machine to full compliance with the Technical Specifications prior to resuming core alterations or fuel movements.
3181997002 | Calvert Cliffs 2 | 04/05/1997 | 05/05/1997 | 9705080252 | <strong>Containment Purge Valve Isolation System Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 5, 1997, it was discovered that core alterations had been performed during past periods of the ongoing Calvert Cliffs Unit 2 refueling outage with the personnel air lock open and the containment purge valve isolation system inoperable. This condition is not allowed by Technical Specification 3.9.9.<br /><br /> The plant was in Mode 6 with the Reactor Coolant System at 95 degrees Fahrenheit and atmospheric pressure. The cause was an inaccurate implementation of Technical Specification 3.9.9. Plant personnel thought that it applied only to the purge valves. However, its Action Statement applies to all containment penetrations. <br /><br /> The personnel air lock interlocks were restored prior to further core alterations and plant operators were made aware of the issue. A review is underway to identify similar cases where the literal requirements of the Technical Specifications may not be met.
3181997003 | Calvert Cliffs 2 | 04/23/1997 | 05/21/1997 | 9705300087 | <strong>Chemistry Sampling Not Performed as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, April 23, 1997, it was discovered that Unit 2 Reactor Coolant System chemistry samples had not been taken as required by Technical Specification 3.4.7. This constituted an unmet Surveillance Requirement, resulting in entry into Technical Specification 3.0.3. <br /><br /> This event resulted from Chemistry personnel incorrectly assuming that the Technical Specification was only applicable in the modes for which there were Action Statements, rather than "at all times," including the defueled and drained condition, as stated in the "Applicability" section of the Technical Specification. <br /><br /> The existing Technical Specification is scheduled to be clarified when Improved Technical Specifications are implemented. Efforts are underway to ensure that all Technical Specifications are implemented as written.
3211997001 | Hatch 1 | 01/29/1997 | 02/19/1997 | 9702270430 | <strong>Pressure Boundary Leakage Results in Condition Prohibited by the Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On 1/29/97 at 0835 EST, Unit 1 was in the Run mode at a power level of approximately 256 CMWT (10 percent rated thermal power). Power had been reduced in order to identify and repair the source(s) of leakage into the drywell floor drain sump. At that time, it was determined leakage was coming from the area of a socket weld on a 3/4-inch line connected to the Residual Heat Removal (RHR) system suction line. The location of the leak was such that it met the Technical Specifications definition of pressure boundary leakage, that is, leakage through a nonisolable fault in the reactor coolant system. Limiting Condition for Operation (LCO) 3.4.4 allows no pressure boundary leakage. Therefore, Operations personnel placed the mode switch in the Shutdown position, shutting down the unit as required by LCO 3.4.4, Required Action C.1. By 2125 EST, the leak had been isolated using manual valve 1E11-F067 and personnel had confirmed the leakage had ceased. By 0725 EST on 1/30/97, plant Maintenance personnel had repaired the line. Valve 1E11-F067 was re-opened. <br /><br /> The cause of this event can not be determined conclusively. However, it appears it may have been caused by a combination of a weld anomaly or discontinuity and high cycle fatigue. The existing weld was removed, the line was shortened and re-welded to the RHR suction line, and dye penetrate and magnetic particle tests were performed successfully on the new weld.
3211997002 | Hatch 1, Hatch 2 | 02/07/1997 | 03/05/1997 | 9703100268 | <strong>Less Than Adequate Procedures Result in a Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 2/7/97, at approximately 1300 EST, Unit 1 and Unit 2 were both in the Run mode at 2558 CMWT (100 percent of rated thermal power). At that time, it was determined that Units 1 and 2 Technical Specifications (TS) surveillance requirement 3.8.1.9 had not been adequately implemented. This surveillance requires in part, that on an 18-month frequency, testing be performed to demonstrate that the emergency offsite power system is disconnected from the onsite emergency 4160 volt busses on a simulated Loss of Offsite Power (LOSP) and that the Emergency Diesel Generators tie to the associated emergency busses. However, a set of contacts and associated wiring and terminal points that function to trip the alternate offsite power supply breaker to an emergency bus on an LOSP were not included in the surveillance tests. This condition existed for each of the three emergency 4160V busses for each reactor unit. This trip function is only required when the emergency busses are aligned to the offsite power system via the alternate supply breakers. The busses are normally aligned via the normal supply breakers. The trip circuit for the normal supply breakers was being tested at the required frequency. Powering the busses via the alternate supply breakers is an abnormal condition. (Records reviewed back to 1988 showed that they had not been closed during reactor operation.) This configuration did not exist at the time of discovery of the event. Therefore, the plant was in compliance with the associated TS limiting condition for operation and no TS required actions were necessary. The cause of the event was less than adequate testing procedures. Corrective actions included issuing an operating order to inform Control Room personnel of the condition, testing of the logic during the next scheduled refueling outages on each unit, and revising the associated procedures.
3211997003 | Hatch 1, Hatch 2 | 03/25/1997 | 04/21/1997 | 9704290057 | <strong>RBM Operability Requirements Do Not Match Rod Withdrawal Error Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On 3/25/97 at 1307 EST, Unit 1 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power) and Unit 2 was in the Refuel mode with the cavity flooded. At that time, plant personnel determined an event reported to Southern Nuclear Operating Company personnel by General Electric involving the Rod Block Monitor (RBM) met the reporting requirements of 10 CFR 50.72 (b)(2)(iii) and 50.73 (a)(2)(v). General Electric reported that their core design procedures contained a step which allowed them to assume the RBM is operable and available to mitigate the consequences of a Rod Withdrawal Error (RWE) irrespective of the individual plant's Technical Specifications requirements for RBM operability. Plant personnel, after thoroughly reviewing this event, determined it was a condition that alone could have prevented the fulfillment of the safety function of the RBM to control (prevent) the release of radioactive material during an RWE.<br /><br /> This event was the result of a disparity between the core analysis design procedure assumptions and the Unit 1 and Unit 2 Technical Specifications requirements regarding RBM operability. As a corrective action, Operations procedure 34GO-OPS-065-0S, 'Control Rod Movement,' now requires the Unit 1 and Unit 2 RBMs to be operable whenever reactor power is above 27 percent rated thermal power. Proposed changes to the Unit 1 and Unit 2 Technical Specifications are being prepared for submittal to the NRC.
3211997004 | Hatch 1 | 07/15/1997 | 08/06/1997 | 9708130270 | <strong>Single Failure Renders Inoperable The RHRSW Long-Term Containment Heat Removal Mode</strong><br /><i>Abstract:&nbsp;</i>On 7/15/97 at 1658 EDT, Unit 1 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, personnel determined a single failure could affect the circuits for the 1A Diesel Generator and the 1CD 4160V/600V transformer. This postulated common failure could prevent timely re-energization of the 1C 600V bus via the 1CD transformer. Without power to this bus, operators could not place the required number of Residual Heat Removal Service Water pumps in the long-term containment heat removal mode. With less than the required number of pumps in the heat removal mode, suppression pool temperature could exceed its maximum analyzed value, adversely affecting long-term containment temperature and pressure response and available net positive suction head for emergency core cooling system pumps. On 7/15/97, operations personnel declared an RHRSW pump inoperable to account for the loss of single failure protection. <br /><br /> This event apparently was caused by an original design error. Circuits for the 1CD transformer were classified incorrectly and were routed through the same raceways as the 1A Diesel Generator. This error created the potential for a single failure to disable the 1A Diesel Generator and the 1CD 4160V/600V transformer. A temporary modification was implemented on 7/16/97 to disarm the differential auxiliary relay circuits for the 1CD transformer thereby ensuring a fault that will inop the 1A diesel generator circuits will not prevent the use of the 1CD transformer. Conversely, a fault in the circuits of the 1CD transformer will not inop the 1A Diesel Generator. A design change will be implemented during the next scheduled Unit 1 refueling outage to provide proper separation of the circuits.
3211997005 | Hatch 1 | 10/14/1997 | 11/10/1997 | 9711170050 | <strong>Control Rod Partially Withdrawn Without Pressure in Scram Accumulator</strong><br /><i>Abstract:&nbsp;</i>On 10/14/97 at 1620 EDT, Unit 1 was in the refuel mode with the vessel head removed. At that time, licensed operations personnel were preparing to perform a check of interlocks in the reactor manual control system. This check consists of withdrawing one control rod one notch, attempting to withdraw another control rod, and confirming that the second rod cannot be moved. In this event, the rod withdrawn had no pressure on its hydraulic control unit (HCU) accumulator. In this condition, the rod is inoperable because it cannot be scrammed. The withdrawn rod was immediately reinserted per the test. <br /><br /> The cause of this event was personnel error on the part of the licensed operator and his peer checker in that rod movement was performed without ensuring HCU accumulator pressure was available before moving the control rod. A contributing factor to the event was that several HCUs were inoperable but were not removed from service to prevent withdrawal of an inoperable rod. <br /><br /> Corrective actions for this event included counseling the involved individuals, tagging out of service HCUs, disabling inoperable HCUs, and initiating training of shift personnel. A maintenance procedure in use at the time of the event will be revised, and the manner in which work on HCUs is done will be changed so that inoperable HCUs will be removed from service, thereby preventing movement of a control rod which has an inoperable HCU.
3211997006 | Hatch 1 | 10/31/1997 | 11/26/1997 | 9712030013 | <strong>Apparent LPRM TIP Calibration Tube Failure Results in Primary System Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On 10/31/97 at 0813 EST, Unit 1 was in the Refuel mode with the head removed from the reactor vessel, the reactor cavity flooded, and core alterations in progress. At that time, plant personnel concluded that a small amount of water found in traversing incore probe (TIP) tubing and the "C" TIP indexer came from a reactor coolant leak in the TIP calibration tube in local power range monitor assembly 28-13. This leak constituted a primary boundary leak as defined in the Unit 1 Technical Specifications. Documented maintenance work history indicated the leak may have existed for as long as two operating cycles; this is contrary to the requirements of Unit 1 Technical Specifications Limiting Condition for Operation 3.4.4, item a, and Condition C. <br /><br /> Based upon the amount of water found and discussions with the manufacturer, this event apparently was caused by a small material or manufacturing flaw in the TIP calibration tube located in local power range monitor assembly 28-13. The "A", "B", and "D" TIP indexers were checked and no signs of water were found. The remaining tubing attached to the "C" TIP indexer also was checked and no water was found. Therefore, this appears to be an isolated case of a leaking TIP calibration tube. <br /><br /> The entire local power range monitor assembly, including the TIP calibration tube, was replaced on 11/2/97 with an assembly from a different manufacturer.
3211997007 | Hatch 1 | 11/18/1997 | 12/10/1997 | 9712170416 | <strong>Pneumatic Leak Results in Closure of Primary Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 11/18/97 at 1651 EST, Unit 1 was in the Hot Shutdown mode having just inserted a manual scram for the purpose of performing repairs to the unit. The unit was just exiting a refueling outage, so decay heat load was low. Consequently, operators closed the inboard main steamline isolation valves (MSIVs) in order to control reactor vessel cooldown rate within limits. When the MSIVs were closed, a high flow signal was received on nitrogen flow in the drywell pneumatic system supply header. After the designed, 10-minute time delay, the supply valve to the header, 1P70-F004, closed automatically. This valve is a primary containment isolation valve. The cause of this event was a nitrogen leak from a pneumatic manifold on MSIV 1B21-F022B. This leak was of sufficient size to trip the leak detection logic for the drywell pneumatic system, which then isolated per design. The cause of the leak was found to be a loose fit between the manifold and the pneumatic actuator for this valve which allowed nitrogen to escape past an o-ring. Corrective actions for this event included repairing the leak and confirming that no similar leaks existed on any of the other MSIVs. These actions were completed prior to restarting Unit 1. Procedures for rebuilding MSIVs will be revised prior to the next refueling outage on each unit.
3211997008 | Hatch 1 | 11/18/1997 | 12/08/1997 | 9712160426 | <strong>Personnel Error and Inadequate Procedure Results in Group 1 Isolation on Low Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On 11/18/97 at 1651 EST, Unit 1 was in the Hot Shutdown mode with reactor pressure at approximately 600 psig, the "A" main steam line isolated, and the inboard main steamline isolation valves closed. At that time, Operations personnel opened main condenser vacuum breakers 1N22-F058A and 1N22-F058B resulting in receipt of a full Group 1 primary containment isolation signal on low main condenser vacuum. Outboard main steamline isolation valves 1B21-F028B, C, and D, reactor water sample line isolation valves 1B31-F019 and 1B31-F020, and main steamline drain valves 1B21-F016 and 1B21-F019 closed per design. Operations personnel reset the Group 1 isolation signal at 1653 EST and re-opened main steamline isolation valves 1B21-F028B, C, and D and main steamline drain valves 1B21-F016 and 1B21-F019. <br /><br /> This event was caused by personnel error and a less than adequate procedure. Operations personnel neglected to place the condenser low vacuum trip bypass switches to the bypass position prior to opening the main condenser vacuum breakers. Plant procedure 34AB-C71-001-1S,"Scram Procedure," did not require the low vacuum isolation signal to be bypassed prior to opening the vacuum breakers. <br /><br /> Corrective actions for this event include counseling involved personnel and revising procedures 34AB-C71-001-1S and 34AB-C71-001-2S, "Scram Procedure."
3231997001 | Diablo Canyon 2 | 03/04/1997 | 04/03/1997 | 9704160276 | <strong>Technical Specification 3.8.1.1, Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1997, at 0559 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, the action time allowed by Technical Specification (TS) 3.8.1.1, Action b., was exceeded. The conditional A.C. offsite power verification surveillance required by TS 3.8.1.1, Action b., was not performed within one hour of declaring Diesel Generator (DG) 2-3 inoperable. <br /><br /> On March 4, 1997, at 0950 PST, Operations personnel commenced the surveillance required by TS 3.8.1.1, Action b., after an Operations shift foreman (SFM) discovered the missed verification. The surveillance was completed satisfactorily at 0953 PST on March 4, 1997, confirming that appropriate offsite power sources were present. <br /><br /> The cause of this event was personnel error (cognitive), in that the SFM who authorized clearing DG 2-3 failed to recognize that a conditional surveillance was required within one hour by TS 3.8.1.1, Action b. <br /><br /> As a corrective action for this event, the SFM will be counseled on the requirements of the TS tracking program.
3231997002 | Diablo Canyon 2 | 03/29/1997 | 04/28/1997 | 9705060078 | <strong>Reactor Trip on Low-Low Steam Generator Water Level Following the Failure of Main Feedwater Pump 2-1 Due to Mechanical Problems</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1997, at 1057 PDT, with Unit 2 in Mode 1 (Power Operation) at 1 00 percent power, the Unit 2 reactor tripped on steam generator (SG) water level low-low in SG 2-2. The Unit was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. A 4-hour, non-emergency report was made to the NRC at 1209 PDT in accordance with 10 CFR 50.72 (b)(2)(ii). <br /><br /> The low-low SG water level was caused by the failure of Main Feedwater Pump (MFWP) 2-1. The feedwater pump failed when a solenoid-operated shuttle valve in the control oil supply to the MFWP turbine governor valve jammed which resulted in the governor valve drifting shut. The valve failure was determined to be caused by iron oxide (rust) particulate contamination buildup in the valve spool. The iron oxide particulate generation occurred in the feedwater pump oil system as a result of water contamination. Steam/moisture entered the oil system from a potentially degraded inboard turbine seal via the adjacent bearing oil seal. <br /><br /> The MFWP 2-1 lube oil system was flushed. The associated filters were replaced. Water contamination was minimized by throttling MFWP 2-1 turbine gland seal supply steam. The planned maintenance and predictive maintenance systems are being improved to ensure proper operation of the MFWP control oil system. The MFWP inboard turbine gland seal will be repaired or replaced in the next refueling outage.
3231997003 | Diablo Canyon 2 | 07/02/1997 | 09/19/1997 | 9709240251 | <strong>Manual Trip on Loss of Normal Feedwater Due to Unknown Condensate/Feedwater Transient</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1997, at 0456 PDT, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, a manual reactor trip was initiated due to a trip of both main feedwater pumps (MFWPs). A 4-hour, non-emergency report was made to the NRC, in accordance with 10 CFR 50.72(b)(2)(ii) at 0853 PDT. <br /><br /> On July 2, 1997, at 0452 PDT, a condensate/feedwater system transient initiated an automatic start of the standby condensate and booster pump set. Approximately 4 minutes later, low condensate flow and increasing MFWP demand resulted in condensate flashing and an overspeed trip of both MFWP steam driven turbines. The overspeed trip of both MFWP turbines resulted in a loss of normal feedwater. Plant operators manually tripped the reactor. <br /><br /> An event response plan (ERP) was initiated to investigate the cause of the event and implement immediate corrective actions to return Unit 2 to Mode 1. ERP actions included verification of proper operation of condensate system components and additional system monitoring during the Unit startup. <br /><br /> Due to the unknown root cause of this event, no corrective action to prevent recurrence could be identified. PG&E believes that a failure of a condensate system control valve coincident with an unknown rapid reduction in condenser vacuum resulted in the loss of main feedwater. <br /><br /> This revision is submitted to identify the contributory causes and add a conclusion regarding the cause of this event in Section III.
3231997004 | Diablo Canyon 2 | 10/17/1997 | 11/17/1997 | 9711260090 | <strong>Auxiliary Saltwater System was outside its design basis because 10 CFR 50, Appendix R, requirements were not met due to personnel error</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1997, at 1630 PDT, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that the auxiliary saltwater system (ASW) safe shutdown electrical circuits did not meet 10 CFR 50, Appendix R, requirements and were therefore outside the design basis of the plant. Two pull boxes did not have adequate fire protection separation. These pull boxes contained redundant ASW safe shutdown circuits, and a fire in either pull box could result in the loss of both trains of ASW. A 1-hour, non-emergency report was made to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B) at 1657 PDT, on October 17, 1997. A preliminary investigation has determined that this condition does not affect Unit 1 ASW safe shutdown circuits. <br /><br /> On October 17, 1997, at 1630 PDT, a continuous firewatch was established as an interim compensatory measure. <br /><br /> The root cause of this event is personnel error (cognitive) in that the ASW safe shutdown circuits were incorrectly evaluated as being entirely embedded; thus the circuits did not receive 10 CFR 50, Appendix R, reviews. <br /><br /> The pull boxes will be modified to meet 10 CFR 50, Appendix R, requirements. PG&E will also review other embedded pull boxes with safe shutdown equipment cables to ensure that 10 CFR 50, Appendix R, requirements are met.
3231997005 | Diablo Canyon 2 | 10/24/1997 | 11/24/1997 | 9712030300 | <strong>Reactor Trip and Safety Injection Caused by Inadvertent Main Steam Isolation Valve Closure Due to personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1997, at 0815 PDT, with Unit 2 in Model (Power Operation) at 100 percent reactor power, a reactor trip (RT) and safety injection (SI) occurred due to inadvertent closure of a main steam isolation valve. One power operated relief valve lifted to relieve reactor coolant system (RCS) pressure seven times during recovery from the RT and SI. The SI actuation signal was reset at 0829 PDT. An unusual event (UE) was declared for this event at 0832 PDT. The San Luis Obispo County Sheriff s Office Watch Commander was notified at 0837 PDT. A 1-hour emergency report was made to the NRC, in accordance with 10 CFR 50.72(a)(1)(i) at 0900 PDT. On October 24, 1997, at 0938 PDT, following stabilization of Unit 2 in Mode 3 (Hot Standby), the UE was terminated. This was the twelfth Unit 2 emergency core cooling system actuation cycle that resulted in a discharge of water into the RCS. The cause of the event was inadvertent actuation of the closed position switch for FCV-44 by a contract laborer removing scaffolding adjacent to the valve. Corrective actions to prevent recurrence include: (1) revision of the scaffolding program procedure and risk assessment procedure and (2) issuance of a maintenance policy to require a risk assessment and management approval for nonroutine work near critical components.
3231997006 | Diablo Canyon 2, Diablo Canyon 1 | 12/11/1997 | 12/18/1998 | 9812240030 | <strong>Nuclear Fuel Outside Design Basis Due to Fuel Pellet-to-Clad Gap Reopening</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1997, at 1115 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that fuel pellet-to-clad gap reopening had been predicted on a 95 percent upper bound basis for lead rods at cycle burnups greater than 18,000 megawatt days per metric ton uranium. This burnup occurred in Unit 2 on September 1, 1997. This condition is outside the design basis for the plant. Additionally, Westinghouse completed analyses which show that although gap reopening is predicted for Unit 2, Cycle 8, the 10 CFR 50.46 criterion for localized 17 percent total oxidation continues to be met. On December 11, 1997, at 1130 PST, PG&E made a 1-hour, non-emergency report to the NRC in accordance with 10 CFR 50.72 (b)(1)(ii)(B). The December 11, 1997, report was updated on January 6, 1998. <br /><br /> Westinghouse discovered the potential for this condition in high duty integral burnable absorber rods when the effects of increased Zirc-4 corrosion on high duty rods were incorporated into the current version of the fuel performance computer code. <br /><br /> The condition was caused by Zirc-4 cladding material corrosion rates higher than previously expected on high duty fuel rods. <br /><br /> PG&E will continue to communicate with Westinghouse through implementation of a long term resolution plan and will take appropriate actions for Diablo Canyon Power Plant, Units 1 and 2.
3241997001 | Brunswick 2 | 06/27/1997 | 07/28/1997 | 9708010275 | <strong>Containment Atmospheric Control Monitor Inoperability Due to Thermoelectric Cooler Failure</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1997, with Unit 2 operating at 100% reactor power, intermittent actuations of the Unit 2 Containment Atmospheric Control (CAC) system division II primary containment hydrogen/oxygen monitor, 2-CAC-AT-4410, trouble alarm occurred. Investigation into the cause of the alarms determined that the 2-CAC-AT-4410 sample line flow switch was actuating due to a sample line low flow condition. The low flow condition resulted from condensation which formed in the sample line due to a failure of the sample line thermoelectric cooler. Following replacement of the 2-CAC-AT-4410 thermoelectric cooler, the monitor was satisfactorily tested and returned to service on June 7, 1997. An assessment of the low flow condition on the past operability of the 2-CAC-AT-4410 monitor and compliance with the requirements of Technical Specifications was completed on June 27, 1997. This assessment concluded that the thermoelectric cooler was inoperable for a period in excess of that allowed by the Technical Specifications <br /><br /> The cause of the 2-CAC-AT-4410 monitor thermoelectric cooler failure was not conclusively determined. However, the most probable cause of the failure is inadequate heat transfer to the cooler's heat sink, stemming from improper assembly techniques. Another possible cause was determined to be internal electrical shorting due to condensation within the thermoelectric cooler. Based on inspection and testing of the other CAC hydrogen/oxygen monitors and the results of an historical review of similar failures, the failure of the Unit 2 CAC or thermoelectric cooler is considered an isolated event. Additional corrective actions the thermoelectric coolers with an improved seal design and development of procedures of thermoelectric performance and monitor condensation accumulation.
3241997002 | Brunswick 2 | 07/24/1997 | 08/25/1997 | 9709030158 | <strong>Core Spray System Minimum Bypass Flow Motor Operated Valve Inoperability</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1997, Unit 2 was operating at 100% power. At 1845, valve 2-E21-F031B was declared inoperable. Valve 2-E21-F031B is a Core Spray (CS) system minimum flow bypass valve which also provides a manually initiated primary containment isolation function. <br /><br /> The inoperability of valve 2-E21-F031B was caused by a reduction of the calculated motor torque below that required. Thus with the existing torque switch setting the valve could fail (stall) not fully closed if both a maximum delta pressure and a degraded voltage condition existed. This condition was discovered during an on going review of Generic Letter 89-10 motor operated valves against revised design criteria. <br /><br /> Valve 2-E21-F031B was declared inoperable and closed as a result of not being able to perform its primary containment isolation function. Manual isolation valve 2-E21-F010B was closed in accordance with the action statements of Technical Specification (TS) 3.6.3. Upon closure of 2-E21-F031B the 2B loop of CS was declared inoperable in accordance with TS 3.5.3.1. The valve was returned to operable status on July 25,1997, after implementing a revised torque switch setting. <br /><br /> This condition is being reported in accordance with the requirements of 10CFR50.73(a)(2)(i) as operation prohibited by the plant's TSs. The primary containment isolation function of valve 2-E21-F031B was inoperable for greater than 8 hours without meeting the appropriate TS 3.6.3 action statement.
3241997003 | Brunswick 2 | 09/08/1997 | 10/08/1997 | 9710150234 | <strong>High Pressure Coolant Injection Inoperability - Installation of Non-Seismically Supported Temporary Air Piping</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1997, Unit No. 2 was operating at 95% reactor power. At 1930 hours, the High Pressure Coolant Injection (HPCI) system was declared inoperable due to seismic concerns associated with temporary non-seismically supported air piping installed over Motor Control Center (MCC) 2XDA, which supplies power to various HPCI system components. Specifically, in a seismic event, the piping could fall and cause damage to the indication lamps which are mounted on the front of MCC 2XDA. Damage to the indication lamps could potentially result in an electrical short in the control logic, causing a loss of control power to various HPCI system components, thus rendering the system inoperable. The temporary air piping had been installed in the Reactor Building in preparation for a refueling outage. <br /><br /> The cause of the non-seismically supported air piping installation was an incorrect evaluation that the temporary air piping did not require a temporary rigging release as described in procedure 0MMM-022, "Instructions for Placement of Temporary Loads." By 2000 hours, the temporary air piping was removed from the area above MCC 2XDA and the HPCI system was declared operable. Lessons learned from this event have been reviewed with personnel involved with temporary installation activities. An evaluation of the guidance provided for requiring seismic analysis during routine temporary installation activities and existing temporary installation procedures will be performed. <br /><br /> This condition is being reported in accordance with there requirements of 10CFR50.73(a)(2)(v) in that during a seismic event, the non-seismically supported piping could have prevented the fulfillment of the HPCI system's safety function.
3241997004 | Brunswick 2 | 10/03/1997 | 05/11/1998 | 9805190242 | <strong>Safety Relief Valves Exceeded Technical Specification Setpoint Limits</strong><br /><i>Abstract:&nbsp;</i>During the Brunswick Steam Electric Plant (BSEP) Unit No. 2 Refueling Outage, eleven safety relief valves (SRVs) were removed and shipped to Wyle Laboratories for set pressure testing and recertification. On October 3, 1997, the results of the testing identified that five of the eleven valves were found to lift at pressures outside the Technical Specification(TS) Limiting Condition for Operation (LCO) 3.4.2 setpoint limits in effect at the time the valves were installed The limits were +/- 1 percent of their required lift pressure values. TS LCO 3.4.2 setpoint limits were amended to +/- 3 percent on November 1, 1996. <br /><br /> Two of the SRVs that exceeded the +/- 1 percent setpoint limit indicated increases in lift setting pressure. The remaining three SRVs indicated decreases in lift setting pressure. The two SRVs that exceeded the 1 percent setpoint limit were within the current TS setpoint limit of 3 percent. Of the three SRVs that were below the +/- 1 percent limit only one, SRV 2-B21-F013E, was outside the current TS setpoint limit. The most probable cause of the setpoint drift for SRV 2-B21-F013E is oxide accumulation on the pilot disc seat which resulted in a small increase in the effective pilot disc seating area. The increased seating area would cause a larger force to be exerted on the pilot disc at any given steam pressure and cause the SRV to lift at a lower pressure. This condition is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(vii).
3251997001 | Brunswick 1, Brunswick 2 | 01/29/1997 | 02/27/1997 | 9703100026 | <strong>Rod Block Monitor Surveillance Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1997, during the closeout review of the Unit 1 test results for surveillance procedure, 0MST-RBM11Q, Rod Block Monitor Channel Functional Test, which had been performed on January 28, 1997, Maintenance personnel identified that the surveillance procedure did not contain the proper reference to procedural steps necessary to ensure testing of the Rod Block Monitor (RBM) instrument channel B inop function. This function is required to satisfy Technical Specification operability requirements. Review of past Performances of the RBM surveillance identified that testing of the RBM instrument channel B inop function had not occurred during scheduled testing of the Unit 1 RBM in November of 1996 and in December of 1996 on the Unit 2 RBM. The error in the RBM surveillance procedure is attributed to an inadequate administrative review of the reformatting changes affecting procedural step references. Upon discovery of the error, a temporary procedure revision was issued to correct the procedure step reference and the procedure was reperformed for the Unit 1 instrument channel B and for the Unit 2 RBM instrument channels A and B on January 29, 1997. Additional corrective actions include a sample review of maintenance surveillance tests to ensure Technical Specification requirements are being properly tested and enhancement to the procedure technical review guidelines. <br /><br /> The safety signficiance of this event is considered minimal in that results of the RBM inop functional tests performed on both units indicated that the equipment was in calibration and capable of performing its intended safety function.
3251997002 | Brunswick 1 | 03/13/1997 | 04/14/1997 | 9704230229 | <strong>Core Spray Header Differential Pressure Instrumentation Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 9,1997, the Unit 1 Core Spray Nozzle A Differential Pressure Switch, 1-E21-PDS-N004A, was identified to be indicating-154' H sub 2 O instead of the -108' H sub 2 O value previously considered normal. This instrument generates a control room alarm on an in-vessel line break which would cause the reading to be positive. Technical Specifications require that the 1-E21-PDS-N004A alarm setpoint be based on the normal reading. Based on preliminary review it was determined that the -154' H sub 2 O should be considered normal, and as a result the instrument setpoint was believed to be outside Technical Specification requirements. At 2030 hours, the instrument was conservatively declared inoperable. On March 13, 1997, an engineering evaluation was completed and confirmed that the 1-E21-PDS-N004A instrument setpoint was outside of the Technical Specification value. The evaluation also found that the most probable cause is a bi-stable condition where voiding of the in-vessel Core Spray piping is triggered by vessel conditions. The piping can be either full of water or full of steam and/or non-condensable gases depending on the local hydraulic/thermodynamic conditions at the core spray nozzles. This accounts for readings being stable at two different 'normal' conditions. Since the-154' H sub 2 O reading was the more conservative normal condition, the setpoint was changed based on this value. Data indicates that -154' H sub 2 O has been a normal reading for this operating cycle, therefore, the setpoint was not in compliance with requirements of Technical Specifications from approximately November of 1996. <br /><br /> The safety significance of this event is considered minimal since, for most core spray line breaks in the vessel annulus, the piping would not remain completely voided and the alarm would have actuated. Additionally, any line break which should have resulted in an alarm would cause core flow to bypass the dryer-separator and affect reactor power sufficiently to alert operators to the problem.
3251997004 | Brunswick 1, Brunswick 2 | 05/06/1997 | 06/05/1997 | 9706110016 | <strong>Spent Fuel Shipping Cask Handling Activities</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1997, Units land 2 were operating at rated power when it was determined that spent fuel shipping cask handling activities had been conducted outside the design bases. Specifically, the site procedures controlling the lifting and loading of an IF-300 spent fuel shipping cask prescribe the use of rigging which is not single failure proof during transfer from the tilting cradle to the secondary yoke, contrary to existing analyses. This transfer occurs on the 20' elevation of the reactor building at a lift height of approximately 7 feet. In addition, during previous spent fuel shipping cask handling activities when the non-single failure proof lift condition existed, the safety-related valve box covers were not installed. Current spent fuel analyses bound a 30' cask drop with the safety-related valve box covers installed. There is not an existing analysis for a spent fuel shipping cask drop without the valve covers installed. <br /><br /> This event was caused by an incomplete understanding of the scope of the NEDO-10084-4, Vectra IF-300 Shipping Cask Consolidated Safety Analysis Report and NUREG-0612, "Control of Heavy Loads at Nuclear Power Plants." Site procedures for spent fuel shipping, handling, and receiving have been placed on administrative hold pending resolution of this issue and NRC review and approval of a related change to the licensing/design bases. A load drop analysis for the postulated spent fuel shipping cask drop accident will be performed in accordance with the applicable guidance of NUREG-0612. In addition, a review of the applicable regulatory requirements and site procedures related to spent fuel shipping cask handling will be performed to ensure consistency.
3251997005 | Brunswick 1 | 04/02/1997 | 08/08/1997 | 9708190059 | <strong>Feedwater Flow Indication Discrepancy - Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1997, with Unit 1 operating at 95% reactor power, while awaiting implementation of power uprate to 100% reactor power, the results of an ultrasonic test (UT) conducted on the Unit 1 Feedwater (FW) system flow venturis indicated that the Unit 1 FW system flow indication was potentially non-conservative. In response, Unit 1 reactor power was reduced to 93% at 1557 hours. Administrative controls were established to ensure core thermal power would not exceed 93% until the FW system flow instrumentation could be re-calibrated. On April 7, 1997, the Unit 1 FW system flow instrumentation were re-calibrated based upon the UT test data. This calibration provided the most conservative feedwater flow indication while a more detailed engineering evaluation of the various venturi tests could be completed; Unit 1 reactor power was subsequently restored to 95%. <br /><br /> Evaluation of the three venturi tests performed since plant construction concluded that the chemical tracer test performed in 1994 and the recent UT test were not as accurate as the original weigh tank test performed during plant construction. Using the original calibration constants as a basis, a review of operating data since the 1994 FW system flow instrumentation calibrations determined that the licensed power level was exceeded by approximately 1.3% and that the thermal limits defined by the Technical Specifications were exceeded for brief periods on six occasions. Corrective actions include internal inspection of the FW system A loop venturi and recalibration of the feedwater flow instrumentation based upon the original weigh tank test results.
3251997006 | Brunswick 1 | 06/08/1997 | 07/07/1997 | 9707150154 | <strong>Engineered Safety Feature Actuation Due to Loss of Emergency Bus E-2</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1997, at 1441 hours, with Units 1 and 2 operating at 100% power, a momentary loss of 4160 volt emergency bus E-2 occurred while manually starting Emergency Diesel Generator (EDG) #2. The loss of emergency bus E-2 resulted in the following unplanned, automatic Engineered Safety Feature (ESF) system actuations: Group 1 Division II logic trip (Main Steam Line) and closure of the 1-B32-F020, Reactor Sample Valve; Reactor Protection System Division II trip; Secondary Containment isolation and start of both Standby Gas Treatment Trains; Group 2 Division II isolation (Drywell Floor and Equipment Drains); Group 3 isolation (Reactor Water Cleanup); Group 6 Division II and applicable containment monitor isolations (Containment Atmospheric Control); and Group 10 Division II isolation (Pneumatic Nitrogen). In addition, EDG #2 auto-started and connected to emergency bus E-2 as designed. At 1907 hours, with EDG #2 supplying power to emergency bus E-2 loads, a 1/4 inch fuel oil line on EDG #2 developed a non-isolable leak. At 1913 hours, EDG #2 was manually tripped resulting in the loss of emergency bus E-2 and the same ESF actuations that resulted from the first loss of emergency bus E-2. During both events, the affected systems operated as required. Investigation into the first event determined that the normally closed trip contacts on emergency bus E-2 undervoltage relay 27PK failed to open when the relay was energized due to a less than adequate contact gap. The inadequate contact gap setting is believed to have existed since receipt of the relay from the vendor. Investigation into the failed fuel oil line determined that a pipe-nipple connection used to mount an EDG #2 fuel oil pressure indicator had failed due to fatigue. Corrective actions include replacement of the degraded relay and fuel oil line pipe-nipple, inspection of other similar relays installed in class 1E applications, relay calibration procedure enhancements, and replacement and inspection of similar EDG pipe-nipple applications. Problems were not identified with the relays and pipe-nipples installed in similar applications.
3251997008 | Brunswick 1, Brunswick 2 | 08/19/1997 | 09/18/1997 | 9709240004 | <strong>Main Stack Radiation Monitor Surveillance Interval Exceeded</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1997, while reviewing a proposed change to the Updated Final Safety Analysis Report (UFSAR) associated with a submittal being prepared for implementation of Improved Technical Specifications, reviewers identified that the response time surveillance requirement specified in the current Technical Specifications (TS) was inconsistent with those specified in the UFSAR. Further review determined that a UFSAR change implemented on February 12, 1996, inappropriately eliminated requirements for response time testing of the Main Stack Radiation Monitor isolation actuation function. Consequently, the next scheduled Unit Nos. 1 and 2 Main Stack Radiation Monitor surveillance test procedures were not performed as required by the TS with in the time allowed. Upon discovery of the missed surveillance the Main Stack Radiation Monitor was declared inoperable and the actions required by TS were implemented for both units. By August 23, 1997, test procedures were developed and performed on the Main Stack Radiation Monitor isolation actuation instrumentation to ensure that TS response time were satisfied; the monitor was subsequently declared operable.<br /><br /> The cause of this issue is attributed to the performance of inadequate reviews of the UFSAR change associated with removal of the Main Stack Radiation Monitor response time test requirements from the TS. Corrective actions include a review of the basis for response time tests which have been eliminated to ensure requirements for test elimination have been satisfied; administrative actions have been taken with the personnel directly involved with the inadequate UFSAR change; and assessment of the adequacy of the UFSAR change technical review process. <br /><br /> This issue is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(i), in that, the elimination of the response time tests resulted in the failure to perform surveillance testing required to satisfy TS.
3251997009 | Brunswick 1 | 07/14/1997 | 08/13/1997 | 9708190050 | <strong>Missed Increased Frequency Inservice Testing Requirement</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1997, surveillance test 1MST-SW12Q, Service Water Diesel Generator Cooling Water Supply Low Pressure Instrument Calibration and Functional Test, was performed as required by Technical Specification 4.0.5 and ASME Section XI Code requirements. During the test, the stroke time of valve 2-SW-V680, Emergency Diesel Generator #2 Unit 1 Service Water Cooling Water Supply Valve, was recorded as 73.93 seconds which represents an increase of more than 35% over the previous stroke time of 54.17 seconds for this valve. The American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code, Section XI, 1980 Edition through Winter 1981 Addenda Section IWV-3417(a), requires an increase in test frequency to once each month in the event an increase in stroke time of 25% or more from the previous test is observed. Contrary to this requirement, the test frequency was not increased as required and as a result, the required monthly testing was missed by approximately two weeks. Inservice Testing (IST) personnel discovered the missed monthly increased frequency test on July 14, 1997, during a review of a maintenance request to reschedule the increased frequency test for valve 2-SW-V680. On July 16, 1997, the valve tested satisfactorily in accordance with ASME Section XI requirements. The cause of the event is attributed to the failure of the Inservice Testing (IST) program to include the controls necessary to ensure that completed valve stroke time tests are trended in a timely manner. Corrective actions include enhancements to IST program procedures and review of recently completed IST surveillance tests.
3251997010 | Brunswick 1, Brunswick 2 | 09/19/1997 | 04/01/1998 | 9804100100 | <strong>Failure To Comply With Surveillance Requirements To Test Emergency Diesel Generators During Shutdown</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1997, engineering personnel questioned whether the surveillance requirements specified in Technical Specification (TS) 4.8.1.1.2 were being appropriately met. TS 4.8.1.1.2.d.1 requires that: "Each diesel generator shall be demonstrated OPERABLE: At least once per 18 months during shutdown by subjecting the diesel to an inspection in accordance with procedures prepared in conjunction with its manufacturer's recommendations for this class of standby service." Bases Section 3/4.8, "Electrical Power Systems," indicates that the term shutdown, as specified in the surveillance requirement, applies to the respective plant's operational condition; review of past performances of the applicable surveillance procedure indicates that the surveillance has not always been performed with the respective plant shutdown. As part of the corrective actions for this issue, a review of TS surveillance requirements was performed. The results of this review revealed that TS surveillance requirements 4.8.1.1.2.d.4 and 4.8.1.1.2.d.5 were not being appropriately met. The root cause of this issue is personnel error, in that, the Emergency Diesel Generator (EDG) surveillance writers/reviewers failed to fully incorporate the requirements of the TSs into EDG testing procedures. The failure to adequately define the intent of these TSs contributed to a misunderstanding of the term shutdown as specified in these TSs. Corrective actions include establishing the controls necessary to ensure that the procedures used to satisfy TS 4.8.1.1.2.d.1,4.8.1.1.2.d.4, and 4.8.1.1.2.d.5 are performed during unit shutdown A TS change to allow performance of the procedures used to satisfy TS 14.8.1.1.2.d.1, 4.8.1.1.2.d.4, and 4.8.1.1.2.d.5 in any operational condition was submitted and approved.
3251997011 | Brunswick 1, Brunswick 2 | 09/12/1997 | 10/13/1997 | 9710200010 | <strong>Simultaneous Drywell and Suppression Chamber Valve Lineups Results in Unanalyzed Pressure Suppression Bypass Flow Path</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1997, a review of industry events related to primary containment pressure suppression bypass paths determined that plant operating procedures allowed simultaneous inerting/purging/deinerting of the drywell and suppression chamber: however, use of this bypass path was not appropriately supported by design analysis. The Containment Atmosphere Control system valve lineups associated with these activities have resulted in an external pressure suppression bypass path between the drywell and suppression chamber air spaces. If a Loss of Coolant Accident occurred with this bypass path open, primary containment design pressures could have been exceeded. The isolation of the bypass path relies on two inboard primary containment isolation system (PCIS) valves and both valves use the same division of isolation logic, making the isolation function susceptible to a single failure. The cause of the issue is that documentation of the design limitations associated with a containment pressure suppression bypass path were not of sufficient detail to allow personnel to recognize that the paths created for primary containment inerting/purging/deinerting must meet the isolation requirements for a containment pressure suppression bypass path, as well as the PCIS function. Administrative controls have been implemented to prohibit simultaneous inerting/purging/deinerting in Operational Conditions 1, 2, and 3, pending revision of appropriate operating procedures; applicable design bases documents are also being revised. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii), as a condition outside the plants' design bases.
3251997012 | Brunswick 1, Brunswick 2 | 09/08/1997 | 10/08/1997 | 9710150153 | <strong>Standby Gas Treatment System Fire Protection System Deluge Valve Surveillance Interval Exceeded</strong><br /><i>Abstract:&nbsp;</i>During review of procedure 0PLP-1.2, "Fire Protection System Operability, Action, And Surveillance Requirements," it was determined that cycling of the Standby Gas Treatment (SBGT) system fire protection (FP) system deluge valves was being performed on an 18 month frequency instead of the required 12 month test frequency. Investigation into the issue determined that revisions to the SBGT system FP system deluge valve surveillance procedures changed the test frequency interval from 12 to 18 months in April 1990. At the time the test frequency was revised, Technical Specification (TS) 4.7.7.2 required cycling of each testable valve in the SBGT system FP system deluge flow path at least once per 12 months. This situation is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(i), in that, the failure to perform testing of the SBGT system FP system deluge valves on a 12 month interval represents a condition that was prohibited by the TS surveillance requirements in effect from April of 1990 until February of 1994. Specific fire protection testing requirements were removed from the TS, in February 1994. <br /><br /> The bases for the changes to the SBGT system FP system deluge valve surveillance procedures were not adequately documented; therefore, a specific root cause of the inadequate procedure revisions could not be determined. However, at the time the revisions to the SBGT system FP system deluge valve functional test procedures were being developed, an adequate definition did not exist for determining whether a valve is testable or non-testable. The lack of this definition is believed to have contributed to the inadequate procedure revision
3251997013 | Brunswick 1 | 10/03/1997 | 11/03/1997 | 9711070214 | <strong>Reactor Core Isolation Cooling System Surveillance Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On October 3, 1997, while performing a review of the Logic System Functional Test (LSFT) procedures in accordance with Generic Letter 96-01, "Testing of Safety-Related Logic Circuits," personnel identified that Reactor Core Isolation Cooling (RCIC) system surveillance procedure 1MST-RCIC23Q, "RCIC Turbine Exhaust Diaphragm High Pressure Instrument Channel Calibration," and the corresponding isolation system LSFT procedure, 1MST-RCIC41R, "RCIC Auto-Actuation and Isolation Logic System Functional Test," did not provide the surveillance overlap necessary to demonstrate that the required components were operable. Procedure 1MST-RCIC41R had been revised in 1993 to move test jumper insertion points to terminals not located in a radiation area. <br /><br /> The cause of this issue is personnel error, in that, the individuals responsible for the revision did not recognize that by moving the insertion points of the test jumper, the LSFT overlap between 1MST-RCIC23Q and 1MST-RCIC41R was eliminated. Corrective actions included revising 1MST-RCIC23Q and performing the revised procedure to verify operability of the RCIC exhaust diaphragm high pressure instrument channel logic. In addition, the lessons learned from this event will be reviewed by the appropriate procedure sponsors and writers. This issue is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(i), in that, the surveillance procedures failed to provide the overlap needed to satisfy Technical Specification 4.3.2.2 LSFT requirements.
3271997001 | Sequoyah 1, Sequoyah 2 | 01/25/1997 | 02/24/1997 | 9703030363 | <strong>Failure to Properly Perform Surveillance Testing on the Emergency Diesel Generator (D/G) Start Timer Relays that are Contained in the Start Logic Circuitry</strong><br /><i>Abstract:&nbsp;</i>On January 25, 1997, at 1530 hours Eastern Standard Time (EST), with Units 1 and 2 in power operation at approximately 100 percent, it was determined that surveillance testing of the emergency D/G start-timer relays which are contained in the start logic circuitry was not being performed as required by technical specifications (TSs). TSs require two channels per shutdown board to be demonstrated operable. Surveillance instruction (SI) reviews found that only one channel was being tested. SIs were being reviewed against schematic drawings and logic diagrams to determined if surveillance tests provided sufficient overlap of the logic circuit in accordance with Generic Letter (GL) 96-01. Reviews determined that redundant timer relays installed in parallel for each of the functions of degraded voltage, safety injection/degraded voltage, and loss of voltage were not overlap-tested Timer-relays in these parallel installation's have been functionally tested as a single circuit and as such only one of the two relays could actually be credited as being functionally tested. The immediate cause was inadequate SIs. The root cause was inadequate procedure review to verify that TS requirements are addressed because of the incomplete understanding that the parallel circuit paths are considered as individual channels. Upon determination of the condition, appropriate limiting conditions of operation were entered, SIs were revised, and testing of the timer relays was performed. The testing found each Channel and circuit to be acceptable. Lessons learned from the condition will be provided to appropriate personnel to clarify that channels can be individual paths or redundant devices. SI reviews, for adequacy of testing of safety-related logic circuits, are continuing as committed in response to NRC GL 96-01.
3271997003 | Sequoyah 1, Sequoyah 2 | 03/05/1997 | 04/04/1997 | 9704150206 | <strong>Failure to Properly Perform Surveillance Testing on the Centrifugal Charging Pump Inlet Isolation Valve Logic.</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1997, at 1040 hours eastern standard time, it was determined that surveillance testing of the centrifugal charging pump (CCP) inlet isolation valve logic (interlock) was not being performed as required by technical specifications. The logic isolates the volume control tank (VCT) flow path to the CCP after a safety injection signal fully opens the path from the refueling water storage tank (RWST). instruction and other documents, as committed in response to NRC Generic Letter 96-01, it was determined that the interlock was not adequately tested. Each VCT isolation valve has two parallel electrical initiation paths: one direct contact from the same train RWST valve and a separation relay contact from the opposite train RWST valve. The surveillance instruction requires a safety injection signal to be initiated, this signal opens the RWST valves which initiates a signal to close the VCT outlet valves. The surveillance instruction does not identify the contact that caused the valves to change state. The root cause was determined to be an inadequate surveillance instruction to test the CCP inlet isolation valve logic. A special test procedure was prepared to test the individual contacts in each circuit. The test was performed on both units and determined to be acceptable. The appropriate surveillance instruction has been revised to adequately test the circuit. Lesson learned from this condition will be communicated to the appropriate Engineering and Operations personnel.
3271997004 | Sequoyah 1, Sequoyah 2 | 03/20/1997 | 11/03/1997 | 9711130223 | <strong>Failure to properly perform surveillance testing on circuit breakers</strong><br /><i>Abstract:&nbsp;</i>This report was revised to provide details concerning two additional breakers that were not being tested because the loads were shown on drawings as 1E rather non-1E. On March 20, 1997, it was determined that seven circuit breakers were not being tested in accordance with surveillance requirements 4.8.3.1 and 4.8.3.3. The root cause was determined to be an inadequate review of surveillance instruction (SI) revisions and inadequate tracking of procedure changes generated as a result of plant modifications. The affected breakers were either for isolating non-1E loads from 1E busses or were overcurrent protective devices for containment penetration conductors. Following discovery, the affected breakers had either the required maintenance performed or successfully completed a functional test as appropriate, or in one case was determined to be within the frequency requirements for the 60-month maintenance. Revision 1 of the LER provided review results that identified an additional fourteen breakers that were not included in the appropriate SIs. Two breakers were determined to be within their frequency requirements or were successfully functionally tested and had the 60-month maintenance performed. The root cause was inadequate review of drawings during initial issue.
3271997005 | Sequoyah 1 | 03/19/1997 | 04/17/1997 | 9704220360 | <strong>Two of Six Tested Main Steam Safety Relief Valves Were Not Within Technical Specification Setpoint Tolerance.</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1997, with Unit 1 in power operation at approximately 80 percent and coasting down for a refueling outage, it was determined that two of the six main steam safety relief valves that were tested exceeded the technical specification (TS) setpoint tolerance of plus or minus one percent. Upon determination of the condition, the valves outside the setpoint tolerance were considered inoperable and the TS limiting condition for operation (LCO) action was entered; the valves were adjusted, retested, and found acceptable; and the LCO action was exited. The cause of the condition was attributed to setpoint drift. The as-found condition of the two valves does not indicate a material problem. The test results were well within the three percent ASME Section XI criteria requirement and the valves demonstrated satisfactory test results after adjustment.
3271997006 | Sequoyah 1 | 03/22/1997 | 04/21/1997 | 9704280096 | <strong>Failure to Perform Surveillance Requirement During Containment Entry</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1997, at 2300 hours Eastern Standard Time, with Unit 1 in Mode 5 shutting down for a refueling outage, during review of radiological work permits (RWPs), it was determined that technical specification surveillance requirements for visual inspection were not performed during containment entry when containment integrity was established. The visual inspections verify that no loose debris is present in the containment which could be transported to the containment sump and cause restriction of the pump suction during loss of coolant accident conditions. On March 22, 1997, an upper-containment entry was made to install contamination control material (oil cloth and Herculite). The entry was made using an RWP that was developed for activities to be performed during Modes 5 and 6 where inspection requirements were not applicable. A subsequent evaluation determined that although the material was strongly secured, the installation of contamination control material in upper containment for upcoming ice condenser maintenance activities had the potential to adversely affect emergency core cooling system pump suction in the recirculation mode of operation. Upon identification of the condition, the involved RWP was closed to prevent further access. The cause of the condition was personnel error. Involved individuals failed to comply with plant procedures to ensure materials taken into containment are adequately controlled. Lessons learned were communicated to appropriate Radiological Control personnel and the appropriate disciplinary action is being taken in response to the personnel errors. The appropriate procedure has been revised to improve administrative controls during containment entries when containment integrity is established.
3271997007 | Sequoyah 1, Sequoyah 2 | 04/04/1997 | 05/01/1997 | 9705070157 | <strong>Diesel generator starts that resulted from cutting a cable while drilling a panel and During repairs to the damaged cable.</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1997, at approximately 0130 hours, Eastern Standard Time (EST), with Unit 1 in a refueling outage with the core offloaded and Unit 2 in power operation at approximately 100 percent, an Engineered Safety Feature (ESF) actuation occurred. Diesel generators (DGs) (1A-A, 2A-A, and 2B-B) started when a drill bit being used to drill into an electrical panel in the main control room, cut into the cable bundle connecting the 1A-A 6900-V Shutdown Board (SDBD) normal feeder handswitch to its associated electrical circuits. The 1B-B DG was tagged with an equipment clearance and did not start. A second ESF actuation occurred at approximately 1036 hours, EST, during repair of the damaged cable bundle, when personnel cut multiple wires simultaneously. The alternate feeder breaker for the 1A-A 6900-V SDBD tripped, which deenergized the board. The load shedding circuitry stripped all loads and three DGs (1-A-A, 2A-A, and 2B-B) started and the 1A-A DG energized the board (DG 1B-1B was already running as the result of a test in progress). The root cause of the first event was inadequate work practice brought on by overconfidence and lack of adherence to job performance standards. The root cause of the second event was improper control over sensitive plant activity due to lack of adherence to job performance standards. Following the first event, work was stopped for all electrical modifications for one shift, and stand down meetings were held site-wide to discuss the event. would perform an evaluation of the conditions prior to drilling. Following the second event, work activities on the cable repair were suspended and an assessment of electrical maintenance employee performance was performed. Disciplinary actions have been taken with the appropriate individuals.
3271997008 | Sequoyah 1, Sequoyah 2 | 03/22/1997 | 12/15/1997 | 9712230085 | <strong>Failure to Properly Perform Surveillance Testing on the Containment Air Return Fan Start Logic, the Blackout and Auto Sequencing of the Station Fire Pumps, and Three Functions of the Solid State Protection System.</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1997, it was determined that surveillance testing of the blackout and auto sequencing timer circuit for the station fire pumps and the containment air return fan auto start signal circuitry may not have been tested correctly. The testing method for the blackout and auto sequencing timer bypassed the blackout auto sequencing circuit so that it was not properly tested. The surveillance instruction for the containment air return fan failed to ensure that the contacts would function properly. The root cause of the identified conditions was determined to be inadequate surveillance instructions. Testing was performed to ensure that the circuits were performing properly. The surveillance instruction for testing the fire pump logic was revised to remove the option to use the handswitch in the main control room. The surveillance instruction for testing of the containment air return fans logic was revised to include steps to require testing of the containment air return fans SSPS contacts each outage. On November 19, 1997, plant personnel determined that the solid state protection system (SSPS) surveillance testing was inadequate for three SSPS functions. The root cause of the condition was a design deficiency in the Westinghouse semi-automatic tester. This resulted in the failure to test all possible parallel logic inputs. The applicable technical specification action was entered, both trains of each unit were tested, and testing found the three SSPS functions operable. Applicable procedures were revised to properly test parallel SSPS inputs.
3271997009 | Sequoyah 1, Sequoyah 2 | 05/21/1997 | 06/20/1997 | 9706260310 | <strong>Failure to Perform Response Time Testing of the Containment Radiation Monitor Following Maintenance Activities as Required by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1997, it was discovered that a Unit 2 containment purge radiation exhaust monitor had not been response-time tested, following completion of maintenance activities, as required by technical specifications. During the extent of condition review, it was identified that a Unit 1 containment purge exhaust radiation monitor had not been response-time tested following replacement of the time-delay relay. The radiation monitors were declared inoperable. A response-time test was performed on the radiation monitors and they were determined to be functioning properly and declared operable. The cause was determined to be a lack of understanding of the response-time surveillance requirements that have to be satisfied for operability of the containment purge radiation monitors following maintenance activities that could affect the response-time of these radiation monitors. Unlike the other radiation monitors, the containment purge radiation monitors require a response-time test for operability. The lessons learned from this event have been communicated with the appropriate personnel. Plant procedures have been revised to require that work order PMTs be structured in two parts: a) for maintenance tests, and b) for TS return to operability. Plant procedures have been revised to add a question to the Operations work pre-approval checklist to address work that could potentially invalidate a previously satisfied TS surveillance requirement. Inconsistencies in the calibration and response-time surveillances as well as in the PMT maintenance test matrix for the containment purge exhaust radiation monitors have been corrected.
3271997010 | Sequoyah 1, Sequoyah 2 | 06/26/1997 | 07/26/1997 | 9708060094 | <strong>Failure to Properly Return a Portion of the Fire Protection System to Service Following Modification Activities.</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1997, TVA personnel discovered that the manual isolation valve for the fire protection system flow control valve (FCV) that supplies the auxiliary control room (ACR) sprinkler header was closed. The ACR sprinkler system was removed from service on June 16, 1997, as part of the fire protection system modification activities. The system was isolated and a portion of piping, including the manual isolation valve, were removed from the system. The piping was replaced and the manual isolation valve was reinstalled. The clearance was removed for the performance of the post modification test (PMT). The clearance was closed based on a leak check being performed. The manual isolation valve position was not verified before returning the equipment to service. The fire impairment permit was closed and the equipment was declared operable. The root cause of this event is a failure to follow procedures. The clearance process was not followed when the equipment was returned to service. The clearance process requires the valves within a clearance boundary to be verified in the correct position before closing the clearance. The verification of the valves within the clearance boundary was not performed. The manual isolation valve was opened and the ACR sprinklers were declared operable. Appropriate personnel actions have been taken for the individuals involved with the event. The lessons learned from this event were communicated to the appropriate site personnel.
3271997011 | Sequoyah 1, Sequoyah 2 | 07/25/1997 | 09/17/1997 | 9709240232 | <strong>Operation of Vital Battery Board #4 Without a Battery Source.</strong><br /><i>Abstract:&nbsp;</i>This report was revised to provide changes to the analysis of the event and additional information relative to performance of operator watchstanding. While conducting a walkdown of the Sequoyah Nuclear Plant (SQN) 125 Vdc vital electrical system, Operations training personnel found the 125 Vdc vital battery board #4 improperly aligned. Specifically, in accordance with plant operating instructions, Operations personnel should have connected the 125 Vdc vital battery #5 to battery board #4 to supply battery power when removing the 125 Vdc battery #4 from service. In this event, operations personnel failed to properly align the 125 Vdc vital battery #5 to the 125 Vdc vital battery board #4 when they misread and incorrectly performed an instruction step in the operations procedure. This resulted in an improper alignment whereby 125 Vdc vital battery board #4 was in service for a period of time with no battery source connected. This is a condition of operation prohibited by SQN Technical Specifications (TS). Upon discovery of the condition, the control room operators took prompt corrective action and connected the 125 Vdc vital battery #5 to the 125 Vdc vital battery board #4 and exited TS actions. The root cause of the event was personnel error. Corrective actions include appropriate disciplinary action for individuals involved in the event, revision of the appropriate instructions to caution of the possibility of breaker misalignment, and provision of unique identifiers for the 125 Vdc vital battery breakers and the 125 Vdc vital battery board breakers.
3271997012 | Sequoyah 1 | 08/01/1997 | 09/02/1997 | 9709090108 | <strong>Manual Reactor Trip Due to Loss of Control Air.</strong><br /><i>Abstract:&nbsp;</i>While implementing a modification to improve the materiel condition of the control and Service Air System at Sequoyah Nuclear Plant (SQN), the control air header pressure dropped rapidly after modifications personnel cut into a six-inch control air header located inside an equipment clearance boundary. The loss of control air pressure resulted in a runback of the Unit 1 and Unit 2 Turbines and instabilities in Unit 1 secondary side flows sufficient to warrant a manual trip of the Unit 1 reactor. The immediate cause of the loss of control air header pressure was corrosion products (rust debris) that inhibited full closure of one of the six-inch gate valves used as a clearance boundary. The root cause of this event is an inadequate work boundary during performance of work on the Control and service Air System. The inadequate work boundary was the result of the poor materiel condition in this portion of the Control and Service Air System. Corrective actions include the following: 1) Operations personnel isolated the breach within approximately 7 minutes following the manual trip of Unit 1, 2) TVA will remove the corrosion buildup in the affected portions of the Control and Service Air System and will inspect other portions of the air system, as appropriate, for excessive corrosion, and 3) TVA will evaluate the adequacy and frequency of preventative maintenance (PM) on the affected portions of the Control and Service Air System and revise the PMs, as appropriate.
3271997013 | Sequoyah 1, Sequoyah 2 | 06/01/1995 | 01/11/1999 | 9901210356 | <strong>Missed Surveillance as a result of an Inadequate Procedure Revisions</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1997, plant personnel determined that the breaker for a fuel handling exhaust fan did not meet the Technical Specification (TS) Surveillance Requirement (SR). The breaker is the isolation device protecting a safety-related bus from the nonqualified load. Plant personnel had performed an inadequate procedure revision and an inadequate review of the revision in March 1990. The procedure was revised and was successfully performed on the breaker to comply with TS requirements. On April 6, 1998, plant personnel determined that the breaker for the onsite paging system did not meet TS SR. The breaker is the isolation device protecting a safety-related bus from the nonqualified load. Plant personnel performed an inadequate review of a modification change package. They failed to identify that the breaker needed to be added to the appropriate procedure to ensure that the SR would be met. The appropriate procedures were revised to ensure the breaker is tested in accordance with TS. On December 16, 1998, plant personnel determined that two penetration overcurrent protection fuses were not included in the surveillance program. Plant personnel had performed an inadequate procedure revision. The appropriate procedures were revised to include the fuses.
3271997014 | Sequoyah 1, Sequoyah 2 | 10/23/1994 | 12/01/1997 | 9712090036 | <strong>Missed Surveillances as a result of Inadequate Procedures and a Failure to Follow a Procedure.</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1997, plant personnel discovered that the Unit 2 reactor coolant system power operated relief valves (PORVs) were not cycled in Mode 4 as required by technical specifications. Cycling of the valves occurred under near equivalent Mode 4 conditions, with the unit in Mode 5 following establishment of a bubble in the pressurizer. Plant personnel subsequently determined that the PORVs on both units were previously cycled in the incorrect mode. Additionally, plant personnel determined that testing of six diesel generator (D/G) load sequence timers and D/G lockout features occurred in the incorrect mode. The cause of the failure to perform the PORV surveillance in the correct mode was ineffective change management. A procedure revision allowed two dissimilar surveillance requirements to be performed by one surveillance instruction and was scheduled by one matrix identification number. Unit 2 was cooled down to Mode 4, and the surveillance was successfully performed in Mode 4 as required by technical specifications. The general operating surveillance checklists were reviewed and revised to ensure that the PORVs are tested in Mode 4.
3281997001 | Sequoyah 2, Sequoyah 1 | 01/17/1997 | 10/06/1997 | 9710150170 | <strong>Missed surveillance on the turbine trip contacts of the reactor trip breakers.</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1997, with Unit 2 in power operation at approximately 100 percent, personnel discovered that the spare breaker installed on August 29, 1996, did not have the P-4 turbine trip contact tested as required by SR 4.3.1.1.1.C.22.G. A second problem was also discovered where the post maintenance test (PMT) procedure used for the replacement of reactor trip breaker "A" (RTA) on August 29, 1996, was inadequate. The procedure only tested the solid state protection system (SSPS) functions of P-4 with the breaker in the as-left position, rather than testing in both the open and closed positions as required to satisfy the surveillance. However, the surveillance was satisfied when the breaker was tested in the closed position during a forced outage on October 17, 1996. <br /><br /> In order to perform the necessary tests for the turbine trip contacts on RTA, Unit 2 entered TS LCO 4.0.3 at 2105 hours Eastern Standard Time (EST) on January 17, 1997. The required testing for the turbine trip contacts was performed, RTA was declared operable, and LCO 4.0.3 was exited at 1249 hours EST on January 18, 1997. Discovery of this problem has resulted in the discovery of several other instances in the past where SQN was in noncompliance with SR 4.3.1.1.1.C.22.G. The root cause was a lack of understanding of the design basis definition of P-4 and of the surveillance requirements necessary to return reactor trip breakers to operable status.
3281997002 | Sequoyah 2 | 04/01/1997 | 05/06/1997 | 9705140023 | <strong>Failure to Maintain Two Offsite Power Sources as Required by Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1997, it was determined that a problem existed with Start Bus 1A alternate feeder breaker. The breaker was removed from service and the normal feeder breaker was placed in service. The breaker was inspected and it was determined that the main contact compression was out of tolerance and a gap of the main contacts caused minor arcing and burning of the arcing contacts. The breaker was determined to be inoperable since April 1, 1997, when it had been placed in service. The cause was determined to be the inadequate refurbishment of quality-related breakers by Asea Brown Boveri (ABB). Installation of ABB refurbished breakers was suspended. Main contact compression checks on two ABB breakers that had been recently refurbished were performed and were determined to be satisfactory. An inspection of the refurbished breakers currently installed on Start Bus 1A was performed, no refurbished breakers are currently installed on Start Bus 1B. An evaluation of the refurbished breakers that are in service was performed. The breakers were determined to be functioning properly. Increased inspection requirements for refurbished breakers has been defined and incorporated into plant procedures. Appropriate procedures have been revised to include post maintenance testing requirements to ensure that breakers function properly following installation.
3311997001 | Duane Arnold | 01/15/1997 | 02/14/1997 | 9702250020 | <strong>Failure to Comply with Technical Specification for Main Steam Line Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage (RFO) 14, the Duane Arnold Energy Center (DAEC) performed Noble Metal Chemical Addition (NMCA). This is a first of a kind process to allow corrosion protection of vessel internals with decreased Hydrogen Water Chemistry (HWC) injection rates and lower radiation dose rates at the facility. On January 15, 1997, following the November 16, 1996 plant startup from RFO 14, it was determined that the DAEC failed to meet the requirement of Technical Specifications (TS) Table 3.2-A, in that the Main Steam Line Radiation Monitors (MSLRMs) were not set to trip at
3311997002 | Duane Arnold | 02/07/1997 | 03/06/1997 | 9703200205 | <strong>Both Standby Gas Treatment Trains Inoperable Due to Low Carbon Bed Efficiencies</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1997, the plant was operating at 100% power when the 'A' train of Standby Gas Treatment (SBGT) failed the carbon bed efficiency test during performance of Surveillance Test Procedure STP 471,003, Standby Gas Treatment System HEPA & Charcoal Filter Efficiency Tests. Carbon bed efficiency was found to be 99.39%. The Technical Specification limit is 99.9% as listed in the surveillance. On January 10, 1997 the 'B' train of SBGT also failed its carbon bed efficiency test with an efficiency of 99.89%. This meant both trains of SBGT were potentially inoperable concurrently. The root cause of these failures was bypass leakage around the carbon bed caused by settling of the carbon, as well as removal of carbon for sampling without refilling the bed. Inadequate corrective actions for a similar failure on the 'B' SBGT train in 1995 also contributed to this event. <br /><br /> Approximately 80 pounds of carbon was added to each train of the SBGT System. (The trains have a design capacity of 2500 pounds). Subsequently each train was retested with satisfactory results. The 'A' SBGT System was declared operable on January 9, 1997 at 1815. The 'B' SBGT System was declared operable on January 10, 1997 at 1714. <br /><br /> The surveillance program will monitor the carbon beds sampled to assure an adequate level of carbon is maintained. By May 28, 1998, additional steps will be taken to ensure that settling is accounted for when filling the beds. By July 28, 1998, further changes to the surveillance program to allow monitoring the beds for settling will be considered. In addition, the Plant Engineering Supervisor will review this event with plant engineers by March 28, 1997, to reinforce the expectation for and the importance of taking adequate corrective actions. <br /><br /> This event had no effect on the safe operation of the plant.
3311997003 | Duane Arnold | 02/20/1997 | 03/17/1997 | 9703240236 | <strong>Reactivity Anomalies Surveillance Requirement Not Met due to Inadequate Technical Review of Procedure Change</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1997, while operating at 100% power, it was determined that the method used for performing reactivity anomaly checks did not comply with the Technical Specification required methodology. The method being used compared design and actual hot eigenvalues rather than rod densities. The applicable Limiting Condition for Operation (LCO) was entered. <br /><br /> The change in method used occurred in 1995 when an improved method was made available to General Electric plants that use 3-D Monicore computer programs. The technical review of the associated test procedure change was inadequate in that the new method was not recognized as conflicting with the Technical Specifications. <br /><br /> The LCO required analysis showed that there was no true reactivity difference. The information needed to re-implement the Technical Specification required methodology was obtained from General Electric, the test procedure was revised accordingly, and the test was satisfactorily performed. The LCO was exited on February 21, 1997. Improvements have been made to the procedure change review process. <br /><br /> There was no effect on safe plant operation because a valid, alternative method of performing reactivity anomaly checks was in use during the period of non-compliance.
3311997004 | Duane Arnold | 02/23/1997 | 03/24/1997 | 9704080373 | <strong>Three of four Main Steam Line Low Reactor Pressure Isolation instrumentation not in agreement with the preferred direction of the numerical values in the Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1997 with the plant operating at 100% power, it was determined that three (3) out of four (4) of the instruments that initiate the isolation of the Main Steamlines (MSL) on low Reactor pressure ( < 850 psig in Run mode) had their as-left settings from their most-recent calibration not in agreement with the numerical value, in the preferred direction, as given in Technical Specifications (TS) Table 3.2-A for Isolation Actuation Instrumentation. <br /><br /> The TS Actions for the MSL isolation instruments were conservatively entered to place the Trip System with the most "inoperable" channels in the tripped condition within one (1) hour and to place the Reactor in Startup mode within six (6) hours. Although the instruments were considered to be Operable per the plant engineering setpoint calculations, the plant calibration procedures were revised to recalibrate the instruments' as-left settings to be in verbatim compliance with the preferred direction of the TS numerical value. The instruments were subsequently recalibrated and the TS Actions exited. This condition was caused by the DAEC TS being "custom" in nature and having a unique definition of Limiting Safety System Setting that allows the Limiting Trip Point For Operation to be controlled outside the TS. There was no effect on safe operation of the plant.
3311997005 | Duane Arnold | 02/24/1997 | 03/26/1997 | 9704080098 | <strong>Setpoint for "Recirculation Flow Upscale" Rod Block Greater than Technical Specification Allowable</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 24, 1997, while operating at 100% power, it was determined that the setpoint for the 'Recirculation Flow Upscale' rod block was not in accordance with the Duane Arnold Energy Center (DAEC) Technical Specifications (TS). The applicable Limiting Condition for Operation (LCO) was entered, appropriate rod block channels were placed in the tripped condition, and the LCO was exited. <br /><br /> The surveillance test procedure (STP) was subsequently revised and performed to adjust the 'Recirculation Flow Upscale' rod block setpoint to be in compliance with the DAEC TS. <br /><br /> The root cause of this event is inadequate implementation of TS Amendment 193, which was issued on April 14, 1993. that the appropriate 'Recirculation Flow Upscale' rod block setpoint was used in STP 42C006-SA. <br /><br /> This event had no effect on the safe operation of the plant.
3311997006 | Duane Arnold | 05/30/1997 | 06/29/1997 | 9707090050 | <strong>Inadequate Functional Test of the High Pressure Coolant Injection System Leak Detection Time Delay</strong><br /><i>Abstract:&nbsp;</i>On May 30, 1997, the plant was operating at approximately 40% power and increasing. During a review of a quarterly functional surveillance test procedure (STP 42A024-Q, Suppression Pool Steam Leak Detection Functional Test) for its adequacy of testing to meet future Improved Technical Specifications (ITS) requirements, it was discovered that the procedure did not fully meet the current Technical Specifications (TS) surveillance requirements. The cause of the event was the procedure contained an incorrect instruction which directed personnel to depress the override hand switch after a timer started but before it timed out to activate the contacts of the time delay relay. In this condition, the contacts were not tested to determine if they would activate when required. The incorrect instruction had existed in the original procedure written in 1974. The root cause of this event is inadequate previous technical reviews which did not identify the incorrect instruction and was subsequently carried on into the current procedure. Corrective actions included revising the procedure, re-performing the functional test, and reviewing other functional test procedures for testing time delays required by the current TS. As a long term corrective action and as part of an ongoing effort for converting to ITS, all future ITS required STPs are receiving or will receive an equivalent level of review to ensure they meet all requirements. This event had no effect on the safe operation of the plant as all logic performed as required when tested.
3311997007 | Duane Arnold | 06/24/1997 | 07/24/1997 | 9708050169 | <strong>Inadequate Test of the Reactor Mode Switch to Shutdown Position Rod Block Function and Rod Block Monitor</strong><br /><i>Abstract:&nbsp;</i>On June 24 and 25, 1997, while operating at 100% power, it was discovered that two surveillance procedures did not fully satisfy the requirements in the current Technical Specifications (TS). The events were discovered during the review of the procedures for their adequacy to meet Improved Technical Specifications (ITS) requirements. The procedures were STP 41A012-CY, Reactor Mode Switch In Shutdown - Instrument Functional Test, and STP 42C002-Q, Rod Block Monitor Functional Test. The applicable Limiting Condition for Operation (LCO) actions were performed; a tagout directing Operations personnel to verify a rod block if the Reactor Mode Switch (RMS) were placed in the "SHUTDOWN" position was hung on the RMS, and a fuse was pulled in Panel 1C28 to insert a rod block in order to prevent control rod withdrawal. <br /><br /> The cause of the events was procedural inadequacy. The root cause is inadequate implementation of TS Amendment 193. A contributing factor to both events was lack of details in the current TS. STP 41A012-CY has been revised and is available for the next plant shutdown. STP 42C002-Q has been revised and was re-performed satisfactorily on both RBM channels at 2300 hours, on July 8, 1997. The ITS will include a more detailed description of what is required for Reactor Manual Control System multiplexer testing. Other ITS-required surveillance procedures will receive an equivalent level of review to ensure they meet all requirements. This will] be completed prior to the implementation of the ITS. <br /><br /> These events did not impact the safe operation of the plant.
3311997008 | Duane Arnold | 06/25/1997 | 07/24/1997 | 9708010247 | <strong>Momentary Loss of Secondary Containment During Routine Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1997, while the plant was operating at 100% power, it was determined that an opening in secondary containment was created that exceeded that which is administratively allowed to comply with Technical Specification (TS) 3.7.J.1. Specifically, during the performance of routine maintenance, personnel removed a valve bonnet and valve internals which created an opening in secondary containment in excess of the size administratively allowed. The maintenance actions resulted in a total breach of secondary containment of approximately 50 square inches. Administrative requirements limit openings to less than 12.7 square inches. Upon discovery of the secondary containment breach, Operations declared secondary containment inoperable and the associated one hour Limiting Condition for Operation (LCO) was entered per TS 3.7.J.2.b. Maintenance personnel reassembled the valve and secondary containment was thereby reestablished. The total duration of this event was approximately 20 minutes therefore, the TS action statement was satisfied. <br /><br /> The cause of this event was less than adequate attention to detail during the preparation of a tagout for maintenance.
3311997009 | Duane Arnold | 07/24/1997 | 08/21/1997 | 9708270064 | <strong>Inadequate Surveillance Testing of Reactor Water Cleanup Area Differential Isolation Logic Caused by Lack of Attention to Detail when Processing a Technical Specification Amendment.</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1997, during a review of surveillance test procedures for conversion to the Improved Standard Technical Specifications (ITS), a deficiency in an existing procedure was discovered. The procedure for the TS required Channel Functional Test (CFT) for the Reactor Water Cleanup (RWCU) Area Ventilation Differential Temperature-High Isolation was not written to perform the CFT in accordance with the TS definition of a CFT. <br /><br /> The cause of this event was inattention to detail associated with processing and implementation of TS Amendment 193, which was issued on July 21, 1993. This amendment inadvertently deleted an exception footnote for the RWCU Area Ventilation Differential Temperature surveillance requirement. This condition resulted in a failure to fully perform Technical Specification required surveillances and is being reported pursuant to 10CFR50.73(a)(2)(i)(B). <br /><br /> Following discovery, the existing annual channel calibration tests were successfully performed, which fully satisfied the requirements of the CFT. Other corrective actions include revising the procedure to incorporate the CFT definition, Licensing department briefings, and continued reviews of surveillance test procedures as part of the conversion to ITS. The actual and potential safety consequences associated with this event were minimal as all equipment performed properly when tested.
3311997010 | Duane Arnold | 08/14/1997 | 10/07/1997 | 9710140180 | <strong>Primary Containment Isolation From Failed CR120A Relay Coil</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1997, while the plant was operating at 100% power, alarms were received indicating isolation of the drywell sumps and shutdown cooling. <br /><br /> Operations declared a 24 hour Limiting Condition for Operation (LCO) per Technical Specifications (TS) 3.6.C.4 for the inoperability of the drywell floor and equipment drain sumps. <br /><br /> Initial investigation found a primary containment isolation system fuse blown. In accordance with procedure, the fuse was replaced while instrumentation monitored current, and the fuse held. This re-energized four of the five relays that had dropped out. Investigating the relay that failed to re-energize, it was found to have an open-circuited coil. The failed relay was a General Electric (GE) CR120A type used for Primary Containment Isolation System (PCIS) Group 2 & 4 Division 2 Outboard Control. <br /><br /> Maintenance personnel replaced the failed relay coil and the drywell floor and equipment drain system was thereby reestablished, and the LCO exited. The total duration of this event was approximately 8 hours and within TS requirements.
3311997011 | Duane Arnold | 09/19/1997 | 10/10/1997 | 9710220042 | <strong>Missed TS Surveillance Testing of Power Operated Primary Containment Isolation Valves Due to Improper Administration of a TS Amendment</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1997, during the revision of a surveillance test procedure, a non-compliance with Technical Specifications (TS) was discovered. TS Surveillance Requirement 4.7.B.1.a. requires a cyclic closure time test of power operated primary containment isolation valves (PCIVs). Included in the list of PCIVs to be tested are 20 solenoid operated valves which provide isolation of the sample supply and return lines for the Containment Atmosphere Monitoring (CAM) system. These twenty valves had been cycled on a quarterly frequency, but had not been closure time tested in accordance with the above TS. <br /><br /> The cause of this event was the improper administration of TS Amendment 181. Prior to Amendment 181, TS Table 3.7-3 listed the PCIVs and, for the solenoid valves in question, annotated the maximum operating times as "NA". The amendment relocated the list of PCIVs from the TS to a plant administrative control procedure (ACP), and in the process, omitted the "NA" for the valves' stroke times. In the absence of the previous "NA" and given the wording of the ACP, and in the context of strict compliance, it is concluded that a TS requirement to closure time test the twenty CAM system solenoid valves was inadvertently created and unrecognized as a result of TS Amendment 181. Corrective actions included a procedure revision, performing the closure time tests, and reviewing all PCIV stroke time testing. There were no actual or potential safety consequences associated with this event.
3311997012 | Duane Arnold | 11/13/1997 | 12/12/1997 | 9712180228 | <strong>Spurious RCIC Steam Leak Detection Isolation</strong><br /><i>Abstract:&nbsp;</i>At 2022 on November 13, 1997, with the plant operating at 100% power, a spurious primary containment isolation system (PCIS) group VI isolation occurred which resulted in the automatic closure of the outboard Reactor Core Isolation Cooling (RCIC) steam supply isolation valve, MO2401. The isolation signal originated from TDS2445A, a RCIC room area differential temperature switch. The isolation signal was present for approximately 3 8 seconds before resetting itself Operators dispatched to the RCIC room confirmed that a steam leak did not exist. Extensive testing of TDS2445A failed to indicate a cause for the event. TDS2445A was replaced and the isolation was cleared. There was no effect on plant operation or safety.
3311997013 | Duane Arnold | 11/19/1997 | 12/19/1997 | 9801020115 | <strong>Inoperable Primary Containment Isolation Valves Exceeded Technical Specification Limiting Conditions for Operation</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1997, the plant was operating at 100% power. It was determined, as a result of a completed design review, that when Control Building/Standby Gas Treatment System Instrument Air Compressors 1K3/4 are out-of-service, all components supplied by these compressors are inoperable. The components supplied by 1K3/4 include primary containment isolation valves (PCIVs) CV4309, CV5704A, CV5718A, CV4306, CV4310, CV5704B, CV5718B, CV4307 and CV4308. Technical Specification (TS) 3.7.13.2 states "With one or more of the primary containment isolation valves inoperable, maintain at least one isolation valve OPERABLE in each affected penetration that is open and within 4 hours either: a. Restore the inoperable valve(s) to OPERABLE status, or b. Isolate each affected penetration flow path." TS 3.7.B.3 states "If Specifications 3.7.B.1, and 3.7.B.2 cannot be met, an orderly shutdown shall be initiated and the reactor shall be in at least HOT SHUTDOWN within the next 12 hours and COLD SHUTDOWN within the following 24 hours." A review of maintenance history for 1K3/4 revealed that 1K3 was removed from service on January 28, 1997 at 0425 until January 31, 1997 at 1955 for a total out-of-service time of 91.5 hours, thus making the aforementioned PCIVs inoperable for 91.5 hours, exceeding the action times of 3.7.B.2 and 3.7.B.3. This condition constitutes an "operation or condition prohibited by the plant's Technical Specifications" as described in 10CFR50.73(a)(2)(i)(B). The cause of this event has been determined to be a misinterpretation of two Technical Specification definitions. Appropriate plant procedures have been revised to provide the correct guidance to operators when 1K3/4 are inoperable or unavailable. <br /><br /> There was no effect on plant operation or safety.
3331997001 | FitzPatrick | 01/23/1997 | 02/13/1998 | 9802230148 | <strong>Manual Reactor Scram Due to Fouling of Circulating Water System Traveling Screens</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1997 at 2210 hours with the plant operating at 100 percent, power reduction was commenced due to potential loss of water inventory in the Circulating Water System's (CWS) intake bays. A high differential water level annunciator indicated fouling of the CWS traveling screens. Attempts to clean the screens resulted in the screens becoming inoperable due to shear pin failures. At 2224 hours, with power level reduced to approximately 57 percent, and following unsuccessful attempts to start the screens, a manual scram was initiated. <br /><br /> Cause of the event was a potential loss of CWS intake water due to restriction of flow through the three CWS traveling screens. A contributing cause was less than adequate work scheduling. <br /><br /> Actions taken included reviewing event lessons learned with plant personnel, revising Operating Procedure OP-4, "Circulating Water System", and evaluating the adequacy of the shear pins used on the screens.
3331997002 | FitzPatrick | 01/24/1997 | 02/24/1997 | 9702280096 | <strong>Shutdown Cooling Isolation</strong><br /><i>Abstract:&nbsp;</i>The plant was shutdown and being cooled down for a maintenance outage. At 0937 hours on 1/24/97, Residual Heat Removal/Low Pressure Coolant Injection (RHR/LPCI) [BO] pump D was started in the shutdown cooling mode and the inboard and outboard shutdown cooling suction isolation valves closed upon initial startup of the pump. The isolation was caused by a pressure transient. When the RHR pump was started, air in the shutdown cooling suction piping caused a pressure pulsation which was felt by the isolation pressure switches. Reactor vessel pressure was verified to be 4.5 psig at the time of the event. After reventing the system, the shutdown cooling system was successfully placed in service at 1256 hours.
3331997003 | FitzPatrick | 02/13/1997 | 10/26/1999 | ML99313001 | <strong>Potential Overpressurization of Containment Penetrations Due to Thermal Expansion</strong><br /><i>Abstract:&nbsp;</i>As a result of Generic Letter (GL) 96-06, ~Assurance of Equipment Operability and Containment Integrity During Design Basis Accident Conditions~, the Authority identified containment penetrations which could be subjected to overpressurization due to thermal expansion ofthe entrapped water during design basis accidents (DBAs) when the penetrations are isolated. On 2/13/97 the Authority reported that the overpressurization of containment penetrations could potentially be a condition that is outside the design basis of the plant. The cause of this event is that pressurization of these penetrations due to thermal expansion of entrapped fluid between the containment isolation valves was not considered during the design of the FitzPatrick plant. <br /><br /> Operability determinations have been completed in accordance with GL 91- 18, '1lnformation to Licensees Regarding Two NRC Inspection Manual Sections on Resolution of Degraded and Non-Conforming Conditions and on operabilityn to verify operability. The operability determination demonstrated that containment integrity is maintained and safety functions are not compromised for the susceptible containment penetrations. Long term resolution of these overpressurization concerns has been evaluated in our response to GL 96-06. The results of this evaluation were submitted to the NRC in correspondence dated May 27, 1997.
3331997004 | FitzPatrick | 04/28/1997 | 05/30/1997 | 9706090047 | <strong>Failure of Safety Relief Valve to Open During Set Point Verification Testing Due to Foreign Material Intrusion</strong><br /><i>Abstract:&nbsp;</i>During testing of actuating mechanisms (pilot assemblies) for Main Steam Safety Relief valves (02RV-71A through L) at Wyle Laboratories, valve 02RV-71J (pilot serial number 1217), would not lift at applied test pressures. The Authority completed an equipment failure evaluation on the subject pilot assembly to determine the cause of the failure. During the pilot valve disassembly and inspection, a small screw was found wedged in the valve operator subassembly, causing the valve not to open when pressurized. <br /><br /> The source of the loose screw was not established, however, the screw was identified as material similar to that which is typically removed from the pilot assembly prior to testing and reattached following completion of testing. <br /><br /> The laboratory has implemented a test procedure revisions to minimize the potential for foreign material intrusion into the valve bonnet area during testing evolutions.
3331997005 | FitzPatrick | 05/25/1997 | 04/13/1998 | 9804210327 | <strong>Manual Reactor Scram Due to Failure of the Number 3 Turbine Control Valve</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1997 at 2102 hours, operators commenced a reactor shutdown from 100 percent power due to number three Main Turbine Control Valve (TCV-3) failing in the fully opened position. Power level was reduced and maintained at approximately 70 percent while unsuccessful attempts were made to close the valve. At 0456 hours on May 25, 1997, operators initiated a manual reactor scram followed by a manual turbine trip to support a reactor shutdown while maintaining reactor pressure control. Following the manual scram, a Primary Containment Isolation System (PCIS) Group II isolation occurred (Reactor Building Ventilation System isolation, and initiation of the Standby Gas Treatment System trains A and B) on low reactor water level. <br /><br /> The TCV failure was the result of a damaged valve spring can coupling. The cause for the damaged coupling was identified as a result of improperly installed bolting material. <br /><br /> Corrective actions included valve spring can coupling bolt replacement on the four TCVs and the four Combined Intermediate Valves (CIVs).
3331997006 | FitzPatrick | 06/16/1997 | 07/16/1997 | 9707230080 | <strong>Instrumentation Isolation Trip Function Surveillance Test Not Performed At Required Frequency</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1997, while performing a review of the Instrument and Controls (I&C) Department Surveillance Test Program, an I&C supervisor discovered that certain Primary Containment Isolation System instrument channel response time tests required per Technical Specifications (TS) had not been performed within the T.S. required surveillance test interval. T.S. Section 4.2.A requires a once per 24 month response time test of one trip channel in each trip system. This interval (including a 25 percent extension period allowed by T.S. 4.0.B) was found to have been exceeded. At the time of the discovery the mode-switch was in the RUN position with the plant operating at 100 percent rated power. <br /><br /> The cause for the missed surveillances was personnel error due to less than adequate scheduling of instrument surveillance test requirements. <br /><br /> Corrective actions include: satisfactory completion of the surveillance tests a review of the I&C surveillance test schedule against T.S. response time testing surveillance requirements to ensure the schedule was current and no other surveillance test had been missed, revising both the Surveillance Test Program schedule and associated Instrument Surveillance Procedures, and conducting briefings on the details and lessons learned from this event.
3331997007 | FitzPatrick | 06/17/1997 | 07/11/1997 | 9707160083 | <strong>Reactor Core Isolation Cooling Automatic Isolation During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>At 11:18 hours on 6/17/97 while performing Surveillance Test, ST-24E "RCIC Logic System Functional and Simulated Automatic Actuation Test" at 100% power, a Reactor Core Isolation Cooling (RCIC) system automatic isolation occurred. During the surveillance test, a RCIC high steam line flow signal was received, causing the isolation. The momentary high steam line flow signal was caused when steam was admitted to a de-pressurized volume of piping between the outboard containment isolation valve (13MOV-16) and the RCIC steam admission valve (13MOV-131). This portion of piping becomes de-pressurized and re-pressurized during the performance of the surveillance test. The RCIC automatic isolation feature functioned as designed. <br /><br /> A Temporary Operating Procedure was used to restore the RCIC system. The RCIC system was verified to be operable. Procedures associate with RCIC system were reviewed to determine if a similar system configuration could result. The review identified an operating procedure that was revised and two surveillance procedures that will be revised prior to their next performance. The revision to these procedures will change the method used to re-pressurize the piping.
3331997008 | FitzPatrick | 08/06/1997 | 09/05/1997 | 9709100077 | <strong>Both Trains of the Standby Gas Treatment System were Declared Inoperable Due to Flow Restriction in the Discharge Line</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1997 at 07:57 while at 100% power, operations observed flow oscillations in the "A" train of the Standby Gas Treatment System (SBGT). When Operations shifted to the "B" train, similar oscillations were observed. At 10:38 operations initiated a surveillance test to verify operability. Neither train met the necessary flow requirements of 6000 SCFM to perform the test. At 11:24 both trains were declared inoperable and the plant entered a limiting condition for operation (LCO) per Technical Specification 3.7.B.3, and 3.7.C requiring the plan to be in cold shutdown within 24 hours. A reactor shutdown was initiated at 12:01. <br /><br /> The installation of a manometer on the discharge line confirmed a restriction in the discharge piping. Further troubleshooting determined a 2 inch drain line connected to a low point on the 24 inch SBGT discharge pipe was clogged. The accumulation of water in the 24 inch line eventually restricted f ow through the line. When the 2 inch drain line was cleared, approximately 1700 gallons of water was drained from the discharge line. At 00:30, 8/7/97, with the plant at approximately 26% power, the SBGT system was declared operable and the plant exited the LCO. Corrective actions include the development of a periodic surveillance that can adequately detect blockage in the drain line and a periodic preventive maintenance task to flush the drain line.
3331997009 | FitzPatrick | 09/05/1997 | 10/06/1997 | 9710160178 | <strong>Exceeded Quarterly Calibration Frequency For Radwaste Building Exhaust Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On September 05, 1997, while reviewing completed surveillance test data for gaseous effluent monitors, a Quality Assurance auditor discovered a Radwaste Building Exhaust Radiation Monitor instrument channel calibration test, required per Radiological Effluent Technical Specifications (R.E.T.S.), that had not been performed within the R.E.T.S. required test interval. R.E.T.S. Table 3.10-2 requires a calibration frequency of once per quarter (92 days). This interval (including a 25 percent extension period allowed by T.S. 4.0.B) was found to have been exceeded. At the time of the discovery, the mode switch was in the RUN position with the plant operating at approximately 100 percent rated power. <br /><br /> The missed surveillance was the result of personnel error. The cause for the error was poor worker practices. <br /><br /> Corrective actions included: the satisfactory completion of the instrument calibration; a review of similar test records to ensure no other surveillance tests had been missed; counseling the individuals involved in the event; conducting briefings with plant staff on the details and lessons learned from this event; and revising the Chemistry surveillance schedule program.
3331997010 | FitzPatrick | 10/21/1997 | 11/20/1997 | 9711260247 | <strong>Surveillance Testing of the Pressure Suppression Chamber - Drywell Vacuum Breakers Could Have Resulted in a Partial Loss of the Primary Containment Pressure Suppression Safety Function</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1997 at approximately 1435 hours, during a review of industry events, Engineering determined that surveillance testing of the Primary Containment Pressure Suppression Chamber - Drywell Vacuum Breakers coincident with a Loss of Coolant Accident (LOCA) will result in a partial loss of the primary containment pressure suppression function. The plant was operating in run at approximately 100% power at the time of the event. <br /><br /> During performance of Surveillance Tests (ST) 15A and ST-15F, the plant utilizes a configuration where both the 24" drywell vent valves and both the 20" torus vent valves are opened to equalize the pressure across the vacuum breakers. The vacuum breakers are then cycled open and closed. Opening the drywell and torus vent valves simultaneously establishes a flow path bypassing the pressure suppression function of the torus. Should a LOCA take place while the plant is in this configuration, an indeterminate amount of direct torus air space pressurization could occur pending full closure of the vent valves from a Primary Containment isolation signal. This could result in containment loads in excess of those currently analyzed. <br /><br /> The apparent cause of this event was that technical reviews of procedures which utilize this configuration were inadequate. The results of reviews identified two additional procedures (ST-39E and OP-37) requiring change. The four identified procedures have been revised to allow the use of a valve line-up which will not create a direct connection between the torus and drywell air spaces via the torus and drywell vent valves when primary containment integrity is required.
3331997011 | FitzPatrick | 10/24/1997 | 11/21/1997 | 9712030241 | <strong>Invalid ESF Actuation and Failure to Perform Technical Specification Required Actions While Performing Troubleshooting Activities</strong><br /><i>Abstract:&nbsp;</i>On 10/24/97 at 2040 hours, with the plant operating at 100% power in the RUN mode, an "invalid" Engineered Safety Feature (ESF) actuation signal occurred during a DC ground troubleshooting repair of the "B" High Pressure Coolant Injection (HPCI) logic circuit. At the time of the event, the HPCI system was inoperable for planned maintenance. The "invalid" ESF actuation signal was determined to be reportable because the HPCI system was not properly removed from service. Specifically, the DC ground troubleshooting repair activity required the removal of fuses 23A-F1 and 23A-F2. Fuse removal de-energized the "B" HPCI logic, which disabled the Primary Containment Isolation System (PCIS) function to the outboard HPCI steam line valves, 23MOV-60 and 23MOV-16. The licensed operators failed to recognize this condition and failed to declare the outboard HPCI steam line valves inoperable. A contributing cause of the event was that plant procedures, which isolated the same circuits, also did not include the impact on the PCIS function. Plant review of the event determined the PCIS function was rendered inoperable by the DC ground troubleshooting repair activity for a period of approximately 16.5 hours. Failure to recognize the PCIS inoperability condition resulted in violation of TS 3.7.D.2, which required the HPCI inboard or outboard steam valves to be closed and deactivated within 4 hours. Had this required action been identified and properly performed, the subsequent "invalid" ESF actuation which occurred during DC ground troubleshooting would not have been reportable. <br /><br /> Root cause evaluations of the event and related activities were completed and corrective actions were identified to prevent recurrence. The corrective actions include revisions to procedures and staff training. <br /><br /> This event was not safety significant. The "A" HPCI logic remained operable throughout the event. In the event that HPCI would have received a valid HPCI steam line isolation signal, 23MOV-15, the inboard HPCI steam line valve, would have performed the HPCI steam line isolation function.
3331997012 | FitzPatrick | 12/14/1997 | 02/10/1998 | 9802240069 | <strong>Drywell Personnel Airlock Outer Door Seals Local Leak Rate Test Not Properly Performed</strong><br /><i>Abstract:&nbsp;</i>On 12/14/97, while performing a restoration valve lineup of an Operations Surveillance Test Procedure, ST-39A, "Type B Leak Test of Airlocks", a licensed operator discovered that a local leak rate test valve (16LLRT-930) was incorrectly labeled. Further review determined the incorrectly labeled valve had resulted in an improperly performed 10CFR50, Appendix J, Type B local leak rate test (LLRT) on the outer personnel access door (i.e. the outer door seals were not tested). Technical Specification (TS) 6.20 requires primary containment leakage rate testing to be accomplished in accordance with the Primary Containment Leakage Rate Testing Program. Section 6.4.2 of the program requires that the airlock door seals be tested prior to re-establishing containment integrity and within seven days after the airlocks are opened when containment integrity is required. Based on a historical review, it has been determined that the mislabeled valve has resulted in invalid performance of the TS 6.20 required Type B LLRT on the personnel airlock outer door seals since 11/24/96. At the time of discovery, the plant was performing a reactor startup with power at approximately 25 percent with the reactor mode switch in RUN. <br /><br /> The mislabeling occurred in the course of valve replacement maintenance during a refueling outage on 11/15/96. The probable cause of the error was inattention to detail on the part of the mechanic who installed the label (it is not possible to identify which of two mechanics involved erred) and on the part of the independent label verifier who subsequently reviewed the installation. <br /><br /> Corrective actions include: removal of the incorrect label, installation and verification of a correct label on 16LLRT-930, performance of the type B LLRT on the outer personnel access door seals, and conducting briefings on the details and lessons learned from this event.
3331997013 | FitzPatrick | 12/16/1997 | 01/15/1998 | 9801220354 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to Instrument Malfunction During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1997 at 1416 hours, while performing Instrument Surveillance Procedure ISP-125B, "HPCI Auto Isolation Instrument Functional Test/Calibration (ATTS)", the High Pressure Coolant Injection (HPCI) System was declared inoperable due to an apparent failure of a Master Trip Unit (MTU) within the HPCI System's automatic isolation logic. At the time of the discovery, the plant was operating at approximately 98 percent rated power with the mode switch in the RUN position. <br /><br /> The reason for the apparent instrument failure was incomplete contact between the MTU card and the MTU card file, which caused the instrument to read downscale. <br /><br /> Corrective actions taken included: (a) completing repair activities to correct adjustments to the MTU; (b) satisfactorily completing instrument test activities and declaring HPCI System operable; and (c) reviewing lessons learned associated with this event with the Instrument and Controls (I&C) Department.
3341997001 | Beaver Valley 1, Beaver Valley 2 | 02/13/1997 | 09/17/1997 | 9709230103 | <strong>Generic Letter 96-01 Inadequate Surveillance Testing of Auxiliary Feedwater Pump Auto Start Circuitry</strong><br /><i>Abstract:&nbsp;</i>As a result of reviews being performed in response to Generic Letter 96-01, "Testing of Safety Related Logic Circuits," the following conditions have been discovered and determined to be reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i). <br /><br /> 1. On February 13, 1997, at approximately 1700 hours, with Beaver Valley Power Station (BVPS) Unit 1 at 100% reactor power, it was identified that the monthly Operational Surveillance Tests (OSTs) which verify operability of the Control Room Emergency Ventilation Subsystem do not contain adequate acceptance criteria. The OSTs were subsequently revised and were performed on February 18, 1997, at which time operability of the affected emergency ventilation subsystem was verified. The details of this condition are found on pages 2 and 3 of this report. <br /><br /> 2. On April 2, 1997, at approximately 1500 hours, with BVPS Unit 1 in Mode 5 at 0% power, it was identified that the OST which tests the Engineered Safety Feature (ESF) auto start circuitry of the Auxiliary Feedwater (AFW) pumps tests only one of two control switch parallel paths. The OST was subsequently revised and operability of the AFW pump autostart circuitry was verified by performance of the OST on April 6, 1997. The details of this condition are found on page 5 of this report. <br /><br /> 3. On April 10, 1997, at approximately 1500 hours with BVPS Unit 1 in Mode 5 at 0% power, it was identified that the ESF Actuation System P-11 interlock function of enabling/disabling automatic actuation of the pressurizer power operated relief valves was not completely tested by existing surveillance procedures. The details of this condition are found on page 7 of this report. <br /><br /> 4. On July 7, 1997, at approximately 0930 hours, with BVPS Units 1 and 2 in Mode 5 at 0% reactor power, it was identified that portions of the wiring for the Overtemperature Delta T Reactor Trip System Instrumentation Function were not tested by existing surveillance procedures. This condition was identified at both Units. Additional testing was performed at both Units to address this. The details of this condition are found on page 10 of this report. <br /><br /> 5. On July 26, 1997, at approximately 1530 hours, with BVPS Unit 1 in Mode 5 at 0% reactor power, it was identified that the surveillance testing of the control circuit logic for the Emergency Diesel Generators' (EDGs') output circuit breaker and for the EDGs' automatic loading was inadequate. Additional testing was performed to adequately address the testing of certain parallel contacts in each circuit. The details of this condition are found on page 13 of this report. <br /><br /> 6. On August 22, 1997, at approximately 1530 hours, with BVPS Unit 1 at 100% reactor power, it was identified that the ESF functions "Loss of Power - 4.16kV Emergency Bus and 480V Emergency Bus (Degraded Voltage)" were not adequately tested by existing surveillance procedures. Additional testing was performed to adequately address this condition. The details of this condition are found on page 16 of this report.
3341997002 | Beaver Valley 1, Beaver Valley 2 | 02/19/1997 | 03/19/1997 | 9703260003 | <strong>Emergency Diesel Generator Watt Meter Inaccuracy Results in Inadequate Technical Specification Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1997, at Beaver Valley Power Station (BVPS) Unit 1, following the completion of an engineering review in response to INPO Operating Experience (OE) 8224, the inaccuracies of the kilowatt (KW) meter instrument loop used for recording Emergency Diesel Generator (EDG) surveillance data were determined not to ensure that the EDGs achieved the minimum Technical Specification (TS) required loading. As a consequence of the identified condition, the Unit 1 EDGs were declared inoperable by the Nuclear Shift Supervisor (NSS) at 2044 hours on February 19, 1997 and TS Limiting Condition for Operation (LCO) 3.8.1.1 was entered at that time. TS 3.8.1.1.e requires that if one of two inoperable EDGs cannot be restored to operable in 2 hours, the plant must be in hot standby within the next 6 hours and in cold shutdown within the following 30 hours. Since it was anticipated that neither EDG would be restored to operable status within the 2 hour window, a power reduction was commenced at 2240 hours. At 2246 hours, one Unit 1 EDG was restored to operable status via performance of a revised operational surveillance test (OST) with loadings which demonstrated sufficient margin to account for the KW meter instrument loop inaccuracies. Initiation of a nuclear plant shutdown required by the plant's Technical Specifications is reportable pursuant to the requirements of 10CFR50.72(b)(1)(i). Therefore, at 2334 hours, on February 19, 1997, a 1 hour Emergency Notification System (ENS) report was made. <br /><br /> Operability was restored for the second Unit 1 EDG via performance of a revised OST with loadings which demonstrated sufficient margin to account for the KW meter instrument loop inaccuracies, and TS 3.8.1.1 was exited at 0700 hours on February 20, 1997. Current operability of the Unit 2 EDGs was not impacted, based upon the results of the latest tests. However, since the operability of the Unit 1 and Unit 2 EDGs was determined to have been inadequately demonstrated by the performance of the OSTs in the past, compliance with TS LCO 3.8.1.1 and its action statements was not historically accomplished. This represents an operation or condition prohibited by the plant's TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(1). There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event was attributed to the lack of consideration of all aspects of the watt meter instrument loop inaccuracies when the KW load requirements were developed for the EDG TS surveillance procedures. <br /><br /> They were no safety implications to the health and safety of the public as a result of this event.
3341997003 | Beaver Valley 1, Beaver Valley 2 | 02/20/1997 | 03/24/1997 | 9703270149 | <strong>Failure to Leak Test Reactor Coolant System Pressure Isolation Valves in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 20, 1997, at 0900 hours, during an audit by the Quality Services Unit at Beaver Valley Power Station (BVPS), it was identified that the March 23, 1996 performance of the Operational Surveillance Test (OST) which implements the Technical Specification (TS) required leak check of Unit 1 Reactor Coolant System (RCS) pressure isolation valves MOV-RH-700 and MOV-RH-701 was not conducted in accordance with TS. Unit 1 TS Surveillance Requirement (TSSR) 4.4.6.3.1 (and Unit 2 TSSR 4.4.6.3.1 for Unit 2 valves) requires that the RCS valves of Table 4.4-3 be leak tested prior to entering Mode 2 after every time the plant is placed in Cold Shutdown. Contrary to this, Unit 1 RCS valves MOV-RH-700 and MOV-RH-701 were leak tested in Mode 4, prior to achieving Cold Shutdown (Mode 5), during the last performance of the OST on March 23, 1996 and were not tested after having achieved Mode 5. On February 21, 1997, at 1000 hours, it was identified that BVPS Unit 2 RCS pressure isolation valves 2RHSMOV701A and B and 2RHS-MOV702A and B also were not tested in accordance with TSSR 4.4.6.3.1 during the last performance of 20ST-10.5 on August 31, 1996. <br /><br />Failure to properly perform the TSSR for the RCS pressure isolation valves implies that the valves have not been demonstrated OPERABLE as required by Limiting Condition for Operation (LCO) 3.4.6.3. The TS LCO action statement requires that, in lieu of demonstrated operability, these valves should have been verified closed and deenergized within 4 hours or the plant placed in HOT STANDBY in the next 6 hours and COLD SHUTDOWN within the following 30 hours. Failure to comply with an LCO and its Action Statement is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system responses as a result of this event. <br /><br />On February 21, 1997 by 1059 hours (for Unit 2 RCS pressure isolation valves 2RHSMOV701A and B and 2RHS-MOV702A and B) and 1101 hours (for Unit 1 RCS pressure isolation valves MOV-RH-700 and MOV-RH-701) the affected valves were declared inoperable, and verified to be closed and deenergized. <br /><br />The apparent cause of this event was operator error. Operations personnel indicated that the reason these valves have been tested in this manner was to facilitate the early identification of valves which would fail prior to the refueling outage and thus enable scheduling of valve repairs during the outage core offload window, if required. Testing the valves after the completion of refueling could necessitate a second core offload prior to repair. There were no safety implications to the health and safety of the public as a result of this event.
3341997004 | Beaver Valley 1, Beaver Valley 2 | 02/26/1997 | 10/24/1997 | 9711030197 | <strong>Failure to Test Post DBA Hydrogen Control System Recombiners in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1997, at 0900 hours, during an audit by the Quality Services Unit at Beaver Valley Power Station (BVPS), it was identified that the Unit 1 Post DBA Hydrogen Control System containment hydrogen recombiners were not tested in accordance with the requirements of Technical Specifications (TS) on March 24, 1996. Contrary to the TS, the Operational Surveillance Tests (OSTs) which implement the required functional test of the containment hydrogen recombiners were not followed by the performance of the Maintenance Surveillance Procedures (MSPs) which implement the electrical inspection to verify the integrity of the heater electrical circuits. On February 26, 1997, at 1200 hours, both Unit 1 hydrogen recombiners were declared inoperable, pending satisfactory completion of required TS testing. On February 26, 1997, at approximately 1400 hours, follow-up investigation identified that the Unit 2 containment hydrogen recombiners had also been inadequately tested during the performance of the applicable OSTs on September 1, 1996. On February 26, 1997 at 1430 hours, both Unit 2 hydrogen recombiners were also declared inoperable, as of 1200 hours, pending satisfactory completion of required TS testing. On February 28, 1997, the required surveillance testing was finalized at 1810 hours for the Unit 2 hydrogen recombiners and at 2230 hours for Unit I hydrogen recombiners, and operability of the respective hydrogen recombiner systems was fully restored. This event is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i) as an operation or condition prohibited by Technical Specifications. There were no automatically or manually initiated safety system responses as a result of this event. The apparent causes of this event were procedural deficiencies and personnel error. The results of the surveillance tests finalized for both Units on February 28, 1997 indicated that the hydrogen recombiners had remained capable of performing their design functions. Based upon this, there were no safety implications to the health and safety of the public as a result of this event.
3341997005 | Beaver Valley 1, Beaver Valley 2 | 03/19/1997 | 09/24/1997 | 9709300293 | <strong>Inadvertent Operation of 345 KV Bus Backup Timer Relay Results in Dual Unit Reactor Trips</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1997, at approximately 0606 hours, while operating at 100% nominal power, Beaver Valley Power Station (BVPS) Units 1 and 2 experienced simultaneous reactor trips due to the opening of the output breakers for both units. The event was initiated by an inadvertent operation of the Bus Backup Timer relay on the #3-345 KV bus in response to a phase to ground fault which occurred on the Ohio Edison system's Mansfield-Hoytsdale 345 KV line. An Emergency Notification System (ENS) report was made pursuant to the requirements of 10CFR50.72(b)(2)(H) at 0922 hours on March 19, 1997. This event is also reportable pursuant to the requirements of 10CFR50.73(a)(2)(i) and 10CFR50.73(a)(2)(iv). <br /><br /> Operations responded to the dual unit trip by entering the appropriate plant Emergency Operating Procedures (EOPs). Stabilization of Unit 1 was completed at approximately 0608 hours on March 19, 1997, with the mitigating equipment operating in the expected manner to control the transient. Unit 1 Emergency Diesel Generator (EDG) EE-EG-1 started due to momentary undervoltage on 4 KV emergency bus AE, but was not required to load, since bus AE did not lose power. Unit 1 EDG EE-EG-2 did not start and was conservatively declared inoperable as of 0606 hours on March 19, 1997, until testing was completed which demonstrated that the undervoltage condition on bus DF was of insufficient duration to start EDG EE-EG-2. Both Unit 1 EDGs functioned as designed. <br /><br /> Stabilization of Unit 2 was completed at approximately 0610 hours on March 19, 1997, with the mitigating equipment operating in the expected manner to control the transient with the exception of "B" Steam Generator Auxiliary Feedwater (AFW) flow indicating lower than normal. Subsequent investigation indicated that this was due to the concurrent event failure of a check valve in the "B" AFW injection header. The "B" AFW injection header was declared inoperable at 1206 hours on March 19, 1997, and, pursuant to the requirements of Technical Specifications (TS), Unit 2 commenced a boration and cooldown towards Mode 4 at 1731 hours on March 19, 1997. An update to the ENS notification pursuant to the requirements of 10CFR50.72(b)(1)(i)(A) was made at 1302 hours. Unit 2 entered Mode 4 at 1731 hours on March 19, 1997. An evaluation of the AFW check valve failure pursuant to the requirements of 10CFR21 was completed April 24, 1997. ENS Notification of 10CFR21 reportability was made at 1403 hours. <br /><br /> The root cause of the dual unit trip event was inadequate implementation of design specifications and design review which resulted in incorrect wiring between the Unit 2 Static Breaker Failure Unit Relay and its associated Static Relay Unit Bus Backup Timer. Both units were safely shut down in accordance with the applicable procedures. There were no implications to the health and safety of the public as a result of this event.
3341997006 | Beaver Valley 1, Beaver Valley 2 | 03/22/1997 | 04/21/1997 | 9704250142 | <strong>Failure to Test Solid State Protection System Logic in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1997, at 0700 hours, at Beaver Valley Power Station (BVPS), during a review of Unit 1 Solid State Protection System (SSPS) testing related to the Safety Injection (SI) function, it was determined that certain Engineered Safety Features Actuation System (ESFAS) Instrumentation and certain Reactor Trip System (RTS) Instrumentation were not being tested in accordance with the requirements of Technical Specifications (TS). Specifically, the following functions were not being adequately tested: (1) the reactor coolant system loop stop valve interlocks with (a) the low steam pressure safety injection function and with (b) the low-low steam generator (S/G) level reactor trip; (2) the SSPS logic circuitry for the ESFAS P-4 interlock (reactor trip status) logic for both the SI Reset/Auto Block and Feedwater Isolation (partial) functions. Furthermore, the review determined that the identical TS surveillance deficiencies existed at Unit 2. Both Units were in Mode 5 at the time the event was discovered, with no applicable Limiting Condition for Operation. <br /><br /> This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i) as an operation or condition prohibited by Technical Specifications. There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event at both Units was procedural deficiencies. <br /><br /> Surveillance testing was performed on March 24, 1997, at Unit 1, and on March 27, 1997, at Unit 2, while both Units were still in Mode 5. This testing demonstrated that the ESFAS instrumentation and the RTS Instrumentation channels involved had remained capable of performing their design function. <br /><br /> Based upon the above information, there were no safety implications to the health and safety of the public.
3341997007 | Beaver Valley 1, Beaver Valley 2 | 03/22/1997 | 04/21/1997 | 9704250136 | <strong>Failure to Test Control Room Emergency Bottled Air Pressurization Subsystem in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1997, Beaver Valley Power Station (BVPS) Units 1 and 2 were both in Cold Shutdown (Mode 5). At approximately 1230 hours, during a review of the surveillance records from the Control Room Emergency Habitability System Monthly Retest Log, it was identified that the common Control Room Emergency Bottled Air Pressurization Subsystem (CREBAPS) discharge trip valves were not tested in accordance with Technical Specifications (TS). Failure to adequately demonstrate operability of these valves renders the associated subsystem inoperable and is a condition prohibited by TS. This is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). <br /><br /> TS require that the CREBAPS be demonstrated operable at least once per 18 months by verifying that a chlorine/control room high radiation/ containment phase B isolation test signal from either unit will initiate system operation. The acceptance criteria for the Operating Surveillance Test (OST) which implements these TS Surveillance Requirements (TSSR), requires that the stroke times for the discharge trip valves do not exceed a prescribed ASME limiting stroke time. These OST acceptance criteria also require that, if the discharge trip valves exceed their previously recorded stroke times (from the last performance of the 18 month test), by greater than 50%, the test frequency will be increased to monthly. During the performance of the discharge trip valve stroke test on January 28, 1997, valves TV-VS-101B, D, and E had stroke times with increases greater than 50% from their previously recorded stroke times. Contrary to the requirements of the OST acceptance criteria, these valves were not retested on February 28,1997. On March 23, 1997, by 1414 hours, CREBAPS discharge trip valves TV-VS-101B, D and E were successfully tested in accordance with OST 44A.11, 'Chlorine Actuation of Control Room Isolation/CREBAPS Systems,' and CREBAPS operability was fully restored for the common Control Room. <br /><br /> The apparent cause of this event was inadequate coordination and communication between responsible site organizations, an d inadequate procedures. A contributing cause was the fact that the Technical Specification surveillance testing program is not the responsibility of a single department. <br /><br /> There were no automatically or manually initiated safety system responses in response to this event. <br /><br /> Surveillance Testing of the CREBAPS discharge trip valves TV-VS-101B, D and E performed on March 23, 1997 demonstrated that there was no loss of safety function. There were no implications to the health and safety of the public as a result of this event.
3341997008 | Beaver Valley 1, Beaver Valley 2 | 03/25/1997 | 09/04/1997 | 9709170149 | <strong>Missed Technical Specification Surveillance - Monthly Position Check of Valves in the Boron Injection Flowpath</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1997, Beaver Valley Power Station Units 1 and 2 were in Cold Shutdown (Mode 5). During a review of the Operating Surveillance Tests (OSTs) which implement the Surveillance Requirements for the Reactivity Control Systems, Unit 2 Operations identified that the monthly position verifications for two (2) motor operated valves (MOVs), in the boron injection flow path, 2CHS-MOV289 and 2CHS-MOV310, were not being performed as required by Technical Specifications (TS). Subsequent investigation identified that the monthly position verifications for the two (2) analogous MOVs at Unit 1, MOV-1CH-289 and MOV-1CH-310, as well as two (2) manual valves, 1CH-83 and 1CH-86, were also not being performed as required by Technical Specifications. The required position verifications for the identified valves were performed on March 25, 1997 for Unit 2 and March 31, 1997 for Unit 1. The valves were in their normal system alignment positions. The applicable OSTs were appropriately revised by April 5, 1997 to ensure that the required position verifications are performed as required by TS. <br /><br /> On June 17, 1997, with Units 1 and 2 in Mode 1 at 100% power, a review of TS surveillance testing was completed for both units as a part of an extent of condition evaluation for the March 25, 1997 event. The review identified that the OSTs which implement the Surveillance Requirements for the monthly verification of the availability of electrical power from separate, operable emergency buses for each ECCS subsystem do not include Unit 1 MOVs MOV-1CH-289 and MOV-1CH-310 or Unit 2 MOVs 2CHS-MOV289 and 2CHS-MOV310. <br /><br /> These events are reportable as an operation or condition prohibited by TS pursuant to the requirements of 10CFR50.73(a)(2)(i). <br /><br /> The apparent cause of these events was a failure to adequately address the Technical Specification Surveillance Requirements for position and electrical power verification of valves in the boron injection flow path by identifying all pertinent valves in the Operating Surveillance Tests which implement those requirements. <br /><br /> Boron injection flow is continuously verified by system alarm functions and routinely verified by Control Room Operators, as are control switch indicating lights in the Control Room, which are indicative of power availability. There were no automatically or manually initiated safety system responses in response to these events. There were no implications to the health and safety of the public as a result of this event.
3341997009 | Beaver Valley 1, Beaver Valley 2 | 04/02/1997 | 09/04/1997 | 9709170153 | <strong>Main Steam Isolation Bypass Valves Do Not Meet Technical Specification Engineered Safety Feature Response Time Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1997, at 1500 hours, Beaver Valley Power Station Unit 1 was in cold shutdown (Mode 5). During an engineering review, it was identified that Unit 1 Main Steam Isolation Bypass Valves (MOV-MS-101A, B and Q have a closure stroke time approximately 11 to 18 seconds, whereas Technical Specifications (TS) Table 3.3-5, "Engineered Safety Features Response Time," item 4.g, lists a response time of less than or equal to 8 seconds for the Steam Line Isolation Engineered Safety Feature (ESF) function. Since the bypass valves receive a Steam Line Isolation ESF signal, it is implicit that they are required to close for those events requiring steam line isolation or that they are closed prior to an event. Consequently, the Main Steam Isolation Bypass Valves do not satisfy the TS Limiting Condition for Operation (LCO) which requires that the response times of the ESF instrumentation channels be consistent with the values in TS Table 3.3-5. This is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). <br /><br /> Additional investigation identified that the Unit 2 Main Steam Isolation Bypass Valves, which are air operated valves with faster stroke times than the motor operated valves used at Unit 1, are capable of meeting their TS Table 3.3-5, item 4.g response time of less than or equal to 7 seconds. Hence, this condition is not reportable for BVPS Unit 2. <br /><br /> There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event was the failure to address the fact that the MSIV Bypass Valves receive a Steam Line Isolation signal and therefore should have been considered when identifying the TS Table 3.3-5 ESF response times for the safety functions. <br /><br /> Dusquesne Light Company (DLC) requested that Westinghouse perform a safety evaluation of this condition and determine the basis for the bypass valve closing requirements and any limits on closure time. The evaluation concluded that an MSIV Bypass Valve failing to close is enveloped by the existing UFSAR analyses and will not adversely affect the safe operation of the plant. The difference between the actual valve response time and the TS required response time for the ESF function does not represent an unreviewed safety question, as defined in 10CFR50.59. Based upon this information, there were no implications to the health and safety of the public as a result of this event.
3341997010 | Beaver Valley 1, Beaver Valley 2 | 04/17/1997 | 09/12/1997 | 9709220091 | <strong>Failure to Perform Gaseous Waste Disposal System Oxygen Testing as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1997 at 1100 hours, with Beaver Valley Power Station Unit 1 in Mode 1 at 100% power, it was identified that the output connection from Gaseous Waste Disposal System Waste Gas Decay Tank Oxygen Analyzer O2AS-GW-110-1 was partially disconnected. The lead from this cable would have been lifted during the last performance of the Waste Decay Tank Oxygen Analyzer calibration procedure which was performed on March 21, 1997. It was subsequently determined that the partially disconnected lead had rendered the associated Explosive Gas Monitoring System instrumentation channel inoperable. Plant Technical Specifications (TS) require that, with one Explosive Gas Monitoring System instrumentation channel inoperable, Waste Decay Tank gas grab samples are to be taken and analyzed at least every 24 hours during Waste Gas Decay Tank filling operations. Contrary to the requirements of TS, Waste Gas Decay Tank filling operations took place on March 27, 1997 during plant degasification and, because Operations was unaware of the inoperable status of the channel for Waste Gas Decay Tank Oxygen Analyzer O2AS-GW-110-1, gas grab samples were not obtained. This is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event was personnel error. The inadequate connection remained undetected because the associated instrument loop has no "pedestal" or minimum output which could be discerned on the recorder when the circuit is intact. Thus periodic surveillance log activities would not have detected the problem. <br /><br /> The partially disconnected lead was reconnected securely. A modification, which will provide for detection of signal failure from the Waste Decay Tank Oxygen Analyzer outputs for both Units will be implemented. The Waste Decay Tank Oxygen Analyzer procedures will be revised to require verification of channel operability subsequent to reconnection of lifted leads.<br /><br /> Waste Gas Decay Tank Oxygen Analyzer O2AS-GW-110-2 remained fully operable. Waste Decay Tank gas grab samples obtained and analyzed on March 30, 1997, were less than 1% oxygen. Based upon this information, there were no implications to the health and safety of the public as a result of this event.
3341997011 | Beaver Valley 1, Beaver Valley 2 | 05/09/1997 | 06/09/1997 | 9706160355 | <strong>Inadequate Testing of Unit 1 Solid State Protection System Relays K630A and K630B</strong><br /><i>Abstract:&nbsp;</i>On May 9, 1997, at approximately 1600 hours with both Units 1 and 2 in Mode 1 at 100% power, it was determined that the Operations Surveillance Procedure (OST) used to perform Post Maintenance Test on August 12, 1996, for the Unit 1 Solid State Protection System (SSPS) relays K630A and K630B failed to verify the operability of contacts 1-2 of these relays. These relays are actuated on a Unit 1 chlorine detection signal to initiate control room emergency habitability system functions for the Unit 1 and 2 common control room. Failure to verify relay contact 1-2 operability implies a consequent failure to verify operability of the Control Room Emergency Bottled Air Pressurization System (CREBAPS) bottles. The bottles are designed to actuate upon a Unit 1 chlorine detection signal by relay contact 1-2 with either respective CREBAPS control transfer switch, TRS-VS-01 for Train "A" or TRS-VS-02 for Train "B", in the "Unit 1" position. The "Unit 1" position is the Normal System Arrangement. The control circuitry for the CREBAPS bottles can be powered from either Unit 1 or Unit 2. <br /><br /> Unit 1 Technical Specification (TS) 3.7.7.1.b and Unit 2 TS 3.7.7.b require five bottled air pressurization subsystems consisting of two bottles per subsystem to be OPERABLE. Relays K630A and K630B were operationally accepted on August 12, 1996, following the inadequate OST. This implies that any time both CREBAPS control transfer switches TRS-VS-01 and TRS-VS-02 were in the "Unit V position during the period August 12, 1996, to May 9, 1997, prior to additional relay testing being performed, all five bottled air pressurization subsystems should have been considered inoperable. Additional testing on May 9, 1997, was begun by 1640 hours and was completed by 2100 hours that verified the operability of contacts 1-2 for relays K630A and K630B. <br /><br /> Failure to either comply with Unit 1 TS 3.7.7.1.b, Unit 2 TS 3.7.7.b or the associated ACTION STATEMENTS is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i). There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event was an inadequate procedure. The approved surveillance procedure used for these relays was itself inadequate to perform its stated function, thereby lacking adequate acceptance criteria to ensure the Operability of all required functions of these relays. Based on the testing performed on May 9, 1997, that verified the operability of contacts 1-2 for relays K630A and K630B, there were no safety implications to the health and safety of the public as a result of this event.
3341997012 | Beaver Valley 1, Beaver Valley 2 | 04/14/1997 | 04/02/1998 | 9804140273 | <strong>Analog Rod Position Indicator Channels Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 14, 1997, April 15, 1997 and May 15, 1997, control rod(s) were observed per the Analog Rod Position Indication (ARPI) system to be reading outside the +/- 12 step allowable band (as compared to the group demand counter values) authorized by Technical Specifications (TS) 3.1.3.1 and 3.1.3.2. In accordance with action statements, ARPI primary voltages for the rod(s) were then obtained. These also indicated that the control rod(s) were outside the +/- 12 step allowable band. <br /><br /> As an immediate corrective action, Abnormal Operating Procedure 1.1.7 (entitled Rod Position Indication Malfunction) was entered, and movable incore flux mapping was performed. This action indirectly verified that the control rods were in their expected positions. A Basis for Continued Operation (BCO) was prepared following the May 15, 1997 event to evaluate the reliability of the ARPI system. The BCO concluded that the ARPI system is operable, with a high level of confidence that important to safety functions can be performed. Compensatory measures recommended by the BCO have been put in place and are adopted as corrective actions. <br /><br /> There were no automatic or manually initiated safety system responses associated with these events. <br /><br /> These events are reportable in accordance with 10 CFR 50.73 (a) (2) (i) (b), as they involve a condition or operation prohibited by TS. <br /><br /> The cause of these events is calibration drift of the ARPI system, due to an existing detector anomaly associated with rod position indication in combination with design limitations. A modification to upgrade the ARPI system has been completed. <br /><br /> It was also determined that procedures associated with rod mispositioning events lack sufficient detail. Procedures associated with rod positioning events will be revised to clarify and standardize required operator actions. <br /><br /> Based upon the fact that control rods G-03, H-02 and P-08 were in their expected position, there is no safety consequence to these events. The health and safety of the public were not affected.
3341997013 | Beaver Valley 1 | 06/11/1997 | 07/10/1997 | 9707160018 | <strong>Failure to Perform DC Bus Train Weekly Breaker Alignment as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1997 at 1649 hours, as a result of a planned review of Units 1 and 2 Technical Specifications Surveillance Requirements for electrical power systems, it was discovered that the circuit breaker alignments for the DC bus train battery chargers were not being verified. Failure to adequately demonstrate the operability of the DC bus train system is a condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event was an inadequate procedure. The Unit I Technical Specifications matrix shows procedures 10ST.39.1A, -.1B, -.1C, -1.D and -.1E as satisfying Surveillance Requirement 4.8.2.3.1, but these did not document this weekly check. Charger breaker alignment was assumed to be verified by charging current measurements. <br /><br /> Upon discovery, breaker alignments were verified on June 11. Other immediate corrective actions taken consisted of surveillance procedure revisions to add breaker alignment for the DC bus train battery chargers, and verification that a similar condition does not exist for Unit 2. Future corrective actions include a technical review of the current process of revising/preparing surveillance procedures and an evaluation of the adequacy of surveillance procedures that implement Technical Specifications. <br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a) (2) (i) (b), condition or operation prohibited by Technical Specifications. <br /><br /> Based upon existing alternate methods in place that would have detected an open circuit breaker on a DC bus battery charger, there is minimal safety consequence to this event. The health and safety of the public were not affected.
3341997014 | Beaver Valley 1, Beaver Valley 2 | 06/12/1997 | 07/10/1997 | 9707170040 | <strong>Failure to Check For And Remove Accumulated Water in the Emergency Diesel Generator Day Tanks as Required by Tech Specs.</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1997, as a result of a planned review of Units 1 and 2 Technical Specifications Surveillance Requirements for electrical power systems, it was discovered that on June 1, 1994, Unit 2 Emergency Diesel Generator 2-1 ran for 62 minutes without checking for and removing accumulated water from the associated day tank. Plant Technical Specifications (TS) require that after each operation of an Emergency Diesel Generator (EDG) where the period of operation was greater than 1 hour, accumulated water in the day tank be checked for and removed. This event is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(b). Further investigation revealed additional occurrences of this on both units. There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event is procedural inadequacy. The procedures that are entered following an automatic start of an EDG do not direct the operator to perform an accumulated water check of the day tank upon shutdown if it has been operating for greater than one hour. <br /><br /> Following discovery, procedure changes were made to require checking for and removal of any accumulated water in an EDG day tank following a run of greater than one hour. Future corrective actions include an evaluation of the adequacy of surveillance procedures that implement Technical Specifications. <br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a) (2) (i) (B), condition or operation prohibited by Technical Specifications. <br /><br /> EDG day, skid mounted, and underground tanks are checked for accumulated water and any found is removed at least once per 31 days. A review of the day tank sampling results for the month immediately following each event described herein showed that no water was detected. No EDG deterioration attributed to water in the fuel has been noted. Based upon this, the safety implications of these events are minimal.
3341997015 | Beaver Valley 1 | 05/01/1997 | 07/28/1997 | 9708060054 | <strong>Proceduralized Voluntary Entry Into T.S. 3.0.3 by Allowing Bypass of Both Source Range Channels Input to High Flux Trip</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1997 with Unit 1 in Mode 1 at 100% power, it was discovered as part of a training procedure review that operating procedure 1OM-51.4.A entitled 'Station Shutdown - Minimum Load to Startup Mode or Hot Standby Mode' directed operators to simultaneously bypass both Source Range channel inputs to the high flux reactor trip while in Mode 3 and with the reactor trip system breakers in the closed position and the control rod drive system capable of rod withdrawal. Under these conditions, the removal of both Source Range channel inputs at the same time constitutes voluntary entry into Technical Specifications 3.0.3 and is thus reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B). There were no automatically or manually initiated safety system responses. <br /><br /> The apparent cause of this event was the misinterpretation of Technical Specification 3.3.1.1, Table 3.3-1, Item 6. A contributing cause is the ambiguity of Technical Specification 3.3.1.1, Table 3.3-1, Item 6. <br /><br /> As a corrective action, procedure 1OM-51.4.A was changed to delete the requirement to simultaneously bypass both source range monitors. Future corrective actions include a Technical Specification change request to clarify Table 3.3-1 items 6.a and 6.b, licensed operator retraining to emphasize recognition and awareness of Technical Specifications, and issuance of a letter to station personnel from management regarding Technical Specification compliance and Technical Specification 3.0.3 entries. <br /><br /> Procedure 1OM-51.4.A only bypassed both Source Range channel trip functions for short periods of time while shutting down while it was verified that no upscale failures had occurred and Source Range channel counts had decreased below the high trip setpoint. During this time, the source range still indicates reactor flux, the Intermediate Range channels were operable and would have provided a reactor trip upon high reactor flux. Based on this, there is minimal safety consequence to this event
3341997016 | Beaver Valley 1 | 06/27/1997 | 09/12/1997 | 9709220094 | <strong>Unit 1 Shutdown Required by T.S.3.0.3 Due to Inoperable Steam Generator Low-Low Level Reactor Protection System Trip</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1997 at 2007, it was determined that the plant had the potential for a control and protection system interaction in the Steam Generator Water Level Control System (SGWLCS) which could prevent the Reactor Protection System (RPS) from initiating a reactor trip on a low-low steam generator level. This was identified during an engineering review of the seismic qualifications of the main feedwater flow transmitters. This trip was required by IEEE 279-1971 as a diverse trip to the two-out-of-three low-low steam generator reactor trip because of the control and protection interaction of the steam generator level channels. This was reported in accordance with 10 CFR 50.72 (b)(1)(i)(A) and (b)(1)(ii)(B). BVPS Unit 1 was then taken to Mode 3. On June 28, an update to the original 10 CFR 50.72 report was provided to indicate that the steam generator low-low level trip was also inoperable. <br /><br /> On July 3, 1997, with the unit in Mode 3, Residual Heat Removal (RHR) sample isolation valve RH-214 was opened to allow sampling of the RHR system. When this valve was opened, no overpressure protection for penetration 97-1 existed and it was declared inoperable, resulting in a unit shutdown to Mode 5 as required by Technical Specification 3.6.1.1. This was reported in accordance with 50.72 (b)(1)(ii)(A). <br /><br /> The apparent cause of the initiating event was a misapplication of IEEE 279-1971 Section 4.7 Control and Protection System Interaction criteria during the original plant design.<br /><br /> Corrective actions for this event include: 1) a design modification to the SGWLCS was implemented to ensure against the identified control and protection system interaction, by installing a Median Signal Selector Switch in each of the three SGWLCS racks, 2) a design review of the Unit 1 and Unit 2 RPSs with respect to compliance with IEEE 279-1971 is being performed. <br /><br /> As potential exists for a control and protection system interaction for the SG level protection system, IEEE-279-1971 requires that a second failure must be postulated. If a second SG level instrument were to fail in an intermediate position, since there are three channels, the requisite RPS trip logic would not be satisfied and a reactor trip and auxiliary feedwater automatic start would not be generated as required when an actual SG low-low level condition occurred. The described condition does not meet IEEE-279 1971 criteria and is outside the Unit 1 design basis.
3341997017 | Beaver Valley 1 | 07/01/1997 | 07/31/1997 | 9708070314 | <strong>Engineered Safety Feature Actuation of the P-12 Interlock Due to Decreasing Reactor Water Temperature</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1997 at 1117, with Unit 1 in Mode 3 at 0% reactor power, an automatic actuation of an Engineered Safety Feature occurred when decreasing reactor water temperature resulted in the actuation of the P-12 interlock. Below the P-12 setpoint of 541 Degrees F, P-12 blocks steam dump to prevent an excessive cooldown rate. The event was initiated by maintenance activities associated with main steam dump valve PCV-MS106B. In the process of checking and calibrating the current-to-pressure (I/P) transformer PY-MS106B, the leads to it were lifted. This I/P is wired in series with the I/P's for the other valves in the first bank of condenser steam dump valves. When the leads to PY-MS-106B were lifted, the current loop to the other I/P's was broken which disabled and failed closed the entire first bank of condenser steam dump valves. The steam dump control system responded by increasing its demand signal. When PY-MS-106B calibration was complete and its leads were restored, the entire first bank of condenser steam dump valves was returned to service. Because the control system had built up a large demand signal while the first bank of valves was disabled, when the valves were returned to service they immediately opened in response to the demand. When operating personnel noted Tavg dropping, they manually closed the dump valves. However, the large increase in steam dump to the condenser caused Tavg to fall rapidly, causing an automatic actuation of the P-12 Engineered Safety Feature Interlock. A letdown isolation also occurred. The automatic actuation of the ESF P-12 interlock was promptly reported in accordance with 10 CFR 50.72 (b)(2)(ii) on July 1, 1997 and is being reported herein in accordance with the requirements of 10 CFR 50.73(a)(2)(iv). <br /><br /> The apparent cause of this event was a human performance problem that resulted in the the work package associated with main steam dump valve PCV-MS106B not containing adequate troubleshooting information necessary to remove it from service without affecting other operating equipment, or being identified as part of the work package review. <br /><br /> Corrective actions include training for all planners, electrical and I & C technicians to review this event, reinforce expectations and administrative controls in the work planning process when lifting leads in energized systems by providing specific direction requiring drawing reviews, and investigation of possible weaknesses in Maintenance troubleshooting procedures. <br /><br /> When Tavg reached 541 Degrees F, the P-12 interlock actuation occurred. Based on this, the safety consequences of this event are minimal.
3341997018 | Beaver Valley 1 | 07/05/1997 | 08/04/1997 | 9708070322 | <strong>Potential for Spurious Seismically Induced Fire Protection System Activation Affecting Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1997, at 1930 hours with Beaver Valley Power Station (BVPS) Unit 1 in Mode 5 at 0% reactor power level, it was determined that a condition existed that could adversely affect the ability of both Emergency Diesel Generators (EDG) (EE-EG-1 and EE-EG-2) to function due to a seismic event. Based on Engineering reviews performed as part of USI A-46, "Seismic Qualification of Equipment in Operating Plants," it was determined that certain Fire Protection System components which are part of the control circuitry for the carbon dioxide fire suppression system for the EDG rooms potentially could spuriously operate during a seismic event. This would result in carbon dioxide discharging into both EDG rooms and adversely affecting the EDGs' ability to function, if called upon, due to air displacement by carbon dioxide flooding. The BVPS Unit 1 UFSAR Section 9.10.1 states, "The fire protection system is designed on the basis that rupture or inadvertent operation will not significantly impair the safety capability of structures, systems, or components important to safety or designed to Seismic Category 1 requirements." Immediately following this determination, both EDGs were declared inoperable, until at 1935 hours on July 5, 1997 when the carbon dioxide fire suppression system in each EDG room was placed in the "abnormal" mode. Placing the system in the "abnormal" mode prevents automatic operation from the non-seismically qualified relays, but still provides fire alarm capability to the control room in the event of a fire in the EDG rooms. Concurrent with disabling the automatic feature of the EDG carbon dioxide fire suppression systems, a continuous fire watch with backup suppression capability was established in each EDG room in accordance with the BVPS Fire Protection Program. The apparent cause of this event is a deficiency in the original design of the carbon dioxide fire suppression systems for the BVPS Unit 1 EDG rooms. <br /><br /> The Fire Suppression System for the Unit 2 EDGs was reviewed and it was determined that no similar problem existed, since the Unit 2 EDGs draw their combustion air from outside the EDG rooms. <br /><br /> At 2120 hours on July 5, 1997, a four hour non-emergency notification was made pursuant to the requirements of 10 CFR 50.72(b)(2)(i). This report is being made pursuant to the requirements of 10 CFR 50.73(a)(2)(ii). This report also fulfills the BVPS Fire Protection Program requirement for a Special Report following carbon dioxide fire protection system inoperability that exceeds 14 days. <br /><br /> There was no actual spurious operation of the Fire Protection System nor were there any equipment failures due to this event. Based upon this information there were no safety implications to the health and safety of the public as a result of this event.
3341997019 | Beaver Valley 1 | 07/10/1997 | 08/11/1997 | 9708180268 | <strong>Containment Penetration Check Valves Not in Accordance with the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1997 at 1345, a self initiated review of the Unit 1 Containment Isolation Valve Table revealed that check valves 1SA-15, 1IA-91, and 1RC-72 associated with containment penetration numbers 42, 45, and 47 did not meet the Unit 1 UFSAR requirements for containment isolation valves. The Unit 1 UFSAR, section 5.3.3, states that weight and spring loaded check valves used for containment isolation are designed to require a D/P across the valve in the normal flow direction exceeding the expected post DBA D/P between atmosphere and the containment in order to open. A spring or weight loaded check valve is needed to maintain the containment subatmospheric after a Design Basis Accident if a passive failure of the penetration outside of containment is postulated in order to prevent air flowbai into containment. Loss of subatmospheric containment conditions after one hour post-LOCA would invalidate the current 10 CFR 100 dose analysis. A review of plant drawings determined that these check valves were not weight or spring loaded. The review also revealed that check valve 1RC-72 did not meet the Unit 1 UFSAR section 5.3.4.2 requirement stating that Westinghouse check valves, when used as containment isolation valves, are loaded to close against a 2 psi positive differential pressure. This event was reported in accordance with 10 CFR 50.72 (b) (2) (i) (B) on July 10, 1997. This event is also reportable in accordance with 10 CFR 50.73 (a) (2) (ii) (B), plant in condition outside its design basis. <br /><br /> At the time of discovery, Unit 1 was in Mode 5. Prior to startup, a temporary modification was performed to install a blank flange downstream of check valve 1SA-15 to provide a containment integrity boundary. A permanent modification will be performed prior to December 15, 1997. Check valves 1IA-91 and 1RC-72 were replaced with qualified valves on July 16, 1997. A review of the similar penetrations on Unit 2 found no similar design discrepancies. <br /><br /> The apparent cause of this event is inadequate design reviews relating to containment penetration-protection during initial plant construction as specified in the Unit 1 UFSAR sections 5.3.3 and 5.3.4. <br /><br /> If a passive failure of the piping outside of containment on a line utilizing one of these check valves was to have occurred during a Design Basis Accident, the containment, designed to be maintained subatmospheric for 30 days, would repressurize to atmospheric pressure as a result of air entering via the broken pipe. This condition, if postulated to occur, does not comply with the UFSAR analysis of dose limits assumptions following a DBA.
3341997020 | Beaver Valley 1 | 07/24/1997 | 08/25/1997 | 9709040158 | <strong>Unqualified Component in Safety Related Ventilation Circuits Affects the Emergency Diesel Generators' Design Basis</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1997, at approximately 1830 hours, with Beaver Valley Power Station (BVPS) Unit 1 in Mode 5 and at 0 percent reactor power, an Engineering review identified a pressure switch contact, without the required quality assurance level category, which was installed in the control circuit for each of the two Emergency Diesel Generator (EDG) room!s safety related ventilation systems. A pressure switch located in each EDG room, as part of the fire protection system and used to sense a carbon dioxide discharge, has a normally closed contact which opens upon sensing a carbon dioxide discharge. Opening of the contact prevents the EDG room ventilation fan from operating. <br /><br /> The review of this condition concluded that, without the required quality assurance level category, the pressure switch contacts must be assumed to fail open during an accident condition. This would result in loss of the EDG room ventilation and with an operating EDG will result in a steadily increasing EDG room temperature leading to EDG performance degradation and eventual inability of the EDG to perform its safety function. This event would not have prevented the EDGs from responding to either an automatic or manual start signal. The apparent cause of this event is a deficiency in the original design of the ventilation system for the Unit 1 EDG rooms. This condition does not apply to Unit 2, since the Unit 2 EDG ventilation system does not have interlocked CO sub 2 pressure switches. <br /><br /> On July 24, 1997, at 1915 hours, both EDGs were declared inoperable pending resolution of this condition. The appropriate Technical Specification ACTION STATEMENT was applied, including a prohibition on entering Mode 4. <br /><br /> Installation of qualified replacement switches was completed by July 27, 1997, with Unit I still in Mode 5. No actual equipment failure or loss of safety function was found. A four-hour non-emergency report of this condition was made on July 24, 1997, at 2004 hours, pursuant to the requirements of 10 CFR 50.72(b)(2)(i). This report is being made pursuant to the requirements of 10 CFR 50.73(a)(2)(ii)(B). Based on the above information, there were minimal safety implications to the health and safety of the public.
3341997021 | Beaver Valley 1 | 07/26/1997 | 09/16/1997 | 9709230093 | <strong>Potential for Seismic Event to Result in Both Trains of Supplementary Leak Collection and Release System to Become Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 26, 1997 at 1715 hours, with Beaver Valley Power Station (BVPS) Unit 1 in Mode 5 at 0% reactor power level, it was determined that a condition existed that could adversely affect the ability of both Supplementary Leak Collection and Release System (SLCRS) trains to function due to a seismic event. Based on Engineering reviews performed as part of USI A-46, "Seismic Qualification of Equipment in Operating Plants," it was determined that certain Fire Protection System components which are part of the control circuitry for the SLCRS Charcoal Filters water deluge system could spuriously operate during a seismic event. This would result in water soaking the charcoal, thus rendering the filters inoperable. The BVPS Unit 1 UFSAR Section 9.10.1 states, "The fire protection system is designed on the basis that rupture or inadvertent operation will not significantly impair the safety capability of structures, systems, or components important to safety or designed to Seismic Category I requirements." Immediately following this determination, both trains of SLCRS were declared inoperable. <br /><br /> At 2025 on July 26, 1997, a four hour non-emergency notification of the Unit 1 condition was made pursuant to the requirements of 10 CFR 50.72 (b)(2)(i). <br /><br /> On August 21, 1997, a follow-up extent of condition evaluation identified that BVPS Unit 2 SLCRS Charcoal Filters water deluge system components could spuriously operate during a seismic event, rendering the filters (both trains of SLCRS) inoperable. At 1622, both trains of SLCRS were declared inoperable. At 1638, a one-hour non-emergency notification of the Unit 2 condition was made pursuant to the requirements of 10 CFR 50.72 (b)(1)(ii)(B). <br /><br /> At each Unit, after declaring the SLCRS inoperable, the water deluge system for each SLCRS train was manually isolated, a roving fire tour was posted (or was already established), and the trains were declared operable. <br /><br /> This report is being made pursuant to the requirements of 10 CFR 50.73 (a)(2)(ii), 50.73(a)(2)(v), and 50.73(a)(2)(vii). This report also fulfills the BVPS Fire Protection Program requirement for a Special Report following fire system inoperability that exceeds 14 days. There was no actual spurious operation of the Fire Protection System at either unit nor were there any equipment failures due to the events. Based upon this information there were no safety implications to the health and safety of the public as a result of the events. Corrective actions planned to prevent recurrence include seismic qualification for relays of concern, replacement of the relays with seismically qualified devices, or evaluation of the filter banks' fire protection system for continued manual control.
3341997022 | Beaver Valley 1 | 07/30/1997 | 08/29/1997 | 9709050038 | <strong>Engineered Safety Feature Actuation of the P-12 Interlock due to Decreasing Reactor Water Temperature</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1997 at 1147, with Unit 1 in Mode 3 at 0 % reactor power, an automatic actuation of an Engineered Safety Feature occurred when decreasing reactor water temperature resulted in the actuation of the P-12 interlock. Below the P-12 setpoint of 543 degrees F, P-12 blocks steam dump to prevent an excessive cooldown rate. The event was initiated following the performance of a temporary operating procedure written to test the operability of Turbine Driven Auxiliary Feed Pump FW-P-2. The testing of this pump required feeding the steam generators with auxiliary feedwater. This resulted in higher than normal no-load steam generator narrow range levels. Steam generator water levels were decreasing due to blowdown flow and steaming. In an effort to return steam generator levels to normal no-load values more quickly, blowdown flow was increased. The B Steam Generator Bypass Feedwater Regulating Valve (BFRV) control loop responded first to maintain level in the B Steam Generator. The A and C BFRV level control loops did not respond immediately and allowed level to drop below the no-load setpoint value. Operating staff then took manual control of the A and C BFRVs, opening them to increase feedwater flow. No response was observed until the valves rapidly opened and steam generator level was observed to be increasing. The increased feedwater flow was sufficient to result in a cooldown of the Reactor Coolant, reaching the P-12 setpoint of 543 degrees F and causing an actuation of the P-12 interlock. The apparent cause of this event is operator unfamiliarity with level controller response in all situations. Inspection of level recorder charts after the event indicates that controllers for the A and C steam generator level control loops were in "windup", which is a normal condition following prolonged operation at higher than no-load setpoint value. This caused the A and C BFRVs to remain closed longer following restoration from the test. When expected response of the A and C BFRVs was not observed, control was switched to manual and eventually excessive feedwater caused a decrease in Reactor coolant temperature and P-12 actuation. A contributing cause was procedure weakness, because the controllers were procedurally allowed to "Windup" without operator notification. <br /><br /> As a follow-up corrective action, this event will be reviewed with all operators and procedure changes will be made. When Tavg reached 543 degrees F, the P-12 interlock actuation occurred. Throughout the event, shutdown margin was maintained as the RCS was borated to cold shutdown boron concentration. Based on this, the safety consequences of this event are minimal. END OF ABSTRACT
3341997023 | Beaver Valley 1 | 08/01/1997 | 08/29/1997 | 9709050003 | <strong>Technical Specification 3.0.3 Entry Due to Two Analog Rod Position Indicator Channels Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1997, control rods were withdrawn from the reactor core during a load increase from 87.5 percent to 95 percent power. Prior to the load increase, Analog Rod Position Indication (ARPI) for rod H-02 was inoperable. Following withdrawal of Control Bank D to 203 steps at 1552, ARPI for rod P-08 was not within 12 steps of the group demand counter indication of position as required by Technical Specifications. It was determined that Technical Specification Limiting Condition for Operation (LCO) 3.0.3 entry was appropriate for inoperable ARPI, during the time period between 1552 and 1610. While in Technical Specification LCO 3.0.3, no power reduction was initiated due to the prompt return of rod P-08 to within specifications. There were no manual or automatic safety system actuations required as a result of this event. <br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition or operation prohibited by Technical Specifications. <br /><br /> The cause of this event was calibration drift of the ARPI system due to an existing detector anomaly associated with rod H-02 position indication,in combination with design limitations. A modification to upgrade the ARPI system will be completed during the upcoming Unit 1 Refueling Outage, and is expected to improve performance. <br /><br /> This event was not applicable to Beaver Valley Power Station Unit 2 which uses a rod position indication system of a different design. <br /><br /> Based upon the fact that control rods H-02 and P-08 were in their expected position, there were no safety consequences for this event. The health and safety of the public were not affected.
3341997024 | Beaver Valley 1 | 08/05/1997 | 09/04/1997 | 9709100119 | <strong>Failure of Refueling Water Storage Tank Level Transmitter Leads to Entry into Technical Specification 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1997, at approximately 1314 hours, with Beaver Valley Power Station (BVPS) Unit 1 in Mode 1 at 99.5% power, while Instrumentation & Controls (I&C) technicians were replacing Refueling Water Storage Tank (RWST) level transmitter LT-QS-100C, RWST level transmitter LT-QS-100B failed offscale high. <br /><br /> With two out of four RWST level transmitters inoperable, Technical Specification (TS) Limiting Conditions for Operation (LCO) could not be met, except as provided in the associated action requirements, and LCO 3.0.3 was invoked. TS LCO 3.0.3 requires that when an LCO is not met except as provided in the associated ACTION requirements, within 1 hour action shall be initiated to place the unit in a mode in which the specification does not apply by placing it, as applicable, in: 1) at least hot standby within the next 6 hours, 2) at least hot shutdown within the following 6 hours, and 3) at least cold shutdown within the subsequent 24 hours. <br /><br /> Control Room operators initiated a TS 3.0.3 shutdown for Unit 1 (turbine load reduction) at approximately 1412 on August 5, 1997. LT-QS-100C was restored to operable status at 1541 hours. The RWST level transmitter TS requirements were expeditiously restored in accordance with plant procedures, and there were no safety implications to the health and safety of the public.<br /><br /> This event is reportable pursuant to the requirements of 10CFR50.72 (b)(1)(i)(A) as "The initiation of any nuclear plant shutdown required by the plant's Technical Specifications." A 1 hour ENS report to NRC was made at 1502 hours on August 5, 1997. This event is also reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B) as "Any operation or condition prohibited by the plant's Technical Specifications..." <br /><br /> There were no manual or automatic safety system actuations required as a result of this event. <br /><br /> The apparent cause of the event was determined to be a crack in the ferrite block for level transmitter LT-QS-100B caused by aging or cyclic fatigue. The Fischer & Porter RWST level transmitters were replaced with new Foxboro transmitters.
3341997025 | Beaver Valley 1 | 08/07/1997 | 09/04/1997 | 9709160045 | <strong>Ground in Feedwater Flow Controller Results in High Steam Generator Level and Subsequent Turbine Trip/Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1997, at 2018 hours, Beaver Valley Power Station Unit 1 was in Mode 1 at 100% power when the unit experienced an automatic turbine trip, reactor trip and feedwater isolation (FWI). The feedwater regulating valve for "A" steam generator (S/G) failed open during the replacement of a resistor block in the S/G level control circuit by Instrumentation and Controls (I&C) technicians. The spurious feedwater regulating valve opening resulted in a rapid rise in S/G level. When Control Room Operators attempted to take manual control of the valve, it would not respond.<br /><br /> When 2 out of 3 level channels on the "A" S/G reached the Hi-Hi setpoint, a full FWI was generated, which also tripped the turbine. The FWI secured both main feedwater pumps and closed the feedwater isolation valves. The turbine trip initiated a reactor trip at 2018 hours. The Control Room crew responded by implementing the required emergency operating procedure (EOP) for reactor trip. S/G level shrinkage from the secondary pressure rise resulted in the expected automatic start of all three auxiliary feedwater pumps. Approximately 30 seconds after the turbine trip, the main generator tripped and a fast bus transfer to the system transformers occurred. The emergency diesel generators started automatically due to a transient bus undervoltage condition, but load shedding and sequencing of loads onto the emergency buses was not required. The reactor trip EOP was exited approximately 3 minutes after the trip and the unit was stabilized and placed in a safe, controlled shutdown condition with no safety implications to the health and safety of the public. <br /><br /> At 2220 on August 7, 1997, a four hour non-emergency notification was made pursuant to the requirements of 10CFR50.72(b)(2)(ii). This report is being made pursuant to the requirements of 10CFR50.73(a)(2)(iv). <br /><br /> An Event Response Team was formed on August 8, 1997 to investigate the reactor trip. The ERT determined that I&C and Operator actions were correct and did not cause the trip. The root cause of the trip was determined to be the existence of excess solder on a circuit card in the S/G feedwater flow control module. The excess solder came in contact with the module chassis, creating an internal ground on the feedwater control loop. Ground current initiated a full open demand signal to the "A" main feedwater regulating valve and also prevented operators from taking manual control of the valve. A new module was installed to replace existing S/G feedwater flow control module FC-FW-478 and was demonstrated to function properly via post maintenance testing on August 9, 1997.
3341997026 | Beaver Valley 1, Beaver Valley 2 | 08/14/1997 | 09/12/1997 | 9709220086 | <strong>Control Room Ventilation Isolation Dampers and Containment Isolation Valves Do Not Meet Technical Specification Engineered Safety Feature Response Time Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1997, at approximately 1600 hours, Beaver Valley Power Station (BVPS) Units 1 and 2 were in Mode 1 at 100% reactor power. During an engineering review, which was performed as a follow-up corrective action for Licensee Event Report (LER) 1-97-009 "Main Steam Isolation Bypass Valves Do Not Meet Technical Specification Engineered Safety Feature Response Time Requirements," it was identified that Engineered Safety Feature (ESF) response time testing for eight Control Room Ventilation System isolation dampers (four per unit) and five Unit 1 Containment Isolation System valves was not conducted in accordance with the requirements of Technical Specifications (TS). Surveillance testing of these components does not satisfy the TS Limiting Condition for Operation (LCO) and associated TS Surveillance Requirements which require that the response times of the ESF instrumentation channels are demonstrated to be within prescribed limits. This is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). <br /><br /> There were no automatically or manually initiated safety system responses as a result of this event.<br /><br /> The apparent cause of this event was inadequate surveillance test procedures for the ESF response time testing of Control Room Ventilation System Isolation dampers and the identified Unit 1 Containment Isolation System valves. Necessary information to ensure the implementation of TS Surveillance Requirements was missing from the appropriate surveillance test procedures. <br /><br /> Surveillance test data was reviewed and testing was completed by August 14, 1997, which demonstrated that the ESF response time requirements of TS for the eight dampers and the five Unit 1 isolation valves were not exceeded. Test data provided reasonable assurance that there was no loss of safety function for these components and they remained capable of achieving their design requirements. The appropriate surveillance test procedures for the ESF response time testing were corrected via field revisions. <br /><br /> Based upon the above information, there were no safety implications to the health and safety of the public.
3341997027 | Beaver Valley 1 | 08/17/1997 | 09/16/1997 | 9709230117 | <strong>Missed Surveillance of the Refueling Water Store Tank Boron Concentration</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1997, at 1325 hours, with Beaver Valley Power Station (BVPS) Unit 1 in Mode 1 at approximately 99% reactor power level, it was discovered that a Technical Specification required surveillance of the Refueling Water Storage Tank (RWST) boron concentration was missed. Technical Specification 3.1.2.8.b.2 requires that the RWST boron concentration be between 2000 and 2100 ppm, and Surveillance Requirement 4.1.2.8.a.1 requires that the boron concentration be verified at least once per seven (7) days. This condition was discovered by a Chemistry Specialist, during a review of the Chemistry Department's Technical Specification Surveillance Requirement check-off sheet. A sample of the RWST boron concentration was immediately taken on 8/17/97 at 1328 hours, and was within the required limits. The time period from the previous sample exceeded the seven (7) day plus the 25 percent allowance by approximately nine (9) hours. <br /><br /> There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B) as "Any operation or condition prohibited by the plant's Technical Specifications." <br /><br /> The apparent causes of the event were: 1. inattention to detail and lack of self checking by the daylight Chemistry Specialist who did not sample the RWST as required, 2. the failure of the afternoon Chemistry Specialist to perform a review of the Chemistry Department's Technical Specification surveillance requirements as required by procedure, and 3. the failure to update the Chemistry Department's Technical Specification Reminder Calendar to reflect that the RWST was scheduled to be sampled weekly on Fridays. <br /><br /> A contributing cause was confusion related to whether the Technical Specification Reminder Calendar or the Technical Specification Surveillance Requirements check-off sheet was to be utilized for the required daily Technical Specification review. A sample for RWST boron concentration was taken on 8/17/97 at 1328 hours, the sample was within the Technical Specification 3.1.2.8.b.2 required range of between 2000 and 2100 ppm. Based upon the results of the sample, there were no implications to the health and safety of the public as a result of this event.
3341997028 | Beaver Valley 1, Beaver Valley 2 | 08/25/1997 | 09/24/1997 | 9709300302 | <strong>Spent Fuel Pool Crane Interlocks and Physical Stops Not Tested Prior to Use in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1997, at 1400 hours, with Unit 1 in Mode 1 at 100% power, it was identified by the Control Room that the Spent Fuel Pool crane had been moved over the storage pool during relamping operations without first performing a surveillance procedure required by Technical Specifications (TS). Technical Specification Surveillance Requirement (TSSR) 4.9.7 requires that the crane interlocks and physical stops which prevent crane travel with loads in excess of 3000 pounds shall be demonstrated operable within 7 days prior to crane use and at least once per 7 days thereafter during crane operation. Contrary to TS, the Spent Fuel Pool crane was used without verifying that the crane interlocks and physical stops were operable. This is an operation prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There was no actual movement of heavy loads over the Spent Fuel Pool. <br /><br /> The crane was relocated to a position not over the fuel pool and the required surveillance testing was performed to satisfy the TSSR. <br /><br /> The apparent causes of this event were: 1) Procedures - Procedures which control the operation and checkout of the Spent Fuel Pool Crane during non-refueling evolutions are inadequate; 2) Program/Process - Work Planning was unaware of the requirement to perform surveillance testing prior to crane use, and the requirement was not included in the work package; 3) Equipment Labeling Large metal placards mounted on the crane pertaining to movement of heavy loads were misleading and the crane safety switch/key were not labeled to identify safety prerequisites; and 4) Training/Qualification - The Mechanical Maintenance Technician operating the crane lacked knowledge of the requirement to perform surveillance testing prior to crane use. <br /><br /> There were no automatically or manually initiated safety system actuations in response to this event. <br /><br /> This event is significant since the crane was operated over the pool without first demonstrating the operability of crane interlocks and physical stops as required by the TS. Although the potential existed for heavy loads to be moved over the Spent Fuel Pool, no movement of heavy loads actually occurred. When the required surveillance test was performed, the interlocks were found acceptable. Based upon the above, there were no safety implications to the health and safety of the public as a result of this event.
3341997029 | Beaver Valley 1 | 09/07/1997 | 10/07/1997 | 9710150003 | <strong>De-energized Chart Recorder Leads to Missed Refueling Water Storage Tank Level Channel Check Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1997 at 2340 hours, with Beaver Valley Power Station (BVPS) Unit 1 in Mode 1 at 100% power, the chart recorder for Refueling Water Storage Tank (RWST) level channel D (LR-QS-100D), was discovered to not be advancing. Subsequent investigation indicated that the power switch for the recorder had been inadvertently bumped to the "OFF" position since 1910 hours on September 6, 1997, when the chart paper was changed by a Nuclear Control Operator (NCO), a licensed Reactor Operator. When it was identified that the chart recorder was de-energized, power was restored. Since the recorder had been de-energized from the time of the most recent chart paper change, the input to the recorder from RWST level transmitter LT-QS-100D had been disabled for 28.5 hours. Technical Specifications (TS) require each engineered safety feature actuation system instrumentation channel to be demonstrated OPERABLE by the performance of a channel check to be performed every 12 hours in Modes 1, 2 and 3. By BVPS procedure, channel checks are performed shiftly (8 hours) to preclude challenging the TS surveillance interval of 12 hours. Since the level recorder was de-energized for 28.5 hours, this condition rendered the channel check surveillances invalid for a 3 shift period. A maximum interval between surveillances of 15 hours is allowed pursuant to the requirements of TS. Therefore, the identified condition represents a missed TS surveillance test and is reportable as an operation or condition prohibited by TS, pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system actuations in response to this event. <br /><br /> The apparent cause of the missed surveillance was operator error. The initial operator error was the inadvertent actuation of the ON/OFF switch and de-energization of the recorder by an NCO during chart paper changeout on the 1600-2400 shift, September 6, 1997. NCOs on the subsequent three shifts (including the 1600-2400 shift NCO who bumped the ON/OFF switch) failed to detect that the recorder was de-energized (inattention to detail). <br /><br /> The RWST level channel operability check was performed at 2400 hours, September 7, 1997. All 4 level channels met the acceptance criteria for the check. RWST level channels are required, by procedure, to be within 2.2 feet of each other, highest to lowest. The In-Plant Computer (IPC) is set to alarm when an RWST level instrument is outside of the range of 49.5 feet (low alarm) to 51.5 feet (high alarm). This span is well within the acceptance criteria for the shiftly channel operability check. A review of IPC Alarm Display panel checks was performed for the shifts of concern, and no alarm messages were displayed. Thus it can be inferred that all channels remained operable. Based upon this information, there were no implications to the health and safety of the public as a result of this event.
3341997030 | Beaver Valley 1, Beaver Valley 2 | 09/08/1997 | 10/08/1997 | 9710170068 | <strong>Failure to Comply with Emergency Diesel Generator Technical Specification Action Statement</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1997, at 0900 hours, Beaver Valley Power Station (BVPS) Units 1 and 2 were in Mode 1 at 100% power. During an Operating Experience review, performed by the Operations Department, of Technical Specification (TS) requirements for the Emergency Diesel Generators (EDGs) and associated procedures, it was identified that BVPS Units 1 and 2 perform offsite power verification in advance of removing an EDG from service for surveillances or other evolutions. TS action statement 3.8.1.1.b requires, in Modes 1, 2, 3 and 4, with one EDG inoperable, that the operability of the alternating current (A.C.) offsite sources must be demonstrated within one hour and at least once per 8 hours thereafter. This operability is demonstrated by verifying correct breaker alignments and indicated power availability. Contrary to TS requirements, both units typically verify the operability of A.C. sources prior to removing an EDG from service and not necessarily within one hour of rendering the EDG inoperable. Failure to comply with a TS action statement is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system actuations in response to this event. <br /><br /> The Condition Report which documented this event identified a recent example of this failure to comply with TS. On August 20, 1997, at 1135 hours, with Unit 1 in Mode 1 at 100% power, EDG 2 was rendered temporarily inoperable in preparation for the performance of a surveillance test. The appropriate TS action statement was entered, however, verification of A.C. offsite power sources was performed at 0915, two hours and twenty minutes before the EDG was inoperable. <br /><br /> The apparent cause of the event was an inadequate interpretation of TS which resulted in inadequate procedures. Nuclear Power Division Administrative Procedure (NPDAP) 3.4, "Clearance Procedure," states: "The actions required by TS 3.8.1.1 are done prior to removal from service and logged on shift turnover checklists to be performed every 8 hours. When done prior to removal from service, the actions need not be within one hour, provided the 8 hour requirement is met." This procedure is inadequate because it is less restrictive than and does not ensure compliance with TS action statement 3.8.1.1.b. <br /><br /> This event is significant in that an action statement required by TS was not met. Although offsite power verification was not performed within one hour as required by TS, the verification was performed prior to removing the EDG from service, providing reasonable assurance of the operability of these sources. Also, the Control Room alarms and control board indications, that alert the operators if offsite A.C. power is lost, remained in a normal state, i.e., offsite A.C. power was not lost during the event. Based upon this information, there were no safety implications to the health and safety of the public.
3341997031 | Beaver Valley 1 | 09/19/1997 | 10/17/1997 | 9710210161 | <strong>Inadequate Testing of the Engineered Safety Feature Function, "Loss of Power - 4.16 kV Bus, Loss of Voltage (Start Diesel)"</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1997, with the Beaver Valley Power Station (BVPS) Unit 1 in Mode 1 at 100 percent reactor power, it was identified by the Generic Letter (GL) 96-01 review effort that the routine surveillance procedures for the Engineered Safety Features (ESF) Actuation System function, "Loss of Power - 4.16 kV Bus, Loss of Voltage (start diesel)" were inadequate. The existing surveillance procedures, as written, did not ensure the operability of the entire control circuit for the function would be verified on a frequency of at least once every 18 months. Therefore, the routine surveillance testing for verifying the diesel start function, by itself, was inadequate to satisfy the Technical Specification Surveillance Requirements (TSSR). <br /><br /> On September 19, 1997, when it was identified that the existing surveillance testing on an 18 month frequency was inadequate, no actual TSSR non-compliance existed. (Non-routine testing performed in March 1997 or actual diesel starts that have occurred within the last 18 months, in combination with the routine surveillance testing, were sufficient to currently satisfy the TSSR.) Therefore, no immediate corrective action was necessary when this surveillance deficiency was identified. Further review of plant records, however, identified instances of past non-compliance with the requirements of the TSSR-, specifically, for the emergency diesel generator EE-EG-2. <br /><br /> This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i) as an operation or condition prohibited by Technical Specifications. There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event was the inadequate development of surveillance procedures to adequately verify, the operability of the ESF function, "Loss of Power - 4.16 kV Bus, Loss of Voltage (start diesel)." Additional routine surveillance testing with an 18 month frequency will be developed by March 1, 1998, to ensure the operability of the entire ESF function is adequately verified. <br /><br /> The Unit 2 surveillance procedures for the corresponding Unit 2 ESF function were reviewed and no similar deficiencies were identified. <br /><br /> This event did not identify any actual loss of safety function. The current operability of the ESF function was not in question. Review of actual plant events from September 1990 to the present shows this ESF function has consistently performed as designed when required by those events. Additionally, the capability of the Unit 1 EDGs to correctly respond to a "loss of voltage" condition is demonstrated at least every 18 months to satisfy other TSSR. Based on this information, there were no implications to the health and safety of the public as a result of this event.
3341997032 | Beaver Valley 1, Beaver Valley 2 | 09/27/1997 | 10/27/1997 | 9711040031 | <strong>Emergency Diesel Generator Automatic Start During Bus Transfer from Unit to System Station Transformer</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1997, at 2125 hours, Beaver Valley Power Station (BVPS) Unit 1 was operating in Mode 1 at 38% power. During the performance of the Operating Surveillance Test 1OST-36.5, "Emergency Switchgear Operation Test - Transfer from Unit to System Station Transformer," on 4KV bus 1D, the automatic start of Emergency Diesel Generator No. 2 (EE-EG-2) occurred. The automatic transfer of two non-emergency 480V busses (1D and 1H) to their respective alternate supplies also occurred. 480V bus 1H transferred to bus 1G and 480V bus 1D transferred to bus 1C. The train "B" Control Room Air Handling Unit (AHU) and the Main Turbine lube oil purifier also tripped. No other actuations occurred. The EDG was not required to load and its output breaker remained open. A four hour non-emergency report was made to the NRC on September 27, 1997, at 2257 hours, via the Emergency Notification System (ENS) pursuant to the requirements of 10CFR50.72(b)(2)(ii). This event is also reportable pursuant to the requirements of 10CFR50.73(a)(2)(iv), as an event or condition that resulted in an automatic actuation of an Engineered Safety Feature (ESF). The root cause of the EDG auto-starting was due to conservative setpoints for starting the EDGs at Unit 1. A causal factor that contributed to the start was the bus loading at the time the surveillance test was being performed. This is based on the 4KV bus 1D and 4KV bus 1DF voltage recovery time being longer than the undervoltage start time for the EDG. The transfers of the 480V busses 1D and 1H were due to the 4KV bus 1D recovery time being longer than the bus transfer time. The train "B" Control Room Air Handling Unit trip was caused by inrush current following the fast bus transfer. The Main Turbine lube oil purifier trip was caused by the effect of the voltage transient on microprocessor control circuitry. The auto-starting of the EDG did not affect its ability to perform its safety function and all affected busses remained energized with the transfer of the two 480 non-safety busses to their alternate supply. These components were returned to their pretest conditions. Control Room ventilation and Main Turbine lube oil purification were also restored. Based upon the above information, there were no safety implications to the health and safety of the public as a result of this event.
3341997033 | Beaver Valley 1 | 10/08/1997 | 11/07/1997 | 9711140022 | <strong>Potential for Nuclear Instrumentation System Supply Voltages to Be Outside Design Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1997, at 1800 hours with Beaver Valley Power Station Unit 1 in Mode 6, a review by the Nuclear Engineering Department identified a potential problem. The voltage supplied to the Nuclear Instrumentation System (NIS) power supplies in the NIS instrumentation protection racks could potentially be outside the voltage range specified by the system vendor. This condition could potentially adversely affect the Reactor Trip System (RTS) Instrumentation protective action functions that rely on NIS data. <br /><br /> Upon identification of this condition, a periodic verification of the adequacy of the NIS instrumentation protection rack voltages was begun starting at 2120 hours on October 8, 1997, until the situation was resolved. Voltages at the NIS racks were found to be within the vendor's specified range. <br /><br /> The apparent cause of this event was an inadequate design change during the original construction of Unit 1 which eliminated voltage regulating transformers on the power feed to the NIS instrument racks. As a corrective action a design change was developed and implemented by October 19, 1997, which added voltage regulating transformers to the power feed of each NIS instrumentation rack. Unit 1 was defueled at the time. <br /><br /> Pursuant to the requirements of 10 CFR 50.73(a)(2)(ii)(B), this event is being reported as a condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. This event was previously reported at the time of discovery as a four-hour report pursuant to the requirements of 10 CFR 50.72(b)(2)(i) on October 8, 1997, at 2124 hours. <br /><br /> This event identified that with the existing design of the power feed to the NIS instrumentation racks, the potential existed for operating with a voltage at the NIS protection racks outside the NIS vendor's specified voltage range. Further, it was determined that this situation could adversely affect the RTS function setpoints that are developed from NIS data. No actual voltage condition outside the vendor's specified range was identified as a result of this event. Therefore, no degradation in safety function has been identified as actually occurring. Based on this information, there were no safety implications to the health and safety of the public as a result of this event.
3341997034 | Beaver Valley 1 | 10/08/1997 | 11/07/1997 | 9711140018 | <strong>Residual Heat Removal System Technical Specification Requirements Historically Not Satisfied During Refueling Cavity Draining Operations</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1997, at 1700 hours, Beaver Valley Power Station (BVPS) Unit 1 was shutdown in Refueling Mode (Mode 6). During a review of the procedure for draining the refueling cavity to the Refueling Water Storage Tank (RWST) it was identified that the Technical Specification (TS) operability requirements for the Residual Heat Removal (RHR) System have historically not been satisfied during refueling cavity draining operations. This is an operation or condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). In Mode 6, Unit 1 Technical Specifications (TS) require one Residual Heat Removal (RHR) loop in operation. The Operating Manual Procedure for draining the refueling cavity requires both RHR return isolation valves to be closed while draining the upper cavity to the RWST, hence return RHR flow to the Reactor Coolant System (RCS) is interrupted. Under these conditions, the TS requirement to have an RHR coolant loop in operation is not met, since RHR return flow to the RCS is isolated. This condition is not applicable to Unit 2, which has a different design. There were no automatically or manually initiated safety system actuations in response to this event. <br /><br /> The apparent cause of this event was technically inadequate procedures. A procedure history review was performed for the refueling cavity draining procedure. It was identified that the steps to close the RHR return valves have been in place since the original procedure was written in 1974. The technical inadequacies in the procedure are believed to be due to the changed interpretation of the TS requirements to maintain an RHR loop in operation. At the time the procedure was developed, an RHR loop was considered to be in operation during refueling cavity draining to RWST, with an RHR pump and heat exchanger in operation and the return valves operable and available, if needed.<br /><br /> This event is significant, since there was a failure to comply with the requirements of Technical Specifications. Refueling cavity draining operations are performed after refueling, when approximately one third of the core has been replaced with new fuel and the decay heat generation rate has been significantly reduced. Although the RHR return flow to the RCS was procedurely isolated during refueling cavity draining to the RWST, the core remained covered. The normal RHR loop flowpaths remained operable and available for immediate restoration. Based upon this information, there were no safety implications to the health and safety of the public.
3341997035 | Beaver Valley 1 | 10/17/1997 | 08/31/1998 | ML99343003 | <strong>Small Bore Piping Support Design Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1997, at Beaver Valley Power Station Unit 1, various original Stone and Webster Engineering Corporation pipe support design deficiencies on small bore piping (2 inch and smaller lines) were identified during an engineering review. It was identified that a sliding support was disengaged from its guide on a 2 inch line that comprises the "B" Reactor Coolant System (RCS) loop drain piping. This sliding support was restored to the proper configuration. Engineering reviewed sliding supports for safety-related small bore lines and modified some additional sliding supports to ensure they would meet design requirements.<br /><br /> Additional evaluation of RCS loop drain small bore pipe supports identified that the design of some bar type anchors was not meeting code requirements. Subsequently, anchors of this style on other small bore safety-related piping were also reviewed and modifications were made for those supports identified during the reviews which were determined to be outside their AISC (support) and ANSI (piping) code design requirements. This condition is not applicable to Unit 2. <br /><br /> Reportability determinations have identified no requirement for a 10CFR50.73 report. The original report was made November 14, 1997 as a voluntary LER to describe identified small bore piping support design concerns and to outline the follow-up investigative approach and associated corrective actions. Assessments were performed to identify any inoperable supports in accordance with Generic Letter 91-18. The apparent cause of this event was inadequate original design by the architect engineer. <br /><br /> A comprehensive evaluation, which included an operability review of the safety-related small bore piping and supports was performed and documented in a Topical Report on December 15, 1997 and a Basis for Continued Operation on December 17, 1997. A summary of the findings of that evaluation is included in this supplement. The final disposition of the identified small bore piping issues will be addressed under the Corrective Action Program. <br /><br /> The actual safety significance of this event is low, since comprehensive evaluations performed indicate that, as a consequence of safety-related small bore piping support design deficiencies, none of the lines would experience pipe stresses or support loading of a magnitude that would result in an inoperable condition or a condition that significantly compromises plant safety. An evaluation performed pursuant to 10CFR Part 21 identified no substantial safety hazard associated with this event. Based upon this information, there were no safety implications to the health and safety of the public as a result of this event.
3341997036 | Beaver Valley 1, Beaver Valley 2 | 11/13/1997 | 12/12/1997 | 9712230345 | <strong>Inadequate Channel Check for Meteorological Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1997, at 1600 hours, Beaver Valley Power Station (BVPS) Unit 1 was in Mode 5 (Cold Shutdown) and Unit 2 was in Mode 1 at 100% power. During the ongoing review of the Technical Specification (TS) surveillance testing program, being conducted by the Operations Department, as committed to in LER 1-97-013-00, it was identified that the daily channel checks for the Meteorological Monitoring Instrumentation were inadequate under certain channel conditions. Current surveillance procedures are inadequate, since they do not ensure this testing is consistently performed in accordance with TS requirements. Therefore, compliance with the applicable Limiting Conditions for Operation (LCO) was not adequately verified. This is an operation or condition prohibited by Technical Specifications and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system actuations in response to this event. Operations performs the Meteorological Monitoring Instrumentation channel checks by utilizing a video display terminal (CRT) in the Unit 1 Control Room. This CRT is part of the Atmospheric Radioactive Effluent Release Assessment System (ARERAS) that runs the Meteorological Information and Dose Assessment System (MIDAS) software package. Since a procedure change in September 1993, the Control Room display and MIDAS software has been used to satisfy the required Technical Specification channel checks for wind direction, wind speed, and differential air temperature (delta-T). However, performance of a channel check cannot be consistently confirmed due to certain default functions of the MIDAS software and the unavailability of individual channel displays to the Control Room Operators during these default modes. In the absence of procedural guidance, for example, it is possible for a primary channel to be inoperable and, due to default displays, for the Operator to be unaware of the true channel status and consequently miss a required channel check. The apparent cause of this event was inadequate change management. Existing procedures do not provide the Operator with guidance to adequately perform a qualitative assessment of channel behavior during operation by observation, particularly when the numeric difference between primary and redundant channels for a given parameter is outside of the predefined tolerance. Currently, Health Physics is daily providing the Control Room with several 15 minute averages of the individual primary and redundant channels for each Meteorological Monitoring, Instrumentation parameter to satisfy the TS channel check requirement. Surveillance procedures were revised to ensure that the Meteorological Monitoring Instrumentation channel checks meet the requirements of TS. There was no loss of capability to respond to the accidents evaluated in the FSAR as a consequence of this event. Emergency Plan Implementing Procedures have contingency procedures to address the actual loss of Meteorological Instrumentation. Consequently, there were no safety implications to the health and safety of the public as a result of this event.
3341997037 | Beaver Valley 1, Beaver Valley 2 | 11/20/1997 | 12/19/1997 | 9712300160 | <strong>Condition Prohibited by Technical Specifications - Inadequate Solid State Protection System Logic Testing</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1997 at 1600 hours, as a result of an Engineering review of industry operating experience applied to Beaver Valley Power Station (BVPS), it was identified that the routine surveillance testing for portions of two Solid State Protection System (SSPS) automatic actuation logic functions was inadequate. This applied to both Units 1 and 2. The identified surveillance deficiencies involved the inadequate verification during the bimonthly testing of the SSPS logic for: (1) the P-14 interlock (two of three high-high steam generator level indication for any one steam generator) isolation of feedwater and (2) the automatic block of the source range high neutron flux reactor trip by the P-10 (10 percent power) interlock. Unit 1 was in Mode 5 at the time the event was discovered and Unit 2 was in Mode 1 at 100 percent reactor power. <br /><br /> This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i) as an operation or condition prohibited by Technical Specifications. There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event at both Units was procedural deficiencies. <br /><br /> Unit 2 entered T.S. 3.0.3 at 1600 hours on November 20, 1997 for the missed surveillances. Additional testing was completed which adequately verified these functions and Unit 2 exited T.S. 3.0.3 at 0400 hours on November 21, 1997, within the 24 hour time limit allowed by T.S. 4.0.3 for completing a missed surveillance. <br /><br /> Since Unit 1 was in Mode 5 at the time of the identification, no specific T.S. Actions applied. Additional surveillance testing was completed at Unit 1 to adequately verify these functions by December 16, 1997 with the Unit still in Mode 5. <br /><br /> There were no safety implications to the health and safety of the public as a result of this event.
3341997038 | Beaver Valley 1 | 05/24/1997 | 01/05/1998 | 9807170320 | <strong>Unsealed Penetration in Main Steam Valve Cubicle Floor</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1997, a degraded penetration seal (MSV-752-1910) associated with a 3/4 inch drain line located in the floor of the Unit 1 main steam valve cubicle was discovered in the field. However, actions to address the degraded floor penetration seal were not taken until September 9, 1997. At that time an hourly fire watch was established. <br /><br /> Installation of a hydrostatic and fire rated seal was completed on October 8, 1997. On December 5, 1997, an engineering evaluation concluded that in the event of a feedwater line break, water could drain through the degraded floor penetration seal and enter the pump room below, causing a temperature rise in the area that could disable the motor driven auxiliary feedwater pumps. In addition, the turbine driven auxiliary feedwater pump may also be unavailable in the event of a feedwater line break. <br /><br /> The degraded floor penetration seal together with the postulated event, could cause three auxiliary feedwater pumps to become inoperable. Since this condition is outside the design basis of the plant, and could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident, it is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B), and 10 CFR 50.73(a)(2)(v). <br /><br /> The cause of the penetration seat degradation could not be determined. The delay from May 24, 1997 to September 9, 1997 in addressing the degraded seal was attributed to a cognitive error by those who dispositioned the degraded seal condition. Personnel failed to recognize the high priority and safety significance associated with fire rated and hydrostatic penetration seals. There were no structures, components, or systems (other than the penetration seal) that were inoperable or that contributed to the condition. Because there were no pipe breaks in the main steam valve cubicle area, the condition had no direct effect on the ability of the auxiliary feedwater pumps to perform their safety function in the room below. The steam driven auxiliary feedwater pump is assumed disabled by the postulated main feedwater line break event. Potential loss of both remaining motor driven auxiliary feedwater pumps would have significantly reduced the defense in depth available to remove decay heat. However, there was no actual safety consequence to this event since there were no pipe breaks; but had the potential for moderate safety consequences. The health and safety of the public were not affected.<br /><br /> An additional degraded penetration seal was discovered on June 11, 1998. This seal had ceramic fiberblanket damming material in its penetration (Fiberfrax), but no sealing material. The seal has now had proper sealing material installed. The room and adjacent room were completely inspected and no further inadequate floor penetration seals were identified.
3341997039 | Beaver Valley 1, Beaver Valley 2 | 12/08/1997 | 01/07/1998 | 9801130109 | <strong>Gas Accumulation in Charging/High Head Safety Injection Pump Piping</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1997 it was determined that Unit 1 and Unit 2 may have operated in a condition that is outside the design basis of the plant. A minimum of one charging/High Head Safety Injection (HHSI) pump may not have been available to provide emergency core cooling as described in the UFSAR due to intrusion of gas into the suction of the pumps, and subsequent gas binding. The determination is based on engineering evaluation of the results of scoping experiments conducted to assess fluid now patterns entering the Unit 1 and Unit 2 charging pumps.<br /><br /> The cause of the condition was attributed in part to the design of charging/HHSI pump minimum flow recirculation line orifices. These orifices were found to strip non-condensable gas from the recirculation flow. In the event of a loss of coolant accident concurrent with a loss of offsite power, this design defect could have resulted in a loss of safety function necessary to mitigate accident consequences. <br /><br /> Flow orifices are being replaced at Unit 1, and at Unit 2, to reduce the generation of gas bubbles. In addition, increased monitoring and vent system improvements are planned. <br /><br /> On December 8, 1997 at 0412 hours, a one hour non-emergency notification of this condition at Unit 1 and Unit 2 was made pursuant to the requirements of 10 CFR 50.72 (b)(1)(ii). The determination that a minimum of one HHSI/charging pump may not have been available to provide emergency core cooling as described in the UFSAR, is considered a condition outside the design bases of the plant and a condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Therefore, this condition is reportable in accordance with 10 CFR 50.72(b)(1)(ii), 10 CFR 50.73(a)(2)(ii), and 10 CFR 50.73(a)(2)(v). <br /><br /> The design defect associated with the charging/HHSI pump minimum flow recirculation line orifices could create a substantial safety hazard, and is reportable pursuant to 10 CFR 21 requirements. This report constitutes a 10 CFR 21 notification. The ability to provide emergency core cooling via the charging/HHSI pumps could have been adversely affected and the safety system may not have performed its' safety function. However, there were no actual concurrent failures of redundant charging/HHSI pumps at either unit. Therefore, there were no safety consequences to the health and safety of the public.
3341997040 | Beaver Valley 1, Beaver Valley 2 | 12/10/1997 | 01/09/1998 | 9801160020 | <strong>Inadequate Testing of Reactor Protection System P-8 Interlock Due to Solid State Protection System Semi- Automatic Tester Design Error</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1997, at 1318 hours, with Beaver Valley Power Station (BVPS) Unit 1 in Cold Shutdown (Mode 5) and Unit 2 at 100 percent power (Mode 1), during an engineering review of Westinghouse Technical Bulletin NSD-TB-97-07, "SSPS P-8 Testing," it was identified that the P-8 Interlock function has not been fully tested during routine Solid State Protection System (SSPS) logic testing. Specifically, although the reactor trip function for Loss of Reactor Coolant System (RCS) Flow - Single Loop is properly tested for the above P-8 condition (reactor trip enabled), the testing was inadequate to verify this reactor trip is blocked below P-8. This condition applies to both units. This is an operation or condition prohibited by Technical Specifications (TS) and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system actuations in response to this event.<br /><br /> Upon discovery, Unit 2 entered the applicable TS Limiting Condition for Operation (LCO) action statement. This requires, with less than the minimum channels operable, within one hour, that the P-8 interlock is verified to be in its required state for the existing plant condition by observation of the associated permissive annunciator window. This action statement was met by 1334 hours on December 10, 1997. There was no applicable action statement for Unit 1, since P-8 is required to be operable only in Mode 1. The applicable surveillance test procedures were revised for both Units on December 10, 1997, to include a manual test to verify P-8 operation. Required testing to verify operability of the P-8 interlock was performed on December 13, 1997, (Train B) and December 16, 1997, (Train A) for Unit 1 and on December 10, 1997, (Train B) and December 29, 1997, (Train A) for Unit 2. <br /><br /> The apparent cause of the inadequate logic testing was a vendor design error in the design of the SSPS semi-automatic tester. The test arrangement did verify that the Loss of Flow - Single Loop (Above P-8) reactor trip can occur. However, the testing scheme did not verify that this reactor trip will be blocked below the P-8 setpoint. Failure to recognize this design inadequacy resulted in inadequate surveillance procedures. The consequences of the P-8 block failing would be conservative for the purposes of reactor protection, since the Loss of Flow - Single Loop (Above P-8) reactor trip would continue to be active below the P-8 setpoint (i.e., 30 percent power). Additionally, the station abnormal operating procedures require a manual reactor trip on loss of a reactor coolant pump, regardless of power level. Based upon this information, there were no safety implications to the health and safety of the public.
3341997041 | Beaver Valley 1, Beaver Valley 2 | 12/15/1997 | 01/14/1998 | 9801260031 | <strong>Failure to Remove Power From the Isolated RCS Loop Isolation Valve Operators Within One Hour as Required by Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1997, with Unit 1 in Mode 4 and Unit 2 in Mode 5, it was discovered as part of an ongoing Technical Specification (TS) surveillance review that no documentation exists to show that, on September 30, 1997, power was removed from Unit 1 reactor coolant system loops B and C isolation valve motor operators within one hour of loop isolation as required by limiting condition for operation 3.4.1.4.2. This represents an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system actuations in response to this event. <br /><br /> The apparent cause of this event is inadequate actions taken to control and implement a change. Unit 1 and Unit 2 TSs for isolated loop startup were amended on March 22, 1996 and April 8, 1996 respectively. Revisions to procedures 1OM6.4AO and 2OM6.4W made as a result of these amendments were incorrect in that they allowed for removal of the power from the loop isolation valve operators beyond the TS limit of one hour. Loop isolation events for both units dating from January, 1995 were reviewed to verify that no other violation of limiting condition for operation 3.4.1.2 had occurred as a result of the incorrect procedure changes. <br /><br /> As completed corrective actions, procedures 1OM6.4AO and 2OM6.4W were revised to conform with TS 3.4.1.4.2. Since the occurrence of this event, the TS Control Program has been revised to require Safety & Licensing Department review of procedure manual or administrative controls to be changed as part of the license amendment implementation. Future corrective actions include review of this event with Nuclear Operations Department procedure writers and operating crews. <br /><br /> The safety consequences of this event are minimal. As discussed in the UFSAR, removal of power from the loop isolation valve operators when an RCS Loop is isolated is one step to ensure that the startup of an isolated loop is performed in a controlled manner that virtually eliminates any inappropriate sudden positive reactivity addition from unborated water. Unisolation of the Unit 1 B and C loops following this event was performed in accordance with Nuclear Operations Department procedure, which in itself eliminated the possibility of inadvertent positive reactivity addition by controlling loop fill source, ensuring sampling was performed, and placing time constraints on the unisolation process to prevent stratification.
3341997042 | Beaver Valley 1, Beaver Valley 2 | 12/15/1997 | 01/14/1998 | 9801260022 | <strong>Failure to Perform Axial Flux Difference Monitor Surveillance as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1997, with Unit 1 in Mode 5 and Unit 2 in Mode 1 at 100% power, it was discovered as part of an ongoing Technical Specification (TS) surveillance review that surveillance requirement (SR) 4.2.1.1.a.2 has historically not been complied with. This surveillance requirement states that "The indicated axial flux difference shall be determined to be within its limits during power operation above 15% of rated thermal power by monitoring the indicated AFD (axial flux difference) for each operable excore channel at least once per hour for the first 24 hours after restoring the AFD Monitor Alarm to operable status.". Contrary to this, in September, 1993, operating procedures were revised to eliminate the requirement to manually log axial flux difference (AFD) as a result of a TS interpretation defining AFD operability. Monitoring of the AFD required by TS 4.2.1.1.a.2 was accomplished by automatic data acquisition utilizing the process computer, instead of manual logging by an operator. This failure to comply with TS 4.2.1.1.a.2 represents an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). <br /><br /> The apparent cause of the event was misunderstood instructions or information, which resulted in inadequate procedures. A TS interpretation letter misinterpreting written TS requirements concerning the performance of the surveillance for axial flux monitoring was inappropriately issued and implemented in site procedures. <br /><br /> As a corrective action, Units 1 and 2 procedures 1OM49.4L, 1OST5A.1, 2OM49.4C and 2OST5A.1 have been revised to eliminate the TS interpretation that computer data history prior to and during the period of inoperability can be used to satisfy the surveillance requirement monitoring criteria. As an additional corrective action, a review of TS interpretations was conducted, which resulted in the deletion of the AFD interpretation. <br /><br /> There is minimal safety consequence to this event. In order to procedurally substitute computer AFD monitoring for the hourly manual logging following the restoration of the AFD to service, it was required that there be zero penalty minutes for 24 hours prior to, and during, the AFD removal from service time period. Upon return of the AFD to service, the AFD was reset to zero minutes. This method eliminated any chance for bad data to affect the AFD calculation. Based on this, the number of penalty minutes accumulated, as defined by SR 4.2.1.2, prior to, during, and following restoration of the AFD was always known and accurate. Consequently, computer AFD monitoring of penalty minutes is technically equivalent to the manual once per hour logging specified in surveillance requirement 4.2.1.1.a.2. However, this does not strictly comply with TS 4.2.1.1.a.2.
3341997043 | Beaver Valley 1 | 12/31/1997 | 01/30/1998 | 9802110118 | <strong>Inadequate Surveillance Testing of Solid State Protection System Resulted in Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On December 31, 1997 at 1300 hours, with Unit 1 in Mode 3, an operator noted during a performance of the monthly Train A Solid State Protection System (SSPS) functional surveillance test OST 1.1.11 that the method for testing the Safety Injection System transfer to recirculation manual initiation function appeared to make two of the four Refueling Water Storage Tank (RWST) Engineered Safety Features Actuation System (ESFAS) level instrument loops inoperable without bypassing them. The Nuclear Shift Supervisor was notified, and an investigation initiated. Investigation verified that opening the test switch for an RWST ESFAS instrument loop caused the loop to fail low and be inoperable but not bypassed. This resulted in the SSPS receiving an actual low ('tripped') signal to both trains from each of the two RWST ESFAS level instrument loops being tested. Unit 1 Technical Specifications (TS) Table 3.3.3, "Engineered Safety Feature Actuation System Instrumentation", Action 16, does not permit any RWST ESFAS low level instrument channels to be inoperable without being placed in the bypass position. As a result, inadvertent entry into TS 3.0.3 occurred each time a RWST ESFAS low level instrument loop was taken out of service (made inoperable) without being placed in the bypass mode during monthly performances of OST 1.1.11. This has occurred since 1978. The same condition existed for the monthly Train B SSPS functional surveillance test OST 1.1.12. Entry into TS 3.0.3 is a condition prohibited by TS and is thus reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i). There were no automatically or manually initiated safety system responses as a result of this event. <br /><br /> The apparent cause of this event was a misinterpretation of TSs during procedure development. It is apparent that the procedure developer was not aware that TS 3.0.3 would be entered during performance of the surveillance tests. <br /><br /> It has been determined that the monthly surveillance of the Safety Injection System transfer to recirculation manual initiation function is already being met through alternate testing, so the test method currently specified in 1OST-1.11 and 1OST-1.12 will be deleted. <br /><br /> Should an actual Safety Injection signal have occurred while two channels were tripped, a transfer to recirculation mode would have occurred causing a loss of suction to all high-head and low-head safety injection pumps. However, the period of time during which both channels were tripped was approximately 20 minutes per month for both trains. Based on this, the safety consequences were low.
3351997001 | St. Lucie 1 | 11/02/1997 | 12/02/1997 | 9712090200 | <strong>Non-Conservative Recirculation Actuation Signal Set Point Resulted in Operation Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1997, Unit 1 was defueled in support of the steam generator replacement refueling outage. During the outage, obsolete Engineered Safety Feature Actuation System (ESFAS) bistables were being replaced to improve system reliability. During this effort on November 2, 1997, non-licensed utility personnel determined that the ESFAS Recirculation Actuation Signal (RAS) bistable set point for refueling water tank level had been set less conservative than the Technical Specification set point. <br /><br /> The apparent cause for the non-conservative RAS set point was an inadequate set point and instrument loop scaling process. The process associated with the implementation of the refueling water tank instrument set point calculation resulted in not all required related plant procedures being revised. <br /><br /> Corrective actions include: revising the ESFAS functional test procedure with the proper set point; implementing and calibrating to the proper set point; reviewing other set points on Unit 1 and 2; revising and training on a new Engineering set point calculation process; and issuing of a technical alert to include lessons learned.
3351997002 | St. Lucie 1 | 02/21/1997 | 03/21/1997 | 9703270101 | <strong>Operation in Excess of Maximum Rated Thermal Power Due to Digital Data Processor Calorimetric Error</strong><br /><i>Abstract:&nbsp;</i>This LER is a voluntary report. On February 21, 1997, St. Lucie Unit 1 was operating at a steady-state power level of 100% Rated Thermal Power (RTP) as determined from the Digital Data Processing System (DDPS) display. While performing a feed water flow instrument loop calibration, maintenance personnel determined that proper scaling constants were not being used for the feed water flow input signals to the DDPS. This condition caused the DDPS calorimetric calculation of reactor core thermal power to be non-conservative in that facility steady-state operation with the DDPS indicating 100% RTP resulted in actual reactor power at 100.43% RTP. Plant operation was limited to not more than 99% RTP (indicated) while the problem was thoroughly investigated and corrected. On March 1, 1997, St. Lucie Unit 1 was returned to 100% RTP. <br /><br /> The cause of this event was failure to implement effective configuration controls for the DDPS computer software. Corrective actions include: 1) Acceptable performance of all critical DDPS functions was verified prior to restoration of full power operations. 2) Review of accountabilities for software modifications and identification of program improvements. 3) Development of verification and validation requirements that challenge all critical attributes for software changes within the DDPS. 4) Development of controlled operating procedures to address DDPS operation. 5) Use of the St. Lucie Total Equipment Data Base or controlled procedures to ensure configuration control of critical DDPS constants. 6) Modification of the software vendor blanket purchase order to clarify that compliance with FPL administrative procedures is required.
3351997003 | St. Lucie 1 | 03/04/1997 | 03/31/1997 | 9704100008 | <strong>Automatic Reactor Trip Resulting from the Loss of Electrical Power to the 1A2 Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1997, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. Reactor Protective System (RPS) following the loss of a reactor coolant pump (RCP). Operation of the RCP was interrupted when the electrical supply breaker for the pump opened. Following the trip, a main feedwater regulating valve failed to close as designed and operator action was taken to mitigate excess feedwater flow. The plant was stabilized in Mode 3 and subsequently returned to Mode 1 operation on March 7, 1997, following replacement of the RCP breaker and repair of the main feedwater regulating valve control circuit relay. <br /><br /> The automatic reactor trip was caused by the loss of the 1A2 RCP when an electrical supply breaker for the pump opened. Loss of the RCP resulted in a valid actuation of the RPS low reactor coolant flow trip. The opening of the supply breaker was evaluated by FPL and an experienced vendor and a specific cause was not determined. Corrective actions were taken for the potential root causes identified. The failure of the main feedwater regulating valve to close was caused by the malfunction of a K2 relay in the control circuitry for the valve. <br /><br /> Corrective actions include: 1) The RCP breaker was replaced and the pump was returned to service. 2) Breaker inspection and testing was performed. 3) Similar breakers were inspected and adjusted. 4) Visual monitoring was installed in the RCP breaker area. 5) The feedwater regulating valve was returned to service following replacement of a failed relay in the valve control circuit. 6) Additional failure analysis is being performed for a relay which was replaced in the feedwater valve circuitry. 7) Unit 2 main feedwater regulating valve testing will be performed during the next scheduled refueling outage.
3351997004 | St. Lucie 1, St. Lucie 2 | 04/02/1997 | 04/30/1997 | 9705060087 | <strong>Operation of Refueling Machine in a Manner Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1997, St. Lucie Units 1 and 2 were operating at 100 percent reactor power. As a result of reviewing operating experience concerning the original design and past operation of the refueling machine, a deficiency was identified that represented a failure to satisfy Technical Specification requirements regarding the manipulator crane overload cut off limit. <br /><br /> The cause of this event was due to the original design of the refueling machine automatic bypass feature, which conflicts with the Technical Specification requirements for the manipulator crane. <br /><br /> The corrective action is to eliminate overload cut off limit bypass by modifying the refueling machine overload protection circuitry. This modification has been implemented for Unit 2 and is planned for Unit 1.
3351997005 | St. Lucie 1 | 04/19/1997 | 05/13/1997 | 9705200337 | <strong>Reactor Shutdown Required by Technical Specifications due to Reactor Coolant Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1997, St. Lucie Unit 1 was operating in Mode 1 at 100 percent reactor power. Leakage from a one inch line on a safety injection (SI) pipe vent was identified and subsequently determined to be reactor coolant pressure boundary (RCPB) leakage. The leakage was restricted to Safety Injection Tank 1B2 inventory, and no reactor coolant leakage resulted. A reactor shutdown was initiated on April 19, 1997, and was completed in accordance with Technical Specification requirements. The Unit was placed in Mode 5 on April 20, 1997, to implement repairs. During the plant cooldown, shutdown cooling (SDC) train 1A was declared inoperable and the redundant train was used to complete the cooldown. The RCPB leakage was repaired and the Unit was subsequently returned to Mode 1 operation on April 23, 1997. <br /><br /> The plant shutdown was required by Technical Specifications due to the presence of pressure boundary leakage. The failure mechanism associated with the pressure boundary leakage was determined to be hot cracking of a socket weld associated with the SI vent line. The hot cracking was caused by weld contamination. The inoperability of the 1A SDC train was due to the misalignment of a minimum flow recirculation line, and the presence of gas voids in the high points of the 1A SDC suction line. <br /><br /> Corrective Actions Include: 1) Repairs were completed to the RCPB and the 1A SDC train was restored to service. 2) Additional analysis was performed to confirm the failure mechanism for the affected socket weld. 3) Weld testing is being performed to evaluate for potential improvements. 4) The 1A SDC train was restored to operation following venting and inspection. 5) SDC system venting procedures are being revised to include additional frequency and temperature requirements.
3351997006 | St. Lucie 1, St. Lucie 2 | 05/01/1997 | 06/02/1997 | 9706100099 | <strong>Operation Prohibited by technical Specifications Due to Inadequately Tested Degraded Voltage System</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1997, Unit 1 was in Mode 1 at 100 percent power and Unit 2 was in Mode 6 and defueled for a refueling outage. As a result of the on-going review of the Unit 2 Engineered Safety Features Actuation System (ESFAS) Test Procedure for compliance with NRC Generic Letter 96-01, it was discovered that the Safety Injection Actuation Signal (SIAS) permissive contact for degraded voltage protection was not adequately tested as required by the Technical Specifications. <br /><br /> The cause of the event was inadequate surveillance test procedures which did not test the degraded voltage protection system SIAS permissive contact. This contact provides an ESFAS function which initiates load shed and Emergency Diesel Generator (EDG) start for a sustained degraded voltage condition.<br /><br /> The Unit 1 A EDG was declared inoperable, due to a missed surveillance, at approximately 0900 on 5/1/97. Testing of the degraded voltage system SIAS permissive was successfully performed at approximately 1630 on 5/1/97, and the 1A EDG was subsequently declared operable. Operability of the Unit 1 B EDG was demonstrated via a previous event where the degraded voltage permissive signal was provided by a Containment Isolation Actuation Signal (CIAS) contact. Testing of the Unit 2 degraded voltage system ESFAS permissives was satisfactorily completed May 9, 1997. <br /><br /> The Unit 2 ESFAS surveillance test procedure was revised to ensure the degraded voltage system SIAS permissive contact is tested. The Unit 1 ESFAS surveillance test procedure will be revised to ensure the degraded voltage system ESFAS permissive contacts are tested.
3351997007 | St. Lucie 1, St. Lucie 2 | 05/02/1997 | 05/29/1997 | 9706040241 | <strong>Reactor Coolant Pump Oil Collection System Outside Appendix R Design Bases</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1997, St. Lucie Unit 1 was at 100 percent power, and St. Lucie Unit 2 was in Mode 6 and defueled for a refueling outage. An outage inspection of the Unit 2 Reactor Coolant Pumps (RCPs) identified minor external oil leakage at the upper and lower RCP motor oil reservoir locations that was not captured by the RCP Oil Collection System. Appendix R Section III.O requires that the RCP Oil Collection System be designed to collect oil from all potential RCP oil leakage sources.<br /><br /> The cause of this event was due to design deficiencies of the RCP Oil Collection System. Corrective actions include repairs to identified leak sites, and modifications to the RCP Oil Collection System to capture any future leakage from these areas.
3351997008 | St. Lucie 1, St. Lucie 2 | 07/28/1997 | 08/27/1997 | 9709040179 | <strong>Inoperable Mechanical Fire Penetrations Outside Appendix R Design Bases</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1997, St. Lucie Units 1 and 2 were in Mode 1 at 100 percent power. FPL was investigating work backlogs and determined that the corrective actions associated with NRC Information Notice (IN) 94-28, that dealt with fire protection barrier deficiencies, were still pending. The original IN review required the evaluation of 218 mechanical penetration seals because the installed condition did not correlate to fire barrier qualification testing. However, the original review did not establish if the 218 seals were operable. <br /><br /> An operability assessment for the 218 penetration seals was performed and of this population, seven penetration seals in Unit 1 and eight penetration seals in Unit 2 are inoperable. <br /><br /> The apparent cause of this event was that the seal manufacturer did not provide formal documentation for installed seals that deviated from qualification test configurations. Additionally, the problem identification and corrective action procedure in place during the original IN review was weak in that the requirements and guidance for performing operability assessments were not well defined. <br /><br /> Corrective actions include: 1) the existing hourly roving fire watch includes the 15 inoperable seals, 2) Generic Letter 86-10 mechanical fire penetration evaluations will be performed for the 218 mechanical seals that are not bounded by tested configurations, and 3) the inoperable mechanical fire penetrations will be modified to meet three hour fire barrier criterion.
3351997009 | St. Lucie 1 | 09/17/1997 | 10/17/1997 | 9710200200 | <strong>Inoperable PORV Block Valve Resulted in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1997, St. Lucie Unit 1 was at 100% power. During Generic Letter 89-10 self-assessment activities, utility personnel determined that the initial Motor Operated Valve Load Sensitive Behavior (LSB) assumptions used in the St. Lucie MOV program were non- conservative. When plant specific LSB was applied to V-1403, a Power Operated Relief Valve (PORV) block valve, the valve's ability to close at design differential pressure could not be analytically confirmed. Therefore, PORV block valve V-1403 was declared inoperable, the valve was closed, and its power removed pursuant to Technical Specification 3/4.4.12 ACTION statement requirements. <br /><br /> The apparent cause of this event was that the St. Lucie Plant GL 89-10 program plan to review plant specific differential pressure test results and incorporate changes into the GL 89-10 program documentation was not being formally tracked. The present day St. Lucie corrective action follow up program, the Plant Manager Action Item (PMAI) system, did not exist at the time the GL 89-10 program was established. All GL 89-10 program requirements and improvements identified during the self assessment are now tracked in the PMAI system. Corrective actions to restore V-1403 to operable status include implementation of maintenance and modifications scheduled for the upcoming St. Lucie Unit 1 SL1-15 refueling outage. Additionally, all GL 89-10 program documentation for V-1403 will be updated.
3351997010 | St. Lucie 1 | 10/27/1997 | 01/27/1998 | 9802050009 | <strong>Inadvertant Core Alteration Prohibited by Technical Specifications Due to Stuck Control Element Assembly (CEA)</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1997, St. Lucie Unit 1 was in Mode 6 with the reactor head removed in preparation for defueling. The containment equipment hatch and personnel access airlock were open, as allowed by Technical Specifications. Personnel commenced Upper Guide Structure (UGS) withdrawal from the reactor vessel in accordance with procedures. As the UGS cleared the alignment pins, a Control Element Assembly (CEA) was discovered attached to the UGS, which had been unexpectedly withdrawn from the core. This constituted a core alteration without the containment penetration status required by Technical Specifications. Containment integrity was set within 21 minutes of discovery of the stuck CEA. A safety evaluation was performed and a procedural revision made to continue the UGS move. Reactor cavity water level was raised to increase shielding. Anticipating elevated containment radiation levels, the Containment Isolation System (CIS) was manually actuated prior to continuing the lift. The UGS lift recommenced on October 28. A remote camera situated beneath the UGS monitored the progress, and the CEA remained attached throughout the transit. Once the transit to the refueling cavity was completed, the CEA was recovered from the UGS. <br /><br /> The cause of the event was personnel error during unlatching that resulted in CEA #24 remaining partially latched to its extension shaft. A high friction condition within the CEA #24 extension shaft was determined to be a contributing factor. Corrective actions included the development of procedural enhancements to preclude this condition, as well as replacement of the CEA #24 extension shaft. <br /><br /> This LER revision transmits the cause and corrective actions for this event.
3351997011 | St. Lucie 1 | 11/02/1997 | 12/02/1997 | 9712090200 | <strong>Non-Conservative Recirculation Actuation Signal Set Point Resulted in Operation Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1997, Unit 1 was defueled in support of the steam generator replacement refueling outage. During the outage, obsolete Engineered Safety Feature Actuation System (ESFAS) bistables were being replaced to improve system reliability. During this effort on November 2, 1997, non-licensed utility personnel determined that the ESFAS Recirculation Actuation Signal (RAS) bistable set point for refueling water tank level had been set less conservative than the Technical Specification set point. The apparent cause for the non-conservative RAS set point was an inadequate set point and instrument loop scaling process. The process associated with the implementation of the refueling water tank instrument set point calculation resulted in not all required related plant procedures being revised. Corrective actions include: revising the ESFAS functional test procedure with the proper set point; implementing and calibrating to the proper set point; reviewing other set points on Unit 1 and 2; revising and training on a new Engineering set point calculation process; and issuing of a technical alert to include lessons learned.
3361997001 | Millstone 2 | 06/21/1996 | 02/27/1999 | 9903160099 | <strong>Inadequate Fire Seal Material Installed Between Some Appendix R Fire Areas</strong><br /><i>Abstract:&nbsp;</i>A review was completed of fire barriers credited in the Millstone Nuclear Power Station - Unit 2 Appendix R Compliance Report. This review found combustible material in areas credited as barriers in the referenced report. This material was installed during original construction as filler material in expansion joints and seismic gaps of the barrier interfaces. The review which found this material is part of the larger on-going effort to reestablish the design and licensing basis for Millstone Unit 2. <br /><br /> The cause of this condition was an error in the evaluation of the combustibility of material in the expansion joints and seismic gaps of Appendix R fire barriers because of a historical lack of ownership of the fire protection program. This material is part of the original plant installation and was not identified as a combustible material that forms part of the required fire barriers. <br /><br /> Upon discovery of combustible material in the joints and gaps of fire barriers, fire watches were established as a compensatory measure as required by the Fire Protection section of the Technical Requirements Manual. Compensatory measures will remain in effect until adequate barriers are re-established. <br /><br /> This is a complete rewrite of the original LER.
3361997002 | Millstone 2 | 01/08/1997 | 02/07/1997 | 9702190114 | <strong>Damper 2-HV-210 Cannot be Manually Operated within ten minutes as Required in the Accident Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1997, at 1230 Hours, it was postulated that the Control Room Emergency Filtration System (CREFS) common inlet damper, 2-HV-210, could become stuck closed, causing a single failure that disables both CREFS Facilities. There is no 'hand operator' and the damper is located about 9 feet above the floor, so operations personnel would not be able to open the damper within the 10 minutes required by the control room habitability analysis. The Millstone Unit 2 (MP2) accident analysis requires the CREFS to be operating in the recirculation/filtration mode within 10 minutes of the accident initiation, and takes credit for manually opening the damper if it does not go to the 'fail open' position. The FSAR TABLE 9.9-17 'Control Room Air Conditioning System Failure Mode Analysis' shows the damper (2-HV-210) does not meet the single failure criterion, but that it can be manually opened within 10 minutes, using the 'hand operator'. Emergency operating procedures and annunciator response procedures direct operations to align one Facility of CREFS for operation. The plant was in Mode 6 at 0 percent power at the time of discovery. <br /><br /> The cause of this event was inadequate evaluation of mechanical binding when the single failure was first discovered and the FSAR revision was prepared in June 1994. Additionally, the ability to manually open the damper was not validated. <br /><br /> The immediate corrective action was to place the damper in the 'fail open' position. An evaluation of 2-HV-210 and associated procedures will be performed. Other operator actions which are included in the safety analyses will be reviewed and validated, as necessary. Design changes and validations which result will be completed before entering Mode 4.
3361997003 | Millstone 2 | 12/16/1996 | 04/15/1997 | 9704220078 | <strong>Historical Technical Specification Noncompliance of Plant Surveillance Procedure Used To Perform Periodic Inspection of Fire Protection System Smoke Detectors</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1996, a discrepancy was discovered in the plant procedure utilized to perform the periodic inspection of the fire protection system smoke detectors. On January 13, 1997, a review of this discrepancy identified that the surveillance procedure utilized prior to November 1995 (Surveillance Procedure (SP) 2618C, "Fire Protection System Smoke Detector Test") did not ensure that the requirements of Technical Specification (TS) Surveillance Requirement 4.3.3.7.1 were met. In addition, on March 16, 1997, it was discovered that SP2618C did not adequately document the trip functions of associated components during the testing of smoke detectors. <br /><br /> Fire protection requirements are no longer contained in the Technical Specifications. These requirements were removed by Millstone Unit No. 2 License Amendment No. 191 which was issued on November 3, 1995. Prior to Amendment No. 191, Technical Specification Surveillance Requirement 4.3.3.7.1 included requirements for smoke detectors in the Auxiliary Building (-5 foot elevation). The requirements for the fire protection equipment were relocated to the Technical Requirements Manual (TRM) which is a plant controlled document. <br /><br /> The cause of both events was failure to properly incorporate Technical Specification surveillance requirements into plant surveillance procedures. <br /><br /> This event reports the historical noncompliance with Technical Specification Surveillance Requirement 4.3.3.7.1. SP2618C has been partially revised to ensure compliance with the fire protection system requirements in the TRM for the smoke detectors.
3361997004 | Millstone 2 | 01/23/1997 | 02/20/1997 | 9702270420 | <strong>Violation of Technical Specification 3.1.2.3 Requirement for Number of High Pressure Safety Injection Pumps Capable of Injecting into the Reactor Coolant System</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 23, 1997, it was discovered that three high pressure safety injection (HPSI) system pumps were capable of injecting water into the reactor coolant system contrary to the requirements of Technical Specification 3.1.2.3. This condition existed for approximately 36 minutes. The incorrect alignment occurred following the monthly operability test of the C HPSI pump and an inservice test of the B HPSI pump. <br /><br /> The cause of this event was personnel error. The Unit Supervisor involved in this event did not correctly identify all of the applicable requirements of the Technical Specifications. Contributing to this event was the failure of the inservice testing procedure to provide appropriate requirements for performance in applicable plant conditions. <br /><br /> As a result of this event, the requirements of Operations Department Instruction (ODI) 1.35, "Response to Personnel Error Events," have been completed by Operations Management to address the personnel error. The procedures for the monthly operating and inservice testing of the HPSI pumps have been revised to include HPSI and charging pump alignment requirements. Additionally, similar changes will be made to the ECCS flow verification surveillance procedure prior to its use.
3361997005 | Millstone 2 | 02/04/1997 | 03/06/1997 | 9703140102 | <strong>Inservice Test Instrumentation does not meet ANSI/ASME Chapter XI Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1997, with the plant defueled, a self-assessment of instrumentation used in support of safety related pump inservice testing identified three deficiencies where instrument calibration requirements imposed by Section XI of the Code of the American Society of Mechanical Engineers (ASME), 'Rules for Inservice Inspection of Nuclear Power Plant Components' were not met. Two deficiencies related to instruments being used outside their allowable calibration range. One deficiency related to instruments not being included in the facility calibration program. Technical Specification 4.0.5 requires inservice testing of safety related components to be performed in accordance with Section XI of the ASME Code. Therefore, this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B). <br /><br /> The cause of this event was an inadequate administrative structure for the IST program. There are no requirements to ensure ASME code requirements are met with regard to calibration, identification, and maintenance of quality related installed instruments under the current IST program. As a result, insufficient supervisory attention was applied to assure all ASME requirements were met. <br /><br /> Corrective action for this event includes the implementation of a procedure to administer and monitor an IST program which complies with the requirements of Section XI of the Code of the ASME, and the evaluation and correction of the identified instrumentation deficiencies.
3361997006 | Millstone 2 | 02/11/1997 | 03/13/1997 | 9703190180 | <strong>Main Steam Line Break Inside Containment Event Could Result in Exceeding Design pressure of Primary Containment During Certain Scenarios</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1997 as the result of a continuing investigation, it was identified that the consequences of a main steam line break (MSLB) inside containment event could result in exceeding the design pressure of the primary containment under certain postulated scenarios. Two scenarios have been identified in which auxiliary feedwater (AFW) flow to the steam generators (SG) could occur sooner or at greater flow than previously analyzed. In these cases, the peak containment pressure can potentially exceed the design pressure of the primary containment (54 psig). <br /><br /> The cause of this event was an inadequate evaluation resulting from the omission of the consideration of the hot zero power condition with both AFW pumps in operation and the AFW discharge regulating valves sufficiently open to allow full flow at MSLB initiation. As a result of this event, corrective actions will be implemented to ensure that the plant response to a MSLB event will not result in exceeding the design requirements of the primary containment. These actions will be completed prior to plant restart from the current outage.
3361997007 | Millstone 2 | 03/08/1997 | 04/04/1997 | 9704150038 | <strong>Inadequate Surveillance Procedure for Verifying Operability of Reactor Coolant System Vents</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1997, while reviewing a revision of Surveillance Procedure, "Reactor Head and Pressurizer Vent Solenoid Valve Operability Test," it was discovered that the procedure was not in compliance with Technical Specification Surveillance Requirement 4.4.11.3. The surveillance requires that the Reactor Coolant System (RCS) vent path be determined operable by "Verifying flow through the reactor coolant vent system vent paths during venting during COLD SHUTDOWN or REFUELING." Two RCS Vents are provided, one from the reactor vessel head, and the other from the pressurizer steam space. The current procedure does not adequately verify flow from the RCS. In addition, the test is not performed "during venting" as required by the TS wording. <br /><br /> The cause of this event was failure to properly incorporate Technical Specification surveillance requirements into plant Surveillance Procedures. <br /><br /> The Surveillance Procedure, "Reactor Head and Pressurizer Vent Solenoid Valve Operability Test," will be revised to ensure that this surveillance requirement is fulfilled, before entering Mode 4 from the current outage. Technical Specification surveillance procedures will be reviewed to ensure compliance with Technical Specification surveillance requirements as part of the Millstone Unit No. 2 Operational Readiness Plan. The review will initially focus on Technical Specification surveillance procedures required for Mode 6 and defueled. Surveillance procedures required for subsequent mode changes will be reviewed prior to mode entry.
3361997008 | Millstone 2 | 03/10/1997 | 04/08/1997 | 9704160147 | <strong>Insufficient Testing of RPS Logic Circuitry (Generic Letter 96-01 Review)</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1997 at 1030 hours, the first of two reports which review the facility's compliance with Generic Letter 96-01 for the Reactor Protective System (RPS) was received. This report determined that all of the circuits within the Reactor Protective System (RPS) were not being properly verified during surveillance activities. Three 'K' relays which control the ladder network for the 2 out of 4 logic to trip the reactor and provide status indication (red lamp on the bistable) were not being properly verified. The fourth 'K' relay, which controls an annunciator window, was being properly verified to ensure it drops-out when voltage is removed. At the time of discovery of this event, the reactor was defueled. <br /><br /> The cause of the event was an inadequate program to ensure surveillance procedures fully implement Technical Specification requirements. <br /><br /> To correct the deficiency, the procedures for the bistables will be enhanced to check the red status lamps on the bistables and a review of the facility surveillance procedures will be performed to ensure they comply with the Technical Specification surveillance requirements.
3361997009 | Millstone 2 | 03/25/1997 | 02/01/1999 | 9902100176 | <strong>Insufficient ESFAS Surveillance Testing (Generic Letter 96-01 Review)</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1997, the first three of fourteen reports which review the facility's compliance with Generic Letter (GL) 96-01 for the Engineered Safety Feature Actuation System were received. Subsequent to this, the remaining eleven reports were completed and reviewed and five additional types of deficiencies were identified. At the time of discovery of these conditions, the unit was defueled. <br /><br /> The cause of these conditions was an inadequate program to ensure surveillance procedures fully implement Technical Specification requirements. <br /><br /> To correct this deficiency, operational surveillances (which perform the functional tests required by the facility TS) associated with deficiencies identified under the GL 96-01 review will be revised to ensure that TS functional requirements are satisfied.
3361997010 | Millstone 2 | 01/12/1997 | 05/01/1997 | 9705090026 | <strong>Heavy Dummy Fuel Assembly and Handling Tool Weight Exceeds Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1997, with the plant in Mode 6, it was determined that the combined weight of the Heavy Dummy Fuel Assembly (HDFA) and the handling tool exceeds the 1800 pound limit of Technical Specification (TS) LCO 3.9.7. The TS LCO states, 'Loads in excess of 1800 pounds, with the exception of the Consolidated Fuel Storage Box, shall be prohibited from travel over irradiated fuel assemblies in the storage pool.' The HDFA has previously been moved over stored irradiated fuel assemblies in the storage pool. The weight of the HDFA is 1745 pounds and the handling tool weighs 270 pounds, for a total of 2015 pounds. Previously, the handling tool had not been considered to be part of the load. The HDFA is stored in the Spent Fuel Pool (SFP) and is used to perform load tests of the SFP platform crane, refueling machine and new fuel elevator. <br /><br /> The cause of this condition was that the weight of the handling tool was never considered to be part of the load. The HDFA weight alone is less than the 1800 pound limit, so the requirements of the TS were considered satisfied. <br /><br /> As a temporary measure, appropriate procedures have been revised to assure the HDFA is prohibited from travel over irradiated fuel assemblies in the SFP. <br /><br /> A TS change request has been initiated to resolve this issue.
3361997011 | Millstone 2 | 04/02/1997 | 05/02/1997 | 9705080299 | <strong>Improperly Adjusted Dual Function Valves</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1997 a report was made to the Nuclear Regulatory Commission (NRC) which documented an event where the closing force for multiple dual function valves [ISV] had been improperly set, resulting in the valves being incapable of closing to a leaktight condition against normal operating system pressure (NOSP). Eleven of the 23 valves tested were not capable of providing an adequate closing force. This deficiency could result in the potential for a release of radioactive materials to the Auxiliary Building greater than analyzed in the facility Final Safety Analysis Report (FSAR). <br /><br /> The cause of this event was an insufficient program to ensure that facility procedures clearly addressed all related design basis functions. <br /><br /> To correct these deficiencies, the affected valves will be adjusted to ensure they properly close against containment design pressure and NOSP, and the appropriate procedures shall be revised to ensure that proper valve control parameters are specified and verified after any maintenance activities are performed that could affect dual function valve closing forces.
3361997012 | Millstone 2 | 04/10/1997 | 05/09/1997 | 9705190057 | <strong>Inadequate Diesel Generator Start Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1997, while researching a plant modification, it was discovered that the Emergency Diesel Generator (EDG) operability surveillance tests, which are used to satisfy Surveillance Requirement 4.8.1.1.2.a.2, & 4.8.1.1.2.c.8.c, inappropriately used the "Diesel Gen Ready to Load" annunciators as the acceptance criteria to verify >/= 90% speed. The annunciator is designed to turn on when the diesel generator is at both >/= 97% of Rated Voltage and >/= 90% of Rated Speed. The speed signal is provided by either of two switches which are wired in parallel. One switch, the Speed Switch Transmitter (SST) closes its contact when Diesel Engine Speed is >/=810 rpm, or >/= 90% of rated speed. The second switch, the Engine Lube Oil Pressure Switch is set to close its contact at >/= 13 psi. This pressure may be reached prior to 810 rpm resulting in the "Diesel Gen Ready To Load" annunciator being turned on before the engine is at 90% of rated speed. This test method would be a non-conservative condition. <br /><br /> The cause of this condition is personnel were unaware that the design of the circuitry for the Diesel Gen Ready To Load annunciator did not adequately represent engine speed. <br /><br /> To correct this deficiency, Surveillance procedures have been revised to verify engine speed. In the response to NOV 336/96-08-07 (NNECO Commitment No. B16076-2), Millstone Unit No. 2 committed to perform a review of Technical Specification surveillance procedures to ensure compliance with Technical Specification surveillance requirements as part of the Operational Readiness Plan.
3361997013 | Millstone 2 | 04/11/1997 | 05/09/1997 | 9705190038 | <strong>Surveillance Procedure Bypasses Wrong Radiation Monitor Annunciator</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1997, during the performance of the Containment Gaseous Radiation Monitor calibration, an error was identified in the calibration procedure which rendered the annunciator for the operating Stack Gaseous Radiation Monitor INOPERABLE. The Containment Gaseous Radiation Monitor calibration procedure included a step to install an electrical jumper across the annunciator's input cable. The intent of this jumper was to eliminate nuisance annunciator alarms during the performance of the calibration, however, the jumper disabled the alarm for the wrong instrument. Instead of disabling the alarm for the Containment Gaseous Radiation Monitor (R-8123B), the jumper disabled the alarm for the Stack Gaseous Radiation Monitor (R-8132B). Verification of this alarm's operability is required by Tech. Spec. Table 4.3-13, Item 1a, Notation 2. This activity was not completed because the alarm was disabled. <br /><br /> The cause of this condition was inattention to detail in the procedure validation and verification. <br /><br /> Upon identification of this condition, a correction to the Containment Radiation Monitors Calibration Procedure was approved. Corrective actions also included a review of other calibration/functional test procedures for similar problems.
3361997014 | Millstone 2 | 04/15/1997 | 03/02/1998 | 9803130351 | <strong>Insufficient RBCCW Flow to HPSI Seal Coolers</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1997 a report was made to the Nuclear Regulatory Commission in accordance with the requirements of 10 CFR 50.72(b)(2)(iii). This report documented that Reactor Building Closed Cooling Water (RBCCW) flow to the High Pressure Safety Injection (HPSI) pump sea] coolers for all three HPSI Pumps may not be adequate to ensure reliable operation of each pump shaft seal. Failure of a seal could result in contamination of HPSI pump bearing oil and eventual pump failure. An engineering evaluation has been conducted that determined 14.2 gpm to the HPSI pump bearing and seals coolers is the minimum required flow during peak RBCCW temperature conditions after an accident. <br /><br /> The RBCCW piping was adequately sized to provide HPSI pump cooling. <br /><br /> The RBCCW Design Basis Flow Distribution calculation has been issued to revise the design flow to the HPSI pump bearing and seal coolers to 15 gpm.
3361997015 | Millstone 2 | 04/15/1997 | 02/10/1999 | 9902230157 | <strong>Performance Deficiency of Containment Air Recirculation Coolers During Design Basis Accidents (Response to Generic Letter 96-06)</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1997, it was determined that the potential existed for waterhammer and two-phase flow to occur in the Containment Air Recirculation (CAR) Cooler piping and therefore, could cause the piping to fail such that the CAR Coolers may not be able to perform their safety function during accident conditions. In addition, it was also determined that certain containment penetrations were susceptible to thermally induced overpressurization. On September 30, 1996, the Nuclear Regulatory Commission informed licensees in Generic Letter (GL) 96-06 that the potential existed for the containment air cooler water systems to be susceptible to either waterhammer or two-phase flow conditions during postulated accident conditions. GL 96-06 requested that licensees evaluate this condition and additionally determine if piping systems that penetrate containment are susceptible to thermally induced overpressurization when isolated. On January 28, 1997, Northeast Nuclear Energy Company (NNECO) responded to the requested actions identified in Generic Letter 96-06 and stated that any issues discovered would be reported in accordance with the provisions of 10 CFR 50.73. It was determined that the Reactor Building Closed Cooling Water System (RBCCW) and certain containment penetrations were susceptible to the conditions identified in GL 96-06. <br /><br /> The cause of this condition was inadequate consideration of potential failure modes during the system initial design and design basis verification. <br /><br /> Plant design changes and procedure revisions have been implemented to ensure that stresses in piping and supports are within acceptable limits if a postulated water hammer event were to occur.
3361997016 | Millstone 2 | 04/15/1997 | 05/15/1997 | 9705220174 | <strong>Technical Specification 4.0.4. Incorrectly Applied To Surveillance Requirements For The TDAFW Pump</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1997, a review of Technical Specification issues discovered that an exception to the provisions of Technical Specification 4.0.4 had been incorrectly applied to Technical Specification Surveillance Requirements (SRs). The current surveillance procedure for testing the Turbine Driven Auxiliary Feedwater (TDAFW) Pump prior to entering Mode 3 did not run the pump for 15 minutes or guarantee that it was started from the Control Room (CR) as required by Technical Specifications SRs 4.7.1.2.a.3 and 4.7.1.2.a.1. It was previously believed that the 15 minute run and start from CR requirements in the Technical Specifications were being met when the pump was run after secondary plant pressure exceeded 800 psig, and that an exception to the provisions of Technical Specification 4.0.4 for performing the run at pressure greater than 800 psig were applicable to the 15 minute run from the CR. <br /><br /> The cause of this event was failure to properly incorporate Technical Specification surveillance requirements into plant surveillance procedures. <br /><br /> The surveillance procedure for the Turbine Driven Auxiliary Feedwater (TDAFW) will be revised prior to entry into Mode 4 from the current outage to ensure that the required 15 minute run of the TDAFW Pump is started from the CR and is performed prior to unit entry into Mode 3. <br /><br /> Technical Specification surveillance procedures will continue to be reviewed to ensure compliance with Technical Specifications surveillance requirements as part of Millstone Unit 2 Operational Readiness Plan (Reference NOV 336/96-08-07, NNECO Commitment No. B16076-2).
3361997017 | Millstone 2 | 04/17/1997 | 05/16/1997 | 9705230015 | <strong>Bypassed Refueling Machine Overload Cut-off</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1997, an evaluation was completed which concluded that overload protection is not provided for approximately nine inches of vertical travel on the refueling machine hoist as it transitions from the "fuel only" region to the "fuel plus hoist box" region. Technical Specification LCO 3.9.6 requires overload protection when the crane is operable. <br /><br /> The cause of this event was a failure to incorporate refueling machine design considerations (overload cut-off bypass function) during development of the original Technical Specification criteria. <br /><br /> An evaluation will be performed to determine if a design modification should be performed for the Refueling Machine hoist overload protection circuit or if a Technical Specification change should be initiated.
3361997018 | Millstone 2 | 04/21/1997 | 05/21/1997 | 9705280415 | <strong>Instrumentation Loop Components Do Not Meet Regulatory Guide 1.97 Category 1 Recommendations</strong><br /><i>Abstract:&nbsp;</i>On November 6, 1996, while performing a review of the plant compliance with the recommendations of Regulatory Guide (RG) 1.97, Rev. 2, it was discovered that discrepancies existed between current plant commitments and the actual installation for certain Type A, Type B, and Type D instrumentation. These instruments, although reported to the NRC as Category 1, do not meet the Category 1 requirements. Northeast Nuclear Energy Company had stated that these instruments were in compliance with RG 1.97, Rev. 2 recommendations. This condition was first identified on November 6, 1996, the evaluation to determine the details and extent of the condition was completed on April 21, 1997, and a prompt report of the condition was made on that date. At the time of discovery the plant was defueled. <br /><br /> The cause of this condition is the ineffective implementation of program controls used to comply with RG 1.97. <br /><br /> The following actions will be taken to correct this condition: Complete the RG 1.97 Rev. 2 compliance review including NNECO commitments and resubmit the results to the NRC before entering MODE 4 from the current outage.
3361997019 | Millstone 2 | 04/22/1997 | 05/22/1997 | 9705290032 | <strong>Automatic Test Initiator Sends Repeated Trip Signals to the RSST Feeder Breaker Timing Circuit</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1997, a review of a Reserve Station Service Transformer (RSST) Load Shed Time delay retest revealed that the load shed time delay would not meet a six to ten second window to comply with Technical Specification requirement Table 3.3-4, item 8b. <br /><br /> The cause of this condition is an unexpected interaction between unrelated signals in the upgraded RSST Load Shed Timer and the Automatic Testing Insertor circuitry. <br /><br /> Noise interaction will be isolated and corrected prior to entering Mode 4 from the current outage.
3361997020 | Millstone 2 | 04/23/1997 | 08/31/1998 | 9809090099 | <strong>Insufficient verification of Boron Injection Flowpaths</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1997 it was discovered that Technical Specification Surveillance Requirement (SR) 4.1.2.1.a was not being performed on the B High Pressure Safety Injection Pump suction and discharge power operated valves. This Technical Specification surveillance requires the valves to be operated to ensure that a viable boron injection flow path is available. Upon further review it was discovered that Technical Specification SR 4.1.2.1.a (applicable in Modes 5 and 6) and 4.1.2.2.c (applicable in Modes 1 through 4) were also not being performed on any of the power operated valves on the discharge line of the charging pumps. Re-analysis of the Small Break Loss Of Coolant Accident assumed charging flow, previously it did not. As a result, two of the valves in the charging pump discharge are no longer testable during Modes 1 through 4. <br /><br /> The cause of this event was failure to properly incorporate Technical Specification surveillance requirements into plant surveillance procedures. <br /><br /> Corrective actions for this deficiency include revising the appropriate surveillance procedures to ensure that the power operated valves for all credited boration flow paths are properly tested. A review of Technical Specification surveillance procedures (which identified these deficiencies) to ensure compliance with Technical Specifications surveillance requirements has been completed.
3361997021 | Millstone 2 | 04/23/1997 | 05/23/1997 | 9706040146 | <strong>Non-QA lamps installed in the QA Category 1 Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1997, an investigation was completed which indicated that a burned out lamp had failed with an internal short circuit. This investigation was initiated due to an April 8, 1997, event in which a technician noticed a burned out lamp on channel B Low Reactor Coolant Pump (RCP) Speed trip unit and an unusual indicator light configuration on the Reactor Protection System (RPS) BC matrix. The technician was preparing to perform a surveillance test at the time of discovery. When he removed the burned out lamp in the trip unit for the Low RCP Speed trip unit, the other lights returned to normal. <br /><br /> The failed lamp was replaced with a new lamp. After further investigation it was postulated that had this failure occurred during operation, there is a possibility that the BC trip matrix could have been unavailable. The other five trip matrices were not affected and would have caused a trip if required. The investigation found that Non-QA lamps were being used in the RPS, a QA Category 1 system, contrary to system design basis. At the time of discovery the unit was defueled. <br /><br /> The cause of this event was an inadequate scope of review in response to NRC Information Notice 94-68: Safety Related Equipment Failures Caused by Faulted Indicating Lamps. <br /><br /> As corrective action an engineering evaluation of low voltage lamp circuit design in safety related equipment which was not reviewed as part of the Information Notice 94-68 response shall be performed. This evaluation will determine if lamp isolation is adequate or if a fault tolerant design exists. It will also evaluate possible interaction between QA and non-QA systems. This action will be completed before entering MODE 4 from the current outage.
3361997022 | Millstone 2 | 06/02/1997 | 05/19/1998 | 9805280067 | <strong>Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>This LER identifies those issues in which a violation of the unit's Technical Specifications (TS) occurred. A detailed review of the unit's TS is ongoing and is expected to identify additional issues. Each of the following TS violations has been characterized as a deficiency which is historical in nature and in which the safety significance of the deficiency is low. <br /><br /> The cause of these conditions is a failure to achieve compliance to Technical Specification Requirements. <br /><br /> A TS change will be initiated or appropriate Surveillance Procedures will be revised. Technical Specification surveillance procedures will be reviewed to ensure compliance with Technical Specifications surveillance requirements as part of Millstone Unit 2 Operational Readiness Plan (Reference NNECO Commitment No. B16076-2).
3361997023 | Millstone 2 | 06/12/1997 | 11/24/1998 | 9812020062 | <strong>Minimum HPSI Flow Used in FSAR Accident Analysis May Be Non-conservative</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1997, during a review of the High Pressure Safety Injection (HPSI) pump Technical Specifications, it was determined that the actual HPSI System flow delivery to the reactor coolant system (RCS) may be less than the flow assumed in the Final Safety Analysis Report Chapter 14 Loss Of Coolant Accident and Main Steam Line Break accident analyses. <br /><br /> The cause of this condition was the use of non-conservative HPSI system flow assumptions in the original design basis accident analyses and subsequent design verification. <br /><br /> As a result of this condition, the affected accident analyses have been re-evaluated with conservative HPSi delivery rates resulting in the conclusion that the accident acceptance criteria are met.
3361997024 | Millstone 2 | 06/19/1997 | 01/14/1999 | 9901220267 | <strong>Violation of Technical Specification 4.0.5, ASME Section XI Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1997, during a review of the Snubber InService Inspection (ISI) Program, it was determined that repair/replacement plans which were required for snubber replacement and rotation from Quality Assurance spares were not performed during the Second Ten Year Interval. On September 17, 1998, during the preparation of ASME Section XI documentation, it was identified that four (4) pipe spools within the MP2 Service Water System had been placed in service in September 1990 without meeting the proper ASME Section XI code requirements for retests associated with replacement components. On October 2, 1998 during a comprehensive review of the Containment Air Monitoring System licensing bases/design bases, it was identified that the ASME Section XI leakage testing requirements had never been applied to the Hydrogen Monitoring System.<br /><br /> The cause of these conditions was misinterpretation and wrong assumptions with respect to ASME Section XI requirements. <br /><br /> To correct these conditions, the appropriate procedures were revised to require development of repair/replacement plans for snubber replacements, the identified pipe spools have been replaced and the identified Hydrogen Monitoring System valves and piping will be added to the IST/ISI Programs.
3361997025 | Millstone 2 | 08/28/1991 | 07/29/1997 | 9708050073 | <strong>Single Failure Vulnerability of the AFW System via the Condenser Hotwell Make-up Valve</strong><br /><i>Abstract:&nbsp;</i>On August 28, 1991 it was discovered that a single active failure of the hotwell make-up valve (2-CN-241) could result in a diversion of water from the Condensate Storage Tank (CST) to the Condenser Hotwell such that sufficient volume would not be available in the CST for Auxiliary FeedWater (AFW) requirements to cooldown the Reactor Coolant System. <br /><br /> The cause of this condition was a failure to consider single failure scenarios in the original design requirements for condensate make-up to the AFW System. <br /><br /> To correct this deficiency, actions were taken to ensure that the CST was maintained at a level that would ensure sufficient water volume was available even if a single failure of the hotwell make-up valve were to occur. Additionally, the trim package for the hotwell make-up valve was changed such that CST drainage to the condenser hotwell would be lessened. The applicable calculations shall be reviewed to verify CST volume losses caused by the single failure of the hotwell make-up valve and the applicable Emergency Operating Procedures will be revised to specify required operator actions. An evaluation shall be performed to identify if system enhancements are necessary to ensure the CST has adequate water volume to meet postulated accident requirements.
3361997026 | Millstone 2 | 07/29/1997 | 08/28/1997 | 9709030069 | <strong>Invalid ESAS Actuation while shifting from Normal to Reserve Station Transformers</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1997, at approximately 0043 hours, two buses (24A and 24C) were inadvertently de-energized by an invalid Engineered Safeguards Actuation System (ESAS) signal after they were shifted from the Normal Station Service Transformer to the Reserve Station Service Transformer. The invalid ESAS signal was generated because of a load-shed signal which was initiated on July 27, 1997 by a random fuse failure. <br /><br /> The cause of this event was an inadequate review of components left in an indeterminate state. <br /><br /> Corrective actions for this event include providing a briefing to Operations personnel regarding the need to analyze equipment which is planned to be left in an indeterminate state.
3361997027 | Millstone 2 | 08/02/1997 | 09/02/1997 | 9709090059 | <strong>Unplanned Automatic Start of "A" Emergency Diesel Generator while Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1997, at approximately 0800 hours, while troubleshooting a blown fuse for the Engineered Safeguards Actuation System actuation Facility 1 Logic Supply 'A', Instrumentation and Control personnel lifted the Diesel Generator Start Signal lead which resulted in an inadvertent start of the 'A' Emergency Diesel Generator (EDG). The lead which had been lifted was required to be re-landed before the EDG could be shutdown. Operations personnel loaded the EDG and shut it down in accordance with the appropriate operating procedures. <br /><br /> The cause of this event was a failure to provide adequate detailed instructions for the preparation, review and approval of a troubleshooting plan. <br /><br /> As a result of this event, adequate measures will be established to ensure appropriate independent and management review of troubleshooting plans by September 30, 1997.
3361997028 | Millstone 2 | 08/22/1997 | 03/19/1999 | 9903310087 | <strong>Electrical Equipment Qualification Program Deficiencies</strong><br /><i>Abstract:&nbsp;</i>In November 1996 and again in June 1997, Engineering Self Assessments were conducted to examine the Electrical Equipment Qualification (EEQ) program for Millstone Unit No. 2. Both assessments found similar deficiencies in the implementation of the EEQ program requirements. Based on these assessments, a major effort was initiated to review and upgrade the EEQ documentation. Walkdowns were conducted for inspection of the field installation of EEQ components, and confirmation of the postulated accident environments to which they may be exposed. As a result of this EEQ upgrade effort, numerous deficiencies have been identified in both the equipment qualification and the program documentation. These deficiencies are reported in this LER. <br /><br /> The cause of these conditions was inadequate management oversight resulting in the unsatisfactory implementation of the EEQ program. <br /><br /> Corrective actions have been implemented to address the specific EEQ conditions reported. In addition, enhancements to the Design Change Program and the Automated Work Order Process have provided added assurance of the proper maintenance of, and adherence to, EEQ Program requirements. These enhancements have also served to strengthen the interface(s) between EEQ and other engineering programs. This supplement is a complete rewrite.
3361997029 | Millstone 2 | 08/26/1997 | 05/06/1999 | 9905180217 | <strong>Piping Stress Analyses performed in support of IE Bulletin 79-14</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1997, during the review of a design modification for a main steam line located outside containment, it was discovered that the present stress analysis of system piping supports performed during the facility review of Inspection and Enforcement Bulletin 79-14 did not consider all loads required by ANSI 1331.1, 1967 Edition. ANSI B31.7, Class II and III, 1969 Edition, and ANSI B31.1, 1967 Edition, are the facility codes of record which are used for pipe stress analysis and determining piping support loads for piping outside containment. Further investigation has determined that the same condition also applied to the stress analysis for the main feedwater lines outside containment. <br /><br /> The cause of this condition was the inappropriate application of a section of ASME Section III to ANSI B31.1 analyses in the calculation of the pipe support loads. <br /><br /> As a result of this deficiency, a review of the piping stress analyses performed in support of the IE Bulletin 79-14 review was undertaken to identify those calculations which referenced subsection NF of ASME Section III. The identified analyses have been revised to comply with the facility design basis.
3361997030 | Millstone 2 | 08/30/1997 | 09/29/1997 | 9710070027 | <strong>Emergency Diesel Generator Piping Analysis Questioned Due to Partial Penetration Welds</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1997, during the investigation of a piping leak, it was determined that the "A" and "B" Emergency Diesel Generators (EDG) skid mounted piping and tubing may not maintain structural integrity during EDG operation. Portions of these systems had partial penetration welds. Evaluation of the welds show that piping with partial penetration welds, when exposed to excessive vibration, are susceptible to failure by vibration induced fatigue. The "B" EDG was not operating at the time of the event and was conservatively declared inoperable. <br /><br /> The cause of this condition was non-conforming partial penetration tubing welds. The original vendor supplied EDG skid mounted piping and tubing did not fully comply with the design drawing requirement for full penetration welds. <br /><br /> As a result of this condition, large bore piping and tubing with partial penetration welds, on both Emergency Diesel Generators, will be reworked and restored to code acceptable full penetration welds.
3361997031 | Millstone 2 | 09/18/1997 | 10/17/1997 | 9710280051 | <strong>Potential Effects on Safety-Related Equipment located outside Containment due to High Energy Line Breaks</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1997, during our ongoing evaluation of the facility High Energy Line Break program for lines outside containment, it was discovered that certain safety-related components and structures required for safe shutdown of the plant such as piping, block walls, and switchgear are not properly protected from the dynamic and environmental effects of pipe ruptures in high energy lines. <br /><br /> The cause of this condition is an inadequate review by the original facility analysis for postulated High Energy Line Breaks. <br /><br /> As a result of this condition, the present pipe rupture design configurations associated with postulated high energy line breaks will be evaluated against the facility design criteria and corrective action required for facility startup, including compensatory measures, will be identified and performed prior to entering Mode 4 from the current outage.
3361997032 | Millstone 2 | 09/22/1997 | 10/18/1997 | 9710280065 | <strong>Main Steam Safety Valves Exceed Allowable Set Point</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1997 during performance of Main Steam safety/relief valve bench testing by the offsite vendor, it was identified that two of the sixteen valves failed to open within their Technical Specification allowable lift set pressures. <br /><br /> The root cause of the setpoint drift is unknown. It is conservatively assumed that the setpoint drift occurred on these valves sometime during plant operation. <br /><br /> As corrective action the valves will be rebuilt, set to their required set pressure (+/- 1 percent) and satisfactorily tested prior to reinstallation. This action will be completed before entering Mode 4 from the current outage.
3361997033 | Millstone 2 | 07/27/1997 | 03/03/1998 | 9803090399 | <strong>Design Deficiencies Identified with ESAS Actuation Cabinet Power Supplies and Associated Fuses</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1997 at 06:43 hours, a 6 Amp fuse (F3) opened in Engineered Safeguards Actuation System (ESAS) Facility Z1 Actuation Cabinet. At the time the fuse opened testing or maintenance activities were not being performed in the ESAS cabinets. This open (blown) fuse was installed on the output of +15 Volt Logic Power Supply "A", which powers the actuation modules associated with the Safety Injection Actuation Signal and Undervoltage Signal. There is a similar power supply and fuse arrangement in the ESAS Facility Z2 Actuation Cabinet. The initial evaluation of this condition concluded that the fuse may open during a design basis event. Subsequent evaluation of this condition identified that the fuse is adequately sized.<br /><br /> As a result of this condition, an Event Review Team was established to investigate the fuse failure. Appropriate corrective actions were completed, including testing to establish the actual power supply and fuse load currents.
3361997034 | Millstone 2 | 10/29/1997 | 11/26/1997 | 9712010204 | <strong>Containment Sump Isolation Valves are Susceptible to Pressure Locking</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1997 it was discovered during a review of a modification to address pressure locking phenomenon for the Containment Sump Isolation Valves (CSIV) that these valves could not only be susceptible to thermally induced pressure locking, but also pressure locking due to variations in containment pressure. The review found that the valve bonnet could be pressurized as high as 54 psig peak containment pressure and at Sump Recirculation Actuation Signal (SRAS), when the valves need to open, could approach 0 psig, resulting in a higher differential pressure across the CSIV disc than previously assumed. Preliminary calculations indicate the CSIV motor operators may not be adequately sized to open the valves under this condition. <br /><br /> The cause of the event was a failure to identify the full range of conditions that could exist, when the valves must operate, for pressure locking and thermal binding evaluations. <br /><br /> As corrective actions, a review has been conducted of other valves that may be susceptible to similar conditions and could cause pressure locking. No similar situations have been found. The MOV System and Design Basis Review Program Instruction has been revised to include formal reviews by Nuclear Engineering that require identification of design and licensing basis MOV Program scenarios. The Containment Sump Isolation Valves will be modified to preclude pressure locking for postulated conditions. The Pressure Locking and Thermal Binding Evaluation Program Instruction will be revised and implemented to include a formal review of the Pressure Locking and Thermal Binding Evaluations by Nuclear Engineering to ensure the full range of system conditions is considered.
3361997035 | Millstone 2 | 11/11/1997 | 12/11/1997 | 9712220082 | <strong>Shutdown Cooling System Isolation Valve Does Not Comply With Appendix R Requirements (Generic Letter 86-10)</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1997, while revalidating compliance with 10 CFR 50 Appendix R requirements, it was discovered that the interface between the Reactor Coolant System (RCS) and the Shutdown Cooling suction line was not in conformance with Generic Letter 86-10. A fire induced three-phase hot short on the power cable for the Shutdown Cooling suction header RCS isolation valve could cause this valve to spuriously open and result in the inability to maintain RCS boundary isolation. <br /><br /> The cause of this condition was inattention to detail and inadequate interdiscipline review during the 10 CFR 50 Appendix R Compliance analysis. <br /><br /> The power cable downstream of the power disconnect switch for the Shutdown Cooling suction header Reactor Coolant System isolation valve will be rerouted so that it is not subject to hot shorts from energized three-phase power cables in the event of a fire. This modification will be implemented prior to entering Mode 4 from the current outage.
3361997036 | Millstone 2 | 11/17/1997 | 12/17/1997 | 9712240153 | <strong>Technical Specification Containment Sump Trisodium Phosphate Volume Insufficient</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1997, during extended fuel cycle calculation review, it was identified that the amount of trisodium phosphate (TSP) specified in Technical Specification Surveillance Requirement 4.5.2.c.3 is not sufficient to meet the licensing basis requirement to increase the containment sump fluid pH to >/= 7.0. The original calculation had used minimum water volumes and boric acid concentrations. A revised calculation performed in 1977 assumed the maximum water volumes and boron concentrations, however, a simple ratio had been used to scale up the TSP required to neutralize higher concentrations of boric acid. <br /><br /> The cause of the condition was an incorrect assumption regarding the amount of TSP required to neutralize a known boric acid concentration. <br /><br /> A Technical Specification Change request to increase the minimum required Trisodium Phosphate volume to the proper value will be initiated. The resulting amendment will be implemented before entry into Mode 3 from the current outage.
3361997037 | Millstone 2 | 11/26/1997 | 11/04/1998 | 9811180182 | <strong>Service Water Piping Liner Material Peeled Off and Lodged in the Strainer for the Emergency Diesel Generator Heat Exchangers Causing Reduced Flow to the Heat Exchangers</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1997, at 0830 hours, while performing a routine strainer maintenance procedure, a piece of debris was discovered in one side of the duplex inlet strainer for the service water system cooling supply to the "B" emergency diesel generator heat exchangers. The debris consisted of one approximately 6 inch by 12 inch piece of plasticized Polyvinyl Chloride (PVC) piping liner material, and was found in the strainer basket that had been in service. The strainer provides for the removal of debris from the inlet piping to the diesel engine heat exchangers. The liner material is a PVC coating used in various portions of the service water system for corrosion protection of carbon steel piping internals from exposure to seawater. <br /><br /> The subsequent root cause investigation and piping inspection determined that the PVC liner failure was caused by a compression rupture of the PVC at the internal shoulder of a piping spool (SK4031) flange located off the "B" Service Water header. Two additional factors which contributed to the extent of condition of the PVC liner failure are a lack of an effective quality control during the original application process and use of an inferior primer. <br /><br /> Corrective actions taken included inspection of 100 percent of the pipe spools with safety related PVC lining from both Service Water system headers. Piping liner repairs (with epoxy materials) have been performed using an approved procedure to assure a quality application process, based upon inspection results, to correct defects identified in the PVC liner on both trains and the cross-connect piping.
3381997001 | North Anna 1, North Anna 2 | 03/12/1997 | 04/08/1997 | 9704150266 | <strong>Auxiliary Service Water Pump Bolts Exceed Design Basis Allowable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1997, with Units 1 & 2 in Mode 1, 100 percent power, it was determined that the Auxiliary Service Water (ASW) pump bolts connecting the top column flange to pedestal base plate exceeded the design basis allowables and the short term operability criteria established in NRC Generic Letter 91-18 during a Design Basis Earthquake. Technical Specification (TS) 3.7.4.1.d allows the 72 hour Action of TS 3.7.4.1.c to be extended to 168 hours provided 3 of 4 Service Water (SW) pumps and 2 of 2 ASW pumps have been operable since initial entry into the action and for the duration of same. The Action of TS 3.7.4.1.d had been entered in the past with the ASW pumps inoperable due to inadequate bolting. As such, this event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by TS. <br /><br /> The cause of the event is attributed to personnel error during initial design and installation. <br /><br /> This event posed no significant safety implications since the ASW pumps are not taken credit for in the design basis accident as stipulated in the TS Bases. Therefore, the health and safety of the public were not affected at any time during this event.
3381997002 | North Anna 1 | 05/15/1997 | 06/12/1997 | 9706170193 | <strong>Safety Valve Setpoints Out of Tolerance due to Setpoint Variance</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1997, with Unit 1 in Mode 6, Refueling, the "as found" set pressure for one Main Steam Safety Valve (MSSV) was found to be outside the setpoint tolerance allowed by the Technical Specifications (TS). During subsequent testing the "as found" set pressures for three additional MSSVs were found to be outside the setpoint tolerance allowed by the TS. The remaining eleven MSSVs tested satisfactorily. Additionally, on May 18, 1997, the "as found" set pressure for one Pressurizer Safety Valve (PSV) was found to be outside the setpoint tolerance allowed by the TS. Although the two remaining PSVs tested satisfactorily, the average of the three PSVS was also found to be outside the TS limit. These events are reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by TS.<br /><br /> The cause of the event is attributed to setpoint variance from what appears to be aging where valves remain in service for extended periods. This event posed no significant safety implications because the safety valves would have performed their safety function in the event of an overpressure condition. Therefore, the health and safety of the public were not affected at any time during this event.
3381997003 | North Anna 1 | 05/16/1997 | 06/05/1997 | 9706120213 | <strong>Positive Reactivity Addition During Refueling Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 17, 1997, with Unit 1 in Mode 6, Refueling, it was determined that a positive reactivity addition occurred on May 16, 1997, while one of two source range neutron flux monitors was removed from service. The reactor cavity was being filled with water from the refueling water storage tank which had a lower boron concentration than that of the reactor coolant system. As such, a positive reactivity addition was being performed. The Technical Specifications (TS) require two source range neutron flux monitors to be operating during positive reactivity additions. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by TS. <br /><br /> The cause of the event is attributed to personnel error. The control room crew did not consider the cavity fill evolution a positive reactivity addition because the refueling water storage tank boron concentration was above the TS limit of 2300 ppm. <br /><br /> This event posed no significant safety implications because the minimum boron concentration of 2300 ppm for the required shutdown margin in Mode 6 was maintained. The shutdown margin was verified to have been satisfied throughout the positive reactivity addition. Therefore, the health and safety of the public were not affected at any time during this event.
3381997004 | North Anna 1 | 05/24/1997 | 06/17/1997 | 9706250045 | <strong>Hi-Hi Alarm Setpoint for 1-RM-RMS-160 Found Out of Tolerance Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1997 with Unit 1 defueled, it was identified that the as-found Hi-Hi alarm setpoint for the containment gaseous radiation monitor (1-RM-RMS-160) had been incorrectly set above the allowable limits of Technical Specifications (TS) 3.3.3.1 during defueling operations. TS requires the containment gaseous radiation monitoring instrumentation channel Hi-Hi setpoint to be less than or equal to 3.6E+3 cpm for Mode 6. The as-found Hi-Hi setpoint was 2.5E+4 cpm. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by TS. <br /><br /> The cause of this event is attributed to a personnel error whereby the 2.7E+3 cpm Hi-Hi setpoint stated on the Process Radiation Monitor Setpoint Record sheet was misread as 27E+3 cpm. <br /><br /> This event did not pose any safety implications. The containment Particulate Radiation Monitor and the Manipulator Radiation Monitor remained OPERABLE during this event. Abnormal Procedure, 0-AP-30, "Fuel Failure During Handling" would also initiate a manual isolation of containment ventilation if a Hi radiation alarm is received from these containment radiation monitors. Therefore, the health and safety of the public were not affected at any time during this event.
3381997005 | North Anna 1 | 05/19/1997 | 06/10/1997 | 9706180407 | <strong>Missed Surveillance On First In-service Inspection Of Steam Generator Tubes</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1997, with Unit 1 in Mode 6, Refueling, it was determined that the eddy-current testing results performed during the current refueling outage did not match signatures reported during preservice baseline testing. This discrepancy became apparent when a review of preservice inspection data was performed during the inspection of "A" steam generator (SG). Additional reviews identified two tubes in "A" SG that were not preservice inspected. Technical Specification 3.4.5 allows a reduced inspection scope if each tube in each SG is preservice inspected. Since the failure to perform a preservice inspection of these two tubes was not previously identified, only two SG's instead of three were inspected during the first refueling outage, as required by TS Table 4.4-1. This event is reportable pursuant to 10CFR 50.73(a)(2)(i)(B). <br /><br /> The cause of this event is attributed to personnel error during preservice inspections which resulted in the failure to perform a preservice inspection of two tubes in the "A" SG. <br /><br /> This event posed no significant safety implications, since the inspections that were performed during the current outage did not identify any concerns relative to tube degradation. Therefore, the health and safety of the public were not affected at any time during this event.
3381997006 | North Anna 1 | 07/31/1997 | 08/20/1997 | 9709040117 | <strong>Entered Technical Specification 3.0.3 Due To Inoperable Control Rod Indicators</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1997, with Unit 1 at 100 percent power, Mode 1, a condition outside Technical Specification (TS) occurred when two individual rod control indicators (IRPI) in the same group were inoperable. With the IRPI for control rod M4 in the test position for calibration (i.e., inoperable) a second IRPI for control rod M12 failed low. Since this condition is outside the requirements of TS 3.1.3.2.a the action of TS 3.0.3 was entered. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by TS. <br /><br /> The cause of this event was due to a failure of one individual rod position indicator while another was out of service for testing. Cause of the IRPI for control rod Ml 2 to fail low is attributed to a failed operational amplifier in the signal conditioning module. <br /><br /> This event posed no significant safety implications since the control rods were able to perform their safety function and the ability to move control rods was never compromised. Actual control rod failure had not occurred and the reactor protection system parameters remained stable. Therefore, the health and safety of the public were not affected at any time during this event.
3381997007 | North Anna 1, North Anna 2 | 08/18/1997 | 09/16/1997 | 9709230165 | <strong>NIS High Flux Trip Setpoint Errors Due To Calorimetric Uncertainties At Low Power</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1997, with Units 1 and 2 at 100 percent power, Mode 1, it was determined that the current calorimetric process does not account for the potential effect of increasing measurement uncertainty at power levels below 85 percent rated thermal power (RTP). This decalibration adds process errors which could cause the 9 percent RTP allowance between the trip setpoint of 109 percent and the safety analysis setpoint of 118 percent to be exceeded. This condition is reportable pursuant to 10 CFR 50.73 (a)(2)(vii), where a single cause or condition caused independent channels to become inoperable in a single system designed to shutdown the reactor and maintain it in a safe condition. <br /><br /> The NIS setpoint adjustment errors are due to the inherent inaccuracies associated with the calorimetric heat balance at low power levels.<br /><br /> This condition posed no significant safety implications since the safety analysis setpoint would not have been exceeded. Therefore, the health and safety of the public were not affected at any time during this condition.
3381997008 | North Anna 1 | 10/27/1997 | 11/04/1997 | 9711100097 | <strong>Both Emergency Diesel Generators Inoperable During Testing</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1997, at 1641 hours with Unit 1 at 100 percent power, Mode 1, the 1J emergency diesel generator (EDG) was declared inoperable to perform surveillance testing. At the time, the 1H EDG was inoperable due to an engine cooling fan failure. With both EDGs inoperable the two hour action statement of Technical Specification (TS) 3.8.1.1e was entered. This condition is reportable pursuant to 10 CFR 50.73 (a)(2)(v)(A) & (D), where a condition alone could have prevented the fulfillment of the safety function of systems that are needed to shut down the reactor and maintain it in a safe condition or mitigate the consequences of an accident. <br /><br /> The two EDGs were inoperable as a result of a TS surveillance requirement to demonstrate operability of the remaining EDG when one is inoperable. <br /><br /> This condition posed no significant safety implications since A.C. offsite power sources were verified operable and capable of supplying power to the station. In addition, the station blackout diesel was operable and 1J EDG could have been quickly returned to service. Therefore, the health and safety of the public were not affected at any time during this condition.
3381997009 | North Anna 1, North Anna 2 | 11/18/1997 | 12/12/1997 | 9712230352 | <strong>Incomplete Surveillance On Solid State Protection Circuits Due To Procedure Error</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1997, with Unit 1 at 100 percent power, Mode 1, and Unit 2 at 99.3 percent, Mode 1, Technical Specification (TS) 4.0.3 was entered at 1707 hours. During a review of an Operating Experience report it was noted that the logic testing for the feedwater isolation from P-14, Steam Generator Hi Hi level, and the P-10 block of the Source Range Trip were not properly tested for both trains of the Solid State Protection System (SSPS). Both trains of SSPS on both units were satisfactorily tested within 24 hours and the TS action was cleared. This incomplete surveillance is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B), for a condition prohibited by the Technical Specifications. <br /><br /> The cause of the incomplete surveillance is attributed to inadequate test design supplied by the vendor. <br /><br /> This condition posed no significant safety implications since the circuits were able to perform their design function. Therefore, the health and safety of the public were not affected at any time during this condition.
3391997001 | North Anna 2 | 03/14/1997 | 04/10/1997 | 9704150158 | <strong>Reactor Vessel Level Dynamic Range Indication Inoperable on "A" Train Due to Procedural Error</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1997, with Unit 2 in Mode 1, 100 percent power, the Reactor Vessel Level Indication System (RVLIS) 'A' train was declared inoperable and the 7 day action of Technical Specification 3.3.3.6 was entered. Vendor specifications require the RVLIS dynamic range indications to be to renormalize at the beginning of each fuel cycle. The vendor specified an operability limit of +/- 4 percent for the RVLIS dynamic range indication at zero power with all reactor coolant pumps running. If the indication of +/- 4 percent is exceeded the RVLIS train is considered inoperable. The Unit 2 RVLIS 'A' Train indication was at plus 5 percent for the dynamic range. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by TS because the RVLIS dynamic range indication on one train was outside its allowed tolerance. <br /><br /> The cause is attributed to inadequate translation of vendor requirements into station procedures. <br /><br /> This event posed no significant safety implications since a one percent deviation in the RVLIS dynamic range indications is not expected to impact the effectiveness of the Inadequate Core Cooling Monitoring System. Therefore, the health and safety of the public were not affected at any time during this event
3411997001 | Fermi 2 | 02/06/1997 | 03/10/1997 | 9703190049 | <strong>Error in Mass Flow Conversion Algorithm in the Heat Balance Methodology for Calculating Core Thermal Power</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1997 during a review of the Reactor Water Cleanup (RWCU) system inputs to the reactor heat balance calculation, an error was discovered in the mass flow conversion algorithm used by the Process Computer for RWCU flow. It was determined that this resulted in a nonconservative error in the heat balance calculation. Due to this error, it is possible that Fermi 2 exceeded its licensed power limit of 3292 megawatts thermal (MWt) on one or more occasions during Cycle 1 and 3293 MWt on one or more occasions during Cycles 2 and 3 by approximately 0.6 MWt. The current licensed power limit of 3430 MWt has not been exceeded as a result of this error because of administrative limits already in place. <br /><br /> Based on the low order of magnitude of the error and conservatism inherent in power levels used for safety analyses, this condition did not result in any adverse impact on the health and safety of the public. <br /><br /> The mass flow conversion algorithm will be corrected and the procedure for the manual heat balance calculation and the software specification will be revised prior to startup from the present outage to include the appropriate algorithm. The software and instrumentation interface in the Process Computer will be evaluated for similar problems.
3411997002 | Fermi 2 | 02/16/1997 | 03/18/1997 | 9703240148 | <strong>Failure of the High Pressure Coolant Injection System Pump Discharge Valve to Open</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1997, while the plant was in a forced outage, the High Pressure Coolant Injection (HPCI) system pump discharge valve (E4150-F006) failed to open when the open push-button was depressed as part of a routine surveillance test. The plant was shutdown at the time and HPCI was not required to be operable. An investigation of the failure was initiated. <br /><br /> The Limitorque valve motor was inspected. The pinion gear on the motor shaft was found to be loose. It had slipped axially along the shaft causing it to disengage from the drive gear. The setscrew was not holding the pinion gear to the shaft although the setscrew was properly secured with lockwire. The cause of the event was determined to be a failure of the pinion gear setscrew. <br /><br /> The motor shaft was spot drilled to provide a seat for the setscrew and a new setscrew was installed in the E4150-F006 valve. The work history for all other Limitorque motor operated valves (MOVs) was reviewed. Other Limitorque MOVs, potentially susceptible to this type failure were identified and a plan for inspection and replacement of the setscrews has been developed.
3411997003 | Fermi 2 | 03/03/1997 | 05/08/1997 | 9705150051 | <strong>Emergency Equipment Cooling Water System Containment Isolation Function Outside Design Basis And Subsequent Identification Of Several New Bypass Leakage Paths</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1997, it was determined that the Emergency Equipment Cooling Water System (EECWS) containment isolation function was outside the design basis. The EECWS is normally in standby and portions of the system piping distribute cooling water supplied by the Reactor Building Closed Cooling Water System (RBCCWS). The RBCCWS is isolated from the EECWS upon initiation of the EECWS. The Updated Final Safety Analysis Report (UFSAR) Containment Isolation System (CIS) design basis identifies that no single failure will result in loss of the containment function. It was determined that a single failure of an electrical division could result in the loss of the EECWS containment isolation function. The EECWS containment penetrations have been modified to provide diverse power such that a single failure will not result in the loss of the containment isolation function. modification, a total of twelve previously unrecognized bypass leakage paths were identified in the EECWS, Post Accident Sampling System, and Compressed Air System. When leak rate data for these new bypass leakage paths was added to previous bypass leakage rate totals, the UFSAR bypass leakage limit of 4% La was exceeded on two occasions. Alarm Response Procedures (ARPs) have been revised to provide guidance to Operators to manually isolate the EECWS return header primary containment penetrations in the event that certain accident conditions exist. A UFSAR revision has been approved to properly identify the twelve new bypass leakage paths and these paths have been added to the bypass leakage program.
3411997004 | Fermi 2 | 03/04/1997 | 08/01/1997 | 9708060197 | <strong>Calibration of Primary Containment Oxygen Monitor in De-inerted environment Challenging Operability of Monitor in Inerted Environment</strong><br /><i>Abstract:&nbsp;</i>Following an engineering evaluation it was determined on March 4, 1997 that if the Primary Containment oxygen monitor is calibrated in the de-inerted containment, it cannot be considered operable in the inerted containment. This is based on a "zero-shift" anomaly which occurs when the containment environment changes from an oxygen to a nitrogen environment. On several occasions in the past the oxygen monitor was calibrated in a de-inerted environment and subsequently operated in an inerted environment. <br /><br /> The preliminary investigation presented questions related to response time of the oxygen sensor. Preliminary laboratory results on two spare oxygen sensors indicated that these sensors do not respond to environmental changes as originally expected. A test of the oxygen monitoring system conducted by the vendor indicates that environmental factors and the housing where the sensor is mounted also affects the rate of response. Either factor appears to be an inherent design feature that has impact on the current calibration process with respect to dwell times of the applied calibration gases that were recommended by the vendor. <br /><br /> Troubleshooting and data-gathering has been performed to verify the preliminary laboratory results regarding sensor response to a change in environment. The oxygen sensor calibration procedures and channel checks have been revised based on the results from the troubleshooting and data-gathering prior to startup from the most recent outage to ensure proper calibration of the oxygen sensor. All commitments made in the original submittal of this LER have been completed.
3411997005 | Fermi 2 | 03/07/1997 | 05/12/1997 | 9705190046 | <strong>Inadequate Design or Consideration of Circuits Involved in Achieving Dedicated Shutdown</strong><br /><i>Abstract:&nbsp;</i>During an engineering review of the Emergency Equipment Cooling Water (EECW) system, it was discovered on March 7, 1997, that the Reactor Building Closed Cooling Water (RBCCW) to EECW return and supply isolation valve interlocks are installed in the EECW makeup tank isolation valve circuit between the Dedicated Shutdown Panel transfer switch and the opening coil. The interlocks are not bypassed when the valve is in local control at the Dedicated Shutdown Panel. There is no assurance that the RBCCW to EECW return and supply isolation valves will close because they are not valves that can be operated from a Dedicated Shutdown Panel and are not protected from fire induced hot shorts. <br /><br /> During a subsequent review of dedicated shutdown procedure circuits being performed as corrective action to the above, it was discovered on April 12, 1997, that smoke/CO sub 2 shutoff dampers in the Division 2 Battery Charger Room may not close, or may re-open during use of the Dedicated Shutdown Procedure. This could hamper access to areas needed to complete the Dedicated Shutdown Procedure. Dedicated Self Contained Breathing Apparatus (SCBA) units have been staged at the dedicated shutdown equipment area in the Radwaste Switchgear Room, and surveillance procedures have been revised to assure the availability of the SCBAs for Dedicated Shutdown Procedure use. <br /><br /> The event was caused by inadequate design or consideration of these circuits. Contributing factors were inadequate cross discipline review and inadequate post modification testing. Currently, process barriers are in place to minimize the chance that this type of event can occur.
3411997006 | Fermi 2 | 03/20/1997 | 07/27/1998 | 9807310285 | <strong>Response Time Testing Not In Conformance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications 4.3.1.3, 4.3.2.3, and 4.3.3.3 require that the Reactor Protection System Response Time for each reactor trip functional unit, the Isolation System Response Time for each isolation trip function, and the Emergency Core Cooling System (ECCS) Response Time for each ECCS trip function, respectively, shall be determined to be within its limit at least once per 18 months. <br /><br /> On March 20, 1997, it was determined that response time testing of Reactor Protection System Actuation Instrumentation and Main Steam Isolation Valve Closure Actuation Instrumentation sensors, and ECCS Actuation Instrumentation loops had not been conducted in accordance with Technical Specification requirements. Changes to response time testing requirements in plant documents had been approved on February 6, 1996, in accordance with 10 CFR 50.5 9, based on the Boiling Water Reactor Owners' Group (BWROG) Licensing Topical Report (LTR) NEDO-32291, "System Analyses for Elimination of Selected Response Time Testing Requirements," as approved by NRC Safety Evaluation Report dated December 24, 1994, and supplemented on May 28, 1995, without recognizing that a change to the Technical Specifications was involved. <br /><br /> There was no effect on the ability to mitigate the consequences of design basis accidents as a result of not recognizing the need for a change to the Technical Specifications. The changes to the response time testing were in accordance with the BWROG LTR and the approval provided by the NRC in their associated Safety Evaluation Report, and on April 18, 1997, the NRC issued License Amendment 111 which allowed these changes to the Fermi 2 response time testing. Therefore, based on the considerations in those reports, the affected instrumentation would have responded as expected.
3411997007 | Fermi 2 | 03/25/1997 | 04/24/1997 | 9704290068 | <strong>Condition Prohibited By Technical Specifications Due To Failure of Reactor Building HVAC</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1997, at 2247 hours, with the plant shutdown in Operational Condition 4 (Cold Shutdown) and Secondary Containment Integrity required to be met because of inoperable low pressure Emergency Core Cooling System (ECCS) subsystems, one of the two operating Reactor/Auxiliary Building Ventilation System (RBHVAC) exhaust fan discharge dampers closed, resulting in high reactor building pressure of +0.5 inch water gauge. This caused a loss of Secondary Containment Integrity. The cause of this event is age and service related mechanical failure of the solenoid valve that controls opening air to the discharge damper for the west RBHVAC exhaust fan, allowing the discharge damper to close. A related problem is the potential malfunction of the exhaust fan no-flow trip function. A no-flow trip of the west supply and exhaust fans may have prevented the loss of Secondary Containment Integrity following the closure of the exhaust fan discharge damper. The west supply and exhaust fans were subsequently manually tripped. Secondary Containment Integrity was restored within approximately two minutes of the event by starting the standby pair of RBHVAC fans. The failed solenoid valve was replaced and sent offsite for failure analysis. Corrective actions include completing the evaluation of the exhaust fan no-flow trip function, and determining the effectiveness of the quarterly walkdown of non-safety related solenoid valves used in this application.
3411997008 | Fermi 2 | 04/10/1997 | 05/12/1997 | 9705190064 | <strong>Potential Common Mode Failure Mechanism for 480-Volt Motor Control Center Disconnect Switches Due to Not Being Fully Latched Due to Inadequate Maintenance</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1997, a 480-Volt motor control center (MCC) fused disconnect switch opened unexpectedly and was found to be bound when an attempt was made to reclose the switch. A review of this event determined that there have been similar events on other switches in the past. operating mechanism is not mechanically latched. The seismic qualification of these switches requires them to be in either the closed-and-latched position or the full open position. On April 10, 1997, a four-hour non-emergency notification was made to the NRC as a potential condition that alone could have prevented the fulfillment of a safety function of systems that are needed to mitigate the consequences of an accident.<br /><br /> The cause of this condition is less than adequate preventive maintenance. The main contributor to the binding is a drying of the grease to a 'hardened' condition, due to aging and lack of the mechanism being exercised on a periodic basis. In addition, dust in the area of the pivot points also contributed to the loss of lubrication and subsequent binding of the operating mechanism. <br /><br /> The fused disconnect switches were cleaned and lubricated to provide reasonable assurance that the switches were left in a known state of being latched. Long term solutions are being evaluated and an implementation plan and schedule will be made prior to the start of the sixth refueling outage. The preventive maintenance program for the fused disconnect switches is being updated to ensure that the switches are inspected, cleaned and lubricated, and operated as necessary to maintain a proper lubrication interface.
3411997009 | Fermi 2 | 04/17/1997 | 05/19/1997 | 9705280008 | <strong>Operation in a Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) 4.1.3.8 requires the control rod drive housing support to be verified in place by a visual inspection prior to startup any time the support has been disassembled or when maintenance has been performed in the control rod drive housing support area. On April 17, 1997, it was determined that the literal wording of the TS requirement has not historically been considered prior to proceeding into Operational Condition 1, 2 or 3. That is, startup has proceeded without inspecting the housing support after maintenance has been done under the reactor vessel (in the housing support area) if the maintenance did not affect the housing support structure. <br /><br /> The cause for the missed surveillances is a lack of clarity in the TS, TS Bases and procedures regarding "when maintenance has been performed in the control rod drive housing support area." The drywell close-out procedure is being revised to clearly note that an inspection of the CRD housing support structure is required to be performed after any maintenance in the under vessel area above the service platform.
3411997010 | Fermi 2 | 05/04/1997 | 06/03/1997 | 9706100119 | <strong>High Pressure Coolant Injection Auxiliary Oil Pump Failure to Start</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1997 during the performance of a High Pressure Coolant Injection (HPCI) Pump Time Response and Operability Test the HPCI auxiliary oil pump (AOP) failed to start and run during the coastdown of the turbine. The AOP started after the operator cycled the control switch. During the shutdown of the HPCI turbine, the turbine was inadvertently restarted. The AOP cycled off and on approximately four times during the second coastdown. Based on the performance of the AOP the HPCI system was then declared inoperable. This event is being reported as any event or condition that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. <br /><br /> The cause of this event was a failure of an auxiliary contact used for seal-in purposes in the start circuitry for the AOP. During the initial event the seal-in contact did not close. The cause of the repetitive AOP cycling was a pressure switch which was out of calibration. This pressure switch controls the starting and stopping of the AOP. <br /><br /> The failed auxiliary contact used for seal-in purposes was replaced. Following the replacement of this contact the AOP was started and the circuit performance monitored. The AOP start circuit functioned properly. The pressure switch was also replaced and subsequently functioned properly.
3411997011 | Fermi 2 | 05/07/1997 | 06/06/1997 | 9706100430 | <strong>Condition Prohibited by Technical Specifications Due to Turbine Stop Valve and Turbine Control Valve Missed Surveillances</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1997 at approximately 0000 hours, while increasing reactor power following a reactor startup, it was determined that the Turbine Stop Valve (TSV) Closure and Turbine Control Valve (TCV) Fast Closure Channel Functional Tests had not been performed prior to entry into Operational Condition 1 as required by Technical Specification Limiting Condition for Operation (LCO) 3.3.1. Reactor power was verified to be less than 30% Rated Thermal Power (RTP), the Channel Functional Tests were performed, and the TSV Closure and TCV Fast Closure scram functions were declared Operable within 24 hours of discovery, as allowed by Technical Specification 4.0.3 following identification of a missed surveillance. <br /><br /> The cause of this event was failure to recognize, during the development of the applicable surveillance procedures and schedules, that LCO 3.3.1 requires the TSV Closure and TCV Fast Closure scram functions to be Operable prior to entry into Operational Condition 1. The Applicability requirements have been misinterpreted since initial plant operation to allow entry into Operational Condition 1 prior to performance of the Channel Functional Tests because of the safety analysis assumptions, and the industry-wide interpretation of the Applicability for these scram functions in the Standard Technical Specifications, from which the Fermi 2 Technical Specifications were derived. <br /><br /> Reactor power remained below 30% RTP during this event; therefore, the assumptions in the accident analyses were met and there was no threat to the public health or safety. Additionally, the Channel Functional Tests were performed satisfactorily, verifying that these scram functions had indeed been Operable. Corrective actions include revising the surveillance procedure and the surveillance scheduling database to reflect the Operational Condition 1 Applicability. The change in the interpretation of the Applicability for this Technical Specification will be included in Licensed Operator Requalification Training.
3411997012 | Fermi 2 | 06/03/1997 | 07/03/1997 | 9707100048 | <strong>Voluntary Report Regarding Surveillance Testing of Recirculation System Overspeed Stops</strong><br /><i>Abstract:&nbsp;</i>Technical Specification Surveillance Requirement (SR) 4.4.1.1.2 requires demonstration every 18 months that each recirculation pump motor generator (MG) set scoop tube mechanical and electrical stop is OPERABLE with overspeed setpoints less than or equal to 110% and 107%, respectively, of rated core flow. The surveillance procedure for testing these stops is divided into two sections, one for cold testing and one for testing at power. Detroit Edison believes that either of these methods is acceptable for satisfying SR 4.4.1.1.2. Members of the NRC staff have taken the position that the cold testing does not meet the Surveillance Requirement; and therefore, SR 4.4.1.1.2 was not performed within its Technical Specification required frequency. This interpretation and the location of this SR within the Recirculation Loops specification created a conflict which could not be resolved within the framework of the Technical Specification Section 1.0 Definitions or Section 3/4.0 Applicability requirements. In order to resolve this situation, the Surveillance Procedure was revised, core flow was reduced and the MG set stops were adjusted downward on June 4, 1997 to demonstrate that the stops were set below the SR 4.4.1.1.2 limits. A License Amendment request has been submitted to relocate the SR 4.4.1.1.2 requirements from the Technical Specifications to the Updated Final Safety Analysis Report as discussed with NRC management on the afternoon of June 4, 1997. Detroit Edison believes that performance of Section 6.1 of Surveillance Procedure 54.000.20 on April 17, 1997 was sufficient to satisfy SR 4.4.1.1.2, and that no condition prohibited by Technical Specifications existed at any time. However, due to the degree of regulatory involvement, and to clarify details associated with this issue, a voluntary Licensee Event Report is being submitted.
3411997013 | Fermi 2 | 06/19/1997 | 07/21/1997 | 9707280241 | <strong>High Pressure Coolant Injection System Isolation While Performing a Surveillance</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1997 at 1653 while performing a Division 1 High Pressure Coolant Injection (HPCI) Turbine Exhaust Diaphragm Pressure Functional test, the HPCI Steam Supply Inboard Isolation Valve closed. The HPCI isolation did not occur in response to an actual HPCI exhaust diaphragm high pressure signal. The Inboard Torus Suction Isolation Valve also received an isolation signal. However, this valve is normally closed and, therefore, did not change position. Approximately 2.8 seconds following initial receipt, the HPCI turbine exhaust diaphragm high pressure signal cleared. The surveillance was immediately terminated and HPCI was declared inoperable. The operability of Emergency Core Cooling Systems, Automatic Depressurization System, and the Reactor Core Isolation Cooling System was verified and a 14 day Limiting Condition of Operation was entered. <br /><br /> The cause of the event was an apparent spurious closure of a relay contact which actuated the relay that completed the circuit logic for an isolation signal to the HPCI Steam Supply Inboard Isolation Valve. The most probable cause of the spurious actuation is an intermittent component failure in the isolation logic for the HPCI Steam Supply Inboard Isolation Valve. <br /><br /> A jumper was installed across the relay contact which had spuriously closed and that channel was declared inoperable. HPCI was then returned to standby status and declared operable on June 20, 1997 at 0935. The appropriate components in the logic circuit have been replaced and are being evaluated to assist in determining what caused the spurious closure of the contact. If the evaluation does not provide any results, then monitoring of the affected channel will be considered.
3411997014 | Fermi 2 | 10/10/1997 | 04/06/1998 | 9804140129 | <strong>Turbine Building and Auxiliary Building Mezzanine Not Fully Meeting License Condition 2.C.9</strong><br /><i>Abstract:&nbsp;</i>During independent design verification of an Engineering Design Package, unsealed electrical penetrations were discovered in the auxiliary building wall fire rated separation barrier and in the adjacent and parallel turbine building fire barrier. This prompted a review of the fire hazards analysis and the 10CFR50, Appendix R assumptions used for this area. This review was completed on October 10, 1997 and revealed that of the 20 penetrations in these walls, 16 were not sealed at the auxiliary building wall and 4 were not sealed at the turbine building wall. There were no openings which were unsealed at both the turbine building wall and the auxiliary building wall. The 16 unsealed penetrations in the auxiliary building wall are located over a horizontal distance in excess of 25 feet and interface with areas which contain both redundant shutdown divisions. The lack of penetration seals in the fire barriers could allow a fire in the turbine building to exit the turbine building through any of the 4 unsealed penetrations and enter the auxiliary building at any of the sixteen unsealed penetrations. These 16 unsealed penetrations could then introduce a fire hazard within 20 feet of cable trays containing both Division I and Division II shutdown divisions. This condition is not in compliance with 10CFR50, Appendix R and is also reportable within 24 hours under License Condition 2.C(9). On October 10, 1997 at 1745 hours, the NRC was notified of this event. <br /><br /> An hourly fire watch was immediately established and will continue until an engineering design modification is installed to bring this area into compliance with 10CFR50, Appendix R. An evaluation using the guidance of Generic Letter 86-10 was performed and documented that the turbine building penetrations were sufficiently sealed.
3461997001 | Davis-Besse | 01/22/1997 | 02/21/1997 | 9702280091 | <strong>Nuclear Instrumentation Inoperable in Excess of Technical Specification Action Statement Requirements</strong><br /><i>Abstract:&nbsp;</i>At 0100 hours on January 22, 1997, with the Unit operating in Mode 1 at approximately 100 percent power, a Potential Condition Adverse to Quality Report (PCAQR) was initiated for NI-6 (power range nuclear instrument) reactor power imbalance signal. A Reactor Operator had noticed NI-6 (IG-AMP) imbalance to be reading more negative than expected. upon investigation of this condition, NI-6 was determined to be in a degraded condition from January 21, 1997, and had shifted approximately 4 direction. A review of the degraded condition by January 23, 1997, determined that in its degraded receives the NI-6 imbalance signal was inoperable intended safety function with respect to tripping 2151 hours until 2309 hours on percent in the negative Plant Engineering on condition, RPS Channel 1 which and incapable of performing its on positive imbalance. <br /><br /> The initiating condition was that a degraded bottom linear amplifier caused a small shift of the indicated NI-6 reactor power imbalance and total power signal to RPS Channel 1. The investigation revealed that the degraded condition existed for one hour and 18 minutes. Technical Specifications (TS) 3.3.1.1 allows an inoperable channel for no more than one hour. This is being reported as a condition prohibited by the TS in accordance with 10 CFR 50.73 (a)(2)(i)(B). The power range bottom linear amplifier was replaced. An an enhancement, Licensed Operators will be trained to make them more aware of instrument degradation of this nature by May 31, 1997.
3461997002 | Davis-Besse | 01/22/1997 | 08/19/1997 | 9708260148 | <strong>Potential Overpressurization of Containment Penetrations During Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1997, with the unit in Mode 1 at approximately 100 percent power, it was identified that the design of some containment penetrations may not have adequately considered all possible accident conditions. This was based on review and evaluation of information contained in Information Notice 96-049, "Thermally Induced Pressurization of Nuclear Power Facility Piping," and Generic Letter 96-006, "Assurance of Equipment Operability and Containment Integrity During Design-Basis Accident Conditions." It was determined that six containment penetrations could exceed interim allowable pipe stress values during design basis loss of coolant accident conditions. Analysis showed that piping stress due to overpressurization is not sufficient to cause piping failure; therefore, no system or containment integrity would be lost. This condition is considered outside the plant design basis and is being reported in accordance with 10CFR50.73(a)(2)(ii)(B). Plant modifications and procedure changes are being developed to prevent overpressurization of the penetration piping.
3461997003 | Davis-Besse | 01/30/1997 | 08/19/1997 | 9708260278 | <strong>Non-conservative Technical Specification Action for Degraded Reactor Coolant Flow</strong><br /><i>Abstract:&nbsp;</i>At 1405 hours on January 30, 1997, with the Davis-Besse Nuclear Power Station (DBNPS) operating at one hundred percent power, a Potential Condition Adverse to Quality Report was initiated with regard to the Technical Specification (TS) Action for degraded reactor coolant system (RCS) flow rate. Framatome Cogema Fuels (FCF) notified the DBNPS that the Action statement for TS 3.2.5, "DNB Parameters," was incomplete and non-conservative for degraded RCS flow conditions. This condition was identified by FCF as a result of evaluating potential reduced flow conditions due to steam generator tube plugging for another Babcock & Wilcox plant. A Preliminary Report of Safety Concerns (Number PT 21-97-1) was initiated by FCF on January 30, 1997. The apparent cause is that calculations performed in support of Amendment 64 to the DBNPS Facility Operating License did not consider the need to adjust Reactor Protection System trip setpoints. Analysis of measured RCS flow rate data at the DBNPS shows that the required flow rate has been maintained. The Nuclear Regulatory Commission was notified by Toledo Edison via the Emergency Notification System at 1739 hours on January 30, 1997, in accordance with 10CFR50.72(b)(2)(iii)(D) that this event is considered a condition that could have alone prevented the fulfillment of a safety function of a system needed to mitigate the consequences of an accident. This report is being submitted in accordance with 10CFR50.73(a)(2)(v)(D).
3461997004 | Davis-Besse | 02/03/1997 | 03/26/2004 | ML04090034 | <strong>Reactor Coolant Pump Motor Oil Piping Not Protected From Leakage As Required Per 10CFR50, Appendix R</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1997, with the plant in Mode 1 operating at 100 percent power, it was discovered that a portion of the oil piping for each Reactor Coolant Pump (RCP) motor was outside the oil collection system that is required per 10CFR50, Appendix R. This piping is the source connection for three pressure switches and a pressure gauge for the lift oil pump system, which is only pressurized when the lift oil pump is operating. On February 19, 1997, after reviewing pictures of the RCP motors as part of the corrective actions for this issue, more piping was found outside the RCP oil collection system. This additional piping included lower bearing remote oil fill connections, which are not pressurized; and piping for lower bearing oil reservoir drains, which is exposed to only two feet static head pressure. The lift oil pumps were not operating, and the remote oil fill connections had not been used that operating cycle. This condition is considered outside the plant design basis and was reported in accordance with 10CFR50.73(a)(2)(ii)(B). Plant modifications were implemented to contain or modify the piping as necessary to ensure compliance with 10CFR50, Appendix R.
3461997005 | Davis-Besse | 02/12/1997 | 12/19/1997 | 9801050270 | <strong>Surveillance Requirement Missed Due To Inadequate Safety Evaluation</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1997, with the plant in Mode 1 operating at 100% power, it was determined that a Technical Specification Surveillance Requirement had not been fulfilled during the last plant startup. The inspection cover on the Decay Heat Valve Pit had been opened after performing the vacuum leakage rate test required per Surveillance Requirement 4.5.2.f. This Surveillance Requirement requires that the vacuum leakage rate test be performed after each opening of the water tight enclosure. As a result of this missed surveillance, both trains of Emergency Core Cooling were declared inoperable, and Technical Specification 3.0.3 and 4.0.3 were entered. The Nuclear Regulatory Commission (NRC) was notified of this condition via the Emergency Notification System in accordance with 10CFR50.72(b)(1)(i)(A). After determining that the surveillance test could not be performed in Mode 1, a plant shutdown was initiated at 1521 hours. The shutdown was terminated when enforcement discretion from the NRC was verbally granted at 2005 hours on February 12, 1997. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. A License Amendment was approved on March 24, 1997, to allow the inspection cover to be opened in Modes 1 to 3 to perform inspections without requiring the performance of the vacuum leakage rate test.
3461997006 | Davis-Besse | 02/25/1997 | 03/27/1997 | 9704030074 | <strong>Both Containment Radiation Monitors Inoperable Due To Missing Gaskets</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1997, with the plant in Mode 1 operating at 100 percent power, both Containment Normal Range Radioactivity Monitors were found to be missing gaskets on the particulate filter and iodine cartridge holders. According to the current vendor for these monitors, these gaskets are necessary for proper operation of the monitors. This rendered one of the three Reactor Coolant System leakage detection systems inoperable. The Technical Specification required action of obtaining and analyzing grab samples every 24 hours with these monitors inoperable was not performed. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. Procedures for changing the particulate filter and iodine cartridge holders have been revised to include instructions to verify that the required gaskets are installed.
3461997007 | Davis-Besse | 03/05/1997 | 06/20/1997 | 9707020238 | <strong>Surveillance Test Acceptance Criteria Not Conservative Due To Calculation Error</strong><br /><i>Abstract:&nbsp;</i>During review of a calculation, it was determined that the acceptance criteria of a Surveillance Test to measure the leakage into the Decay Heat Valve Pit was potentially non-conservative. This Surveillance Test is performed to ensure that the valve operator motors within the pit will not become flooded within seven days following a design basis loss of coolant accident (LOCA). A preliminary calculation was performed to determine the proper acceptance criteria. The most recent performance of this test was reviewed and the test results were determined to be adequate to prevent flooding of the valve motor operators within the pit. A review of past test results completed on March 5, 1997, with the plant in Mode 1 operating at 100% power, determined that the results of the Surveillance Test performed September 10, 1983, possibly would have allowed the valve operator motors in the pit to become flooded following a LOCA. The discovery of this past event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3461997010 | Davis-Besse | 05/04/1997 | 06/03/1997 | 9706110303 | <strong>Reactor Trip Due To Main Transformer Deluge System Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1997, at 1731 hours, with the plant at 100 percent power, the Main Transformer Deluge System automatically actuated due to a degraded temperature sensor in the transformer fire detection system. At 1735 hours, a flashover occurred when the Main Transformer faulted to ground due to the deluge system actuation. The Main Generator locked out on overall differential current, which initiated a trip of the Main Turbine and a subsequent reactor trip by the Anticipatory Reactor Trip System. The plant was cooled down to replace the Main Transformer that was damaged as a result of the flashover. The temperature sensors that actuate the deluge system have been replaced with a different type of temperature sensor to prevent inadvertent actuation, and four nozzles near the top of the transformer have been realigned to reduce the chances of a transformer flashover upon a deluge system actuation. This event is being reported in accordance with 10CFR50.73(a)(2)(iv).
3461997012 | Davis-Besse | 09/04/1997 | 05/10/1998 | 9805190384 | <strong>Decay Heat Cooler Seismic Design Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1997, with the Davis-Besse Nuclear Power Station operating at one hundred percent power, a Potential Condition Adverse to Quality Report was initiated with regard to the Decay Heat Coolers (DHCs). The DHCs were classified as outliers in accordance with the Seismic Qualification Utility Group program. During the evaluation of the DHCs as outliers, it was identified that loads from piping attached to the DHCs were not considered in the analysis of the DHC supports. The results of a calculation, which accounted for all of the applied loads on the DHC, indicated that portions of the DHC support system would exhibit localized yielding as a result of Safe Shutdown Earthquake loads. Engineering evaluation concluded that the localized yielding in the support system could prevent the DHC from performing its function unless the bolting between the DHC saddle and the stand was tightened to an acceptable condition. At 0900 hours on September 4, 1997, both DHCs were declared inoperable and LCO 3.0.3 was entered. Immediate Action Maintenance was completed to tighten these bolts to restore the system functionality and LCO 3.0.3 was exited at 0922 hours. The apparent cause for this occurrence is inadequate design of the DHC support system. Since the plant was in a condition outside the design basis of the plant, the NRC was notified by Toledo Edison via the Emergency Notification System at 0942 hours in accordance with 10CFR50.72(b)(1)(ii)(B). This event is being reported under 10CFR50.73(a)(2)(ii)(B) as a condition outside the plant's design basis, and 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3461997013 | Davis-Besse | 10/02/1997 | 11/03/1997 | 9711070168 | <strong>Missed Surveillance for the Safety Features Actuation System Channel 2 Containment Radiation Functional Unit</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1997, with the plant in Mode 1 and 100 percent power, a Potential Condition Adverse to Quality Report (PCAQR) documented failure to perform a surveillance test (ST) before the Technical Specification (TS) Surveillance Requirement (SR) late date. On June 5, 1996, a Maintenance Work Order (MWO) was implemented to perform adjustments on the SFAS Channel 2 Containment Radiation monitor. The calibration test for the Safety Features Actuation System (SFAS) Channel 2 Containment Radiation instrument string was partially performed on June 6, 1996 as the post-maintenance test for the adjustments. When the test was being reviewed on October 2, 1997, as part of an experience review for another unrelated PCAQR, it was realized that an administrative error had been made in the surveillance and periodic test schedule. Upon completion of the test, the Test Cover Sheet was erroneously marked and the schedule was updated to indicate the test was performed to meet the surveillance test schedule, even though the test was not performed in its entirety. The SR refueling test interval plus 25 percent maximum TS allowable extension was exceeded because the ST should have been performed in its entirety by August 27, 1997. This placed the plant in TS 3.3.2.1 and TS 4.0.3 was invoked for a missed SR. The missed surveillance was completed at 1915 hours on October 2, 1997. Since the SR was not met within the allowable surveillance interval, the plant was operated in a condition that is prohibited by the TS and this condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B).
3461997014 | Davis-Besse | 08/01/1997 | 11/26/1997 | 9712090150 | <strong>Pressurizer Pilot-Operated Relief Valve Setpoint Less Than Allowable Value Due To Degraded Wire Splice</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1997, with the plant in Mode 1 operating at 100 percent power, a problem was discovered involving the Nuclear Instrumentation output from the Reactor Protection System (RPS) to the Non-Nuclear Instrumentation System. Troubleshooting revealed a faulty wire splice connecting the RPS signal common and power common bus bars to the instrument ground bus had caused a voltage difference between the bus bars. The wire splice was repaired on August 7, 1997. On August 11, 1997, it was determined that this problem affected the Pressurizer Pilot-Operated Relief Valve (PORV) setpoint, but the PORV setpoint was determined to remain within the Technical Specification allowable value. Further research conducted in October, 1997, showed that the results of the last calibration of the associated PORV instrumentation combined with the setpoint shift resulting from the voltage difference may have caused the PORV setpoint to be outside the Technical Specification allowable value. Since the PORV remained in service while the voltage difference existed, this event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3461997015 | Davis-Besse | 12/10/1997 | 05/08/1998 | 9805190261 | <strong>Emergency Diesel Generator Tachometer Circuit Outside 10CFR50 Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1997, at 1020 hours, with the unit in Mode 1 at 100% power, during a review of the condition report from the Fort Calhoun Station, it was discovered that a problem with the Emergency Diesel Generator (EDG) tachometer circuitry existed at Davis-Besse. A postulated hot short condition could cause a failure of the EDG speed switch before the operator could manually disconnect the EDG tachometer control room circuitry from the EDG speed switch. Technical Specification 3.3.3.5.2 was entered to track the inoperable circuit, and an hourly fire watch was established in the cable spreading room. On December 18, 1997, at 1345 hours, it was determined that this condition represented a condition that was outside the 10CFR50 Appendix R design basis of the plant. The control room tachometer circuit was isolated at 1356 hours using the installed local disconnect switch, and the NRC was notified via the Emergency Notification System at 1415 hours on December 18, 1997 in accordance with 10CFR50.72(b)(1)(ii)(B). A review of all circuits previously identified as potentially experiencing a single hot short will be performed to determine if the consequences were adequately evaluated. This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(B), 10CFR50.73(a)(2)(i), and the Special Report requirement of Technical Specification 3.3.3.5.2.b.
3481997001 | Farley 1, Farley 2 | 02/06/1997 | 03/07/1997 | 9703130416 | <strong>Technical Specification Ventilation System Deficiencies</strong><br /><i>Abstract:&nbsp;</i>As a result of an investigation initiated by questions concerning the Penetration Room Filtration (PRF) system, several deficiencies were discovered with the engineered safety features (ESF) ventilation systems at Farley Nuclear Plant (FNP). Both Unit 1 and Unit 2 operated in mode 1 at 100% reactor power during these events. At 1315 on 02/06/97, it was discovered that FNP had previously operated in a condition prohibited by Technical Specifications (TS). During an evaluation of previous surveillance test results, it was identified that the TS surveillance requirement for PRF system flow was not met for the 12/1/92 surveillance performed on Unit 2 'A' Train PRF system. However, the previous and subsequent tests to the 12/1/92 test were completed satisfactory and no maintenance that would have affected the PRF system flow was performed during that time. Therefore, it was concluded that the system was capable of performing its specified function. In addition, on 02/26/97, it was determined that the TS surveillance requirements for 3/4.7.7 Control Room Emergency Filtration/Pressurization System (CREFS), 3/4.7.8 PRF, and 3/4.9.14 Containment Purge Exhaust Filter system (CPEF) had not been completed to the extent required. Therefore, due to the surveillances not being completed, CREFS and PRF were declared inoperable and, at 1227 on 02/26/97, FNP entered TS 3.0.3. The CPEF system was not affected at this time since both units were in a mode in which the CPEF was not required to be operable. At 1351 on 02/26/97 enforcement discretion was granted by the NRC and TS 3.0.3 was exited. These events were caused by cognitive personnel error. The applicable procedures addressing the inadequate flow test have been revised and the responsible person will be coached on the event. For the ESF ventilation systems, a proposed TS amendment has been submitted to clarify the surveillance requirements and additional testing and inspections will be performed where possible. This condition will be fully corrected following NRC approval of the submitted TS amendment and SNC implementation. Lessons learned from the events will be communicated to the appropriate personnel.
3481997002 | Farley 1, Farley 2 | 02/18/1997 | 03/14/1997 | 9703200060 | <strong>Safety-Related 4160 Volt A.C. Breakers Not Seismically Qualified in Any Position Except in the Connect Position</strong><br /><i>Abstract:&nbsp;</i>As part of an investigation for applicability of similar industry events, Farley Nuclear Plant (FNP) requested an engineering evaluation be performed on the safety-related 4160 volt switchgear breakers [EB] installed at FNP relating to seismic qualification. On February 18, 1997, with Unit 1 and 2 in Mode 1 operating at 100% power, it was determined that Farley Nuclear Plant (FNP) had been operating in a condition that alone could have prevented the fulfillment of the Safety Function of a system needed to shutdown the reactors and maintain them in a safe shutdown condition. Breakers for the safety-related 4160 volt switchgear have not been seismically qualified in any position other than in the 'connect' from unrestrained breakers in the 'disconnect' position to cause relay/breaker chatter in adjacent breaker cubicles that could compromise safety-related equipment operations. Safety-related 4160 volt A.C. breakers not being seismically qualified in all positions was due to personnel error in that the original design failed to consider the seismic qualification of these breakers 'in positions other than the 'connect' position. Operating procedures have been modified to include removing any safety-related 4160 volt A.C. breaker that can not be maintained in the 'connect' position from their respective switchgear cubicle and moving them to a position at least 30 inches away from any safely-related equipment. In addition, any breakers that have been removed will have their wheels secured to prevent the breakers from rolling and impacting the switchgear if a seismic event were to occur. Long-term plans include the installation of interlocking channels on the breaker and switchgear cubicle to restrain the breaker in a front-to-back and side-to-side motion when the breaker is either in the 'test' or 'disconnect' positions.
3481997003 | Farley 1, Farley 2 | 03/15/1997 | 09/08/1998 | 9809150010 | <strong>Failure to Comply with Technical Specifications 4.5.3.2 and 3.5.2</strong><br /><i>Abstract:&nbsp;</i>At 1239 on March 15, 1997 it was determined that Unit 1 had been operated in a condition prohibited by Technical Specifications (TS) in that TS surveillance requirement 4.5.3.2 had not been performed, as required by the operating procedure, prior to entry into mode 4 during a unit shutdown in preparation for a refueling outage. This condition lasted for approximately 6 minutes. During the investigation of this event, it was determined that similar situations have occurred in the past two years where FNP has operated in a condition prohibited by TS 4.5.3.2. In addition, it was determined that operating within the requirement of TS 4.5.3.2, as specified in the operating procedure, would have resulted in operating in a condition prohibited by TS 3.5.2. Subsequent to the above event, on June 1, 1997 with Unit 1 in mode 4, TS 3.0.3 was voluntarily entered twice while in preparation for transitioning from mode 4 to mode 3 as the unit was returned to operation following the refueling outage. Additionally, subsequent to the above events, on March 28, 1998, Unit 2 voluntarily entered TS 3.0.3 while transitioning from mode 3 to mode 4 and again on May 13, 1998 while transitioning from mode 4 to mode 3. On August 17, 1998, Unit I entered TS 3.0.3 while transitioning from Mode 3 to Mode 4 and again on September 1, 1998, while transitioning from mode 4 to mode 3. The cause of operating in a condition prohibited by TS 4.5.3.2 was personnel error in that operations personnel failed to adequately review the operating procedure prior to mode 4 entry. The RHR discharge to charging pump suction MOVs 8706A and 8706B were verified closed and the breakers for the valve operators locked open at approximately 1245. Operations personnel involved in this event have been coached concerning procedure adherence. <br /><br /> The cause of previously operating in a condition prohibited by TS 3.5.2 as described above was due to an inconsistency existing within TS. Specifically, TS failed to provide an allowed time between modes 3 and 4 to lock open the MOV breakers. Operating procedures were written to ensure the specific surveillance requirement of TS 4.5.3.2 was met; however, personnel failed to note that TS 3.5.2 was not being met. A review of Technical Specifications has been performed to determine if similar situations of inconsistencies during mode changes exist. The cause of entering TS 3.0.3 on June 1, 1997, on March 28, 1998, on May 13, 1998, on August 17, 1998, and on September 1, 1998 was due to the inconsistency within TS as discussed above.
3481997004 | Farley 1, Farley 2 | 03/18/1997 | 04/15/1997 | 9704230221 | <strong>Safety-Related 600 Volt Position Sensitive Seismic Qualification</strong><br /><i>Abstract:&nbsp;</i>As put of an investigation for applicability of industry events related to the seismic qualification of breakers, Farley Nuclear Plant (FNP) requested an engineering evaluation be performed on the Westinghouse DS safety-related 600 volt load center breakers [ED] installed at FNP. On March 18, 1997, Unit 1 was in Mode 5 at approximately 100 degrees F reactor coolant system (RCS) temperature and 0 psig RCS pressure and Unit 2 was operating in Mode 1 at 100% power. It was determined that FNP had been operating in a condition that alone could have prevented the fulfillment of the Safety Function of a system needed to shutdown the reactors and maintain them in a safe shutdown condition. The engineering evaluation concluded that breakers for the Westinghouse safety-related 600 volt load centers were not seismically qualified in all positions. The potential exists for impact from unrestrained breakers in the 'removed' position to cause relay/contact chatter in adjacent breaker cubicles that could compromise safety-related equipment operation. Operating Westinghouse DS safety-related 600 volt breakers not being seismically qualified in all positions was due to personnel error in that the original design failed to consider the seismic qualification of these breakers in all positions. Operating procedures have been modified to include removing any Westinghouse DS safety-related 600 volt load center breaker that can not be maintained in either the 'connect', 'disconnect' or 'test' positions from their respective load center cubicle and moving them to a position at least 12 inches away or the height of the breaker which ever is greater from any safety-related equipment. and/or breakers to ensure these breakers will maintain their seismic adequacy.
3481997005 | Farley 1, Farley 2 | 03/15/1997 | 09/03/1998 | 9809100356 | <strong>Failure to Perform Nuclear Instrumentation Surveillance Requirements Prior to Mode 2 and 3 Entry</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1997, with Unit 1 in mode 6, it was discovered that Farley Nuclear Plant (FNP) had been operated in a condition prohibited by Technical Specifications (TS) in that TS 3.0.4 was not met on March 15, 1997, when Unit 1 entered mode 2 during a unit shutdown without meeting the Source Range surveillance requirements (SR) of TS 4.3.1.1 for functional testing. In addition, TS 3.0.4 was not met when Unit 1 reduced power below the P-6 (block of source range reactor trip) setpoint without meeting the requirement of TS 4.3.1.1 for a channel check. Subsequently, during a review of TS SR required prior to mode changes during plant shutdowns, performed as part of the corrective action for LER 97-003-00 (Shared), it was discovered, on April 8, 1997, that the TS 4.3.1.1 SR for the Power Range high flux low setpoint bistable calibration had not been met prior to Unit 1 entering mode 2 on March 15, 1997. This resulted in Unit 1 entering TS 3.0.3 for approximately 7 minutes until the unit entered mode 3. Although not specifically identified in this LER, the failure to meet TS 4.3.1.1 SR during unit shutdowns has resulted in previous occurrences where Units 1 and 2 have operated in a condition prohibited by TS. The cause of these events was cognitive personnel error. Subsequent similar events involving failure to meet TS 4.3.1.1 channel check requirements occurred on March 28, 1998 on Unit 2 and August 17, 1998 on Unit 1. Failure to meet the TS 4.3.1. 1 Source Range functional test requirement resulted from inadequate test procedures, and failure to meet the channel check requirement was due to an inconsistency existing within TS. Failure to meet TS 4.3.1.1 Power Range high flux low setpoint calibration resulted from a failure to ensure the SR for mode changes during a shutdown were incorporated into the procedure. Applicable procedures were revised. Lessons learned from the original events were provided to the appropriate personnel. A TS amendment has been submitted.
3481997006 | Farley 1 | 04/01/1997 | 05/28/1997 | 9706050074 | <strong>Steam Generator Tube Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1997, Farley Nuclear Plant steam generator inspection results were classified as Category C-3 in accordance with Technical Specification 4.4.6.5.c. A voluntary notification report to the NRC of the C-3 inspection classification was made on April 1, 1997. <br /><br /> In accordance with Technical Specification 4.4.6.5.a, FNP is reporting that during the Unit 1 Fourteenth Refueling Outage (U1RF14) 113 tubes were plugged. Repair included the installation of 996 sleeves, which includes the return to service of 149 previously plugged tubes. The plugging and repair work was completed on May 23, 1997. <br /><br /> Eddy current inspections were performed on one hundred percent of the available tubes in all three steam generators (S/G). As a result of this inspection, more than 1% of the inservice tubes in each S/G during Cycle Fourteen were found to be defective, which requires inspection results in each S/G to be classified as Category C-3. Defective indications were identified within the tubesheet, above the top of the tubesheet in the sludge pile area, at the tube support plates, and in the freespan. In addition to the required tube repair and plugging, several ongoing programs have been established to reduce the probability of future tube degradation.
3481997007 | Farley 1, Farley 2 | 04/22/1997 | 05/22/1997 | 9705280013 | <strong>Outside of Design Basis due to Degraded Cork Material</strong><br /><i>Abstract:&nbsp;</i>On April 17, 1997, as a result of a plant walkdown, licensed operators reported some of the self expanding cork seal was missing from the gap between the main steam valve room (MSVR) and containment building. Deficiency Reports (DRs) were submitted. A licensed operator questioned if this condition could result in the flooding of the lower level equipment room (LLER) and what would be the effects if it did. As a result of this question, repairs to the Unit 2 seal were initiated and an engineering evaluation was requested to review this condition. On April 22, 1997, with Unit 1 in Mode 6 at approximately 85 Degrees F reactor coolant system (RCS) temperature and 0 psig RCS pressure and Unit 2 in Mode 1 operating at 100% power, it was determined that Farley Nuclear Plant (FNP) had operated in a condition that was outside the design basis of the plant. These seals are required to function as watertight barriers to contain flood volume in the MSVR. The current main feedwater line break analysis assumes only one motor-driven auxiliary feedwater pump (MDAFWP) and the turbine-driven auxiliary feedwater pump (TDAFWP) are available. With sections of the seal missing, a flooding event in the MSVR could result in flooding of the LLER that is sufficient to render the TDAFWP and support equipment unavailable. With these conditions, auxiliary feedwater (AFW) flow to the steam generators could be less than assumed in the accident analyses. Similar conditions had been reported on June 22, 1996 and December 10, 1996 and DRs were submitted. The DRs were evaluated but the possibility of flooding was not considered. The repair of these seals was given a low priority and became part of the backlog of maintenance deficiencies. The causes of this condition were insufficient routine inspection which prevented timely detection of the degraded condition of the cork seal and incorrect evaluation of the deficiency and prioritization of work on the maintenance backlog. The Unit 2 seal repair has been completed. The Unit 1 seal will be repaired prior to Unit 1 entering an operating mode in which the seal is required.
3481997008 | Farley 1 | 04/23/1997 | 05/23/1997 | 9705290065 | <strong>Outside of Design Basis Due to RCS Support Gaps Not Being Consistent With Design</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1997 with Unit 1 in Mode 6 at approximately 80 degrees F reactor coolant system (RCS) temperature and 0 psig RCS pressure, it was determined that a condition existed where Unit 1 may have operated outside the design basis of the plant. An evaluation concluded on May 16, 1997 that Unit 1 had been operated in a condition outside the design basis of the plant. Specifically, a condition of high stresses in the RCS piping and lateral supports existed during plant operation due to gaps associated with the 1C steam generator (SG) support bumpers not being consistent with design. The evaluation concluded that the high stresses that occurred during normal plant operation did not exceed design code requirements. However, these stresses concurrent with the postulated safe shutdown earthquake (SSE) would have exceeded the code allowable stresses.<br /><br /> During normal plant operation, higher than normal vibration was noted on the reactor coolant pump in Loop C. After the shutdown for the scheduled refueling outage, an investigation determined that hot gaps associated with the 1C SG support bumpers appeared to be too large on two of the bumpers and no gaps were present on two others. It was determined that interference between the RCS loop and the bumpers occurred during plant operation, resulting in a condition of high stresses in the RCS piping and the LS-12 support location. <br /><br /> This event was caused by cognitive personnel error during the initial installation of the support shims when the shims on three 1C SG support bumpers were not installed in accordance with the design. The existing installed shim configuration has been modified. Hot gaps in all loops will be verified to be consistent with the original design.
3481997009 | Farley 1, Farley 2 | 04/30/1997 | 05/27/1997 | 9706040178 | <strong>Lack of Missile Protection For Service Water Flow Switches</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1997, with Unit 1 in Mode 5 at approximately 90 Degrees F reactor coolant system (RCS) temperature and 0 psig RCS pressure and Unit 2 in Mode 1 operating at 100% power, it was determined that Farley Nuclear Plant (FNP) had operated in a condition that was outside the design basis of the plant in that four Category 1 Service Water differential pressure switches had not been protected from Design Basis Tornado generated missiles. FSAR Section 3.5.4 requires that Category 1 equipment and piping be housed in Category 1 structures or be buried underground. Contrary to this requirement, these four switches are installed on the outside of the Diesel Generator (DG) Building. The switches susceptibility to tornado generated missiles was discovered during a plant walkdown by design personnel. Since a tornado generated missile could have caused a malfunction of these switches, Service Water flow to the Diesel Building could have been inadvertently isolated when the associated Service Water isolation motor-operated valves (MOVs) closed and shut off cooling water flow to the Emergency Diesel Generators. The loss of cooling water could render one or more of the Emergency Diesel Generators inoperable. Since a loss of offsite power should be assumed with a Design Basis Tornado, the Emergency Diesel Generators would be required to safely shutdown the plant. The cause of this condition is inadequate design in that the lack of missile protection for these switches was an oversight of the design organization. The automatic isolation function of the isolation valves from the SW Building to the DG Building has been disabled on both units.
3481997010 | Farley 1, Farley 2 | 05/23/1997 | 04/29/1998 | 9805050208 | <strong>Motor Operated Valve Local - Remote Control Circuit Wiring Discrepancies</strong><br /><i>Abstract:&nbsp;</i>At 1630 on May 23, 1997, while Unit 1 was in Mode 5, it was determined that Unit 1 had operated in a condition outside its design basis. During a fuse inspection, it was concluded that the control circuitry for the operation of five Motor Operated Valves (MOVs) was not wired per design. At 1325 on May 25 while Unit 2 was operating in Mode 1 at 100% power, subsequent investigation determined that the same condition existed on Unit 2. For the MOVs affected, the portion of the control circuitry which is used to select either local (Hot Shutdown Panel) or remote (Main Control Board) mode of operation was found to have the associated control power fuses wired in series rather than parallel. A one hour non-emergency notification was made to report this condition for Unit 2 at 1334 CDT on May 25, 1997. In this configuration, any fault which resulted in the opening of either fuse would have prevented operation of the valve from the local (Hot Shutdown Panel) location. The remote (Main Control Board) mode of operation would have operated as designed and would only have been lost in the event of a fault which opened its associated control power fuse. All affected MOVs were rewired in accordance with design. The cause of the improper wiring has been determined to be cognitive personnel error in that inadequate design instructions were provided to implementing personnel during the performance of design changes which established local-remote operation capability.
3481997011 | Farley 1 | 07/06/1997 | 07/31/1997 | 9708060329 | <strong>Entry Into TS 3.0.3 Due to The Failure to Follow the Work Control Process Procedure</strong><br /><i>Abstract:&nbsp;</i>At 1027 on July 6, 1997 while in Mode 1 at 100 percent power Unit 1 entered a condition prohibited by Technical Specifications (TS) in that TS requirement 3.7.4 for maintaining two independent service water system loops operable was not satisfied. TS 3.0.3 was entered due to portions of both the Train A and Train B service water system to the turbine building motor operated valves (MOVs) automatic isolation capability being inoperable. This condition lasted for approximately 39 minutes. <br /><br /> The cause of this event was the failure to follow the procedure associated with controlling the work control process. Specifically, operations supervision and two instrumentation and control technicians incorrectly concluded the work order associated with the previous investigation which had been narrowed to a specific component was adequate to continue with an additional investigation on different components within the same system. However, specific limits should have been identified and documented on the work order prior to approval and release of the expanded work activities. A contributing cause to this event was inadequate communication between operations supervision and the technicians during the pre-job briefing in understanding the bounds of expanded work activities. Operations assumed the technicians would perform maintenance functions on PDS 568 and PDS 566 only, whereas, the technicians assumed they had permission to perform certain maintenance activities on all four PDSs. <br /><br /> Appropriate operations and maintenance personnel will be instructed on the expectations that specific limits must be identified and documented on the work order prior to approval and release of the work order for investigation activities.
3481997013 | Farley 1, Farley 2 | 08/18/1997 | 09/12/1997 | 9709170303 | <strong>Operating Outside the Design Basis Due to Control Room Exhaust Isolation Dampers Not Closed</strong><br /><i>Abstract:&nbsp;</i>On 8/18/97, with Units 1 and 2 operating at 100% reactor power, it was determined that Farley Nuclear Plant (FNP) had been operated outside the design basis of the plant due to the three control room exhaust isolation dampers being in the open position during normal operation. FSAR Section 6.4.1.1 for habitability systems requires that, during design basis accident conditions, greater than 1/8 inch water gauge positive pressure will be maintained in the control room. Contrary to this requirement, an evaluation determined that, with the dampers open, a single failure could have prevented the control room ventilation system (CRVS) from maintaining the required pressure to assure control room habitability. The design basis for the dampers is that the dampers require should be closed except when purging smoke or toxic gas from the control room. An investigation revealed that the dampers had been open by procedure since 3/84. During the development of the CRVS Functional System Description (FSD), which defines the system functional design requirements, the discrepancy with the dampers not being in the designer assumed closed position was identified. In 4/95, an evaluation was performed to resolve the damper position discrepancy. Due to a misinterpretation of the results of this evaluation, the dampers were left open. On 8/11/97, during the FSAR verification process, the open damper position was once again questioned and the dampers were closed as a precautionary measure at 1700 on 8/13/97. The cause of the dampers being left in the open position has been determined to be cognitive personnel error, in that, the design basis was not adequately described in the FSAR and the results of the 1995 evaluation were misinterpreted. The operating procedure has been revised and administrative controls established to ensure the dampers are operated within the design basis. The CRVS FSD observations will be reviewed for adequate resolution. An FSAR change will be initiated to clarify the design basis of the system. Lessons learned from this event will be discussed with the personnel who misinterpreted the 1995 evaluation.
3481997014 | Farley 1 | 09/22/1997 | 10/07/1997 | 9710140260 | <strong>RCS Leak Detection System Inoperable Due to Defective Procedure Results in Operating in Condition Prohibited By TS</strong><br /><i>Abstract:&nbsp;</i>On 8/15/97, during resolution of a potential FSAR discrepancy identified during a training lesson plan review, it was discovered that the containment air cooler drain valves were mispositioned. The mispositioned valves could have prevented the containment air cooler condensate level monitoring (CCLM) system from performing its design function of detecting a 1 gpm reactor coolant system (RCS) leak within 1 hour. Preliminary calculations indicated the CCLM sensitivity was adequate. However, on 9/22/97, with Unit 1 operating at 100% reactor power, the final results of an evaluation concluded that the CCLM system had been inoperable. This condition resulted in Farley Nuclear Plant (FNP) having been operated in a condition prohibited by Technical Specification (TS). Although not specifically identified in this LER, there have been previous occurrences which, although it was not recognized at the time, resulted in Unit 1 operating in one of the following conditions prohibited by TS: (1) not performing the required compensatory actions of TS 3.4.7.1 when either the containment atmosphere particulate (R11) or gaseous (R12) radiation monitors was inoperable or, (2) entering TS 3.0.3 when both R11 and R12 were inoperable. To meet its design function, the CCLM system should have drain valves with or throttled to an approximate flowrate of .06 gpm. An investigation found all four drain valves in the full open position, as specified by the operating procedure, which exceeded the design flow conditions. The valves originally installed were throttled during startup testing to obtain the required flowrate, however, the throttling requirement was not reflected in the operating procedures and the valves were subsequently positioned fully open. The cause of this event was attributed to a defective procedure in that the system design flowrate criterion was not adequately incorporated into plant operating procedures. The valves have been throttled to their required position and the system operating procedure has been revised to specify the throttled position for the drain valves.
3521997001 | Limerick 1, Limerick 2 | 10/26/1984 | 02/21/1997 | 9703030010 | <strong>Safety-Related Logic Circuits Not Fully Tested</strong><br /><i>Abstract:&nbsp;</i>In January and February 1997, the engineering review performed in response to NRC Generic Letter (GL) 96-01 identified 3 issues involving contacts within a EDG/4kV subsystem logic channel that were not tested per the Technical Specification (TS) Surveillance Requirements (SR). These contacts are similarly contained in each of the 4 EDG/4kV subsystems for each unit. The untested contact circuits involve the Emergency Diesel Generator output breaker trip while in test logic, the off site power voltage monitoring logic, and the 4kV load breaker connected position trip logic. All of the contacts have been tested and restored to an operable status and only one contact failed to operate correctly. The TS SR had not been met since the original plant start-up resulting in operation prohibited by TS. The actual and potential consequences from these conditions were minimal. Inadequate review of the logic circuits and/or misinterpretation of the TS SR scope during the original procedure development and subsequent reviews resulted in the incorrect procedures. The review of the safety-related logic channels as stipulated in the response to GL 96-01 has been completed for Unit 1 and Unit 2. No additional deficiencies were identified. The appropriate procedures will be revised prior to the next performance.
3521997002 | Limerick 1, Limerick 2 | 01/23/1997 | 02/24/1997 | 9703040119 | <strong>Failure to Implement Technical Specification Required Visual Inspections of Blind Flanges.</strong><br /><i>Abstract:&nbsp;</i>On 11/15/96, during a 10CFR50.54(f) task team review, a recently modified primary containment penetration (involving a blind flange) was identified for further review for conformance with station administrative requirements. On 1/23/97, it was determined that a total of fifteen (15) penetrations on both units had blind flanges that constituted a primary containment boundary subject to the visual inspection surveillance requirements of Technical Specification 4.6.1.1.b. Since these flanges were not periodically visually inspected and the associated actions per Technical Specification 3.6.1.1 were not taken within the required time, operation prohibited by Technical Specifications occurred. This condition has existed since start-up of each unit and was caused by a misinterpretation of the surveillance requirements for blind flanges on containment penetrations. The consequences of this event were minimal in that no radioactive material was released and no events occurred requiring containment integrity while the penetrations were out of surveillance. Corrective actions included review of containment penetrations with blind flanges and incorporation into surveillance tests of those flanges previously not routinely inspected.
3521997003 | Limerick 1, Limerick 2 | 02/04/1997 | 05/12/1997 | 9705190083 | <strong>Degraded Back Pressure Dampers Needed for Pipe Rupture Mitigation Results in Operation Outside Design Basis.</strong><br /><i>Abstract:&nbsp;</i>During the February 1997 refueling outage for Unit 2, a total of eight (8) Unit 2 pairs, one (1) Unit 1 pair, and several single Back Pressure Dampers (BPDs) failed to actuate following a test signal. The BPDs are required to mitigate the consequences of a postulated pipe rupture. On 02/06/97 it was determined that this condition may have resulted in a failure to meet the design basis for a high energy line break (HELB) event. All Unit 2, common Control Enclosure (CE) and all accessible Unit 1 BPDs were tested and additional failures were immediately corrected. All of this testing was completed prior to the restart of Unit 2. The six (6) inaccessible Unit 1 BPDs were tested during a power reduction on 04/12/97. Four (4) of the six (6) Unit 1 inaccessible dampers and one (1) Unit 2 damper in a subsequent test sample failed to actuate. These five (5) failures were immediately corrected. Excessive friction in the bushing located between the solenoid and the BPD linkage caused all of the damper failures. Periodic cycling of the BPDs was not included in the original preventive maintenance (PM) program. An engineering analysis concluded that the additional components potentially impacted by the HELB event would still be capable of performing their safety function, but were not fully qualified. The appropriate PM activities for each BPD have been developed.
3521997004 | Limerick 1, Limerick 2 | 10/26/1984 | 03/11/1997 | 9703190048 | <strong>Previous Condition Prohibited by Technical Specifications in that 10 Fire Rated Assemblies were not Inspected Since Issuance of the Facility Operating Licenses For Each Unit.</strong><br /><i>Abstract:&nbsp;</i>On 02/11/97, a review of the Units 1 and 2 fire rated assembly Surveillance Test (ST) procedures revealed 10 Unit 1 and Unit 2 fire rated assemblies were omitted and had not been inspected per previous Technical Specifications (TS) requirements and the current Technical Requirements Manual (TRM). An evaluation determined a TS noncompliance occurred between issuance of the facility operating licenses for each unit and 12/20/95. On 12/20/95, the Fire Protection System TS requirements were relocated to the TRM. The above review was prompted when performance of the Unit 2 ST procedure on 02/11/97 identified several fire rated assemblies that were omitted from the Unit 2 ST procedure. The affected ST procedures were revised and inspections of the subject fire rated assemblies were performed. No degradation of the fire rated assemblies were identified. Inadequate reviews of the Architectural (A) drawing A-300 during original development of the ST procedures and during a subsequent review to address a previous event resulted in the incorrect ST procedures. Reviews with verifications of the ST procedures against drawing A-300 will be performed. Any corrective measures are expected to be completed by 06/24/97.
3521997005 | Limerick 1 | 03/11/1997 | 06/09/1997 | 9706170182 | <strong>Two Seperate Reactor Water Clean-up (RWCU) Isolations, Engineered Safety Features, Caused by Lifting of a Filter Demineralizer Pressure Safety Valve.</strong><br /><i>Abstract:&nbsp;</i>On 03/11/97, at 2209 hours and 2310 hours, 2 separate Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuations initiated, Engineered Safety Features, causing Reactor Water Cleanup (RWCU) system isolations. The 2 PCRVICS actuations were initiated by high differential flow conditions. An investigation revealed the high differential flow occurred when the pressure safety valve, PSV-045-1-62B, for 'B' RWCU filter demineralizer lifted. On 03/13/97, the PSV was replaced and the RWCU system was restored. There were no adverse consequences and no radioactive material was released to the environment as a result of this event. The appropriate RWCU filter demineralizer PSVs will be monitored to determine if a generic concern exists. Any findings, including the potential need to replace these PSVs on an established frequency, will be addressed as necessary.
3521997006 | Limerick 1 | 10/26/1984 | 10/17/1997 | 9710280241 | <strong>Previous Condition Prohibited by Tech Specs in that a Fire Protection System Deluge Valve may not have Functioned per Design Since Issuance of the Unit 1 Operating License</strong><br /><i>Abstract:&nbsp;</i>On 07/29/97, Station personnel identified that a Star Model 'D' deluge valve, XV-022-170, did not actuate during performance of a surveillance test (ST). The valve was on increased test frequency due to successive failures resulting from suspected mechanical problems. Compensatory measures were taken to initiate a continuous firewatch for the affected area. Adjustments were made to the valve to optimize mechanical operation. Based on satisfactory test performances, the continuous firewatch was removed. An Engineering evaluation concluded that a voltage mismatch existed between the Star deluge valve and the Chemtron release control panel, resulting in marginal power available to operate the valve. An evaluation identified a Technical Specifications (TS) noncompliance occurred between issuance of the facility operating license for Unit 1 on 10/26/84, and 12/20/95, since valve XV-022-170 may have been unable to perform its TS design function. On 12/20/95, the Fire Protection System TS requirements were relocated to the Technical Requirements Manual. On 09/04/97, the Star Model 'D' 6 inch deluge valve XV-022-170 was replaced with a Star Model 'G' valve which is matched to the Chemtron release panel. Work orders have been generated to replace the remaining 6" Star Model 'D' valves previously contained in TS.
3521997007 | Limerick 1 | 09/10/1997 | 10/09/1997 | 9710150158 | <strong>Isolation of the Reactor Water Clean-up System, an Engineered Safety Feature, Resulting from Lifting of a Filter Demineralizer Pressure Safety Valve Caused By Setpoint Drift.</strong><br /><i>Abstract:&nbsp;</i>On 09/10/97, a Primary Containment and Reactor vessel Isolation Control System (PCRVICS) actuation initiated, an Engineered Safety Feature, causing the Reactor Water Cleanup (RWCU) system to isolate. The PCRVICS actuation was initiated by a high differential flow condition. An investigation revealed the high differential flow occurred when the pressure safety valve, PSV-045-1-62B, for 'B' RWCU filter demineralizer lifted. On 09/11/97, the PSV was removed and pressure tested. The as- found setpoint of the PSV was identified to be 1200 psig. The required setting of the PSV is 1290 psig, +/- 1%. The PSV was adjusted to 1290 psig, +/- 1% and re-installed. The 'B' RWCU system was returned to service on 09/14/97. There were no adverse consequences and no radioactive material was released to the environment as a result of this event. The cause of the low as found pressure setpoint has been concluded to be setpoint drift resulting from low simmer margin and cyclic-partial actuation (simmer). Modifications have been planned to correct the appropriate RWCU PSVs. In the interim, the system procedures have been revised to alert Operations personnel of the potential of high differential flow while pressurizing a filter demineralizer.
3521997008 | Limerick 1, Limerick 2 | 10/26/1984 | 10/15/1997 | 9710200180 | <strong>Failure to Perform Annual Maintenance Inspections of Onsite Portable Fire Extinguishers.</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1997, Fire Protection Group personnel discovered that annual inspection of fire extinguishers had not been performed in accordance with NFPA 10 since initial licensing at Limerick Generating Station (LGS), Units 1 and 2. This constitutes a failure to maintain the provisions of the Fire Protection Program as described in the UFSAR, is a violation of the Facility Operating License Condition 2.C.(3), "Fire Protection," for both Units 1 and 2, and is reportable under License Conditions 2.F and 2.E, for Units 1 and 2 respectively. The annual inspections were completed and any problems were corrected by September 20, 1997. The potential consequences of this event were minimal. The cause of this event was personnel error in that wrong assumptions were made concerning the accountability for conducting the annual fire extinguisher inspections between the site Fire Protection Group and PECO Energy's offsite Fire Shop. The appropriate administrative controls for performing annual portable fire extinguisher inspections will be established.
3521997009 | Limerick 1, Limerick 2 | 10/15/1997 | 11/17/1997 | 9711260199 | <strong>Radiation Monitor was incorrectly Configured Due To Personnel Error and Could Have Prevented the Safety Function of a System Needed to Control Release of Radioactive Material</strong><br /><i>Abstract:&nbsp;</i>On 10/15/97, a contract engineer identified that the 'A' and 'B' Emergency Service Water (ESW) discharge to 'Al Residual Heat Removal Service Water (RHRSW) return header is downstream of the supply line to the 'A' RHRSW radiation monitor. The Updated Final Safety Analysis Report (UFSAR)states that the common RHRSW radiation monitor samples both the ESW and RHRSW systems. This design deficiency created a condition which could have prevented fulfillment of a safety function required to control the release of radioactive material. The actual and potential consequences of this event were minimal. The cause of this event was personnel error resulting from less than adequate review and control of configuration drawings during a 1989 modification. Corrective actions for the event include correction of the design deficiency, an assessment of the Design Change Request process requirements, verification that other radiation monitors are performing their design function, and training on this event.
3521997011 | Limerick 1 | 10/25/1997 | 06/10/1998 | 9806160125 | <strong>HPCI System Rendered Inoperable Due to Closing Turbine Exhaust Line PCIV</strong><br /><i>Abstract:&nbsp;</i>On 10/25/97, the Unit 1 High Pressure Coolant Injection (HPCI) system turbine exhaust line primary containment isolation valve (PCIV) failed to go fully closed during an increased frequency surveillance test. Operations closed and deenergized the valve in accordance with Technical Specifications (TS) requirements for an inoperable Primary Containment Isolation Valve (PCIV). The valve was diagnostically tested with no abnormalities identified, and was returned to service. In January 1998, following subsequent failures of the valve to close, the valve was disassembled and inspected. The cause of the valve failure was mechanical interaction between the valve internal components. The valve was repaired, and other similar valves on Units 1 and 2 were disassembled and inspected with no similar deficiencies identified. There were no actual consequences from this event and the potential consequences were minimal. LER 1-97-011, Rev. 0, pursuant to 10CFR50.73(a)(2)(v), reported a condition that alone could have prevented the fulfillment of the safety function of the HPCI system due to the inoperable turbine exhaust line PCIV. Upon further review of the cause of PCIV failure, we have determined that there was not adequate assurance that the valve would continue to meet its TS required stroke time when restoring the valve to an operable status. Therefore, this revised report is also being submitted pursuant to the requirements of 10CFR50.73(a)(2)(i)(B) for a condition prohibited by TS.
3521997012 | Limerick 1 | 11/20/1997 | 12/19/1997 | 9712300275 | <strong>Unplanned Closure of a Primary Containment Isolation Valve, an ESF, Caused by an Inaccurate Drawing and an Inadequate Partialed Surveillance Test.</strong><br /><i>Abstract:&nbsp;</i>On 11/20/97, Unit 1 Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) relays for secondary containment isolation actuation instrumentation were replaced. To verify operation of the relays, a partialed surveillance test (ST) was performed. During the return to normal section of the ST, Technicians discovered that the Instrument Gas Traversing Incore Probe Purge Primary Containment Isolation Valve had isolated, an unplanned Engineered Safety Feature. An investigation revealed isolation relay B21H-K107D was omitted in the partialed ST. The causes for this omission were an incorrect electrical drawing and an inadequately partialed ST. The incorrect electrical drawing depicted relay B21H-K107D as B21H-K107B. The Technicians incorrectly incorporated this information into the partialed ST. Corrective actions include involvement of a Subject Matter Expert in the review of the remaining PCRVICS relay replacement tests, counseling of the involved individuals, dissemination of the lessons learned from this event to appropriate work groups, and issuance of a change request for the drawing discrepancy. The consequences of this event were minimal and there was no radioactive material released to the environment.
3521997013 | Limerick 1, Limerick 2 | 12/05/1997 | 07/20/1998 | 9807240251 | <strong>Various PCIVs Out of Technical Specification Surveillance and Three Otherwise Inoperable.</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1997, a difference was identified between the control logic diagram and motor control center compartment wiring for the Unit 1 RCIC Steam Supply Inboard Primary Containment Isolation Valve (PCIV). The review concluded that the existing wiring configuration would not ensure that the valve is torque seated when actuated with an automatic isolation signal, as required during accident conditions. The valve was declared inoperable and the appropriate Technical Specification action was taken. A complete review of the control logic for all PCIVs, and selected in-plant inspections, were performed. One other wiring discrepancy was identified. Further review of this issue identified that the subject contact in the closing circuit had not been tested as required by Technical Specification Surveillance 4.6.3.2. A total of 89 automatically closing and 26 remote manually operated PCIVs (on both units combined) that rely on this logic configuration and had not been adequately tested since start-up of each unit were initially identified. A generic review subsequently identified an additional 20 valves with a similar configuration that had not been adequately tested in accordance with Technical Specifications 4.3.3.2 and 4.3.5.2. Actions were taken for the missed surveillance in accordance with Technical Specification 4.0.3. Testing of these contacts was satisfactory, with one exception that was subsequently repaired. There were no actual consequences from this in-plant discrepancy and the potential consequences were minimal. The cause of the two wiring discrepancies was an original construction drawing error. The inadequate test method was caused by personnel error during initial test development and carried through subsequent test reviews. Planned corrective actions include revising identified document deficiencies and revising PCIV surveillance tests.
3521997014 | Limerick 1, Limerick 2 | 12/22/1997 | 01/21/1998 | 9801280289 | <strong>Residual Heat Removal Service Water System Pump Trip On High Rad Signal.</strong><br /><i>Abstract:&nbsp;</i>On 12/22/97, the common plant 'B' Residual Heat Removal Service Water (RHRSW) system pump tripped due to an invalid high high radiation trip signal. This constitutes an Engineered Safety Feature actuation. Subsequent Chemistry sampling of the RHRSW system verified there was no release of radioactive material, and station personnel concluded the pump tripped as a result of a spurious high high radiation signal generated on the 'B' radiation monitor. The 'B' radiation monitor (OBS 578) was declared inoperable and station Chemistry personnel commenced compensatory sampling. The RHRSW high high radiation signal was bypassed and the RHRSW pump was restarted. The consequences of this event were minimal. The causes of this event were 1) degraded condition of a cable for the 'B' radiation monitor, and 2) less than adequate work practices in the vicinity of the degraded cable where a nearby worker bumped the cable. Corrective actions include replacement of the defective cable on the "B" RHRSW radiation monitor, counseling the involved work group, and notifying the station system managers of the generic implications for their systems.
3531997001 | Limerick 2 | 02/07/1997 | 03/10/1997 | 9703180049 | <strong>Condition Prohibited by Technical Specifications in that Control Rods were Removed from the Core with Source Range Monitors inoperable.</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1997, Operators identified that control rod drive and control rod removal were in progress without the Source Range Monitor functions required by Technical Specifications (TS) Section 3.9.10.2, Multiple Control Rod Removal. The Unit 2 Source Range Monitors were rendered inoperable when the 2B reactor protection system uninterruptible power supply electrical bus was de-energized to support planned modification work. The cause of this event was personnel error in that individuals reviewing a planned testing and modification activity overlooked an applicable TS Section and did not identify the impact of SRM inoperability on control rod removal. The consequences of this event were minimal in that administrative controls, design features and protective functions maintained adequate shutdown margin throughout the event. Corrective actions for this event include additional pre-outage training and evaluation of a change to the applicable TS Section.
3531997002 | Limerick 2 | 02/12/1997 | 03/14/1997 | 9703190105 | <strong>N12B, 2" RPV Instrument Nozzle Safe End Leak</strong><br /><i>Abstract:&nbsp;</i>On 2/11/97, Unit 2 was in refueling condition and In-service Inspection (ISI) activities were in progress. At 1000 hours, leakage (< 1 drop per minute) was observed from a 2' reactor pressure vessel (RPV) instrument penetration. The observed leakage was from the nozzle safe end and was an unisolable portion of the reactor coolant system pressure boundary. The associated RPV instrumentation was declared inoperable pending evaluation of the as found condition and reactor coolant temperature was maintained below 120 degrees F in accordance with the action statement of Technical Specification Section 3.4.8. No release of radioactive material was involved. Sufficient safety systems were operable to satisfy Technical Specification requirements. The leak was determined to be from a 0.2 inch axial crack in the heat-effected zone of the instrument line to nozzle safe end connection. The cause of the crack was determined to be improper original installation. The instrument line was welded into the nozzle at an approximate 6 degree angle from true center. This misorientation caused extreme localized stresses that ultimately caused the crack. The flawed portion of the connection was removed and sent off-site for analysis, and replaced prior to unit startup. A review of the Pre-Service Inspection and ISI data for all RPV instrument nozzles on both units was performed. Additional inspections were performed and are planned for the next Unit 1 refueling outage.
3531997003 | Limerick 2 | 04/29/1997 | 05/28/1997 | 9706030077 | <strong>Corrosion Induced Bonding Results in Several Main Steam System Safety Relief Valves Having Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On 04/29/97, Station Engineering was informed that as-found test results for 11 of 14 Main Steam Safety Relief Valves (SRVs) did not meet the 1% setpoint tolerance of Technical Specification 3.4.2. These results were for 11 SRVs replaced during the fourth Unit 2 refueling outage (2R04) in February 1997, and for 3 SRVs replaced during the 19th Unit 2 maintenance outage (2M19) in December 1996. The performance of these SRVs for Unit 2 Cycle 4 resulted in a condition where a common cause resulted in more than 2 independent trains in a single safety system becoming inoperable. The consequences were minimal since there was only minimal challenge to the reactor overpressure protection system. Fourteen SRV pilot valves were replaced with calibrated spares during 2R04 and 2M19. The SRVs are Target Rock Corporation Model 7567F pilot operated 2 stage valves. The cause of the setpoint drift was corrosion induced bonding between the pilot disc and seat. Seven of the 14 pilot valves during cycle 4 contained platinum pilot discs recommended by the BWR Owners Group. Performance of the platinum pilots was no better than the standard stellite pilot discs since 5 of 7 SRVs with platinum discs exceeded the required setpoint tolerance. PECO Energy is in the process of evaluating alternative SRV designs.
3531997004 | Limerick 2 | 03/16/1993 | 07/07/1997 | 9707230014 | <strong>Offgas System Grab Sample Obtained Late</strong><br /><i>Abstract:&nbsp;</i>On 03/16/93, a compensatory grab sample of the Unit 2 offgas system for hydrogen analysis was not obtained within the four (4) hour sample interval required by Technical Specification (TS) 3.3.7.12, ACTION 110. The assigned Chemistry technician obtained the sample thirty-four (34) minutes past the required sample time. The sample was analyzed within the following four (4) hours in accordance with the TS. The cause of the event was a personnel error. A review on June 5, 1997 determined that this event is reportable under 10CFR50.73 (a)(2)(I)(B) as a condition prohibited by the TS. Corrective actions taken subsequent to this event and reported in LER 1-96-005 have been implemented to prevent a similar occurrence.
3531997005 | Limerick 2 | 06/05/1997 | 07/03/1997 | 9707230021 | <strong>Facility Operating License Thermal Power Limit Exceeded Due to EHC Malfunction</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1997, a Unit 2 Electrohydraulic Control (EHC) system malfunction caused a brief reactor pressure transient. The reactor pressure transient caused core thermal power to reach 102.4%, exceeding the core thermal power limit specified in Facility Operating License NPF-85 Condition 2.C.1. Equipment response to this transient was as designed. The operators responded by reducing power to a nominal 25% power, within bypass capacity, to facilitate troubleshooting. The cause of the EHC system transient has not yet been determined. Monitoring equipment was installed on the EHC system to provide information if a similar transient occurs. Monitoring equipment was also installed to detect the source of a Balance of Plant DC system ground which has been occurring intermittently and may be associated with the EHC malfunction. Consultants were brought in and other Stations with similar EHC equipment were contacted to independently assess the EHC transient, actions taken, and to identify other industry experience.
3531997006 | Limerick 2 | 06/11/1997 | 07/09/1997 | 9707160033 | <strong>Automatic Closures of the Reactor Core Isolation Cooling Steam Supply Primary Containment Isolation Valves, an ESF, Caused by Personnel Error During Restoration of a Clearance.</strong><br /><i>Abstract:&nbsp;</i>On 06/11/97, a Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) actuation initiated, an Engineered Safety Feature (ESF), causing the Reactor Core Isolation Cooling (RCIC) system steam supply line inboard and outboard Primary Containment Isolation Valves (PCIVs) to close. During restoration of the RCIC system from maintenance, the steam supply line outboard PCIV was opened out of sequence. This supplied reactor steam to the depressurized RCIC steam lines, and a high steam line flow isolation signal was initiated. An inspection of the RCIC system was performed and no abnormalities were identified. The isolation was reset and the RCIC system was restored. The cause of this event was personnel error in that a Reactor Operator (RO) restoring RCIC in the Main Control Room (MCR) failed to perform an added step in the clearance to warm the steam lines prior to opening the outboard PCIV. The following factors also contributed to the cause of the event. The RO performing the MCR restoration activities was not the original individual assigned the restoration tasks. Also, the RO did not obtain a pre-job briefing and failed to adequately familiarize himself with the restoration activities and the procedures involved prior to performing the clearance. Corrective actions included counseling of the involved individuals and issuing a briefing sheet on this event to all Operations personnel.
3531997007 | Limerick 2 | 06/23/1997 | 07/23/1997 | 9707300068 | <strong>Unit 2 HPCI System Inoperable Due to Clogged Turbine Exhaust Drain Line.</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1997, during the performance of RT-6-055-380-2, "HPCI Drain Pot Flow Orifice Test," flow from the turbine exhaust drain pot could not be confirmed. Given this situation, an undetermined amount of condensed water was present in the High Pressure Coolant Injection (HPCI) turbine. The HPCI System was declared inoperable, because the water in the turbine may impair the ability of the system to fulfill its design safety function. A four-hour notification was made to the NRC in accordance with 10CFR50.72(b)(2)(iii)(D). Corrective maintenance on the HPCI turbine exhaust drain pot drain line identified the cause as foreign material in the drain line flow orifice. A similar event to this occurred in 1989, which in part, led to the creation of the routine test (RT) that identified this 1997 problem. Additional planned corrective actions include: evaluation of turbine maintenance activities to ensure appropriate foreign material exclusion (FME) practices are specified, evaluation of the HPCI System for increased monitoring in accordance with Limerick's Maintenance Rule Program, communication of this event to appropriate personnel, and a review of FME Program enhancements in progress to ensure that this situation is addressed by planned actions. This report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(v).
3531997008 | Limerick 2 | 07/26/1997 | 08/25/1997 | 9709020308 | <strong>Automatic Closure of Drywell Chilled Water System Primary Containment Isolation Valves, An ESF Actuation, Resulting From Emergency Diesel Generator Voltage Regulation Failure.</strong><br /><i>Abstract:&nbsp;</i>On 07/26/97, with Unit 2 at 100 % power, Special Test SP-178 "D21 Diesel Generator Governor Test" was being performed as a post-maintenance test. During performance of the test, the 2A Residual Heat Removal pump was loaded to the D21 4KV Safeguard Bus while the D21 Emergency Diesel Generator (EDG) was supplying power to the bus in the isochronous mode. In response to this test step, the bus voltage dropped momentarily and then rose above its normal set point of 4160 VAC to 5118 VAC. In response to the overvoltage condition, the main control room operator opened the EDG output breaker. The breaker reclosed twice before being successfully secured open. Numerous equipment anomalies resulted from the voltage transient, including the isolation of Drywell Chilled Water System primary containment isolation valves. This isolation was caused by a failed Agastat relay in the control logic, caused by the overvoltage condition. No release of radioactive material was involved. Plant operation continued within Technical Specification (TS) requirements and in accordance with existing plant procedures. The overvoltage condition was caused by a rectifier bank failure in the D21 EDG voltage regulation circuit. Corrective actions included replacing the failed relay, swapping to an alternate rectifier bank on the EDG, and planned failure analysis of the rectifier bank. This LER is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(iv) for the DWCS valve closure, an Engineered Safety Feature actuation. Additionally, this LER is being utilized to address the Special Report required for the EDG valid test failure per the requirements of TS Section 6.9.2 as required by TS Surveillance Requirement 4.8.1.1.3.
3531997009 | Limerick 2 | 08/06/1997 | 09/05/1997 | 9709090135 | <strong>Unit 2 Reactor Water Clean-up (RWCU) Isolation, An ESF, Caused by a RWCU Filter Demineralizer Y-Strainer Manual Drain Valves Leaking INto the Backwash Receiving Tank</strong><br /><i>Abstract:&nbsp;</i>ABSTRACT: On 08/06/97, a Primary Containment and Reactor Vessel Isolation Control System (PCRIVCS) actuation initiated, an Engineered Safety Feature, causing the Unit 2 Reactor Water Cleanup (RWCU) system to isolate. The PCRIVCS actuation was initiated by a high differential flow condition while restoring a filter demineralizer to service. The high differential flow condition was caused by the `B' RWCU filter demineralizer Y-strainer manual drain valves leaking into the backwash receiving tank. The affected valves were adjusted, and on 08/07/97, the filter demineralizer was returned to service. No problems exist with similar RWCU valves. There were no adverse consequences as a result of this event. In addition, several factors that could have provided an opportunity to mitigate this event were identified. These include ineffective communication between the Main Control Room and the local operator, an unusual flow noise, and the fact that the operator had infrequently performed this task. Corrective measures involve procedure enhancements, establishment of communication during RWCU system alignments, and training. END OF ABSTRACT
3531997010 | Limerick 2 | 11/07/1997 | 12/08/1997 | 9712150391 | <strong>Noncompliance with Technical Specifications Surveillance Requirement 4.4.6.1.4 Due to Failure to Perform a First Cycle Analysis of a Reactor Flux Wire Specimen.</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1997, it was determined that the Limerick Generating Station (LGS), Unit 2, reactor vessel flux wire specimen analysis had not been performed in accordance with Technical Specifications (TS) Surveillance Requirement (SR) 4.4.6.1.4. This SR requires that the reactor flux wire specimen be removed at the first refueling outage and examined to determine reactor pressure vessel fluence. The cause of this event was an incomplete surveillance test (ST) procedure. The ST procedure that was generated to satisfy the TS SR required that work requests be initiated to remove the flux wire specimen from the reactor vessel and to perform the neutron fluence analysis. However, the procedure did not provide for documenting completion of the analysis, and any resulting changes to the TS, as required, to ensure that the TS SR requirements were satisfactorily completed. An Engineering evaluation has been performed, including a 10CFR50.59 Review, which concluded that the LGS, Unit 2, reactor vessel predicted fluence is conservative as calculated in accordance with the methodology provided in Regulatory Guide 1.99, "Radiation Embrittlement of Reactor Vessel Materials," Rev. 2.
3541997001 | Hope Creek | 01/03/1997 | 02/03/1997 | 9702180233 | <strong>Emergency Diesel Generator and Fire Suppression System Interaction Results In The Plant Being In a Condition Outside of the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On January 3, 1997 at 1958 hours, during a design review of the interface between the Emergency Diesel Generator (EDG) Room Fire Suppression System logic and the EDG Room Ventilation System logic, a common mode failure potential was discovered. As a result, all four EDGs were declared inoperable and Technical Specification Limiting Condition of Operation 3.0.3 was entered. A one hour report was made to the NRC in accordance with the requirements of 10CFR50.72(b)(1)(ii)(B) to report the condition as any event or condition during operation that results in the condition of the nuclear power plant being in a condition that is outside the design basis of the plant. A temporary modification to limit the interface between the systems was immediately implemented. Compensatory actions were taken in accordance with the Fire Protection Program. No reactor power reduction was necessary. The cause of this event is attributed to inadequate analysis to support the approved exception to the Standard Review Plan as described in Section 9.5.1.6.30 of the Hope Creek Updated Final Safety Analysis Report. Human performance issues contributed to the delayed identification of this problem. A design change to implement a permanent correction to the design deficiency is under review.
3541997002 | Hope Creek | 01/17/1997 | 02/14/1997 | 9702210119 | <strong>Inconsistency Between Filtration, Recirculation, and Ventilation System Technical Specifications and the Ability to Withstand Prescribed Single Failures Under Design Basis Conditions</strong><br /><i>Abstract:&nbsp;</i>On January 17, 1997, an inconsistency between Technical Specifications (TS) and design basis documents for the Filtration, Recirculation, and Ventilation System (FRVS) was discovered. The Recirculation subsystem of FRVS consists of six units with 25% capacity fans. Four of the six units are credited in the design basis for post accident conditions. A recently completed 10CFR50.59 safety evaluation revealed that the current TS does not assure that the design requirements of FRVS are maintained. Since TS 3.6.5.3.2 only requires five of the six units to be operable, the sixth unit could be (and has been) unavailable for indefinite amounts of time. Given that the sixth unit was allowed to be unavailable, the system may not have met its design basis under specific circumstances. <br /><br /> The apparent cause of the inconsistency was the failure to consider the postulated single failures when developing the FRVS TS during the initial licensing phase. The unique design of FRVS compared to other Boiling Water Reactor plants was a contributor. There were no actual safety consequences associated with this condition. Potential safety consequences consisted of a slight reduction in the margins used within design calculations. Corrective actions include administrative controls to prevent unlimited unavailability of the sixth unit and the submittal of a TS amendment request to include the sixth unit.
3541997003 | Hope Creek | 02/04/1997 | 03/06/1997 | 9703110123 | <strong>Unplanned Reactor Core Isolation Cooling System Inoperability Due to an Inservice Test Failure of the Turbine Steam Exhaust Containment Isolation valve</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1997 at 1942 hours, the Reactor Core Isolation Cooling (RCIC) System was declared inoperable due to an inservice test (IST) failure of the turbine steam exhaust containment isolation check valve, 1FCV-003. A 14 day Limiting Condition for Operation was entered in accordance with Technical Specification 3.7.4. A four hour report was made to the NRC in accordance with 10CFR50.72(b)(2)(iii)(D), to report the unplanned inoperability of a single train safety system as an event or condition that alone could have prevented the fulfillment of a safety function. The cause of this occurrence was failure of the valve test lever to provide proper valve position indication. A design change implemented in 1989 did not adequately implement requirements to drill the test lever hinge pin to the proper depth to accept the cam set screw. This allowed the testing cam to rotate on the hinge pin. The failure of the set screw to retain the testing cam in place on the hinge pin rendered the valve untestable but did not result in a functional failure of the valve. The valve was inspected and the cam was restored to the correct position. The valve IST was performed satisfactorily on February 5, 1997 at 2342 hours and the RCIC system was declared operable. To ensure future testability of the valve, the test Lever hinge pin will be reworked prior to the next 1FCV-003 IST.
3541997004 | Hope Creek | 02/07/1997 | 03/10/1997 | 9703170180 | <strong>B Division Primary Containment Isolation Due to Personnel Error During Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1997, during the performance of a radiation monitoring system channel calibration, an annunciator failed to clear as prescribed by procedure. During investigation into the cause of the inconsistency, a technician using a Digital Multi-Meter (DMM) to verify the channel status, made contact with the wrong terminal point. As a result, at 2016 hours, a 'B' Division Primary Containment Isolation System (PCIS) isolation occurred. The cause was determined, the isolation was reset, and the effected components were restored at 2129 hours. The effected components performed as designed. A four hour event notification was made to the NRC at 2235 hours pursuant to 10CFR50.72(b)(2)(ii). <br /><br /> The cause of the event was personnel error. The cause of the original annunciator problem was the failure of an optical isolator. Corrective actions include: communications of lessons learned, personnel disciplinary actions, implementation of guidance on relay contact verification and the use of DMMs, replacement of the optical isolator, and successful completion of the channel calibration. There were no actual safety consequences associated with this event.
3541997005 | Hope Creek | 04/07/1994 | 04/25/1997 | 9705050051 | <strong>Operation in a TS Prohibited Condition Due to Failure to Perform Monthly Flowpath Verification Surveillance Checks of Residual Heat Removal System Crosstie Valves.</strong><br /><i>Abstract:&nbsp;</i>As a result of recent reviews of a safety evaluation for an April 1994 Residual Heat Removal (RHR) system design change, a Technical Specification (TS) surveillance test deficiency was identified. The design change added a crosstie line with two valves installed between the discharge of the 'A' and 'C' RHR pumps. Neither of the two valves were required to be maintained locked closed, therefore, the monthly Emergency Core Cooling Systems (ECCS) flow path verification requirements of TS 4.5.1.a.1.b should have been made applicable, but were not. This resulted in operation in a TS prohibited condition and is being reported pursuant to 10CFR50.73(a)(2)(i)(B). This condition was corrected on December 22, 1995, when a normally closed crosstie valve was locked closed. <br /><br /> The cause of this deficiency was the failure to identify the needed surveillance procedure revision during the 10CFR50.59 safety evaluation and the design change review process. Personnel errors and review process failures led to this deficiency. Corrective actions include a separate evaluation of 10CFR50.59 and engineering performance issues, previous enhancements to the safety evaluation and design change processes, a design basis review of ECCS systems associated with 10CFR50.54(f), disciplinary action, and a re-assessment of the safety evaluation conclusions. There were no safety consequences associated with this deficiency.
3541997006 | Hope Creek | 03/22/1997 | 04/21/1997 | 9704280085 | <strong>High Pressure Coolant Injection Isolation Due to Personnel Error During Performance of Functional Test</strong><br /><i>Abstract:&nbsp;</i>On March 22, 1997, during the performance of a scheduled functional test of the Nuclear Boiler Division 1 High Drywell Pressure Instrumentation, a technician using a Digital Multi-Meter (DMM) to verify contact status, made contact with the wrong test points. As a result, at 0504 hours, an actuation of an Engineered Safety Feature system occurred when the High Pressure Coolant Injection (HPCI) system turbine steam supply outboard primary containment isolation valve closed. The HPCI system was declared inoperable. The isolation was reset, and a series of functional tests were then performed satisfactorily. Initial investigation indicated that the cause was personnel error. Satisfactory completion of the functional tests and the initial investigation indicating personnel error resulted in reasonable assurance of operability of the HPCI system. The HPCI system was declared operable at 0150 hours on March 24, 1997. The effected components performed as designed. A four hour event notification was made to the NRC at 0555 hours pursuant to 10CFR50.72(b)(2)(ii). <br /><br /> The cause of the event was personnel error. Corrective actions include: communication of lessons learned, personnel disciplinary actions, implementation of guidance on relay contact verification and the use of DMMs, and successful completion of the functional test. There were no safety consequences associated with this event.
3541997007 | Hope Creek | 04/07/1997 | 05/07/1997 | 9705140420 | <strong>Struthers-Dunn 219NE Series Relay Failures Due to Thermal Degradation of Magnetic Vinyl Plastic Bearing Pad Material</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1997, Public Service Electric & Gas Co. (PSE&G) completed its evaluation of an increase in the failure rate of Struthers-Dunn 219NE series relays with 120 VAC and 24 VAC coils and concluded that the failures were due to the use of magnetic vinyl plastic for the bearing pad material in normally energized relays. Based upon the extent of the condition, PSE&G concluded that, if undiscovered, it could have caused one or more safety systems to fail to perform their intended function. A four hour notification was made to the NRC at 1848 on April 7, 1997, pursuant to 10CFR50.72(b)(2)(iii). This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(v) and 10 CFR 21. The apparent cause of the high failure rate was thermal degradation of the magnetic vinyl plastic bearing pad material in Struthers-Dunn 219NE series 24 VAC and 120 VAC relays. Panels containing the degraded relays are being inspected weekly to assure continued operability until the relays are replaced. The degraded relays will be replaced before the end of Hope Creek's seventh refueling outage. There were no actual safety consequences associated with this condition. There was no impact on public health and safety.
3541997008 | Hope Creek | 05/20/1997 | 06/19/1997 | 9706250169 | <strong>Engineered Safety Feature Actuation: "C" Service Water Pump Auto-Start</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1997, at 1700, a Nuclear Controls Operator (NCO - licensed reactor operator) removed the "C" Service Water Pump from service in accordance with the system operating procedure while the "A" Service Water Pump was running in manual. Three seconds after the "C" Service Water Pump was stopped, the pump automatically restarted. The auto start signal originated from a low flow signal on the "A" Service Water Pump. At 1707, the "C" Service Water Pump was placed in manual and successfully removed from service. All other plant equipment responded as expected. On May 20, 1997, at 2052, a four hour notification was made in accordance with 10CFR50.72(b)(2)(ii). The apparent cause of this event was silt accumulation combined with a hydraulic perturbation that caused the transmitter to sense a low differential pressure across the "A" strainer, and provide an auto-start signal to the "C" Service Water Pump. The safety consequences associated with this event were minimal. Corrective actions include back-flushing the sensing lines, changing recurring task frequencies and evaluating potential design improvements or procedure enhancements. This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an event or condition that resulted in an Engineered Safety Feature actuation.
3541997009 | Hope Creek | 05/28/1997 | 06/27/1997 | 9707030320 | <strong>Unplanned HPCI Inoperability due to Minimum Flow Bypass Valve Failure Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>During a High Pressure Coolant Injection (HPCI) pump surveillance test at approximately 1151 on May 28, 1997, the minimum flow bypass valve (1BJHV- F012) failed to close as expected when flow exceeded the minimum flow setpoint. The HPCI pump was secured and the minimum flow bypass valve was observed to close automatically. The HPCI system was declared inoperable at 1251 and a 14 day Limiting Condition for Operation (LCO) was entered pursuant to TS 3.5.1. A four hour notification was made at 1435 pursuant to 10 CFR 50.72(b)(2)(iii) for the inoperability of the single train safety system. Troubleshooting found the minimum flow transmitter isolated and the equalizing valve open. The transmitter was restored to service and the HPCI system was tested to demonstrate proper operation of the minimum flow bypass valve. This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(v) and 10 CFR 50.73(a)(2)(i)(B). The cause of this event was personnel error. The isolated flow transmitter was returned to service. There were no actual safety consequences associated with this condition. There was no impact on public health and safety.
3541997010 | Hope Creek | 05/27/1997 | 06/25/1997 | 9707070155 | <strong>Special Report - Overpower Event Due to Loss of Feedwater Heaters</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1997, at 1136, an electrical failure caused a trip of the "C" feedwater heater string, which resulted in a feedwater temperature decrease and in an unplanned reactor power increase. Reactor power reached 105% for several seconds before the operators manually reduced power to 80% using recirculation flow and control rod insertion. All other plant equipment responded as expected. The operators effectively responded to this unplanned power transient. Reactor power was returned to 100% at 0229 on May 28, 1997. On May 28, 1997, at 1030, a twenty-four hour notification was made to report operation outside of License Condition 2.C(1), which authorizes PSE&G to operate at reactor core power levels not in excess of 3293 megawatts thermal (100% rated power). This event is being reported as a Special Report in accordance with the requirements of License Condition 2.F. The electrical failure that caused the "C" feedwater heater string to trip was caused by a failed power factor module circuit card in an Uninterruptible Power Supply (UPS) inverter. Corrective actions include the replacement of the failed card, failure analysis, and trending.
3541997011 | Hope Creek | 06/02/1997 | 07/03/1997 | 9707140216 | <strong>Technical Specification Prohibited Condition - Failure To Complete Flood Protection Actions Within Required Timeframe</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1997, the Hope Creek Generating Station was in operational Condition 1 (POWER OPERATION). At 2039 hours, the Delaware River water level reached 95 feet (6.0 feet above Mean Sea Level). At this river water level, Technical Specification Action Statement 3.7.3.a.1, requires that, "with the water level at the service water intake structure above 95 feet, initiate and complete the closing of all service water intake structure watertight perimeter flood doors identified in Table 3.7.3-1 within 1 hour." By 2135 hours, all service water intake structure watertight doors were closed in compliance with the Technical Specification ACTION Statement. At 2321 hours, the river water level dropped below 95 feet and the watertight doors were no longer required to be closed in accordance with the Technical Specifications. On June 3, 1997, at 0105 hours, operators were re-opening the watertight doors and observed that the inflatable door seals for watertight door #4 were deflated due to small leaks in the fittings of the seal air supply system. Corrective actions were initiated to resolve the SSWS watertight door #4 equipment problems and restore the watertight door to a fully operable status. There were no safety consequences associated with this event.
3541997012 | Hope Creek | 06/13/1997 | 07/11/1997 | 9707180047 | <strong>Engineered Safety Feature Actuation: "Single Rod Scram"</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1997, at 2156, during the weekly Reactor Protection System (RPS) manual scram testing required by the plant Technical Specifications, a single control rod scrammed. Specifically, Control Rod 26-27 scrammed from a full out position (Position 48) to a full in position (Position 00) when a "B1" RPS channel manual scram was inserted. The expected response was a "B" channel half scram and the single rod scram was unexpected. Expected alarms from a single rod scram were received and no thermal limits were exceeded. All other control rods were verified to be in their pre-trip condition. Plant power decreased approximately 3% as a result of the rod insertion. On June 13, 1997, at 2347, a four hour notification was made in accordance with 10CFR50.72(b)(2)(ii). The cause of the scram was a failed open "A" RPS fuse (located in the HCU) supplying power to the "A" side scram solenoid for Control Rod 26-27. The safety consequences associated with this event were negligible. Corrective actions taken included replacing the fuse and retesting the "B1" RPS channel logic. This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an event or condition that resulted in an Engineered Safety Feature actuation.
3541997013 | Hope Creek | 06/18/1997 | 10/01/1997 | 9710100195 | <strong>Unplanned High Pressure Coolant Injection Inoperability</strong><br /><i>Abstract:&nbsp;</i>This supplement is being provided to include additional details. The original event was reported due to the inoperability of the High Pressure Coolant Injection (HPCI) system. HPCI was declared inoperable on 6/18/97 due to concerns regarding limit switches on a HPCI injection valve. Because the issue with the HPCI system had first been identified on 6/16/97, the Action Statement related to the Limiting Condition for Operation was conservatively backdated to 0330 on 6/16/97. For a period of time on 6/17 and 6/18, HPCI was technically inoperable in conjunction with "A" and "C" Residual Heat Removal (RHR) outages. The HPCI inoperability was attributed to equipment failure. The failure to enter Technical Specification 3.0.3 was attributed to a lack of recognition that HPCI was inoperable. Corrective actions for this event include satisfactorily completing maintenance on the affected HPCI injection valve, a review for procedural enhancements, and development of case studies. A four-hour notification was made on 6/18/97, at 2230 pursuant to 10CFR50.72(b)(2)(iii) for the unplanned inoperability of a single train safety system (HPCI). This event is being reported pursuant to 10CFR50.73(a)(2)(v) as an event or condition that alone could have prevented the fulfillment of a safety function and 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3541997014 | Hope Creek | 07/08/1997 | 07/31/1997 | 9708060176 | <strong>Technical Specification Prohibited Condition-Failure To Complete Offsite Power Distribution Line Up Within Required Time Frame</strong><br /><i>Abstract:&nbsp;</i>At 1039 hours on July 8, 1997, during performance of the monthly Emergency Diesel Generator (EDG) Surveillance Test, the 'A' EDG keyswitch was taken to the 'maintenance' position in accordance with procedure HC.OP-ST.KJ-0001 (Q) to support pre-start barring requirements. The 'A' EDG is inoperable when its keyswitch is in the 'maintenance' position because the EDG cannot start in response to automatic initiation signals. At this time, the on-shift Licensed Operators did not recognize that Technical Specification Action Statement (TSAS) 3.8.1.1.b required an electrical distribution line up to be completed within one hour. At 1200 hours, the 'A' EDG keyswitch was removed from the 'maintenance' position and returned to the 'remote' position, restoring operability of the 'Al EDG. At 1750 hours, non-compliance with TSAS 3.8.1.1.b was identified through the oncoming shifts, questioning attitude. The action to comply with TSAS 3.8.1.1.b was immediately initiated and completed satisfactorily at 1758 hours. The cause of the failure to comply with TSAS 3.8.1.1.b for an inoperable EDG was personnel error. Disciplinary actions have been implemented. There were no safety consequences associated with this condition. This condition is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant Technical Specifications.
3541997015 | Hope Creek | 07/08/1997 | 07/31/1997 | 9708060185 | <strong>Radioactive Effluent Samples Not Analyzed Within Required Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1997, Hope Creek Chemistry determined that Technical Specification 4.11.1.1.1 was routinely not being met. The composite samples were not being analyzed within the required monthly frequency. Technical Specification Surveillance Requirement 4.11.1.1.1 states that radioactive liquid wastes shall be sampled and analyzed according to the sampling and analysis program of Table 4.11.1.1.1-1. The table indicates that a monthly composite sample be analyzed for gross alpha on a monthly frequency. The cause of this event is attributed to an incorrect interpretation of the Technical Specification surveillance requirements by Chemistry personnel. As a result, the samples were not being sent to the vendor in an expeditious manner. Corrective actions include training, an increased sensitivity to the Technical Specification requirements, and an improved method to handle the subject samples. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
3541997016 | Hope Creek | 07/16/1997 | 01/06/1999 | 9901060131 | <strong>Filtration Recirculation and Ventilation System Technical Specification Surveillance Requirement Compliance</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1997, Hope Creek received notification from the NRC, via Hope Creek Technical Specification (TS) Amendment No. 99, dated July 9, 1997, that the NRC considered that the monthly Filtration Recirculation and Ventilation System (FRVS) recirculation unit surveillance was being performed in a manner that did not provide compliance with Hope Creek's UFSAR commitments to USNRC Reg. Guide 1.52. As a result, the FRVS recirculation units were considered to be inoperable, and the provisions of TS 4.0.3 were utilized to delay the Shutdown Action requirements for 24 hours due to this missed surveillance. To restore operability to the FRVS units, Hope Creek revised the licensing basis commitments to USNRC Regulatory Guide 1.52 and submitted a TS change request to the NRC to justify modulating heater operation for this surveillance test. On December 7, 1998, the NRC informed PSE&G that proposed changes could not be approved. As a result, the Hope Creek FRVS testing methodology implemented since 1991 did not satisfy TS 4.6.5.3.1.b and 4.6.5.3.2.b requirements. Corrective actions included revisions to the FRVS surveillance procedures, UFSAR changes and the withdrawal of the associated TS change request.
3541997017 | Hope Creek | 07/31/1997 | 08/28/1997 | 9709100117 | <strong>Violation of License Condition - Missed Emergency Lighting Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 7/31/97, PSE&G personnel confirmed that the battery powered emergency lighting 8 hour functional test had not been performed since 11/94. At 1730, the Hope Creek Control Room was notified of the missed functional test. UFSAR Section 9.5.3.2.2, Emergency Lighting, requires this test to be performed every 18 months; therefore, this test should have been performed by 6/96. Testing of the emergency lights was initiated on 8/1/97. Approximately 43% of the units did not remain lit for the entire 8 hours. The cause of the missed surveillance test was a programmatic breakdown in the implementation of the fire protection surveillance schedule. The cause of the failure of a large number of the lights during testing was an inadequate preventive maintenance program with inadequate program management contributing to the event. Corrective actions taken included implementing temporary compensatory measures and completing testing of the Appendix R emergency lights. Planned corrective actions include replacing the batteries for Appendix R emergency lights, including fire protection surveillances in the normal surveillance scheduling process, analyzing the failure data, defining appropriate test requirements, and modifying the preventive maintenance program to address the identified weaknesses and to incorporate the defined test requirements.
3541997019 | Hope Creek | 08/07/1997 | 09/17/1997 | 9709240038 | <strong>Engineered Safety Feature Actuation - Closure of the "B" Safety Auxiliaries Cooling System to Turbine Auxiliaries Cooling System Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On 8/7/97, at 0317, Hope Creek operations swapped the Turbine Auxiliaries Cooling System (TACS) from the "A" loop of Safety Auxiliaries Cooling System (SACS) to the "B" loop. At 0334, the "C" SACS Pump automatically started in response to a low flow signal to TACS. The low flow signal was caused by the spurious closure of the "B" SACS to TACS supply isolation valve. The low flow signal resulted in the automatic start of the "C" SACS pump and the initiation of an automatic TACS transfer back to the "A" SACS loop. All plant equipment responded to the low flow signal as expected. On 9/4/97, at 1703, the "B" SACS to TACS supply and return isolation valves automatically closed in response to a spurious Low Low Low SACS Expansion Tank level signal. The Fuel Pool Cooling Pump tripped at the same time; all other plant equipment responded as expected. The cause of these events was a loose fuse clip in the 1E Analog Cabinet, which provides inputs to the Digital Logic Control System. The corrective action was to replace the fuse clip. On 8/7/97, at 0643, and on 9/4/97, at 1703, four hour notifications were made in accordance with 10CFR50.72(b)(2)(ii). These events are being reported pursuant to 10CFR50.73(a)(2)(iv) as events that resulted in actuations of an Engineered Safety Feature.
3541997020 | Hope Creek | 08/28/1997 | 09/27/1997 | 9710080023 | <strong>Past Inoperability of the Safety Related Chillers due to Operation with Low Safety Auxiliaries Cooling System Temperature</strong><br /><i>Abstract:&nbsp;</i>During a review of the Safety Auxiliaries Cooling System (SACS) design basis, PSE&G identified a potential design deficiency associated with the safety related Control Area Chilled Water System chiller units that could have prevented the fulfillment of a safety function. In the event of an accident resulting in a loss of instrument air, concurrent with low Ultimate Heat Sink temperature, all of the safety related chillers could trip. The chillers are operable when the Ultimate Heat Sink temperature is at least 55 degrees F. PSE&G is evaluating actions to correct the condition as part of its corrective action program. The cause of this event was human error in the original design and in subsequent design reviews. Corrective actions include an operability determination, revising the engineering evaluation, and evaluating and implementing a design change. On 8/28/97, at 1311, a four hour notification was made in accordance with 10CFR50.72(b)(2)(iii). This event is being reported pursuant to 10CFR50.73(a)(2)(v) as a condition that alone could have prevented the fulfillment of a safety function of systems needed to mitigate the consequences of an accident.
3541997021 | Hope Creek | 08/21/1997 | 09/22/1997 | 9709290092 | <strong>Standby Liquid Control System Tank Concentration Below Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1997, at approximately 1145 hours, a monthly sample of the Standby Liquid Control (SLC) storage tank concentration and sodium pentaborate weight, required by Technical Specification (TS) 4.1.5.b.2, indicated 13.42% (weight percent) SLC concentration (equivalent to approximately 5633 pounds of available sodium pentaborate). As a result, Action Statement a.2 of LCO 3.1.5 was entered for the inoperability of both SLC subsystems. At 1415 hours, a second set of samples confirmed the low SLC concentration. At 2116 hours, with the SLC concentration back into compliance with the TS requirements through the addition of sodium pentaborate, both SLC subsystems were declared operable and Action Statement a.2 of LCO 3.1.5 was exited. The cause of the event was attributed to leaking valves in the demineralized water system and removal of sodium pentaborate during SLC pump tests, which diluted the SLC concentration in the storage tank. Corrective actions include the repair of the leaking valves and enhanced monitoring of SLC concentration in the storage tank until the valve repairs are completed. This event is reported under the provisions of 50.73(a)(2)(v) since the low SLC concentration was a condition alone that could have prevented the ability of a system needed to shutdown the reactor and maintain it in a safe shutdown condition.
3541997022 | Hope Creek | 09/10/1997 | 10/06/1997 | 9710150009 | <strong>Engineered Safety Feature Actuatjion - Unplanned Manual Scram following a Relay Malfunctjion in the "A" Phase Main Generator Step-Up Transformer</strong><br /><i>Abstract:&nbsp;</i>On 9/10/97, at 1033, a Main Transformer Trouble alarm was received in the Control Room. Equipment operators were dispatched to investigate and to determine the source of the alarm. The operators discovered the cooling fans and oil pumps on the "A" Phase Main Generator Step-Up Transformer were not operating, heard "popping" noises, and noticed a smell coming from the transformer. This information was relayed to the Control Room. Operations initiated a reactor recirculation pump runback that lowered reactor power level to 38%. At 1040, a manual scram was initiated using the mode switch. At 1041, the main generator was manually tripped. All control rods were verified to be inserted and all systems responded as expected. The loss of cooling was due to a failed relay in the transformer's control panel, which caused the oil pumps and cooling fans to trip. The apparent cause of the failed relay was internal coil heating that caused the coil temperature to exceed the capacity of the insulation. Corrective actions include replacing the relay in the "A", "B", and "C" transformers and considering preventive maintenance. on 9/10/97, at 1344, a four hour notification was made to the NRC in accordance with 10CFR50.72(b)(2)(ii). This event is being reported pursuant to 10CFR50.73(a)(2)(iv) as an Engineered Safety Feature actuation due to the unplanned manual reactor scram.
3541997023 | Hope Creek | 09/19/1997 | 11/28/1997 | 9712050185 | <strong>CORE SPRAY NOZZLE WELD THROUGH-WALL LEAK</strong><br /><i>Abstract:&nbsp;</i>At 1305 on 9/19/97, through-wall leaks were identified on the Core Spray (CS) nozzle-to-safe-end weld associated with the "A" CS subsystem. The condition placed the operability of the "A" CS subsystem in question, and the plant entered Limiting Condition for Operation (LCO) 3.5.2, "ECCS - Shutdown" and LCO 3.4.8, "Structural Integrity." The cause of the through-wall leakage has been attributed to intergranular stress corrosion cracking (IGSCC) in the Alloy 182 weld material. The weld was a field weld performed during the replacement of safe-ends in the early 1980s. The cause of the failure to detect the IGSCC during the last UT examination in 1995 was human error with a contributing factor being lack of use of information on weld configuration and history during review of the data. Corrective actions taken include nondestructive examination of the subject weld, review of the 1995 ultrasonic test (UT) data for the weld as well as for other Category "D" welds (i.e., welds that are not made with resistant materials and that have not been given stress improvement treatment but that have been inspected and found to be free of cracks), review of radiographs for field welds made for the safe end replacements in the early 1980s, UT examination of additional Category D welds, and repair of the leak using an engineered weld overlay. Corrective actions planned include establishing an as-built configuration for each weld and making that information available to personnel analyzing UT data and establishing requirements to ensure independent evaluation of UT data for Category D welds.
3541997024 | Hope Creek | 10/01/1997 | 10/20/1997 | 9710240284 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On October 1, 1997, Hope Creek personnel received the initial results of Safety Relief Valve (SRV) {RV/--} setpoint testing required by Technical Specification (TS) 4.4.2.2. This testing revealed that, following Hope Creek Cycle 7, 10 out of a total 14 SRVs experienced setpoint drift outside of the TS 3.4.2.1 limit of +/- 1%. The cause of the occurrence is most likely corrosion bonding of the pilot disc to the pilot seat. This drift is a known current industry wide problem. The issue is being addressed generically by the Boiling Water Reactor Owners Group (BWROG). Hope Creek has implemented a BWROG/Carolina Power & Light Company developed corrective action involving platinum ion implantation to mitigate this problem. Hope Creek will continue to work with the BWROG to resolve the issue of SRV setpoint drift. There was no impact to the health and safety of the public as a result of this issue. This condition is reportable under 10CFR50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant Technical Specifications.
3541997025 | Hope Creek | 10/04/1997 | 10/27/1997 | 9711040109 | <strong>Design Deficiency - Potential for an Unmonitored Release Path Through the Station Service Water System</strong><br /><i>Abstract:&nbsp;</i>On 10/4/97, Engineering personnel confirmed that a potential unmonitored release path has existed since plant startup. This path was identified while performing an engineering evaluation concerning relay performance in a Station Service Water System vacuum breaker time delay circuit. While reviewing the effects on other systems and boundaries, Engineering discovered the potential unmonitored release path. The postulated condition involves the failure of one of the vacuum breakers to close after a Loss of Power/Loss of Coolant Accident event creating a loss of secondary containment and an unmonitored release path to the outside environment. This release path would allow contaminated air to enter the service water piping through the open vacuum breaker and to subsequently be released to the outside environment via the discharge piping. The failure to identify this release path is a non-compliance with General Design Criteria. This event is being reported pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition that was outside the design basis of the plant. The cause of the failure to recognize and correct this condition was human error in the original design and in subsequent design reviews. Corrective actions are interim compensatory measures and a design change to minimize the potential for an unmonitored release.
3541997026 | Hope Creek | 10/20/1997 | 11/19/1997 | 9712030002 | <strong>Condition Prohibited by Technical Specifications - "E" Filtration, Recirculation, Ventilation System Recirculation Unit Inoperability due to Tripped High High Temperature Switch - Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1997, a surveillance test was being performed in accordance with the requirements of Technical Specifications 4.6.5.3.1 and 4.6.5.3.2. At 2000 hours, maintenance personnel discovered that there was no electric power available to the "E" Filtration, Recirculation, and Ventilation System (FRVS) recirculation unit heater as required per the surveillance test. The unit was subsequently declared inoperable. The High High Temperature Switch associated with the temperature controller for the "E" FRVS recirculation unit had been tripped during the previous surveillance test that was conducted on August 17, 1997; therefore, the "E" FRVS Recirculation unit had been inoperable for greater than the seven days allowed by Technical Specification Action Statement 3.6.5.3.2.a.1. The cause of this event was a procedural deficiency. Corrective actions were taken to complete the surveillance test satisfactorily and revise the procedure. The inoperability of the "E" FRVS recirculation unit for greater than 7 days is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications.
3541997027 | Hope Creek | 11/14/1997 | 12/15/1997 | 9712220400 | <strong>Technical Specification Surveillance Requirement Implementation Deficiencies - 125/250 VDC Batteries</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1997, a review of Hope Creek Technical Specifications (TS) determined that surveillance requirement 4.8.2.1.b.1 requires that specific gravity of each connected 125 VDC and 250 VDC battery cell be corrected for electrolyte temperature of each connected cell. At Hope Creek, the electrolyte specific gravity for each 125 VDC and 250 VDC battery cell has been corrected for electrolyte temperature using the electrolyte temperature of the associated pilot cell (every sixth cell) as opposed to the individual cell. Therefore, at 1558 hours on November 14, 1997, the Hope Creek Generating Station entered TS Action Statement 3.8.2.2, "D. C. Sources - Shutdown", and declared the 125 VDC and 250 VDC batteries technically inoperable due to an improperly performed surveillance test. The apparent cause of the improperly performed surveillance test is an inadequate review and approval, during the near-term operating license stage in the 1980's, of surveillance activities intended to satisfy Hope Creek's Technical Specifications. In addition, Hope Creek believed that because they satisfied IEEE 450-1980, they were satisfying the TS. There were no actual safety consequences associated with this event. The surveillance procedures were revised and the surveillances performed satisfactorily. The inoperability of the 125 VDC and 250 VDC batteries due to an improperly performed surveillance is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications.
3541997028 | Hope Creek | 11/17/1997 | 12/17/1997 | 9801060336 | <strong>Technical Specification Prohibited Condition - Failure to Perofrm Secondary Containment Isolation Actuatijon System Surveillances</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1997, while conducting a review of surveillance and preventive maintenance reports to ensure closure prior to startup from a refueling outage, Planning Department personnel identified an overdue channel functional surveillance test. This test is associated with the Reactor Vessel Water Level - Low Low, Level 2 trip function of the Secondary Containment Isolation Actuation Instrumentation System when the plant was in Operational Condition *_/ (when handling irradiated fuel in the secondary containment and during CORE ALTERATIONS and operations with a potential for draining the reactor vessel). A review of outage activities confirmed that Hope Creek failed to satisfy the required TS actions when the surveillance was overdue. Since the TS LCO was not met, and the associated TS actions were not satisfied, a condition prohibited by the TS occurred, which is reportable under the provisions of 50.73(a)(2)(i)(B). The cause of the event was attributed to personnel error, due to inattention to detail. Corrective actions include the successful performance of the overdue surveillance, disciplinary action for the ,personnel involved and a review of the details of this event with other departments responsible for performing surveillance status reviews.
3541997029 | Hope Creek | 11/18/1997 | 12/15/1997 | 9712220321 | <strong>Technical Specification Prohibited Condition: Mistakenly Removed Snubber Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1997, during implementation of a Design Change Package (DCP) to replace snubber 1-P-BC-144-H002 on the Residual Heat Removal shutdown cooling suction line, Inservice Inspection/Inservice Testing (ISI/IST) personnel identified that the snubber had been mistakenly removed during Hope Creek's fourth refueling outage in 1992 as part of a snubber reduction DCP. The apparent cause of this event is attributed to personnel error. Specifically, ISI/IST personnel failed to use the approved snubber reduction DCP to generate the work orders to remove individual snubbers in accordance with the DCP in 1992. Corrective actions were taken to install the snubber, verify required snubbers were installed per design, and hold personnel accountable. An analysis will be performed to determine the effects on the ability of the piping to perform its intended safety function. This Technical Specification prohibited condition is being reported under the provisions of 10CFR50.73(a)(2)(i)(B).
3541997030 | Hope Creek | 11/22/1997 | 12/19/1997 | 9801020054 | <strong>On 11/12/97, During the ten year review of the Hope Creek In-Service Test (IST) Program, the program reviewers discovered that the accumulator check valves for two Containment Atmosphere Control System Vacuum Breaker Isolation Valves were listed as Categ</strong><br /><i>Abstract:&nbsp;</i>On 11/12/97, during the ten year review of the Hope Creek In-Service Test (IST) Program, the program reviewers discovered that the accumulator check valves for two Containment Atmosphere Control System Vacuum Breaker Isolation Valves were listed as Category C valves. The reviewers believed that the valves should also be considered Category A valves. This discovery was validated, and the valves were re-categorized as both Category A and C valves. On 11/21/97, the leak rate tests were performed. The accumulator check valves failed their leak rate test. Follow up investigation determined that an assumption that operator actions to support operation of the Vacuum Breaker Isolation Valves would be taken within two hours had not been proceduralized. The apparent cause of this event was the failure to review an accumulator sizing calculation during the original development of the IST program in 1986. The engineering conclusions from the calculation were not disseminated to either the IST department or the Operations department. Corrective actions include updating the IST program, repairing the valves, and revising the appropriate procedures. This event is being reported under the provisions of 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v).
3541997031 | Hope Creek | 11/30/1997 | 12/24/1997 | 9801060227 | <strong>Engineered Safety Feature Actuation - Reactor Core Isolation Cooling System Isolation</strong><br /><i>Abstract:&nbsp;</i>On November 30, 1997, the Hope Creek Generating Station was preparing to enter Operational Condition 1, POWER OPERATION, following the seventh refueling outage (RFO7). During warm-up of the Reactor Core Isolation Cooling (RCIC) system, an automatic isolation signal was received at 2050 hours. Although the RCIC Isolation Actuation Instrumentation was required to be operable, the RCIC system was not required to be operable at the time the isolation signal was received since reactor pressure was below 150 psig (the Technical Specifications require RCIC to be operable with reactor pressure above 150 psig). In accordance with procedures, operators determined that a RCIC steam line break did not occur, re-set the isolation signal, and completed the warm-up of the RCIC steam lines. At 2247 hours, a four hour report was made to the NRC for this Engineered Safety Feature (ESF) actuation in accordance with the requirements of 10CFR50.72(b)(2)(ii). The cause of the event was attributed to steam flashing resulting in spurious steam line pressure and/or steam line flow signals. Corrective actions include continuing evaluations of the expected steam line dynamics during the RCIC warm-up process.
3541997032 | Hope Creek | 12/05/1997 | 01/02/1998 | 9801140220 | <strong>HPCI AND RCIC INOPERABILITY AND ENTRY INTO TECHNICAL SPECIFICATION 3.0.3</strong><br /><i>Abstract:&nbsp;</i>At 0529 on 12/5/97, during Inservice Testing (IST) of the Reactor Core Isolation Cooling (RCIC) system, the Control Room Operator manually initiated a remote trip of the RCIC turbine due to inability to control RCIC flow. As a result, the RCIC system was declared inoperable. At 1338 on 12/5/97, with the RCIC system still inoperable, the High Pressure Coolant Injection (HPCI) system was placed in service for Inservice Testing (IST). The HPCI turbine initially tripped and then reset. Approximately 14 minutes into the run, noise was heard and increasing vibration was recorded. At 1403, the HPCI turbine was manually tripped as a result of the noise and vibration, and HPCI was declared inoperable. Since both HPCI and RCIC were inoperable, Technical Specification Action Statement 3.0.3 was entered. A plant shutdown and cooldown was initiated at 1500. At 1535, a one hour notification was made to the NRC in accordance with 10CFR50.72(b)(1)(i)(A). The causes of the RCIC flow control issue were unsuitability of a replacement governor valve stem installed in March 1997, over-compression of the valve stem spring due to improper positioning of the valve stem guide, and misalignment of the remote servo - governor lever. The cause of the HPCI trip was a tappet spring that had lost its force due to vibration affecting the spring adjusting sleeve. The cause of the HPCI noise and vibration was rubbing between the shaft and carbon gland steam seal rings that were the result of corrosion and bowing of the shaft. Corrective actions include procedure changes and roll out of lessons learned. The plant shutdown is being reported under 10CFR50.73(a)(2)(i)(A). The inoperability of HPCI and the inoperability of RCIC are being reported in this LER under 10CFR50.73(a)(2)(v).
3541997033 | Hope Creek | 12/10/1997 | 01/09/1998 | 9801220163 | <strong>Technical Specification Prohibited Condition - Failure to Perform Secondary Containment Isolation Actuation Instrumentation Channel Checks</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1997, during a review of surveillance activities required to satisfy Limiting Condition for Operation (LCO) 3.10.8, "Inservice Leak and Hydrostatic Testing," operations personnel identified two cases concerning Technical Specification (TS) non-compliance during the past refueling outage (RFO7). The first case involved a failure to perform TS required surveillances during the performance of a hydrostatic test in RFO7. The second case involved a failure to perform required channel check surveillances on half of the reactor water level instruments that are required to be operable in Operational Condition (handling irradiated fuel in the secondary containment, core alterations, and operations with a potential to drain the reactor vessel). The cause of these events is attributed to an inadequate review of TS surveillance status and inadequate TS implementing procedures. Corrective actions included the successful performance of the required channel checks and procedure revisions to appropriately indicate operational condition requirements for these trip function surveillances.
3541997034 | Hope Creek | 12/26/1997 | 04/06/1998 | 9804150114 | <strong>Condition Prohibited by Technical Specifications: Missed Emergency Diesel Generator Surveillance</strong><br /><i>Abstract:&nbsp;</i>At 1525 on December 26, 1997, the "D" Emergency Diesel Generator (EDG) was declared inoperable due to the failure to perform inservice testing of the excess flow check valves that separate the safety related portion of the starting air system from the non-safety related portion within the surveillance interval required by Technical Specification (TS) 4.0.5 and the Hope Creek Inservice Test Program. The "A" primary containment instrument gas compressor was out of service for scheduled maintenance concurrent with the "D" EDG inoperability resulting in a failure to comply with the main steam isolation valve (MSIV) sealing system operability requirements of TS 3.6.1.4. As a result, TS 3.0.3 was entered. The affected excess flow check valves were isolated at 1559 and TS 3.0.3 was exited prior to initiating a plant shutdown. At 0100 on December 27, 1997, testing of the excess flow check valves was completed with satisfactory results. This supplement is being submitted because an additional occurrence of failure to perform the surveillances associated with the "A" EDG excess flow check valves was identified that had gone overdue during Refueling Outage 7 in October 1997. The causes of the missed surveillances were improper coding of the surveillance tests (ST) as preventive maintenance (PM) activities in the work order system and failure to follow the process for deferral of PM activities as a result of personnel errors. Corrective actions taken include properly coding the surveillance test, implementing the PSE&G discipline policy, identifying and correcting other occurrences of improper coding, and rolling out lessons learned to appropriate personnel. Additional corrective actions to be taken include procedure changes to ensure that online maintenance and surveillances are properly considered during outage planning.
3611997001 | San Onofre 2, San Onofre 3 | 01/09/1997 | 05/09/1997 | 9705190089 | <strong>Surveillances Not Current Upon Improved Technical Specification Implementation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. Edison implemented new standard Technical Specifications (TS) for Units 2 and 3 on 8/5/96. Prompted by the condition reported in LER 2-96-009, Edison initiated a detailed review of the new TS. During this review, Edison identified three cases, each containing examples where the new TS Surveillance Requirements (SRs) were not adequately implement by surveillance procedures. This LER discusses these examples separately. The five examples in Case A resulted from inadequate project management of the TS improvement project. The seven examples in Cases B (errors at the time of plant startup circa 1982) and the two examples in circa 1990-1995 C (contemporary errors) are examples where past surveillance practices did not satisfy the TS SRs. All of the examples are being reported under 10CFR50.73(a)(2)(i). As corretive action, Edison will bold meetings with appropriate personnel to discuss these examples and management's expectations, will provide special training, and will revise applicable documents. Edison believes in all examples the effected equipment was capable of performing its intended safety function. Therefore, there was no safety significance to these occurrences, and these items should be viewed as administrative in nature.
3611997002 | San Onofre 2 | 01/28/1997 | 03/07/1997 | 9703120032 | <strong>Increase in Pressurizer Level due to valve alignment error.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 28, 1997, with Unit 2 in Mode 5 for a refueling outage, operators had removed Train A LPSI pump 2P015 from service for maintenance. To ensure compliance with TS 3.4.8, operators planned to align Containment Spray (CS) Pump 2P012 to shutdown cooling (SDC) Train A by closing 2MU062 (manual isolation valve between CS Pump 2P012 and Refueling Water Storage Tank (RWST)), and then opening SDC to CS suction valve 2MU994. Due to an individual personnel error, valve 2MU062 was not completely closed prior to opening 2MU994 which created a flowpath from the RWST to the Reactor Coolant System (RCS) through the running LPSI pump. At about 2004, the control room received a Reactor Water Level alarm and immediately noted pressurizer level was increasing and instructed that valve 2MU062 be closed. During the four minutes that 2MU062 and 2MU994 were simultaneously opened, about 1177 gallons of water was transferred from the RWST to the RCS. Edison is voluntarily reporting the occurrence due to NRC interest. The worker involved was temporarily removed from his normal duties, and counseled by management. This event was reviewed with all operating crews. During this event, the plant was in Mode 5. In accordance with the requirements of TS 3.5.4, the RWST inventory boron concentration is maintained between 2350 and 2800 ppm. Consequently, there could not have been a significant reduction in RCS boron concentration and there was minimal safety significance to this event.
3611997003 | San Onofre 2 | 02/25/1997 | 03/18/1997 | 9703240096 | <strong>Pressurizer Safety Valve Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During the Unit 2 Cycle 9 refueling outage, the pressurizer [AB,PZR] safety valves (PSVs) [AB,RV] were removed. The valves were shipped to Wyle's Western Service Center (WSC) in Beaumont, CA. in February 1997 for the required as-found setpoint testing. On February 25, 1997, the valves were tested for their as-found lift setpoints, and both valves setpoints were found to be above the Technical Specification (TS) setpoint band of 2500 psia +/- 1 percent. The valve removed from plant tag location 2PSV0200 was determined to lift at 2528 psig (2543 psia); 2PSV0201 was determined to lift at 2511 psig (2526 psia). Edison reviewed overhaul and test data, and confirmed the valves were set correctly when installed at the beginning of cycle 8. It is likely that one or both were outside TS limits longer than their allowed out of service time limit (15 minutes) during cycle 8 mode 1 operation. Therefore, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). were disassembled, inspected, reassembled, and reset to the proper setpoint by qualified vendor personnel at the WSC. Edison believes the cause of this condition to be setpoint drift. A recently completed PSV setpoint analysis confirmed the TS setpoints could be expanded from the current +/- 1 percent. Because the as-found setpoints were bounded by this analysis, there was no safety significance to this event. LERs 2-95-010 and 3-96-002 reported a similar condition for pressurizer safety valves and indicated Edison would evaluate expanding the TS tolerances, as recommended by the NRC (TAC No. M86339), to reduce TS violations caused by setpoint drift. The above referenced analysis was completed to support such a TS change, which Edison expects to submit in the near future.
3611997004 | San Onofre 2 | 03/03/1997 | 04/02/1997 | 9704100001 | <strong>Reactor Coolant System Leakage - Pressurizer Thermowell</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. At about 2045 on March 3, 1997, an Operator making a routine Mode 4 inspection inside containment noted steam emanating from the pressurizer. At that time, Unit 2 was in Mode 4 at 0% power. Technical Specification (TS) 3.4.13.a allows no pressure boundary leakage in Modes 1 through 4. If this LCO is not met, this TS requires the Unit to be in Mode 5 within 36 hours. Operators returned the Unit to Mode 5 at 1041 on March 4, 1997 (about 14 hours after discovery). Because Unit 2 was returned to Mode 5 within 36 hours of the onset of pressure boundary leakage, the TS requirements were satisfied and a report to the NRC is not required. Edison is voluntarily reporting this occurrence due to potential industry interest and for NRC reference. Edison concluded the leak was caused by Primary Water Stress Corrosion Cracking (PWSCC) of alloy 600 type materials of the pressurizer liquid temperature thermowell nozzle. The nozzle was removed and replaced with Inconel 690. The crack was oriented parallel to the long axis of the nozzle. Consequently, a complete circumferential failure of an RCS instrument nozzle is not believed to be a credible event. Nevertheless, the consequences of such a failure would be bounded by the small break loss of coolant accident (SBLOCA) analyzed in the UFSAR. The actual leak rate during this occurrence was about 0.76 gpm of water. Consequently, this event had minimal safety significance.
3611997005 | San Onofre 2 | 03/19/1997 | 04/15/1997 | 9704230043 | <strong>Reactor Coolant System Leakage - Shutdown Cooling System Valve Packing Leakoff Plug</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 3/18/97, Operators were moving Unit 2 from Mode 4 to Mode 3 at the end of the Cycle 9 refueling outage. At about 2045, an Engineer performing a routine inspection noted steam emanating from the Shutdown Cooling System isolation valve. At 0500 on 3/19/97, the leak was determined to be through the body of the valve's packing leakoff plug. Technical Specification (TS) Limiting Condition For Operation (LCO) 3.4.13.a allows no Reactor Coolant System pressure boundary leakage in Modes 1 through 4. If this LCO is not met, this TS requires the Unit to be in Mode 5 within 36 hours. In response to the observed leak, Operators returned the Unit to Mode 5 at 0638 on 3/20/97, within the 36 hour limit of the TS LCO. While Edison has determined that 10CFR50.72 and 50.73 do not require a report to be submitted for this occurrence, Edison is voluntarily submitting this report due to potential industry interest and for NRC reference. packing leakoff plug. The defective plug was replaced. Edison believes this is an isolated event. The defective plug was installed during this refueling outage (U2C9) and developed a leak within four days after entering Mode 4. Inspections of similar plugs in Units 2 and 3, all with much longer service times, identified no leaks. The defective plug did not adversely affect the valve's operation. The plug is a 1/2 inch nominal pipe size (approximately 5/8 inch diameter hole). Catastrophic failure of the plug, while not considered credible, is bounded by the small break loss of coolant accident analysis in the UFSAR. Therefore, this event did not pose a substantial safety hazard.
3611997006 | San Onofre 2, San Onofre 3 | 03/19/1997 | 04/18/1997 | 9704220199 | <strong>Missed Surveillance on RPS Operating Bypass Functions</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. In Generic Letter 96-01, the NRC noted that some utilities had not been fully complying with the requirements of their Technical Specifications (TS) regarding the surveillance testing of electronic circuits. Licensees were requested to review plant records to ensure all TS required surveillances were being completed. During this review, Edison recognized that operating bypass circuitry for some trip parameters of the Reactor Protective System was not tested by the existing surveillance procedures. Although the surveillance procedures were verifying the operating bypass removal function (automatic and manual) for Log Power, Pressurizer Pressure, Loss of Load, and Reactor Coolant Flow, Edison was not verifying the automatic bypass removal function for the Core Protection Calculator (CPC) trips for Departure from Nucleate Boiling Ratio (DNBR) and Local Power Density.' Therefore, Edison is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i). existed since the applicable surveillance procedure was first drafted (circa 1982). Due to the passage of time, the specific cause of the omission is not known. As allowed by SR 3.0.3, Edison prepared special test instructions and completed the surveillance at Unit 3 within 24 hours of its discovery. Similar tests were completed at Unit 2 on 3/21/97. Edison will revise appropriate plant procedures to incorporate the required testing of all operating bypass functions. The revisions are scheduled for completion prior to the next required surveillance.
3611997007 | San Onofre 2, San Onofre 3 | 04/03/1997 | 07/18/1997 | 9707250062 | <strong>Incomplete Surveillance Testing of Containment Purge Exhaust Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>In 1989, Edison revised the surveillance test procedures for performing channel functional tests on the containment purge exhaust radiation monitors. These changes provided an option to not stroke the outside containment valves, but to rely on an overlapping test to stroke the valves. Personnel performing the test thereafter routinely used this option. Subsequently, Edison determined that the alternative test was not an overlapping test, and that former Technical Specification (TS) Surveillance Requirements (SRs) to test these and other radiation monitors for downscale failure were not performed. Because the valves were not always verified to isolate the containment purge exhaust pathway in conjunction with the channel functional test, Edison originally reported this occurrence in accordance with 10CFR50.73(a)(2)(i). Edison is submitting this supplemental report to provide these subsequent determinations. Inadequate management of the surveillance test procedure change process allowed the procedures to be revised without appropriate review. Edison did not recognize the need to deviate from the standard Radiological Effluent TS regarding the requirement for downscale failure testing. Miscommunication between Edison personnel resulted in an incorrect understanding of the nature of the violations, requiring submittal of a revised LER. Edison tested the valves, corrected the procedures, and conducted a review of the TS SRs which revealed no instances of improper or inadequate overlap testing. Prior to submittal of the original report, the TS SR for downscale failure testing had been either relocated to the licensee-controlled Offsite Dose Calculation Manual (ODCM) or otherwise eliminated from the TS. Edison revised the ODCM to (1) delete the requirement for downscale failure testing, and (2) change the frequency for verifying isolation of the effluent pathway from once per quarter to once per refueling interval.
3611997008 | San Onofre 2 | 03/04/1997 | 04/18/1997 | 9704290012 | <strong>Missed Technical Specification Surveillance - Pressurizer Cooldown Rate</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 3/4/97, plant operators were cooling Unit 2 from Mode 4 to Mode 5. A high cooldown rate was discovered by an NRC resident inspector who was monitoring pressurizer temperature in real-time on a networked personal computer in his office. The inspector notified the Control Room. Technical Specification (TS) Surveillance Requirement (SR) 3.4.3.1.1 requires Edison to verify pressurizer heatup and cooldown rates are within limits once every 30 minutes during heatup and cooldown operations. Edison initially believed this TS SR was satisfied because a dedicated operator was graphing the required data. subsequently, on April 7, 1997, Edison and the NRC resident inspector concluded that this TS SR had not been satisfied because the operator graphing the data did not verify the cooldown rate was within TS limits. Consequently, Edison is reporting this missed TS SR in accordance with 10CFR50.73(a)(2)(i). The cause of the missed TS SR was the operator did not recognize that a real-time evaluation of plant data was required. Edison reviewed this event with all operating crews. The Operator performing the TS SR was coached regarding SR 'verification'. verification requirement was revised to enhance the graphs and tables. An engineering evaluation of the pressurizer vessel, surge line, surge line nozzle and spray nozzle determined that the components are acceptable for continued service. Therefore, the safety significance of this event is minimal.
3611997009 | San Onofre 2, San Onofre 3 | 05/09/1997 | 06/05/1997 | 9706120228 | <strong>Class 1E 125 VDC Battery Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>The Class 1E 125V dc distribution system for each unit consists of four separate and independent 125V dc subsystems each of which includes a 58-cell battery and 2 spare cells (8 batteries, 4 per unit). The Technical Specifications (TS) have two different surveillance requirements (SR) which measure battery design and accident capabilities; SR 3.8.4.7 - Service Test - requires Edison to verify battery capacity is adequate to supply, and maintain the required emergency loads for the design duty cycle once every 24 months; and SR 3.8.4.8 - Performance Test - requires Edison to verify battery capacity is equal to or greater than 80% of the manufacturer's rating once every 60 months. In 1993, Edison replaced three of these batteries. However, Cycle 8 testing indicated an apparent drop in capacity of two of the new batteries. By letter dated June 4, 1996, Edison committed to complete a performance test in addition to the TS required service test for batteries 2D1 and 3D2 during the Cycle 9 outages. Edison completed the performance tests first. Edison and the vendor recognized a longer equalizing charge would be prudent to restore the battery to a condition similar to its pre-performance test condition prior to completing the service test. Because the TS bases for both tests require "as-found" conditions, Edison questioned if recharging would affect the "as-found" conditions. Edison also questioned if including spare cells in the TS SRs (and pro-rating the results downward) was a pretest enhancement. Edison concluded that neither concern was a pretest enhancement. Nevertheless, Edison recognized this could appear so and is voluntarily submitting this report for NRC and industry information. Edison will revise the Bases for TS 3.8.4.7/8 to clearly indicate that battery recharging between tests may be required and that spare cells may be included during surveillance testing.
3611997010 | San Onofre 2, San Onofre 3 | 06/26/1997 | 08/13/1997 | 9708210028 | <strong>Charging Subsystem Check Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On 6/26/97 while Unit 3 was shutdown for refueling, an investigation of the cause of high auxiliary spray flow found a check valve in the Charging Subsystem that would not open completely. This would cause the charging flow distribution to the Reactor Coolant System to be different than that assumed in the safety analysis. Because of the similarity of the Unit 2 Charging Subsystem, Edison immediately entered the Technical Specification action statement for one or more trains of Emergency Core Cooling System (ECCS) inoperable, but 100 percent of the ECCS equivalent flow to a single operable ECCS train available. As a conservative action, Edison also reduced Unit 2's power to about 90 percent, where charging flow is not required for accident mitigation. On 6/28/97, Edison tested Unit 2 and found that a similar check valve also would not open completely. As required by the Technical Specifications, Edison shutdown Unit 2 to repair the valve. Completion of that shutdown is being reported as required by 10CFR50.73(a)(2)(i). Because this valve failure was caused by a design defect, Edison is including 10CFR21 information in this report. Edison replaced the faulty design valves in the charging injection lines and auxiliary spray line in each unit with another type valve. Edison's evaluation of the cause(s) is on-going. This LER will be revised if the evaluation determines a cause other than faulty design. The 1979 computer model requires charging system flow for mitigation of some small break loss of coolant accidents. However, this model assumes plant conditions that are not allowed by the Technical Specifications. Using an EPRI analysis program and actual, allowed, plant parameters, Edison concluded that the condition resulted in a negligible increase in plant risk and had no actual safety significance.
3611997011 | San Onofre 2, San Onofre 3 | 07/04/1997 | 08/05/1997 | 9708110131 | <strong>Wrong Boron Sample Used for Shutdown Margin Surveillance</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications for SONGS 2 and 3 require Edison to verify the shutdown margin (SDM) by performing an SDM calculation once every 24 hours when a reactor is in Modes 3, 4 or 5. This includes consideration of the reactor coolant system (RCS) boron concentration. Between SDM calculations, two channels of instrumentation provide continuous confirmation that the reactor remains shut down. If one channel becomes inoperable, an SDM calculation is required within 4 hours and once per 12 hours thereafter. On 7/4/97 with Unit 3 in Mode 5, instrumentation channel 1 was declared inoperable. The boron concentration used by the operator (utility, licensed) making the initial SDM calculation was erroneously from the refueling water storage tanks (RWST), not from the RCS. Consequently, the required 4 hour SDM calculation was not completed correctly. Edison is reporting this in accordance with 10CFR50.73(a)(2)(i). Additionally, the 12 hour SDM surveillances were not correctly implemented because RCS boron samples were taken on a 24 hour frequency. This event was caused by cognitive personnel error in using RWST boron concentration, and by procedural error (inadequate procedure -- i.e., the surveillance procedures did not specify how recent must be the RCS boron sample results). The operator was coached in the need for attention to detail. Edison has revised the procedures for performing SDM calculations.
3611997012 | San Onofre 2, San Onofre 3 | 08/14/1997 | 09/12/1997 | 9709220082 | <strong>Design Inadequacy In Backup Nitrogen Supply To Component Cooling Water Surge Tanks</strong><br /><i>Abstract:&nbsp;</i>In response to NRC Generic Letter 96-06 and an open item from the design document reconstitution program, an investigation was conducted of the adequacy of the design of the backup nitrogen system (BNS) to the component cooling water (CCW) surge tanks. A scenario not previously considered was identified which could deplete the BNS after a postulated accident. On 8/14/97 (the discovery date), plant management (other utility personnel) concluded that under the postulated scenario there may not be sufficient bottled nitrogen to ensure the CCW surge tank remains pressurized for 7 days following a postulated accident as required by the Technical Specifications (TS). Because this condition may have existed since the TS for BNS operability was approved in 1995, Southern California Edison is reporting this condition in accordance with 10CFR50.73 (a)(2)(i). Plant personnel promptly declared both trains of BNS inoperable for both Units and took compensatory action to restore system operability by requiring, during the postulated scenario, a dedicated operator to be stationed to maintain CCW surge tank level. This action restored the BNS to operable status. Design engineers (other utility personnel) did not recognize the postulated scenario when sizing the BNS during a 1991-1992 CCW surge tank upgrade [NRC Cause Code: cognitive personnel error]. This LER will be required reading for design engineers, and a topic in their continuing training program. Design changes are being considered to minimize backup nitrogen consumption during the postulated scenario.
3611997013 | San Onofre 2, San Onofre 3 | 10/10/1997 | 11/07/1997 | 9711140209 | <strong>Charcoal Filter Surveillance Testing Not Current</strong><br /><i>Abstract:&nbsp;</i>In August 1996, Southern California Edison (SCE) implemented the Technical Specification Improvement Program (TSIP). Before then, the Fuel Building Post-Accident Cleanup (PACU) units and the Control Room Emergency Air Cleanup System (CREACUS) Technical Specification (TS) Surveillance Requirement (SR) required a test analysis of the charcoal filters meet the criteria of Regulatory Position C.6.a of Regulatory Guide 1.52, Rev. 2, March 1978. After the TSIP, the SRs reference the Ventilation Filter Testing Program (VFTP). The VFTP requires filter testing be in accordance with Regulatory Guide 1.52, Rev. 2, and ASME N510-1989. The new TS changed the testing conditions and acceptance criteria to be more restrictive. Prior to the TSIP, SCE incorrectly concluded that the SR changes were not a new surveillance test, and it did not need to be re-preformed upon TSIP implementation. Consequently, the PACU and CREACUS filters did not have a current test of record following the TSIP. Therefore, SCE is reporting this occurrence in accordance with 10 CFR 50.73(a)(2)(i). The failed CREACUS filter has been replaced. The PACU filter replacement will be completed before irradiated fuel is next moved. Consequently, SCE is in full compliance with the affected TS. To prevent recurrence, SCE will review these events with appropriate SCE personnel. The charcoal efficiency test failures were caused by a change in the test conditions, not an actual change in the filters' efficiency. SCE believes the affected equipment was capable of performing its intended safety function. Moreover, the PACUs are not credited for mitigating the consequences of a fuel handling accident in the Fuel Building. Therefore, there was minimal safety significance to these events.
3611997014 | San Onofre 2, San Onofre 3 | 10/20/1997 | 11/10/1997 | 9711200060 | <strong>Licensed Operators Did Not Have Corrective Lenses For Use With Respirators</strong><br /><i>Abstract:&nbsp;</i>The NRC issued Information Notice (IN) 97-66 on 8/20/97 to alert licensees that at some plants, some licensed operators with corrective lens license restrictions did not have lenses for use with full face respirators. Southern California Edison (SCE) has determined that approximately 16 SONGS operators (utility, licensed) similarly did not have respirator lenses. Actual on-shift staffing by fully qualified operators was nearly always above the required minimum, though there may have been occasions when the shift superintendent position was not staffed in complete compliance with licensed conditions while wearing respirators. Consequently, on 10/20/97 (discovery date), management began an investigation which concluded this condition may be reportable under 10 CFR 50.73(a)(2)(i). As stated in IN 97-66, the cause of this condition was that SCE "...had not established administrative controls for special lens inserts and had not ensured that the requisite special lenses were available...." SCE has procured corrective lenses for all affected operators and is improving the associated procedures to prevent recurrence. Due to the: (1) very limited actions operators may be required to perform while wearing respirators, (2) very limited number of postulated accident scenarios that require operators to use respirators, and (3) small number of operators affected (approximately 16 of 60), this occurrence had minimal safety significance. LER 2-94-006 reported minimum staffing requirements were not met for reasons unrelated to individual operator license conditions.
3611997015 | San Onofre 2, San Onofre 3 | 11/17/1997 | 12/11/1997 | 9712170426 | <strong>Inadequate Surveillance Testing of Charging Pump Relay Contacts</strong><br /><i>Abstract:&nbsp;</i>Each charging pump at San Onofre Nuclear Generating Station (SONGS) has non-safety-related trips on low suction pressure and high pressurizer level when in automatic control. A contact on the subgroup relay (K108) which starts the pump on a safety injection actuation signal disables these non-safety-related trips. Technical Specification (TS) Surveillance Requirement (SR) 3.5.2.8 requires verification once every 24 months that each pump starts automatically on an actuation signal. On 11/17/97, Southern California Edison (SCE) concluded that, since surveillance testing had not verified the K108 subgroup relay contact properly defeats the non-safety-related charging pump trips, the condition was reportable as a missed TS surveillance. At 1420 on 11/17/97, SONGS entered TS SR 3.0.3. The K108 subgroup relay contacts were tested satisfactorily within the 24 hour period allowed by TS SR 3.0.3. This occurrence was caused by an inadequate surveillance test procedure which did not specify testing the K108 subgroup relay contacts. SCE established the testing methodology circa 1982, believing it to meet the TS requirements at that time. SCE no longer believes this practice satisfies the TS requirements. The surveillance test procedure will be modified. TS SR 3.5.2.8 does not specifically require testing of the K108 relay contacts, nor does the associated TS Basis indicate that testing of these relay contacts is required. SCE will revise the TS Basis to clarify SCE's current understanding of required surveillance testing.
3611997016 | San Onofre 2, San Onofre 3 | 12/02/1997 | 01/02/1998 | 9801130084 | <strong>Fire Damper Not In Technical Specification Data Base</strong><br /><i>Abstract:&nbsp;</i>On 2/6/96, SONGS personnel unsuccessfully drop-tested fire damper SARW504165001FD, then repaired it and made it operable. on 12/2/97, during an audit of the Plant and Equipment Data Management System (PEDMS), SONGS personnel recognized that fire damper SARW504165001FD was not in the Licensee Controlled Specification (LCS) surveillance procedure. Consequently, between August 1993 (date damper added to Technical Specifications (TS)) and February 1996 (date damper drop tested), Southern California Edison (SCE) had not visually inspected this fire damper every 18 months as required by (then in force) TS Surveillance Requirement 4.7.9.2. Additionally, due to the condition of the damper when tested on 2/6/96, it is likely the damper was inoperable for more than one hour. Because SCE could not have known the damper was inoperable prior to its drop-test, and did not know the damper was a TS damper, a roving fire watch was not posted as required by (then in force) TS 3.7.9.a. Consequently, SCE is reporting this occurrence in accordance with 10 CFR 50.73(a)(2)(i). This occurrence was caused by a cognitive personnel error (utility, non-licensed). When certain fire barriers were added to the TS on 8/24/93, fire damper SARW504165001FD was inadvertently omitted. Immediately upon discovery, on 12/2/97, SONGS workers verified fire damper SARW504165001FD operable by inspecting and drop testing it satisfactorily. The damper was added to the LCS surveillance procedure. SCE completed the PEDMS audit. This occurrence has been reviewed with appropriate SONGS personnel.
3611997017 | San Onofre 2, San Onofre 3 | 12/16/1997 | 01/13/1998 | 9801210087 | <strong>Shift Technical Advisors - Respirator Qualifications</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1997, it was questioned whether Shift Technical Advisors (STAs) were respirator qualified, and if STAs who are required to wear glasses have the appropriate corrective lenses to wear with their respirators. On December 16, 1997 [the discovery date], Southern California Edison (SCE) completed a review of STA training records and confirmed that respirator training for some STAs had lapsed, and that some did not possess respirator lenses. Consequently, SCE concluded this occurrence was reportable in accordance with 10 CFR 50.73(a)(2)(i). At the time of this determination, both Units 2 and 3 were at about 100 percent power. As planned and discussed in the original FSAR, the SONGS 9-person shift crews included five ROs. When SONGS Units 2 & 3 were licensed (1982), the NRC was just creating the requirements for STAs on shift (NUREG-0660 and NUREG-0737). Consequently, during 1982, the number of ROs was reduced and the STAs position was added. It appears that SCE did not adequately assess respirator requirements listed in the UFSAR for the modified crew composition and incorporate this requirement in plant procedures. Due to the passage of time (about 15 years), the cause of this omission could not be determined. SCE has requalified and certified all STAs for respirator use. Future STA respirator training will be incorporated in the Operations department training program.
3621997001 | San Onofre 3 | 04/12/1997 | 05/09/1997 | 9705160202 | <strong>Reactor Coolant System Leakage - Instrument Thermowell Nozzles</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 11, 1997, plant operators began reducing reactor power for the Unit 3, Cycle 9 refueling outage. Between April 12-17, 1997, Edison inspected all Inconel Alloy 600 instrument nozzles in the RCS. During this inspection, Edison noted that four RCS nozzles had leaked during plant operation, and a fifth is suspected of leaking. Technical Specification (TS) 3.4.13.a allows no pressure boundary leakage in Modes 1 through 4. If this LCO is not met, this TS requires the Unit to be in Mode 5 within 36 hours. Based on the existence of boric acid crystals around some of the leak locations, Edison believes it likely, that one or more of the leaks existed during plant operation (more than 36 hours prior to entering Mode 5). Consequently Edison is reporting these occurrences in accordance with 10CFR50.73(a)(2)(i). Based on evaluation of the leak size, leak location, deposition of boric acid crystals, and previous experience with Inconel 600 nozzle leakage, Edison suspects the leakage to be from a crack through the nozzle in the heat affected zone (HAZ) of the partial penetration weld on each of the instrument nozzles. Historically, Edison has determined that similar cracks were caused by Primary Water Stress Corrosion Cracking (PWSCC) of alloy 600 type materials. Cracking of Inconel 600 material is well known and is likely the root cause of these leaks. If, after further analysis, a cause other than provided here is found, this LER will be supplemented with additional details. Edison will replace the outer half of the Inconel 600 material of the original nozzles with Inconel 690. Required welding will be completed in accordance with the ASME III, Class 1 welding guidelines. [Note: This repair is similar to that reported in LER 2-97-004.]
3621997002 | San Onofre 3 | 07/03/1997 | 07/30/1997 | 9708060190 | <strong>Reactor Coolant System Leakage-Instrument Thermowell Nozzles</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1997, plant personnel inspected the Unit 3 RCS nozzles at 350 psia. One nozzle had an increased amount of white residue, and an isotopic analysis determined the residue was boric acid from the RCS. Three other "suspect" nozzles were re-inspected; two had a slight residue increase, the third did not. Edison assumed the residue from these other nozzles was also boric acid from the RCS. Technical Specification (TS) 3.4.13.a allows no pressure boundary leakage in Modes 1 through 4. If this LCO is not met, this TS requires the unit to be in Mode 5 within 36 hours. Based on the existence of boric acid crystals around some of the leak locations, Edison believes it likely that one or more of the leaks existed during Mode 3 and 4 operations. Consequently, Edison is reporting these occurrences in accordance with 10CFR50.73(a)(2)(i). Edison has previously determined that similar cracks were caused by Primary Water Stress Corrosion Cracking (PWSCC) of alloy 600 type materials. Cracking of Inconel 600 material is well known, and is believed to be the root cause of the leaks reported herein. Based on evaluation of the leak size, leak location, deposition of boric acid crystals, and previous experience with Inconel 600 nozzle leakage, Edison suspects the leakage is from a crack through the nozzle in the heat affected zone (HAZ) of the partial penetration weld on each of the instrument nozzles. These nozzles were originally designed and installed as a one piece nozzle made of Inconel 600 welded with a J-Groove weld on the inside of the RCS piping. Edison replaced the outer half of the nozzles (Inconel 600 material) with Inconel 690 material. Required welding was completed in accordance with the ASME III, Class 1 welding guidelines.
3621997003 | San Onofre 3 | 12/18/1997 | 11/25/1998 | 9812020017 | <strong>Pressurizer Safety Valve Setpoints Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>During the Unit 3 Cycle 9 refueling outage (4/12/97 - 7/21/97), two pressurizer [AB, PZR] safety valves (PSVs) [RV] were removed. The valves were shipped to NWS Technologies in Spartanburg, South Carolina in November 1997 for as-found setpoint tests. Both valves' as-found lift setpoints were determined to be outside the Technical specification (TS) setpoint band of 2500 psia +/- 1 percent. 3PSV-0200 was determined to lift at 2528 psig (2543 psia); 3PSV-0201 was determined to lift at 2392 psig (2407 psia). Southern California Edison (SCE) reviewed overhaul and test data and confirmed the valves were set correctly when installed at the beginning of Cycle 8. It is likely that one, or both, were outside TS limits longer than their allowed out of service time limit (15 minutes) during Cycle 8, Mode 1 operation. Therefore, SCE is reporting this occurrence in accordance with 10 CFR 50.73(a)(2)(i). The valves were inspected and reset to the proper setpoint by qualified personnel at NWS technologies in mid January 1998. SCE has completed a PSV setpoint analysis confirming the existing TS setpoints can be expanded to +3/-2 percent, which bounds the as-found setpoint for 3PSV-0200. Because 3PSV-0201 lifted below the expanded band, SCE completed a cycle-specific analysis and confirmed the plant remained bounded by the accident analyses in the UFSAR. Consequently, there was no safety significance to this event. The increased tolerance, +3/-2 percent, has been incorporated into an Amendment Change Request which was submitted to the NRC on September 4, 1998.
3621997004 | San Onofre 3 | 12/05/1997 | 01/05/1998 | 9801130351 | <strong>Typographical Error In The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 12/5/97, an engineer [utility, non-licensed], while preparing for a scheduled 1998 containment tendon surveillance, found a typographical error in Unit 3's Licensee Controlled Specification (LCS). This error was traced to the original 1982 Unit 3 Technical Specification (TS). Due to this error, prior tendon surveillances were not performed in verbatim compliance with the "typographically incorrect" original Unit 3 TS. Therefore, this occurrence is being reported under 10 CFR 50.73(a)(2)(i). The typographical error was likely caused in preparing the original Unit 3 TS. Apparently, the tendon identification in the original TS was incorrectly copied from the original source document. SCE immediately confirmed that all previously performed surveillances affected by this error were properly performed and adequately demonstrated operability. Therefore, this typographical error has no safety significance.
3641997001 | Farley 2 | 01/13/1997 | 02/12/1997 | 9702200149 | <strong>Nuclear Instrumentation System Inaccuracies Below 50% Power</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Westinghouse Technical Bulletin ESBU-TB-92-14-R1 describes the potential decalibration effects of calorimetric power measurements on the power range nuclear instrumentation (NI) at low power levels. As a result of evaluating the applicability of the bulletin, on January 13, 1997, with Unit 2 in mode 1 operating at 100 percent reactor power, it was determined that between January 31, 1996 and February 1, 1996, Unit 2 had been operated in a condition prohibited by Technical Specifications. Specifically, Unit 2 had operated with less than the Technical Specifications minimum required power range channels [JC] operable due to channels NI-41 and NI-44 being adjusted in the non-conservative direction while the unit was in a low power condition. Channels NI-41 and NI-44 were functional; however, in the event of an overpower condition, their associated high flux high setpoint reactor trip signal may not have been initiated before thermal power exceeded the assumed design basis safety analysis limit of 118% rated thermal power (RTP) by approximately 0.5% RTP. Channels NI-42 and NI-43 remained operable and would have actuated within the safety analysis limit. This event was caused by personnel error in that the NSSS vendor failed to identify the potential magnitude of the instrument uncertainty associated with the secondary side power calorimetric performed at low RTP conditions. Unit operating procedures have been modified to specify that for sustained operation (greater than 24 hours) below 50% RTP, or if power range NI's must be adjusted in accordance with the results of a calorimetric below 50% RTP, then the power range high flux high trip setpoint will be reduced to less than or equal to 85% power.
3641997002 | Farley 2 | 10/30/1996 | 04/02/1997 | 9704090141 | <strong>Inappropriate Interpretation of Penetration Room Filtration System Power Supply Requirement</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 6, 1997, it was determined that Unit 2 had been operated, beginning on October 30, 1996, in two conditions prohibited by Technical Specifications (TS). Unit 2 had operated in a condition prohibited by TS in that fuel movement and crane operation with loads over the fuel in the spent fuel pool (SFP) had been performed with both trains of penetration room filtration (PRF) systems considered inoperable for approximately 10 hours on October 30, 1996. In addition, with one PRF system considered inoperable, crane operation with loads over the fuel in the SFP exceeded the TS allowed action statement time of 48 hours by approximately 24 hours beginning on October 30, 1996. On October 28, 1996 a portion of the Train A normal and emergency electrical distribution system was removed from service for Unit 2 outage work. SNC concluded that the Train A PRF system was operable and it was appropriate to conduct fuel movement and crane operations in the SFP without entering the action statement of TS 3/4.9.13. In addition, SNC concluded that it was appropriate on October 30, 1996 to continue fuel movement and crane operations in the SFP while performing a surveillance test on the Train B penetration room filtration (PRF) system that would require closing the Train B SFP to PRF system suction damper. These actions were considered appropriate by the application of TS 3/4.8.1.2. Subsequent questions by an operating crew resulted in suspending crane operations in the SFP. An additional review of the TS interpretation concluded the TS interpretation was valid and no TS violations occurred. Subsequently, an NRC inspector concluded that it was an inappropriate interpretation. SNC submitted its interpretation in a letter to the NRC on November 27, 1996. On March 6, 1997, the NRC formally responded to the SNC letter and disagreed with the SNC interpretation of the TS requirements. The cause of this event was cognitive personnel error in that SNC personnel incorrectly interpreted TS requirements by the misapplication of TS 3/4.8.1.2 to TS 3/4.9.13. SNC has revise
3641997003 | Farley 2 | 04/24/1997 | 05/22/1997 | 9705280110 | <strong>Failure to Perform Diesel Generator Surveillance Requirements Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At 0900 on April 24, 1997 while in Mode 1 at 100% power, it was determined that Unit 2 had been operated in a condition prohibited by Technical Specifications (TS). The requirements of Unit 2 TS Surveillance Requirement (SR) 4.8.1.1.2.c.8 had not been verified as acceptable for the 1-2A Diesel Generator (DG) within the required frequency of 18 months. Past performances of this surveillance had been performed with the 1-2A DG connected to the Unit 1 4160 Volt Bus 1F and credit for the Unit 2 requirement was inappropriately taken based on 1-2A DG being a shared component. A review of this SR and the associated circuitry determined that not all Unit 2 components were being tested and it was concluded that required Unit 2 surveillance had been missed. Concurrent with this review, the surveillance test was performed satisfactorily with the 1-2A DG connected to the Unit 2 4160 Volt Bus 2F. The possibility of previous inadequate surveillance testing associated with this SR was first questioned at approximately 1300 on April 23, 1997 during a review to determine the completeness and adequacy of plant procedures in fulfilling TS SRs prior to mode changes. The cause of the missed surveillance was procedural inadequacy in that the Shared (Unit 1 and 2) Surveillance Schedule did not provide sufficient guidance to ensure that required testing was being performed for each Unit individually.
3641997004 | Farley 2 | 09/10/1997 | 10/10/1997 | 9710170020 | <strong>Operating Outside of Technical Specifications Due to Required Containment Atmospheric Grab Samples Not Being Taken</strong><br /><i>Abstract:&nbsp;</i>At approximately 1000 on 9/17/97 during a root cause investigation while operating at 100% power, it was determined that Unit 2 had operated in a condition prohibited by Technical Specifications (TS). This determination was based on a review of information obtained during the investigation into problems associated with performance of containment atmosphere particulate (R-11) and gaseous (R-12) radiation monitors. It was concluded that these monitors most likely became inoperable at approximately 0357 on 9/9/97 although it was not recognized at that time. With these monitors inoperable, the containment air cooler condensate level monitoring system remained as the only operable TS Reactor Coolant System (RCS) Leakage Detection System. TS 3.4.7.1 requires that containment atmosphere grab samples be taken and analyzed at least once per 24 hours with only one of the required RCS Leakage Detection Systems operable. R-12 was declared inoperable on 9/9/97, but since R-11 readings remained normal, it was considered operable and the required grab samples were not taken from 9/10/97 through 9/12/97. These radiation monitors were inoperable because the containment atmosphere sample path inlet and outlet solenoid valves were closed due to an inadvertent disconnection of the leads in their control circuit. The root cause investigation concluded that multiple equipment problems caused R-11 to appear normal and prevented plant personnel from recognizing that R-11 was inoperable. During troubleshoot of the problems with R-12, both radiation monitors were subsequently declared inoperable on 9/12/97 and the required grab samples were performed on 9/13/97 and 9/14/97. At 2220 on 9/14/97 the leads were reconnected, a valid flow path was established, and both R-11 and R-12 were returned to service with proper indication. To prevent a recurrence appropriate plant personnel will be trained on this event and appropriate procedures will be enhanced.
3661997001 | Hatch 2 | 01/25/1997 | 02/24/1997 | 9703060122 | <strong>High Pressure Coolant Injection System Inoperable Following Unplanned Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 1/25/97 at 2335 EST, Unit 2 was in the Run mode at a power level of 2558 CMWT (100 percent of rated thermal power). At that time, Instrument and Control (I&C) technicians were calibrating a time delay relay when, per the procedure in use at the time, they lifted wires from the neutral connection of the relay. When the wires were lifted, Control Room operators received annunciation indicating that power had been lost to the initiation logic for the High Pressure Coolant Injection (HPCI) system. Also, the HPCI system turbine exhaust line vacuum breaker isolation valve closed automatically. With this valve closed and the initiation logic disabled, the HPCI system was inoperable. Operators immediately notified the I&C technicians of what had occurred. The I&C technicians then relanded the wires, restoring power to the HPCI system initiation logic. Operators then opened the isolation valve, and the HPCI system was thus returned to operable status. This event was caused by a less than adequate procedure. The procedure directed wires to be lifted from the time delay relay but did not state that the HPCI system initiation logic would be disabled. Also, with the wires lifted, the normal neutral circuit was interrupted, resulting in the current path being directed through two adjacent relays. One of these relays changed position due to the current passing through it, which actuated the isolation logic for the isolation valve. The valve closed as designed. Corrective actions for this event included restoring the HPCI system to operable status and prohibiting use of the affected procedure until it has been corrected. Additional procedure reviews will be conducted to prevent similar events from occurring, and if other reportable conditions are identified, a revision will be issued to this LER.
3661997002 | Hatch 2, Hatch 1 | 03/25/1997 | 04/22/1997 | 9704290241 | <strong>Grounded Jumper Causes Blown Fuse and Engineered Safety Features Actuations</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 3/25/97, Unit 2 was in the refuel mode with the reactor pressure vessel head removed and the core partially unloaded. No fuel movement was in progress. Unit 1 was in the run mode at a power level of 2558 CMWT (100 percent of rated thermal power). An electrician was replacing the coil in a General Electric type CR120A relay when he accidentally grounded a jumper. This caused a fuse to blow in the Group 2 primary containment isolation system (PCIS) logic. Group 2 PCIS valves were already closed. However, several valves did close in response to the signal. Operations personnel reopened the valves that were needed for the plant condition which existed at the time and left the remainder closed. jumper. The root causes of this event were less than adequate policies regarding the working conditions inside the involved control room panel and the use of jumpers. These policies allowed difficult working conditions to exist without remediation in control room panel 2H11-P623 and did not require the use of jumper designs which could have reduced the risk of installing jumpers in this panel. Corrective action for this event included replacing the blown fuse. In addition, the policies which contributed to this event will be reviewed by 6/1/97.
3661997003 | Hatch 2 | 03/28/1997 | 04/22/1997 | 9704290244 | <strong>Excessive Leakage Identified on Secondary Containment Bypass Valves</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 3/28/97 at 1110 EST, Unit 2 was in the Refuel mode with fuel in the vessel and the reactor cavity flooded for refueling operations. At that time, plant personnel determined Primary Containment Isolation Valves 2G11-F003 and 2G11-F004, drywell floor drain sump pump isolation valves, had failed their associated Local Leak Rate Tests. Both valves are located in the same penetration and are classified as secondary containment bypass valves because the sump drain piping is routed to the Radwaste Building which is located outside the secondary containment and, consequently, not served by the Standby Gas Treatment System. The causes of the failures of these two valves include undersized valve operators and inappropriate valve and operator orientation. Corrective actions for this event included moving valves 2G11-F003 and 2G11-F004, and 2G11-F019 and 2G11-F020, drywell equipment drain sump pump isolation valves, to a different location so they could be oriented vertically and installing a different type and size of valve and operator.
3661997004 | Hatch 2 | 03/31/1997 | 04/29/1997 | 9705060390 | <strong>Inaccurate List of Primary Containment Isolation Valves Results in Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 03/31/97 at 1439 EST, Unit 2 was in the refuel mode with the vessel head removed and the core partially loaded. At that time, an engineer from the Nuclear Safety and Compliance (NSAC) department was reviewing a letter from the plant's Architect/Engineer (A/E) regarding related tables in the Hatch Unit 2 Final Safety Analysis Report (FSAR) and Technical Requirements Manual (TRM). The engineer realized that four primary containment isolation system (PCIS) valves had been omitted from a monthly surveillance procedure which checks PCIS valve position indicating lights. Since the unit was in the refuel mode at the time, the primary containment was not required to be operable, and no immediate actions were required. This event was caused by an incomplete listing of PCIS valve position indications that are considered qualified post accident monitoring instrumentation in Unit 2 FSAR Table 7.5-1 and TRM Table 10.3-1. Valve position indications for automatic isolation valves are considered Type B variables in accordance with Regulatory Guide 1.97, Revision 2. surveillance procedure. Corrective actions for this event included performing the missed surveillance, reviewing both units' surveillance procedures for similar omissions, and revising affected procedures. These actions are complete. In addition, the FSAR and TRM will be revised.
3661997005 | Hatch 2, Hatch 1 | 04/02/1997 | 04/25/1997 | 9705060085 | <strong>Personnel Error Results in Unplanned Automatic Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 4/2/97, at approximately 1740 EST, Unit 1 was in the Run mode at 2558 CMWT (100 percent of rated thermal power) and Unit 2 was in the Refuel mode on the eighteenth day of a scheduled refueling outage with the fuel loaded in the reactor core and the reactor vessel head removed. Licensed personnel were in the process of returning the Unit 2 Emergency 4160V 2F bus to service following preventive maintenance on the bus switchgear. During the performance of a step in the restoration sequence, Emergency Diesel Generator 1B, which provides onsite emergency power for the 2F emergency bus, automatically started. The 2F emergency bus had not yet been reenergized as part of the return to service activity. Therefore, the protection logic sensed no power on the bus and generated an actuation signal to the 1B EDG. This resulted in an unplanned, automatic actuation of an engineered safety feature (ESF). However, the EDG did not tie to the bus because the EDG output breaker was racked-out under a clearance. Operations personnel confirmed proper operation of the EDG. Personnel then proceeded with returning the bus to service. The 2F emergency bus was reenergized at 1802 EST. Following completion of the restoration, at 1827 EST, the EDG was secured and returned to the standby mode. The cause of the event was cognitive personnel error resulting in the restoration sequence of the bus being incorrect for the plant configuration and less than adequate procedure. Corrective actions included restoring the bus to service, securing and placing the EDG in standby, counseling licensed personnel with regards to the need for attention to detail in restoring equipment to service, and revising procedures.
3661997006 | Hatch 2 | 04/07/1997 | 05/07/1997 | 9705140033 | <strong>Data Entry Error Results in Missed Technical Specifications Surveillance on Source Range Monitors</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 4/7/97 at 2330 EDT, Unit 2 was in the refuel mode with fuel in the vessel and the reactor vessel head studs being tensioned in preparation for the vessel leakage test. At that time, licensed personnel performed control rod movement in support of refueling outage activities without all the prerequisites for control rod movement being satisfied. Specifically, the channel functional test and determination of signal-to-noise ratio for the source range monitors (SRMs) had not been performed within the previous 7 days; therefore, the SRMs should have been considered inoperable. By moving a control rod with the SRMs inoperable, the plant was placed in a condition prohibited by the Technical Specifications. The cause of this event was a data entry error on the part of the surveillance scheduler. Specifically, the due date entered for the SRM surveillance was incorrect, thus, control room personnel believed that the surveillance was current. Corrective actions for this event included suspending control rod movement, performing the surveillance, and counseling the responsible individual. In addition, independent verification will be required for manual surveillance schedule updates, and the surveillance scheduling software will be enhanced.
3661997007 | Hatch 2 | 04/22/1997 | 05/08/1997 | 9705210049 | <strong>Loss of Main Condenser Vacuum Results in a Main Turbine Trip and Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 4/22/97 at 1907 EDT, Unit 2 was in the Run mode at a power level of 1418 CMWT (55 percent rated thermal power). At that time, the reactor shut down automatically on Turbine Stop Valve and Turbine Control Valve fast closure when the turbine tripped on low condenser vacuum. Water level decreased due to void collapse from the rapid reduction in power and the trip of the operating Reactor Feedwater Pump (RFP) on low condenser vacuum. The decrease in water level resulted in receipt of Group 2 and Group 5 Primary Containment Isolation System isolation signals and closure of the Group 2 and Group 5 Primary Containment Isolation Valves per design. Water level reached a minimum of approximately 45 inches below instrument zero (113.44 inches above the top of the active fuel) resulting in automatic initiation of the Reactor Core Isolation Cooling (RCIC) and High Pressure Coolant Injection (HPCI) systems per design. Secondary containment automatically isolated and all four trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low low water level per design. Level was restored to normal within one minute by the RCIC and HPCI systems and the standby RFP. Pressure reached a maximum value of 980 psig; no Safety/Relief Valves lifted nor were any required to lift to reduce or control pressure. This event was caused by reduced heat rejection from the main condenser resulting in a heat buildup in the condenser and a decrease in vacuum. The condenser waterboxes were vented, the circulating pump inlet screens were cleaned, and the redundant steam jet air ejector was placed into service.
3661997008 | Hatch 2 | 08/18/1997 | 09/10/1997 | 9709170158 | <strong>Main Pump Journal Bearing Damage Renders the HPCI System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 8/18/97 at 2125 EDT, Unit 2 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, personnel discovered damage to the High Pressure Coolant Injection (BPCI) system main pump outboard mechanical sea]. Upon being informed of the damage found, Operations personnel declared HPCI inoperable. On 8/20/97, personnel, during disassembly of the outboard journal bearing to access the seal, found the bearing damaged. The bearing's babbit material contained numerous grooves several mils deep; babbit material partially blocked the housing oil port, and the top surface of the bearing indicated shaft impact. The damage to the bearing evidently led to the seal damage by allowing increased shaft vibration in the seal area. This event apparently was caused by small particles that contaminated the bearing housing. The contamination lodged between the bearing and the pump shaft damaging the babbit material. The damage to the bearing led to increased pump shaft vibration which eventually was sufficient in magnitude to damage the seal. The source and type of contamination could not be determined. Corrective actions included replacing the inboard and outboard pump bearings, rebuilding the pump thrust bearing, replacing the outboard seal, draining, flushing, and cleaning the oil system, replacing the oil system filters, checking alignment using proximity probes, and performing procedures 34SV-E41-002-2S, "HPCI Pump Operability," and 34IT-E41-003-2S, "BPCI Turbine Speed Control Test." Operations personnel returned the BPCI system to operable status on 8/24/97 at 0415 EDT.
3661997009 | Hatch 2 | 09/11/1997 | 10/07/1997 | 9710150019 | <strong>Removal of DG Battery Chargers From Service Results in Inoperability of Both the 2A and 2C DG DC Electrical Power Subsystems</strong><br /><i>Abstract:&nbsp;</i>On 9/11/97 at 0907 EDT, Unit 2 was in the Run mode at a power level of 2558 CMWT (100 percent rated thermal power). At that time, the control room received the "Battery Volts Low or Fuse Trouble" annunciator for the 2C Emergency Diesel Generator (DG), followed at 0910 by the same annunciator for the 2A DG. Upon investigating, operations personnel found that the normal and standby battery chargers for both the 2A and 2C DGs were disconnected. This caused battery voltage to decrease, resulting in the annunciators alarming. Personnel concluded that having no battery charger in service for either DG DC electrical power subsystem rendered each subsystem inoperable. In this condition, the Technical Specifications require the unit to enter the Limiting Condition for Operation (LCO) 3.0.3. This event was caused by personnel error. A plant equipment operator (PEO) did not use a procedure to change each 2A and 2C DG battery charger from the normal charger to the standby charger. This resulted in all four chargers being disconnected from their respective batteries, effectively causing both DC power subsystems for each DG to not meet their Technical Specifications operability requirements. Corrective actions have included counseling the PEO and will include review of this LER by all other Operations PEOs as part of their beginning of shift training.
3661997010 | Hatch 2 | 11/20/1997 | 12/08/1997 | 9712160419 | <strong>Manual Reactor Shutdown Results in Water Level Decrease and Group 2 and 5 PCIS Actuations</strong><br /><i>Abstract:&nbsp;</i>On 11/20/97 at 2053 EST, Unit 2 was in the Run mode at a power level of 1816 CMWT (71 percent rated thermal power). At that time, personnel manually scrammed the reactor so the condensate system could be isolated to repair damage. Water level decreased due to void collapse from the rapid reduction in power resulting in Group 2 and 5 primary containment isolation system isolation signals and closure of the Group 2 and 5 primary containment isolation valves. Level reached a minimum of approximately 38 inches below instrument zero (120.44 inches above the top of the active fuel) causing automatic initiation of the reactor core isolation cooling (RCIC) and high pressure coolant injection systems. Level was recovered by the reactor feedwater pumps (RFPs) before either system could inject to the vessel. Secondary containment automatically isolated and the Unit 1 and Unit 2 standby gas treatment systems automatically started per design. Level was restored to normal within one minute by the RFPs and maintained by the RCIC system. Pressure reached a maximum value of 990 psig; no safety/relief valves lifted nor were any required to lift. This event was caused by component failure. The hinge pin in discharge check valve 2N21-F019A broke resulting in the valve failing to close when condensate booster pump 2N21-C002A was removed from service. This caused high pressure water to damage the pump and its low pressure suction piping and bellows. Corrective actions include repairing the damage. The failure of the hinge pin appears to be an isolated case.
3681997001 | Arkansas 2 | 01/29/1997 | 02/28/1997 | 9703070111 | <strong>Inadequate Surveillance Caused By Personnel Error Resulted In Two Degraded Steam Generator Tubes Being Left In Service During The Subsequent Cycle Of Operation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 097%. On January 29, 1997, it was determined that steam generator tube surveillances which were performed during refueling outage 2R11 had failed to identify existing tube flaws for further evaluation as required by the steam generator tube surveillance program. Testing conducted during the next outage (2F96-1) identified tubes 16-56 and 70-98 in the 'A' steam generator as being degraded equal to or greater than 40 percent through-wall. A review of 2R11 data revealed that tube 16-56 had been classified as clean by one analyst and as a non-quantifiable indication by another. Ultimately tube 16-56 was dispositioned as clean and removed from further testing scrutiny. Review of the 2R11 data concluded that this tube should have been classified as a distorted support indication and would likely have been removed from service if further testing had been conducted. Additionally, the review identified that tube 70-98, which was dispositioned as clean during 2R11, should also have been identified for further testing. Both tubes contained axial cracks at the first tube support plate on the hot side of the generator. The root cause of this event was personnel error with contributing causes of inadequate training and a lack of adequate oversight of the testing process. Corrective actions will include increased Entergy oversight of the testing process and enhancements to the analyst training process.
3681997002 | Arkansas 2 | 02/04/1997 | 03/06/1997 | 9703110256 | <strong>INADEQUATE CONFIGURATION CONTROL RESULTED IN CLOSED PRESSURE SWITCH ISOLATION VALVES THAT COULD HAVE PREVENTED ONE TRAIN OF EMERGENCY FEEDWATER FROM AUTOMATICALLY SWITCHING THE PUMP SUCTION TO SERVICE WATER AND CAUSED OPERATION PROHIBITED BY TECHNICAL SP</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 097%. During monthly surveillance testing of the motor-driven Emergency Feedwater (EFW) pump on February 4, 1997, the function that provides automatic transfer of the pump suction source to Service Water during certain conditions was discovered to be inoperable. Instrument isolation valves for two pressure switches, one of which provides the signal to cause the suction source transfer, were found closed. These valves are located in tubing between the root valve and the instruments. The root cause evaluation could not positively determine if the valves had been left closed following pressure switch calibration on January 6, 1997, or had been inadvertently closed as part of operation of similar valves for other instruments in that area on January 7, 1997. the EFW train to have been inoperable for a period longer than allowed by Technical Specifications. The other EFW train had also been inoperable for maintenance and testing for short periods while the switch was isolated. The valves were opened, the surveillance test was successfully completed, and verification of the valve positions for similar instrumentation was completed. The root cause of the condition was attributed to inadequate configuration control of the instrument isolation valves. Corrective actions include identification and implementation of appropriate configuration control mechanisms, training enhancements, and procedure changes.
3681997003 | Arkansas 2 | 05/14/1997 | 10/14/1997 | 9710210045 | <strong>Technical Specifications Allowing Operation With One Channel of Refueling Water Tank Level Tripped Established The Potential For Premature Initiation Of Recirculation Actuation Signal During A Loss Of Coolant Accident Placing The Plant Outside Its Design</strong><br /><i>Abstract:&nbsp;</i>Design Engineering personnel discovered a deficiency in the ANO-2 Technical Specifications (TS) that provided a potential for premature actuation of the Recirculation Actuation Signal (RAS) during a Loss Of Coolant Accident (LOCA). The TS allow indefinite operation with one channel of Refueling Water Tank (RWT) level in a tripped condition. If a LOCA were to occur in this condition, the failure of another RWT level channel low could cause premature RAS actuation before sufficient water was available in the containment sump to provide the Emergency Core Cooling System (ECCS) design functions. Only two instances (1981 and 1985) of ANO-2 actually having operated with an RWT level channel tripped have been identified, and those were of short duration. The potential for a single failure preventing ECCS functions from a normal, allowable operating configuration placed the plant outside its design basis. As part of the corrective actions, a similar condition was discovered involving the potential for not automatically isolating a faulted Steam Generator during certain steam line break scenarios if a channel of Steam Generator differential pressure (Emergency Feedwater Actuation Signal) was tripped. The root cause has been identified as a deficiency in the original Technical Specifications. Administrative controls have been established to prevent placing a channel in a tripped state. A TS amendment request has been submitted.
3681997005 | Arkansas 2 | 06/04/1997 | 07/03/1997 | 9707080354 | <strong>Main Steam Safety Valve As-Found Lift Values Did Not Meet Technical Specification Requirements Due To A Combination Of Maintenance, Testing, And Design Factors</strong><br /><i>Abstract:&nbsp;</i>Prior to and during a scheduled refueling outage, testing revealed that eight of ten Main Steam Safety Valves (MSSVs) had as-found lift values exceeding the maximum of one percent above the setpoint allowed by Technical Specifications. A root cause evaluation team, including consultants and representatives from the MSSV vendor, conducted an extensive assessment of the condition. This included a significant number of tests and inspections of the MSSVs at an off-site test facility. Several potential contributing factors were identified and investigated. The team was unable to identify a conclusive root cause. The cumulative effect of a number of different maintenance, testing, and design factors was assigned as the most probable cause. Before startup from the outage, nine of the ten MSSVs were replaced with valves that had been fully inspected and tested at the off-site facility. Engineering evaluations demonstrated that the as-found lift values would have allowed the MSSVs to provide the required safety functions if events requiring those functions had occurred during the previous operating cycle.
3681997006 | Arkansas 2 | 06/06/1997 | 09/05/1997 | 9709110089 | <strong>Inadvertent Emergency Diesel Generator Start Which Resulted From Inadequate Written Guidance Regarding System Component Testing</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1997, at approximately 0347, an inadvertent start of the #2 Emergency Diesel Generator (EDG) occurred while testing the air start solenoid valves. During a final review of Generic Letter (GL) 96-01 review information, it was determined that the two redundant air start subsystems for each EDG were not being tested separately to verify their ability to respond to an Engineered Safety Features Actuation System initiation signal. Although not required by the Technical Specifications, this verification is within the scope of GL 96-01 recommendations. A job order was prepared to test the air start solenoid valves independently. Even though the test required the air start system isolation valves to be closed, the first time that an air start solenoid valve for the #2 EDG was actuated open, the engine started. Air pressure trapped in the header and filters between the isolation valve and the air start solenoid valve was sufficient to roll and start the engine. The engine started easily because it was still warm and pre-lubed from a previous run. The root cause of this event was inadequate written communication in that the job order did not contain instructions to vent the air start header after isolation. The job order was revised to require venting the header and testing was satisfactorily completed. Appropriate personnel will be trained regarding the lessons learned from this event.
3681997007 | Arkansas 2 | 06/26/1997 | 07/28/1997 | 9708050140 | <strong>Fuel Handling Area Ventilation Flow Rate Less Than Technical Specification Requirement During Crane Operation With a Load Over The Storage Pool Due To Personnel Error Regarding Verification Of Equipment Condition Before Evolution Authorization</strong><br /><i>Abstract:&nbsp;</i>Crane operation with a load over the spent fuel storage pool occurred while the fuel handling area ventilation system flow rate was less than required by Technical Specifications. The load, a filtration/vacuum assembly weighing 465 pounds wet, was moved from the pool to the cask loading pit in approximately ten minutes. The ventilation system flow controller had been calibrated but post-maintenance testing to establish acceptable flow rate had not been completed when the move occurred. The radiation monitoring instrumentation normally used to verify flow rate was in an abnormal configuration for routine testing. The ventilation fan had been started on a previous shift for an activity that did not require the flow rate to meet the Technical Specifications value. The root cause of the event has been attributed to personnel (work practices) error by not adequately verifying that Technical Specification requirements were being met before authorizing use of the crane. The actual ventilation system flow rate was approximately eighty-five percent of the required value during the activity. No abnormal releases of radiation occurred as a result of this event. Corrective actions include a "lessons learned" for Operations personnel and additional guidance in crane hold card instructions requiring verification of acceptable flow before placing it in service.
3681997008 | Arkansas 2 | 10/02/1997 | 10/27/1997 | 9711040096 | <strong>Hindsight Review Of Eddy Current Data From 1996 Steam Generator Inspection Indicated That Not Having Dispositioned Distorted Support Indications For Further Characterization Resulted In Operation Prohibited By Technical Specifications When Potentially De</strong><br /><i>Abstract:&nbsp;</i>During refueling outage 2R12 in May and June of 1997, eddy current data from Steam Generator tube eddy current testing was compared with data obtained in late 1996 in outage 2F96-1. It was determined that up to 25 tubes could have been dispositioned as distorted support indications (DSIs) and further characterized with motorized rotating pancake coil (MRPC) but were not. This hindsight analysis to evaluate flaw growth rate revealed that the indications in these 25 tubes could have been greater than 40 percent through-wall during startup from outage 2F96-1. The tubes remained in service for approximately five months until 2R12 when they were removed from service by mechanical plugging. Although the signals were within the latitude of analyst judgment available at that time, a review indicated that some of them could have been dispositioned for further evaluation. Startup and operation with tubes containing indications that may have been greater than 40 percent constituted operation prohibited by Technical Specifications. The root cause of this condition has been attributed to personnel error on the part of the eddy current analysts. Corrective actions to enhance analyst training and inspection process oversight were implemented after the outage in which this condition originated. The condition did not compromise Steam Generator structural integrity.
3691997001 | McGuire 1 | 03/18/1997 | 05/19/1997 | 9705280056 | <strong>Failure To Comply With Technical Specification 3.6.3 Following Valve 1CF-26AB Inoperability</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 1 (Power Operation) at approximately 28% Rated Thermal Power (RTP). Event Description: On November 27, 1996, at 0040, with the unit at 100% RTP, a hydraulic fluid leak on the actuator for valve 1CF-26AB, a containment and feedwater isolation valve, resulted in a condition under which the valve could not meet Technical Specifications (T.S.) requirements. T.S. 3.6.3 requires inoperable Containment Isolation Valves to be closed and deactivated within 4 hours, or the unit be placed in Hot Shutdown within the following 6 hours. During subsequent Maintenance troubleshooting, this valve was not properly maintained deactivated and closed until approximately 1020 on November 28, 1996. Event Cause: The failure to comply with all of the requirements of T.S. in a timely manner was caused by misinterpretation of reference documents regarding applicability of T.S. 3.6.3 to this valve. Corrective Action: The correct application of T.S. 3.6.3 to this valve has been clarified to Operations, Engineering, and Regulatory Compliance personnel involved in these operability determinations.
3691997002 | McGuire 1, McGuire 2 | 03/13/1997 | 05/12/1997 | 9705150186 | <strong>Inoperability of Feedwater Isolation Valves Due To Hydraulic Oil Degradation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Unit Status: Unit 1 Was Defueled and unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: During Preventive Maintenance (PM) of the hydraulic actuators for Feedwater Isolation valves (FWIVs) 1CF-28AB and 1CF-30AB, deenergizing the train A or B safety solenoids did not cause the accumulator to discharge pressure and close the valve. Subsequent testing of Unit 2 FWIVs determined that valves 2CF28AB & 2CF30AB were unable to close within the required time. Event Cause: The FWIV failures are attributed to hydraulic oil degradation which produces gel and phosphate salts that interfere with the movement of critical parts within the solenoid valves. oil degradation occurs naturally over time but is accelerated with higher water content and higher oil temperature, coincident with stagnated oil. Design of the actuator exposes the oil to heat from the normally energized solenoid coils. Corrective Action: The FWIV solenoid coils and plungers were replaced or cleaned to remove the gel, phosphate salts, and degraded oil. The FWIVs were then successfully retested. The PM frequency to inspect and clean the solenoids coils and plungers will be changed from 5 years to 1 Refueling outages (RFO). Modifications were implemented to reduce the solenoid coil operating temperature.
3691997003 | McGuire 1, McGuire 2 | 03/26/1997 | 04/23/1997 | 9704290282 | <strong>Inoperability of Both Trains Of The Control Room Ventilation System Due To Isolated Air Intake Valves</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Unit Status: Unit 1 was Defueled and Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On March 26, 1997, at 0854, radiation monitor 1EMF-43A spiked, procedurally requiring Operations personnel to close the A Train control room ventilation (VC) outside air intake valves. The B Train VC outside air intake valves were already closed to support maintenance on 1EMF-43B; therefore, both trains of air intake valves were closed causing the VC system to be briefly inoperable. At 0856, with the alarm cleared, the A Train valves were reopened, restoring the A Train VC system to operable. Event Cause: This event was caused by a spurious spike on a radiation monitor associated with the Control Room Ventilation Air Intake System. Additionally, the alarm response procedure did not provide optimal response for the plant configuration existing at the time of the event. Corrective Action: The radiation monitor will be evaluated to determine if any changes are needed in the design or maintenance of this equipment to minimize spiking. procedure will be reviewed to ensure appropriate guidance with varying initial system configurations.
3691997004 | McGuire 1, McGuire 2 | 03/20/1997 | 06/02/1997 | 9706100037 | <strong>Main Steam Safety Valve Technical Specifications Inaccuracies</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was Defueled and Unit 2 was in Mode 1 (Power Operation) at 100 percent power at the time of discovery. Event Description: Technical Specification Table 3.7-1, Maximum Allowable Power Range Neutron Flux High Setpoint With Inoperable Steam Line Safety Valves During Four Loop Operation, specifies a non-conservative maximum allowable flux setpoint when applied to one or more inoperable Main Steam Safety Valves on the same loop. McGuire has never operated in a condition requiring plant operation to be restricted due to inoperable main safety valves. Event Cause: This event was caused by an incorrect vendor-supplied algorithm used to initially calculate the Power Range Neutron Flux High Setpoint for inoperable steam line safety valves. Corrective Action: Administrative directions are in place providing plant operation guidelines for operators when one or more steam line safety valves are inoperable. Additionally, a revision to Technical Specification Table 3.7-1 will be submitted to the NRC to change the appropriate setpoint values.
3691997006 | McGuire 1 | 05/12/1997 | 06/11/1997 | 9706180244 | <strong>Unit 1 Engineered Safety Features Actuation Due To Tripping Of The Main Feedwater Pumps</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 3 (Hot Standby) at 0 percent power. Event Description: On May 12, 1997, at 1458, an Engineered Safety Features (ESF) actuation occurred on Unit 1 when the Main Feedwater (CF) Pumps tripped, causing automatic start of the Auxiliary Feedwater Pumps on both trains. As a further result, the Steam Generator Blowdown system was automatically isolated, and the Nuclear Service Water Pump automatically started on Train A. Event Cause: This event was caused by an unknown, possible manufacturing/installation deficiency associated with the level switches providing High-High water level protection for the Outboard Doghouse, coupled with a spurious actuation of another switch in the logic. The deficiency had caused one switch on each train to remain in the closed position. Momentary actuation of a second switch satisfied the 2 out of 3 logic for that train, generating a trip signal to the CF Pumps. This event is considered to be of no significance with respect to safety of the public since minimal feedwater flow was required for the operating Mode and power level at the time of the event, and no transient resulted from the event. Corrective Action: Due to the sensitivity of these components, procedural guidance with regard to the functional verification of this equipment after maintenance will be enhanced.
3691997007 | McGuire 1 | 05/14/1997 | 06/13/1997 | 9706180291 | <strong>Unit 1 Reactor Trip During Power Range Nuclear Instrumentation Testing</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - Mode 3 (Hot Standby) at 0 percent power with Shutdown Rod Banks A and B withdrawn. Event Description: On May 14, 1997, at 1104, the Unit 1 Reactor tripped during performance of Power Range (PR) Detector N42 Analog Channel Operational Testing (ACOT). Prior to the performance of the ACOT, PR Detector channel N41 had been bypassed due to being connected to the Reactivity Computer in preparation for Zero Power Physics Testing. The procedure chosen to bypass the N41 channel failed to bypass Permissive P-8, which unblocks reactor trip due to turbine trip. During simulation of reactor power rising to 120 percent on PR Detector N42 per the ACOT, Permissive P-8 logic was met on two out of four channels which, along with the tripped turbine, tripped the reactor. Permissive logic P-10 was met on two out of four channels, which de-energized both Source Range Detectors causing momentary entry into Technical Specification 3.0.3. A Feedwater Isolation signal occurred due to a Reactor trip signal concurrent with the Low Tavg Bistables. Event Cause: This event was caused by personnel utilizing an inappropriate procedure for the existing plant conditions. This event is considered to be of no significance with respect to the safety of the public. Corrective Actions: Corrective actions include a review of subject and associated procedures to determine any necessary enhancements or revisions.
3691997008 | McGuire 1, McGuire 2 | 05/12/1997 | 06/11/1997 | 9709190161 | <strong>Inoperability Of The Auxiliary Feedwater System Due To Potential Air Entrainment</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event discovery, Unit 1 was in Mode 3 (Hot Standby) at 0 percent power and Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On May 12, 1997, a scenario was identified that could potentially affect Auxiliary Feedwater (CA) system operability. If all CA system Pumps are operating with suction aligned to the Upper Surge Tank (UST), and the UST is not isolated prior to emptying, the possibility exists for air to accumulate in the high points of the CA Pump suction piping upon automatic swapover to the assured safety makeup source. As the UST refills from recirculation flow, the air accumulated in the suction piping could be forced into the pumps rendering them inoperable. Event Cause: The ongoing engineering analysis is considering many different postulated secondary system failure scenarios. At this time, no failure mode has been identified which renders the CA system past or presently inoperable. If further evaluation of this postulated scenario should determine that a valid operability issue exists, the event cause will be determined and subsequently reported in a revision to this report. Corrective Action: Engineering evaluation of the issue will continue. In the interim, a contingency plan documenting compensatory actions has been put in place by an Operations Special order to assure continued operability of the CA system.
3691997009 | McGuire 1, McGuire 2 | 09/06/1997 | 10/06/1997 | 9710080173 | <strong>Reactor Trip On Both Units Due To An Equipment Failure And Operation Prohibited by Technical Specifications Due To Failure To Comply With Required Action Statements</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On September 6, 1997, at 2146, the trip of an auxiliary supply breaker, while the Units were in an abnormal alignment, caused the loss of non-vital power to plant components on both Units. For Unit 1, this resulted in a trip of both Main Feedwater Pumps followed by a main Turbine and subsequent Reactor trip. For Unit 2, it resulted in the closure of the Main Steam Isolation Valves followed by a Reactor trip on Pressurizer high pressure. Additionally, the power loss resulted in loss of the automatic operating function for the Pressurizer Power Operated Relief Valves (PORVs) on both Units, and loss of indication from the Process Radiation Monitor associated with one set of the Control Room Ventilation Outside Air Intakes. This equipment was inoperable for a period of 62.5 minutes, exceeding Technical Specification (TS) limits of 60 minutes without implementation of required actions. Event Cause: The cause of the breaker trip has been determined to be heat build-up created by a loose cable connection on the load side of the breaker, actuating breaker thermal trip units. The cause of the loose connection is a construction/installation deficiency. A contributing factor is management deficiency due to lack of establishing adequate preventive maintenance. Failure to implement required TS actions with regard to the Pressurizer PORVs and Process Radiation Monitor is attributed to failure of Control Room personnel to recognize the need to do so. With the loss of KXA, multiple Control Room indications were lost. Due to the absence of these indications and lack of procedural direction to alert them, actions were not taken within the one hour requirement. Corrective Action: Corrective actions include evaluation of preventative maintenance on shared vital and auxiliary control and instrumentation buses, development of procedures for plant operation during loss of instrumentation and control buses, enhancement of existing procedural guidance, and training for all licensed operations personnel. To be reported through EPIX
3691997010 | McGuire 1, McGuire 2 | 10/23/1997 | 11/21/1997 | 9712020234 | <strong>Potential Existed For Inadequate Margin To Be Maintained With Regard To Reactor Coolant System Flow Rate Due To Inadequate Analytical Basis For the Associated Technical Specification</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event discovery Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was de-fueled. Event Description: During analysis associated with engineering support work for McGuire and Catawba Nuclear Stations, it was discovered that the analytical bases for operation at reduced power levels to compensate for less than full Technical Specification (TS) allowed Reactor Coolant system flow were insufficient and; therefore, potentially non-conservative. The TSs allow operation with power reduced by 2 percent for each 1 percent that Reactor Coolant system flow is less than TS specified flow, for Reactor Coolant system flows as low as 95 percent of full TS flow. These operating conditions are based on maintaining the initial Departure From Nucleate Boiling Ratio (DNBR) margin. While the analysis is valid for many of the Updated Final Safety Analyses Report (UFSAR) Chapter 15 transients, it does not demonstrate that the reduction in initial power level adequately compensates for lower flow. McGuire has never operated in this reduced power level condition since Reactor Coolant system flow has always been maintained in excess of the full power value. Event Cause: This event is assigned a cause of analysis deficiency resulting in technical inaccuracies in written communication. The vendor information supplied to Duke Power Company during development of the TS did not include sufficient analysis to support the power/flow tradeoff as presented in TS. Corrective Action: Engineering guidance was provided to Operations prohibiting operation with NC flow less than 382,000 gpm. A TS change will be submitted to eliminate potential non-conservatism. n replaced by EPIX
3691997011 | McGuire 1, McGuire 2 | 11/11/1997 | 12/10/1997 | 9712150378 | <strong>Inadequate SSPS Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was Defueled at the time of discovery. Event Description: As a result of an engineering review, on November 11, 1997 Catawba and McGuire Nuclear Stations discovered the Solid State Protection System (SSPS) surveillance testing to be inadequate. Because this is considered to be a missed surveillance, McGuire and Catawba immediately entered into Technical Specification 4.0.3. This provided twenty four hours for both plants to complete the surveillance. Later that afternoon, the vendor was contacted to discuss the testing needed to adequately check the SSPS. McGuire, Catawba, and the vendor agreed on the test and appropriate surveillance procedures were revised. On November 12, 1997, both trains on each unit at Catawba and McGuire were tested satisfactorily. The action statement for Technical Specification 4.0.3 was exited prior to exceeding the twenty four hour deadline. Event Cause: The cause of this event is inadequate test design supplied by the vendor. The test procedures were supplied with the SSPS. Corrective Action: The surveillance procedures for both SSPS trains on each McGuire unit were revised. The SSPS trains on both McGuire units were successfully tested. *NPRDS no longer exists, the failure will be reported through EPIX
3701997001 | McGuire 2 | 05/27/1997 | 06/25/1997 | 9707010315 | <strong>Diesel Generator Load Sequencer 2B Inadvertent Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On May 27, 1997, at approximately 1135, Instrument and Electrical (IAE) Technicians were performing the Train B Diesel Sequencer Timer Calibration when a partial actuation of Train B Blackout equipment occurred. The Turbine Driven Auxiliary Feedwater Pump and the 2B Nuclear Service Water Pump auto started, and several Nuclear Service Water valves realigned. Subsequently, when IAE Technicians were verifying a sliding link was securely open, a partial actuation of Train B Safety Injection (SI) equipment occurred. No abnormal equipment actuation was identified and operator actions were appropriate for the event. The health and safety of the public and plant personnel were not affected as a result of this event. This event is not considered significant. Event Cause: The partial actuation of Blackout equipment was caused by inadequate development and review of a change made to the Sequencer Timer Calibration procedure. The partial actuation of SI equipment could not be conclusively determined, but is believed to have been caused by IAE personnel inadvertently making contact with both sides of a sliding link while verifying the link was securely open. Corrective Action: A review of similar procedures which test safety related logic circuits is being conducted to apply lessons learned from this event. Additionally, a communication of lessons learned on this event will be given to appropriate IAE and Plant Engineering personnel.
3701997002 | McGuire 2 | 07/11/1997 | 11/03/1997 | 9711120035 | <strong>Reactor Trip Due To Reactor Coolant Pump Motor Failure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - Mode 1 (Power Operation) at 100 percent power. Event Description: On July 11, 1997, at approximately 0516 hours, Unit 2 Reactor Coolant (NC) Pump 2D tripped due to a ground fault in the motor stator winding. Subsequently, the reactor tripped on low flow in one of four loops with reactor power greater than P-8. This event is not considered to be significant with respect to the health and safety of the public. Event Cause: A design/manufacturing deficiency existed in the NC Pump motor. The inadequate tying down of the stator wiring end turns to the stator surge ring was found to have allowed excessive vibration of the stator windings. This caused degradation of the winding insulation during years of operation. The degradation resulted in a ground fault in the stator windings. Corrective Action: The 2D motor stator was replaced with a rewound spare. The two remaining NC Pump motor stators will be replaced during upcoming refueling outages for their respective Units. Upon completion of the NC Pump motor stator replacements, a long-term motor maintenance and monitoring program, consisting of on-line partial discharge testing and off-line electrical testing, will be implemented.
3701997003 | McGuire 2 | 07/18/1997 | 08/15/1997 | 9708200143 | <strong>Inoperability Of Ice Condenser Lower Inlet Doors Due To An Equipment Failure Caused By Unanticipated Environmental Interaction</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 5 (Cold Shutdown) at 0 percent power. Event Description: On July 17, 1997, inspection revealed that 10 doors in 8 of the 24 bays required more than the maximum opening force allowed by Technical Specifications. It was determined that the failure was caused by interference between the Door Frame Flashing and Lower Inlet Doors. The interference was removed and the doors retested satisfactorily. This event is considered to be of no significance with respect to safety of the public since the Ice Condenser would have been able to fulfill the design function with the doors in the as found condition. Event Cause: The cause of this event is determined to be equipment failure caused by unanticipated environmental interaction. The flashing had risen due to an uplift of the Ice Condenser Wear Slab. Movement of the Wear Slab has been attributed to water intrusion into the floor concrete, which along with several freeze/thaw cycles had caused the water/ice to expand and contract thus moving the floor slab. Corrective Action: Corrective actions include modifications to remove portions of the flashing which may cause interference, and initiation of monitoring of floor slab position during outages.
3731997001 | LaSalle 1, LaSalle 2 | 01/08/1997 | 02/07/1997 | 9702190075 | <strong>Special Report Not Written as Required by Technical Specifications When the Loose Parts Monitoring System was Inoperable During Power Operations</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. The Loose Parts Monitoring System (LPMS) was designed with an automatic tape recorder. In 1985, upon failure of the automatic recorder, it was removed. This is not in conformance with the response to Question Q221.14 of the FSAR or the SER for the FSAR which states that the recorder is installed. This design conformance discrepancy with the FSAR was documented with a Problem Identification Form (PIF) on November 5, 1996. During the subsequent detailed operability determination completed on January 8, 1997, it was identified that the system design also was not as described in Section 4.4.1 of the Safety Evaluation Report (SER). The design basis states that there is an automatic tape recorder that initiates on a loose part alarm. The system was declared inoperable on January 8, 1997, since no automatic recording function was available. It has been determined that the LPMS had been inoperable during power operations from 1985 to 1996 and no Special Report was prepared as required by Technical Specification Section 4.3.7.12. An automatic recording function will be installed to comply with the description in the FSAR, SER, and the UFSAR will be updated to describe the corrected configuration of the LPMS prior to the start up of either unit. The LPMS provides information only and is not considered in any design basis accident or transient analysis. The loss of this instrument is a non-significant risk contributor to core damage frequency and offsite release.
3731997002 | LaSalle 1, LaSalle 2 | 02/03/1997 | 06/24/1997 | 9707010139 | <strong>The Main Control Room and Auxiliary Equipment Room Ventilation System found outside of the design basis due to inadequate initial design.</strong><br /><i>Abstract:&nbsp;</i>The Main Control Room (MCR) ventilation (VC) and Auxiliary Electric Equipment Room (AEER) ventilation (VE) systems are engineered safety features designed to maintain habitable environments in their respective areas during normal and abnormal conditions. During certain heavy snow fall conditions, snow can enter the inlet filter for the air cooled condensing coil. Snow accumulation on the intake filter of the operating refrigeration unit, on occasion, results in a high differential pressure. Operator action has been taken to open an access panel door on the condensing unit to allow warmer building air into the condensing unit. This has had the effect of reducing incoming snow quantities and drying of the intake filters. Operation in this manner is outside the system design basis. The effects of the negative pressure caused by opening the doors have been analyzed and determined to be within the UFSAR limits. An analysis concluded that operation of the condenser fan in a degraded condition from snow build-up will not prevent the condensing unit from performing its design function. The cause of this event was inadequate initial ventilation system design, incomplete evaluation of operating requirements, and failure to recognize and correct these inadequacies in a timely manner. This resulted in operation of the system in a manner not described in the design basis.
3731997003 | LaSalle 1, LaSalle 2 | 02/13/1997 | 06/06/1997 | 9706170085 | <strong>Inadequate Procedure for Racking 4.16 KV Switchgear Breakers Results in Seismically Unqualified Condition Outside the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1997, LaSalle reported to the NRC that several safety-related 4.16 KV breakers were found to be racked in seismically unqualified positions. Therefore, the plant configuration was considered to be outside the design basis. The cause for this condition was an inadequate operations procedure for racking out 4.16 KV breakers and an incomplete seismic analysis. Immediate corrective action was to perform a walkdown of safety-related switchgear. Breakers found racked in a seismically unqualified position were returned to a qualified position. Corrective actions completed and planned include operator training, procedure revision, and an engineering evaluation to review the process, including implementation, for qualifying electrical switchgear and incorporating seismic limitation into operations procedures.
3731997004 | LaSalle 1 | 02/14/1997 | 03/17/1997 | 9703260156 | <strong>Incomplete Understanding of Engineered Safety Features Filter Testing Requirements Resulted in Non-Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. The Technical Specifications for Main Control Room (MCR) ventilation, Auxiliary Electric Equipment Room (AEER) ventilation and Standby Gas Treatment systems require surveillance testing of electric heaters and the charcoal and HEPA filters to demonstrate system operability. A System Functional Performance Review of the MCR ventilation system determined that Engineered Safety Feature air filtration testing performed at LaSalle was not in verbatim compliance with the Technical Specification. All three systems were already inoperable and this concern was added to the issues requiring resolution prior to declaring them operable. The cause of this event was an incomplete understanding of the verbatim requirements of the Technical Specification for testing of ESF ventilation systems. A Technical Specification change will be submitted to more clearly reflect the filter testing that is required to conform to Regulatory Guide 1.52. The testing discrepancies were not safety significant and both units were already shutdown.
3731997005 | LaSalle 1, LaSalle 2 | 02/20/1997 | 06/15/1998 | 9806190290 | <strong>Potential Loss of Both Trains of SGTS and Containment Pressure Suppression During the First 10 Seconds of a LOCA Due to Deficiencies in Original Design Analysis and Procedures</strong><br /><i>Abstract:&nbsp;</i>At 1415 hours on February 20, 1997, during a review of the draft for Improved Technical Specifications, a question arose regarding the potential for damaging the Standby Gas Treatment System in the event of a loss of coolant accident (LOCA) during routine containment purging or hydrogen recombiner testing. Subsequent review identified two other issues: 1) operating procedures allowed both the drywell and suppression chamber to be purged or vented simultaneously creating a bypass around the drywell floor, and 2) the containment purge system ductwork in the auxiliary building will fail in the event of a LOCA during purging. The consequences of these events would have been a potential increase of offsite and onsite doses. A design review of the containment purge and vent system has been performed. Design and procedure changes will be performed as required, to ensure proper operation of the system. The root causes of this event are unknown; however, the apparent causes of the event were weaknesses in the design, design review, and procedure review processes, in the early 1980's, when containment inerting was added to the design. These weaknesses apparently resulted in the design review missing the effect of design changes on the interfacing systems and the procedure reviews missing the improper valve alignments.
3731997006 | LaSalle 1, LaSalle 2 | 02/21/1997 | 03/24/1997 | 9704010436 | <strong>Diesel Generator Testing Did not Meet Surveillance Requirements Due to Misinterpretation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. Technical Specification Surveillance 4.8.1.1.2.d.4.a).2) requires that diesel generator LOCA load sequence testing include verification of start of all 'auto-connected loads.' Existing procedures did not test the start of Control Room and Auxiliary Electric Equipment Room Ventilation Systems (VC/VE) fans. This condition has existed since plant licensing in April 1982. This condition appears to have been caused by misinterpretation of the term 'auto-connected loads' while defining the scope of surveillance testing to prove diesel generator voltage and frequency recovery in the LOCA load sequence intervals. Corrective actions include: 1) The surveillance procedures for diesel generator LOCA load sequence testing are being reviewed for items in other systems that are required to be sequence start tested. 2) The procedures will be revised to include sequence start testing of the VC/VE fans and other loads found in the review. 3) Testing per the revised surveillance procedures will be performed prior to start-up of either unit.
3731997007 | LaSalle 1 | 02/25/1997 | 03/27/1997 | 9704010523 | <strong>Missed Technical Specification Surveillance on the High and Low Discharge Pressure Switches for the 1A RHR Pump Due to procedural and Human Performance Errors.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 25, 1997, the functional test of pressure switches on the Unit 1A Residual Heat Removal (RHR) pump discharge line was identified as past due. This test is required by Technical Specification 4.5.1.a.2.a. and was due to be completed per surveillance LIS-RH-316A by February 4, 1997. The surveillance had been rescheduled when a conflict occurred on the due date. An error in the instrument surveillance program indicated the test was not required with Unit 1 in Operating Condition 4. Controls in place to ensure management review of rescheduled surveillances failed to identify that this test delay would result in non-compliance with Technical Specification requirements. This resulted from a management deficiency in not establishing suitable accountability for tracking surveillances and human error in not adhering to review requirements. The safety significance of this event is minimal since shutdown cooling remained available to the reactor from the 1A RHR system and the Low Pressure Core Spray (LPCS) system. Two additional backup systems were also maintained as available. Corrective actions have been taken to correct the surveillance program and improve the administration and oversight for the plant's surveillance program.
3731997008 | LaSalle 1, LaSalle 2 | 02/20/1997 | 03/24/1997 | 9704010433 | <strong>Rod Block Monitor Not Enabled At Power Level Required By Technical Specifications Due To Nonconservative Test Method In An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 20, 1997, a determination was made that calibration procedures for the Unit 1 and 2 Rod Block Monitor (RBM) did not verify that the RBM would be enabled at prior to obtaining 30 percent Core Thermal Power (CTP) as required by plant Technical Specifications. This limit is established to ensure adequate protection against control rod withdrawal errors at high power. Subsequent investigation determined, on February 26, 1997, that on 4 occasions between 1988 and 1993 the RBM reference downscale bypass functions were calibrated in the decreasing power direction with setpoints which may have resulted in the RBM being enabled between 30.2 and 31.68 percent CTP. This was due to a hysteresis (reset differential) of as much as 2.7 percent between the decreasing and increasing setpoints. Due to Critical Power Ratio (CPR) margin present during low speed recirculation pump operation, there would have been no challenge of the Minimum Critical Power Ratio (MCPR) safety limit had a control rod withdrawal error event taken place. Thus, the safety significance of this event was minimal. This event was caused by inadequate procedures. The affected procedures and instrument data sheets will be revised. Selected calibration procedures will be reviewed for similar problems.
3731997009 | LaSalle 1, LaSalle 2 | 03/11/1997 | 04/08/1997 | 9704160008 | <strong>Inadequate Understanding of Lake Design Basis Results in Lake Level Higher Than Permitted by UFSAR</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. LaSalle County Station entered an Unusual Event at 19:45 on 3/11/97 when it was determined that the 701.8 foot elevation of the lake level at that time was above the 701 foot maximum level described in the UFSAR and used in plant flooding potential analyses. The high lake level resulted principally from a lack of knowledge and consideration of the design basis for the maximum lake level. This led to operating and surveillance procedures which provided upper limits for lake level higher than the UFSAR specified value of 701 ft. Contributing factors were high rates of precipitation, poor materiel condition of the lake make-up and blowdown lines and the unavailability of the lake blowdown valve. operable for the higher than analyzed lake level. However as prudent measures, plant personnel monitored lower elevations of the plant, and the flood wall on the north side of the condenser pit was effectively raised by placement of sand bags to an elevation of 701 ft. 10 in. Operating procedures were revised and additional revisions are in progress. The lake blowdown valve was returned to full service on 3/13/97 to begin reducing lake level to its normal range. The Unusual Event was terminated at 17:00 on 3/26/97 with the lake level at 700.68 ft. The lake level was within normal operating range on 4/3/97.
3731997010 | LaSalle 1 | 03/18/1997 | 09/29/1997 | 9710210265 | <strong>Unit 1 Division 2 Equipment Inoperable Due to Failure to Install Sprinkler System Hangers as Designed</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1997, all Unit 1 Division 2 equipment was declared inoperable because the safety related cables in the Unit 1 Division 2 Cable Spreading Room (CSR) could be damaged by the sprinkler system piping during a Safe Shutdown Earthquake (SSE) event. Hangers were identified missing during an engineering walkdown of the CSR. The missing hangers were replaced to restore the sprinkler system to the "as designed" condition. A seismic "two over one" evaluation has demonstrated that the "as designed" condition of the sprinkler system will not prevent the function of any plant feature required for safe shutdown during a SSE. The Unit 1 Division 2 equipment was declared operable on March 29, 1997. The root cause of the event was incomplete installation and inspection during construction of the plant. Seismic "two over one" evaluations for the other safety related areas protected by sprinkler systems have determined that no other equipment required for safe shutdown during a SSE would have been impacted by sprinkler system piping. Therefore, if the SSE would have occurred at power operation, all other safety related divisions (Unit 1 Division 1 & 3 and Unit 2 Division 1, 2 & 3) would have been free from damage. Some potential interactions of sprinkler nozzles and sewage piping with safety related cables were identified. These potential interactions are being evaluated and will be reported in a supplemental LER if required.
3731997011 | LaSalle 1, LaSalle 2 | 03/18/1997 | 04/14/1997 | 9704220162 | <strong>Source Range Monitor Detector Retract Permit Enabled Lower Than Allowed By Technical Specifications Due To Nonconservative Setpoint In An Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 18, 1997, a determination was made that calibration procedures for the Unit 1 and Unit 2 Source Range Monitor (SRM) did not set the retract permit >/= 100 counts per second (cps) as stated in a footnote in Technical Specifications (TS). Since the calibration procedures use a nominal setpoint of 100 cps, this value could have allowed the function to be bypassed as low as 72 cps when considering tolerances. A review of some past calibrations indicates that approximately half of the time a channel may have been found or left in the 72 to 100 cps range. The normal value of 100 cps is the setpoint described in the UFSAR for SRM System Trips. Engineering documents provide this same nominal setpoint. Corrective actions include performing a setpoint determination, resolving the discrepancy between the documents, and revision of the calibration procedures. This event was caused by inadequate review of engineering documents and UFSAR upon the initial issuance of the TS. The procedure for operating the SRMs assures that the indication is maintained between 500 and 5E4 cps when retracting the SRMs if the Intermediate Range Monitors (IRM) are on scale. Indication of core activity and overlap to the IRMs was maintained. The safety significance of this event was minimal.
3731997013 | LaSalle 1, LaSalle 2 | 03/20/1997 | 04/14/1997 | 9704220187 | <strong>Misinterpretation of Technical Specifications Resulted in Failure to Perform the Isolation Valve Surveillance For All Transversing Incore Probes</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 20, 1997 the Primary Containment Isolation (PCIS) System Functional Performance Review Team (SFPR) identified a concern regarding LaSalle Electrical Surveillance LES-PC-107(207), Unit 1(2) Group 7 Isolation Logic System Functional Test. The concern was whether the testing methodology used in this procedure met the surveillance requirements of Technical Specification 4.3.2.2. Technical Specification 4.3.2.2, Logic System Functional Test, shall be performed at least once per 18 months, this includes the actuated device to verify operability. Contrary to this requirement LES-PC-107, and LES-PC-207, Unit 1/2, Primary Containment Isolation System (PCIS) Functional Test did not check the actuated device on all 5 TIP machines. This condition has existed since initial plant licensing. This condition appears to have been caused by misinterpretation of Technical Specification surveillance requirement 4.3.2.2. Corrective actions include revising the procedures to check all five TIP machines and testing the system per the revised surveillance procedures prior to start-up of either unit.
3731997014 | LaSalle 1, LaSalle 2 | 04/15/1997 | 05/09/1997 | 9705200328 | <strong>Drywell/Suppression Pool Vacuum Breaker Isolation Valve Packing Not Locally Leak Tested Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. The LaSalle System Functional Performance Review Team identified a concern during a review of the Primary Containment Vacuum Breaker Lines. The concern was that the manual drywell/suppression pool vacuum breaker isolation valves 1(2)PC002A-D and 1(2)PC003A-D stem seals (packing) are not tested as required per 10 CFR 50 Appendix J requirements. A review concluded that the configuration of the valves is such that the valve packing is on the opposite side of the valve disc and is not exposed to pressure during vacuum breaker line pressurization. Therefore, the packing on valves 1(2)PC002A-D and 1(2)PC003A-D is not locally tested as required. This condition has existed since initial plant licensing. The root cause was determined to be personnel error as LaSalle failed to properly evaluate all primary containment potential leakage paths when developing the initial Appendix J program. Contributing causes were failure to address NRC Information Notice 86-16 and lack of self assessment. An evaluation of the Appendix J program following this event identified several additional configurations such as this. LaSalle will take corrective actions to resolve the packing issue prior to startup of both Units 1 and 2. The safety significance associated with this event is considered to be minimal based on safety-related maintenance practices and previous ILRT results.
3731997015 | LaSalle 1, LaSalle 2 | 04/30/1997 | 05/30/1997 | 9706040177 | <strong>Diversion of Low Pressure Coolant Injection Flow to the Suppression Pool Due to Manual Override Logic</strong><br /><i>Abstract:&nbsp;</i>The System Functional Performance Review identified a concern regarding the manual override logic associated with the Residual Heat Removal (RHR) Test Return Valve (F024). Specifically, the concern is that if the operator was throttling the valve open (i.e., holding the control switch in the open position) and a simultaneous Emergency Core Cooling System (ECCS) actuation occurred, the manual override logic would be activated and the valve would not automatically close. With the valve in the open position, Low Pressure Coolant Injection (LPCI) flow is diverted to the suppression pool. The apparent cause of this event is that the potential for actuating the manual override if an ECCS initiation occurred while throttling the valve in the open direction was not recognized during the design of the system and was therefore, not analyzed. Based on the probability of the condition occurring and the ability to manually close the valve, the safety significance associated with this event is considered minimal. LaSalle Station will a) conduct training to alert operators of this condition, b) review other valves for a similar condition and c) generate an analysis to address this condition. There were no previous occurrences. This is a voluntary report which may be of generic interest. it is considered voluntary since it is an unanalyzed condition which has been determined to be of minimal safety significance.
3731997016 | LaSalle 1, LaSalle 2 | 04/14/1997 | 05/14/1997 | 9705200448 | <strong>Rod Block Monitor Functions Not Completely Tested Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 14, 1997, it was determined that the 'Inoperable' and 'Bypass' functions of the Unit 1 and 2 Rod Block Monitor (RBM) were not adequately functionally tested as required by Technical Specifications. Additional deficiencies related to the adequacy of RBM channel calibrations were identified on April 22, 1997. Due to system redundancy and verification of normal system operation during plant startups an adequate margin of safety was maintained and the safety consequences of this event were minimal. This event was caused by inadequate procedures. The affected procedures will be revised and performed prior to plant restart. The review process which identified these problems is continuing to review additional procedures for similar problems.
3731997017 | LaSalle 1, LaSalle 2 | 04/16/1997 | 05/09/1997 | 9705140273 | <strong>Deficiencies Identified in ASME Testing of the Residual Heat Removal Pump Suppression Pool Spray Flow Using Instruments Not Included in a Calibration Program Due to Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 16, 1997, a deficiency was identified in how the Residual Heat Removal (RHR) suppression pool spray line flow rate was determined. The flow recorders being used were out of tolerance. Technical Specification 4.6.2.2 requires spray flow to be verified pursuant to Specification 4.0.5. Surveillance requirements for inservice testing of ASME components are according to publication ASME/ANSI OM-1987, Operation and Maintenance of Nuclear Power Plants. This establishes acceptable instrument accuracy in percent of total loop accuracy and requires instrument loop calibration according to the quality assurance program. Although the instrument loop was accurate and calibrated properly, the recorders were not. Use of the recorders started in January, 1994. Actions were not taken then to include the recorders in the instrument loop calibration or a periodic calibration program due to management deficiency. The recorders could introduce errors into the flow determination, preventing identification of an actual low flow, a condition prohibited by Technical Specifications. Since the RHR pumps would remain available for containment heat removal in this condition and because credit is not taken for spray flow heat removal or fission product removal, the event is not safety significant. The recorders have been calibrated and added to the calibration program. Also, the inservice test coordinator now reviews changes to ASME test procedures.
3731997018 | LaSalle 1, LaSalle 2 | 04/21/1997 | 05/21/1997 | 9705270209 | <strong>Fire Protection Carbon Dioxide (CO2) Systems Inoperable Due to Improper Installation of Fire Damper Electrical Leads</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1997, the fire protection carbon dioxide (CO2) suppression systems protecting the 0 and 1A Emergency Diesel Generator (EDG) Rooms were declared inoperable because the electrical leads to a fire damper could have interfered with the proper closing of the curtain type dampers. The condition was identified by the Fire Protection Group during a periodic visual inspection of fire dampers. Fire watches were immediately implemented. The electrical leads were modified to ensure they would not interfere with the dampers. After the modifications were completed, the CO2 system protecting the 1A EDG Room was declared operable on May 2, 1997, and the CO2 system protecting the 0 EDG Room was declared operable on May 3, 1997. The root cause of the event was improper installation during original construction of the plant. All other fire dampers having electrical leads that isolate boundaries to areas protected by CO2 were inspected and no similar conditions were identified. The safety significance of this event was low. Subsequent analysis determined that the design basis concentration of CO2 would have been achieved even if the dampers failed to close. The design basis fire previously analyzed in the UFSAR assumes loss of the EDG, and the affected fire dampers are not located in barriers that separate redundant equipment required for safe shutdown. Therefore, had a design basis fire occurred, and the CO2 system was not effective, at least one train of equipment necessary to achieve and maintain safe shutdown would have been available.
3731997019 | LaSalle 1, LaSalle 2 | 04/22/1997 | 05/22/1997 | 9705290018 | <strong>Post LOCA Hydrogen Analyzers Do Not Monitor to 10 Percent as Stated in UFSAR Due to Ineffective Design Control</strong><br /><i>Abstract:&nbsp;</i>At 1200 hours, on April 22, 1997, with Unit 1 in Mode 4, Cold Shutdown and Unit 2 defueled, all four Post LOCA Hydrogen Analyzers 1(2)AY-CM009/015 were declared inoperable due to a failure to comply with design bases specified in UFSAR Section 7.5.2.2.2.1. The UFSAR requires the primary containment hydrogen concentration be analyzed and recorded up to 10 percent hydrogen by volume with an accuracy of +/- 5 percent of full scale (full scale is 10 percent). Per LaSalle procedure LIS-PC-107(207), the hydrogen analyzer is calibrated up to 4 percent span; hence, the primary containment hydrogen concentration can only be recorded up to 4 percent. The apparent cause of this event is a failure to fully implement design basis requirements into the calibration procedure. The event affects emergency operating procedure actions to terminate operation of the hydrogen recombiner at less than 6 percent hydrogen concentration following a LOCA, since the recorder would not indicate above 4 percent regardless of actual hydrogen level. The emergency action prevents a potential fire in the drywell and the recombiner system if a condition outside the plant design bases causes hydrogen concentration to exceed 4 percent. Corrective actions will change the calibration method of the hydrogen analyzers. The analyzers will be calibrated over the full range of their capability and ensure design bases compliance.
3731997020 | LaSalle 1, LaSalle 2 | 04/22/1997 | 05/01/1998 | 9805070087 | <strong>Recirculation Flow Converter Calibration And Functional Testing Deficiencies Due To Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1997, the System Functional Review Program made a determination that the calibration and functional test procedures for the Unit 1 and Unit 2 Recirculation Flow Converters did not verify overlap to the Average Power Range Monitor channels (APRM) and demonstrate operability of the flow reference signal low value gate to the APRM channels. This did not meet the Technical Specification definition of channel calibration of any series of sequential overlapping or total channel steps such that the entire channel is calibrated. In addition, the power supplies were adjusted prior to recording all "as found" data. This could resulted in a discrepant condition going unidentified or not reported. This could resulted in a discrepant condition going unidentified or not reported. This event is reportable per 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant Technical Specification. The cause of this event was inadequate implementation of Technical Specification requirements as applied to this testing sequence. The safety consequences of this event were minimal. The immediate corrective action was to initiate Problem Identification Forms (PIF) #97-2932, 97- 2970, 97-2933 to investigate and resolve the calibration and functional testing deficiencies.
3731997022 | LaSalle 1, LaSalle 2 | 05/29/1997 | 06/19/1997 | 9706250267 | <strong>Minimum Shift Manning not Met due to Ineffective Tracking of Active License Maintenance Requirements</strong><br /><i>Abstract:&nbsp;</i>An internal investigation of Nuclear Regulatory Commission (NRC) Operator License active status maintenance revealed that on five occasions during the Third Quarter of 1996, an NRC licensed Senior Reactor Operator (SRO) assumed positions requiring an active NRC Operator License when he had not properly maintained his license active during the Second Quarter of 1996. As a result during each of these five shifts the station violated Minimum Shift Crew Composition requirements of LaSalle Technical Specifications Figure 6.1-3. A review of policies and practices associated with the maintenance of active licenses revealed a number of deficiencies associated with the administration of the program intended to meet the requirements of 10 CFR 55.53(e) and (f) regarding license conditions. The cause of this event includes inadequate tracking of licensing requirements, a poorly administered program for keeping track of license conditions, insufficient management oversight of the program, inappropriate interpretation of the governing regulations, and a lack of formal procedural compliance. There were no adverse nuclear/radiological safety consequences. Corrective actions include improving the management of the maintenance of active licenses including proper individual accountability, and appropriate oversight and review. There were no previous occurrences of this event.
3731997024 | LaSalle 1, LaSalle 2 | 06/12/1997 | 07/07/1997 | 9707170046 | <strong>Missed Technical Specification Surveillance and Inadequate Post Maintenance Testing of Reactor Manual Control System Instrumentation Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>During a functional review of the Reactor Manual Control System (RMCS), inadequacies in the post maintenance testing of transponder card replacements and inadequacies in the Control Rod Drive (CRD) SCRAM accumulator instrumentation calibration were identified. This logic is required to be tested per Technical Specifications 3.1.3.5, "Control Rod Scram Accumulators" in operational modes 1, 2, and 5. The consequences of this event are minimal because the transponder cards are bench tested prior to being accepted for installation in the field. Accumulator pressures are also checked on a weekly basis. In addition, during a review of the station procedure used to satisfy Technical Specification surveillance 4.1.3.5.b, it was discovered that the accumulator annunciator in the control room was being defeated prior to performing the surveillance. Technical Specifications require the accumulator annunciator alarm to be tested. The consequences are minimal because the accumulator alarm on the full core display is verified to illuminate for each accumulator tested. These issues are reportable per 10 CFR 50.73(a)(2)(i)(B) due to conditions prohibited by the station's Technical Specifications. This event was caused by inadequate post maintenance and surveillance testing resulting from less than adequate procedures. The affected procedures will be revised.
3731997025 | LaSalle 1 | 06/13/1997 | 07/09/1997 | 9707170156 | <strong>Erroneous Determination of Residual Heat Removal System Pump Operability Results in Operation Outside of Technical Specification Requirements due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1997, the prescribed conditions for flow and pressure could not be obtained during a quarterly surveillance intended to verify the operability of the Unit 1B Residual Heat Removal (RHR) System. Six hours elapsed before the Low Pressure Coolant Injection (LPCI) mode of the 1B RHR System was declared inoperable and 24 hours elapsed before the Shutdown Cooling (SDC) mode of RHR was declared inoperable. Control Room personnel and the Shift Manager improperly delayed a determination of inoperability pending investigation of conflicting indications between the Main Control Room flow indication and a computer display of the same parameter. A subsequent calibration check indicated that the main Control Room flow indication was within tolerance. The lack of timeliness in declaring RHR inoperable for the LPCI and SDC modes of operation resulted in exceeding the allowed time to accomplish an Action Statement of the licensee's Technical Specifications. The cause of this event was personnel error due to failure to make a conservative operability determination. There were no adverse nuclear/radiological safety consequences from this event. Corrective actions include verifying that the RHR Pump and flow and pressure indicators were operating properly and counseling the three individuals involved. There were no previous occurrences of this event.
3731997026 | LaSalle 1, LaSalle 2 | 07/15/1997 | 06/26/1998 | 9806300554 | <strong>Inadequate Channel Functional Testing of the Reactor Manual Control System Refueling Interlocks Due to Procedure Deficiencies</strong><br /><i>Abstract:&nbsp;</i>During System Functional Review of the Reactor Manual Control System (RMCS) an LER was written on deficiencies discovered in the rod block Technical Specification 4.3.6 and 4.9.1.2 surveillance procedures. Further investigation has revealed the Scram Discharge Volume (SDV) bypass switch and the refueling interlock rod block procedures are the only ones deficient. These deficiencies are due to misinterpretation of the definition of a channel function. The safety consequences are minimal. LaSalle has not operated in a condition in which the SDV scram bypass switch rod block was required (5**), and at least one refueling interlock channel has always been verified to function properly prior to use. The affected procedures will be revised and a logic system functional test procedure will be created for completeness. The deficient refueling interlock procedures (not testing both channels) are reportable per 10 CFR 50.73(a)(2)(i)(B) due to conditions prohibited by the station's Technical Specifications.
3731997027 | LaSalle 1, LaSalle 2 | 07/15/1997 | 11/17/1997 | 9711250131 | <strong>Equipment Not Seismically Restrained in Seismic Category I Areas Due To Ineffective Implementation of Requirements</strong><br /><i>Abstract:&nbsp;</i>Numerous pieces of temporary and service equipment and a transient monitoring cabinet located in safety related areas were discovered to lack proper restraints to prevent impacting safety related equipment, should a seismic event occur. Had a seismic event occurred, the potential existed to disable some safety related equipment. A walkdown of remaining accessible safety-related areas was performed and additional unrestrained equipment was found. The causes of this even include less than adequate written guidance, lack of Understanding of the regulatory requirement and lack of previous effective corrective action. Immediate corrective action was to move this equipment to locations that are not in the vicinity of safety related equipment or to seismically restrain it. Other corrective actions include providing appropriate station guidance and training on seismic issues in order to improve station awareness of these issues and effectively implement associated regulatory requirements. There were no health or safety consequences as a result of this event. This event is reportable per 10 CFR 50.73 (a)(2)(ii)(B) as a condition outside the design basis of the plant.
3731997028 | LaSalle 1 | 06/18/1997 | 08/21/1997 | 9708250349 | <strong>Residual Heat Removal System Increased Frequency Surveillance Missed Resulting in Operation Outside of Technical Specification Requirements due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1997, an internal review of the LaSalle Station Inservice Test (IST) Surveillances revealed that increased frequency testing had not been performed on the 1A Residual Heat Removal (RHR) System Pump as would have been appropriate for an Alert Range differential pressure result on a surveillance which was conducted April 22, 1997. The cause of this event was personnel error due to failure of operating personnel to obtain an appropriate engineering technical review of an IST Alert Range reading and the failure of clerical personnel to appropriately route the completed surveillance to the IST Engineer. The 1A RHR Pump was tested on July 17, 1997, at the normal quarterly frequency vice at a 46 day frequency as required by ASME/ANSI, OMa-1988, Part 6, Section 6. The surveillance exceeded the critical performance date on June 18, 1997, resulting in inoperability of the 1A RHR Pump from June 18 to July 17, 1997, in the Low Pressure Coolant Injection (LPCI) and Shutdown Cooling (SDC) Modes. The plant remained in the cold shutdown mode throughout this event. There were minimal adverse nuclear/radiological safety consequences from this event. Corrective actions include improving procedures governing station surveillances and ASME inservice testing and counseling individuals involved. There have been two similar occurrences of events involving ASME testing.
3731997029 | LaSalle 1 | 07/23/1997 | 08/22/1997 | 9708270125 | <strong>Unit One Scram During Main Steam Isolation Actuation Logic System Functional Test Due To Deferral Of SSPV Maintenance</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1997, with Unit 1 in cold shutdown, a full scram signal was generated during performance of LES-PC-108, "Main Steam Isolation Actuation Logic System Functional Test." There was no rod movement due to the scram signal. Reactor vessel water level decreased two inches during this event, due to water draining to the SDV. There were no other safety consequences. The cause of the event was inappropriately deferring scheduled maintenance to replace 204 SSPVs, coupled with continued half scram testing without compensatory measures. Scram solenoid pilot valves used are Automatic Switch Company model HVA-90-405 using BUNA-N rubber diaphragms and are susceptible to hardening during service. Corrective actions include replacement of the 204 SSPVs, testing the instrument air header pressure regulator for correct function and response, and review the existing preventative maintenance program to ensure adequate preventative maintenance is being performed. This event was a valid Engineered Safety Feature (ESF) actuation and is reportable per 10 CFR 50.73 (a)(2)(iv).
3731997030 | LaSalle 1, LaSalle 2 | 08/19/1997 | 05/14/1998 | 9805220293 | <strong>Containment Integrated Leak Rate Test Error Due To Failure to Track an Issue to Resolution</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1997, LaSalle Station identified that Containment integrated Leak Rate Tests (CILRTs) on both units were performed with liner weld channel vent plugs installed. This configuration challenges the channels and plugs as the containment boundary instead of the containment liner welds. This is reportable as an operation or condition prohibited by the plant's Technical Specifications. The cause of this event is a failure to track, follow-up and resolve a known technical issue. No safety consequences resulted because CILRT results demonstrated acceptable leak rates. Byron and Braidwood Stations have a similar configuration of channels and vent plugs. An NRC Safety Evaluation concluded that this configuration is acceptable. At LaSalle evaluations were determined as corrective actions that verify, except for eighteen channels for each unit, the channels and plugs qualify as part of the pressure boundary for the primary containment. Justification was submitted to the NRC for concurrence to leave the vent plugs for these channels in place during testing. For the remaining channels in Unit 1, pigs were permanently removed and the channel tested satisfactorily. Corresponding Unit 2 channels will be tested in the same manner. Other actions include upgrading the procedure to inspect the accessible channels and plugs for deterioration, updating SAR to include channels and vent plugs, and replacing missing plugs.
3731997032 | LaSalle 1 | 09/04/1997 | 10/03/1997 | 9710090071 | <strong>Failure to Comply with a Technical Specification Action Statement due to Non-Conservative Maintenance Planning</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1997, LaSalle Station Unit 1 was in a forced outage maintenance period with only the Division 2 supplied Emergency Core Cooling Systems (ECCS) operable, provided by the "B" and "C" subsystems of the Residual Heat Removal (RHR) System. Diesel Generator 1A failed a surveillance test, and Division 2 ECCS systems were rendered inoperable due to loss of their emergency power supply, the plant was unable to comply with Technical Specification 3.5.2 Action Statement b. to establish Secondary Containment integrity within eight hours. The plant remained in non-compliance with this Technical Specification for nearly 37 hours from 1248 on September 4, 1997, until 0145 on September 6, 1997, when the 1A Diesel Generator was restored to operability. The cause of this event was that the station failed to take a sufficiently conservative approach to the maintenance outage conditions planned for the Unit 1 forced outage, LIF35. The safety significance of this event was minimal, due to plant conditions, but could have been serious in other circumstances. Corrective actions include expedited maintenance efforts to restore ECCS system and Secondary Containment operability as well as a more conservative approach to planning maintenance outages and review of the outage plan. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a failure to comply with the plant's Technical Specifications.
3731997033 | LaSalle 1, LaSalle 2 | 09/11/1997 | 03/02/1998 | 9803090320 | <strong>Reactor Building High Energy Line Break Bounding Temperature Unconservative Due to Inadequate Technical Review of Calculations</strong><br /><i>Abstract:&nbsp;</i>On September 3, 1997, during engineering reviews for the Reactor Water Cleanup (RWCU) pump and pipe replacement design change, High Energy Line Break (HELB) calculations were reviewed to determine the potential impact of increasing the RWCU pump suction line size. The data indicated that the HELB calculations for the existing RWCU design may not be conservative in determining the bounding temperature in the Reactor Building following a HELB. On September 11, 1997, a preliminary assessment determined that the HELB peak temperature may exceed the bounding temperature as specified in the UFSAR. An ENS notification was made on September 11, 1997. This event is reportable per 10 CFR 50.73(a)(2)(ii)(B), as a condition that is outside the design basis of the plant. The apparent causes appear to be insufficient detail in the identified purpose of the calculation resulting in incorrect usage within the architect engineering firm's organization, and a failure to identify and subsequently track an unverified assumption in the calculation. Corrective actions include revising the HELB calculations, and installing modifications to maintain current equipment qualifications. Had a HELB occurred, the Plant could have been outside the design basis. A recent LER (373-97-031) reported a similar problem involving leak detection calculation errors.
3731997034 | LaSalle 1, LaSalle 2 | 10/08/1997 | 11/07/1997 | 9711120141 | <strong>Missed Technical Specification Surveillance to Verify Auto-connected Loads on Emergency Diesel Generators Do Not Exceed Rating Due to Misinterpretation of Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1997, during review of the Unit 1 Integrated Division III ECCS Response Time Test, it was determined that the method used to satisfy Technical Specification 4.8.1.1.2.d.9 for verifying auto-connected loads was non-conservative. All diesel generator's were declared inoperable at 10:30 a.m. on October 8, 1997. The cause of this event was misinterpretation of the Technical Specification surveillance requirement. There was no safety consequences to this event. A previous occurrence of a similar nature is LER 97-006. Corrective actions include a review of diesel loading calculations, a review of appropriate SFPR documents, and development of a surveillance procedure to capture the Technical Specification surveillance requirement. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) as an operation prohibited by the plant's Technical Specifications and applies to all five emergency diesel generators.
3731997035 | LaSalle 1, LaSalle 2 | 10/07/1997 | 11/06/1997 | 9711120083 | <strong>Channel Calibration of the Average Power Range Monitors Not Performed According to Technical Specification Requirements Due to Misinterpretation of a Table Notation</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1997, it was determined that the surveillance for weekly channel calibration of Average Power Range Monitors (APRM) Flow Biased Simulated Thermal Power-Upscale did not conform with Technical Specification requirements. Table 4.3.1.1-1, note (e) was determined to require a channel adjustment for recirculation drive flow prior to Operational Condition 1. However, this surveillance is performed at 25 percent reactor power. This occurred from incorrect application of the table notation. Note (e) was misinterpretated and applied with a second note associated with the surveillance in which the 25 percent initial condition was appropriate. The deficiency was identified by applying a literal interpretation to these table notations as a result of a finding at another station. A review determined the note was misapplied since initial plant operation. Both Units were shutdown when the event was identified. The safety significance of this deficiency is minimal. The APRM channels have been tested satisfactorily prior to startup to verify trip and alarm functions and would remain as adjusted in the previous power run. As corrective action, surveillance procedures will be revised to perform flow adjustment prior to entry into Operational Condition 1 and the other notations associated with Table 4.3.1.1-1 will be reviewed to ensure proper application.
3731997036 | LaSalle 1, LaSalle 2 | 10/14/1997 | 11/13/1997 | 9711180067 | <strong>Missed Technical Specification Surveillances and Inadequate Post Maintenance Testing of Motor Operated Valve Thermal Overload Bypass Circuitry Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1997, an internal station review of past practices with regard to Post Maintenance Testing (PMT) of Motor Operated Valve (MOV) Thermal Overload Bypass Circuitry identified an error in the station's method of accomplishing the Channel Functional Test requirements of Technical Specification (TS) 4.8.3.3.1.b. A long standing improper precedent had been established in 1989, where the PMT methods specified did not always fully check the entire thermal overload bypass channel as required by a Channel Functional Test. The improper practice permitted the thermal overload bypass contact to be closed with the installation of a jumper as opposed to actuating the associated relay to demonstrate that the contact directly performed the overload circuit bypass function. Inadequate testing resulted in Technical Specification violations related to three MOVs. The cause of this event is personnel error in the preparation and review of Post Maintenance Testing procedures. The safety consequences of this event were minimal. Corrective actions include revising deficient PMT procedures, insuring that MOVs listed in Table 3.8.3.3-1 for both Units have a current satisfactory Channel Functional Test prior to required operability and ensuring that personnel who review PMT procedures understand Channel Functional Test requirements. The station has had events similar related to Channel Functional Testing on other equipment. This event is reportable as a failure to comply with the plant's Technical Specifications per 10 CFR 50.73(a)(2)(i)(B).
3731997037 | LaSalle 1, LaSalle 2 | 11/05/1997 | 12/05/1997 | 9712100261 | <strong>Diesel Generator Response Time Test Not Consistent with Technical Specifications Due to Inadequate Review of Procedures</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1997, during review of the acceptance criteria for the Division I and II Diesel Generator load sequence timer for the A and B RHR [BO PRA] pumps, it was determined that the acceptance criteria specified in the procedure was not in compliance with Technical Specification. Procedures specified an acceptance criteria of 4.0 to 5.0 seconds. Engineering completed a review of the design interval per Technical Specification 4.8.1.1.2.d.12, and determined the appropriate acceptance criteria to be 4.5 to 6.0 seconds and calibration criteria to be 4.5 to 5.0 seconds based on a review of UFSAR Section 7.3.1.2.4.3 and UFSAR Table 8.3-1. This event is reportable per 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The apparent cause of the inappropriate acceptance criteria is an inadequate technical review of the procedures. All Diesel Generators that are required to be operable at this time have had the time delay relays recalibrated and left in the range of 4.5 to 5.0 seconds. The safety consequences of this event are minimal. Previous related events identified testing deficiencies due to non-conservative interpretation and misinterpretation of the term "auto-connected loads" in Technical Specification Surveillance requirements.
3731997038 | LaSalle 1, LaSalle 2 | 10/20/1997 | 11/19/1997 | 9711260102 | <strong>Inadequate Calibration of Hydrogen Recombiner Instrumentation Due to a Misinterpretation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1997, the LaSalle Engineering Department identified that the operability of the trip/interlock functions is not verified during channel calibration surveillance testing of several hydrogen recombiner temperature and pressure switches. This event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. This event was identified during review of the hydrogen recombiner logic circuits and surveillance procedures for Generic Letter 96-01. The root cause of this event is inadequate engineering oversight leading to misinterpretation of the Technical Specification requirement to perform the Channel Functional Testing. There are no safety consequences as a result of this event. The Channel Functional Test requirements for the hydrogen recombiner system will be corrected through appropriate procedure changes. Procedure changes will be completed prior to restart of either unit, and appropriate testing will be successfully completed to ensure the Technical Specification surveillance requirements are satisfied. Similar events were discovered during the System Functional Performance Review.
3731997040 | LaSalle 1, LaSalle 2 | 10/24/1997 | 04/02/1999 | 9904140084 | <strong>Unanalyzed Condition for Alternate Shutdown Cooling Steam Lines Due to Inadequate Implementation of Licensing Basis</strong><br /><i>Abstract:&nbsp;</i>Since plant startup when alternate shutdown cooling flow paths were used per procedure LOP-RH-17, "Alternate shutdown Cooling", the plant has been in an unanalyzed condition. On October 24, 1997, no piping analysis could be found that evaluated the affected piping during its use as an alternate shutdown cooling method. The unanalyzed condition resulted from Reactor Core Isolation Cooling and Main Steam lines, used for alternate shutdown cooling (abnormal operation), not being analyzed filled with water and addressing seismic Category II/I concerns. These lines are filled with steam during normal operation. There are no safety consequences associated with this event, since corrective action included evaluations for the alternate shutdown cooling lines which concluded that water in the lines was acceptable, including seismic loads. The root cause of this event is considered a management deficiency from poor technical review and inadequate 10 CFR 50.59 safety evaluations for preparation and revision of the procedure developed in 1984. This event is reportable per 10 CFR 50.73(a)(2)(ii)(A) as being an unanalyzed condition that could have compromised plant safety.
3731997041 | LaSalle 1, LaSalle 2 | 11/20/1997 | 12/19/1997 | 9712240162 | <strong>Failure to Verify Thermal Limits Prior to Exceeding 25 Percent Power During Unit Startups Prior to 1996 due to Misinterpretation of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On November 20, 1997, during reviews of previously completed surveillances, it was determined that surveillances to verify adequate thermal limit margins had not been performed prior to exceeding 25 percent Rated Thermal Power during startup as required by specifications. The root cause of this event is personnel error in misinterpreting the applicability of Technical Specifications 3/4.2.1, 3/4.2.2 (now deleted), 3/4.2.3, 3/4.2.4, and 4.0.4. These events were determined to have occurred during startups performed prior to 1996. Currently, both reactors are shutdown and no immediate action is required. The normal unit startup procedure will be revised to clarify and formalize the surveillance for thermal limit margin verification. The safety consequences of this event are minimal. Fuel integrity was assured during the time thermal limits were not monitored since transients or accidents did not occur and low power conditions existed which normally provide adequate margin to thermal limits. This event is reportable per 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
3731997042 | LaSalle 1, LaSalle 2 | 11/20/1997 | 02/06/1998 | 9802130120 | <strong>High Pressure Core Spray (HPCS) Safety Function Inoperable Due to Inadequate Circuit Breaker Lubrication</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1997, the Unit 1 System Auxiliary Transformer (SAT)[EB] feed breaker to Division III bus 143 (AP)[EB] failed to close during a surveillance test while shutdown. The 4.16KV, GE (General Electric) Magne-blast, AM Series air circuit breaker was removed from service, a Unit 2 breaker was installed and tested satisfactorily, and Division III was declared operable. GE performed the failure analysis and determined on November 20, 1997, that the cause was lack of lubrication, combined with the presence of old, residual grease, on the lower link pin bushings. Based on this finding, Division III High Pressure Core Spray (HPCS) for Units 1 and 2 was declared inoperable on November 20, 1997, due to the eight breakers associated with Unit 1(2) Division III having the same potential failure mechanism. An Emergency Notification System (ENS) phone call was made on November 20, 1997, at 1513. This event is reportable per 10 CFR 50.73(a)(2)(v)(D) Which could have prevented HPCS actuation in the event of an accident. The root cause was a deficiency in the general maintenance requirements for lubrication. Corrective actions include overhaul of the remaining safety related AM series breakers by GE, revision of the affected maintenance procedure and review of other safety related circuit breaker maintenance. There were no safety consequences from this event.
3731997043 | LaSalle 1, LaSalle 2 | 11/25/1997 | 12/23/1997 | 9801020089 | <strong>Incomplete Technical Specification Surveillance on Division III Emergency Diesel Generators Due to Inadequate Procedure Review</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1997, during review of test procedure LTS-800-109, "Division III Trip and Trip Bypass", it was determined that this procedure did not satisfy Technical Specification 4.8.1.1.2.d.11.b) in that; 1) it did not require the test to be performed with the diesel generator running, and 2) it did not verify the Emergency Diesel Generator would continue to supply emergency bus by verifying that the Generator overcurrent relays reset prior to the trip of the DG. As a result of this finding, both the 1(2)B, Division III Emergency Diesel Generators were declared inoperable and will remain inoperable until completion of testing in compliance with the Technical Specification. The Division I and Division II Emergency Diesel Generators are unaffected by this issue. This event is reportable per 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The apparent cause is inadequate technical review of the procedure during initial preparation. There were no safety consequences from this event. Corrective actions include revision to the test procedures, and review of other diesel generator test procedures. Previous related events identified testing deficiencies due to non-conservative interpretation in Technical Specification Surveillance requirements and inadequate review of test procedures.
3731997044 | LaSalle 1, LaSalle 2 | 12/05/1997 | 03/05/1998 | 9803130142 | <strong>Potentially Unanalyzed Condition for Automation Depressurization System Accumulator Capacity Due To Lack Of Design Basis Information</strong><br /><i>Abstract:&nbsp;</i>In May 1997 it was identified that station specific calculations for the capacity of the Automatic Depressurization System (ADS) accumulators could not be identified. Preliminary calculations performed prior to the original LER submittal showed the most limiting of the UFSAR licensing basis statements (two actuations of the ADS valves at 70 percent of a Drywell design pressure of 45 psig) may not be met. Review of the UFSAR and Safety Evaluation Report (SER) (NUREG-0519) determined that there is conflicting information as to the licensing basis requirements for the accumulator sizing. This event was conservatively determined to be potentially reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A) as an unanalyzed condition that could have significantly compromised plant safety based on Information available when the LER was originally submitted. Further analysis and calculations show the plant was not in licensing basis requirement. Based on this analysis, the event is not reportable per 10 CFR 50.73 (a)(2)(ii)(A).
3731997045 | LaSalle 1, LaSalle 2 | 12/23/1997 | 01/22/1998 | 9801270099 | <strong>Post Accident Monitoring System Instrumentation Outside Design Basis Due To A Personnel Error Which Resulted In A Non-Conservative Environmental Qualification Life Calculation</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1997, with LaSalle County Unit 1 and Unit 2 in Cold Shutdown and defueled respectively, Engineering determined by calculation and review of maintenance history, that the thermal environmental qualification (EQ) lives have expired for several components located in the Unit 1 and Unit 2 Post Accident Monitoring System. These systems are currently inoperable. Although the qualified life for some components expired approximately nine years ago, there were no safety consequences resulting from this event since the system had not been called upon to provide containment monitoring following a loss of coolant event. Prior to restart of each Unit, the affected components will be replaced. The deficiencies occurred as the result of human performance error by a contracted Engineering firm in preparing the calculation. Also, the error was not identified during the review and approval of the calculation. In 1984, the procedure for performing EQ calculations was much less rigorous than the current EQ calculation procedure. The qualified life calculation has been revised and will be incorporated into EQ binder, EQ-LS022. This event is reportable per 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the design basis of the plant.
3731997046 | LaSalle 1, LaSalle 2 | 12/16/1997 | 07/14/1998 | 9807170229 | <strong>Potential Pressurization of the Turbine Building Ventilation Exhaust Tunnel Resulting from a Main Steam HELB due to Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1997, the preliminary results of an engineering analysis to evaluate the latch release setpoint determined that in the event of a Main Steam High Energy Line Break, the Turbine Building Ventilation isolation dampers, 1(2)VT079YA, B & C, would not close fast enough to prevent the pressure from exceeding the pressure retaining capability of the walls, floors, and ceilings that separates the VT exhaust tunnel from the safety related High Pressure Core Spray (HPCS) electrical switchgear room. The apparent causes include an invalid calculation assumption. The potential exists that a high energy line break could result in a rupture of the wall separating the vent riser from the 687' - 0" switchgear room, Division 3 HPCS electrical switchgear and the wall at elevation 815' 0" at the upper VT tunnel. This could result in the Division 3 electrical power to that unit being inoperable and unavailable to supply power to mitigate the consequences of a Design Basis Event. This event is reportable per 10 CFR 50.73(a)(2)(ii)(B), as a condition that is outside the design basis of the plant.
3741997001 | LaSalle 2 | 07/17/1997 | 03/07/2000 | ML00369432 | <strong>Discovery of a Broken Fuel Rod in the LaSalle Unit 2 Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>
3821997001 | Waterford 3 | 01/29/1997 | 02/27/1997 | 9703040259 | <strong>REG. GUIDE 1.97 CONTAINMENT ISOLATION VALVE POSITION INDICATION</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. Per Technical Specification (TS) 3.3.3.6, Category 1 containment isolation valves are required to have a minimum of 1 channel of position indication available per valve (less than the minimum operable channels is allowed for a time period not to exceed 48 hours). Pursuant to the bases for TS 3.3.3.6, this position indication will be consistent with the,recommendations of Regulatory Guide (RG) 1.97. Feedwater (EFW) Flow Control Valve (FCV), EFW-224A (see Figure 1, attached), was relied upon for containment isolation for a period of 62.5 hours. The position indication for EFW-224A does not meet the requirements of Regulatory Guide (RG) 1.97 in that it does not have 'direct' position indication. Therefore, EFW-224A should not have been credited as a containment isolation valve, (CIV). Licensing Document Change Request 97-0110, approved on January 9, 1997, revised the Technical Requirements Manual and Final Safety Analysis Report to ensure the FCVs are no longer relied upon as CIVs. This event did not compromise the health and safety of the public.
3821997002 | Waterford 3 | 01/30/1997 | 03/03/1997 | 9703060082 | <strong>POTENTIAL COMMON MODE FAILURE OF SHUTDOWN COOLING</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On December 20, 1996, a 72 hour administrative action statement was entered due to declaring Shutdown Cooling Heat Exchanger B inlet and outlet valves (SI-125B and SI-412B) inoperable. An engineering evaluation determined that nitrogen voiding discovered in Low Pressure Safety Injection (SI) Train B may render those valves unable to open because of pressure locking. 1996, after bonnet pressure relief devices were installed. On January 27, 1997, as a result of monitoring activities, nitrogen voiding in SI Train A was found. SI-125A and SI-412A were declared inoperable. Although there is no evidence to indicate pressure locking has occurred, on January 30, 1997, Waterford 3 determined that the potential for a common mode failure of SI-125A(B) and SI-412A(B) due to nitrogen in the SI headers may have existed prior to the December 1996 event. Bonnet pressure relief devices were installed on SI-125A and SI-412A on January 30, 1997. This event did not compromise the health and safety of the public.
3821997003 | Waterford 3 | 01/30/1997 | 03/03/1997 | 9703050179 | <strong>Process Analog Computer Card Failed on Essential Services Chilled Water Train 'B'</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 30, 1997, at 1801 hours, a Process Analog Control (PAC) card failed on Essential Services Chilled Water (CHW) Train 'B.' The 'B' Train of CHW and those systems affected by that train (including Containment Spray Train 'B') were declared inoperable due to cascading Technical Specifications. At that time, Containment Spray (CS) Pump 'A' was out of service for scheduled maintenance. In consequence, the plant entered Technical Specification (TS) 3.0.3 because the Technical Specifications do not provide explicit action requirements when two trains of CS are inoperable. Preparations were made for a plant shutdown. A new PAC card was installed and calibrated. CHW Train 'B' was declared operable at 1918 hours and the plant exited TS 3.0.3. This event did not compromise the health and safety of the public.
3821997004 | Waterford 3 | 10/31/1995 | 03/06/1997 | 9703100263 | <strong>INCORRECT INTERPRETATION OF TS SURVEILLANCE 4.6.2.2.B.2</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. Since initial plant startup, the flowrate specified in Technical Specification (TS) Surveillance 4.6.2.2.b.2 has been used to verify that the containment fan cooler (CFC) flow control valves opened fully on a SIAS. Following, a, special Component Cooling Water (CCW) System flow test performed during Refuel 7 (RF7), questions were raised concerning Waterford 3's interpretation of this TS Surveillance and the CCW flowrates to the CFCs. As a result, a TS interpretation was requested from NRR by the site Resident NRC Inspector. NRR determined the purpose of TS Surveillance 4.6.2.2.b.2 was to verify a flow rate to each CFC greater than or equal to the design flowrate assumed in the Safety analysis and not to verify control valve position. TS Surveillance was incorrect. In addition, as a result of the RF7 CCW flow test, from 10-31-95 through 3-10-96, the plant did not meet the flow rates specified in the TS Surveillance Requirement and was in violation of TS. This event did not compromise the health and safety of the public.
3821997005 | Waterford 3 | 07/15/1989 | 03/10/1997 | 9703120019 | <strong>Failure to Perform Reactor Coolant Low Flow Trip Operating Bypass Surveillance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 20, 1997, it was discovered that on July 15, 1989 the start-up surveillance requiring testing of the reactor coolant low flow trip operating bypass logic as required by Technical Specification (TS) Surveillance Requirement 4.3.1.2 had not always been performed. Surveillance Requirement 4.3.1.2 states that the logic for the bypasses shall be demonstrated operable prior to each reactor start-up unless performed during the preceding 92 days. On July 15, 1989, the reactor coolant low flow trip operating bypass surveillance was not performed as a prerequisite for entering Mode 2. The root cause for this condition is attributed to failure to ensure that procedural controls existed for testing the reactor coolant low flow bypass in accordance with TS 4.3.1.2 when the bypass was installed in 1988. Corrective actions for this event include review of this event with Operations personnel, updating repetitive tasks and procedures to include this test and modification of the circuitry to allow testing with the reactor coolant pumps running. This event did not compromise the health and safety of the public.
3821997006 | Waterford 3 | 02/21/1997 | 03/24/1997 | 9703260222 | <strong>TS 3.0.3 ENTRY DUE TO NOT COMPLETING TS SURVEILLANCE 4.5.2J</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 21, 1997, at 0327 hours, ultrasonic testing of Low Pressure Safety Injection (LPSI) system piping, which is being performed on a periodic basis, revealed a 7.58 ft**3 void at Penetration 39. On February 21, 1997, at 2000 hours, Waterford 3 (M) entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 when plant personnel questioned if the intent of TS surveillance 4.5.2j was being met. TS 4.5.2j states that each Emergency Core Cooling System (ECCS) subsystem shall be demonstrated OPERABLE following any maintenance which drains portions of the system, by venting the ECCS pump casings and discharge piping high points. TS Surveillance Requirement 4.0.3 was invoked simultaneously to allow for completion of the TS 4.5.2j surveillance. TS 3.0.3 was conservatively entered based on vent valves not being available at penetrations 36, 37, 38, and 39. On February 22, 1997, at 1829 hours, Waterford 3 exited TS 3.0.3 after reducing the void in both trains of LPSI system piping. This event did not compromise the health and safety of the public.
3821997007 | Waterford 3 | 03/09/1997 | 05/16/1997 | 9705200206 | <strong>Discovery of Additional Refueling Water Storage Pool Instrument Uncertainty</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 2/23/97, Waterford personnel observed the indicated level of the Refueling Water Storage Pool (RWSP) change during startup of the Controlled Ventilation Area System (CVAS). The root cause of this condition is an inadequate design for the reference leg of the level transmitters. The low side of each RWSP level transmitter is vented to an area filtered by CVAS whereas the high side is connected to the RWSP. Thus, CVAS operation affects the differential pressure between the two legs of the transmitters. These transmitters are intended to measure RWSP level and initiate a Recirculation Actuation Signal (RAS) at the required setpoint. CVAS operation causes indicated RWSP level to differ from actual RWSP level in the non-conservative direction. Near-term actions included recalibrating the RWSP transmitters and conducting tests to determine additional ventilation effects. On 3/17/97, another impact associated with operation of the non-safety Condenser Off-Gas system. The system was placed in a condition that negated the impact. On 4/8/97, voluntary LER 97-007-00 was issued to document this event. Subsequently, engineering determined the CVAS effect impacts the RWSP instrument setpoint analysis and does not preserve the previously calculated analytical limit. This event is reportable as a condition prohibited by Technical Specifications. This event did not compromise the health and safety of the public.
3821997008 | Waterford 3 | 04/19/1988 | 04/16/1997 | 9704180175 | <strong>INCORRECT QUANTITY OF TRI-SODIUM PHOSPHATE USED FOR ECCS SUBSYSTEM PH DETERMINATION</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 17, 1997, at 1430 hours, Chemistry personnel discovered that Technical Specification (TS) surveillance requirement 4.5.2.d.4 had been performed on April 19, 1988, with a quantity of Tri-Sodium Phosphate (TSP) that exceeded TS requirements. Specifically, TS 4.5.2.d.4 requires verifying that when a representative sample of 3.99 to 4.01 grams of TSP from a TSP basket is submerged, without agitation, in 3.9 to 4.1 liters of water at 110 degrees F to 130 degrees F and borated within Refueling Water Storage Pool (RWSP) concentration limits, the pH of the mixed solution is raised to greater than or equal to 7 within 3 hours. Contrary to that requirement, however, the sample of TSP used on April 19, 1988, contained 4.032 grams of TSP. The root cause of this event is personnel error. The employees who performed the surveillance and the supervisor who reviewed and approved the surveillance documentation failed to recognize the error. Upon discovery, a corrective action document was generated. All similar surveillances performed since 1988 were verified to comply with TS requirements. Theoretical calculations demonstrated that surveillance results were not negatively impacted by the incorrect sample size. The pH of the mixed solution would have been within TS requirements. This event did not compromise the health and safety of the public.
3821997009 | Waterford 3 | 03/25/1997 | 04/19/1997 | 9704230206 | <strong>STEAM GENERATOR LOW PRESSURE SETPOINT BELOW TECHNICAL SPECIFICATION</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At 0450 hours on 3-10-97, it was discovered that the setpoint for Steam Generator (SG) #1 was 680 psia on channel B. The Technical Specification (TS) low limit for this setpoint is greater than or equal to 768 psia. The setpoint was lower than normal due to the performance of Surveillance Procedure OP-903-107, Plant Protection System Channel _A_B_C_D Functional Test, section 7.20. This surveillance is a functional test of the B channel SG #2 low pressure setpoint and was performed on 3-9-97 at 1658 hours. The functional test requires lowering the B channel setpoint using the pressure setpoint reset pushbutton. Depressing this button lowers the B channel pressure setpoint for both steam generators. The SG #1 low pressure setpoint for B channel was decreased below its lower limit and the bistable was not put in bypass as required by the ACTION statement for TS 3.3.1 and 3.3.2. The root cause of this event was an inadequate surveillance procedure. The surveillance procedure has been revised to require the channel for each SGs to be placed in bypass during the functional test. This event did not compromise the health and safety of the public.
3821997010 | Waterford 3 | 03/05/1997 | 04/21/1997 | 9707080411 | <strong>FAILURE TO MEET SHIELD BUILDING VENTILATION TS FLOW CRITERIA</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 5, 1997 in-place filter testing and flow testing of Shield Building Ventilation (SBV) System Train B was performed per Technical Specification (TS) 4.6.6.1.b. The results of the in-place testing were acceptable with the exception that the TS-required flow of 10,000 cfm +/- 10 percent was not met. However, the test engineer and vendor failed to recognize that the acceptance criteria had not been met and the system was considered to remain operable until March 20, 1997, when the error was finally noted. The root cause of this event is personnel error with a contributing factor of needed procedural human factor enhancements. Short term corrective actions included readjusting the SBV Train B flow rate to within the TS acceptable range and re-performing the in-place testing at the TS flow rate. Long term actions include reviewing surveillance procedures for human factors improvements and reviewing the surveillance process for tests which take longer than one day to complete. This event did not compromise the health and safety of the public. SBV Train B could have performed its safety function at all times.
3821997011 | Waterford 3 | 03/21/1997 | 07/18/1997 | 9707220125 | <strong>CONTAINMENT SPRAY WATER LESS THAN REQUIRED DUE TO INSTRUMENT UNCERTAINTY</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1997, Engineering personnel discovered that the level of water in the Containment Spray (CS) Risers could have been less than required by Technical Specification (TS) 4.6.2.1.a. The instruments used to verify the TS required water level (e.g., greater than or equal to 149.5 feet Mean Sea Level elevation) are located approximately 31.5 feet below sea level and measure the height of water in the CS Risers. Historically, operators have performed the level verification by ensuring that the instruments indicate a height of water greater than or equal to 181 feet. The indicated verification value was chosen because an actual water height of 181 feet is equal to 149.5 feet MSL elevation. When considering the effects of instrument uncertainties, however, verification that the indicated level is greater than or equal to 181 feet is not sufficient to ensure TS compliance. The root cause of this event was the failure to consider instrument uncertainty when establishing a minimum indicated CS riser level value that ensures compliance with the TS required value. The height of water in CS Risers A and B, as indicated by level instruments, was verified to be 196 feet and 183, respectively. The indicated water level in CS Riser B was raised to 191 feet. In addition, the surveillance procedure was revised to ensure future compliance. This event did not compromise the health and safety of the public.
3821997012 | Waterford 3 | 04/04/1997 | 06/04/1997 | 9706060185 | <strong>PROGRAMMATIC BREAKDOWN OF OVERTIME PROGRAM</strong><br /><i>Abstract:&nbsp;</i>On April 4, 1997, a determination was made that a programmatic breakdown in the administration of the Technical Specification limits for allowed overtime had occurred. On several occasions, during the month of February, 1997, maintenance and operations personnel exceeded the allowed overtime limit specified in Technical Specification 6.2.2.e without obtaining the required approvals. The cause of this occurrence has been attributed to a lack of management oversight in administering and implementing the plant's working hour policy. To address this issue, the requirements of the Technical Specification and the working hour policy have been reemphasized to management and supervisory personnel. In addition, the working hour procedure, UNT-005-005, will be revised to clarify requirements. Although personnel worked in excess of the allowed overtime hours, the amount of hours worked had no impact on their ability to do quality work and therefore had no impact on the health and safety of the public or plant personnel.
3821997013 | Waterford 3 | 04/07/1997 | 05/07/1997 | 9705120286 | <strong>REFUELING MACHINE FAILED TO MEET TECHNICAL SPECIFICATION REQUIREMENTS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 7, 1997, engineering personnel determined the Refueling machine's fuel mast and Control Element Assembly (CEA) mast have elevation zones during extension and retraction of their hoist assemblies which do not have overload protection provided. This condition is contrary to Technical Specification 3/4.9.6 which requires both the fuel mast and the CEA mast to have operable overload protection features prior to use. The zones where no overload protection was provided are associated with the areas where load transitions occur during extension and retraction of the mast assemblies. The zones were engineered into the design to prevent erroneous readings during the load transitions. Additionally, the Surveillance Procedure which validates the minimum lift capacity of the CEA hoist was inadequate. The procedure required a load test be performed by raising the CEA hoist to the upper limit and then using a hand wheel to generate a load of 1600 pounds, which does not ensure that the hoist motor can lift it's minimum load capacity. The corrective action for these two conditions consists of a modification to the refueling machine overload protection software to eliminate the bypass feature for the load transition zones, and a revision to the Surveillance Procedure which requires test weights to be used when testing the lifting capacity of the CEA hoist. These conditions did not compromise the health and safety of the public.
3821997014 | Waterford 3 | 04/08/1997 | 05/08/1997 | 9709020112 | <strong>Inadequate Surveillance Identified Pursuant to Generic Letter 96-01</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1997, with the plant in mode 1 at 100% power, it was determined that no test procedure verified operability of sequencer relay contacts associated with Emergency Feedwater Pump breaker control circuits. It was further determined that no test procedure verified operability of Containment Spray Pump breaker logic circuit sequencer relay contacts. Subsequently it was determined that parallel under-voltage relay contacts, which provide auto start inputs for the EDG were not being individually verified operable. An NRC violation identified that surveillance tests for pressurizer heater group and other identified loads were not verifying load shed during simulated loss-of offsite power test or loss of off-site power in conjunction with a safety injection actuation signal test. The cases above were determined to be due to inadequate surveillance test procedures. The contacts were tested via updated test procedures or special test procedures / work authorizations and found to function properly. The identified condition did not compromise the health and safety of the general public.
3821997015 | Waterford 3 | 04/18/1997 | 05/19/1997 | 9705220221 | <strong>Ultimate Heat Sink Did Not Incorporate Conservative Assumptions</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. Personnel determined the Essential Chillers may not have been able to perform their safety function in the event of a LOCA. As a result of design basis upgrade work, personnel determined additional conservative assumptions should be used in the design basis of the UHS. New analysis established that if the additional conservative assumptions are factored in the analysis of record, the heat input to the UHS is increased by about 21 E06 Btu/hr in the event of a LOCA. This additional heat to the UHS impacts the Component Cooling Water (CCW) temperature to essential equipment, the consumption of water in the Wet Cooling Tower (WCT) basins, and the Essential Chiller cooling capacity. The impact of the additional heat load on the Essential Chiller cooling capacity was determined to be potentially safety significant since there were a number of occurrences during Cycle 6 operation when both the Train A and B Essential Chillers could have tripped due to low flow had a LOCA occurred. This condition did not compromise the health and safety of the public.
3821997016 | Waterford 3 | 05/15/1997 | 10/16/1997 | 9710200054 | <strong>POTENTIAL FOR INADVERTENT RECIRCULATION ACTUATION SIGNAL ALLOWED BY TECH SPECS</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1997, with Waterford 3 in Mode 6 and at 0% power, a Technical Specifications (TS) deficiency was discovered which could contribute to an inadvertent Recirculation Actuation Signal (RAS). If this were to occur under certain accident conditions, Emergency Core Cooling System (ECCS) and Containment Spray (CS) system pumps suction could shift to the containment sump prematurely. On September 16, 1997, a review of other Engineered Safety Features Actuation System (ESFAS) instrumentation circuits revealed that under certain emergency conditions, automatic isolation of a faulted steam generator from Emergency Feedwater would not occur as assumed in the Waterford 3 safety analysis. The root cause has been determined to be a deficiency in the TS in that they allow continued operation with an inoperable channel of ESFAS instrumentation in the tripped condition. A Technical Specification Change Request (TSCR) has been submitted to limit the time that one channel of RAS instrumentation can be in the tripped condition. The TSCR will be revised and resubmitted for the Emergency Feedwater Actuation Signal condition. Precautions have been instituted to limit continued operation in this condition until the TS are changed. These conditions did not compromise the health and safety of the public.
3821997017 | Waterford 3 | 05/15/1997 | 06/19/1997 | 9706260004 | <strong>CONTROL ROOM EMERGENCY FILTRATION UNIT COMMON MODE FAILURE</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1997, Waterford 3 discovered the possibility that both trains of Control Room Emergency Filtration Units (CREFU) would be rendered inoperable if either Emergency Filter Modulating Damper, HVC-213A(B), failed open. Both CREFUs were declared inoperable and Technical Specification 3.7.6.2b was entered. Operations and Systems Engineering performed Control Room pressure testing in accordance with OP-903-123, "Control Room Envelope Pressure Test," utilizing both trains of CREFUs and various Control Room Heating and Ventilation System (HVC) lineups. Results indicated that a single failure of HVC-213A(B) would prohibit either CREFU from pressurizing the Control Room envelope to 1/8 inch of water gauge with less than or equal to 200 cubic feet per minute of flow. As a corrective action, dampers were closed isolating the outside air intake paths for CREFU Train A. This effectively stopped the common suction path for both units allowing CREFU Train B to remain operable. CREFU Train A will remain available for recirculation only. This event did not compromise the health and safety of the public.
3821997018 | Waterford 3 | 04/28/1997 | 06/27/1997 | 9707010129 | <strong>Voluntary LER for Dropped New Fuel Assembly</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1997, at approximately 2137, during Waterford 3 Refueling Outage 8 fuel shuffle, new fuel assembly LAR338 disengaged from the Spent Fuel Handling Tool and dropped approximately five inches. The assembly came to rest straddling spent fuel storage racks leaning at an angle of about 40 degrees, against the south side wall of the Spent Fuel Pool. Off-normal procedure OP-901-405, "Fuel Handling Accident", was entered, fuel assembly LAJ229, which was in the process of being hoisted by the Refueling Machine in Containment, was reinserted, and the Fuel Handling Building (FHB) was evacuated of non-essential personnel. Health Physics personnel took air samples of the FHB +46 elevation for particulate, iodine, and gas and checked the SFP liner leakage detection drains. All samples were normal and no liner leakage was detected. The root cause of this event has been identified as human error. The spent fuel handling tool was found approximately 75% open and locked. The locking device could not have repositioned if properly engaged and therefore it was concluded that the fuel handling tool was inadvertently mispositioned. This event did not compromise the health and safety of the public. This event is being voluntarily reported.
3821997020 | Waterford 3 | 06/04/1997 | 03/16/1998 | 9903220176 | <strong>Potential Safety Related Static Uninterruptible Power Supply (SUPS) Common Mode Failure</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1997, during Refueling Outage eight (shutdown), while evaluating a plant condition, it was determined that a fire in the switchgear room could potentially result in the momentary loss of both trains of safety related Static Uninterruptible Power Supplies (SUPS). The plant established hourly fire watches in that area in accordance with Fire Protection Program requirements. The apparent cause of the condition was determined to be a combination of 1) the inherent design of the SUPS units and 2) unprotected SUPS associated circuits that are not separated per Appendix R criteria. Other plant areas are affected by the condition. In addition to fire, low probability vulnerability to tornado missile damage exists in one plant area. Corrective measures during Refuel Outage 9 (RF09) include.replacement of a SUPS and Operator response procedure enhancement. Post RF09 changes include cable reroutes and color coded breaker panel markings (human factors enhancement). Compensatory measures will continue in the interim. No actual loss of both trains of SUPS units occurred. This condition did not compromise the health and safety of the general public.
3821997021 | Waterford 3 | 06/11/1997 | 12/16/1997 | 9712190128 | <strong>Inside and Outside Containment Isolation Valves Failed Leakage Criteria</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1997, at approximately 1100 CDT, while in MODE 5 and at 0% power, leakage rate testing found the inside containment isolation valve for fire protection containment penetration 60 to have failed to meet its leakage acceptance criteria. The outside containment isolation valve for this penetration had been leak tested earlier in the outage and was also found to have failed to meet its acceptance criteria. The unacceptable leakage for both valves has been attributed to excessive corrosion. The outside containment isolation valve was reworked and reinstalled, and the inside valve has been replaced. The as-found condition is being reported per 10CFR50.73(a)(2)(ii). This condition did not pose an actual threat to the health and safety of the public.
3821997022 | Waterford 3 | 06/14/1997 | 07/18/1997 | 9707220420 | <strong>POSITIVE REACTIVITY ADDITION IN VIOLATION OF TS 3.7.6.2.b</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1997, at 2112 hours, Control Room Emergency Filtration Units A and B were declared inoperable to install gravity dampers per Design Change DCP-3536. Technical Specification (TS) 3.7.6.2b requires the suspension of all operations involving positive reactivity changes. On June 12, 1997, at 0132 hours, OP-903-115, "Train A Integrated Emergency Diesel Generator/Engineering Safety Features Test," was performed. As a result of this surveillance, approximately 9% of the volume of Boric Acid Makeup Tank B was pumped into the Reactor Coolant System (RCS). This resulted in RCS boron concentration being greater than Refueling Water Storage Pool (RWSP) concentration. On June 14, 1997, Operations performed a makeup to the RCS using the operable boration flow path from the RWSP. Because the RWSP boron concentration was lower than the RCS, this condition is reportable per 10 CFR 50.73(a)(2)(i)(B) as a violation of TS 3.6.7.2b. All operations involving possible positive reactivity additions were stopped until the TS action statements were exited. TS 3.7.6.2b will be revised to remove the reference to positive reactivity addition. This event did not compromise the health and safety of the public.
3821997023 | Waterford 3 | 07/08/1997 | 08/07/1997 | 9708110017 | <strong>MISSED EMERGENCY DIESEL GENERATOR FUEL SYSTEM SURVEILLANCE</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1997, Emergency Diesel Generators (EDGs) A and B were declared inoperable due to Technical Specification (TS) Surveillance Requirement 4.8.1.1.2.h.2 not being completed within its ten year plus 25% surveillance interval. The apparent cause was a failure of Waterford 3 personnel to properly determine the correct start and end dates for the ten year testing interval. This condition is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS. At the time of discovery, Waterford 3 was in Mode 5 (Cold Shutdown) while conducting Refueling Outage 8 activities. EDGs A and B were declared inoperable, and Waterford 3 submitted an emergency change request to the TS. Because no leakage or integrity issues existed with the fuel oil system at the time, the Emergency Diesel Generators remained available if needed. The health and safety of the public was not compromised at any time.
3821997024 | Waterford 3 | 05/28/1997 | 08/19/1997 | 9708210284 | <strong>EMERGENCY DIESEL GENERATOR AUTOSTART DUE TO START-UP TRANSFORMER FAILURE</strong><br /><i>Abstract:&nbsp;</i>On May 28, 1997, at 09:01, while in Mode 5 (Cold Shutdown) of Waterford 3 Refueling Outage 8, a loss of off-site power occurred in the "B" train Off-site Power System. The root cause of this event was failure of Startup Transformer "B." Emergency Diesel Generator "B" started and loaded as expected. The Control Room staff implemented actions of off-normal procedures, and the temperature of the reactor coolant system was maintained using shutdown cooling train "A". Preparations for backfeeding through Main Transformer "B" and Unit Auxiliary Transformer "B" were immediately undertaken, and off-site power was restored to the B train at approximately 23:29 on May 29, 1997. This event did not compromise the health and safety of the public and is being voluntarily reported.
3821997025 | Waterford 3 | 10/17/1997 | 11/17/1997 | 9711200028 | <strong>GAG FOR CC-835B WAS PARTIALLY ENGAGED RESTRICTING VALVE TO APPROXIMATELY 80% OPEN</strong><br /><i>Abstract:&nbsp;</i>On 10-17-97, it was discovered that the gag for valve CC-835B, the component cooling water (CCW) flow control valve for containment fan coolers B & D, was partially engaged, restricting the valve to approximately 80% open. This was discovered while performing the valve's quarterly stroke test in accordance with OP-903-118, "Primary Auxiliaries Quarterly IST Valve Tests". It was determined that the valve was gagged on 9-9-97 during maintenance. The gag was to have been disengaged upon completion of work. It is therefore assumed that the gag has been engaged on valve CC-835B since 9-9-97. This valve would not have been able to actuate to its full open position on an SIAS signal as required by TS surveillance 4.6.2.2.b.3. The root cause of this event was inadequate work instructions in the Work Authorization (WA). No instructions were included in the WA requiring CC-835B be stroke tested following maintenance to ensure the gag was completely disengaged. Upon discovery, the gag was disengaged. Instructions will be included in future WAs to stroke test the valve when the gag is used. This event did not compromise the health and safety of the public.
3821997026 | Waterford 3 | 11/05/1997 | 12/05/1997 | 9712090258 | <strong>SINGLE FAILURE EFFECTS CONDENSATE STORAGE POOL INVENTORY</strong><br /><i>Abstract:&nbsp;</i>The CCW makeup pumps start when levels in the CCW surge tank, EDG standpipes or the essential chilled water expansion tanks reach a predetermined setpoint. Once started, the pumps continue to run until secured by plant operators. A single failure of any of several components could result in a continuous demand for makeup. The CCW surge tank, EDG standpipes and the essential chilled water expansion tanks are each vented and continuous makeup to any of these locations could result in overflow. The CCW makeup pumps take suction from the CSP and the continuous demand depletes CSP inventory. This water inventory is credited in response to design bases accidents. The apparent root cause of this event is a design deficiency in not considering the affects of certain single failures. A procedure change was initiated to allow operator action to ensure adequate CSP inventory is maintained until permanent corrective actions can be developed. This event did not compromise the health and safety of the public.
3821997027 | Waterford 3 | 11/10/1997 | 06/09/1998 | 9806110361 | <strong>Controller for ACCW Valve ACC-126A Left in Manual</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1997, at approximately 1025, personnel discovered that both trains of the Auxiliary Component Cooling Water (ACCW) System had been inoperable for about seven and one half hours. Three root causes for that condition were identified. (1) The controller for valve ACC- 126A was not placed in automatic per procedural requirements. (2) Control board walkdowns were inadequate in that they did not detect the controller misposition. (3) Procedural requirements to verify that ACCW Train 'A' was operable prior to declaring ACCW Train 'B' inoperable were vague. Immediate corrective actions included placing the controller for ACC-126A in automatic, debriefing the Control Room crew responsible for the misposition, and commencing a thorough technical evaluation. Other corrective actions included performing control board walkdowns, implementing a walkdown checklist, and revising Operations' procedures to clarify expectations. Evaluation results confirm that in the event of an accident, the safety systems would have performed their design functions, and design values in the analysis of record would not have been exceeded. The condition was judged to have low safety significance and a very low risk significance. The public health and safety was not compromised.
3821997028 | Waterford 3 | 07/20/1997 | 12/15/1997 | 9712180069 | <strong>EDG AUTOSTART DUE TO 86A2 RELAY</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1997, a loss of power to the 3A Safety Bus occurred resulting in the automatic start of Emergency Diesel Generator (EDG) A. At the time of discovery, Waterford 3 was in Mode 4 (hot shutdown). The loss of power was the result of a spurious trip of the 86A2 relay. An investigation of the cause of the relay trip and a visual inspection of the relay were conducted. No abnormalities were detected, and the 86A2 relay was replaced. Although EDGs are not considered to be a part of the Engineered Safety Features at Waterford, this condition is being reported voluntarily. The health and safety of the public were not compromised at any time.
3821997029 | Waterford 3 | 11/13/1997 | 12/15/1997 | 9712180081 | <strong>INADEQUATE SURVEILLANCE TESTING OF RELAY CONTACTS IN SAFETY-RELATED LOGIC CIRCUITS</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1997, with the plant in mode 1 at 100% power, it was determined that an ESFAS relay contact in each of the following safety-related logic circuits was not tested under existing test procedures: 1) Charging Pump A(B)(AB), 2) CAR-201 Valve A(B) and 3) HVC-103 Damper A(B). The root cause of the condition was an inadequate surveillance procedure (OP-903-094). The procedure has subsequently been revised and the applicable contacts have been tested, with the exception of one contact (associated with Charging Pump AB) for which testing is pending performance of scheduled Emergency Diesel Generator 'A' subgroup relay testing. The contacts that were tested were found to function properly. LER 97-014 (Revisions 00 and 01) reported a similar condition associated with, recently completed, Generic Letter (GL) 96-01 reviews. The relay contacts currently being reported were inadvertently not identified and/or tested during the GL review effort due to inadequate design documents and human performance deficiencies. The inadequate design documentation will be corrected and the isolated incorrect assumption made by a reviewer has been clarified with the reviewer. ESFAS relay contact listings have been independently compiled and are being compared with GL 96-01 review documentation to ensure that all ESFAS relay contacts are accounted for. This condition did not compromise the health and safety of the general public. ATTACHMENT 1 TO 9712180081 PAGE 1 OF 1 Attachment "REQUIRED NUMBER OF DIGITS/CHARACTERS FOR EACH BLOCK" omitted.
3821997030 | Waterford 3 | 11/14/1997 | 06/22/1998 | 9806240322 | <strong>TS 3.6.3 Noncompliance Due To Design Error Associated with the CARs CIVs</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1997, with Waterford 3 in Mode 1 and at 100% power, a condition was discovered wherein the normally closed inside and outside Containment Isolation Valves for the Containment Atmosphere Release System were subject to a single failure which could result in failure of the isolation valves to automatically close or remain closed upon receipt of a Containment Isolation Actuation Signal. The provisions of Technical Specification (TS) Action Statement 3.6.3b require inoperable automatic containment isolation valves to be closed and deactivated. The valves were closed, except briefly during surveillance testing, but were not deactivated as specified. This circumstance was discovered while performing the quarterly surveillance test procedure. The procedure had been recently revised due to the failure to test safety related logic circuits pursuant to Generic Letter 96-01 (see LER 97-029-00). At the time of this event, TS 3.6.3 had been previously entered. The applicable valves remain inoperable per TS action 3.6.3b. The root cause was determined to be an inadequate modification. The control circuitry will be rewired to resolve this condition. This condition did not compromise the health and safety of the public.
3821997031 | Waterford 3 | 11/20/1997 | 12/22/1997 | 9712300114 | <strong>HYDROGEN ANALYZER VALVE POSITION INDICATION</strong><br /><i>Abstract:&nbsp;</i>ABSTRACT: On November, 20, 1997, Waterford 3 personnel determined the configuration of limit switches for Hydrogen Recombiner Analyzer valves 109 A(B), 110 A(B), and 126 A(B) did not meet the requirements of Technical Specification (TS) 3.3.3.6 for containment isolation valve position indication. At the time of discovery, Waterford 3 was in Mode 1 at 100% power. The root cause for this event is an inadequate design. Control Wiring diagrams for the valves indicated that the limit switches were wired in series. This configuration provided open/close indication when the first valve reached the open/close status with other valves potentially in travel. The wiring for the limit switches has been changed to parallel in order to provide positive indication when all three valves have completed their travel to the open/close position. Although position indication was inadequate prior to the change, the condition did not interfere with the ability of the valves to perform their required safety function. Therefore, this condition did not compromise the safety and health of the public. END OF ABSTRACT
3821997032 | Waterford 3 | 11/26/1997 | 10/08/1998 | 9810130103 | <strong>HRA NONCOMPLIANCE WITH GDC 54</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1997, Design Engineering determined Hydrogen Analyzer (HRA) piping penetrating containment did not meet the requirements of General Design Criteria (GDC) 54 which requires reliable redundancy to ensure containment isolation. Given noncompliance with GDC 54, operators declared outboard containment isolation valves (CIVs) HRA 110 A(B) inoperable, deactivated the valves and secured them in the isolated position per Technical Specification (TS) 3.6.3. As a result of those actions, HRA 109 A(B) and HRA 126 A(B) and both hydrogen analyzers were declared inoperable. The root cause of this condition was an inadequate design. On November 28, 1997, HRA 109 A(B), 110 A(B), and 126 A(B) were reclassified under the provisions of 10CFR50.59 from normally locked closed, automatic CIVs to remote manual, locked closed CIVs. Furthermore, surveillance procedure OP-903-031, "Containment Integrity Check," was revised to require periodic verification that the reclassified valves are secured in their proper position. This condition did not compromise the health and safety of the public.
3821997033 | Waterford 3 | 12/05/1997 | 01/05/1998 | 9801090071 | <strong>10CFR50.46 ACCEPTANCE CRITERIA EXCEEDED DUE TO INADEQUATE PROCEDURE</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1997, Waterford 3 estimated that application of maximum High Pressure Safety Injection (HPSI) flow measurement uncertainty to a previously approved Emergency Core Cooling System (ECCS) model would exceed 10 CFR 50.46 acceptance criteria. Specifically, it is estimated that application of the uncertainty to model inputs using recently measured HPSI flow rates would cause the calculated peak fuel cladding temperature to increase by more than 50 degrees F and exceed 2200 degrees F. The apparent cause of this event is inadequate procedures and instructions. The calculation used to support HPSI minimum flow rate requirements utilized a 5 gpm/leg flow measurement uncertainty versus a revised maximum flow measurement uncertainty of approximately 18 gpm/leg. A small break loss of cooling accident ECCS analysis will be performed using a new ABB/CE ECCS evaluation model. That model was NRC approved for use at Waterford 3 on December 18, 1997. The new ECCS model provides sufficient margin to accommodate the uncertainty deviation. Therefore, this condition did not compromise the health and safety of the public.
3821997034 | Waterford 3 | 12/17/1997 | 01/16/1998 | 9801200129 | <strong>MISSED MECHANICAL SNUBBER SURVEILLANCE</strong><br /><i>Abstract:&nbsp;</i>As a result of a failed functional test in refueling outage (RFO) 5, snubber MSSR-226A was replaced with a like PSA-100 snubber and should have been retested during RFO6 in accordance with TS surveillance requirement 4.7.8. A record search performed by engineering on 12/17/97, revealed that the snubber was not tested as required in RFO6 or any subsequent refueling outage. The apparent cause of this event was personnel error. The failed functional test in RFO5 was inadvertently identified on the surveillance tracking form as satisfactory. As a result, this snubber was missed when testing was scheduled for the following refueling outage. On 12/18197, MSSR-226A was replaced with a like PSA-100 snubber. The replacement snubber had been tested and determined to be functional prior to installation. The snubber removed was tested on 1/7/98 and determined to be functional. This event did not compromise the health and safety of the public.
3871997001 | Susquehanna 1, Susquehanna 2 | 01/02/1997 | 01/30/1997 | 9702050035 | <strong>SPING Terminals Not Communicating With Field Units</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At 0825 hours on January 2, 1997, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, a gas sample and flow verification as required by Technical Specifications was not performed within the time limit of the ACTION Statement, thus constituting a condition prohibited by Technical Specifications. The sample is required while the Ventilation Monitoring System (VMS) is out of service. At approximately 0630 on January, 1, 1997, the Control Room Control Terminal stopped continuous communication with the field units. LCO's 3.3.7.5 (Action 81) and 3.3.7.11 (Actions 111, 112, 113, 114, and 116) were entered on January 2, 1997 at 0825, when all SPINGS were declared inoperable. The required ACTIONS of LCO 3.3.7.11 require a gas sample to be taken within 8 hours (Actions 111 and 114) or within 4 hours (Action 1 16), and flow rate through the vent path be estimated at least once per 4 hours (Action 113). The equipment was not identified as inoperative until the time limits specified in the ACTION Statements were exceeded. The LCO's were cleared at 1525 on January 2, 1997 when the VMS terminals were reset and the problem cleared. The cause of the event has been determined to be a software problem involving interfacing with the plant process computer; and inadequate procedural guidance for the operator to recognize a problem with the communication terminal of the VMS. There were no safety consequences or compromises to the public health or safety. Corrective actions include: Restoration of the VMS; procedural guidance to the operator to ensure the VMS control terminal is communicating with the field units; evaluation for possible changes to improve system performance; removal of the auto time correct feature via the plant process computer; and implementation of an alarm on the plant process computer to provide a warning any time a VMS point is not getting valid data.
3871997002 | Susquehanna 1, Susquehanna 2 | 01/30/1997 | 03/03/1997 | 9703100002 | <strong>Reactor Water Clean-up (RWCU) System Delta-Flow Isolation Setpoint Non-Conservative</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 30, 1997, with Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, the Reactor Water Cleanup (RWCU) System delta-flow isolation setpoint was found during the Design Basis Documentation review process to be non-conservative. The setpoint is based on 'cold' conditions in the RWCU System rather than 'hot' conditions. The equivalent 'hot' condition setpoint was greater than the allowable value in the Technical Specifications. This is a condition prohibited by Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). The cause of the RWCU System delta-flow setpoint being non-conservative was that during the preparation of the original setpoint calculation it was not recognized that the calculation should have been done for 'cold' conditions and not 'hot' conditions because of less than adequate documentation of the design basis for the setpoint. The setpoint calculations were revised, the RWCU System delta-flow instruments were recalibrated using the new setpoint, and the alarm response and surveillance procedures have been revised to include the new setpoint. In addition a review of all other relevant systems for similar potential setpoint methodology application errors will be done. The appropriate design basis for the differential flow setpoint will be incorporated into RWCU Design Basis Documentation.
3871997003 | Susquehanna 1, Susquehanna 2 | 01/31/1997 | 03/03/1997 | 9703100046 | <strong>Condition Prohibited by Plant's Technical Specifications - Interpretation Not In Strict, Verbatim Compliance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 31, 1997, with Unit 1 and Unit 2 in Operational Condition 1 at 100% and 75% power, respectively, it was determined that an interpretation of the plant's Technical Specifications to allow testing of individual control rods with the plant in Operational Conditions 3 or 4 was not in strict, verbatim compliance with the wording of the Technical Specifications. Namely, footnote *** to Table 1.2, which states that the reactor mode switch may be placed in the Refuel position when the plant is in Condition 3 or 4 while a single control rod is being recoupled, was interpreted to allow this action for performing single rod testing. The interpretation had been used to support single control rod testing during refueling outages on both Susquehanna units from 1995 to present. Although technically justifiable, this constituted a non-compliance with the Technical Specifications from a strict, verbatim compliance perspective. There were no safety consequences or compromises to public health or safety. The root cause for this condition was attributed to human error at the time the original interpretation was issued in 1994, in that strict, verbatim compliance with the wording of the Technical Specifications was not assured. The interpretation was deleted and a Technical Specification amendment request was issued to the NRC. Training on the circumstances of the event and reemphasis on verbatim compliance with licensing basis documents was completed for applicable personnel.
3871997004 | Susquehanna 1 | 02/01/1997 | 02/28/1997 | 9703060173 | <strong>Reactor Core Thermal Power Exceeded 102%</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 1, 1997 at 2334 hours, with Unit 1 at 100% Power in Condition 1, the control room received the APRM UPSCALE and the ROD OUT BLOCK alarms. The 'A' reactor recirculation pump had run up to its high speed limit increasing core power. As a result, the core thermal power went to maximum of 103.5% (3560.8 MWth) of rated power (3440 MWth). Speed of the 'B' recirculation pump was reduced to control power. Power was returned to below 3440 MWth in approximately 65 seconds. This constitutes a condition outside of the operating guidance set forth in NRC memorandum SSINS #0200. The root cause of the event is attributed to a failed fuse on a circuit card in that pump's generator speed control loop. The reactor recirculation pump controller failure high is an analyzed accident which completely bounds this event. No licensing safety limits were approached and as such, there were no safety consequences to the plant or compromises to public health and safety. Corrective actions completed include: Reducing core thermal power to within design limits, and replacing the circuit card. In addition, a failure analysis of the removed circuit card will be performed.
3871997005 | Susquehanna 1, Susquehanna 2 | 02/04/1997 | 03/27/1997 | 9704030085 | <strong>Closed System Integrity Not Verified By Testing</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 4, 1997, with Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, the redundant containment isolation barrier (closed system) for the Residual Heat Removal (RHR) System full flow test and the RHR suppression pool spray penetrations were found not tested per Technical Specification requirements. This is a condition prohibited by Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). In addition, on February 26, 1997, two additional penetrations on the RHR System were found not tested per Technical Specifications. A conclusive cause could not be determined. The most likely cause was human error associated with the original design engineers not ensuring that design requirements were adequately incorporated into testing requirements. Several causal factors related to human performance were identified. Corrective actions include: testing of the closed systems, performance of leakage quantification testing, revision to surveillance procedures, revision to the leak rate test program and training on closed system design and testing requirements. There were no safety consequences or compromises to public health and safety by not having the redundant barrier tested since isolation of the penetrations was provided by closed valves which were tested in accordance with Technical Specification requirements.
3871997006 | Susquehanna 1 | 02/25/1997 | 03/27/1997 | 9704040134 | <strong>Unit 1 Manual SCRAM - Loss Of Vacuum</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 064%. On February 25, 1997, at 1723 hours with Unit 1 in Condition 1 (Power Operation) at 64% power, the unit was manually scrammed due to a loss of condenser vacuum. Condenser vacuum was lost when the Unit 1 Offgas System isolated on a false high-high hydrogen signal from an electrical short caused by water intrusion into a hydrogen analyzer from an in-plant work activity. Neither the common nor the Unit 1 Offgas recombiner could be restored to operation as a result of solenoid valve problems. The plant was safely shutdown and there were no safety consequences or compromises to public health or safety during this event, nor would there have been under different initial operating conditions. generated due to water intrusion as a result of maintenance activities in the vicinity. While provisions had been made to capture and divert the fluid, the collection device became plugged and overflowed. Subsequent investigation indicated that less than adequate assessment of risk associated with work activities contributed. Procedural inadequacies for Offgas System operation inhibited the successful swap to the Common recombiner and complicated the recovery of the Unit 1 recombiner. The corrective actions include: repair of the hydrogen analyzer and subject solenoid valves; completion of a risk assessment review for work presently in the field; procedural revisions; training of involved personnel on this event; evaluation of training frequencies; reinforcement of standards with Maintenance Supervision; additional oversight on in-plant work activities; and performance of an assessment of the treatment of Maintenance Rule Non-Risk Significant Systems.
3871997007 | Susquehanna 1 | 03/01/1997 | 04/18/1997 | 9704240141 | <strong>Jet Pump Flow Transmitter Found Isolated - Condition Prohibited By The Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. At 0530 hours on March 19, 1997, with Unit 1 in Operational Condition 1 (Power Operation) at 73% power, it was discovered, by a field operator on rounds, that the flow transmitter for jet pump #14 was isolated and had been isolated since February 27, 1997. Since the time period from when the jet pumps were required to be operable in Operational Condition 2 (3/3/97) until the transmitter was restored exceeded the Technical Specification LCO Action time, this represented a condition prohibited by the plant's Technical Specifications. The root cause of this event was determined to be that actions had been taken to change the configuration of the transmitter using information contained in a note on the personnel protective permit for a work activity and not in accordance with plant procedures. The jet pump remained capable of performing its specified safety function throughout the time the transmitter was isolated. The transmitter was restored. Actions to prevent recurrence include: clarifying station policies and procedures regarding control of work activities and changes to work documents; and reviewing the event with station personnel.
3871997008 | Susquehanna 1, Susquehanna 2 | 02/26/1997 | 04/25/1997 | 9705010227 | <strong>Requirements For Response Time Testing Not Met - Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 26, 1997, at 2025, with Unit 1 in Condition 1 (Power Operation) at 100% power and Unit 2 in Condition 5 (Refuel) at 0% power, it was determined that the requirements of Technical Specification surveillances 4.3.1, 4.3.2 and 4.3.3 (Response Time Testing (RTT)) were not fulfilled. This constitutes a condition prohibited by Technical Specifications. Technical Specification 3.0.3 was entered for Unit 1, until enforcement discretion was granted. Susquehanna SES had removed the RTT tables from the Technical Specifications, relocating them to the Final Safety Analysis Report, and then modified the tables via 10CFR50.59. Due to a later interpretation of the Technical Specification requirements, based on the NRC's letter to another licensee, it was determined that the requirements for RTT were not fulfilled. This Technical Specification non-compliance is due to PP&L's original assumption that no Technical Specification change was required for RTT elimination. A review of the 10CFR50.59 document for elimination of the RTT, and the no significant hazards written for removal of the RTT table from the Technical Specification, indicates that the health and welfare of the public was not compromised. Enforcement discretion for this event was requested and approved, and an exigent Technical Specification change has been requested from the NRC. A thorough review of the appropriate surveillance procedures will be completed and revisions made as required.
3871997009 | Susquehanna 1, Susquehanna 2 | 04/02/1997 | 05/01/1997 | 9705070079 | <strong>Fire Watch Rounds Not Completed Within Time Limits</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 2, 1997, with Unit 1 in Condition 1 (Power Operation) at 100% power and Unit 2 in Condition 5 (Refueling) at 0% power, it was discovered during line management review that, on two separate occasions, roving fire watch patrols did not survey fire areas as required by Technical Specification ACTION statement 3.7.7.a. These events are reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. The causes of the events were determined to be that the subject individuals' on-the-job fire watch training and qualification was ineffective and the methods used to document fire watch rounds did not provide timely feedback if an error should occur. The corrective actions include the survey of the areas missed, refresher training for fire watch personnel, revision to the on-the-job training practices, additional training for supervisors with respect to instructing and coaching, and evaluation of methods to provide prompt feedback to the fire watch patrol. Plant operation was not affected, and no fire occurred nor went undetected during the time period involved. As such, there were no safety consequences or compromises to public health and safety.
3871997010 | Susquehanna 1 | 10/13/1996 | 05/23/1997 | 9706020129 | <strong>Reactor Vessel Water Level Instrumentation In Condition 4 Not Tripped In Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1997, with Unit 1 in Condition 1 (Power Operation) at 100% power, Engineering personnel (Utility; non-licensed) discovered during a review of the Boundary System Leakage/Hydrostatic Pressure Test procedure for Unit 2, that the Reactor Vessel Level (Low Level 3) instruments had been isolated but the Limiting Condition for Operation (LCO) for Technical Specification 3.3.2 had not been entered during the Unit 1 Boundary System Leakage/Hydrostatic Pressure Test in October 1996. The applicable operational condition for the reactor vessel water level switches had been revised in a Technical Specification Amendment dated December 18, 1995. During the investigation of this event, it was determined on April 30, 1997, that the time limits of the LCO ACTION statements had been exceeded during the October 1996 test performance. This constituted a condition prohibited by Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). The cause was determined to be that the list of procedures requiring revision (approximately 380), generated using a draft of the proposed amendment to the Technical Specifications, was not validated against the list that would have been generated if the actual submitted amendment request had been used. Corrective actions include the revision to surveillance and test procedures, and review of the event with station personnel reemphasizing that procedural revisions required for Technical Specification implementation are validated against the actual submitted amendment request, per the approved administrative procedure. There were no safety consequences or compromises to public health and safety as a result of these events since, even though the automatic isolation signal was not available, the isolation valves were functional and could have been manually closed in accordance with plant operating procedures.
3871997011 | Susquehanna 1 | 04/22/1997 | 05/22/1997 | 9705290197 | <strong>Loss of Turbine Building Ventilation Stack Flowrate</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1997, at 1100 hours, with Unit 1 in Condition 1 (Power Operation) at 100% Power, it was identified that the indicated flowrate through the Unit 1 Turbine Building (TB) Ventilation Stack had been decreasing since March 31, 1997. At that time, the TB Vent Stack Flow monitoring channel was declared inoperable. The applicable requirement of the Technical Specification Limited Condition for Operation (LCO) ACTION Statements were invoked. Investigation of the condition identified that one of the tubing lines inside of the SPING panel had been crimped, most likely occurring during previous work done on March 31, 1997. Further review of the TB SPING flow daily averages indicated a decreasing trend from March 31, 1997, reaching a level that would place it outside of the flow surveillance allowable tolerance on approximately April 7, 1997. Since the indicated vent flow was reading non- conservatively low from at least April 7, 1997, the event is determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by Technical Specification Table 3.3.7.11-1, ACTION 113, in that the required 4 hour flow estimates were not taken. The cause of the event has been determined to be the crimped tube as a result of the previous work evolution and insufficient trending of flow to earlier identify the anomaly. The crimped tubing was repaired and normal operation resumed. Review of estimated flowrates indicated that at no time did the release rate exceed the SPING setpoint or the Technical Specification limits. Therefore, the health and welfare of the public was not compromised. Corrective actions include repair of the damaged tubing and performance of the applicable flow surveillance prior to return of the SIDING to operable status and training of personnel involved on the significance of the event and attention to detail in the work process. In addition to these corrective actions, an evaluation will be done to identify the most effective trending method of the flow channel to allow detection of flow problems in a more timely manner.
3871997012 | Susquehanna 1, Susquehanna 2 | 04/24/1997 | 05/27/1997 | 9706030090 | <strong>Firewatch Not Established Within Time Limits</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 24, 1997, with Unit 1 in Condition 1 (Power Operation) at 100% power and Unit 2 in Condition 5 (Refueling) at 0% power, Operations Engineering personnel (Utility; non-licensed) discovered during a review of the surveillance procedure which verifies valve alignment in the fire protection systems, that the shutoff valves for the carbon dioxide (CO sub 2) fire protection system had been deleted from this surveillance procedure during a revision to the procedure in December 1996. Technical Specification 4.7.6.3.1 requires that these valves be surveilled monthly to insure their proper alignment and the operability of the CO sub 2 fire protection system. Since these valves had not been surveilled since November 1996, the Limiting Condition for Operation (LCO) for Technical Specification 3.7.6.3 should have been entered and a continuous firewatch posted. The continuous firewatch was not established within the time limits of Technical Specification 3.7.6.3 ACTION a; therefore, this constitutes a condition prohibited by Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). Upon discovery that the valves were deleted from the monthly surveillance procedure, the procedure was revised and the surveillance of the valves was satisfactorily performed. The cause of the event was determined to be an inadequate review of the revision to the surveillance procedure. The corrective actions that were completed include revision to the surveillance procedure, performance of the surveillance, and discussion of the importance of accuracy and verification with the individuals involved with the revision of the surveillance procedure. Additional corrective actions include revising the procedure change process and reviewing and revising the fire protection operational surveillances to ensure accuracy. There were no safety consequences or compromises to public health and safety as a result of this event, since when the surveillance was performed, the valves successfully passed and there is no other indication that the valves were in other than their requi re d position during this time frame.
3871997013 | Susquehanna 1, Susquehanna 2 | 07/19/1997 | 07/21/1997 | 9707290220 | <strong>Requirements for Testing Activated Carbon Samples Not Met</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1997, at 1400, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, during a review of the specification used to purchase new activated carbon, it was determined that the requirements for periodic testing of used activated carbon samples by laboratory analysis differed from the requirements as specified by Technical Specification surveillances 4.6.5.3.b.2, 4.6.5.3.c, 4.7.2.b.2, and 4.7.2.c. On June 25, 1997, it was determined that the Technical Specification requirements for testing were not being met. This constitutes a condition prohibited by Technical Specifications. Limiting Condition For Operation (LCO) 3.0.3 was entered until enforcement discretion was granted. The cause of the event was determined to be human performance in that it was not recognized that the Technical Specifications needed to be revised when improved industry standards for testing activated carbon were identified in 1987. A Technical Specification change has been requested from the NRC. In 1996, specific training on maintaining licensing basis documents has been provided to engineering and management personnel. An evaluation of processes, such as revising tests and standards used by PP&L, will be performed to insure consistency with licensing documents. There were no safety consequences or compromises to public health and safety as a result of this event since the test methodology used provided greater assurance to determine the adsorption capability of the charcoal.
3871997014 | Susquehanna 1, Susquehanna 2 | 07/19/1997 | 07/14/1998 | 9807210395 | <strong>Operation With the Ultimate Heat Sink Temperature in Above the Maximum Allowed</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1997 at 0900, with Unit 1 and Unit 2 both in Condition 1 (Power Operation) at 100% power, engineering personnel determined that on several occasions the average temperature of the Ultimate Heat Sink (UHS) exceeded the maximum initial temperature allowed (as supported by calculations). During an engineering review, a calculational methodology error was identified in the decay heat input to the UHS calculation. Correct inputs were entered into the calculation for UHS initial temperature, which resulted in a lower UHS maximum allowed initial temperature. The original (flawed) calculation indicated a maximum allowed initial temperature of 88 degrees F, as does the Technical Specifications, while the new calculation could support only an 82 degrees F initial temperature with the operating procedures as they existed. There were 10 occasions in the past where 82 degrees F was exceeded. Analysis indicates that, although the initial temperature was exceeded, the safety significance of these events were very minor. PP&L immediately took steps to administratively control UHS average temperature to ensure it did not exceed that value supported by calculation. PP&L has also made procedural changes, supported by calculation, to allow an increase in the maximum UHS initial average temperature from 82 degrees F to 85 degrees F. At no time was the health and safety of the public compromised as a result of this event. Also, at no time were the current Technical Specification limits exceeded. This is being reported to the Commission pursuant to 10CFR5073(a)(2)(ii) as a condition where the plant operated outside of its design basis, although, as stated previously, the conditions discussed here were of minor significance from a safety perspective. Corrective actions include: a review of other calculations that may have used the calculation methodology error, performance of a calculation to bound UHS temperature with design basis conditions, initiating Final Safety Analysis Report changes, requesting a Technical Specifications change, counseling appropriate engineering personnel on use of the decay heat standard. and reviewing the event for inclusion in Engineering Continuing Training.
3871997015 | Susquehanna 1, Susquehanna 2 | 07/02/1997 | 08/01/1997 | 9708070114 | <strong>Liquid Effluent Grab Sample Analysis Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1997, at 1630 hours, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, it was determined during a review of procedures as a follow-up to a previous plant event, that the requirement of Technical Specification Table 3.3.7.10-1, ACTION 101 was not being met. Technical Specification Table 3.3.7.10-1, ACTION 101, requires a gross radioactivity analysis on liquid effluent grab samples when the associated effluent monitoring instrumentation is not operable to be performed. Performance of gamma isotopic analysis does not meet the Technical Specification requirement since it does not measure gross radioactivity to a sensitivity of 1E-7 microcurie/ml. This event was determined to be a condition prohibited by Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). The cause of the event was determined to be human performance. It was not recognized that a change to the Technical Specifications was required since it was viewed that the isotopic analysis was an improved method of analysis. There were no safety consequences or compromises to public health and safety as a result of this event as the isotopic analysis is a better analysis in determining radioactivity in effluents. Corrective actions include: providing requirement to perform the gross radioactivity analysis along with the isotopic analysis and submitting a revision to the Technical Specifications.
3871997016 | Susquehanna 1, Susquehanna 2 | 07/03/1997 | 08/04/1997 | 9708080116 | <strong>Fire Hose Station Surveillances Not Completed Within Time Limit</strong><br /><i>Abstract:&nbsp;</i>On July 3, 1997, at 1500 hours, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power while performing a review of surveillance performance dates as part of an audit of the fire protection program, it was determined that the monthly surveillance to inspect fire hose stations had not been completed within the frequency as required per Technical Specification Surveillance Requirement 4.7.6.5.a. Technical Specification Surveillance Requirement 4.7.6.5.a requires inspection of the fire hose stations listed in Table 3.7.6.5-1 at least once per 31 days. The frequency for performing this surveillance including the grace period was exceeded seven (7) times since January 1995. In addition, while reviewing other surveillances that use a fixed schedule, it was determined that the 6-month surveillance of fire hydrants had exceeded its frequency, including the grace period on one occasion since January 1995. This is a condition prohibited by Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). The cause of the event was determined to be that the scheduling tool used to track these surveillances used a fixed date each month for the determination of the start of the surveillance instead of calculating the start date from when the surveillance was last performed. Corrective actions include: revising the method of tracking these surveillances and discussion of this event with appropriate plant personnel. There were no safety consequences or compromises to public health and safety as a result of this event since during subsequent surveillances, no problems with fire hose stations or fire hydrants were found.
3871997017 | Susquehanna 1, Susquehanna 2 | 07/11/1997 | 08/07/1997 | 9708140101 | <strong>Loss Of Control Structure HVAC Due To 'A' Diesel Generator Governor Knob Mispositioning</strong><br /><i>Abstract:&nbsp;</i>On July 11, 1997, at 1715 hours, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, the 'A' Emergency Diesel Generator (D/G) governor load limit control knob was observed to be mispositioned. This condition rendered the 'A' D/G inoperable, and Technical Specification 3.8.1.b was entered at 2010 hours. The loss of the 'A' D/G could, under a Loss of Coolant Accident (LOCA) / Loss of Off-site Power (LOOP) condition, lead to the loss of the 'A' Engineered Safeguard System (ESS) Electrical Power Bus. Loss of this bus will result in the loss of the 'A' Control Structure Heating, Ventilation and Air Conditioning (HVAC). The 'B' Control Structure HVAC was out of service for maintenance. The loss of the Control Structure HVAC constitutes a potential loss of a system required for the safe shutdown of the plant. This condition is reportable per 10CFR50.72(b)(2)(iii)(A) and per 10CFR50.73(a)(2)(v). Analysis shows that the plant could be shut down and maintained shut down for the first three (3) days following an accident without the Control Structure HVAC system. The 'B' Control Structure HVAC train could be returned to service in that time, so this is seen to have minor safety significance. At no time was the health and welfare of the public compromised. Corrective actions that have been taken include: restoration of the 'A' D/G to operable status, heightened awareness on the part of Operations and Security, limiting personnel access to the D/G Bays, performance of confidence check on critical plant components, installation of tamper paint on all D/G governor control knobs, periodic checks of governor control knob position during operator rounds, and briefing of all plant personnel on this event. The following actions are being taken: An independent review of this event is in progress, modification of the D/G governor to install a cover over the control knobs, and re-evaluation of the current personnel access program/procedures.
3871997018 | Susquehanna 1 | 08/08/1997 | 09/08/1997 | 9709120083 | <strong>Relay In Isolation Logic Not Response Time Tested</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1997 at 1515 hours, with Unit 1 in Condition 1 (Power Operation) at 100% Power, it was determined that the requirements of Technical Specification Surveillance 4.3.2.3 were not fulfilled. This constitutes a condition prohibited by the Technical Specifications. During preparation of a Technical Specification Change Request, it was identified that two relays associated with two Reactor Building Closed Cooling Water (RBCCW) isolation valves had not been response time tested and are outside the scope of the Licensing Topic Report NEDO32291A, for equipment not requiring response time testing. Upon identification, the appropriate Limited Condition for Operation (LCO) actions were entered. The relays were promptly tested and deemed to meet their associated valve's closing time requirements. The cause of the event has been identified as weaknesses in the surveillance procedures and programs at the time of inception of the Response Time Testing (RTT) procedures. These shortcomings have been addressed by program enhancements during the ensuing years. The subject relays have been periodically logic tested (but not time response tested) with no observed misoperation. The safety significance of this event is considered minor. The health and welfare of the public was not compromised. The following corrective actions have been completed: the RTT was completed and approved and comprehensive review of the Isolation Actuation System Logic with respect to RTT was completed. Incorporation of the timing of the subject relays into an appropriate surveillance is scheduled for future completion.
3871997019 | Susquehanna 1, Susquehanna 2 | 08/13/1997 | 09/11/1997 | 9709170105 | <strong>Control Structure Chiller Will Not Auto-Start</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1997 at 1200 hours, with Unit 1 and Unit 2 in Condition 1 (Power Operations) at 100% Power, engineering personnel determined that prior to March 1, 1997, the Control Structure Chilled Water System was operating outside of its design basis, constituting a reportable condition per 10CFR50.73(a)(2)(ii). The Final Safety Analysis Report (FSAR) states in part that the standby Control Structure Chiller will auto-start on a failure signal to the operating chiller. Contrary to this, there was a condition that existed for the 'A' chiller that inhibited its auto-start while in standby. No similar condition existed for the 'B' Control Structure Chiller. The condition, once identified, was promptly corrected via the temporary modification process, and tested to operate as described in the FSAR. The logic changes have subsequently been made permanent. At the time of discovery of the logic error on March 1, 1997, the condition was entered into the Susquehanna SES corrective action program. It was incorrectly identified as not reportable at that time. Subsequent review has determined this to be reportable. The Control Structure Chiller is required to maintain Control Structure habitability and the Unit 1 emergency switchgear cooling post-accident. Although the standby chiller would not have auto- started on a trip of the operating chiller (for one specific failure signal), it would have started on high return air temperature approximately one to two hours following loss of cooling. Evaluations have been performed that indicate cooling to the emergency switchgear could be lost for up to ninety-six hours post-accident with no loss of safety function. Similarly, no significant degradation of Control Structure habitability would occur. Based on this, the safety significance of this event is minor. Corrective actions completed were the permanent modification of the Control Structure Chiller logic to allow auto-start of the standby compressor on all operating chiller failure trips and reportability determination training for the involved personnel.
3871997020 | Susquehanna 1 | 09/10/1997 | 05/24/1999 | 9905270259 | <strong>Operation Prohibited By Technical Specification - Loss Of MSRV Acoustic Monitor</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1997, at 1750 hours, with Unit 1 in Condition 1 (Power Operation) at 100% Power, the acoustic monitor for the 'S' Main Steam Relief Valve (MSRV) was declared inoperable and Technical Specification 3.3.7.5, ACTION 80, and 3.4.2.c ACTION were entered. Repair of the acoustic monitor requires a primary containment entry. Operators, using guidance from the appropriate off-normal procedure, were able to assure that the 'S' MSRV was closed. Enforcement Discretion was requested by PP&L and granted by the NRC for continued operation until an outage of sufficient duration, not to exceed the Unit 1 10th Refuel Outage. This event is reportable per 10CFR50.73(a)(2)(i)(B), in that Susquehanna Unit 1 was in a condition prohibited by Technical Specifications when it remained at power operation beyond the limit specified in the ACTION statements of Technical Specifications. The cause of the acoustic monitor failure was determined to be degradation of the charge converter components due to aging. Operation with the 'S' acoustic monitor inoperable does not create a significantly degraded condition in the Station's ability to protect the health and safety of the public and the ability of the plant to shut down safely is unaffected. The following actions have been completed: troubleshooting to the extent possible at the time of the event, request for Enforcement Discretion (granted) at the time of the event, alarm removed from service at the time of the event,determination of cause of failure of the acoustic monitor, and replacement of acoustic monitor components inside containment in both Unit 1 and Unit 2.
3871997021 | Susquehanna 1 | 09/21/1997 | 10/31/1997 | 9711060283 | <strong>Condition Prohibited By Technical Specification - Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1997, at 1247 hours, with Unit 1 in Condition 1 (Power Operation) at 100% Power and Unit 2 in Condition 4 (Cold Shutdown) at 0% Power, a voluntary entry into Technical Specification 3.0.3 was made. Prior to this, a damper in the Common Refuel Floor Ventilation System failed its stroke time test. As a result, the associated penetration was isolated as required by the ACTION statement of Technical Specification 3.6.5.2. Following the damper repair, dynamic stroke testing is required for operability. To accomplish this, the damper must be stroked with the ventilation system in service, requiring entry into Technical Specification 3.0.3, since there is no exception to the requirements in the ACTION of Technical Specification 3.6.5.2 to allow administrative control of the isolating dampers. This condition is addressed and corrected in the Improved Technical Specifications. The damper was modified to improve its closing time. The required building pressure (-1/4" wg) was maintained, and Standby Gas Treatment was available for the duration of the event. The safety significance of the event was minor. The health and welfare of the public was not compromised. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), in that this event resulted in a voluntary entry into Technical Specification 3.0.3, and is required to be reported per the guidance of NUREG 1022, Supplement No. 1.
3871997022 | Susquehanna 1, Susquehanna 2 | 10/06/1997 | 11/05/1997 | 9711120008 | <strong>Degasifier Exhaust Treatment Inoperable - Condition Outside Of Technical Specification 3.11.2.5</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1997 at 1200 hours, with both Unit 1 and Unit 2 in Condition 1 (Power Operation) at 100% power, it was discovered that the Primary Coolant Degasifier Exhaust Filter system was inoperable, when the exhaust treatment system showed evidence of water intrusion. Technical Specification 3.11.2.5 requires the appropriate portions of the Ventilation Exhaust Treatment System to be operable. The degasifier system is designed to remove oxygen from the primary coolant processes, and route the gases to the plant exhaust stack via a treatment system. Further investigation revealed that the treatment system was not available for an extended period. This report is being made pursuant to 10CFR50.73(a)(2)(i)(B), in that the requirement for the exhaust system operability was not met, and also fulfills the requirement of a Special Report per Technical Specification 3.11.2.5. Administrative controls were used to control effluent activity in lieu of maintaining operability of the degasifier exhaust treatment system by correcting the water condensation problems. The degasifier effluent was monitored via the Unit 1 Turbine Building Gaseous Effluent monitor and all other fission product barriers were intact. The health and safety of the public was never compromised. Corrective actions include removal of the degasifier system from service, procedural changes, degasifier modifications, and review of the event with appropriate personnel.
3871997023 | Susquehanna 1, Susquehanna 2 | 10/07/1997 | 11/06/1997 | 9711120119 | <strong>Fire Protection Features Not Surveilled</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1997, with both Unit 1 and Unit 2 in Condition 1 (power Operation) at 100% power, Engineering personnel (Utility; non-licensed) discovered that certain carbon dioxide (CO sub 2) fire protection suppression systems required to be included in the Technical Specifications had not been included nor surveilled in accordance with the Technical Specifications. This condition was discovered during a review of surveillances on fire protection features to ensure compliance with the Technical Specifications. The review of the surveillances versus Technical Specification requirements also determined that additional required fire protection features (detection, suppression and barriers) had not been included in the Technical Specifications, nor surveilled. Since these fire protection features had not been surveilled in accordance with the Technical Specification requirements, this constitutes a condition reportable per 10CFR50.73(a)(2)(i)(B). The cause of these events was attributed to less than adequate human performance on the part of engineering and licensing personnel and inadequate change management. Corrective actions include: declaring the fire protection features inoperable and taking the actions as required by the Technical Specifications; revising surveillance procedures; revising engineering calculations; and communicating Management's expectations with respect to the Technical Specification and its Bases. There were no consequences to public health and safety from these events.
3871997024 | Susquehanna 1, Susquehanna 2 | 10/22/1997 | 11/21/1997 | 9712010084 | <strong>Inboard Isolation Valves For The Drywell And Suppression Chamber Purge System Are Not Single Failure Proof</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1997, with Unit 1 and Unit 2 both in Condition 1 (Power Operation) at 100% power, engineering personnel determined, based on information provided in a 10CFR Part 21 Notification from General Electric Company, that during a postulated single failure of an electrical raceway, both inboard containment isolation valves on the Drywell and Suppression Chamber Purge System could open, thus causing the Drywell and Suppression Chamber atmospheres to communicate during a postulated Loss of Coolant Accident (LOCA). This single failure condition could result in bypass leakage of the postulated LOCA environment around the suppression pool, thus losing the benefit of both quenching the blowdown energy and the scrubbing of any fission products. This event was determined to be reportable in accordance with 10CFR50.73(a)(2)(ii). Technical Specification 3.0.3 was conservatively entered on both units until at least one inboard containment isolation valve, in the affected penetrations, was deactivated in the closed position. The entry into Technical Specification 3.0.3 is reportable in accordance with 10CFR50.73(a)(2)(i)(B), per the guidance of NUREG-1022, Supplement No. 1, Item 2.4. The most likely cause was human error on the part of the original designers for failing to recognize the potential for creating a suppression pool bypass path through the nitrogen supply line. The corrective actions include: 1) Deactivation of both inboard containment isolation valves in the closed position on both units; 2) other containment penetrations with the potential to be suppression pool bypass paths will be reviewed to determine if they are susceptible to the same single failure; and 3) participate in the BWR Owners Group on-going effort to evaluate the credibility of the postulated single failure. There were no safety consequences or compromises to public health and safety as a result of this event since there were no events which challenged prima containment integrity
3881997001 | Susquehanna 2 | 02/16/1997 | 03/18/1997 | 9703260002 | <strong>Loss of Both Trains of Emergency Switchgear Room Cooling</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 095%. On February 16, 1997, at 0800 hours, with Unit 2 in Condition 1 (Power Operation) at 95% power, the 'A' emergency switchgear room cooling fan breaker tripped due to thermal overload protection thus rendering the 'A' train of switchgear cooling inoperable. The 'B' train of emergency switchgear room cooling was out of service due to an inoperable fan discharge damper. These fans are required to mitigate the consequences of an accident by providing cooling to the Emergency Switchgear Rooms thus keeping the Engineered Safety System (ESS) 4.16 KV busses operable. Since fans on both trains of Switchgear Room Cooling were inoperable, this event is considered to be a loss of a safety system needed to mitigate the consequences of an accident and is reportable per 10CFR50.73(a)(2)(v)(D). The thermal overload protection was reset, the breaker closed in and the 'A' train fan restarted. Subsequently, the discharge damper on the 'B' train was repaired and the thermal overload protection replaced in the 'A' train fan breaker. The cause of the tripping of the 'A' train fan was determined to be that the thermal overload protection was under-sized since initial operation of the plant and an approved design change to replace the thermal overload protection was not implemented. Corrective actions include the replacement of the thermal overload protection, review of the existing plant change control process, revising the appropriate maintenance procedure to require verification of the installed overload protection to that specified by design documents, and a review of deficiency and work documents for safety-related equipment to assure that there are no outstanding issues with equipment tripping on thermal overload protection. to public health and safety as a result of both trains of Emergency Switchgear Room Cooling being inoperable since the cooling function was restored promptly.
3881997002 | Susquehanna 2 | 02/20/1997 | 04/09/1997 | 9704160383 | <strong>Isolation of Both Loops of Containment Radiation Monitoring</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 094%. This is a supplemental report to Licensee Event Report 50-388/97-002-00. At 0347 hours on February 20, 1997, with Unit 2 in Condition 1 (Power Operation) at 94% power, and at 0330 hours on March 11, 1997, with Unit 2 in Condition 1 (Power Operation) at 88% power, the control room received half scrams on Division I and Division II, respectively. The half scrams resulted from trips of the Reactor Protection System (RPS), which resulted in unplanned Engineered Safety Feature (ESF) actuations, including containment isolations. Isolation of both Containment Radiation Monitors (CRM) during each event and during restoration required entries into Technical Specification 3.0.3, constituting conditions prohibited by the Technical Specifications. The equipment response to the RPS trip was as expected. The conclusion of the investigation of both events is that the RPS trip was caused by an aging component on the RPS voltage regulator control card. The cards were replaced. Corrective actions include replacement of all subject cards on both Susquehanna units; failure analysis of the failed cards; evaluation of preventative maintenance activities and upgrades/enhancements of the RPS motor-generator sets; and an amendment to the Technical Specifications with respect to the Containment Radiation Monitors.
3881997003 | Susquehanna 2, Susquehanna 1 | 03/20/1997 | 04/18/1997 | 9704240100 | <strong>Required Sample Was Not Collected And Analyzed Within Technical Specification Time Limit</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 20, 1997, with Unit 2 in Condition 5 (Refuel) at 0% power, a sample required by Technical Specifications was not collected and analyzed within the time limit of the ACTION statement, thus constituting a condition prohibited by Technical Specifications. The sampling was required while the Service Water Radiation Monitor was out of service. A sample is required to be collected and analyzed once per 8 hours. The analysis was completed 13 minutes after the Technical Specification time limit. The cause of the event was attributed to less than adequate attention to detail by the technician performing the work. There were no safety consequences or compromises to the health and safety of the public. Corrective actions include: completion of sample analysis, restoration of the Service Water Radiation Monitor, placement of the involved technician into the company's program for performance improvement, and training of all Chemistry technicians to re-enforce employee expectations.
3881997004 | Susquehanna 2 | 03/22/1997 | 04/18/1997 | 9704240137 | <strong>Main Steam Line Penetration Leakage Rate Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. At 1730 hours on March 22, 1997, with Unit 2 in Condition 5 (Refueling, 0% power), an evaluation of data from the scheduled Main Steam Line (MSL) penetration Local Leak Rate Testing (LLRT) determined that the 'as-found' leakage through both the inboard and outboard Main Steam Isolation Valves (MSIV) was in excess of the limit of Technical Specification 3.6.1.2.c for the MSL containment penetration maximum pathway leakage of 300 standard cubic feet per hour (SCFH). The total 'as-found' maximum pathway leakage was in excess of 700 SCFH. However, the total 'as-found' minimum pathway leakage was only 78.8 SCFH. The evaluation determined that the MSIV LLRT excess 'as-found' maximum pathway leakage was reportable pursuant to 10CFR50.72(b)(2)(i) and 10CFR50.73(a)(2)(ii). The cause was determined to be that 2 MSIVs had excessive leak rates. The causes of the excessive leak rates were due to normal wear on one MSIV and loose internal parts on the other MSIV. The corrective actions include reworking of 2 MSIVs and revision of a Maintenance procedure. Since the leakage (the minimum path leak rate - 78.8 SCFH) that would have actually reached the condenser is well below the 300 SCFH analyzed in the dose calculations, there were no safety consequences or compromises to public health and safety as a result of this event.
3881997005 | Susquehanna 2, Susquehanna 1 | 03/25/1997 | 04/22/1997 | 9704250256 | <strong>Reactor Building Vent Continuous Sample Lost For twenty (20) Minutes</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 25, 1997, at 1830 hours with Unit 2 in Condition 5 (Refuel) at 0% Power, the sample flow from the Reactor Building ventilation stack was lost for a period of 20 minutes. Chemistry technicians were in the process of transferring from an alternate sample system to the SPING system when a spurious criticality monitor alarmed, forcing the technicians to evacuate the area immediately. Some 20 minutes later, the technicians again accessed the area and completed the transfer placing the SPING in service. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant Technical Specification Table 3.3.7.11-1, ACTION statement 112, in that continuous sampling of the Unit 2 Reactor Building vent was not maintained. The cause of the event was determined to be the false alarming of the fuel pool criticality monitor. Upon determination that the alarm was false, the continuous sampling was promptly placed in service. Vent sampling immediately before and after the flow interruption were analyzed, and showed levels well below the LLD's referenced in Technical Specifications. Additionally, there were no changes in plant conditions that would be indicative of a release. Therefore, it was concluded that no significant release of radioactivity occurred while sampling was lost, and thus, there was no compromise to the health and welfare of the public. Corrective actions included restoration of the SPING sampling unit. An additional action will be to request from the NRC, clarification to Technical Specification 3.3.7.11-1, ACTION statement 112, for an interpretation of continuous sampling.
3881997006 | Susquehanna 2 | 09/18/1997 | 10/20/1997 | 9710240226 | <strong>Recirculation Discharge Valve Bonnet Vent Line Crack</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1997 at 2120 hours with Unit 2 in Condition 4 (Cold Shutdown) at 0% power, it was discovered that a 1800 through wall crack in a weld existed on the 'B' Reactor Recirculation Discharge Valve bonnet 3/4" vent line, immediately upstream of the inboard vent valve. The unit had been conservatively shut down on September 17, 1997 due to an increase in unidentified drywell leakage prior to any Technical Specification limit being exceeded. The crack was discovered during an investigation into the source of the unidentified drywell leakage. This event is reportable pursuant to 10CFR50.73 (a)(2)(ii) in that Unit 2 was in a degraded condition. The cracking of the weld resulted from vibration-induced fatigue during operation that resulted from the piping being in a cantilevered configuration. The 'B' Reactor Recirculation Discharge Valve bonnet vent line in the vicinity of the weld was replaced during the Unit 2 eighth Refueling Outage in the Spring of 1997. The cantilever condition was not detected because of confusion over, and misinterpretation of, the requirements to perform hanger inspections in the design specification. Corrective actions that were completed include cutting and capping the affected vent line; inspection of similar configurations in Unit 2; and review of other similar work plans that were completed in the Unit 1 8RIO and Unit 2 7RIO. Proposed corrective actions include revising of the design specification; reviewing work packages not already implemented to insure the proper requirements for hanger inspection are incorporated; inspecting similar configurations in Unit 1; and training on the revision to the design specification. There were no safety consequences or compromises to public health and safety as a result of this event since even if a complete failure of the weld had occurred, the resulting small pipe break is bounded by an analyzed condition. The inventory loss from the break would be made-up by either the Reactor Core Isolation Coolant System (RCIC) or the High Pressure Injection System (HPCI). Both of these systems were operable at the time of the event.
3881997007 | Susquehanna 2 | 10/17/1997 | 03/30/1999 | 9804090017 | <strong>Entry Into Technical Specification 3.0.3 - Rod Block Monitor Operability Testing</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1997, at 0920 hours, with Unit 2 in Condition 1 (Power Operation) at 100% Power, a Technical Specification 3.0.3 entry was voluntarily made. In accordance with the guidance of NUREG 1022, a Technical Specification 3.0.3 entry requires an LER to be submitted within 30 days of the event. The entry was made to allow completion of surveillance testing of one channel of the Rod Block Monitor (RBM), after considering the other available options. There is no provision provided in current Technical Specifications to allow operability testing without entry into Technical Specification 3.0.3. The Technical Specification 3.1.4.3 ACTION statement had been entered to perform surveillance testing of one channel of the RBM. Unexpected results had been obtained during the testing. Investigation of these results determined that 11 LPRMs were not providing an output to the RBM. The testing resumed prior to the expiration of Technical Specification 3.1.4.3 ACTION allowable time limit, but would not be completed before the limit expired. Operations management voluntarily entered Technical Specification 3.0.3. and did not take the ACTIONS described in Technical Specification 3.1.4.3.a, that is placing the inoperable channel of the RBM in the trip condition. In reconsidering this event, PP&L has recognized that the ACTION of Technical Specification 3.1.4.3.a should have been taken to avoid a condition that could be construed as an entry into Technical Specification 3.0.3 made for operational convenience. The cause of the LPRM failures has been traced to inadequate post maintenance testing following earlier work associated with these components. The failed components were repaired/replaced, testing was completed and the RBM returned to operable status. The safety significance of this event was minor, and the health and welfare of the public was not compromised. The technical aspect of this event will be reviewed with the work group and a review of associated work plans and procedures will be performed, and appropriate changes implemented. Administratively, guidance dealing with voluntary Technical Specification 3.0.3 entry and guidance dealing with actions to be taken once Technical Specification 3.0.3 has been entered, will be provided. These changes will be communicated to appropriate personnel.
3881997008 | Susquehanna 2 | 10/30/1997 | 12/01/1997 | 9712080119 | <strong>PICV Position Indication Not Surveilled in Accordance With the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1997, with Unit 2 in Condition 1 (Power Operation) at 100% power, Operations personnel (Utility; non-Licensed) determined that the position indication for the Containment Radiation Detection System primary containment isolation valves and the Traversing Incore Probe (TIP) Shear valves had not been surveilled in accordance with Accident Monitoring Instrumentation Technical Specification Table 4.3.7.5-1, Item 12. Additionally, the position indication in the Control Room for Containment Atmosphere Control System primary containment isolation valves had not been surveilled. This event was determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B). The position indications for these valves were declared inoperable and Technical Specification 3.3.7.5, ACTION 80 was entered. The subject position indications were satisfactorily surveilled and declared OPERABLE. The cause of the event was determined to be human performance in that the subject valves' position indication verification had not been incorporated into the surveillance testing procedure. Corrective actions include: 1) the surveillance procedure for Technical Specification 3.3.7.5 was revised to include the subject valves; 2) the ITS Bases will be revised to provide a link between the primary containment isolation valve listing and the accident monitoring requirements; 3) the current Technical Specifications will be reviewed to ensure there are no other similar links between Technical Specification Sections that are not clearly annotated, and 4) this event will be reviewed with the appropriate functional groups.. There were no consequences to the health and safety of the public from not surveilling the position indication of these valves since 1) other means such as flow indication are available to the operator to determine valve position and 2) when the surveillances were performed the indication satisfactorily passed the surveillances.
3891997001 | St. Lucie 2 | 04/23/1997 | 05/21/1997 | 9705280064 | <strong>Containment Isolation Actuation due to Increased Radiation Levels During Removal of Upper Guide Structure</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1997, St. Lucie Unit 2 was in Mode 6 during a scheduled refueling outage. At 1758, a containment isolation actuation signal (CIAS) was received during the removal of the upper guide structure (UGS) in preparation for fuel movement. The CIAS was anticipated based on previously identified high radiation levels in the area of the upper incore instrumentation (ICI) guide tubes. Nonessential personnel had been removed from the area prior to UGS movement and the evolution was completed without further incident. The CIAS was reset following verification of component actuation and the completion of the UGS relocation to its refueling storage location. The CIAS was generated as a result of high radiation as measured by two-out-of-four containment isolation radiation monitoring instruments. The monitor set points had been adjusted to 90 mR/hr as required by plant Technical Specifications during the refueling mode. The elevated radiation levels were caused by the presence of irradiated ICI segments which had broken during removal and remained in the upper section of the ICI guide tubes contained in the UGS. Corrective Actions include: 1) Proper actuation of containment isolation components was verified. 2) ICI material found in the guide tubes was removed or relocated within the guide tube to ensure adequate shielding during UGS movement. 3) An engineering safety evaluation was performed to verify the acceptability of operation with simulated incore assemblies and ICI remnants. 4) Procedure changes were made to improve the ICI removal process. 5) FPL is continuing to evaluate the ICI failure mechanism and the need for additional corrective actions. 6) Radiological survey practices are being reviewed for improvement.
3891997002 | St. Lucie 2 | 05/18/1997 | 12/22/1998 | 9812300154 | <strong>Containment Sump Debris Screen not in Accordance with Design due to Gaps in Screen Enclosure</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1998, St. Lucie Unit 2 was in mode 6 at 0% reactor power. The Facility Review Group reviewed and approved the determination that various sump screen anomalies found during the Unit 2 cycle 11 refueling outage were reportable as a condition that was outside the design basis of the sump. As part of the long term corrective actions associated with the St. Lucie cycle 10 refueling outage identified ECCS sump deficiencies, surveillance procedure MSP-68.01, "Containment Sump Inspection," and QC Technique Sheet 10.54 were developed to provide detailed inspection scope and acceptance criteria for the ECCS sump screen enclosure inspections. The cycle 11 refueling outage inspection activities identified anomalies not found during the cycle 10 refueling outage sump repair activities. The cause of deficiencies found during the cycle 11 refueling outage was inadequate corrective actions for the sump screen anomalies found during the cycle 10 refueling outage. All identified sump screen deficiencies were dispositioned and/or repaired.
3891997003 | St. Lucie 2 | 05/21/1997 | 06/19/1997 | 9706250210 | <strong>Failure to Perform Post Maintenance Testing Caused Entry Into TS 3.0.3 Due to SIT Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 5/21/97, Unit 2 was in Mode 4 and less than 1750 psia. Each Safety Injection Tank (SIT) had a contained water volume of greater than 833 but less than 1250 cubic feet. At approximately 1045, FPL determined that a required post maintenance open stroke test for valve V3245, the 2B2 SIT discharge check valve, had not been performed. The 2B2 SIT was declared inoperable at 1225. Each of the remaining three SITs contained less than 1250 cubic feet of water, therefore the other three SITs could not be considered operable. Technical Specification 3.0.3 was immediately entered. The partial stroke Post Maintenance Test (PMT) for V3245 was successfully completed at 1235, and the 2B2 SIT was declared operable at that time, and Technical Specification 3.0.3 was exited. The cause of this event was personnel error in that the 2B2 SIT was incorrectly returned to service for Mode 4 operation prior to performing the required testing. Contributing to this error was the fact that each deferred PMT and its associated mode hold was not individually identified in Equipment Out Of Service (EOOS) log.
3891997004 | St. Lucie 2 | 06/11/1997 | 07/11/1997 | 9707150008 | <strong>Incorrect Original Cable Tray Fire Stop Assembly Installation Outside Appendix R Design Bases</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1997, St. Lucie Unit 2 was in Mode 1 at 100 percent power. Inspection results indicated that generically, two sided cable tray fire stop assemblies lacked the installation of ceramic fiber between cables within the fire barrier. FPL determined that the as-built configuration of two sided cable tray fire stop assemblies did not meet the tested configuration for a three hour fire rated assembly. All the St. Lucie Unit 2 two sided cable tray fire stop assemblies were declared inoperable. The apparent cause of this event was due to personnel error during the implementation of design drawings or insufficient design guidance during initial installation. Corrective actions include the posting of hourly fire watch patrols that were established to compensate for the inoperable fire stop assemblies. Repairs or plant modifications will be implemented to restore the affected fire stop assemblies to their required three hour fire rating.
3891997005 | St. Lucie 2 | 06/25/1997 | 07/25/1997 | 9707300101 | <strong>Past Inoperability of FI-3306 Resulted in Operation of Facility in a Manner Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1997, Unit 2 was in Mode 1 at 100 percent power. The St. Lucie Quality Assurance organization was reviewing Nuclear Plant Work Orders, and discovered that the Hot Shutdown Control Panel Shutdown Cooling Flow Indicator, FI-3306, was inoperable from March 9, 1997 through May 9, 1997. At the time this event was discovered, the instrument was operable. Maintenance was performed on FI-3306 on March 9, 1997 to repair a problem with the fluorescent display. The instrument was incorrectly calibrated and returned to service. This condition was not diagnosed until May 9, 1997. The apparent cause of this event was due to weaknesses in the work order and procedure used to repair FI-3306. This event is considered reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) because the Shutdown Cooling Flow Indicator, FI-3306, was inoperable in excess of 30 days. This resulted in the facility being operated in a manner prohibited by Technical Specifications. Corrective actions include: reviewing this event with I & C maintenance planners and I & C shop personnel; revising the procedure used to repair Versatile Instruments Measuring 2000 Bargraph Indicator displays to provide additional calibration and post maintenance test requirements; and updating the Total Equipment Data Base to include relevant calibration information.
3891997006 | St. Lucie 2 | 06/30/1997 | 07/29/1997 | 9708050269 | <strong>Operation Prohibited by Technical Specifications due to Inadequate Surveillance Testing of Engineered Safety Features Subgroup Relays</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1997, St. Lucie Unit 2 was operating in Mode 1 at 100 percent power. An engineering review identified a deficiency in the performance of Engineered Safety Features (ESF) logic testing associated with two subgroup relays for the containment isolation system. The subgroup relays were required to be tested at a semi-annual frequency, but had instead been tested once per 18 months. This represented a failure to perform a surveillance requirement within the allowed surveillance interval and therefore a condition prohibited by the plant Technical Specifications. The subject relays function to secure the operation of the containment purge fans and to close the containment purge isolation valves during actuation of a containment isolation signal. Since these containment purge components are required to be maintained in their post-accident configuration during reactor operation, the missed testing was not safety significant. The subgroup relays were recently tested satisfactorily and are currently within the allowable surveillance interval. The failure to test the ESFAS subgroup relays at the required surveillance interval was caused by an inadequacy in implementing the TS requirements in the plant surveillance procedures. Corrective Actions include: 1) Plant surveillance procedures will be revised to include the appropriate requirements for surveillance testing of the subgroup relays. 2) Surveillance testing is to be performed i accordance with revised procedural instructions and within the allowable surveillance interval. 3) Logic circuit test procedures are continuing to be reviewed at St. Lucie Unit 1 for proper TS implementation.
3891997007 | St. Lucie 2 | 10/08/1997 | 11/07/1997 | 9711120154 | <strong>Inoperable Containment Cooling Fan Results in Operation of Facility Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1997, Unit 2 was in Mode 1 at 100 percent power. Utility licensed operators questioned the 31 day surveillance method used to test the containment cooler fans and satisfy Technical Specification 4.6.2.1.1.a.1 requirements. Each fan cooler is equipped with a two-speed motor (with separate windings) to satisfy both the normal (fast speed) and post-accident (slow speed) functions. The apparent cause for the inadequate surveillance was non-cognitive personnel error that occurred at the time of plant licensing when the inadequate surveillance procedure was developed. FPL started and operated the containment cooling fans in fast speed during the surveillance, which does not demonstrate that the fan coolers can perform their post-accident function. On October 6, 1997, FPL discovered an additional issue with the containment cooling system when the fans were started and run in slow speed. Containment cooler fan 2-HVS-1D generated a low flow alarm during slow speed testing. The fan cooler was declared out of service and Unit 2 entered ACTION statement 1.b of Technical Specification 3.6.2.1. On October 8, 1997, FPL determined that the 2-HVS-1D containment cooling fan was rotating in reverse when run in slow speed. The apparent cause for the reverse rotation of containment cooling fan 2-HVS-1D was human error that occurred during the execution of post maintenance testing performed on May 16, 1997. Corrective actions include: correcting the slow speed rotation of containment cooler fan 2-HVS-1D; revising the 31 day containment cooler fan surveillance procedure to ensure the fans are tested in slow speed; investigating whether similar problems may exist with other surveillance procedures; training on the event; and the enhancement of several Maintenance procedures.
3891997008 | St. Lucie 2 | 11/07/1997 | 12/05/1997 | 9712110174 | <strong>Inadequate Control Room Ventilation Surveillance Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1997, St. Lucie Unit 2 was in Mode 1 at 100 percent reactor power. Utility personnel identified a concern with an 18 month control room Technical Specification surveillance procedure while reviewing HVAC surveillance procedures to ensure that the intent of the Technical Specification surveillance requirements were being met. The surveillance procedure did not adequately test control room pressurization on an individual train basis. Operations declared both trains of the Control Room Emergency Cleanup System out of service and entered the 24 hour Technical Specification 3.7.7 ACTION statement. Both trains of the Control Room Emergency Cleanup System were satisfactorily tested to the new test procedure on November 8, 1997, and the ACTION statement was exited. The cause for the Unit 2 Control Room Emergency Cleanup System surveillance procedure deficiency was non-cognitive personnel error that occurred at the time of plant licensing during the development of the surveillance procedure. Corrective actions included 1) revising the surveillance procedure to provide for train specific testing, and 2) Other HVAC system Technical Specification surveillance procedures were reviewed for adequacy, with no additional issues identified.
3901997001 | Watts Bar 1 | 01/13/1997 | 02/10/1997 | ML07324132 | <strong>NONCOMPLIANCE WITH TECHNICAL SPECIFICATION SURVEILLANCE REQUIREMENT 3.3.2.11</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 13, 1997, with Unit 1 operating in Mode 1 at 100 percent rated thermal power (RTP), it was determined that a misinterpretation of Technical Specification (TS) Surveillance Requirement (SR) 3.3.2.11 had occurred resulting in the SR not being performed for two of the five P-4 interlock functions. The P-4 interlock as described in the TS basis performs the following five functions: 1) turbine trip, 2) isolate main feedwater coincident with low Tavg, 3) prevent re-actuation of safety injection (SI) after manual reset, 4) transfer the steam dump controller from load rejection to unit trip controller, and 5) prevent opening of the main feedwater valves if closed due to Si, high-high steam generator water level, or high main steam valve vault water level. Since the P-4 interlock is described in TS table 3.3.2-1 and in the basis as an Engineered Safety Feature Actuation System (ESFAS) interlock, this was interpreted to mean that the only functions requiring SR verification were the functions that established the ESFAS interlock. Two of the above functions (items 1 and 4) are not ESFAS actuations and were considered not to require the SR verification. However, based on re- examination of this interpretation, it was determined that SR verification of these functions was required. Corrective action required revisions of SIs 1-SI-99-4-A, -4-B, -10-A, and -10-B to incorporate the SR verifications for the two functions, revisions of 1-SI-85-1, 1-SI-85-4, 1-SI-99-201-A and 1-SI-99-201-B to be made prior to refueling outage performances, and feedback provided to the individuals involved in initial interpretation of the SR.
3901997002 | Watts Bar 1 | 01/22/1997 | 02/20/1997 | ML07324132 | <strong>REACTOR/TURBINE TRIP DUE TO LOSS OF TWO MAIN FEEDWATER PUMPS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 22, 1997, at 1350 EST, while the plant was operating in Mode 1 at 100 percent reactor thermal power in steady state producing 1208 MWe, both turbine driven main feedwater pumps (TDMFPs) tripped on low turbine condenser vacuum. With both TDMFPs inoperable, the main turbine and reactor tripped at 1351. The Auxiliary Feedwater System automatically responded as designed to control steam generator levels and the plant was then stabilized in Mode 3. The TDMFP trip conditions on low turbine condenser vacuum were met after one of two TDMFP condenser drain tank pumps had been turned off at the local junction box with both TDMFPs running causing increasing fluid level in combination with a pre-existing failure of the TDMFP condenser drain tank level switch. The B pump handswitch had apparently been inadvertently bumped by a painter to the 'off' position while working on the local junction box. Corrective actions consist of replacement of the failed level switch float assembly, review and replacement of similar float switch assemblies as necessary, installing protective covers over the turbine condenser drain tank pump local handswitches to prevent accidental operation, and conducting stand down meetings with applicable workers on configuration control expectations.
3901997003 | Watts Bar 1 | 02/01/1997 | 03/03/1997 | ML07325024 | <strong>Performance of a Surveillance Instruction was not current following the return to the applicable mode.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 050%. Surveillance Instruction (SI) 1-SI-0-21 is required to be performed once every 7 days or during power ascension in accordance with General Operations (GO) 4, prior to exceeding 50 percent power. The performance of 1-SI-0-21 scheduled for January 29, 1997, was canceled due the plant being in a mode where the SI was not applicable. A conditional performance of 1-SI-0-21 was not rescheduled at this point, since it was anticipated that it would be implemented prior to reaching 50 percent power in accordance with GO-4. However, on February 1 Operations personnel waived the performance of 1-SI-0-21 after verifying that the SI was within frequency from a conditional performance on January 25. The failure to ensure a conditional performance of 1-SI-0-21 was scheduled and performed allowed the 7 day frequency to be exceeded. The cause of this event was the failure to follow procedures by the individuals involved in preparation and approval of the cancellation of the scheduled performance of 1-SI-0-21 on January 29. The immediate action taken was to verify that 1-SI-0-21 was in frequency. The actions to prevent recurrence include; counseling of the individuals directly involved in this event, revision of Site Standard Practice 8.02 to more clearly define the responsibilities of the individuals preparing and approving schedule extensions for performance of SIs, revision of GO-4 to require a conditional performance of 1-SI-0-21 prior to exceeding 50 percent power, and a review of conditional SIs and Technical Requirement Instructions that are also periodically scheduled to determine if similar performance or scheduling problems exist.
3901997004 | Watts Bar 1 | 01/18/1997 | 06/09/1997 | ML07325027 | <strong>AUXILIARY BUILDING GAS TREATMENT SYSTEM (ABGTS) INOPERABLE</strong><br /><i>Abstract:&nbsp;</i>On February 14, 1997, TVA discovered that the Auxiliary Building Gas Treatment System (ABGTS) Train-B air heater had not been operational since January 18, 1997. The air heater, located in the first stage of the air cleaning filter assembly, had not been working due to a loose terminal connection at the thermal overloads for the associated magnetic starter. The problem had not been properly diagnosed during 10 hour surveillance test runs. The amount of time the heater was inoperable exceeded the Watts Bar Nuclear Plant Technical Specifications Limiting Condition for Operation (LCO) LCO 3.7.12, action statement A, for one train of ABGTS out-of-service for more than 7 days. Further review determined that ABGTS Train-A had been removed from service for approximately 36 hours to perform surveillance testing and to repair a filter assembly stud during the period that Train-B had been inoperable. Train-A was removed from service at 0830 EST on February 7, 1997. While ABGTS Train-A was inoperable, the Operations crew was unaware that the ABGTS Train-B air heater problem existed. Thus, both ABGTS trains were inoperable until Train-A was restored. The cause of this event has been attributed to a lack of questioning attitude by Operations personnel during Train-B 10 hour surveillance test runs. Corrective actions consist of determining the cause of the hardware failure, correcting hardware problems, improving the test acceptance criteria in the applicable surveillance procedures, development of additional training, and counseling and retraining applicable personnel concerning management expectations for similar situations.
3901997005 | Watts Bar 1 | 02/26/1997 | 03/24/1997 | ML07325025 | <strong>NONCOMPLIANCE WITH TECHNICAL SPECIFICATION SURVEILLANCE REQUIREMENT 3.3.3.3.-26</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 26, 1997, with Unit 1 operating in Mode 1 at 100 percent rated thermal power (RTP), it was determined that the calibration method for Auxiliary Building passive sump level transmitter 0-LT-77-134 contained an error in the input pressure that resulted in the transmitter output indicating 12.5 inches lower than actual level. It was subsequently determined that this calibration method existed in surveillance instructions for both Auxiliary Building sump level channels. The two functions of these channels are to provide indication to monitor for a breach of the spent fuel pit and to monitor for a breach in the Auxiliary Building of a system containing primary coolant. With this condition, both channels were deemed not in compliance with Surveillance Requirement (SR) 3.3.3.3.26, and therefore the operators entered Limiting Condition of Operation (LCO) 3.3.3, 'Post Accident Monitoring (PAM) Instrumentation,' until both channels were returned to service. Corrective actions required calibration of level transmitter loops 0-LPL-77-134 and 0-LPL-77-135 in accordance with revised Surveillance Instructions (SIs) 0-SI-77-1 and -2 which provided corrected calibration data. The extent of condition has been determined to be limited to these two transmitter channels.
3901997006 | Watts Bar 1 | 03/06/1997 | 04/07/1997 | ML07325025 | <strong>REACTOR/TURBINE TRIP DUE TO LOW-LOW STEAM GENERATOR LEVEL</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 6, 1997, at approximately 0517 EST, while Unit 1 was operating at 100 percent RTP, the reactor automatically tripped due to low-low water level in steam generator No. 4. Three conditions led to the low-low level; (1) the main feed pump B (MFP B) shaft fractured and broke in half at approximately 0513, (2) the standby main feed pump was temporarily out-of-service for recirculation line repairs, and (3) flow was partially restricted to steam generator No. 4 at the inlet nozzle. When the shaft broke, the resulting damage caused the pump turbine to trip resulting in an automatic balance of plant runback to 85 percent. Operators further reduced the load to approximately 54 percent, as directed by procedure, to arrest decreasing steam generator water level, since the SBMFP was unavailable. However, steam generator No. 4 was experiencing high inlet pressure due to foreign material obstruction at the feedwater inlet. It decreased to the low-low level trip setpoint at 0517 causing an automatic reactor/turbine trip and subsequent Auxiliary Feedwater System (AFW) actuation at 0518. Operators responding to the trip monitored and observed steam generator No. 4 level off with feed flow approaching steam flow and believed the transient was beginning to reverse, therefore did not initiate a manual reactor trip prior to the automatic trip. AFW responded as designed to control steam generator water levels. The plant was then stabilized in Mode 3. Corrective actions consist of inspecting and repairing hardware, restoring equipment to service, evaluating component failures and material applications, and improving personnel awareness.
3901997007 | Watts Bar 1 | 03/06/1997 | 04/07/1997 | ML07325025 | <strong>NONCOMPLIANCE WITH TECHNICAL SPECIFICATION SURVEILLANCE REQUIREMENTS 3.3.1.15 AND 3.3.2.10</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 6, 1997, with Unit 1 in Mode 3, it was determined that the response time test requirements of Technical Specification (TS) Surveillance Requirements 3.3.1.15 and 3.3.2.10 had not been met during the post maintenance testing for pressure transmitter 1-PT-68-340. During review of a proposed Technical Specification change, an instrument maintenance engineer requested the response times obtained during the February 9, 1997, replacement of 1-PT-68-340. It was discovered that the above surveillance requirements had not been included as part of the post maintenance testing. Pressure transmitter 1-PT-68-340 is one of four channels which provide trip functions for high and low pressurizer pressure. In addition, it is one of three channels which provide protection against the inadvertent opening of a steam generator relief or safety valve, small line break, inadvertent opening of a pressurizer relief or safety valve, loss of coolant accident, and steam generator rupture. Once discovered, action was initiated to perform these surveillance requirements. The cause of this condition was determined to be inadequate work package preparation which resulted in failure to perform the required response time test. Corrective actions included a revision to a site procedure to include guidance for response time testing of transmitters and additional training for personnel involved in the planning of transmitter replacement work orders.
3901997008 | Watts Bar 1 | 03/06/1997 | 04/07/1997 | ML07325025 | <strong>Safety Injection Actuations Following a Reactor Trip.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During cooldown following a reactor trip, steam line pressure was reduced to <675 psig initiating a safety injection (SI) signal at 17:43 EST on March 6. Following recovery from this event, cooldown continued and SI blocks were instated in accordance with plant procedures. However, at 20:22 EST an SI was initiated by an invalid signal from the Solid State Protection System (SSPS). A third SI initiation occurred at 04:20 EST on March 7 due to another invalid signal. The cause of the first SI was attributed to a failure by Operations to self-check during the cooldown process. The corrective measures for the first SI include action by management to assess the event and the actions of the shift crew. Based on this, management reemphasized expectations to the shift crew regarding crew performance. Other planned actions include the resequencing of operating procedures to insure SI blocks are established at proper points and the training of Operations personnel on this event. The cause of the invalid SI actuations was attributed to one P-11 channel being out-of-service and another P-11 Eagle 21 EPT board channel degrading causing a momentary reset of the P-11 permissive signal in the SSPS allowing the initiation of an SI. The corrective measures for the invalid SIs include the evaluation of the failed EPT board by Westinghouse and the testing of each of the Eagle-21 output voltage inputs to the SSPS. Upon review of the Westinghouse evaluation and information pertaining to similar events from within the industry, additional corrective measures may be required. This report will be supplemented if generic industry concerns are identified.
3901997009 | Watts Bar 1 | 04/10/1997 | 05/12/1997 | ML07325026 | <strong>Main Control Room Heating, Ventilation and Air Conditioning (HVAC) Inoperable</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At 0615 EDT on April 8, 1997, Operations personnel initiated action to switch from the Train A MCR HVAC to the Train B HVAC. During the transfer between the units, the Train B unit failed to start due to low suction pressure and LCO 3.7.11 was entered for one train of CREATCS being inoperable. Investigation of the Train B chiller found a small hole in a capillary tube and a problem with a reed switch on an expansion valve. On April 10, 1997, at 1309 EDT, Operations personnel initiated action to switch from the Train A MCR HVAC to the Train B HVAC for post maintenance testing of the Train B unit. For this manipulation, the guidelines contained in Sections 5.5 and 7.1 of SOI-31.01 were followed in error. This resulted in the handswitch which controls the Train A HVAC being placed in pull-to-lock while the Train B HVAC handswitch was also in the pull-to-lock position. Due to both trains of CREATCS being inoperable, Action E of LCO 3.7.11 was entered which required entry into LCO 3.0.3 for 3 minutes until the Train A HVAC was returned to service. The cause of this event was a failure of the Operations personnel to self-check to ensure the correct section of SOI-31.01 was used for the transfer of the HVAC units. The corrective actions for this event include: 1) Disciplinary action was taken against the Operations personnel involved in placing both trains in pull-to-lock; 2) SOI-31.01 has been updated and reorganized to prevent manipulations which may cause entry into LCO 3.0.3; 3) The cause and corrective action for this event will be addressed in an Operations Training newsletter.
3901997010 | Watts Bar 1 | 04/20/1997 | 05/20/1997 | ML07325026 | <strong>Reactor Trip due to Operation of a Generator Protective Relay</strong><br /><i>Abstract:&nbsp;</i>At 0125 EDT on April 20, 1997, the WBN Unit 1 main generator pneumatic circuit breaker (PCB) opened initiating a turbine trip and a subsequent automatic reactor trip. Investigations found that the turbine trip was initiated by operation of the generator backup relay, relay 121GB. Operation of this relay results in the opening of the main generator PCB and closure of the steam supply to the turbine. Meggar testing was performed to establish a possible cause for the operation of the protective relay. For the A phase main transformer high side potential device (PD) circuit, a low meggar reading was found. Additional troubleshooting found evidence that the phase A capacitance tap connector from the 500KV bushing to the PD had experienced arcing. Moisture was also found in the bushing well and the lubricant around the bushing well was blackened indicating a fault on the A phase capacitance tap connector. Once this problem was found, the capacitance tap bushing area was cleaned and new lubricant was applied. In addition, the exposed surfaces of the connector were sealed with an RTV sealant. Resistance tests were subsequently performed with the readings found to be normal. Due to the problems found on the A phase, the B and C phase capacitance tap connectors were inspected even though the PD circuits meggar tested satisfactorily. No problems were found on the B phase. C phase was found to have lost a portion of its lubricant, and the remaining lubricant was blackened but no significant burn odor was noted. The same type of repairs performed on the A phase were made to both the B and the C phases.
3901997011 | Watts Bar 1 | 04/28/1997 | 12/19/1997 | ML07325030 | <strong>INCOMPLETE SURVEILLANCE INSTRUCTION</strong><br /><i>Abstract:&nbsp;</i>The purpose of this LER is to report findings in accordance with 10 CFR 50.73 associated with Generic Letter (GL) 96-01, "Testing of Safety Related Logic Circuits" reviews. GL 96-01 requires each licensee to compare electrical schematic drawings and logic diagrams for the Reactor Protection System, Emergency Diesel Generator load shedding and sequencing, and actuation logic for the Engineered Safety Feature Actuation System (ESFAS) against plant surveillance test procedures to ensure that all portions of the logic circuitry including the parallel logic, interlocks, bypasses and inhibit circuits are adequately covered in the surveillance procedures to fulfill the Watts Bar Technical Specification requirements. The first surveillance deficiencies identified involved unverified parallel circuit paths and were discovered on April 28, 1997. Some additional findings have been discovered since April 28 and have been included in the report. The cause of the surveillance instruction deficiencies have been attributed to inadequate technical reviews. Corrective actions consist of completing the reviews, addressing verification of any unverified logic circuits, informing technical reviewers of the requirements of GL 96-01, and correcting any hardware deficiencies found.
3901997012 | Watts Bar 1 | 05/24/1997 | 06/24/1997 | ML07325027 | <strong>Missed surveillance due to procedural errors</strong><br /><i>Abstract:&nbsp;</i>During a review of 1-SI-0-4, "Monthly Surveillances," on May 24, 1997, a licensed operator noted that two items on Appendix C did not have the correct modes identified for which the step must be performed. A subsequent review of the past performances of 1-SI-0-4 found that one of the items, SR 3.3.3.1, had been appropriately implemented. The other item on Appendix C fulfills SR 3.3.4.1 for Item 1.a of Technical Specification Table 3.3.4-1. Implementation of SR 3.3.4.1 for Item 1.a performs a channel check of the source range neutron monitors to assure remote shutdown capabilities. The mode problem identified during the review was that the applicable modes listed in 1-SI-0-4 for both SRs were Modes 2 and 3. The modes applicable to the SRs are 1, 2, and 3. The review of past performances of 1-SI-0-4 found that SR 3.3.4.1 had been implemented only 9 of the 18 required times. The cause for the error in 1-SI-0-4 is attributed to a failure by the writer of the initial document, Revision 0, to ensure that the correct modes were captured in the procedure. Further contributing to the problem was a failure by the reviewer of Revision 0 of the procedure to identify the error. The corrective actions for this event are: 1) the revision of 1-SI-0-4 to correct the identified mode problems, 2) the performance of a detailed review of 1-SI-0-4 to ensure the applicable Technical Specifications are properly translated, 3) issuance of an Operations Night Order explaining the cause for the modes being incorrect in 1-SI-0-4, and 4) counseling of the reviewer of Revision 0 of the procedure.
3901997013 | Watts Bar 1 | 08/08/1997 | 09/08/1997 | ML07325028 | <strong>Missed surveillance During performance of maintenance activities</strong><br /><i>Abstract:&nbsp;</i>Calculations EPM-AMP-081789 and EPM-CES-082989 established revised values for the outside ambient air temperatures for which an emergency diesel generator (EDG) is functional when the ventilation fans are out-of-service. These revisions resulted in a reduction in the temperatures from the values previously used in the System Operating Instructions (SOIs) for the EDGs. Based on the revisions, Engineering performed a review to establish if there had been any instances since initial fuel load where the fans were taken out-of-service during a period where the outside ambient temperature was higher than the values currently established in the calculations. From this review, the three prior instances were identified. For these situations, the affected EDG should have been considered inoperable and Action B of LCO 3.8.1 invoked to verify the availability of the offsite power supplies. The cause of this event was the usage of temperatures listed in a design memorandum for which there was no corresponding design output document. Operations personnel responded to this event by revising the affected SOIs to reflect the revised temperatures. A test plan is being developed which will remove various combinations of the EDG fans from service during an upcoming 24 hour endurance run of the EDGs. This will allow for collection of temperature values which better represent actual operating conditions to be defined. Design and procedural changes will be initiated as required. In order to ensure that other cases do not exist where documents such as a memorandum were used for design values, a sample of Operation's procedures will be reviewed.
3901997014 | Watts Bar 1 | 10/09/1997 | 11/10/1997 | ML07325029 | <strong>APPENDIX R CONDITIONS</strong><br /><i>Abstract:&nbsp;</i>The purpose of this LER is to report two conditions in accordance with 10 CFR 50.73 (a)(2)(ii) which were determined not to meet 10 CFR 50, Appendix R requirements. The first condition involves a missing reactor coolant pump (RCP) number 2 oil cooler cover which is part of the RCP oil collection system which helps contain RCP motor oil should a leak occur. This RCP oil collection system is required by Section III.O of Appendix R. Neither the cause of the missing cover nor when it was removed could be determined. Corrective actions include the replacement of the cover and a procedure revision to confirm cover installation prior to containment closure following an outage. Without this cover, the RCP oil collection system would have been effective for some postulated leak locations. The second condition being reported involves two cables for the main control room air handling units found to have been routed such that one single fire could disable both air handling units thus preventing them from performing their fire safe shutdown function. The root cause was determined to be technical inaccuracies in the design input (Appendix R analysis) resulting from personnel error. Corrective actions include the installation of a manual control station at the 480V Control & Auxiliary Vent Boards for isolation purposes during an Appendix R fire and a revision to plant procedure AOI-30.2 to implement change of manual actions due to the addition of a manual control station.
3901997015 | Watts Bar 1 | 10/19/1997 | 11/18/1997 | ML07325029 | <strong>MANUAL REACTOR TRIP TO FEEDWATER ISOLATION</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1997 at 0950 EDT during Unit 1 startup, the reactor was in Mode 1, approximately 12% power. The turbine was at 1800 RPM and preparing for connection to the grid. Steam generator levels began decreasing due to isolation of the inservice feedwater heaters. Auxiliary feedwater was manually initiated and reactor power was manually decreased to 4% using control rods. The reactor was manually tripped due to decreasing steam generator levels, The feedwater heaters isolated on high-high level. The main control room alarms for high feedwater heater levels did not alarm. All other systems responded to the initiating event as expected and within analyzed parameters. There were no abnormal radiological conditions throughout the event. The cause of the event was isolation of the high pressure feedwater heater strings due to high level with a contributing cause of failure of the high level alarms in the heaters to provide annunciation in the control room. The high level in the A1 and B1 heaters was due to a failure to recognize that additional operator attention was required to control the level in the A1 and B1 heaters with the C1 heater isolated, during turbine roll and main generator synchronizing. The procedure was revised to caution operators on the impact of feedwater heaters out of service during this period. The high-high alarm level switches on the feedwater heaters were repaired and verified to be operable.
3901997016 | Watts Bar 1 | 12/05/1997 | 12/24/1997 | ML07325030 | <strong>DIESEL GENERATOR FUEL OIL TRANSFER HANDSWITCHES</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1997, with Unit 1 operating at 100 percent reactor power, two Emergency Diesel Generator (EDG) 2B-B fuel oil transfer handswitches were found in the "OFF" position rather than the required "AUTO" position. As a result, this condition would have prevented fuel oil transfer pumps from starting and pumping fuel to the tank used to supply fuel to EDG 2B-B. This condition resulted in the EDG 2B-B being technically inoperable. It is important to emphasize that this condition would not have prevented EDG 2B-B from performing its function had a signal to start been received. The control room would have received an alarm due to low level in the fuel oil tank. Ample time exists to dispatch personnel to the Diesel Generator Building to correct the problem. The specific cause of this condition could not be determined. However, it was concluded from the investigation that the most likely cause was an unintentional mispositioning during other work activities. As a result, EDG 2B-B was technically inoperable for a unknown period of time (although not likely, it is possible it was as long as from November 25, 1997 through December 5, 1997). This amount of time would exceed the Technical Specification limitation of 72 hours. Therefore, this condition is conservatively being reported under 10CFR50.73(a)(2)(i)(B) as a condition which is potentially in violation of the Technical Specification. Corrective actions consist of specific training for operations personnel, standdown meetings for site employees, and additional management monitoring and oversight of operational activities.
3951997001 | Summer 1 | 04/22/1997 | 05/20/1997 | 9705280367 | <strong>Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1997, plant personnel conservatively initiated a manual reactor trip in response to a leak on the Main Turbine Electro-Hydraulic Control (EHC) system. It was subsequently determined that an ""O"' ring on the shutdown servo t Combined Intercept Valve (CIV) #1 had failed. Although Feedwater Isolation was achieved, one Feedwater Regulating Valve (FRV) was slow to completely close in response to a Feedwater Isolation Signal. All other systems functioned per design. Repairs were accomplished and the plant restarted.
3951997002 | Summer 1 | 04/26/1997 | 05/27/1997 | 9706030032 | <strong>Automatic Reactor Trip; Turbine Feedwater Isolation</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1997, at 2043 hours, a main turbine trip from 42% power occurred due to a Hi-Hi Lv1 in "C" steam generator (P-14) signal. This signal also generated a feedwater isolation, causing all main feedwater (FW) pumps to trip, and sent a signal for the feedwater isolation valves (FWIVs), feedwater regulation valves (FRVs), and feedwater regulation bypass valves (FRBVs) to close. Although emergency feedwater pumps auto started upon loss of all main FW pumps, this flow could only meet the steam demand for about 4% power. At 2047 hours, an automatic reactor trip from approximately 6% reactor power occurred due to Lo-Lo Lv1 in "A" steam generator (S/G) during the power reduction. All systems functioned per design in response to this trip. After verification of system integrity and and proper plant response, plant restart was initiated.
3951997003 | Summer 1 | 08/17/1997 | 09/16/1997 | 9709230087 | <strong>Entry into TS 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>During a review of an instrument calibration procedure at VCSNS it was discovered that time constants in the Overtemperature [symbol omitted]T (OTDT) and Overpower [symbol omitted]T (OPDT) reactor trip setpoint channels were nonconservative relative to the Technical Specification values. On August 17, 1997, at 1400 hours, the plant entered TS 3.0.3 and commenced plant shutdown. Power was reduced while calibration was conducted to return the time constant settings to within Technical Specification values. At 1445 hours, after two channels of OTDT were calibrated, the licensee exited TS 3.0.3. The plant was restored to 100% power.
3951997004 | Summer 1 | 10/12/1997 | 11/11/1997 | 9804100101 | <strong>Technical Specification Noncompliance and Piping Analysis Exceeds Code Allowables Due to Snubber Failures</strong><br /><i>Abstract:&nbsp;</i>On October 12 and 15, 1997, plant personnel found two (2) snubbers which were in the locked position. These components are mechanical shock arrestors attached to the Reactor Coolant pressurizer spray line and Nuclear Blowdown piping respectively. The inoperable snubbers were found and replaced during refueling outage (RF) surveillance testing, performed in accordance with Technical Specification (TS) 3/4.7.7, Snubbers. Preliminary engineering analysis of potential impacts to the associated piping concluded that the stress on the piping had exceeded ASME Code allowable limits and was therefore, outside the design basis. System walkdowns did not find any transient induced damage and ultrasonic inspection of welds on the pressurizer spray line failed to find any indications of stress/service induced flaws. Due to the incompatibility of the Nuclear Blowdown line with standard NDE techniques the line was replaced to return the pipe to its design basis condition. Westinghouse completed an ASME code fatigue qualification on the pressurizer spray line on March 17, 1998 with the conclusion that the calculated usage factors for 40 years remains less than 1 and no restrictions to plant transients are required. Both of these systems are considered to be operable at this time. Exceeding the design basis for these piping systems is reportable per the requirements of 10 CFR 50.73(a)(2)(ii)(B). On October 18, engineering review of three (3) snubber failures on a feedwater line determined that a transient on December 5, 1994 had caused the snubber damage. System walkdowns during this outage (RF 10) and at the time of the transient failed to find any apparent damage; however, due to personnel oversight, freedom of motion tests of suspect snubbers were not verified during RF 9 (spring of 1996) per the requirements of TS Surveillance 4.7.7.c. This TS noncompliance is being reported per the requirements of 10 CFR 50.73(a)(2)(i)(B). Station Administrative Procedure 1122 will be revised by April 1, 1998 to ensure that engineering initiates component evaluations required by TS 4.7.7.
3951997005 | Summer 1 | 10/24/1997 | 11/23/1997 | 9712020089 | <strong>Missed Surveillance on C Charging/HHSI Pump Required by ASME Code Section XI</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1997, ASME Section XI Code full flow testing on the C Charging/Safety Injection Pump determined that the vibration level on the pump outboard horizontal test point exceeded the Code alert limit of 0.325 inches per second (ips). The measured value was 0.357 ips. The Code requirement for this alert range is that the frequency of the testing be doubled or that relief be obtained from this requirement. During a review of past vibration levels it was discovered that his Pump had exceeded the Code alert limit on one previous occasion, during full flow testing in Refueling 8 (Fall 1994). The increased frequency testing as specified for this range in the pump had remained operable throughout the past two operating cycles. As a result, Virgil C. Summer Nuclear Station (VCSNS) was in noncompliance with Technical Specification 4.0.5. In 1994 VCSNS committed to the 1989 edition of the ASME Code which referenced the ASME/ANSI OM-1987, Operations and Maintenance of Nuclear Power Plants, addenda OMa - 1988. The conversion to OMa and the referenced NUREG 1482 introduced some confusion in which requirements had precedence over acceptance criteria. The apparent cause of this failure to perform the required surveillance was due to confusion on whether the Code alert limit of 0.325 inches per second (ips) or 2.5 times the reference value (Vr) was the absolute limit. At the time it was believed that either could be the limit as long as there was sound engineering judgment for the decision. The data sheet used in the field for this test did not have any reference values documented; as such, the test personnel were unsure of the status of the test. A relief request is being generated to permit VCSNS to not perform the increased frequency full flow surveillance test during the current cycle, as the necessary conditions for the test include a refueling mode with the reactor vessel closure head removed. Also the test procedure has been revised to state the acceptance criteria for the vibration measurements is 2.5 times the whichever is smaller.
3951997006 | Summer 1 | 11/13/1997 | 12/12/1997 | 9712230343 | <strong>Technical Specification Breaker Alignment Surveillance Not Performed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1997, plant personnel failed to verify the operability of the A.C. offsite sources at the Virgil C. Summer Nuclear Station within the eight (8) hour interval as required by Technical Specification (TS) 3.8.1.1.b, Action Item b.1. The electrical alignment verification was being performed at an increased frequency because of an inoperable Emergency Diesel Generator (EDG). At the time of the occurrence, plant personnel were involved in testing the inoperable EDG to determine the adequacy of repairs. The distraction of these equipment operability checks was a contributing factor in the personnel oversight that resulted in the performance of this surveillance 45 minutes after it was due. Following identification that the surveillance had not been performed by its due time of 1215 hours, an operator was dispatched to perform the surveillance. The surveillance was completed at 1300 hours with no electrical alignment errors found. Additionally, Operations personnel confirmed that there had been no plant alarms or realignments of breakers associated with the plant electrical busses and verified with the Dispatcher that there had been no switchyard breaker realignments since the last performance of the surveillance. Improvements will be made in the tracking program for Operations non-routine (daily or shift) surveillances initiated by TS Action Statements by March 31, 1998.
3971997001 | Columbia | 02/11/1997 | 03/13/1997 | 9703210322 | <strong>REACTOR WATER CLEANUP SYSTEM BLOWDOWN FLOW ISOLATION SETPOINT SLIGHTLY ABOVE TECHNICAL SPECIFICATION ALLOWABLE VALUE DUE TO CALCULATION ERROR</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 094%. On February 11, 1997 at 1314 hours with the plant in Mode 1 at 94 percent reactor power, it was determined that WNP-2 did not comply with a Technical Specification action requirement for Reactor Water Cleanup (RWCU) System Isolation Actuation Instrumentation. During the revision of a Leak Detection (LD) System calculation, Design Engineering personnel determined that the RWCU high blowdown flow isolation trip signal was calculated incorrectly and set non-conservative to the Technical Specification allowable value. The calculation was being revised to provide the basis for an RWCU high blowdown flow time-delay in support of conversion to the Improved Technical Specifications. The root cause of this event was an analysis deficiency in that the setpoint calculation and subsequent flow switch settings would not have limited RWCU System blowdown flow to </=271.1 gpm. An incorrect formula was used to convert the differential pressure flow measurement term to a voltage setpoint that was then utilized to calibrate and set the flow switches. Due to the error in the setpoint calculation, the components (flow switches) had been set at 275.7 gpm. The setpoint calculation and surveillance procedures did not satisfy the Technical Specification requirement. The surveillance procedures were developed with the setpoint calculation as a basis. The setpoints were recalculated using a more appropriate design input. Following applicable procedural revisions, the flow switches were recalibrated to the new setpoint value and the system was returned to service. Further corrective action includes performing a detailed review of instrument setpoint calculations for those that include differential pressure transmitters as the flow monitoring method. This event posed no threat to the health and safety of either the public or plant personnel. The small difference between the actual and required setpoint of the flow switches did not affect the ability of the system to perform its intended safety function of mitigating a high energy line break.
3971997002 | Columbia | 02/18/1997 | 03/20/1997 | 9703250092 | <strong>ROD BLOCK MONITOR CALIBRATION VALUES NOT SET IN ACCORDANCE WITH TECHNICAL SPECIFICATIONS</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1997 at 1332 it was determined that WNP-2 had not been in compliance with Technical Specification (TS) Table 3.3.6-1 and TS 3.1.4.3 during past plant startups due to the non-conservative calibration of the Rod Block Monitor (RBM) reference downscale instrumentation setpoints. TSs require that RBM instrumentation be operable (not bypassed) at or above 30% rated thermal power. Due to calibration procedure inadequacies, an incorrect RBM reference downscale setpoint resulted in RBM instrumentation not being operable until almost 33% rated thermal power. At time of discovery the RBM instrumentation was determined to be operable because rated thermal power at 91% was significantly greater than the incorrectly calibrated reference downscale setpoint. Immediate corrective action was to revise and re-perform RBM channel calibration procedures to ensure the RBM reference downscale instrumentation setpoint resulted in RBM instrumentation being operable at or above 30% rated thermal power. This issue is being reported in accordance with 10CFR50.73(a)(2)(i)(B) due to operating during past plant startups in a condition prohibited by plant TSs. The root cause of this event is "Misapplication or Interpretation of Design Inputs," due to the apparent use of a vendor reference document calibration procedure as a basis for the WNP-2 RBM reference downscale calibration procedure. This event was identified based on a review of RBM channel calibration procedures that was prompted by a review of INPO Network Operating Experience Entry OE 8215, "Rod Block Monitor Low Power Bypass Setpoint Non-conservative at Hope Creek."
3971997003 | Columbia | 03/20/1997 | 04/21/1997 | 9704290081 | <strong>NOTIFICATION OF NONCOMPLIANCE WITH TECHNICAL SPECIFICATIONS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. At 1645 on March 20, 1997, with the plant operating at 100% power, NRC staff notified the Supply System that WNP-2 Technical Specifications (TS) Surveillance Requirements (SRs) for Response Time Testing (RTT) were not being met for specified instrumentation in the Reactor Protection System, Primary Containment Isolation System, and Emergency Core Cooling System. WNP-2 declared the specified equipment inoperable and entered the applicable Technical Specification Action Statements (TSAS). This action required subsequent entry into LCO 3.0.3 necessitating initiation of a plant shutdown within 1 hour and placing the reactor mode switch in the startup position within 7 hours. At 1740 WNP-2 declared an unusual event based on entry into LCO 3.0.3 and initiated a power reduction required by the TS. WNP-2 then requested enforcement discretion for a one-time exemption from the applicable Technical Specification SRs until April 18, 1997 or until the issuance of a license amendment changing the Technical Specifications. At 2136 WNP-2 received verbal notification of enforcement discretion. The TSAS and LCO 3.0.3 were exited at this time. The unusual event was terminated at 2200 based on exit from LCO 3.0.3. The elapsed time the equipment was declared inoperable was 4 hrs 50 min. The March 20 letter indicated the failure to meet the SRs was caused by an inconsistency between WNP-2's method of implementing Licensing Topical Report NEDO-32291 'System Analyses for Elimination of Response Time Testing Requirements' and WNP-2 Technical Specification SRs and RTT definitions. The Supply System's failure to clarify the staff s expectations before proceeding with implementation was also a cause.
3971997004 | Columbia | 03/27/1997 | 09/24/1997 | 9710010084 | <strong>TECHNICAL SPECIFICATION REQUIRED MANUAL SCRAM DUE TO ENTRY INTO REGION A OF THE POWER-TO-FLOW MAP</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1997 at 0907 hours with the plant in Mode 1 at 46 percent power, plant operators manually scrammed the reactor as required by the Technical Specifications due to indication of entry into Region A of the power-to-flow map during Reactor Recirculation (RRC) and Reactor Feedwater (RFW) System testing. (It was determined by followup, engineering analyses that Region A of the power-to-flow map had not been entered.) The post-modification testing was being performed to demonstrate that the feedwater level control system and recirculation flow runback feature would avoid a scram following the trip of a single reactor feedwater pump during power operation. During the test and after the planned trip of pump RFW-P-1B, an expected reactor recirculation pump speed runback to 27 Hz was observed. Following this planned runback, a second unexpected runback to 15 Hz occurred which, based upon evaluation of plant heat balance data, appeared to have placed the reactor into Region A of the power-to-flow map. The second runback was caused by a reactor recirculation pump differential temperature cavitation interlock condition. Plant operators responded conservatively by immediately scramming the reactor and maneuvering the plant to a safe shutdown condition in accordance with procedures. The root cause of this event was inadequate attention to detail and a lack of a questioning attitude during the design phase of the modifications for the adjustable speed drive and digital feedwater level control systems. Corrective actions included the establishment of internal and external event evaluation teams to investigate the event, and successfully repeating the reactor feedwater pump trip test. There were no indications of power oscillations during the event period. This event posed no threat to the health and safety of the public or plant personnel.
3971997005 | Columbia | 03/27/1997 | 04/28/1997 | 9705060022 | <strong>VALID REACTOR SCRAM SIGNAL WHILE SHUTDOWN WITH CONTROL RODS FULLY INSERTED DUE TO REACHING LOW WATER LEVEL SETPOINT DURING PREPARATIONS FOR SAFETY RELIEF VALVE TESTING</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 27, 1997 at 1247 hours with the plant shutdown in Mode 3 (Hot Shutdown), a valid reactor scram signal was received due to a low water level condition during preparations for safety relief valve testing. The low level condition occurred following closure of a safety relief valve that had been open for pressure control. Closure of the valve resulted in a large drop in reactor pressure vessel water level. During the time the valve was open, vessel pressure decreased from 1030 psig to about 880 psig. When the valve was closed, vessel level dropped rapidly from an initial value of +61 inches to +20 inches in approximately 20 seconds. Vessel level continued to decrease to +13 inches, the Reactor Vessel Water Level - Low (Level 3) setpoint, over the next 30 seconds. Plant operators responded immediately to the low level condition and promptly restored vessel water level to within normal limits. The scram signal was reset at 1249 hours. The root cause of this event was risks and consequences of decisions not completely identified and assessed. The attempt to set up for safety relief valve testing without a contingency plan contributed significantly to the event. Further corrective action includes coaching the Operations crew involved, developing expectations for plant shutdown schedules, and providing simulator training on safety relief valve actuation at normal level and pressure with the plant shutdown. This event posed no threat to the health and safety of the public or plant personnel. The Reactor Protection System functioned as designed to cause a reactor scram signal and plant operator actions to recover level were prompt and correct. The lowest vessel level reached during the event was + 13 inches, before being recovered to the normal operating level. AR control rods were fully inserted throughout this event.
3971997006 | Columbia | 05/27/1997 | 06/26/1997 | 9707090026 | <strong>NON-PERFORMANCE OF SURVEILLANCE REQUIREMENT 3.6.1.3.2 FOR BLIND FLANGES ASSOCIATED WITH PRIMARY CONTAINMENT</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1997, with the plant in Mode 1 at approximately 57% power, a Problem Evaluation Request (PER) was initiated to assess the applicability of Technical Specification Surveillance Requirement (TSSR) 3.6.1.3.2 to five structural assemblies providing a flanged pressure boundary for the Residual Heat Removal (RHR) System. TSSR 3.6.1.3.2 requires that each primary containment isolation manual valve and blind flange located outside primary containment be verified closed every 31 days. The Bases for SR 3.6.1.3.2 specifically states that this monthly check applies to isolation devices "capable of being mispositioned". In consideration of the description in the Bases it was thought that due to the permanent nature of these assemblies and the difficulties involved in mispositioning, they were not required to be verified in place every 31 days per TSSR 3.6.1.3.2. As a corrective action for the PER, System Engineering reviewed the applicability of TSSR 3.6.1.3.2 to all blind flanges associated with primary containment. The review revealed two 2-inch conventional blind flanges which are required to be verified in place every 31 days. On May 27, 1997, with the plant in Mode 5, another PER was initiated for the two 2-inch blind flanges. After subsequent discussions with the staff concerning their interpretation of the intent of TS 3.6.1.3.2 it was later decided that the Specification applies to all seven flanges. As a corrective action, the applicable surveillance procedure was revised to add checks of all seven flanges. The root cause of this event was that the wording of the original Technical Specification led plant staff members to conclude the specification did not apply to permanently installed blind flanges. As of March 10, 1997, when Improved Technical Specifications were implemented at WNP-2, the intent of this Specification is clear. This event is reported per 10CFR50.73(a)(2)(i)(B). The safety significance of this event is minimal.
3971997007 | Columbia | 06/11/1997 | 07/23/1997 | 9707300094 | <strong>VOLUNTARY REPORT OF AUTOMATIC START OF DG-1 AND DG-2 DUE TO SM-7 AND SM-8 UNDERVOLTAGE</strong><br /><i>Abstract:&nbsp;</i>On 6/11/97, with the plant in Operating Mode 4, Circulating Water Pump motor CW-M-P/1C experienced internal electrical faulting shortly after pump startup. The pump ran for approximately 15 seconds prior to tripping the CW-M-P/1C feeder breaker due to phase differential current. The motor fault caused a momentary undervoltage condition on electrical busses SM-7 and SM-8 which initiated an automatic start of emergency diesel generators, EDG-1 and EDG-2. The diesel generators started and ran unloaded, as designed, until manually shutdown by operating personnel. The output breakers for EDG-1 and EDG-2 did not close and load the EDGs because the undervoltage condition was only momentary, and plant busses continued to be fed from the startup transformer, TR-S. Immediate corrective actions were to return EDG-1 and EDG-2 to standby readiness and initiate an investigation into the cause of CW-M-P/1C trip. The root cause of EDG-1 and EDG-2 auto start was an undervoltage condition on electrical busses SM-7 and SM-8 This event is voluntarily. The safety significance of this event is considered minimal.
3971997008 | Columbia | 07/16/1997 | 08/15/1997 | 9708250397 | <strong>INOPERABILITY OF FOUR AUTOMATIC DEPRESSURIZATION SYSTEM VALVES DUE TO CIA-PCV-2B PRESSURE SETPOINT DISCOVERED SET LESS THAN REQUIRED</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1997, with the plant operating at 90% power, the wire seal used to lock containment instrument air pressure control valve, CIA-PCV-2B, was found not intact. This valve controls backup nitrogen pressure (actuating medium) to the four subsystem B automatic depressurization system (ADS) valves. Subsequent maintenance troubleshooting activities revealed the setpoint for CIA-PCV-2B was set to approximately 63 psig, well below the intended setpoint of 180 +/-2 psig. Security and Operations have conducted an investigation into this event. It was determined that this valve was set to its required setpoint during CIA system startup following system maintenance during the last outage. No clear evidence of tampering was found since that time, and the cause of the misadjustment of CIA-PCV-2B is unknown. As a corrective action, the setpoint for CIA-PCV-2B has been readjusted to 180 +/-2 psig and a new locking wire seal was installed. This condition is reported per 10 CFR 50.73(a)(2)(ii) as a condition prohibited by Technical Specifications. Due to the redundant design features of ADS, both the long term and short term functions of ADS would have been accomplished during the period when CIA-PCV-2B was misadjusted. Therefore, the safety significance of this event is minimal.
3971997009 | Columbia | 07/17/1997 | 08/18/1997 | 9708250368 | <strong>MISSED INSERVICE TEST FOR TIP-V 6</strong><br /><i>Abstract:&nbsp;</i>On July 17, 1997, with the plant operating at 90% power, an error was discovered in the recently preformed Inservice Testing (IST) procedure, OSP-TIP/IST-R701. The procedure is to be performed each refueling outage and, among other components tested, is used to exercise the Traversing Incore Probe (TIP) purge inboard containment isolation valve, TIP-V-6, as required by the WNP-2 IST Program Plan. The procedure allows credit to be taken for successful completion of a Local Leak Rate Test (LLRT) to demonstrate the exercise of TIP-V-6. The performers of the procedure used LLRT results for this valve from the 1996 refueling outage instead of performing a 1997 test, and the procedure was erroneously accepted as complete. As a result, TIP-V-6 was initally declared inoperable and the TIP purge outboard containment isolation valve, TIP-V-15, was closed and deactivated per Technical Specification Action Statement (TSAS) 3.6.1.3.A.1. Plant staff subsequently determined that guidance in NUREG 1482 allowed use of Generic Letter (GL) 91-18 to evaluate operability of the valve. A Followup Assessment of Operability (FAO) was performed, and consequently TIP-V-6 was declared operable and the TSAS exited. On August 12, 1997, discussions with the NRC staff revealed that a more proper course of action would have been submittal of a request for Enforcement Discretion From TSAS 3.6.1.3.A, to be followed within 48 hours by an Exigent Technical Specification Amendment Request for Technical Specification 5.5.6. Thus, TIP-V-6 was again declared inoperable and TSAS 3.6.1.3.A reentered. The root cause of this event is procedure inadequacy. The safety significance of this event is minimal.
3971997010 | Columbia | 09/06/1997 | 11/07/1997 | 9711200090 | <strong>Voluntary Report on Use of Surveillance Requirement 3.0.3 Applicability for Reactor Coolant System Total Leakage Surveillance 3.4.5.1</strong><br /><i>Abstract:&nbsp;</i>At 0800 on September 5, 1997, with the plant at 100 percent power, it was discovered that Technical Specification (TS) Surveillance Requirement (SR) 3.4.5.1 for the "Identified" portion of Reactor Coolant System (RCS) Total Leakage would not be able to be performed within the time limits of SR 3.0.2. Two methods are available to meet SR 3.4.5.1; a flow totaling instrument loop or a manual determination method. The reactor containment Equipment Drain (EDR) Flow Transmitter, EDR-FT-37, was declared inoperable at 0800 on 09/05/97. The manual method was performed at 1530, but not before the limits of SR 3.0.2 expired at 1100 on 09/05/97. The flow transmitter was declared inoperable because the flow totalizer was not responding to the actual low flow signals as expected, indicating below actual values. Performance of the manual method was delayed due to recovery actions from high sump area contamination levels, using the provisions of SR 3.0.3. This event is being reported as an item of generic interest to highlight differences in the reporting guidelines of NUREG 1022 and requirements of the Improved Technical Specifications. The root cause for failure to perform the surveillance in accordance with SR 3.0.2 limits is that methods did not permit timely response to changing radiological conditions. At no time were the LCO 3.4.5 limits exceeded. Therefore, there is no safety significance associated with this event.
3971997011 | Columbia | 10/10/1997 | 11/10/1997 | 9711190086 | <strong>HIGH PRESSURE CORE SPRAY (HPCS) BATTERY CHARGER FAILURE RESULTING IN HPCS SYSTEM INOPERABILITY</strong><br /><i>Abstract:&nbsp;</i>On October 10, 1997 at 2057 hours with the plant in Mode 1, the High Pressure Core Spray (HPCS) Battery Charger (HPCS-C1-1) failed resulting in degraded 125 VDC bus voltage. The HPCS System was immediately declared inoperable. Concurrent with the HPCS failure, the Reactor Core Isolation Cooling (RCIC) System was inoperable due to system testing. With both HPCS and RCIC inoperable, Technical Specification LCO 3.5.1 Action D.1 (be in Mode 3 within 12 hours) was entered. The RCIC System was declared operable approximately 17 minutes later and LCO 3.5.1 Action D.1 was exited. The HPCS Battery Charger tested satisfactorily following installation of new control circuit boards and was declared operable on October 15, 1997 at 0150. The root cause of this event was failure of the "A" phase firing control circuit board due to component degradation (aging) after seven (7) years of reliable operation. At all times, adequate core cooling was assured by the operability of the redundant and diverse low pressure Emergency Core Cooling System (ECCS) injection/spray in conjunction with the Automatic Depressurization System (ADS); therefore, this event had no safety significance.
4001997001 | Harris | 01/31/1997 | 03/03/1997 | 9703070191 | <strong>Reactor Trip on low-low S/G level due to inadvertent closure of a Main Feedwater Isolation Valve (1FW-159).</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 097%. On January 31, 1997, with the plant operating in Mode 1 at 97% power, an automatic reactor trip resulted from steam generator low-low level in the 'A' Steam Generator (S/G). This trip occurred while performing quarterly surveillance testing on the Main Feedwater and Main Steam Isolation Valves (Operations Surveillance Test, OST-1018). During this testing, the Main Feedwater Isolation valve to the 'A' S/G (1FW-159) was taken to the TEST position which should have caused the valve to stroke in the closed direction to the 90% open position. However, 1FW-159 stroked fully shut causing a decrease in feed flow and S/G level. The reactor operator performing the surveillance test in the main control room recognized that 1FW-159 had fully shut and attempted to restore feedwater flow the S/G by taking the control switch for 1FW-159 to the SHUT/RESET position and then holding the control switch in the OPEN position. The 'A' feedwater regulating valve was also fully opened to increase feed flow. 1FW-159 would not re-open, thus resulting in a continued decrease in 'A' S/G level. A locally stationed auxiliary operator reported that 1FW-159 opened approximately 2-3 inches then re-shut several times. Based on these conditions, the Unit Senior Control Operator commenced a load reduction to reduce steam demand and made plans to manually trip the reactor if S/G level decreased to 40%. (S/G low low level reactor trip setpoint is 38.5%) At 0438 hours, with lowest main control board indicated S/G level at approximately 44%, an automatic S/G low-low level reactor trip occurred. Feedwater system started as required. All support systems functioned as required except for the pressurizer bank-A backup heater supply breaker, which tripped open after approximately ten minutes of operation. The plant was then stabilized in Mode-3 (Hot Standby). This event was caused by faulty hydraulic relays (solenoid operated shuttle valves) that control the position of 1FW-159. Investigation revealed that the shuttle valve's o-ring seals were leaking by which prevented proper hydraulic oper
4001997002 | Harris | 02/07/1997 | 07/07/1998 | 9807160281 | <strong>Inoperable Main Feedwater Isolation Valves caused by cold weather conditions.</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1997, with the plant operating in Mode 1 at 100% power, investigation determined that cold weather conditions resulted in the Main Feedwater Isolation Valves (MFIVs) being potentially inoperable during a period from January 17, 1997 through January 20, 1997. The MFIVs serve as containment isolation valves and are required to stroke closed in 10 seconds or less to provide feedwater isolation in the event of a main steam line break or spurious opening of a feedwater regulating valve. Based on purchase specification documents and discussions with the MFIV vendor, a minimum operating temperature of 60 degrees exists to ensure that the MFIVs will stroke in the required 10 seconds. The MFIV actuators are hydraulic to open and shut with nitrogen pressure, but even the shut sequence utilizes hydraulic oil operation. Therefore, with actuator temperature below 60 degrees the hydraulic oil may be too viscous to provide a valve stroke time of 10 seconds or less. This condition was identified when a nearby instrumentation line was found frozen and brought into question the operability of the safety-related MFIVs. (The frozen instrument line had no adverse effect on plant operation.) This event was caused by a combination of inadequate design and improper functioning of the HVAC system that serves the Steam Tunnel (area that MFIVs are located in). The steam tunnel HVAC supply fans (S64 Fan and S65 Fan) take a suction from the outside atmosphere and exhaust directly into the area of the MFIVs. They are designed with an automatic low ambient temperature shutoff at 30 degrees, but plant process computer data indicates that the fans continued to operate with outside temperatures well below the 30 degree setpoint. Even if the fans had shutoff as designed at 30 degrees, MFIV actuator temperatures may have dropped to just slightly below the minimum MFIV actuator operating temperature of 60 degrees. This LER revision is being provided to more accurately describe the initial corrective actions taken to address the steam tunnel low temperature conditions and to incorporate additional actions taken to date.
4001997003 | Harris | 02/27/1997 | 03/31/1997 | 9704030123 | <strong>Steam Generator low level protection circuitry outside design basis.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 27, 1997, with the plant operating in mode 1 at 100% power, engineering review concluded that the Steam Generator (S/G) upper instrument line tap arrangement for S/G flow and narrow range level channels do not completely satisfy the design requirements of IEEE Standard 279-1971. This conclusion was reached following a review of Westinghouse Nuclear Safety Advisory Letter (NSAL) 96-004, 'Control and Protection Interaction', which requires redundant protection channels to be capable of providing protective action even when degraded by a second random failure. Due to the arrangement of the S/G upper instrument line tap connection for S/G steam flow instruments, which share a common tap connection with a S/G narrow range level channel, combined with the logic utilized in the reactor protection system circuitry logic, a potential scenario exists that results in the S/G low-low level reactor trip being unavailable. This constitutes operation outside the design basis of the plant and was reported to the NRC via the emergency notification system at approximately 1513 hours on February 27, 1997. This condition was caused by an inadequate failure modes and effects analysis performed on the as-built piping configuration for S/G level instrumentation during initial plant construction. the potential failure scenario by placing the Steam Flow - Feed Flow selector switch on the main control board to the 'Channel III' position and placing caution tags on the switch. A review was also performed of other protection channels to ensure that protection and control interaction requirements were met. o a atonal discrepancies were identified during this review. Planned corrective actions will include a permanent resolution to the identified design deficiency.
4001997004 | Harris | 03/04/1997 | 04/03/1997 | 9704080112 | <strong>In-Plant Spent Fuel Cask Handling Activities.</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1997, with the plant operating in Mode 1 at 100% power, investigation determined that spent fuel cask handling activities have been conducted outside of the design and licensing basis of the plant. In preparing the Harris Nuclear Plant (HNP) response to NRC Request for Additional Information (RAI) to Bulletin 96-02, "Movement of Heavy Loads Over Spent Fuel, Over Fuel in the Reactor Core, or Over Safety-Related Equipment," dated December 5, 1996, investigation revealed that the HNP evaluation of a cask drop to a flat surface, documented in FSAR 15.7.5.2, did not consider the potential consequences of dropping or otherwise damaging a loaded spent fuel cask after it has been prepared for unloading; that is, with the cask head detensioned and valve box covers removed. The FSAR 15.7.5.2 determination that the cask is designed to withstand a free drop through air of less than or equal to 30 feet onto a flat, essentially unyielding, horizontal surface assumed the loaded cask to be in a fully secured, transportation ready condition with valve box covers installed and cask closure head fully tensioned. Spent fuel casks received at HNP are prepared for unloading by removing the valve box covers and all but four of the head sleeve nuts before moving the cask to the unloading pool. Consequently, the existing cask drop evaluation in FSAR 15.7.5.2 does not address a potential drop of a cask in a less than fully secured condition. This event was caused by an incomplete understanding of the purpose and scope of the IF-300 Cask Safety Analysis Report (CSAR) and a misconception that following the requirements of the CSAR would maintain the cask in a condition that was analyzed for a free drop of 30 feet, through air, onto a flat, essentially unyielding, horizontal surface. A contributing cause is inadequate 10 CFR 50.59 evaluations for procedure CM-M0300 that failed to identify that the cask drop analysis conducted to confirm that the cask could withstand a 30 foot free drop without a loss of integrity only applied to a cask in a fully-secured, ready-for- shipment (10 CFR 71 compliant) condition. This discovery has been submitted to the NRC as an unreviewed safety question (ref. CP&L Letter HNP-97-064, dated 3/14/97). CP&L has suspended cask handling activities by placing procedure CM-M0300 on hold pending NRC review and approval of the USQ submittal. CP&L will review the subject event with personnel responsible for making changes to CM-M0300 and other procedures to be used for loading and unloading NRC approved packages.
4001997005 | Harris | 03/20/1996 | 03/17/1997 | 9703240130 | <strong>Failure to perform core flux mapping following plant operation with reactor power greater than 100%.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 20, 1996, a calculated reactor power level of 100.08% was identified during the daily secondary calorimetric heat balance. Following verification of the reactor power calculation, reactor power was reduced from approximately 99.9% to 99.5% indicated power. Technical Specification (TS) 3.2.3 action C.1 requires reactor core flux mapping to be performed within 24 hours of initially entering the 'prohibited region of operation.' This region is defined by TS figure 3.2-3, which has a vertical line at exactly 100.0% power. Flux mapping was not performed following this event based on guidance contained in the bases for TS 3.2.3, which was inserted following a previous violation of this technical specification (reference LER #96-03). This guidance was intended to clarify when thermal power is considered to be within 100.0% rated thermal power and was implemented for the ending continuous calorimetric capability. However, following additional review and delays in implementing the continuous calorimetric, the TS bases revision was considered inappropriate. On February 13, 1997, the bases revision was withdrawn, thereby resulting in the March 20, 1996 event being considered reportable as a violation of TS 3.2.3 for not performing core flux mapping. This event was caused when the bases change for TS 3.2.3 was implemented containing inappropriate guidance for short power excursions over 100.0% power. (reference CP&L letter to NRC dated February 8, 1996) Corrective actions included withdrawing the TS 3.2.3 bases change and issuing an Operations Night Order communicating this action to Operations personnel.
4001997006 | Harris | 03/18/1997 | 04/17/1997 | 9704230176 | <strong>Breach in Reactor Auxiliary Building 3-hour rated fire barrier (Thermo-lag wall in Cable Spread Room).</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 18, 1997, with the plant operating in mode 1 at 100% power, a breach was identified in the thermo-lag fire barrier wall which provides separation between the A-train and B-train cable spread rooms within the Reactor Auxiliary Building. This breach consists of a 'L-shaped' hole approximately 8 inches wide by 6 1/2 inches high at the point where the fire barrier wall joins the cable spread room ceiling. A 3/4 inch conduit containing two wire conductors was also found penetrating the breach. These wires were unconnected at each end and investigation revealed that they were unscheduled and not included in plant design. The breach is very difficult to see due to its location and configuration, coupled with the fact that it is behind several cable trays. It was identified by maintenance personnel during modifications to the cable spread room fire barrier to resolve concerns expressed in NRC Information Bulletin 92-01. Follow-up investigation revealed an additional thermo-lag fire barrier deficiency in a floor drain assembly in the cable spread room. Since there are safety-related cables near both sides of the identified fire barrier breach/deficiency, it is possible that a fire in the cable spread room could adversely affect both the A-train and B-train safety-related cables. These conditions do not comply with the 3-hour-fire-rated barrier requirement in the Harris Nuclear Plant (HNP) Final Safety Analysis Report and Safety Evaluation Report (NUREG-1038), and were determined to constitute operation outside the design basis of the plant. The fire barrier deficiencies appear to have existed since initial plant construction and were most likely caused by inadequate initial design, poor construction methods, as well as incomplete as-built design verification. Immediate corrective actions included a visual inspection of thermo-lag barrier walls located in the cable spread rooms and auxiliary control panel room. The unscheduled conduit was removed from the penetration on April 11, 1997. The identified barrier reach and floor drain assembly deficiency wi ll be resolved by an existing Engineering Service Request for penetration upgrades by September 15, 1997.
4001997007 | Harris | 03/25/1997 | 04/24/1997 | 9704290152 | <strong>Inoperable Component Cooling Water System-Technical Specification 3.03 Entry</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 25, 1997, with the plant operating in Mode 1 at 100% power, a chemical addition was made to the Component Cooling Water (CCW) System using procedure OP-145, 'Component Cooling Water.' The chemical addition section of the CCW system is non-seismically qualified. The remainder of the CCW System is seismically qualified. The system alignment used to add the chemicals resulted in the simultaneous interconnection of the A-SA and B-SB trains of the safety-related CCW System with non-seismic chemical addition equipment. As a result, both CCW trains were simultaneously inoperable, at which time the plant unknowingly entered Technical Specification 3.0.3. This condition was identified and corrected within nine minutes. This event was caused by a combination of procedural inadequacies, improper use of procedural guidance, and poor communications between personnel involved in the chemical addition process. CP&L has taken the following corrective actions in response to this event: (1) counseled applicable individuals involved in this event; (2) changed a misleading note in OP-145, and (3) issued a night order clarifying the impact of cross-connecting seismic and non-seismic systems. CP&L will: (1) review procedures specified in LER 96-13 to ensure that the changes are unambiguous; (2) provide real time training to operations crews regarding the specifics of this event, the operability concerns associated with connecting non-seismic portions of a system to safety-related equipment, and the company position that local, continuous operator monitoring is no longer an acceptable method for maintaining operability; and (3) evaluate the following items for inclusion into the operator training programs: 1) the procedure convention of using parentheses to distinguish between different trains of equipment; 2) the seismic/non-seismic interface (LER 96-13); and 3) the company position that local, continuous operator monitoring is no longer an acceptable method for maintaining operability.
4001997008 | Harris | 04/04/1997 | 05/05/1997 | 9705130398 | <strong>Safety-related Air Handling Units not declared inoperable During maintenance on associated temperature switches resulting in a violation of Technical Specifications.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 4, 1997, with the plant in mode-1 operating at 100% power, investigation determined that certain safety-related air handling units had not been declared inoperable during maintenance on their associated temperature elements, temperature transmitters and/or temperature switches. During certain postulated scenarios, these temperature circuitry components would be required for the air handling units to perform their safety function. In the instances described in the event description, the temperature circuitry components were out of service for a period of time that exceeded the Technical Specification (TS) action statement for the specific component cooled by the air handling unit and/or were out of service during plant mode changes, which would result in a violation of TS 3.0.4. This condition was caused by an incorrect interpretation of operability requirements related to safety-related air handling units. TS Interpretation #87-002 Revision-2, which was approved in August 1988, provided guidance on this issue by stating that the automatic start of a fan on high temperature was not an operability requirement. Based on this, maintenance performed on associated air handling unit temperature elements, temperature transmitters, and/or temperature switches was considered to have no effect on operability. This incorrect interpretation resulted in deficient plant procedures and processes that provide guidance for control of component operability. An Operations Night Order was issued to address the operability requirements associated with the safety-related air handling units and their associated temperature circuitry components. Additional corrective actions will include: (1) training for appropriate Operations and Maintenance personnel, (2) revisions to the site computerized equipment database system (EDBS) and component operability database system (SPECAPRAISAL), and (3) revisions to affected maintenance temperature loop test and calibration procedures.
4001997009 | Harris | 04/07/1997 | 05/07/1997 | 9705140136 | <strong>Technical Specification compensatory measures were not taken prior defeating the Control Room Ventilation Isolation signal by removing a fuse During clearance preparation.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 7, 1997, with the plant in Mode-5 (cold shutdown) for refueling outage 7, a fuse (L4/2973) was removed at approximately 2300 hours from the Control Room Ventilation Isolation Signal (CRVIS, EIIS Code: VI) power supply circuitry. This fuse was removed per clearance #96-0158 in preparation for a plant modification (ESR 96-00320). By removing the fuse, the B-train CRVIS signal was defeated, including the actuation input signal from the control room outside air intake radiation monitor. With the plant in Mode-5 and the radiation monitor's actuation capability rendered inoperable, Technical Specification (TS) 3.3.3.1, action #29 requires the respective outside air intake to be isolated within 1 hour. This TS action was not identified during review and approval of the clearance and subsequently was not performed as required. The cause of this condition was personnel error on the part of the individuals involved in preparing and approving the clearance. Inadequate work practices and communication techniques allowed the clearance to be prepared, approved and implemented without identifying and performing the compensatory measures required by TS 3.3.3.1, action #29. Corrective actions included counseling the individuals involved in preparing and approving the clearance and reviewing the event with Operations and Engineering personnel.
4001997010 | Harris | 04/18/1997 | 05/19/1997 | 9705270290 | <strong>Design Deficiency - Reactor Coolant Pump Motor Oil Collection System.</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1997, with the plant in Mode-6 (Refueling) for refueling outage 7, a walkdown performed by Harris Nuclear Plant (HNP) Engineering and Fire Protection personnel determined that the Reactor Coolant Pump motor Oil Collection System (OCS) did not meet applicable design requirements. Specifically, a six inch wide gap exists in the OCS enclosure at the base of the upper lube oil cooler on each of the three installed Reactor Coolant Pump (RCP) motors, which could allow RCP oil to splash or spray out in the event of a lube oil cooler or lube oil piping leak. During subsequent investigation, additional design discrepancies were also identified and are described in the event description. HNP Final Safety Analysis Report (FSAR) Section 9.5.1 states that the RCPs are equipped with an oil collection system that is designed and installed such that failure will not lead to a fire during normal and design basis accident conditions. It also states that the system is capable of collecting oil from all potential pressurized and unpressurized leakage sites in the RCP lube oil systems. This design was established to meet the fire protection program requirements of NUREG-0800/NRC Branch Technical Position CMEB 9.5-1. The deficient RCP OCS enclosure does not satisfy these design requirements and is being reported per 10CFR50.73.a.2.iii as operation outside the design basis of the plant. This condition was caused by inadequate RCP OCS design detail and a lack of knowledge on the part of HNP construction and start-up personnel regarding the design basis for the system, which allowed the OCS enclosures to be incorrectly fabricated during initial plant construction. Corrective actions will include modifying the RCP OCS enclosures for the installed RCPs to satisfy design requirements. This will be completed prior to plant re-start from the current refueling outage. The spare RCP motor has been placed on hold and hold will be modified prior to use in the plant.
4001997011 | Harris | 04/22/1997 | 05/22/1997 | 9705290267 | <strong>Inappropriate Technical Specification Interpretation resulted in violations of ECCS Accumulator Technical Specification and entry into Technical Specification 3.0.3.</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1997 with the plant at 0% power in Mode 6 Refueling, investigation determined the "A" ECCS Accumulator had been inoperable approximately 14 hours on December 10, 1996 and 46 hours from March 20, 1997 to March 22, 1997. Also on March 21, 1997, the "B" ECCS Accumulator was inoperable from 0255 to 0337. During these periods, the plant was operating at 100% power with the ECCS Accumulators required to be operable. The "A" ECCS Accumulator was not declared inoperable and consequently the Technical Specification (TS) 3.5.1 required actions were not taken. The LCO Action times were exceeded for the "A" ECCS Accumulator in both these examples, resulting in a violation of TS 3.5.1. Failure to take the required action for the "A" ECCS Accumulator was due to inappropriate interpretation of TS Surveillance Requirement (SR) 4.5.1.1a.1. This SR verifies proper accumulator pressure and level by the absence of alarms. A TS Interpretation (TSI 88-001) was in place to allow manual logging of accumulator level or pressure when the respective alarm was sealed in or otherwise inoperable. TS 3.5.1 Action a. requires the plant to be in Hot Standby within 7 hours of accumulator inoperability for inadequate level or pressure. The "A" ECCS Accumulator inoperability coincided with the "B" ECCS Accumulator inoperability on March 21, 1997, requiring entry into TS 3.0.3. The "B" ECCS Accumulator was inoperable due to connections with non-seismically qualified piping while filling from and draining to the Refueling Water Storage Tank (RWST). HNP has taken the following corrective actions in response to these events: (1) cancelled TS[ 88-001; (2) revised procedures that referenced TSI 88-001 and (3) initiated a Night Order informing Operations personnel of TSI 88-001 cancellation. HNP submitted a license amendment request on March 10, 1997 for NRC approval of this alternate method of operability verification. HNP will review other TSI's for other potential TS conflicts.
4001997012 | Harris | 05/05/1997 | 06/04/1997 | 9706160096 | <strong>Auxiliary Control Panel surveillance testing deficiency.</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1997, with the plant defueled for refueling outage 7, a condition related to inadequate testing of control power circuitry for the Auxiliary Control Panel (ACP, EIIS Code:EB-REL/FU) was determined to be reportable. Specifically, on a transfer to the ACP from the main control board, there are 17 interposing relays that energize and actuate to transfer the control power supply path through alternate fuses in several 6.9KV and 480V Emergency Bus Panels. These alternate control power fuses provide a back-up power supply path in the event that a fire in the main control room causes a failure of the primary fuses. Investigation determined that previous ACP testing had not verified the operability of the interposing relays and the subsequent transfer function to the alternate control power fuses. This condition was caused by an incorrect interpretation of Technical Specification testing requirements and an incomplete understanding of the function of the interposing relays. The failure to test these components has existed since initial surveillance test procedure development. Corrective actions included a review of other ACP circuits and testing of the ACP interposing relays and their 1 subsequent actuation functions. Procedures will also be revised to ensure that future surveillance testing includes verification of this function.
4001997013 | Harris | 05/08/1997 | 06/09/1997 | 9706190208 | <strong>Entry into Mode-6 without required operable components, resulting in Technical Specification 3.0.4. violation.</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1997, at approximately 0718 hours, mode-6 was entered when the first fuel assembly was reloaded into the reactor vessel during refueling outage 7. Just prior to entering mode-6 at 0644 hours, a feeder breaker tripped which de-energized the SIII Instrument Bus. Operations personnel in the main control room reviewed plant conditions per the abnormal operating procedure (AOP-024) for the de-energized SIII Instrument Bus and determined that there was no adverse impact on commencing fuel movement and entering mode-6. Operations personnel were aware that with the SIII Inverter Bus de-energized, the heaters for the R-2A Control Room Emergency Filtration Unit would not be available which results in a 7-day LCO per the action statement of Technical Specification (TS) 3.7.6. However, the operators did not realize the impact on Technical Specification 3.0.4, which prevents entry into an operational mode while relying on the provisions of a TS action statement. Therefore, entry into mode-6 with the SIII Instrument Bus and the R-2A Unit inoperable constituted a violation of TS 3.0.4 and is reportable per 10CFR50.73.a.2.i. This event was caused by personnel error on the part of Operations personnel in the main control room when the requirements of TS 3.0.4 were not identified. This event occurred early in the shift and the on-coming crew did not take adequate time to thoroughly evaluate plant conditions and the impact of the de-energized SIII Instrument Bus prior to allowing fuel movement and entry into mode-6. Corrective actions included counseling the involved personnel. Training for other Operations personnel will also be conducted.
4001997014 | Harris | 05/14/1997 | 06/13/1997 | 9706250446 | <strong>Safety Injection During Solid State Protection System surveillance testing.</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1997, with the plant in mode 5 for refueling outage 7, a Safety Injection (SI) signal was generated, which caused SI system valves to automatically align and allow gravity forced flow from the Refueling Water Storage Tank to the Reactor Coolant System. This occurred during surveillance testing on the Solid State Protection System (SSPS). The cause of this event was inattention to detail during a recent revision to the surveillance test procedure being used. This revision was approved approximately 3 weeks before the outage to incorporate testing that would verify the proper function of the individual inputs for the SSPS general warning circuitry. During the revision process, personnel that completed and reviewed the procedure revision did not realize that positioning a particular SSPS switch would remove the steam line low pressure SI signal blocking feature. Corrective actions included revising the deficient surveillance procedures and counseling the individuals involved in the revision preparation, review, and approval process. This condition is being reported per 10CFR50.73.a.2.iv as an unplanned Engineered Safety Feature actuation. This report also satisfies the 90-Day Special Report requirement contained in Technical Specification 3.5.2 Action Statement b, for Emergency Core Cooling System (ECCS) actuations that result in ECCS injection into the RCS. Though water was injected into the RCS via gravity feed from the RWST, this event did not include a plant cooldown and did not constitute an actuation cycle for the affected safety injection nozzles. Therefore, the SI nozzle usage factor did not increase from its previous value of 0.2.
4001997015 | Harris | 06/02/1997 | 07/02/1997 | 9707090073 | <strong>Inadequate Auxiliary Feedwater System Flow Control Valve surveillance testing resulting in Technical Specification violation.</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1997, with the plant in mode 4 for refueling outage 7, a deficiency was identified related to previous testing of the Auxiliary Feedwater (AFW) System flow control valves (FCV). Specifically, Technical Specification (TS) 4.7.1.2.1 requires the motor driven AFW pump FCVs to open upon receipt of an auto open signal. This requirement was added by amendment 42 to the facility operating license following a plant modification (PCR-6502), completed in April 1994 during refueling outage 5. PCR-6502 was installed to provide an automatic open feature for the FCVs, which would allow AFW flow to be throttled during plant start-up activities. Operations surveillance test procedures have tested these valves on a quarterly basis, but did not verify their ability to open during high differential pressure conditions that exist during plant start-up while in mode 3, with low Steam Generator pressures present. In May 1994, Operations personnel identified that the FCVs experienced sticking problems when S/G pressures were very low while in mode 3. To address this condition, maintenance was performed on the valve actuators and procedures were revised to alert operators of this condition and provide guidance on how to open the FCVs if they stuck closed. During additional investigation in March, 1996, testing confirmed that the FCVs would not open from the fully shut position if steam generator pressures were less than 320 psig. However, during these previous instances, plant personnel did not consider the condition to be mode limiting or reportable as a technical specification surveillance requirement violation. This condition was caused by the failure to recognize the impact on TS 4.7.1.2.1 that the AFW FCV actuator deficiencies created when low steam generator pressures were present while in mode 3. This resulted in past surveillance testing that did not completely satisfy the requirement for the AFW FCVs to respond as required per Technical Specification 4.7.1.2. 1. Corrective actions included readjusting the AFW FCV actuator spring pre-loading and testing the FCVs to verify their operability. The site surveillance test scheduling process will also be revised to ensure that future testing of the FCVs is performed with the high differential pressure conditions present.
4001997016 | Harris | 06/08/1997 | 10/14/1997 | 9710210120 | <strong>Reactor Trip and Auxiliary Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1997, with the plant at approximately 28% power in Mode 1, a Reactor Trip occurred due to personnel error while attempting to adjust a Power Range (PR) Nuclear Instrumentation (NI) channel following the performance of a calorimetric. The plant was performing a startup following a refueling outage, when PR NI channel N41 was declared inoperable. The PR Neutron Flux High Setpoint, Low Setpoint, High Flux Rate, and Overtemperature differential temperature trips for N41 were placed in the tripped condition per TS 3.3.1 Table 3.3-1 Action 2 a. and 6 a. When the Plant reached approximately 28% Reactor Power the PR NI's were adjusted to match calculated power in accordance with the calorimetric procedure. PR NI channel N41 was adjusted first. PR NI channel N42, was to be adjusted next. As the operator unlocked the coarse adjustment potentiometer, N42 spiked, generating a negative rate trip signal on PR NI channel N42. This signal coupled with the rate trip signal from N41 being inoperable, met the 2/4 coincidence for the PR Flux Rate Trip and a reactor trip occurred. Following the reactor trip, a breaker failure caused a non-safety 6.9 kV bus to deenergize, resulting in the trip of the only running Main Feedwater Pump and initiated an Engineered Safety Features Actuation Signal start of both Motor - Driven Auxiliary Feedwater (MDAFW) Pumps. Harris Nuclear Plant (HNP) has performed the following corrective actions: (1) An Operation's Night Order was issued prohibiting adjustment of a PR NI when a redundant channel is inoperable and on the use of diverse and redundant indications for instrumentation. (2) The Manager - Operations discussed this event with the operating crew. (3) The breaker for auxiliary bus 1A was replaced prior to startup. (4) Procedures were revised to provide operators an aid in identifying, at the PR channel instrument drawer, inoperable PR NI channels. (5) Procedures were revised preventing PR NI adjustment channels with a redundant PR NI channel in a tripped condition. (6) License operators reviewed LER 97-01 6-00 for lessons learned from the causes of this event.
4001997017 | Harris | 06/12/1997 | 07/11/1997 | 9707160125 | <strong>Failure to recognize inoperable reactor axial flux difference (AFD) monitor, resulting in violation of Technical Specification surveillance requirements.</strong><br /><i>Abstract:&nbsp;</i>At approximately 0800 hours on June 12, 1997, with the plant operating in mode 1 at approximately 99% power, a licensed reactor operator on shift in the main control room identified that the reactor axial flux difference (AFD) monitor alarm was disabled. This alarm function is provided by the plant's process computer (Emergency Response Facility Information System, ERFIS) and with the alarm function disabled, the AFD monitor is considered inoperable. The plant had just completed refueling outage 7 and reached 50% power on June 10, 1997 at approximately 2300 hours. At this point indicated AFD was manually logged once per hour as required per procedure, by the control room operators. However, the control room operators involved in raising reactor power to 50% and above, did not notice the disabled alarm status on ERFIS and did not take the actions required for an inoperable AFD alarm. Plant procedures also require the AFD monitor to be checked once every 8 hours. These operability checks were performed, but also failed to identify the disabled AFD alarm status on ERFIS. Technical Specification (TS) 4.2.1.1.b requires that, with an inoperable AFD monitor, AFD shall be determined to be within its limits during operation above 50% power by logging the indicated AFD at least once per hour for the first 24 hours and at least once per 30 minutes thereafter. With the AFD monitor inoperable, the manual AFD logging frequency should have been increased to once per 30 minutes, 24 hours after reaching 50% power. However, since operators were not aware that the AFD alarm on ERFIS was disabled, the AFD logging frequency was not increased to once per 30 minutes as required by TS. This event was caused by personnel error on the part of the control room operators that failed to properly establish and periodically verify the AFD monitor function in ERFIS. Corrective actions will include counseling the involved operators and having Operations management review the event with the operating crews during licensed operator re-qualification classes.
4001997018 | Harris | 07/01/1997 | 07/31/1997 | 9708060308 | <strong>Operation with procedures not properly reviewed and approved</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1997, with the plant at approximately 100% power in Mode 1, an investigation determined that some Harris Nuclear Plant (HNP) procedures had not received proper reviews and approvals. Specifically, approximately 150 temporary procedure changes affecting over 100 procedures were not reviewed and approved within 14 days in accordance with Technical Specification (TS) 6.8.3 and 6.5.1. Additionally, many of these procedures were used to operate the plant without the required TS review and approval, The cause of this TS violation is failure to comply with plant administrative procedure AP-006. Contributing factors were: (1) A misunderstanding of the basis of the requirements in the AP-006 by site personnel. (2) Inadequate management involvement once the problem was brought to management's attention as evidenced by not stopping the Handwritten Revision non-intent process once a problem was identified. The following corrective actions have been performed: (1) HNP procedures identified as deficient have been properly reviewed and approved in accordance with TS, (2) Involved Site Management has been counseled that procedure noncompliance must be prevented and promptly corrected upon discovery, (3) Communications to appropriate site personnel have been made on how AP-006 implements TS requirements, (4) AP-006 has been revised to clarify implementation of TS requirements and (5) The Supervisor-Operations Support, involved in this event, has been disciplined by Plant Management. A comprehensive review of the procedure change and review process will be completed by 9/1/97.
4001997019 | Harris | 07/20/1997 | 08/18/1997 | 9708250133 | <strong>Turbine Trip/Reactor Trip due to failure of generator exciter.</strong><br /><i>Abstract:&nbsp;</i>At approximately 0256 hours on July 20, 1997, with the plant at 100% power in mode 1, a Turbine Trip/Reactor Trip occurred due to a generator lock-out resulting from loss of the main generator excitation field. As a result of the trip, the Auxiliary Feedwater (AFW) System automatically started as required to provide feedwater flow to the Steam Generators (S/G). Operators in the main control room immediately implemented Emergency Operating Procedure (EOP Path-1) and upon verification that a safety injection was not required and had not occurred, entered the Reactor Trip Response procedure (EOP-EPP-004) to stabilize the plant. Approximately 5 minutes after the plant trip, AFW flow to the S/Gs was secured in order to return Reactor Coolant System (RCS) temperature back to 557 degrees (RCS temperature reached approximately 548 degrees during AFW operation). Various plant components not required for plant recovery were observed tripped in the main control room due to the electrical transient involved in the plant trip. Automatic protection and safeguards systems functioned as required and the plant was stabilized in mode 3 (Hot Standby). The cause of the Turbine Trip/Reactor trip was a three phase fault that collapsed the excitation field in the main generator, resulting in a generator lockout. Investigation could not conclusively determine the reason for the electrical fault in the generator exciter. However, the most probable cause appears to be entry of foreign material into the exciter housing that caused multiple shorts on the exciter diode wheel. Corrective actions for this event included replacement of the exciter rotor assembly and inspections to ensure no foreign material was present in the exciter and exciter housing area. Additional actions will include strengthening the plant's Foreign Material Exclusion Program with regards to the Generator Exciter. This will be performed via a revision to Maintenance Procedure, PM-E0045 "Generator Exciter Cleaning, Inspection, and Testing" to specify cleanliness close-out requirements for the Generator Exciter.
4001997020 | Harris | 08/14/1997 | 09/12/1997 | 9709180097 | <strong>Inadequate fire protection provided for safety-related EDG Fuel Oil Transfer Pump cables resulting in operation outside design basis.</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1997, with the plant at approximately 100% power in mode 1, design discrepancies were identified during an Engineering review of the Safe Shutdown Analysis in Case of Fire. These discrepancies pertain to safety-related Emergency Diesel Generator Fuel Oil Transfer pump electrical cables. These cables are required for safe shutdown in case of a fire, but were not adequately protected. Specifically, section 9.5.1 of the Harris Plant Final Safety Analysis Report (FSAR) provides separation requirements for redundant safe shutdown divisions to maintain safe shutdown capability. During the Engineering review, Cables 12549E-SA and 12550A-SB, located in the 261' elevation of the Reactor Auxiliary Building were found to not meet the specific design requirements. The first cable (12549E-SA) was in an area that had automatic fire detection/suppression systems, but was not separated by a 3-hour fire barrier or 20 feet of horizontal distance and was not enclosed in a 1-hr rated barrier. The second cable (12550A-SA) was separated by 20 feet horizontally, but no suppression/detection system was provided in its location, nor was a 3-hour barrier provided. These design deficiencies were caused by engineering oversight and inadequate design verification during initial plant construction. Immediate corrective actions included establishing fire watches for the areas with unprotected cables. A plant modification will be developed and installed to provide the required protection.
4001997021 | Harris | 08/14/1997 | 06/30/1998 | 9807070218 | <strong>Technical Specification Surveillance Procedure Review Project Identified Deficiencies.</strong><br /><i>Abstract:&nbsp;</i>On August 14, 1997, with the plant at approximately 100% power in mode 1, a condition was identified during the on-going Technical Specification (TS) surveillance procedure review project related to inadequate maintenance of Spent Fuel Pool water level. Specifically, Technical Specification (TS) 3/4.9.11 requires that "at least 23 feet of water shall be maintained over the top of irradiated fuel assemblies seated in the storage racks." This depth of water will provide sufficient "scrubbing" to remove 99% of the assumed 10% iodine gap activity released from the rupture of an irradiated fuel assembly. Contrary to this requirement, water level has not been verified greater than 23 feet above the boiling water reactor (BWR) fuel assemblies received from CP&L's Brunswick Plant, which are currently stored in the Harris Plant fuel pools. These BWR assemblies have a bail handle that extends approximately 6 inches above the top nozzle base plate. When the BWR storage racks were installed in 1991, the 23 foot water level reference mark was established from the top nozzle base plate of the BWR fuel seated in the storage racks, not from the top of the bail handles. This approach was determined at the time to be conservative since the base plate elevation exceeds that of the fuel rods which would be the source of any released fission gasses. However, verbatim compliance with the TS requirements would require 23 feet of water over the BWR fuel assembly structure, including the top bail handle. This condition was caused by a misinterpretation of TS requirements and design inputs during the establishment of the 23 foot water level reference mark and the subsequent setup of water level indicators, when the BWR fuel storage racks were initially installed at the Harris Plant. Corrective actions included directions to Operations to maintain and monitor-fuel pool level at or above 23 feet 7 inches to ensure required water level over the BWR bail handles. This was completed by issuing an Operations night order and revising the daily surveillance procedures. Additional actions will include reviewing this event with appropriate Engineering personnel to emphasize the importance of verbatim TS compliance and an evaluation of the fuel pool level alarm setpoints. This revision is submitted to revise the due date for planned corrective action No. 1.
4001997022 | Harris | 08/29/1997 | 09/29/1997 | 9710030154 | <strong>Technical Specification Required Shutdown due to expiration of AFW limiting condition for operation.</strong><br /><i>Abstract:&nbsp;</i>On August 29, 1997, following operation in mode 1 at 100% power, a plant shutdown was completed as required by the Auxiliary Feedwater System Technical Specification Limiting Condition for Operation (TS LCO 3.7.1.2) This shutdown was necessary when it became apparent that repairs to the Turbine Driven AFW (TDAFW) Pump would not be completed within the 72 hour LCO period. Specifically, on August 26, 1997, high vibration readings were recorded on the TDAFW Pump's inboard bearing during routine quarterly surveillance testing. All other test points associated with the TDAFW were acceptable and consistent with previous testing. Initial troubleshooting and misdiagnosis of this condition resulted in a decision to replace the TDAFW pumps inboard bearing to reduce vibration revels. This bearing was successfully replaced, however during the pump re-coupling process, the pump end "shrink-fit" coupling hub was oriented incorrectly. Due to time considerations and difficulty experienced during the removal of the coupling hub, a decision was made to replace the pump's rotating element. Disassembly of the pump revealed slightly loose thrust bearings and a scratched balancing drum at the outboard end of the pump. This resulted in a slight degradation of structural stiffness at the pump's outboard end. Due to the pump's internal construction, this manifested as vibration at the pump's opposite end (inboard end) and was the actual source of high vibration. An additional error occurred during pump re-assembly involving installation of the casing gasket which caused excessive leakage. The combination of these errors resulted in the 72 hour LCO period expiring. The misdiagnosis was caused by personnel error on the part of those involved in the troubleshooting process. The incorrect orientation of the TDAFW Pump coupling hub during repair efforts was caused by maintenance technician personnel error. The cause of the pump casing leakage issue was inadequate procedural guidance. Applicable maintenance procedures/technical manuals did not contain proper instructions for cutting the pump casing gasket. Corrective actions include (1) completing repairs to the TDAFW Pump and returning the plant to service on August 31, 1997, (2) development of structured troubleshooting guidance, (3) training for applicable plant personnel, (4) maintenance procedure reviews and revisions to address the pump casing gasket issue.
4001997023 | Harris | 07/21/1992 | 11/24/1997 | 9712100265 | <strong>Reactor Coolant System Pressure Isolation Valve Testing Deficiency (OST-1506)</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1997, with the plant at Approximately 100% power in mode 1, an evaluation was completed by Operations personnel related to a deficiency in the Reactor Coolant System (RCS, EIIS Code:AB-V) Isolation Valve Leak Test Procedure (Operations Surveillance Test, OST-1506). This procedure deficiency involved the calculation used to determine the actual leak rate for the RCS pressure isolation valves being tested. Specifically, a correction factor was not included in the calculation as it should have been to consider the effects of back pressure on the downstream side of the valve being tested and the frictional headloss and elevation differences between the valve and testing rig. With this correction factor not applied, test results for certain valve testing configurations could have been influenced in the non-conservative direction. During the above mentioned Operations evaluation, past testing results were reviewed and the appropriate correction factor was applied. One instance was identified where application of the correction factor resulted in the test results failing to meet the leak rate limit allowed by Technical Specification (TS) 3.4.6. This occurred on July 21, 1992, during leak rate testing for 1SI-346, which is a 10 inch check valve in the low head safety injection header. This condition represents a TS violation for not meeting the required 5 gallon per minute maximum allowed leakage through 1SI-346 and subsequently, not taking the appropriate actions as required by TS. The leak rate calculation procedural deficiency in OST-1506 and resulting TS violation were caused by the failure to consider all testing variables during initial surveillance procedure development. Surveillance test procedure OST-1506 was revised to incorporate the appropriate correction factor to account for head loss and elevation differences during RCS pressure isolation valve leak rate testing.
4001997024 | Harris | 11/18/1997 | 12/18/1997 | 9712230205 | <strong>Solid State Protection System (P-10 & P-14 Permissives) Testing Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1997, with the plant at approximately 100% power in Mode 1, Harris Plant Engineering personnel determined that an operating experience item (OE #8636) generated at the McGuire and Catawba stations was applicable to the HNP Solid State Protection System (SSPS). This OE entry described a deficiency during testing of SSPS universal logic boards in a memory configuration, that would not allow detection of an internal card subcomponent failure. This potential card failure scenario could affect the: (1) Feedwater Isolation signal from Safety Injection inputs and P-14 Permissive inputs, and (2) the Source Range De-energization from the P-10 Permissive input. The test anomaly occurs in the bimonthly SSPS Actuation Logic and Master Relay tests (MST-I0001 & MST-I0320) when a test signal provides two simultaneous inputs to the 2 out of 4 logic cards and another input is provided separately (total of three), such that one of the simultaneous inputs cannot be independently verified. At HNP, the logic card in the P-10 permissive source range block circuit provides a de-energization of the source range detectors if power range is above the P-10 setpoint (10% reactor power). This block signal serves as a backup for manual operator source range de-energization that is procedurally directed at the P-6 setpoint (10**- 10 amps, intermediate range). This automatic function is described in the Technical Specifications (TS) Limiting Safety System Setting Bases Section. The P-14 and Safety Injection circuit provides a Feedwater Isolation signal to the Main Feedwater Regulating Valves (1FW-133, 1FW-249, and 1FW-191). Other valves and components that perform the feedwater isolation function are not affected by the potential card failure scenario. Based on this, previous tests performed to satisfy the requirements of Reactor Trip Instrumentation TS 4.3.1.1. item 21 and Engineered Safety Feature Actuation System Instrumentation TS 4.3.2.1 item 5 have been inadequate in light of the identified testing anomaly. Therefore, these conditions constitute a TS surveillance testing violation. This condition was caused by an inadequate testing scheme provided by the SSPS vendor that resulted in not properly testing all inputs for the P-10 and P-14 functions. Corrective actions included revising and performing the applicable test procedures to verify P-10 and P-14 operability.
4091997001 | La Crosse | 01/02/1997 | 01/21/1997 | 9702070109 | <strong>Less Than Required A.C. Power Sources</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. The La Crosse Boiling Water Reactor (LACBWR) Technical Specification (T.S.) 4.3.1, A.C. Sources, Limiting Condition for Operation states: 'As a minimum, the following A.C. electrical sources shall be OPERABLE ... b. Diesel Generator 1A or 1B, aligned to but not energizing, the same essential switchgear bus,....' High coolant temperature on 1A Emergency Diesel Generator (EDG) during the monthly test done on 1/2/97 led to the discovery that the radiator fan breaker was open. It is assumed that it was left open after fan motor meggering on 12/5/96. In this condition, 1A Emergency Diesel Generator (EDG) was technically inoperable. On 12/19/96, the 1B EDG was found to have a leaky engine heater hose and was removed from service for repair. During the hours 1B Emergency Diesel Generator (EDG) was out of service, there were less than the required A.C. power sources available.
4101997001 | Nine Mile Point 2 | 03/26/1997 | 04/25/1997 | 9705050126 | <strong>Technical Specification Violation Caused by Inadequate Response Time Testing of the High Pressure Core Spray Actuation Instrumentation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 26, 1997 at about 1530 hours, with Nine Mile Point Unit 2 (NMP2) in Operational Condition 1 (Power Operation) and the reactor thermal power at approximately 100 percent, Niagara Mohawk determined that NMP2 was in violation of Technical Specification (TS) Surveillance Requirement (SR) 4.0.2, in that required surveillance testing had not been properly performed for a portion of the initiation logic circuit for High Pressure Core Spray (HPCS). section of the circuit had been removed from the surveillance procedures in 1993 as a result of an evaluation that incorrectly concluded that the testing was not required. Because the required surveillance testing could not be completed within 24 hours, NMP2 was in a condition not covered by the TSs and entered TS 3.0.3 at 1530 hours on March 27, 1997. The cause of this event was determined to be inadequate managerial methods in that a 1993 evaluation of surveillance requirements associated with ECCS response time testing was inadequate. The evaluation failed to properly assess the significance of the definition of ECCS Response Time as stated in the TSs, and concluded that response time testing was not required based on information contained in the Nuclear Steam Supply System (NSSS) vendor specification and accident analysis. Corrective actions for this event included declaring HPCS inoperable, performing adequate response time testing of the logic circuit, and reviewing and revising response time testing procedures.
4101997002 | Nine Mile Point 2 | 04/07/1997 | 10/28/1997 | 9711030227 | <strong>Potential Inoperability of Emergency Diesel Generator Service Water Cooling Outlet valves During a Control Room Fire</strong><br /><i>Abstract:&nbsp;</i>On April 7, 1997, NMPC determined that portions of the control circuits for the Division I and II Emergency Diesel Generators (EDG) cooling water outlet valves were not isolated from the control room as described in NMP2 USAR Section 9B.8.2.3. Assuming a control room fire with no other compensatory actions, it could be postulated that either one or both of the EDGs could have been disabled due to a control circuit short which would have disabled the Remote Shutdown Panel (RSP) controls for these valves. As a result of our corrective actions, NMPC identified on May 8, 1997, additional deficiencies in the design of the circuits for 2RHS*MOV4A and 2RHS*MOV4B, minimum flow valves for RHR Pump 1A and 1B and in the evaluation of emergency lighting requirements to achieve cold shutdown. On June 7, 1997, NMPC determined that the Recirculation System pump discharge valves could not be closed locally as required by procedure in the event of a loss of offsite power. The cause of this deviation is an error in the original design and implementation of modifications outlined in the NMP2 USAR Section 9B.8.2.3 with respect to EDG cooling water outlet valves, the RHR minimum flow valves, and the Recirculation System pump discharge valves. This also resulted in not meeting the requirements of 10CFR50 Appendix R, Section III.J. NMP2 Technical Specification LCO 3.3.7.4 Action b was entered until modifications to the EDG cooling water valve circuits were completed. N2-OP-78 has been revised to direct action to provide an alternate means of minimum flow protection for the RHR pumps and to initiate alternate shutdown cooling. Additionally, required emergency lights have been or will be installed in areas requiring manual actions to achieve cold shutdown, including access and egress pathways.
4101997003 | Nine Mile Point 2 | 06/08/1997 | 07/08/1997 | 9707160172 | <strong>Technical Specification Violation Caused by Procedural Non-Compliance due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1997 at 2205 hours, while performing Attachment 3 of procedure N2-OSP-LOG-D001 (Daily Checks Log) in accordance with Technical Specification (TS) Surveillance Requirement 4.8.4.1, circuit 2LAR-PNLU03-12 was found in the energized state. Attachment 3 contains a list of primary containment AC circuits which are required to be deenergized. This particular circuit supplies power to the drywell communication equipment. This was in violation of TS 3.8.4.1, which requires this circuit to be deenergized in Modes 1, 2, and 3 prior to power ascension and following final drywell inspection. The last performance of Attachment 3 was documented as being completed satisfactorily on June 8, 1997 at 1729 hours. The plant changed Operational Conditions from Mode 2 (Startup) to Mode 1 (Run) during the time the circuit was energized. Changing Operational Conditions while the circuit was energized was also a violation of TS 3.0.4, which states that entry into an Operational Condition shall not be made unless the conditions for the Limiting Condition for Operation are met without reliance on provisions contained in the Action requirements. The cause of this event was determined to be personnel error in that self-checking was not adequately applied to verify that the circuit was deenergized. Upon discovery, NMP2 TS LCO 3.8.4.1 was entered, the circuit was deenergized as required by the Action statement, and LCO 3.8.4.1 was exited.
4101997004 | Nine Mile Point 2 | 06/13/1997 | 07/14/1997 | 9707240059 | <strong>Reactor Water Cleanup Isolation on High Differential Flow Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1997, at 1528 hours, Nine Mile Point Unit 2 (NMP2) experienced the actuation of an Engineered Safety Feature (ESF). Specifically, the Reactor Water Cleanup System (WCS) isolated on high differential flow. Filter demineralizer evolutions were in progress at the time. Both divisions of the isolation logic actuated and isolated the inboard and outboard containment isolation valves as designed. The plant was operating in Operational Condition 1 at approximately 95 percent of rated thermal power. The root cause of the event was determined to be personnel error in that procedural steps were not performed correctly. A WCS filter/demineralizer was not properly isolated from the system when its associated effluent strainer was backwashed. As a result, reactor water was drained to the WCS phase separators, causing a system high differential flow. Immediate corrective actions included responding to and verifying WCS system automatic isolation, implementing the required actions of Technical Specification (TS) 4.4.4.c for reactor water continuous conductivity monitoring, and removing the "A" WCS pump (2WCS-P1A) from service for inspection and seal replacement. Additional actions were taken to prevent future recurrence.
4101997005 | Nine Mile Point 2 | 06/23/1997 | 01/30/1998 | 9802130065 | <strong>High Pressure Core Spray System Inoperable due to Failed Unit Cooler</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1997, at approximately 1215 hours, while operating at approximately 95 percent reactor power, the Nine Mile Point Unit 2 (NMP2) Division III switchgear room unit cooler failed, which per station procedures rendered the Division III switchgear and High Pressure Core Spray (HPCS) system inoperable. The cause of the unit cooler failure was degradation of the Custom Termination Module (CTM) in the unit cooler temperature controls. A failure analysis has been completed to determine the cause of the CTM degradation. The results of the failure analysis are inconclusive. The CTM was replaced, successfully post-maintenance tested and the systems were declared operable. The remaining CTMs will be systematically replaced on a planned basis.
4101997006 | Nine Mile Point 2 | 08/04/1997 | 03/13/1998 | 9803230118 | <strong>Plant Shutdown due to Rising Unidentified Leakage</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1997, while operating at 95 percent power, Nine Mile Point Unit 2 (NMP2) experienced a rapid rise in unidentified drywell leakage. Operators immediately commenced an orderly shutdown. The cause of the excessive leakage was determined to be a failed flexible hose connection in the Reactor Recirculation System. The cause of the failed flexible hose connection has been determined to be Intergranular Stress Corrosion Cracking (IGSCC). A modification was installed which eliminated the flexible connection. The remaining 26 hoses susceptible to IGSCC will be removed and capped, or replaced with stainless steel-tubing during refueling outage 6.
4101997007 | Nine Mile Point 2 | 08/13/1997 | 09/12/1997 | 9709220041 | <strong>Failure to Calibrate Hydrogen Recombiner Instruments as Required by Technical Specifications due to Procedure Omission</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1997 at 1300 hours, Nine Mile Point Unit 2 staff identified eight instruments in the Hydrogen Recombiner System (HCS) (four instruments in each division) that had not been calibrated as required by Technical Specification (TS) Surveillance Requirement (SR) 4.6.6.1.b.1. Specifically, the TS SR requires that a channel calibration be performed at least once per 18 months. NMP2 identified this error as part of an ongoing review based on commitments made in response to Generic Letter (GL) 96-01, "Testing of Safety-Related Logic Circuits." The root cause of the event was inadequate written communications when the procedure was initially developed in that these instruments were omitted. A contributing cause was poor work practices in that the deficiency was not identified during subsequent revisions of the procedure. Both divisions of HCS were declared inoperable. TS Limiting Condition for Operation (LCO) 3.0.3 was entered but actions were delayed based on TS SR 4.0.3. The surveillance procedure was revised to incorporate calibration of the control portion of the instrument loops (the required testing that was omitted). Testing was completed and verified that all circuits were within their required tolerances and were capable of performing their intended design functions. Each division of HCS was declared operable when the associated testing was completed for that division. The review of logic circuits is continuing and any future deficiencies will be evaluated.
4101997008 | Nine Mile Point 2 | 08/26/1997 | 09/23/1997 | 9710030162 | <strong>Potential Spurious Actuation of RWCU High Pressure/Low Pressure Interface Valves</strong><br /><i>Abstract:&nbsp;</i>On August 26, 1997, Niagara Mohawk (NMPC) determined that a fire in the Nine Mile Point Unit 2 (NMP2) Reactor Building elevation 328 could potentially have caused spurious actuation of the Reactor Water Cleanup System (RWCU) high pressure/low pressure interface valves. This is contrary to the requirements of 10CFR50 Appendix R Section III G. This condition would occur only if offsite power was available, since these valves automatically close upon loss of power or loss of air. The cause of this event has been determined to be personnel error during the original evaluation of NMP2 for compliance to 10CFR50 Appendix R. Immediate corrective action was to place a fire watch in the affected fire zone.
4101997009 | Nine Mile Point 2 | 08/27/1997 | 09/26/1997 | 9710030161 | <strong>Missed Technical Specification of the Control Room Envelope</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1997, Niagara Mohawk (NMPC) determined that the surveillance test which had been performed to meet Surveillance Requirement (SR) 4.7.3.e.2 of the Nine Mile Point Unit 2 (NMP2) Technical Specifications (TS) did not appropriately include testing of the control building relay room, which is included in the control room envelope as described in the NMP2 Updated Safety Analysis Report (USAR) Section 6.4.2. In addition, it was determined that the procedure did not test the redundant air conditioning units (ACU) in the required lineups. The cause of failure to include the control building relay room in the surveillance and not test the system in the required ACU alignments has been determined to be inadequate technical review. Both divisions of the control room outside air special filter train were declared inoperable. TS limiting condition for operations (LCO) 3.0.3 was entered but actions were delayed based upon TS SR 4.0.3. The surveillance procedure was revised to incorporate testing of the control building relay room and verification of ACU alignments. Testing was completed and the control room outside air special filter trains were declared operable.
4101997010 | Nine Mile Point 2 | 08/27/1997 | 09/26/1997 | 9710030157 | <strong>Main Steam Safety Valve Discovered Not Meeting Required Relief Capacity</strong><br /><i>Abstract:&nbsp;</i>On August 27, 1997, with Nine Mile Point Unit 2 (NMP2) in Operational Condition (OC) 1 (Power Operation) and reactor thermal power at approximately 95 percent, it was determined that NMP2 had operated in violation of Technical Specification (TS) 3.2.2 during previous startups and other power maneuvers. This violation occurred when APRMs were setup to 2 percent lower than required by the TS 3.2.2 action statement, due to the improper application of TS Table 4.3.1.1-1 Note g, RPS Instrumentation Surveillance Requirements. The root cause of these events is inadequate technical review. No immediate corrective actions were required since NMP2 was not operating in a condition requiring the APRM gain adjustment needed to satisfy TS 3.2.2 at the time of discovery. Procedures have been revised to ensure that APRMs are adjusted to greater than or equal to the required setting per TS 3.2.2.
4101997011 | Nine Mile Point 2 | 09/12/1997 | 10/10/1997 | 9710200045 | <strong>Technical Specification Violation of APRM Testing Requirements</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1997, Niagara Mohawk Power Corporation (NMPC) determined that the surveillance testing performed to meet the Nine Mile Point Unit 2 (NMP2) Technical Specification (TS) Surveillance Requirements (SR) 4.3.1.1-2a, 4.3.1.1-2b, 4.3.1.1-2c, 4.3.1.2 and 4.3.1.3 were not met for Average Power Range Monitors (APRMs) channels E and F. The cause of the event is attributed to inadequate written communications (omission of relevant information) when the procedures were developed. A contributing factor is poor work practices in that during the development and revision of the procedures, personnel did not perform an adequate technical review. Immediately upon discovery, operators declared APRM channels E and F inoperable. The applicable procedures were revised and the tests were performed to verify that channels E and F met the SRs. Channels E and F were then declared operable.
4101997012 | Nine Mile Point 2 | 09/22/1997 | 10/21/1997 | 9710310011 | <strong>Missed Technical Specification Surveillance of the Control Building Relay Room Temperature</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1997, Niagara Mohawk Power Corporation (NMPC) determined that the surveillance test which had been performed to meet Surveillance Requirement (SR) 4.7.3.a of the Nine Mile Point Unit 2 (NMP2) Technical Specifications (TS) did not appropriately include verification of the Control Building Relay Room temperature, which is included in the control room envelope as described in the NMP2 Updated Safety Analysis Report (USAR) Section 6.4.2. This condition existed from initial operation of NMP2 to September 30, 1996 when shiftly surveillance procedures were revised to verify relay room temperature as a result of the disposition of Deviation/Event Report (DER) 2-96-2348. The cause of the failure to include the Control Building Relay Room temperature in the surveillance of the control building has been determined to be inadequate technical review. The cause of not identifying this event as reportable when DER 2-96-2348 was dispositioned is inadequate written communication. No immediate corrective actions were required since procedures have been previously revised to verify and log Control Building Relay Room temperature.
4101997013 | Nine Mile Point 2 | 10/29/1997 | 12/01/1997 | 9712170187 | <strong>Prior to 1992, Emergency Switchgear Not Seismically Qualified With Breakers Racked Out</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1997, Niagara Mohawk Power Corporation (NMPC) determined that prior to April 30, 1992, Nine Mile Point Unit 2 (NMP2) had racked out breakers from a 4160 volt switchgear in a manner which did not meet the seismic qualification requirements. This was discovered on October 17, 1997, during a review of NRC Information Notice (IN) 97-53, when an operations engineer discovered that other licensees had reported similar conditions, but could not find a report for NMP2. After a thorough search of records, it was determined that the event should have been reported previously. The cause of the improper racking out of switchgear breakers has been determined to be inadequate translation of engineering requirements into plant procedures. The cause of the failure to report the event in 1992 cannot be determined. Procedures were developed in 1992 to assure the emergency switchgear breakers are manipulated in accordance with seismic qualification requirements.
4101997014 | Nine Mile Point 2 | 11/10/1997 | 12/10/1997 | 9712170496 | <strong>Failure to Adequately Perform Technical Specification Surviellance on Rod Sequence Control System Due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1997, a reactor startup was in progress at Nine Mile Point Unit 2 (NMP2). While performing the surveillance procedure to demonstrate the Rod Sequence Control System (RSCS) operability, a reactor operator raised a concern that performing the test with the Rod Worth Minimizer (RWM) also in service might not adequately demonstrate the RSCS operability. Since the RWM also enforces a rod withdrawal block, verification that the RSCS was actually initiating a rod block could not be verified using the procedure as written. The procedure was stopped, the RWM was bypassed, and the RSCS operability was successfully demonstrated. The root cause of the event was inadequate change management in that change related documents were not developed. The appropriate steps to bypass the RWM were not added to the RSCS procedure when the RWM was modified in 1990. An inadequate technical review of the procedure in 1991 also failed to identify this error. The operability test procedure was revised to bypass the RWM while testing the RSCS rod block function to ensure the RSCS initiates the appropriate rod block. A review of unique system redundancies will be performed to ensure similar discrepancies do not exist. Previous corrective actions and revisions to the modification process and the procedure preparation and review process should prevent recurrence.
4101997015 | Nine Mile Point 2 | 11/14/1997 | 07/02/1998 | 9807140176 | <strong>Opening Between Reactor Building and Reactor Building Auxiliary Bay</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1997, Niagara Mohawk Power Corporation (NMPC) discovered an opening in the wall between the Nine Mile Point Unit 2 (NMP2) Reactor Building stair tower and the North Auxiliary Bay (NAB). The Reactor Building and Auxiliary Bays form the Secondary Containment. This opening allowed the Reactor Building atmosphere to communicate with the NAB and therefore, safety-related equipment located in the NAB could have been exposed to High Energy Line Break (HELB) and Loss of Coolant Accident (LOCA) environment. Since the wall design was to prevent migration between the Reactor Building and the NAB atmosphere, this condition placed the plant outside of the design basis. The cause of this opening has been determined to be improper construction when the plant was constructed. The appropriate Technical Specification was entered for the affected electrical distribution equipment. Corrective actions were to repair the opening, and perform a preliminary inspection of similar walls to verify that there were no other openings. An analysis has been completed to determine the impact of migration through the opening on equipment.
4101997016 | Nine Mile Point 2 | 12/03/1997 | 01/02/1998 | 9801130124 | <strong>Missed Technical Specification Surveillance Requirement 4.3.4.1.2 for ATWS-RPT Trip of LFMG</strong><br /><i>Abstract:&nbsp;</i>On December 3, 1997, Niagara Mohawk Power Corporation determined that the Anticipated Transient Without Scram Recirculation Pump Trip (ATWS-RPT) Logic System Functional Test (LSFT) did not test the Low Frequency Motor Generator (LFMG) trip for high reactor vessel pressure. The LSFT did appropriately test for the LFMG trip on low reactor water level and for the high speed trip to the LFMG of the recirculation pumps on high reactor pressure. Failure to perform an LSFT of the LFMG trip on high reactor vessel pressure is a violation of Technical Specification Surveillance Requirement 4.3.4.1.2. The cause of this event has been determined to be a misinterpretation of the ATWS-RPT regulatory requirements due to analysis deficiency. On November 9, 1997, during forced outage 97-03, the ATWS-RPT LFMG trip was successfully tested.
4121997001 | Beaver Valley 2, Beaver Valley 1 | 01/06/1997 | 10/28/1999 | ML99316031 | <strong>Reactor Trip Due to Main Transformer Ground Protection Relay</strong><br /><i>Abstract:&nbsp;</i>On 1/6/97, at approximately 0556 hours, while in Mode 1 at approximately 98% power, Unit 2 experienced a reactor trip caused by a turbine trip due to Operation of Main Transformer (MT) Ground Protection Relay 59-202G, which actuated MT Auxiliary Relay P7~202Xl. Post- trip control and protection systems functioned correctly, plant parameters were established within normal control bands, and the plant was placed in shutdo~~. NRC 4-hour notification of this event was made, at approximately 0616 hours (same day). The root cause of this event is inadequate design implementation of relay 59-2020, which was in service during operation other than MT backfeeding, since initial Unit startup. Actuation of relay 59-2020 is attributed to an arc to ground in the Main Unit Generator (MUG) when one of the air diffuser screens on the MUG 'B' phase Flexible Links Compartment (FLC) became detached, due to failed support welds, and momentarily contacted the MUG 22 kilo- volt (KV) isophase bus. Relay 59-202G was functionally tested and found acceptable. Other protective relays which could have actuated in response to an actual 22 KV ground fault were tested with no anomalies noted. The relay setting sheet and Operating procedures for relay 59-2020 were revised to ensure the relay is only in service during MT backfeeding. The corresponding Unit 1 relay setting sheet and procedures were reviewed and determined to be correct. The failed air diffuser screen was reattached with bolting and the other Unit 2 air diffuser screens were fastened with similar bolting. Unit 1 utilizes a different design for the MUG isophase leads box air diffuser screens. During the next Unit 1 refueling outage, the Unit MUG FLC will be inspected to ensure no loose components in the compartment.
4121997002 | Beaver Valley 2, Beaver Valley 1 | 01/11/1997 | 02/10/1997 | 9702200127 | <strong>Technical Specification Required Shutdown Due to Missing or Degraded Recirculation Spray System Pump Flood Seals</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 11, 1997, at 1550 hours, while in Mode 3 at 0% reactor power, Beaver Valley Power Station (BVPS) Unit 2 entered Technical Specification 3.0.3 for a cooldown to Mode 5. Based on engineering review, it was determined that design basis requirements for flood protection were not maintained. It was identified that Recirculation Spray System (RSS) Safeguards Room flood protection seals were not in accordance with the Updated Final Safety Analysis Report (UFSAR). External penetration seals were missing for all 4 RSS pumps and 3 of 4 internal penetration seals were degraded. Given the condition of these flood protection seals, equipment in the Safeguards Building required for long-term recirculation following a Design Basis Accident (DBA) may not be capable of performing its intended function, assuming a design basis flood (Probable Maximum Flood) event occurred. The causes of the non-conforming condition of the RSS flood seals were determined to be incomplete construction contractor documentation and the lack of overall knowledge of flood protection by the RSS flood seal installation crew. The plant was cooled down to Mode 5 on January 12, 1997 at 2205 hours. The missing external RSS flood protection seals were installed. The degraded internal RSS flood protection seals were repaired. An extensive walkdown and inspection of selected Unit 1 and 2 flood protection hydrostatic seals was performed. The RSS pump cubicle deep manway hatch flood protection seals were identified as degraded during the walkdown and were subsequently repaired. An immediate report of this condition was made on January 11, 1997, at 1741 hours, pursuant to the requirements of 10CFR50.72(b)(1)(i)(A) and 10CFR50.72(b)(2)(i). This report is being made pursuant to the requirements of 10CFR50.73(a)(2)(i)(A), 10CFR50.73(a)(2)(i)(B), and 10CFR50.73 (a)(2)(ii)(A). The plant was cooled down to Mode 5 based upon a conservative management decision. It was decided that, although the flood seal repairs could have been made in Mode 3, cooldown to Mode 5, where the RSS is not required t
4121997003 | Beaver Valley 2 | 05/21/1997 | 04/21/1998 | 9805050004 | <strong>Technical Specification 3.0.3 Entry Due to Inoperability of Both trains of the Supplemental Leak Collection and Release System</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1997, the A Supplemental Leak Collection and Release System (SLCRS) exhaust air filter train (TRAIN) was removed from service for maintenance in accordance with Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.8.1. On May 21, in order to allow the installation of test equipment onto TRAIN A, the B SLCRS TRAIN was removed from service for a four minute interval by shutting off its fan and placing the control switch in pull-to-lock. It was necessary to have both TRAINS out of service because leaking suction ventilation dampers on both trains allowed a vacuum to be created on the A TRAIN whenever the B TRAIN was in service. Opening the A TRAIN housing doors under these conditions could create the risk of personnel injury and equipment damage. By stationing a licensed operator at the control switch for the B train fan who would manually restart it if needed, Operations personnel took credit for this train as being operable. The following operating shift was requested to remove the B train from service while the A train was still out of service for maintenance in order to remove the previously installed test equipment. This request was denied pending further review. A later reportability review of this event determined that both SLCRS TRAINS were inoperable during the period that the B TRAIN control switch was in pull-to-lock, and this required entry into Technical Specification 3.0.3. A review of all SLCRS surveillance tests to determine if the identified hardware deficiency resulted in entry into TS 3.0.3 revealed a total of eight tests (3 Unit 1 airflow and filter efficiency BVTs, 4 Unit 2 airflow, filter efficiency, and charcoal test sample removal BVTs, and 1 Unit 2 fire system testing OST) that procedurally authorize shutting down both SLCRS filter train exhaust fans on a unit simultaneously in order to open filter access doors. A review of Unit 1 and Unit 2 BVT past performances has revealed instances of both fans being shut down simultaneously on both units. The cause of this event is the failure of station personnel to recognize that operating in this condition constitutes a conditio prohibited by Technical Specifications. This resulted from inappropriate application of compensatory actions. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(I)(b), condition or operation prohibited by TS.
4121997004 | Beaver Valley 2 | 09/11/1997 | 09/11/1998 | 9809220275 | <strong>Four Containment Isolation Valves Not Tested in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1997, at 0900 hours, Beaver Valley Power Station (BVPS) Unit 2 was in Mode 1 at 100% power. During a Containment Isolation Valve (CIV) tables in the Updated Final Safety Analysis Report (UFSAR) and the Licensing Manual (LRM), the four CIVs for penetrations 14 and 25 were noted to have a stroke time limit and a Containment Isolation Phase B (CIB) actuation listed in both the UFSAR and the LRM. This review was performed as a follow-up corrective action in response to Licensee Event Report (LER) 1-97-019-00, "Containment Penetration Check Valves Not in Accordance with the Design Basis." Although these valves are listed in CIV tables which indicate they are automatically actuated and tested, they have not been stroke time tested or stroked via a CIB signal since 1993, when a design change was implemented under a Technical Evaluation Report (TER) to maintain these valves administratively closed. There were no automatically or manually initiated safety system actuations in response to this event. Technical Specifications (TS) require, at least once per 92 days, in Modes 1, 2, 3 and 4, power operated or automatic containment isolation valves which are testable during plant operation to be cycled through a complete cycle of full travel. TS also require, at least once per 18 months, during Cold Shutdown or Refueling Mode: 1) verification that on a Phase B Containment Isolation (CIB) test signal, each Phase B isolation valve actuates to its isolation position and 2) cycling each valve through at least one cycle of full travel and measuring the isolation time. The tables that list the CIVs impacted by these requirements were relocated from the TS to the LRM by an amendment. Contrary to TS requirements. CIVs 2SWS-MOV-153-1, 153-2, 154-1 and 154-2, although still included in the CIV table, are not tested in accordance with the applicable surveillance requirements. This is a verbatim compliance issue. Failure to comply with TS Limiting Condition for Operation (LCO) requirements by failing to implement the associated surveillance requirements is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). The apparent cause of this event was inadequate change management. The change management process provided an inadequate evaluation and interpretation of the impact upon the plant's licensing basis documents effected by changing the CIVs for containment penetrations 14 and 25 from active valves with CIB closure capability to normally locked shut valves. The decision to terminate TS surveillances was not supported by sufficient and adequate justification, since the UFSAR and TS were not revised to reflect the configuration of the CIVs. An approved safety analysis was performed to justify the TER which implemented closure of these valves. These valves are de-energized and locked shut and are verified shut in accordance with plant operating and surveillance procedures. Penetrations 14 and 25 remain fully operable and capable of performing their required containment function. Based upon this information, there were no implications to the health and safety of the public as a result of this event.
4121997005 | Beaver Valley 2 | 10/15/1997 | 11/14/1997 | 9711200234 | <strong>Conditions Prohibited by Technical Specifications During Routine 4.16kV and 480 Volt Emergency Bus Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On October 15, 1997, with the Beaver Valley Power Station Unit 2 in Mode 1 at 100 percent reactor power, it was determined by the Generic Letter 96-01 review team that the routine monthly channel functional surveillance testing for four Engineered Safety Feature Actuation System (ESFAS) Instrumentation Functions results in conditions prohibited by the Unit 2 Technical Specifications (T.S.). During routine monthly channel functional testing of three ESFAS functions, "Loss of Power, 4.16 kV Emergency Bus Undervoltage (Trip Feed)," "Loss of Power, 4.16 kV Emergency Bus (Degraded Voltage)" and "Loss of Power, 480 Volt Emergency Bus (Degraded Voltage)" both channels per bus were made inoperable. For each function this is a condition beyond the Limiting Condition for Operation (LCO) and the associated ACTION requirement does not address the situation. Therefore, each monthly performance of these channel functional tests constituted an inadvertent entry into T.S. 3.0.3. Additionally, during the routine monthly testing of the ESFAS function "Loss of Power, 4.16 kV Emergency Bus Undervoltage (Start Diesel)" the required entry into the associated T.S. ACTION requirement was not made. The channel functional tests did adequately verify the operability of the ESFAS functions; therefore, no operability concerns existed. The apparent cause of this event was primarily the inadequate design of undervoltage test panels used to perform the monthly testing. The test panels disabled both channels per bus of the "Trip Feed" function and both "Degraded Voltage" functions, while in "TEST". Failure to recognize this design inadequacy resulted in inadequate surveillance procedures. Additionally, the procedure failed to require entry into the associated action statement while testing the "Start Diesel" function. An alternative method of performing the monthly testing was implemented to prevent future inadvertent entries into T.S. 3.0.3. This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant's T. S. The non-compliances only existed for the short period of time each ESFAS function was actually in "TEST". The opposite safety train was not in test and should have been capable of performing any required safety function. No actual failure to perform a safety function occurred. Based upon this information, there was no safety implication to the health and safety of the public as a result of this event.
4121997006 | Beaver Valley 2 | 12/01/1997 | 12/23/1997 | 9801060127 | <strong>Technical Specification Requirements for 4.16 KV Bus Undervoltage Trip Feeder Breaker Function ESF Response Time Not Met</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1997, at approximately 1515 hours, Beaver Valley Power Station Unit 2 was in Mode 1 at 100% power. During a review of 4.16 KV undervoltage relay testing, it was identified that the Technical Specification (TS) requirements for the Engineered Safety Feature (ESF) response time of the fast undervoltage trip function had not been met. This is an operation or condition prohibited by TS and is reportable pursuant to the requirements of 10CFR50.73(a)(2)(i). There were no automatically or manually initiated safety system actuations in response to this event. This event was not applicable to Unit 1. It was identified by System and Performance Engineering (SPED) that the time delays for four undervoltage relays in the 4.16 KV loss of voltage trip feeder function had been set at values in the mid band of their acceptable range. As a result, the overall ESF response time for the 4.16 KV loss of voltage trip feeder function (TS limit 1 +/- 0.1 second) was exceeded for both trains. Train "B" undervoltage relay time delays had been set to values which caused the ESF response time for the fast undervoltage trip function (the longest was 1.178 seconds) to be exceeded on October 25, 1997. Train "A" undervoltage relay time delays had been set to values which caused the ESF response time for the fast undervoltage trip function (the longest was 1.150 seconds) to be exceeded on November 5, 1997. The apparent cause of this event was the fact that the relay calibration procedures for the undervoltage relays in the 4.16 KV loss of voltage trip feeder function were not revised by SPED to specify time delay values which provide for compliance with TS requirements for the associated ESF function response time. SPED had historically relied upon verbal communications with the Relay Crew, rather than revising specific procedures, to convey the necessity for setting the time delays at the lower end of the range in order to meet this TS requirement for ESF response time. Subsequent to evaluation by the Nuclear Shift Supervisor (NSS) at 1728 hours, it was identified that TS response time requirements for both the A and B trains of the 4.16 KV undervoltage trip feeder function were not met, and that the unit had entered TS LCO 3.0.3 at 1515 hours on December 1, 1997. The four relays were recalibrated and set in the lower end of their range to achieve compliance with TS requirements. TS 3.0.3 requirements were satisfied at 1707 hours on December 1, 1997. The Maintenance Surveillance Procedures (MSPs) for these relays have been revised to provide the acceptable range for the time delay settings. This event is significant since a TS requirement was not met. However, although the ESF response time for the 4.16 KV loss of voltage trip feeder function was exceeded, there were no safety implications to the health and safety of the public. A safety evaluation was performed pursuant to 10CFR50.59 to support a TS amendment request which demonstrates that a change in ESF response time function from 1 +/- 0.1 seconds to < 1.3 seconds is acceptable.
4121997007 | Beaver Valley 2 | 12/05/1997 | 12/30/1997 | 9801080092 | <strong>Inadequate Routine Surveillance Testing of the Power Range, Neutron Flux High Positive Rate Reactor Trip Function</strong><br /><i>Abstract:&nbsp;</i>On December 5, 1997 at 1530 hours, as a result of the Generic Letter (GL) 96-01 review effort, it was determined that the routine surveillance testing for the Unit 2 Reactor Trip System (RTS) Instrumentation Function "Power Range, Neutron Flux High Positive Rate" was inadequate. During both the Channel Functional Test and the Channel Calibration of that function, performed on a quarterly frequency and a once every 18 month frequency, respectively, a portion of the channel circuitry was not being tested. Upon the determination that the existing surveillance testing for the RTS function, "Power Range, Neutron Flux High Positive Rate" was inadequate, at 1530 hours on December 5, 1997, Unit 2 declared all four channels of this function inoperable and entered Technical Specification (T.S.) 4.0.3. No channels for this function being operable is a condition not defined by the T.S.; therefore, T.S. 3.0.3 applied. T.S. 4.0.3, however, allows the actions of T.S. 3.0.3 to be delayed for up to 24 hours to permit the completion of a surveillance requirement. The apparent cause of this event was procedural deficiencies due to a lack of awareness during procedural development to ensure adequate overlap testing. The applicable Unit 2 surveillance procedure was revised on December 5, 1997 to incorporate additional testing to adequately test the portion of the Power Range, Neutron Flux High Positive Rate function that was not being tested. This additional testing was successfully completed using the revised procedure. T.S. 4.0.3 was exited at 2216 hours on December 5, 1997. This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i) as an operation or condition prohibited by Technical Specifications. There were no automatically or manually initiated safety system responses as a result of this event. No loss of safety function was identified as a result of this event. Based on this information, there were no safety implications to the health and safety of the public as a result of this event.
4121997008 | Beaver Valley 2, Beaver Valley 1 | 12/16/1997 | 03/27/1998 | 9804090013 | <strong>Failure to Meet Single Active Failure Criteria For C. R. Emergency Ventilation System Results in Entry Into T. S. 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1997, with Unit 2 operating in Mode 1 at 100 % power, it was determined that the Control Room Emergency Ventilation System did not meet single active failure criteria as specified in the UFSAR and design bases. Review determined that certain 'A' Train component failures could induce failures in 'B' Train. As a result of this information, Unit 2 entered Technical Specification (TS) Limiting Condition for Operation 3.0.3 and commenced shutting down to Mode 3. This was reported pursuant to the requirements of 10CFR50.72(b)(1)(I)(A) as the initiation of any nuclear plant shutdown required by the plant's TS. Under the LER Rule it is also reportable pursuant to the requirements of 10CFR50.73 (a)(2)(I)(A) as the completion of any nuclear plant shutdown required by the plant's TS, as well as 10CFR50.73(a)(2)(I)(B) any operation or condition prohibited by the plants' TS, since it involved entry into TS 3.0.3. There are two root causes for this event. The design of the control system for pressure differential switch 2HVC*PDS241, located between the discharge of Train "A" Control Room Filtered Air Intake Fan, and the common suction duct, a component in the original plant design of the Control Room Emergency Ventilation System was less than adequate. Also, independent reviews of the Control Room Emergency Ventilation System, performed in 1982, 1984, and 1986 by the architect/engineer, were less than adequate in that these evaluations did not recognize that the current design was susceptible to several credible single failures. As completed corrective actions, a scoping assessment of the potential single active failures to equipment in the Control Room Emergency Ventilation System was performed, and Design Change Request packages were completed to modify the Unit 2 Control Room Emergency Pressurization System to correct single failure concerns and to prevent multiple starts of the Control Room Filtered Air Intake Fan 2HVC*FN241B. A detailed extent of condition review for a sampling of similar QA Category 1 ventilation systems was performed. Should a single active failure cause both Unit 2 Control Room Emergency Ventilation Trains to fail while the system is required to automatically initiate and function (as a result of a Containment Isolation B or Control Room High-High radiation signal), Control Room habitability will be negatively impacted. Although the Control Room complex is common for ventilation purposes, and although Unit 1 has a separate emergency ventilation system, Unit 2 takes no licensing credit for the Unit 1 system. The Unit 1 Emergency Ventilation System could have been manually initiated in the event that a Design Basis Accident occurred at either unit.
4121997009 | Beaver Valley 2 | 12/18/1997 | 01/20/1998 | 9801270057 | <strong>Missed Surveillance of the Gaseous Waste Storage Tank Radioactive Material Quantity Determination</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1997, at 0400 hours, with Beaver Valley Power Station (BVPS) Unit 2 in Mode 5 at 0% reactor power level, it was discovered that a Technical Specification (TS) required surveillance of the quantity of radioactive material contained in the Gaseous Waste Storage Tanks (GWST) was missed. On 12/15/97 at 0848 hours, 2GWS-RQ104A, the radiation monitor for the fill header to the GWSTs, was removed from service for the routine performance of Maintenance Surveillance Procedure 2MSP-43.07-1, and was noted in the Operations Shift Log with no TS actions required. When this monitor is out of service, the GWST's pressures are logged once per shift per the Health Physics (HP) shift logs. The shift log procedure provides instructions to sample the tank at least once per 24 hours when radioactive material is being added to the tank as observed by increases in the tank pressure. On 12/16/97 at 1836 hours, operators commenced degassing of the Reactor Coolant System (RCS) to the GWSTs. The pressures of the GWSTs were recorded on the HP shift log, including the increase in tank pressures. However, the shift radiation technician failed to follow the log instructions to sample the GWSTs when the increases in tank pressures were observed. On 12/18/97 at 0400 hours, another shift radiation technician discovered the missed sample of the GWSTs, and a sample of the tanks was immediately taken on 12/18/97 at 0405 hours. The sample analysis was completed on 12/18/97 at 0557 hours, and was determined to be well below the TS limit of 19,000 curies. The completion of TS Surveillance Requirement (SR) 4.11.2.5.1 was due to be performed by 12/18/97 at 0246 hours including the addition of a 25% grace period. This requirement was not completed until 12/18/97 at 0557 hours, which was 3 hours, 11 minutes past due. There were no automatically or manually initiated safety system responses as a result of this event. This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B) as "Any operation or condition prohibited by the plant's Technical Specifications," since SR 4.11.2.5.1 was not performed within the required time period. The apparent causes of the event were: 1. personnel error by the shift radiation technician who failed to follow the instructions on the HP shift log, 2. the procedural step for verifying if radiation monitor 2GWS-RQ104A was in service in Operating Manual procedure 2OM-19.4.G was inadequate in that it only checked for a "green" status light on the control panel, and 3. the operating crews failed to recognize the TS impact upon removing 2GWS-RQ104A from service. A sample of the radioactive material in the GWSTs was taken on 12/18/97 at 0405 hours. Based on the results of this sample, the quantity of radioactive material in the GWSTs was well below the TS limit of 19,000 curies; therefore, there were no implications to the health and safety of the public as a result of this event.
4121997010 | Beaver Valley 2, Beaver Valley 1 | 12/19/1997 | 01/16/1998 | 9801220359 | <strong>Lack of Electrical Isolation in the Unit 2 Emergency Diesel Generator Room Ventilation System Temperature Control Circuits</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1997, at 1335 hours, as a result of an extent of condition review for a previous condition report at Beaver Valley Power Station (BVPS), it was determined that the Unit 2 Emergency Diesel Generator (EDG) Ventilation System temperature control circuitry did not have electrical isolation between the Class 1E and non-Class 1E portions of the circuit. Both Units were in Mode 5 at the time. As a consequence, it was postulated that a failure in the non-safety related portion of the control circuit could potentially degrade the safety related portion of the circuit and prevent it from performing its safety function. This function is to maintain the ambient air temperature in the EDG rooms within design limits while the EDGs are operating. In addition, it was concluded that without electrical isolation between the Class 1E and non-Class 1E portions of the involved circuits, they were not completely Quality Assurance Category 1 circuits and should not be credited with being capable of performing their safety related function. At 1335 hours on December 19, 1997, both Unit 2 EDGs were declared inoperable and the appropriate Technical Specification (T.S.) action statement was entered. Additionally, a prohibition was placed on Unit 1 entering Mode 4 until this issue was resolved. With both Unit 2 EDGs inoperable, Unit 1 could not meet its T.S. Limiting Condition for Operation (LCO) for its Control Room Emergency Habitability System. Unit 1 was already in the associated T.S. action statement for this LCO as described in BVPS Unit 2 LER 97-008-00. The apparent cause of this event was an inadequate design of the subject EDG ventilation system temperature control circuits during the original plant construction for Unit 2. Temporary modifications were completed on December 20, 1997 to address the lack of electrical isolation. Following completion of the temporary modifications, both Unit 2 EDGs were declared operable at 1816 hours on December 20, 1997. A permanent design change was completed by December 31, 1997 which added the required electrical isolation to these circuits. This event is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. A four-hour non-emergency report of the event was made on December 19, 1997 at 1440 hours pursuant to the requirements of 10 CFR 50.72(b)(2)(i). This event identified a lack of electrical isolation that could potentially have resulted in the degradation or failure of one or both of the Unit 2 EDGs. However, no actual loss of safety function occurred. Based upon this information, there were no safety related implications to the health and safety of the public as a result of this event.
4121997011 | Beaver Valley 2, Beaver Valley 1 | 12/29/1997 | 01/28/1998 | 9802040009 | <strong>Inadequate Electrical Isolation in Secondary Process Rack Circuitry Due to Design Error</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1997, at 1940 hours, as a result of an extent of condition review at Beaver Valley Power Station (BVPS) for BVPS Unit 2 Licensee Event Report 97-010-00, it was determined that a design error existed in the Unit 2 safety related Secondary Process Racks. This resulted in inadequate electrical isolation between non-Class 1E circuits contained in the racks and the Class 1E power supplies, which power all circuits in the racks. Consequently, a fault in the non-Class 1E circuits could potentially trip the Class 1E power supplies, thereby disabling Class 1E circuits that these power supplies also feed. Unit 1 was in Mode 3 and Unit 2 was in Mode 5 at the time of this event. At 1940 hours on December 29, 1997, the appropriate Unit 2 Technical Specification (T.S.) action statements were entered and both Unit 2 Emergency Diesel Generators (EDGs) were declared inoperable due to the potential to disable EDG room ventilation system temperature control circuits. These circuits are required to maintain the EDG room ambient air temperature within design limits while the EDGs are operating. Additionally, with both Unit 2 EDGs declared inoperable, Unit 1 could not meet its T.S. Limiting Condition for Operation (LCO) 3.7.7.1.a for its Control Room Emergency Habitability Systems and entered the applicable T.S. action statement at 1940 hours on December 29, 1997. Since neither Unit 2 EDG was restored to operability within 7 days, a Unit 1 shutdown to Mode 5 was required. This was completed by 1052 hours on January 4, 1998. Based on subsequent corrective actions to correct the identified electrical isolation deficiencies, Unit 2 EDG 2-1 was declared operable at 0219 hours on January 15, 1998. This removed any T.S. restrictions on Unit 1 as a result of this event. All necessary corrective actions to restore equipment operability and to remove any T.S. restrictions from Unit 2 as a result of this event were completed by 1350 hours on January 26, 1998 with Unit 2 still in Mode 5. The apparent cause of this event was an error in the design of the Unit 2 safety related Westinghouse 7300 Series Secondary Process Rack circuitry. This design error occurred during the original plant construction of Unit 2. The inadequate electrical isolation identified in the Unit 2 Secondary Process Racks is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. The required shutdown of Unit 1 for failure to satisfy the applicable action statement for T.S. LCO 3.7.7.1.a is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(A) as the completion of any nuclear plant shutdown required by the plant's T.S. Although this event identified inadequate electrical isolation in the Unit 2 Secondary Process Racks, no actual loss of safety function occurred. Based upon this information, there were no safety related implications to the health and safety of the public as a result of this event.
4131997001 | Catawba 1, Catawba 2 | 02/10/1997 | 03/12/1997 | 9703190044 | <strong>Unanalyzed Postulated Single Failure Affecting the Steam Generator Tube Rupture Analysis</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Unit Status: Units 1 and 2 were in Mode 1, Power Operation, at 100% power. Event Description: On February 10, 1997, at 1835 hours, the Nuclear Regulatory Commission was notified of a potentially more limiting single failure than previously analyzed with regard to Steam Generator (S/G) Tube Rupture (SGTR) accidents. Engineering, during a dose analysis review of chapter 15 of the Updated Final Safety Analysis Report (UFSAR), identified single failures which would cause the loss of power to two steam generator power operated relief valves (PORVs). Subsequent evaluation of the SGTR scenario determined that the recently identified failures are more limiting with respect to S/G overfill and that Technical Specification 3/4.7.1.6 is non-conservative. Administrative restrictions were implemented to ensure adequate margin to S/G overfill and ensure offsite dose is bound by the latest dose analysis. Root Cause: The cause of this event is attributed to less than adequate single failure analysis of S/G PORV power supplies during Catawba's 1987 implementation of the WCAP-10698 analysis for SGTR. Corrective Action: A proposed amendment to T/S 3/4.7.1.6 and the UFSAR has been submitted to the NRC. Planned corrective action includes additional PORV failure mode analysis, final SGTR dose analysis, and common cause analysis of similar design bases events.
4131997002 | Catawba 1 | 04/03/1997 | 06/09/1997 | 9706170074 | <strong>Feedwater Containment Isolation Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 - mode 1, power operation, 100% power. Event Description: On 05/06/97 Engineering determined that Feedwater Containment Isolation valve 1CF-51 was inoperable on 04/03/97 from 0608 to 2318 due to actuator low nitrogen pressure. Technical Specification 3.6.3 allowable action times for that inoperability were exceeded. Root Cause: The Operator Aid Computer (OAC) Alarm Response information was inadequate, because the need for immediate action was not identified. A contributing factor was the close proximity of the alarm value (2080 psig) to the minimum allowed operability pressure (2050 psig). Corrective Action: Nitrogen pressure was restored to an operable value. The OAC Alarm Response has been revised to require determination of the nitrogen pressure within 4 hours of the alarm. Planned Corrective Actions are to determine if there are other OAC Technical Specifications alarm responses that need enhancement and correct as needed. The low nitrogen pressure alarm setpoint will be evaluated to determine if the setpoint should be increased.
4131997003 | Catawba 1, Catawba 2 | 05/15/1997 | 06/16/1997 | 9706230432 | <strong>Auxiliary Feedwater System Found Outside of Design Basis</strong><br /><i>Abstract:&nbsp;</i>Event Description: on 5/15/97, with both units in Mode 1, at 100% power, engineering was reviewing the hydraulics of the non-safety suction source to the Auxiliary Feedwater (CA) pumps, when a problem was discovered that would lead to the introduction of air into the suction of the CA pumps. The event scenario is a dual unit Loss Of Offsite Power (LOOP) coincident with a steam line or feedwater line break on one unit occurring prior to transfer of suction for the CA pumps to the safety grade assured source, Nuclear Service Water (RN). Root Cause: This event is attributed to an unanticipated interaction of systems or components. The limiting design criteria, for ensuring the CA pumps receive a constant water supply, was assumed to be the ability of the CA System to survive a break in the nonseismic condensate piping at a point downstream of where the three condensate sources tie together. Because this was the criteria used, no transient analysis of the individual sources was performed. Corrective Actions: Following the initial evaluation on 5/15/97, the CACST was isolated pending further evaluation. Engineering, with off-site assistance will continue evaluation of the condensate quality suction sources issue to ensure that all possible configuration concerns have been identified and evaluated, and that all necessary corrective actions have been taken.
4131997004 | Catawba 1, Catawba 2 | 05/14/1997 | 07/02/1998 | 9707090368 | <strong>Inadequate Surveillance Resulting From a Conflicting Technical Specification Limiting Condition of Operation and Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Units 1 and 2 were in Mode 1, Power Operation, at 100% power. Event Description: On June 6, 1997, Engineering determined that existing station procedures were not adequate to ensure the requirements of Technical Specification (T/S) surveillance 4.5.3.2 for Reactor Coolant (NC) system overpressure protection in Mode 4, Hot Shutdown, are satisfied. Follow-up analysis has determined that adequate pressure relief capacity was available to ensure the NC and Residual Heat Removal (ND) systems were protected from overpressure concerns. Root Cause: This event is attributed to the interpretation of conflicting T/S requirements. Conflict exists between surveillance requirement 4.5.3.2 and T/S 3.5.3 in that the Limiting Condition for Operation (LCO) specifies a maximum of one Chemical and Volume Control (NV) system pump and one Safety Injection (NI) system pump operable in Mode 4, whereas the surveillance verifies all charging and safety injection pumps are inoperable except for one NV pump. This specification was interpreted in 1988 to be met when the requirements of the LCO are satisfied. Corrective Action: Station procedures have been revised to ensure T/S surveillance 4.5.3.2 is met. Planned corrective actions include a T/S amendment crediting the use of the ND suction relief valves for overpressure protection which will allow the operability of a second charging pump when less than 285 degrees Fahrenheit in Mode 4 and causal analysis to evaluate events involving the T/S surveillance program.
4131997005 | Catawba 1, Catawba 2 | 06/23/1997 | 07/23/1997 | 9707290114 | <strong>Violation of Technical Specification 4.0.5 Due To Inadequate Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>EVENT DESCRIPTION: On June 23, 1997, both units were in mode 1. During a site review of the residual heat removal system it was determined that an Emergency Core Cooling System check valve surveillance procedure was inadequate. The surveillance procedure, performed each refueling outage, to ensure adequate forward flow through the valves, did not check for reverse flow prevention. Prevention of reverse flow for certain check valves is a requirement of the Inservice Test Program referred to in technical specification (T/S) 4.0.5. ROOT CAUSE: The root cause of this event is an inadequate procedure. The procedure adequately tested each valve for flow, but system alignments were inadequate to demonstrate reverse flow prevention. In addition, the procedure did not indicate that one of the purposes was to test for reverse flow prevention, nor did it contain acceptance criteria, against which check valve performance could be evaluated. CORRECTIVE ACTIONS: Corrective actions included successful testing of the affected check valves for reverse flow prevention, initiation of a comprehensive evaluation of the Inservice Test Program to identify and correct any additional immediate testing concerns, and a planned corrective action to revise the test procedures for these valves under the Inservice Test Program.
4131997006 | Catawba 1, Catawba 2 | 08/04/1997 | 09/25/1997 | 9709300096 | <strong>Missed Technical Specification Surveillances on P-11 and P-13 Permissive Interlocks Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 and 2 were in mode 1, power operation, 100% power. Event Description: On August 4, 1997, Catawba was notified via the Operating Experience Program of a potential problem with testing of the P-11 permissive interlocks. Engineering determined that under certain normal operating conditions, surveillance procedures did not fully meet the intent of Analog Channel Operational Test (ACOT) for P-11. It was later determined that there was a similar problem with testing of the P-13 permissive interlocks. Technical Specifications 4.3.2.1 and 4.3.1.1 were violated for P-11 (Unit 1 and 2) and P-13 (Unit 2 only) respectively, when ACOT procedures were performed that did not adequately test the permissive functions. Root Cause: This event is attributed to procedures that were inadequate to test P-11 and P-13 under varied plant conditions. Corrective Action: Unit 1 and 2 P-11 and Unit 2 P-13 permissive interlocks were tested successfully. The ACOT procedures for P-11 were revised. Planned corrective actions include necessary changes to the P-13 ACOT procedures that will allow testing with the turbine above 10% turbine power.
4131997007 | Catawba 1, Catawba 2 | 10/23/1997 | 11/21/1997 | 9711280298 | <strong>Technical Specification 3.2.5 Is Inadequate For Reduced Flow Operation</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Both units were in Mode 1 (Power Operation), 100 percent power. Event Description: While performing engineering support work for McGuire and Catawba Nuclear Stations, an error was discovered in the analytical bases for Power Operation at less than the minimum Technical Specification (TS) Reactor Coolant (NC) system flow. Power level restrictions, based on maintaining the initial DNBR margin, may not be adequate for all UFSAR Chapter 15 transients. Event Cause: The cause of this event is deficiency of analysis. Analyses performed by the licensee for the Catawba revision to TS 3.2.5 were inadequate to support the curve of Reactor Coolant System Total Flow Rate versus Rated Thermal Power. These analyses were based on the inadequate analyses provided to McGuire by a vendor. Corrective Action: A TS interpretation was issued that prohibited reduced power operation by TS figure 3.2-1, if actual NC flow drops below the TS minimum. Planned corrective actions include revising TS 3.2.5 to provide operational limits if actual NC flow drops below the minimum requirement.
4131997008 | Catawba 1, Catawba 2 | 11/11/1997 | 12/11/1997 | 9712170456 | <strong>Inadequate Solid State Protection System Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Units 1 and 2 were in Mode 1, Power Operation, at 100% power. Event Description: During an Engineering review on November 11, 1997, Catawba and McGuire Nuclear Stations discovered that an inadequate vendor test design prevented the current Solid State Protection System (SSPS) bimonthly surveillance test method from adequately testing three circuits involving Universal Logic Boards in a memory configuration. Engineering identified a postulated internal card subcomponent failure which would not be detected during bimonthly testing. Catawba and McGuire immediately entered Technical Specification 4.0.3 which provided twenty four hours for both plants to complete the surveillance. Catawba and McGuire, in consultation with the vendor of the SSPS, developed a modified test which fully verified proper operation of the SSPS logic cards and compensated for the identified test design deficiency. Appropriate surveillance procedures were revised. On November 12, 1997, both trains on each unit at Catawba and McGuire were tested satisfactorily. The Technical Specification 4.0.3 action statement was exited well within the twenty four hour deadline. Event Cause: The cause of this event is inadequate test design supplied by the vendor. The test procedures were supplied with the SSPS. Corrective Action: The surveillance procedures for both SSPS trains on each Catawba unit were revised. The SSPS trains on both Catawba units were successfully tested.
4131997009 | Catawba 1, Catawba 2 | 11/18/1997 | 05/17/1999 | 9905240086 | <strong>Unanalyzed Postulated Single Failure Affecting Steam Generator Tube Rupture Analysis</strong><br /><i>Abstract:&nbsp;</i>During a design review, a more limiting Steam Generator (S/G) Tube Rupture (SGTR) accident scenario than previously analyzed in Updated Final Safety Analysis Report was identified. In this scenario, the most limiting single failure is loss of one of the 125 VDC Vital I&C Distribution Centers, EDE or EDF, resulting in the loss of control power to two S/G power operated relief valves (which was previously identified as most limiting) as well as inability to remotely isolate auxiliary feedwater flow to two S/Gs. Local manual action within a short time frame would be necessary to prevent S/G overfill. This event was caused by a less than adequate review when implementing the generic Westinghouse SGTR analysis methodology in 1987. This event is similar to an event reported in Licensee Event Report 413/97-001. Administrative controls on primary and secondary coolant specific activities have been put in place to ensure offsite doses are bounded by guideline values. A review of equipment needed to prevent S/G overfill to ensure equipment failure effects are appropriately reflected in accident analyses was completed. Two additional categories of single failures with the potential to lead to steam generator overfill were identified. Future corrective actions include a plant modification, further evaluation of certain failures, and submittal of a license amendment, based on risk informed techniques, to exclude certain failures from the plant's licensing basis.
4131997010 | Catawba 1 | 12/29/1997 | 01/26/1998 | 9802040269 | <strong>Reactor Trip Breakers Opened Due to Uncertainty of Rod Position</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 4, Hot Shutdown, with Reactor Coolant System temperature at 336 degrees F. Unit 1 had been shutdown for a refueling outage and was in the process of startup for cycle 11. Event Description: On December 29, 1997, at 13:38 hours, a Unit 1 manual Reactor Trip occurred because of the uncertainty over the actual position of Rod J-3 in Shutdown Bank B due to a card failure in the Digital Rod Position Indicaton (DRPI) System. Operations personnel were in the process of withdrawing rods for Shutdown Bank B, to provide instantaneous shutdown capability in the event of an unanticipated reactivity excursion during Unit heatup, when alarms from the DRPI System for Shutdown Bank B and Rod J-3 were received. Operations personnel opened the Reactor Trip Breakers per action statement of Technical Specification 3.1.3.3. Since the Unit was not at power at the time of the trip, the primary and secondary system effects were negligible. All safety systems responded as designed. Root Cause: The cause of the DPRI System Urgent Failure is attributed to failure of a detector/encoder card in Data "A" Cabinet of the DRPI System. Corrective Actions: Operations personnel opened the Reactor Trip Breakers due to uncertainty over the actual position of Rod J-3 and stabilized the plant per station procedures. The failed detector/encoder card was replaced by a new detector/encoder card. The new card was successfully tested in service and the correct position of Rod J-3 was confirmed.
4131997011 | Catawba 1 | 12/30/1997 | 01/28/1998 | 9802110149 | <strong>ESF Actuation due to Reactor Coolant System Leakage from Loop Drain Valves</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 3, Hot Standby at 0% Power. Event Description: At 1741 on 12-30-97, during startup from a Unit 1 refueling outage, Operators identified a reactor coolant system leak. The leak was determined to be approximately 40 gallons per minute through two loop drain valves that were not tightly closed. Operators started a second centrifugal charging pump (a manual ESF Actuation). The leak was stopped when the first drain valve off the reactor coolant loop piping was closed. During the event the Refueling Water Storage Tank level dropped below its minimum value allowed by the technical specification. Tank level and boron concentration were subsequently restored to the required values. Event Cause: The event was caused by leakage through two drain valves that were not tightly closed. Cause analysis was not able to identify a root cause for this event. Corrective Actions: The leaking valves were located and closed. The plant was stabilized in Mode 3. An Engineering evaluation determined that there was no damage to safety related plant equipment as a result of this event. An evaluation will be performed to determine the need for a check of critical plant valves during plant heatup and pressurization and to determine the need for physical protection of critical plant valves to prevent inadvertent mispositionings.
4131997012 | Catawba 1, Catawba 2 | 12/31/1997 | 01/30/1998 | 9802110154 | <strong>RTD and Incore Thermocouple Cross Calibrations were performed inconsistent with Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1, Mode 6, Refueling at 0% Power Unit 2, Mode 1, Power Operation at 100% Power Event Description: On 12-31-97 it was determined that Technical Specification (T/S) 3.3.2 had been violated in the past history of the plant due to the method of performing the Incore Thermocouple and RTD Cross Calibrations. The problem was that all four protection channels were being removed from service without declaring them inoperable as required by T/S 3.3.2. A previous event in 1990 had identified a concern with how this calibration was performed. In response to that concern Catawba elected to perform the calibration one channel at a time. In 1995 a better method for performing this calibration became available which required taking all four channels out of service at the same time. The new method was implemented without considering a previous LER commitment to remove only one channel at a time and without realizing the need to follow the T/S Action Statement which is applicable when more than one channel is removed from service. Event Cause: The cause was an inadequate process for identifying commitments. Corrective Actions: Engineering provided instructions to allow calibration of all four channels while remaining in compliance with Tech. Specs. An assessment will be performed to determine if improvements are needed in the commitment management process.
4141997001 | Catawba 2 | 01/03/1997 | 02/03/1997 | 9702110121 | <strong>Nitrogen Supply To Two Main Steam Power Operated Relief Valves Was Isolated</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Unit Status: Unit 2 - mode 1, power operation, 100% power. Event Description: On January 3,1997, during routine maintenance to replace a low nitrogen cylinder, maintenance found the nitrogen supply isolation valves for power operated relief valve (PORV) 2SV-1 closed. Operations instructed maintenance to open the nitrogen supply isolation valves to 2SV-1 and check the remaining three unit two and all four unit one PORVs. The nitrogen supply isolation valves for 2SV-13 were found closed, and opened according to Operations' instructions. The remaining PORV nitrogen supply isolation valves were found open. Root Cause: The root cause of this event is poor work practices in that the test procedure was not followed correctly. A contributing factor is performance of multiple actions in a test procedure step. Corrective Action: Nitrogen isolation valves for 2SV-1 and 2SV-13 were opened. The remaining unit 2 and all four Unit 1 PORV nitrogen isolation valves were verified open. The individuals involved in this event were counseled. PT/1(2)/A/4200/31A, SG PORV and block valve D/P stroke test, will be revised to included separate actions for each valve manipulation. To prevent recurrence Engineering will review test procedures for steps requiring multiple actions separated by time or distance and make changes as necessary.
4141997003 | Catawba 2 | 02/17/1997 | 04/19/1997 | 9704280008 | <strong>Component Cooling System Unavailability</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Unit Status: Unit 2- mode 1, power operation, 100% power. Event Description: On 03/20/97 Engineering determined that between 01/25/97 and 02/17/97, the 2A1 KC pump would not have restarted by automatic sequencer action during an event requiring it to be load shed from the essential bus. After losing power, the 2A1 KC breaker would not have reclosed when power was restored. Root Cause: There was a failure of the breaker charging springs motor coils when the breaker was closed on 01/25/97. The breaker and pump remained in operation until 02/16/97 when A train KC was secured for testing. The charging motor failure was age related. In 1995, these safety related breakers were incorporated into a new periodic refurbishment program that includes an inspection of the breaker closing springs motor, but the 2A1 KC pump breaker had not yet been refurbished. Corrective Action: Train A of the Unit 2 KC system was declared inoperable and the appropriate Technical Specification action was entered. The failed breaker was replaced with an operable breaker.
4141997004 | Catawba 2 | 04/24/1997 | 07/02/1997 | 9707090379 | <strong>Inadequate Test Of A Containment Isolation Valve When Procedure Step Not Performed</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 - mode 1, power operation, 100% power. Event Description: On April 24, 1997, during scheduled leak rate testing of containment isolation valve 2NV-874, one step in the periodic test procedure was mistakenly marked not applicable (NA). On June 4, during procedure completion verification the Operations test supervisor found the mistake. Operations shift management was notified and 2NV-874 was declared inoperable. The valve was tested and exceeded the allowable leakage limit. Maintenance completed repairs and the valve was successfully retested. Root Cause: The root cause of this incident is attributed to inadequate work practices in that self checking was not used to ensure that each step in the test procedure was correctly completed. Corrective Action: The individual was counseled for improved performance. Planned corrective action includes evaluating how Catawba currently performs procedure completion verification and determine if any process changes are needed.
4141997005 | Catawba 2 | 06/26/1997 | 07/24/1997 | 9708040137 | <strong>Unit Two Reactor Trip On 2B Reactor Coolant Pump Low Flow</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2- mode 1, power operation, 100% power. Event Description: On June 26, 1997, an automatic reactor trip occurred while in mode 1. While searching for an electrical ground, the reactor coolant pump lost power when its associated bus isolated. Bus isolation and the loss of the reactor coolant pump resulted in low flow in one loop of the reactor coolant system and subsequent automatic trip of the reactor. A faulty push button caused the electrical ground. Root Cause: The root cause of the reactor trip was equipment failure of a Cutler-Hammer E30JY5 close/trip push button switch. Corrective Action: Maintenance and Engineering found and replaced the defective switch. The failed switch has been sent to Duke Power Testing Lab to determine cause of failure. Engineering will evaluate the results of the testing and determine any additional corrective actions necessary.
4141997006 | Catawba 2 | 07/26/1997 | 08/25/1997 | 9709040013 | <strong>Manual Reactor Trips Following Main Steam Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 1, Power Operation, at 100% power. Event Description: On July 26, 1997, at 2223 hours, and on August 17, 1997, at 0130 hours Unit 2 was manually tripped to preclude an automatic trip following closure of Main Steam Isolation Valve (MSIV) 2SM-1. During both events all safety systems responded as designed. Auxiliary Feedwater (CA) automatically started upon receipt of a low steam generator (S/G) level signal to maintain S/G level. Emergency Core Cooling System (ECCS) actuation was not necessary and did not occur. A second CA autostart occurred during the August 17 event when the level in the S/G isolated by 2SM-1 closure inadvertently decreased below the low level setpoint. Root Cause: The cause of both manual reactor trips is attributed to failure of a digital optical isolator (DOI) within the control circuitry of MSIV 2SM-1. The July event involved the "A" train circuitry and the August event involved the "B" train circuitry. Corrective Action: Operations personnel correctly diagnosed each event and tripped, evaluated and stabilized Unit 2 per station procedures. Failed and suspect DOIs have been replaced. An improved method of testing DOIs for the identified failure has been developed. All DOIs in MSIV applications have been tested and will receive additional testing. All DOIs in critical control applications with the same model number as the DOIs noted in this LER and having AC input and DC output will be tested. Additional failure analysis by vendors is being performed to identify the failure mechanism internal to the DOI. Engineering will review the results of the failure analysis and recommend additional corrective actions as necessary.
4161997001 | Grand Gulf 1 | 03/12/1997 | 05/13/1997 | 9705210068 | <strong>Standby Service Water System Subsystem (Missed Technical Specification Surveillance)</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 12, 1997 at approximately 0930 hours, while operating in OPERATIONAL CONDITION 1 and approximately 100% power, temporary maintenance and testing (M&TE) equipment was installed in the Standby Service Water System (SSW) 'A' subsystem Room Coolers. The temporary M&TE (annubars) was installed to collect cooling water flow rate data in support of thermal performance testing. Standard operating practice, where temporary M&TE is utilized, is to conservatively declare the affected subsystem inoperable and implement the associated Technical Specification ACTIONS until system operability is restored. For this specific testing evolution, the REQUIRED ACTIONS of Technical Specification Limiting Condition for Operation (LCO) 3.7.1, CONDITION D i. e., complete surveillance requirement (SR 3.8.1.1) of LCO 3.8.1 'AC Sources Operating' within one hour of declaring the affected subsystem inoperable was applicable. The 'A' subsystem was subsequently declared inoperable on March 12, 1997 at 1236 hours and the required actions of Technical Specification 3.8.1.1 were immediately implemented, although exceeding the LCO time requirement. The 'A' subsystem was retested, with no malfunctions identified and restored to operable status at approximately 1650 hours on March 12, 1997. The 'B' Standby Service Water subsystem [BI] was operable and in standby during performance of the testing activities. Therefore, the ability to achieve and maintain safe shutdown was not adversely impacted, nor was public health and safety compromised by this event.
4161997002 | Grand Gulf 1 | 06/19/1997 | 07/17/1997 | 9707300048 | <strong>Both Divisions Of Relief/Low-Low Set Logic Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1997, the Safety Relief Valve (SRV) Test Switch for Division I Relief/Low-Low Set logic was taken to the "Test" position for Instrument and Control (MC) surveillance testing. On the same day, at 2014, during performance of Technical Specifications required rounds, the SRV Test Switch for Division II Relief/Low-Low Set logic was placed in the "Test" position. Consequently, both divisions of SRV Relief/Low-Low Set logic were inoperable at the same time. The error was immediately-recognized and the Division II Relief/Low-Low Set logic "Test" switch was returned to the "Normal" position. Taking the Division II Relief/Low-Low Set logic test switch to"Test" while the Division I Relief/Low-Low Set logic test switch was already in the "Test" position placed the system in a condition that would have prevented it from fulfilling its safety function. Therefore, this event is reportable pursuant 10 CFR 50.73 (a)(2)(v)(D). The total time that both divisions of Relief/Low-Low Set logic were inoperable was approximately 10 seconds. The safety function and the Automatic Depressurization System (ADS) function of the SRVs were not affected by this event. During this short duration, no events occurred requiring initiation of Relief/Low-Low Set logic. Therefore, the health and safety of the general public were not compromised as a result of this event.
4161997003 | Grand Gulf 1 | 06/18/1997 | 09/30/1997 | 9710070154 | <strong>Control Room Envelope Leakage Potentially Exceeding License Condition 2.C(38) Limit</strong><br /><i>Abstract:&nbsp;</i>During inspection activities related to fire rated barriers, certain control room envelope (CRE) conduit internal seals were determined to be missing. GGNS controls CRE in-leakage by limiting the open area of CRE penetrations (license condition limit of 590 cfm correlates to 24 square inches of open area). Activities were then begun to verify and/or restore CRE conduit internal seal integrity. A cumulative sum of total CRE opening was maintained during inspections. On June 18, 1997 based on conservative assumptions and partial field data, it was believed that the allowed CRE open area previously exceeded the limit of LC 2.C(38). This was docketed in a interim report and inspections continued. Once all electrical conduits penetrating the CRE had been inspected, results revealed that approximately 22.9 square inches of open area existed. Of this, 11.5 square inches were opened after the 1983 CRE in-leakage test which established the basis for the license condition limit. This area effectively eroded the license condition margin on CRE openings to approximately 12.5 square inches versus the 24 square inch limit imposed by LC 2.C(38). The remaining 11.4 square inches existed during performance of the 1983 in-leakage test and were therefore accounted for in the boundary leakage performance. From the review performed, no definitive data is available to confirm that the CRE in-leakage rate (590cfm) was ever exceeded. Therefore, GGNS has elected to treat this condition reportable. The ability to achieve and maintain safe shutdown was not adversely impacted, nor was public health and safety compromised by this condition.
4161997004 | Grand Gulf 1 | 09/11/1997 | 10/13/1997 | 9710210129 | <strong>Failure to Declare Valve Inoperable During Work Having ISI Required Stroke Time Retest</strong><br /><i>Abstract:&nbsp;</i>A work order was initiated to document a packing leak on valve 1P11F064, Condensate and Refuel Water Transfer Auxiliary Building Isolation Valve [KA], a secondary containment isolation valve. The work scope of the original job plan was to repack the valve based on the initial walkdown and evaluation of the leak. The work instructions impact statement included the statement that the valve would need to be stroked for retest. A subsequent walkdown determined that sufficient gland travel remained to tighten the packing and stop the leak without repacking. The impact statement was amended to allow this alternative, the work was authorized on 9/9/97, and the packing was retorqued on 9/10/97. During final review of the work order by Operations, performed on the next shift, the need to stroke time test the valve was questioned by onshift personnel. It was decided the appropriate participants would resolve the issue the next morning. On 9/11/97, the correct resolution was reached; i.e., that the ISI required retest did apply because the packing had been adjusted. The valve was stroked and the stroke time found to be 3.5 seconds, the same as prior to the packing adjustment. However, assuming the valve was inoperable when the packing was tightened, the valve exceeded the allowable LCO time for required action. Appropriate personnel in the departments involved are being trained on this event and its lessons learned. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B).
4161997005 | Grand Gulf 1 | 09/30/1997 | 10/30/1997 | 9711050100 | <strong>Inadequate Retest of Containment Airlock Air Seal System</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1996, a work order (WO) to troubleshoot problems with the inner airlock required adjusting pressure switches and regulators on the air seal system. Sections of a surveillance procedure were added to the WO to provide instructions and retest requirements. Adjustments were made to the pressure switches which required removing air lines to the switches. An undocumented leak test was performed on the pressure switches and the air lines that were disconnected. The work was completed on December 30,1996. On September 9, 1997, the inner airlock failed a pressure test. Two leaks were found. The first was on a valve and the second was on an air supply line fitting. A second air drop test was performed successfully on September 10, 1997. The leakage was originally attributed to the work from 1996. Because of the magnitude of the leakage and the inoperability of the outer door during a surveillance, the NRC Operations Center was notified of the potential for a loss of containment pressure boundary integrity under some accident conditions. During the investigation, information on the undocumented test as well as the determination of the magnitude of the fitting leak were uncovered. Because the maintenance test was not documented and was not approved to meet the retest requirements, GGNS is conservatively reporting this occurrence under 10CFR50.73(a)(2)(i)(b) for a condition prohibited by the plant's Tech Specs. The root cause of the condition was inadequate use of administrative controls, in that the planner did not adequately follow the procedures established to assure that retest requirements are specified in applicable WOs.
4161997006 | Grand Gulf 1 | 11/21/1997 | 01/06/1998 | 9801200076 | <strong>Release of Contaminated Liquid Outside the Controlled Access Area</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1997, approximately 1.2 gallons of contaminated liquid was spilled onto the ground in a concrete and gravel area outside the Controlled Access Area (CAA). The spill resulted from the use of a hydrolazer in the cask loading pool. The hydrolazer was being used to clean temporary equipment used to cut up control blades and to stir sediment to aid vacuum cleaning of the pool. No radiological release limits were exceeded nor were any specific reporting criteria met due to this spill, therefore this information is provided as a voluntary Licensee Event Report. The Apparent cause of the spill was a lack of administrative control of hydrolazing inside the CAA and a less than adequate design of the hydrolaze piping resulting in a short term (approximately 2 minutes) siphoning of the spent fuel pool. The spill area was secured and cleanup commenced. Additionally, the hydrolaze piping will be modified to prevent siphoning and written guidelines will be developed governing hydrolazing.
4231997001 | Millstone 3 | 01/04/1997 | 02/03/1997 | 9702060045 | <strong>Lack of Verbatim Compliance with Technical Specification Surveillance Requirements for 125 Volt Batteries and Battery Chargers</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 4, 1997, with the plant in Mode 5, it was identified that 125 volt battery surveillance testing was being performed in a manner that was not in verbatim compliance with the Technical Specifications (TS). Similarly, on January 9, 1997, with the plant in Mode 5, it was identified that 125 volt battery charger surveillance testing was being performed in a manner that was not in verbatim compliance with the TS. These conditions were determined to be reportable pursuant to 10CFR50.73(a)(2)(i), as an event or condition prohibited by the Technical Specifications. While the surveillance testing performed may have been more accurate or more conservative than the verbatim requirements of the specifications involved, this event is significant in that it identifies further examples of a lack of verbatim compliance with TS requirements. These conditions were identified as the result of a heightened awareness of the potential for additional lack of verbatim TS compliance such as those described in previous Licensee Event Reports, LER 96-038-00, and LER 96-048-00. Corrective actions included immediate revision and performance of the battery and battery charger surveillance testing procedure requirements to effect verbatim TS compliance with the TS. Additionally, a review of the affected TS will be conducted for potential wording changes to ensure clarity, followed by the development and submittal of any resultant amendment request.
4231997002 | Millstone 3 | 01/08/1997 | 02/07/1997 | 9702120305 | <strong>Torquing of Battery Connections Not Performed As Part Of Connection Tightness Checks</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 8, 1997, with the unit in Mode 5, it was discovered that the 18 month battery surveillance procedure did not include checking the torquing of battery connections against the manufacturer's recommended torque value as required by the Surveillance Requirement (SR) 4.8.2.1.c.2 bases which reference IEEE Standard 4501980. This condition was determined to be reportable pursuant to 10 CFR50.73(a)(2)(i), as an operation or condition prohibited by the Technical Specifications. There was no safety significance because the batteries were capable of performing their intended safety function as evidenced by the cell-to-cell and terminal connection detail resistance readings and the passing of battery service tests. There were no safety consequences associated with this condition. However, the failure to perform the surveillances in accordance with the Technical Specifications is significant. The battery surveillance procedures were revised to contain the appropriate torquing requirements and the batteries were tested.
4231997003 | Millstone 3 | 01/13/1997 | 02/11/1997 | 9702260042 | <strong>Potential For Recirculation Spray System (RSS) Piping Failure Due To RSS Pump Stopping And Restarting During Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 13, 1997, an engineering evaluation determined the Recirculation Spray System (RSS) heat exchangers and piping may be susceptible to water column separation, and subsequent water hammer, if the RSS pumps are restarted during design basis accident conditions. This condition has been determined to be outside the design basis and the RSS was declared inoperable. NRC notification of this event was made pursuant to 10CFR50.72(b)(1)(ii)(B), on January 13, 1997. The Unit was in Mode 5 and in an extended shutdown. The cause of this event is design deficiency due to inadequate RSS design scope which did not incorporate and analyze the system susceptibility to waterhammer and its effects. An evaluation of the RSS water column separation issue will be performed to determine if transient piping and equipment loads are acceptable or require design modification.
4231997004 | Millstone 3 | 01/14/1997 | 02/11/1997 | 9702260115 | <strong>Lack of Verbatim Compliance with Technical Specification Surveillance Requirements for Molded Case Circuit Breakers</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 14, 1997, with the plant in Mode 5, it was identified that the performance of 480 volt molded case circuit breaker (MCCB) surveillance testing was being performed in a manner not in verbatim compliance with the Technical Specifications (TS). These conditions were determined to be reportable pursuant to 10CFR50.73(a)(2)(i), as an event or condition prohibited by the Technical Specifications. This event is significant in that, by not performing expanded population testing for MCCB failures, it created the condition wherein the reliability of the remaining untested population of the type of MCCB which failed was not ensured. This, in turn, could have resulted in a loss of safety function. This event is also significant as an example of a lack of verbatim compliance with TS requirements. These conditions were identified as the result of a heightened awareness of the potential for additional lack of verbatim TS compliance such as those described in previous Licensee Event Reports, LER 96-038-00, LER 96-048-00, and LER 97-001-00. Corrective actions include a change to the affected surveillance testing procedure to ensure verbatim compliance with the TS and performance of the required testing.
4231997005 | Millstone 3 | 01/15/1997 | 02/13/1997 | 9702200137 | <strong>Safety Related Breaker Testing performed With Gages Not in The MT&E Program</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 15, 1997, with the plant in Mode 5, during the performance of Preventative Maintenance (PM's) on Safety related Motor Control Center (MCC) breakers, Load Center breakers, and 4160 volt breakers it was determined that gage utilized for measurements during the PMs were not included in the Measuring and Test Equipment (M&TE) Program. A review identified several tools which were historically not controlled within the M&TE program. The tools identified were measured for accuracy. Gages that had been previously used to perform PMs on safety related 4160 volt breakers were found to be out of tolerance. These gages were used to ensure proper alignment of various parts within the breaker operating mechanism. As a result, a condition was created in which multiple safety related breakers could have become inoperable as a result of a single cause. The condition was reported to the NRC on January 15, 1997 pursuant to 10CFR50.72 (b)(2)(iii)(B). The cause of this event is attributed to programmatic deficiencies resulting from inadequate management expectations. The required PMs for the safety related 4160 volt breakers will be completed by March 15, 1997. Additionally, Electrical, Mechanical, and I&C Department procedures will be reviewed to identified instruments and tools that require calibration. The safety significance and consequence of this event are minimal in that following completion of the PMs a test was performed to ensure breaker functionality.
4231997006 | Millstone 3 | 01/17/1997 | 04/30/1997 | 9705080243 | <strong>Residual Heat Removal Suction Isolation Valves Open But Not Under Administrative Control as Required in Mode 4 by Technical Specification Surveillance Requirement 4.6.1.1.a</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 17,1997, with the unit in Mode 5, it was determined that Residual Heat Removal (RHR) System Suction Containment Isolation Valves (3RHS*MV8701A/B and 3RHS*MV8702A/B) had not been maintained closed in Mode 4 as required by Technical Specification 3.6.1.1. Historically, the RHR System Suction Containment isolation Valves had been opened in Mode 4 in accordance with the unit operating procedures to provide a flow path for cooldown to cold shutdown as required by plant design. No allowance is provided in Specification 3.6.1.1 for these valves to be opened in Mode 4. Opening these valves in Mode 4 without a Technical Specification (TS) allowance violates the Specification 3.6.1.1 requirements for maintaining containment integrity and constitutes a condition reportable pursuant to 10CFR50.73(a)(2)(i), as an operation or condition prohibited by the TS. There were no safety consequences associated with this condition in that the plant has not experienced an event requiring closure of these valves for containment isolation while the valves were open for RHR system operation. Unit design and operating procedures provide assurance that the RHR suction valves will be isolated when required and Containment integrity maintained in the event of an accident. The corrective actions described in the original LER are complete. A Technical Specification change is being developed to include the RHR Suction CIVs in the note to Surveillance Requirement 4.6.1.1.a.
4231997007 | Millstone 3 | 01/23/1997 | 02/21/1997 | 9702280057 | <strong>Non-Conservative Assumptions Used In Technical Specifications Shutdown Margin Curve</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 14, 1997, as the result of an engineering review, it was postulated that an incorrect assumption had been made in determining the degree of error in a Cycle 6 Shutdown Margin Curve which had previously been found to be in error. Subsequent Engineering evaluation concluded that the Cycle 6 Shutdown Margin - Mode 3 curve had been non- conservative. On January 23, 1997, with the unit in Mode 5, a prompt event report was made to the Nuclear Regulatory Commission of this historical condition pursuant to 10CFR50.72(b)(2)(iii)(A) as an event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition. The cause of this event has been determined to be the lack of procedures for the generation and documentation of reactor plant operational information. This condition was significant in that the use of an incorrect curve in determining the RCS boron concentration required to ensure adequate shutdown margin could have prevented the fulfillment of the safety function of the systems needed to maintain the reactor in a safe shutdown condition. A comparison between the actual RCS boron concentration values measured during periods of Mode 3 operation and the required shutdown margin RCS boron concentrations for Cycle 5 and Cycle 6 verified that, due to intentional over-boration, there had been no violation of the shutdown margin requirements contained within Technical Specification 3.1.1.1.2. Therefore, the safety consequence of this event was minimal.
4231997008 | Millstone 3 | 01/24/1997 | 02/22/1997 | 9703040211 | <strong>Failure To Enter Technical Specification 3.0.3 Action Statement For MSIV Closure</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 24, 1997, it was determined that the plant had previously operated in a condition prohibited by Technical Specifications (TS). Specifically, while conducting a scheduled plant shutdown on April 15, 1995, Unit 3 operators shut all four Main Steam Isolation Valves (MSIV)s in Mode 4. Due to the known inability of the valves to satisfy surveillance test requirements at the low steam pressures in Mode 4, the valves were declared inoperable. TS 3.7.1.5 for Modes 2, 3, and 4 states that 'With one MSIV inoperable, operation may proceed provided that the isolation valve is maintained closed. Otherwise, be in Hot Standby within the next 6 hours and in Cold Shutdown within the following 30 hours'. The plant complied with these required actions. However, the TS do not provide for the condition of four MSIVs inoperable which would require entry into TS 3.0.3. It has also been determined that TS 3.0.4 has been historically violated based upon entering Mode 4 from Mode 5 with the MSIVs closed, but inoperable because the valves could not meet TS surveillance acceptance criteria at the low steam pressures existing in Mode 4. This condition is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by the TS. It was determined that there was no safety significance nor adverse safety consequence in that the valves were closed in their safety function position and the plant was brought to hot shutdown and cold shutdown conditions in the specified times of TS 3.0.3.
4231997009 | Millstone 3 | 01/23/1997 | 09/17/1997 | 9802090060 | <strong>Open High Energy Line Break (HELB) Barrier Door in Mode 1 Results in Violation of HELB Requirements</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1997, with the unit in Mode 5, an investigation into High Energy Line Break (HELB) door control problems resulted in discovery of a previously unidentified historical reportable event. On August 3, 1995, with the unit in Mode 1 at 100 percent power, three fire doors, that were also HELB barriers, on the 66 foot level of the Auxiliary Building, were found open without a continuous fire watch posted. A fourth fire door was properly controlled from a fire protection perspective but was not recognized as a HELB door. On August 8, 1997, several deficiencies were identified for HELB doors in the Auxiliary and Control Buildings as part of follow-up field walkdowns performed after a self-assessment of the HELB program. These deficiencies consisted mostly of door adjustment and maintenance issues, e.g.; damaged thresholds and gasket bars, missing sections of gaskets and weather-stripping, and several gaps around door gaskets exceeding allowable criteria. The cause of the August 1995 historical event was a failure to develop and implement an effective high energy line break door control program. This resulted in personnel not understanding HELB requirements associated with the design basis. The cause of deteriorated HELB door conditions identified in August 1997 was a failure to develop and implement an effective HELB door (barrier) periodic inspection and maintenance program prior to initial licensing. Recognition of inspection criteria development and necessity to inspect doors prior to startup should have been addressed within the original corrective actions to this Licensee Event Report. As a result of the August 1997 HELB area walkdown/inspections the following additional corrective actions will be taken prior to entry into Mode 4: HELB doors identified not to comply with high energy line break barrier design requirements will be restored to compliance, and procedures and work control documents will be revised and/or developed to provide for periodic inspection and position verification of HELB doors.
4231997010 | Millstone 3 | 01/29/1997 | 02/28/1997 | 9703070202 | <strong>Electrical Calculation Discrepancies in Minimum Voltage Analysis For Class 1E Electrical Systems</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 13, 1997, with the plant in Mode 5, a review of electrical calculations associated with Class 1E 480V and 120V systems identified discrepancies between related electrical calculations used to demonstrate design basis compliance. On January 29, 1997, these concerns were sufficiently substantiated to question the validity of the Degraded Grid Voltage calculations. A prompt report was made, pursuant to 10CFR50.72(b)(2)(iii) as an event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition. The degraded grid voltage (DGV) relays are required to ensure that safety related equipment and devices either have adequate voltage to perform their safety functions or are not damaged due to a degraded voltage condition. These analytical limit worst-case minimum values were not utilized as the source voltage for separate voltage drop calculations performed for the 480V and 120V bus loads. If the 4160V bus voltage were to be at its analytical limit worst-case minimum value then inadequate voltage at individual devices supplied by the distribution system could result. Therefore, these systems may not be able to perform their design safety functions under degraded grid voltage conditions. The cause was determined to be a lack of configuration management for the comprehensive calculation program which is required to establish and maintain the design basis of the unit. The calculation program is being reviewed and revised as part of the ongoing 50.54(f) effort. In addition, in order to address configuration management of the calculation program, formal work practices have been established for processing nuclear engineering calculations.
4231997011 | Millstone 3 | 01/29/1997 | 02/28/1997 | 9703100012 | <strong>Hydrogen Recombiner Heaters Potentially Outside Of Design Basis Under Degraded Voltage Conditions</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During a review of design attributes and supporting design specifications and calculations for Technical Specifications, discrepancies were found between the minimum required voltages for safety related heaters and their capability to perform their design functions based on reduced voltage at the safety related buses. Reviews performed of heater applications found that the heaters were able to perform their design function with the exception of the Hydrogen Recombiner heaters. On January 29, 1997, with the unit in Mode 5, a prompt event report was submitted regarding the reduction in Hydrogen Recombiner heating capability under degraded voltage conditions pursuant to 10CFR50.72 (b)(1)(ii)(B) as a condition outside the design basis of the plant. There have been no safety consequences as the result of a degraded grid voltage supply to the Hydrogen Recombiner heaters. Recombiner heaters is safety significant in that it could result in reliance on operation of the Containment Hydrogen Purge system to remove hydrogen from the containment following a Loss of Coolant Accident. The cause has been determined to be a lack of configuration management for the comprehensive calculation program which is required to establish and maintain the design basis of the unit. As reported on LER 97-010-00, 'The calculation program is being reviewed and revised as part of the ongoing 50.54(f) effort. In addition, in order to address configuration management of the calculation program, formal work practices have been established for processing nuclear engineering calculations. Additional corrective action includes evaluation of Hydrogen Recombiner heater performance under degraded voltage conditions, and, if required, implementation of design changes to restore the Hydrogen Recombiners to their design basis requirements.
4231997012 | Millstone 3 | 01/29/1997 | 02/28/1997 | 9703070196 | <strong>Noncompliance of Tornado Missle Protection for Manhole Covers due to Removal of Temporary Anchoring Ballast for Approximately Three Minutes</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 29, 1997 at approximately 1435 hours, with the plant in Mode 5, temporarily installed concrete blocks serving as ballast for tornado missile restraint of safety related electrical manhole covers were removed from the covers. This was done to allow removal and reinstallation of sealant on the covers. Within approximately three minutes, the blocks were properly reinstalled following recognition by the Unit Supervisor, that the blocks were functioning as a temporary modification for tornado protection. Prompt notification to the NRC of this event was made pursuant to 10CFR50.72(b)(1)(ii)(B) on January 29, 1997 as a condition outside the design basis of the plant. The blocks were previously installed in 1996 as part of corrective action to an event reported in LER 96-027-00, which identified an original lack of installed tornado restraint on the subject covers. This event resulted from failure of the Operations Department personnel reviewing the work activity to recognize the safety-related function of the concrete blocks on the manhole covers. Consequently, the involved work documentation was coded as minor maintenance and subsequent planning prior to the work activity did not identify that the blocks were functioning as a temporary modification. In addition, prior to removing the blocks, workers did not notice an installed tag that identified the blocks as a temporary modification. Personnel involved in the event have received appropriate counseling on the importance of attention to detail during review and planning of job activities.
4231997013 | Millstone 3 | 01/30/1997 | 02/28/1997 | 9703100022 | <strong>Failure to Meet General Design Criteria 57 for the Main Steam Supply Containment Isolation Valves to the Auxiliary Feedwater Pump Turbine</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On January 30, 1997, with the unit in Mode 5, it was identified that the instrument air operated, Turbine Driven Auxiliary Feedwater Pump (TDAFW) Steam Supply [Containment] Isolation Valves (3MSS*AOV31/A/B/D) do not satisfy the remote manual operation requirement specified in General Design Criteria (GDC) 57. Air to permit remote operation of these valves cannot be assured in the event of an accident due to the non-seismic nature of the instrument air lines. On February 3, 1997, an engineering evaluation confirmed these valves do not meet containment isolation valve criteria. As a result an immediate notification was made on February 3, 1997, pursuant to 10CFR50.72(b)(1)(ii)(B). This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(B) as an existing condition outside the design basis of the plant. While the TDAFW Steam Supply Isolation Valves do not fulfill all the requirements of GDC 57, the downstream valves meet the requirements and do satisfy GDC 57. Therefore, in the event of an accident the potential failure of the TDAFW Steam Supply Isolation Valves would not prevent isolation of the affected penetrations. The procedures and design documentation are being revised to reflect the revised containment boundary for these penetrations.
4231997014 | Millstone 3 | 02/03/1997 | 03/05/1997 | 9703100189 | <strong>Both Trains of Control Room Envelope Pressurization System Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 3, 1997, with the plant in Mode 5 while performing the Control Room Envelope Pressurization System (CREPS) Train A Valve Lineup, Instrument Air System (IAS) isolation valves (3-IAS-V644 and 3-IAS-V725) were found open. These valves were last opened in accordance with applicable procedure on January 15, 1997 to allow purging the Cable Spreading Room. These valves supply air to several solenoid valves which control air operated dampers in the Control Building Purge Supply and Exhaust System. These solenoid valves are not qualified as Category I (CAT I) safety related components therefore, it must be postulated that they will fail to the most adverse position. This creates the potential for a breach of the Control Room envelope which would render both trains of CREPS inoperable. Technical Specification (TS) Limiting Condition for Operation (LCO) action statement 3.7.8.b requires suspension of core alteration and suspension of positive reactivity changes whenever both trains of CREPS are inoperable in Mode 5. Additionally, it requires that action be initiated within one hour to restore operability of the CREPS trains. Contrary to this, both trains were inoperable for 18 days without action being initiated to restore the system to operable status. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by TS. This event resulted from failure of plant personnel to execute a procedural step, which requires the valves be closed upon completing the purge. Additionally, procedural inadequacies directly led to this event. Upon discovery, the valves were closed, reestablishing TS compliance and terminating the event. Involved personnel have been counseled on the importance of procedure adherence. Additionally, the procedure for the Control Building Purge Supply and Exhaust System will be revised.
4231997015 | Millstone 3 | 02/04/1997 | 03/05/1997 | 9703100203 | <strong>Potential Vortexing of Recirculation Spray System Pumps</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 4, 1997, with the unit in Mode 5, a review of design calculations identified that the calculated minimum water level in the containment sump at the time of Recirculation Spray System (RSS) pumps start (approximately eleven minutes after a Containment Depressurization Actuation signal) would be below the level of the containment sump vortex suppression gratings during a large break Loss of Coolant Accident (LOCA). Vortex formation and the resulting air entrainment, could result in cavitation of the RSS pumps, such that they might be unable to perform their intended safety function(s) in an accident. Following evaluation, this condition was immediately reported on February 7, 1997, pursuant to 10CFR50.72(b)(1)(ii)(B), and is being reported pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition outside the design basis of the plant. There were no adverse safety consequences from this condition, in that the unit has not experienced a LOCA and therefore operation of the RSS has not been necessary. However, the potential inoperability of the RSS pumps is significant because it represents a condition outside the design basis of the plant. The RSS is credited in the safety analyses to cool the containment by spraying containment sump water into the containment atmosphere post-accident, provide iodine removal, and provides long-term core cooling post-accident. Formation of vortexes due to the water level being below the level of the vortex suppression gratings, resulting in cavitation, could create a common cause failure of the four RSS pumps, resulting in potential loss of safety function. Corrective actions needed to ensure operability of the RSS and design basis compliance will be implemented prior to entry into mode 4 from the current outage.
4231997016 | Millstone 3 | 02/06/1997 | 03/07/1997 | 9703140111 | <strong>Piping Supports for Portions of the Residual Heat Removal system In A Condition Inconsistent With The Design Installation Details</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 6, 1997, at 17:00 with the plant in Mode 5 at 0-percent power, it was determined that piping supports for portions of the Residual Heat Removal system (RHS) were in a condition inconsistent with the design installation details. Specifically, while implementing piping support modifications to address conditions previously identified in LER 96-007-00, workers found the piping system to be outside of its designed configuration. An engineering review determined on February 7, 1997 that the supports would not function as designed. As a result, an immediate notification was made pursuant to 10CFR50.72(b)(1)(ii)(B) of a condition during operation that resulted in the nuclear power plant being in a condition that is outside of the design basis of the plant. This condition is significant in that had the plant experienced a design basis accident in containment the potential existed that the RHS might have been unable to fulfill its required safety function. However, there were no adverse safety consequences from this condition since the RHS system has never been required to operate in a post accident environment nor has it experienced a seismic event. Immediate corrective action was taken to restore the piping supports to their designed configuration. In addition, a representative sample of other safety related pipe supports will be inspected to determine if conditions exist which would cause the piping support to not perform as designed.
4231997017 | Millstone 3 | 02/06/1997 | 10/11/1997 | 9710220090 | <strong>Inadequate Overlap Testing of Logic Circuits</strong><br /><i>Abstract:&nbsp;</i>In February 1997, deficiencies were identified by the Nuclear Regulatory Commission (NRC) concerning overlap testing within surveillance procedures for safety related logic circuits. Following this event an ongoing verification program is being performed using, in part, the guidance of Generic Letter (GL) 96-01, "Testing of Safety Related Logic Circuits:" to verify that the Technical Specification surveillance procedures adequately test the logic circuitry. On February 6, 1997, it was determined that a parallel logic circuit in the undervoltage scheme and an output contact in the degraded voltage scheme were not included in Technical Specification (TS) surveillance testing. On February 13, 1997, it was determined that surveillance testing of the low-low steam generator level circuit failed to include the response of certain Auxiliary Feed Water System valves. On May 23, 1997 it was discovered that the isolation function of the Supplementary Leak Collection and Release System (SLCRS) intake and exhaust dampers was not being completely tested. On September 10, 1997, it was identified that during a simulated loss-of-offsite power condition that the auto-start of the Control Room Chillers and the Instrument and Computer Rooms Air Conditioning Units by the Emergency Diesel Generator Load Sequencer was not being properly tested. This condition was determined to be reportable on September 17, 1997. These conditions represent a failure to adequately test the automatic actuating circuitry of safety related, post-accident mitigation systems and are reportable pursuant to 10CFR50.73(a)(2)(i)(B),as conditions prohibited by the plant TS. The root cause was determined to be inadequate initial development of the surveillance test procedures. Prior to entry into Mode 4, testing procedures will be revised to ensure that complete testing of the safety related circuitry is performed which satisfies the TS requirements.
4231997018 | Millstone 3 | 02/08/1997 | 03/07/1997 | 9703140117 | <strong>Technical Specification Parameter Compliance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 8, 1997 with the plant in Mode 5 it was determined that the plant had operated in conditions prohibited by 3 different Technical Specifications (TS). Each of these TS specify parameters without specific ranges. Therefore, verbatim compliance with the specified parameters is not possible. These conditions occurred as a result of interpreting the Technical Specifications for intent rather than conducting operations in strict compliance with the specification. These conditions were determined to be reportable pursuant to 10CFR50.73(a)(2)(i)(B) as any operation prohibited by the Technical Specifications. The non-compliances have no plant safety consequence. The Surveillances and Safety System Settings will be conducted in the same manner after revision of the Technical Specifications. These non-compliances were identified as the result of heightened awareness to the potential for lack of verbatim Technical Specification compliance. These non-compliances are significant as examples of a lack of compliance with TS requirements identified due to a heightened awareness resulting from previous Licensee Event Reports. The Technical Specifications and/or Bases will be revised.
4231997019 | Millstone 3 | 02/18/1997 | 03/20/1997 | 9703280268 | <strong>Violation Of Technical Specification As A Result of Failure To Account For Instrument Uncertainty In DWST Level</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 18, 1997, with the plant in Mode 5, it was determined that the Technical Specifications Limiting Condition for Operation (LCO) for the Demineralized Water Storage Tank (DWST) had not been met on some historical occasions. Specifically, it is required that the DWST be operable with a contained volume of at least 334,000 gallons of water. The applicable surveillance procedure specifies that DWST level indicators must indicate greater than or equal to 334,000 gallons to meet this requirement. This acceptance criteria did not include an allowance for instrument uncertainty. Based on a review of previously completed surveillance procedures and accounting for instrument uncertainty, it has been determined that the time limitations of LCO 3.7.1.3.b were not being met. Therefore, this condition is being reported pursuant to 10CFR50.73(a)(2)(i)(B),as a condition prohibited by the plant Technical Specifications. This condition is not significant in that had the plant experienced a total Loss-of-Offsite Power (LOP), the DWST would have contained adequate volume to ensure that the Reactor Coolant System (RCS) could be brought to 350 degrees Fahrenheit as required in the design basis. The cause of this event was a failure to adequately define within the Technical Specification LCO requirement or bases section the term 'contained volume'. Provisions will be made by October 10, 1997, so the surveillance requirements ensure adequate volume is contained within the Demineralized Water Storage Tank.
4231997020 | Millstone 3 | 02/18/1997 | 03/20/1997 | 9703280233 | <strong>Elevated Containment Temperature Due to Reduced Cooling Capability Restricts Ability to Enter Containment and Operate Equipment Required for Cold Shutdown During Certain Fire Events</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 18, 1997, with the unit in Mode 5, it was identified that operator entry into the Containment could potentially be restricted due to elevated ambient temperature during a loss-of-offsite-power (LOP) event. A LOP event is considered coincident with postulated fires in accordance with the 'Millstone Nuclear Power Station, Unit 3, Branch Technical Position (BTP) 9.5-1 Compliance Report.' For certain postulated fire events, Containment entry is credited to operate equipment necessary to achieve cold shutdown. Insufficient cooling flow was supplied to the Containment Air Recirculation (CAR) System fans cooling coils by the Reactor Plant Component Cooling Water (CCP) System during a LOP. An engineering estimate indicates a resulting Containment temperature of approximately 160 Degrees F. Personnel entry to Containment at this temperature may not be possible to operate equipment, even with compensatory measures. Consequently, the fire shutdown strategy assumed in the BTP 9.5-1 compliance report as part of the design basis may not be possible. This event is considered reportable pursuant to 10 CFR 50.73 (a)(2)(ii)(B), as a condition outside the design basis. The cause of this event was the original design placement of the throttle valves controlling flow to the CAR System fans when cooling is supplied by the Reactor Plant Component Cooling Water System. The secondary side of the Containment Air Recirculation System will be reconfigured to provide the required flowrates when supplied by the Reactor Plant Chilled Water (CDS) or CCP Systems. Containment temperature and personnel entry concerns as a result of CAR fan cooling capability will be reevaluated.
4231997021 | Millstone 3 | 02/18/1997 | 03/19/1997 | 9703250231 | <strong>Defective Design of RSS Expansion Jiont Tie Rod Assembly</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 18, 1997, with the unit in Mode 5, it was determined that defects existed in the original design of tie rod assemblies in eight Recirculation Spray System (RSS) expansion joints (3RSS*EJ1A through D and 3RSS*EJ2A through D). These joints are essential to containment integrity and to the heat removal function of the RSS. The specific design deficiency is a failure to provide adequate clearance for intermediate tie rod nuts. As a result of this defect, if the joints were subjected to their design basis loads, the stress levels in the joint tie rod assembly could have exceeded its analyzed operating limits and the joint could experience deformation. This condition was reported on February 18, 1997 pursuant to 10CFR50.72(b)(1)(ii)(B) as a condition during operation that resulted in the nuclear power plant being outside of the design basis of the plant. The cause of this event was determined to be a defective design which had been issued by the vendor, the Temp Flex division of Johnson Controls. This vendor has subsequently gone out of business. This condition is significant since failure of the joints could adversely affect containment integrity and long term cooling capability for the core. There were no adverse safety consequences from this condition in that the plant has not experienced a design basis event that would challenge the expansion joint. The required physical modifications to the eight expansion joints within the RSS will be completed prior to entry into mode 4. Additionally, a review of similar expansion joints provided by the original vendor will be performed.
4231997022 | Millstone 3 | 02/18/1997 | 03/20/1997 | 9703280315 | <strong>Improper Surveillance Testing of the Control Room Emergency Air Filtration System Filters</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 14, 1997, with the unit in Mode 5, following the completion of a routine filter replacement for the 'B' Train (3HVC*FLT1B) Control Room Emergency Air Filtration System, a discrepancy in the testing required to be completed prior to declaring the system OPERABLE was identified. It was confirmed on February 18, 1997 that Technical Specification (TS) Surveillance Requirements related to testing filter trains following replacement had historically not been performed prior to declaring the trains OPERABLE. Specifically, two (2) historical instances were identified, one in each train of the Control Room (CR) Emergency Air Filtration System. Contrary to TS requirements, the system was prematurely declared OPERABLE prior to one of the required surveillances being performed. Therefore, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B),as a condition or operation prohibited by plant technical specifications. The cause of this event was determined to be to a lack of trigger mechanisms within applicable maintenance procedures or work orders to identify applicable surveillances for the affected system following a full or partial changeout of filter media. This event is significant in that the operability of both trains of the CR air filtration equipment was in question between March 1995 and November 1995. However, there was no adverse consequence as a result of this event in that no uncontrolled radioactive releases have occurred that would have impacted the CR emergency air filtration system. Subsequent surveillance testing verified that penetration and bypass leakage for the equipment was within acceptable limits.
4231997023 | Millstone 3 | 02/20/1997 | 03/22/1997 | 9703260254 | <strong>Technical Specifications for Main Steam Isolation Valves (MSIV)</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 20, 1997, with the plant in Mode 5, it was determined that the Main Steam Isolation Valves (MSIV) had not been tested in accordance with the literal requirements contained within the Technical Specifications (TS). Specifically, TS 4.7.1.5.1 requires that 'each MSIV be demonstrated operable by verifying full closure within 1 0 seconds in Mode 1, 2, and 3 when tested pursuant to Specification 4.0.5.' Contrary to this requirement, the MSIVs have not been full stroked tested in Modes 1 and 2. Failure to perform TS required surveillances is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by the TS. There was no safety significance nor adverse safety consequence involved in this event. The MSIVs were tested successfully during startups. However, this event is significant as an example of a lack of verbatim compliance with TS requirements. This condition has existed since the initial issuance of the Technical Specifications and is due to an inadequate review during the development and certification. A License Amendment request will be submitted by April 30, 1997 to eliminate the requirement for full stroke testing of the MSIVs in Modes 1 and 2.
4231997024 | Millstone 3 | 03/03/1997 | 04/02/1997 | 9704090107 | <strong>Engineered Safeguards Building Monitor Noble Gas Activity Monitor Sensitivity Not Meeting Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 3, 1997, with the unit in Mode 5, it was identified that the Engineered Safeguards (ESF) Building Monitor - Noble Gas Activity Monitor (3HVQ*RE49) was inoperable and that best efforts to repair the monitor had not been initiated in accordance with Action B to Technical Specification 3.3.3.10, 'Radioactive Gaseous Effluent Monitoring Instrumentation'. The radiation monitor was inoperable because it did not have sufficient sensitivity to measure in accordance with Technical Specification requirements. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B), as an event or condition that is prohibited by the Technical Specifications. The cause of this event was failure by Operations personnel to recognize that the ESF Building Monitor - Noble Gas Activity Monitor was inoperable because of an error induced in the stored background reading. Operating procedures will be revised to provide guidance on purging. Operations and Chemistry personnel will be be briefed on this event and additional radiation monitor system training will also be provided.
4231997025 | Millstone 3 | 03/10/1997 | 04/09/1997 | 9704180096 | <strong>Historical Event: A Failure to Enter Technical Specification 3.0.3 Upon Loss of Vital AC Bus VIAC-1</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 10, 1997, with the unit in Mode 5, it was identified that with either 120-Volt (V) alternating current (A.C.) vital bus VIAC-1 or VIAC-2 inoperable, the four channels of 4160-V emergency bus undervoltage - grid degraded voltage detection instrumentation associated with the respective 4160-Volt Emergency Bus, #34C or #34D would be inoperable. Technical Specification (TS) 3.3.2, 'Engineered Safety Features [ESF] Actuation Instrumentation,' Functional Unit 8.b, 'Loss of Power, 4 kV Bus Undervoltage - Grid Degraded Voltage' specifies required actions for a single channel inoperable. Four channels inoperable requires entry into TS 3.0.3 because this condition is not addressed. During the investigation it was determined that a historical, reportable, event had occurred on March 27, 1988, when the '120-Volt A.C. Vital Bus #VIAC-1' had been inoperable for two (2) minutes, without entry into TS 3.0.3. Failure to enter TS 3.0.3 when required is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by the unit Technical Specifications. The cause of this historical event was attributed to a failure to address an inconsistency between Technical Specification 3.3.2 and TS 3.8.3.1 during development. Abnormal operations response procedures affected by a loss of VIAC-1 or VIAC-2 will be revised to require entry into TS 3.0.3.
4231997026 | Millstone 3 | 03/25/1997 | 04/24/1997 | 9705080228 | <strong>Missed Performances of Service Water System Support Examinations Required by ASME Section XI</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 25, 1997, with the unit in Mode 5, a review of past inservice inspection (ISI) results concluded that the American Society of Mechanical Engineers (ASME) Section XI examinations had not been performed on some Service Water System (SWS) supports during the 1989 refueling outage. Additionally, one component support had not received a successive examination as required by Section XI, Article IWF-2420 during the second period of the inspection interval. Examination of additional component supports resulted in the total population of SWS component supports being required to be examined in accordance with Section XI, Article IWF-2430. Twenty-five component supports located in inaccessible areas were not examined. Relief was not requested to exclude inspecting these component supports. Failure to perform these examinations, as required by Technical Specification (TS) Surveillance Requirement 4.0.5, is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the TS. The apparent cause of this event was an inappropriate decision regarding the classification of these component supports as inaccessible and subsequent failure to apply for relief from these inspections. The condition is significant because of the resultant operation in a condition prohibited by the Technical Specifications. However, there were no safety consequences due to the event, in that, the twenty-five Service Water System component supports which were considered inaccessible in 1989, when subsequently inspected, were determined to be acceptable. Guidance will be added to the ISI program for the ASME Section XI requirements for performing additional and successive exams and requesting relief from code requirements.
4231997027 | Millstone 3 | 03/26/1997 | 04/25/1997 | 9705060383 | <strong>Corrective Actions Not Met for Trending Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 26, 1997 with the unit in Mode 5, it was determined that trending of containment isolation valve (CIV) leakage rates, and repair or replacement of CIVs when leakage limits could not be met, were not being performed. American Society of Mechanical Engineers (ASME), titled 'Inservice Testing of Valves in Nuclear Power Plants,' paragraphs IWV-3426 and IWV-3427 were not being implemented. These paragraphs require that leakage rate trending be performed for CIVs; and that these valves be repaired or replaced when the leakage exceeds the maximum leakage limits established by the Owner for the valve, or exceeds the value determined from the leakage rate equations given in paragraph IWV-3426. The trending and corrective action requirements of Section XI of the ASME Code had not been met for the twenty-three identified instances where a penetration had exceeded its maximum leakage limit. Therefore, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as a condition or operation prohibited by the plant's technical specifications (TS). The cause of this event was determined to be inadequate implementation of commitments made during the establishment of the Inservice Testing Program (IST). This event is significant because it resulted in operating in a condition prohibited by the TS. However, there were no adverse safety consequences in that the containment integrity was not compromised because the total containment penetration leakages did not exceed the TS limit. Procedures changes will be implemented to specify that individual CIV leakages are required to be below the maximum allowable leakage limits prior to entering Mode 4. Trending of CIV leakage will be implemented, for those LLRTs performed until adoption of the new edition of Section XI. An administrative procedure will be developed to coordinate Appendix J and IST testing requirements.
4231997028 | Millstone 3 | 04/10/1997 | 05/09/1997 | 9705220334 | <strong>Potential Loss of Net Positive Suction Head Recirculation Spray System Pumps</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On April 10, 1997, with the unit in Mode 5, a review of design calculations for Net Positive Suction Head (NPSH) identified that a potential for flashing existed in the suction lines to the Recirculation Spray System (RSS) pumps (3RSS*1A,B,C&D). Calculations for the RSS System had originally determined that sufficient NPSH existed at the centerline of the first stage of the RSS pump impellers utilizing a saturated sump model. However, these calculations contained an inherent assumption that the fluid would remain single phase. This assumption is inappropriate when utilizing the saturated sump model. Flashing, resulting in insufficient NPSH, would result in cavitation of the RSS pumps, such that they might be unable to perform their intended safety functions during a design basis event (DBE). In this condition the RSS system would not be capable of supplying the minimum volume of cooling water credited in the containment analysis. Following evaluation, this condition was immediately reported on April 16, 1997, pursuant to 10CFR50.72(b)(2)(iii)(D) as a loss of safety function. It is being reported pursuant to 10CFR50.73(a)(2)(v)(D) and 10CFR50.73(a)(2)(ii)(B), as a loss of safety function and as a condition outside the unit design basis. There were no adverse safety consequences from this condition, in that the unit has not experienced a DBE and therefore operation of the RSS has not been necessary. However, the potential inoperability of the RSS pumps is significant because it represents a condition outside the design basis of the plant. The RSS s credited in the safety analyses to cool the containment by spraying containment sump water into the containment atmosphere post-accident, provide iodine removal, and provides long-term core cooling post-accident. Insufficient NPSH, resulting in cavitation, could create a common mode failure of the four RSS pumps, potentially resulting in a loss of safety function. Corrective actions to ensure operability of the RSS and compliance with the design basis will be implemented prior to entry into mode 4 from t he current outage.
4231997029 | Millstone 3 | 04/17/1997 | 05/15/1997 | 9705220358 | <strong>Design Basis Concern on Steam Generator Tube Rupture (SGTR) Analysis for Main Steam Pressure Relief Bypass Valves (MSPRBV)</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On March 17, 1997, with the unit in Mode 5, it was determined that between February 8, 1996 and March 18, 1996, the minimum number of Main Steam Pressure Relief Bypass Valve (MSPRBV) flowpaths required to depressurize the Reactor Coolant System (RCS) to satisfy the steam generator margin to overfill analysis may not have been available in the event of a Steam Generator Tube Rupture (SGTR) concurrent with a single failure. Further investigation confirmed on April 17, 1997 that the minimum number of MSPRBV flowpaths required after a SGTR combined with a single failure, could not be met. This condition existed for a period of approximately one month. This event is being reported pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition that resulted in the plant being outside the design basis. The cause of this event was a failure to recognize design and single failure requirements necessitating that the MSPRBV be included in the Technical Specifications. A Technical Specification change request establishing a requirement for control of the MSPRBVs will be submitted prior to June 15, 1997.
4231997030 | Millstone 3 | 05/01/1997 | 05/30/1997 | 9706050062 | <strong>Non-Conservation in the Low Temperature Overpressure Protection and Pressure/Temperature Limit Curves in the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1997, at 1030 hours, with the unit in Mode 5, it was identified that the current Reactor Coolant System heatup and cooldown pressure and temperature (P/T) limit curves and the Power-Operated Relief Valve (PORV) setpoint curves for the Cold Overpressure [Protection] System (COPS) contained in Technical Specifications (TS) 3.4.9.1, "Pressure/Temperature Limits," and 3.4.9.3, "Overpressure Protection Systems," respectively, were non-conservative. From initial startup until May 9, 1997, the P/T limits and the PORVs setpoint (COPS) curves contained within the TS did not properly account for instrumentation and system configuration uncertainties. Since 1993, interim administrative controls were imposed within operating procedures to account for the pressure drop across the core with the RCPs in operation. However, the PORV setpoint curves were not revised to account for this effect or the other uncertainties recently identified and therefore, PORV operation may not have occurred in the past when required. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the unit design basis. Inadequate design verification and validation was performed by the Nuclear Steam Supply System vendor and the utility. Administrative precautions on system operation minimize the likelihood and severity of COPS events. A review of system operational aspects will be performed to determine if the 10 CFR 50 Appendix G limits have been met since startup. Based on preliminary information Appendix G limits are considered to have been met.
4231997031 | Millstone 3 | 05/07/1997 | 06/05/1997 | 9706160365 | <strong>RHR Valve Low Pressure Open Permissive Bistable Setting Set Non-Conservatively</strong><br /><i>Abstract:&nbsp;</i>At 1330 on May 7, 1997, with the Unit in Mode 5, a system engineering review of the Reactor Coolant System (RCS) wide range pressure channel calibration procedures concluded that the Residual Heat Removal System (RHR) Low Pressure Interlock (LPI) setpoint did not comply with Technical Specification (TS) Surveillance Requirement 4.5.2.d.1. The existing LPI setting allows the RHR isolation valves to be opened at RCS pressures higher than those presented in the TS. Consequently, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as a condition or operation prohibited by the plant's TS. This condition was caused by the implementation of incorrect calibration information supplied during unit initial startup. However, there were no adverse consequences as a result of the event since the RHR pressures did not exceed the RHR suction header relief valve limits. No immediate corrective action is required, however, prior to entry into Mode 4, the RHR suction/isolation valve LPI bistable calibrations will be re-evaluated and the LPI bistables will be recalibrated to comply with the TS.
4231997032 | Millstone 3 | 05/16/1997 | 06/13/1997 | 9706270059 | <strong>Calibration of Pumped Capacity Monitoring System Timers Not In Accordance With 18 Month Surveillance Requirement of the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1997, with the unit in Mode 5, it was identified that the run timer-relays (62A and 62B) associated with the unidentified leakage sump pump (3DAS-P10), had not been tested at the proper frequency. These relays are part of the Containment Drain Sump Level and Pumped Capacity Monitoring System listed in Technical Specification (TS) 3.4.6.1, "Reactor Coolant System Leakage, Leakage Detection Systems." TS Surveillance Requirement (SR) 4.4.6.1.b states that the "Containment Drain Sump Level and Pumped Capacity Monitoring System - be tested by performance of a CHANNEL CALIBRATION at least once per 18 months. Contrary to this, the unidentified leakage sump pump run timer-relays have been calibrated on a 3 year frequency as part of the Preventative Maintenance program since initial plant startup. Therefore, because calibration of the unidentified leakage sump pump timer-relays was not performed every 18 months as required by SR 4.4.6.1.b, the CHANNEL CALIBRATION requirements were not met. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the unit's Technical Specifications.
4231997033 | Millstone 3 | 05/27/1997 | 06/26/1997 | 9707080427 | <strong>P-6 Bistable Reset Function Set Non-Conservatively Resulting in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1997, with the Unit in Mode 5, a system engineering review of Technical Specification (TS) interlocks concluded that the Intermediate Range Neutron Flux, P-6 interlock was calibrated in a manner that did not comply with TS, Table 2.2-1, "Reactor Trip System Instrumentation Setpoints," Functional Unit 18(a). The P-6 interlock reset value of 5.0 E-11 amps, where the interlock function is automatically reinstated on decreasing power, is set per approved procedures lower, and therefore, less conservative than the Allowable Value specified in TS Table 2.2-1 of greater than or equal to 6.0 E-11 amps. This would result in instances between 5.0 and 6.0 E-11 amps where the Intermediate Range Neutron Flux, P-6 interlock would be bypassed and the Source Range Neutron Flux monitoring instrumentation not re-energized and OPERABLE as required. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition or operation prohibited by the plant's Technical Specifications. This is an historical event and the cause is indeterminate. The potential impact of the P-6 interlock bistable reset value on TS compliance was only recognized recently during the reviews of design and licensing basis documentation. The Source Range Neutron Flux trip is not credited within the safety analyses but provides a tertiary backup to the Power Range Neutron Flux - Low Setpoint trip if an uncontrolled rod withdrawal error event from a subcritical or low power condition occurred. Consequently, even though a violation of the TS occurred there were no adverse safety consequences as a result of this event. The Intermediate Range Neutron Flux, P-6 interlock bistable calibration will be brought into compliance with the TS.
4231997034 | Millstone 3 | 05/29/1997 | 06/27/1997 | 9707070113 | <strong>Valves Not Included in Containment Isolation Valve Surveillance</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1997, with the unit in Mode 5, it was discovered during a Configuration Management Program review of a commitment closure package, that the Containment Manual Isolation (Outside Containment) Valve Checklist did not contain the complete list of manually operated containment isolation valves (CIVs) that required monthly closure verification. Technical Specification (TS) Surveillance Requirement (SR) 4.6.1.1 (a) states that in Modes 1 through 4, all penetrations not capable of being closed by operable containment automatic valves or operator action, be verified closed at least once per 31 days to ensure the integrity of the containment isolation boundary. This is a failure to follow the SR and is reportable pursuant to 10 CFR50.73(a)(2)(i)(B) as a condition or operation prohibited by the plant's Technical Specifications.
4231997035 | Millstone 3 | 06/03/1997 | 07/03/1997 | 9707140458 | <strong>Potential Non-Conservatism for the Steam Generator Water Level Low-Low Setpoint Due to Process Measurement Accuracy Term Uncertainties</strong><br /><i>Abstract:&nbsp;</i>On June 3, 1997, with the Unit in Mode 5, a Configuration Management Program review identified that the present Technical Specification (TS) instrumentation setpoints for Steam Generator (SG) Water Level Low-Low may be non-conservative. Margin in interim TS setpoints developed in response to a separate issue had been utilized to account for an increase in the Process Measurement Accuracy term. However, on August 7, 1993, the SG Water Level Low-Low interim setpoints within the surveillance procedures were approved to be restored to the values specified within the TS. On June 13, 1997, the condition was determined to be reportable, and the investigation concluded that from approximately August 7, 1993, until the present, the unit has implemented a SG Water Level Low-Low setpoint that is inconsistent with the safety analyses. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the design basis. This is a historical event. The interim Steam Generator Water Level Low-Low setpoints in effect for the Process Measurement Accuracy issue were changed back to the Technical Specification values without proper coordination and administrative control, resulting in elimination of previously credited margin. The probability that the instrument will fail to actuate by the bottom 1 to 2 percent of span where there is a possibility that the Nominal Trip Setpoint could be exceeded on a decreasing level is low. Additionally, the SG Water Level Low-Low trips are a result of a 2 out of 4 logic per SG. Two or more instruments on the affected SG would have to fail to actuate by the required setpoint to not get the protective trip. Therefore, performance of the safety functions of the SG Water Level Low-Low is only minimally affected. The Steam Generator Water Level Low-Low trip function will be in compliance with the safety analyses prior to entry into Mode 4.
4231997036 | Millstone 3 | 06/05/1997 | 10/31/1997 | 9712230063 | <strong>Pipe Break Exclusion Zones Differ From Those Provided in The Final Safety Analysis Report</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1997, with the Unit in Mode 5, the Configuration Management Program Final Safety Analysis Report (FSAR) verification identified that incorrect stress analysis limits may have been used in the design of moderate-energy fluid system piping. Also, the affects of a design change which changed the Containment design from sub-atmospheric to atmospheric on Containment leakage integrity were not evaluated. These two conditions were determined to be reportable on June 9, 1997. On October 1, 1997, it was determined that the failure to include in the ISI program some weld locations (for high and certain moderate-energy lines) within penetration areas required to be identified as break exclusion areas (BEA's) was reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition or event prohibited by the plant's Technical Specifications. The cause for not applying the correct stress limits in the design of moderate-energy piping, was inadequate communication within the Architect/Engineer (A/E) organization during the original design. The cause for not reviewing the effects on Containment integrity of changing from a sub-atmospheric to an atmospheric design was inadequate technical review within the utility engineering and A/E organizations during operation. There were no adverse safety consequences from these conditions. These conditions are significant in that a through wall pipe crack would result in exceeding the leakage assumptions utilized in dose assessment calculations. Pipe stress calculations will be reconciled to the proper allowable stresses. The FSAR and design documents will be updated. The ISI program will be updated to include weld inspection for the defined BEA's.
4231997037 | Millstone 3 | 05/16/1997 | 07/22/1997 | 9708040136 | <strong>Residual Heat Removal System (RHS) Testing During Transition to Mode 4 Incorrectly Using RHS One Hour Out- of-Service Allowance</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1997, with the Unit in Mode 5, a potential violation of Technical Specifications (TS) was discovered during a review of the Units' heatup procedure. It was determined that the past practice of transitioning from Mode 5 to Mode 4 may not have been in compliance with TS Limiting Condition for Operation (LCO) 3.4.1.4.1, which requires one Residual Heat Removal System (RHR) loop be OPERABLE in Mode 5. On June 24, 1997, after evaluating RHR system OPERABILITY bases requirements, it was confirmed that during the transition period between Modes 5 and 4, there were no RHR loops OPERABLE. During heatup from Mode 5 to Mode 4, both RHR loops are sequentially aligned for safety injection mode and the suction isolation valves leak rate tested prior to the unit entering Mode 4. Historically, plant staff considered this practice as acceptable under the provisions contained in the TS which allow the operating RHR pump to be "de-energized" for up to 1 hour, and with the knowledge that the other train, although no longer aligned for RCS cooling, could be readily returned to OPERABLE status if necessary. Prior to the expiration of the 1-hour "de-energized" allowance, the unit would then transition to Mode 4 where RHR cooling is no longer required. Failure to enter the LCO action statement with no RHR cooling loops OPERABLE while in Mode 5, is a failure to follow the TS requirement and is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as a condition or operation prohibited by the plant's technical specifications. This condition was caused by an improper interpretation of the 1-hour time allowance provision contained in the TS. A Technical Specification change request will be submitted prior to plant start-up that will permit both Residual Heat Removal loops to be removed from operation during a planned heatup to Mode 4 when at least one Reactor Coolant Pump loop is operable and in operation and when two steam generators are operable.
4231997038 | Millstone 3 | 06/13/1997 | 07/11/1997 | 9707220157 | <strong>Single Failure Potential for Fuel Building Filter Exhaust Fans</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1997, with the Unit in Mode 5, during a Configuration Management Program review of documentation associated with a modification to the fuel building filter exhaust fan auto trip / overcurrent alarm, it was identified that a failure of the train's exhaust filter ventilation system filter inlet or outlet damper could stop the operating train exhaust fan and inhibit auto starting of the standby exhaust train. This would result in the loss of negative pressure in the Fuel Building. This is a historical event, attributable to a failure to recognize a design deficiency in the automatic actuation circuitry of a safety related, post-accident mitigation system. As a result of this condition, assurance that the Fuel Building Exhaust Filter Ventilation System would perform its intended safety functions can not be verified. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(D), which requires reporting of any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. No immediate actions are required since the Fuel Building Exhaust Filter Ventilation System is not required until fuel related activities are conducted. However, prior to entry into Mode 4, a design change will be prepared and implemented such that a single failure to the operating train Fuel Building Exhaust Filter Ventilation System damper will not inhibit the startup of the backup train.
4231997039 | Millstone 3 | 06/14/1997 | 07/14/1997 | 9707220209 | <strong>Inoperability of Turbine Building Sump Effluent Monitor DAS-RE50 Due to a Failure to Recognize a Design Deficiency That Resulted in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1997, with the Unit in Mode 5, during the performance of Control Room rounds, it was identified that the low pressure alarm on the Turbine Building (TB) Sump Effluent Monitor was not properly resetting after sump pump start. The TB Sump Effluent Monitor, 3DAS-RE50, reads activity levels of the TB sump water prior to discharge to the normal drainage system. The Radiation Monitoring System (RMS) alarm log was checked and it was noted that the low pressure alarm had not cleared, as expected, from the time a channel calibration was performed on the monitor on May 13, 1997, until noticed on June 14, 1997. Further investigation indicated that the low pressure condition was attributable to a rusted and partially shut inlet solenoid valve on the sump water discharge sample line. TS 3.3.3.9 (b) requires one channel to be continuously operable to monitor TB floor drain water activity levels. Because of the low sample pressure, the operability of the monitor can not be confirmed. This is a failure to follow the TS requirements and is reportable pursuant to 10CFR50.73(a)(2)(i)(B), as a condition or operation prohibited by the plant's Technical Specifications. The cause of this event was inadequate effluent monitor system design and the inability of operators to recognize a low sample pressure alarm condition. Prior to entry into Mode 4, (1) the solenoid valve will be repaired or replaced as necessary, (2) a design change will be prepared and implemented to ensure that operators are alerted to a low sample flow condition, and (3) post-calibration and restoration procedures will be reviewed and revised, as necessary, to ensure operability of the effluent monitor. In addition, (4) other similar type radiation monitors will be evaluated for applicability to this condition.
4231997040 | Millstone 3 | 06/27/1997 | 07/25/1997 | 9708190083 | <strong>Historical Event: Quarterly IST Closure Testing of Service Water System Check Valves 3SWP*705, 706, 707 and 708 Not Performed</strong><br /><i>Abstract:&nbsp;</i>On June 27, 1997, with the unit in Mode 5, a Configuration Management Program (CMP) review of historical inservice testing activities identified that four check valves in the Service Water (SW) System (3SWP*V705, 3SWP*V706, 3SWP*V707 and 3SWP*V708) had not been exercised closed quarterly during the first operating cycle, as then required by the American Society of Mechanical Engineers (ASME) Code, Section XI, required In-Service Testing (IST) Program, and relief from Code requirements had not been granted by the Nuclear Regulatory Commission. Technical Specification (TS) Surveillance Requirement 4.0.5.a required, in part, that the unit be maintained in accordance with ASME Section XI (as specified in 10 CFR 50.55a) "... except where specific written relief has been granted." Not performing this required testing is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as an event or condition prohibited by the Technical Specifications. The cause of this event was a programmatic or managerial deficiency where the required testing for these valves was not addressed within the IST Program. This is a historical event identified as part of the CMP review process. There were no safety consequences from this event because the four SW System check valves, when subsequently disassembled and inspected in accordance with the approved relief, were determined to be capable of performing their required closure function. Corrective actions implemented in response to LER 96-021-00 should reduce reoccurrence of this type of condition due to administrative controls placed in the IST Program. On January 15, 1988, following approval of the relief request for these Service Water System check valves the IST Program was brought into compliance with the requirements of 10 CFR 50.55a for these valves. No further corrective actions are required.
4231997041 | Millstone 3 | 06/10/1997 | 08/13/1997 | 9708190079 | <strong>Voluntary Report: Operation of Service Water System With Only One Pump Operable</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1997, with the Unit in Mode 5, it was identified during review of a proposed Technical Specifications (TS) Bases change, that on those occurrences when Millstone Unit 3 (MP3) personnel removed an individual Service Water (SW) System pump from service for maintenance, the SW System may have been placed in a condition where, following a design basis Loss of Coolant Accident (LOCA), the SW System may not have been able to support the assumed Spent Fuel Pool (SFP) load several hours after the accident. With one SW pump out-of-service for maintenance, an accident scenario can be postulated where a design basis LOCA, coincident with a single failure loss of the opposite SW loop (e.g., failure of the common loop piping, or failure of the Emergency Diesel Generator supplying power to the loop), results in one SW pump remaining OPERABLE. The TS LCO does not define the number of pumps required for SW loop operability. As a result, from initial unit startup until the current outage, while in Modes 1 through 4, individual SW pumps have been removed from service without entry into a TS Allowed Outage Time (AOT). The combination of events necessary for this accident scenario to occur are remote. One SW pump can provide the minimum cooling requirements necessary to mitigate the consequences of a design basis LOCA coincident with a single failure of the opposite SW train. However in the MP3 FSAR, several hours post-LOCA, additional SW cooling is relied upon necessitating OPERABILITY of a second SW pump. There were no actual safety consequences as a result of this finding. As a result of this discovery, an OPERABLE SW loop will be defined as two pumps per loop. This Licensee Event Report is voluntary and was determined to be not reportable.
4231997042 | Millstone 3 | 07/01/1997 | 08/02/1997 | 9708190047 | <strong>Reactor Coolant Dilution Isolation Valves Inoperable Due to Not Being Included in the In-Service Test Program Results in the Inoperability of the Emergency Boration System</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1997, with the unit in Mode 5, a Configuration Management Program review of the Chemical and Volume Control System (CHS) identified three valves (3CHS*FCV111A, 3CHS*V302 and 3CHS*V310) with an active safety function that had not been included in the In-Service Testing (IST) Program. These valves have not been tested in accordance with the requirements of Section XI of the American Society of Mechanical Engineers Code as required by Technical Specification (TS) 4.0.5. This condition was determined to be reportable on July 3, 1997. Because these valves have not been tested they can not be considered capable of performing their intended safety functions, which rendered the Boric Acid Storage System's flow path(s) INOPERABLE, resulting in several occasions where the requirement for two operable flow paths of TS 3.1.2.2, "Boration Systems Flow Path - Operating" was not maintained. Operation of these valves is necessary to ensure the capability of the emergency boration function to achieve Safety Grade Cold Shutdown. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as an event or condition prohibited by the Technical Specifications and 10 CFR 50.73(a)(2)(v)(D), as a loss of safety function. The cause of this condition was a programmatic deficiency where the required testing for these valves was not recognized and addressed within the IST Program. There were no adverse safety consequences from this condition, in that the unit has not experienced a Design Basis Event where operation of the emergency boration function has been necessary. The IST Program Plan and surveillance test procedures will be revised to indicate the testing requirements for these valves and they will be tested to demonstrate operability.
4231997043 | Millstone 3 | 06/23/1997 | 07/25/1997 | 9708190073 | <strong>Inadequate TS Surveillances for the ESFAS and Reactor Trip System Instrumentation Interlocks: for Pressurizer Pressure, P-11; Low-Low Tavg, P-12; and Turbine Impulse Chamber Pressure, P-13</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1997, with the unit in Mode 5, it was identified during a system engineering review of Technical Specification (TS) interlocks that surveillance test procedures may not have adequately tested the Engineered Safety Features Actuation System (ESFAS) interlock for Pressurizer Pressure, P-11 (required OPERABLE in Modes 1, 2 and 3). On June 30, 1997, it was determined that the testing was not adequate and therefore this condition was determined to be reportable. Additionally, it was identified during the investigation that the ESFAS interlock for Low-Low Tavg, P-12 (required OPERABLE in Modes 1, 2 and 3) and the Reactor Trip System interlock for Turbine Impulse Chamber Pressure, P-13 (required OPERABLE in Mode 1) had also not been adequately tested during certain plant conditions. Failure to perform a complete Analog Channel Operational Test (ACOT) or Channel Calibration in accordance with the TS requirements resulted in transitions through operational modes without surveillance requirements being met. This is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition or operation prohibited by the unit's TS. This is a historical event and the cause is indeterminate. The system design and testing information provided by the Nuclear Steam Supply System vendor did not include testing provisions to generate a change in state of the channel bistable status light when performing the ACOT or the channel calibration under the plant conditions when the bistable is deenergized. A review of surveillance test records indicate that P-11, P-12 and P-13 were successfully calibrated and tested at subsequent test performances under plant conditions where the bistable was energized. This provides assurance that the instrumentation would have functioned properly. The Channel Calibration and ACOT procedures for P-11, P-12 and P-13 will be revised to comply with the TS.
4231997044 | Millstone 3 | 07/01/1997 | 07/31/1997 | 9708110062 | <strong>Missed Technical Specification Surveillance of ESFAS Purge Isolation Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1997, with the unit in Mode 5, it was identified as part of a review of scheduled I&C surveillances, that the Engineered Safety Features Actuation System (ESFAS) Containment Purge Isolation Instrumentation had not been tested at the required frequency stated in the Technical Specifications (TS). In addition, during a follow-up investigation, it was identified that on April 1, 1996, with the unit in Mode 5, the unit had conducted a containment purge with less than the minimum number of radiation monitoring channels operable. These two instances are a failure to follow the TS requirements and are reportable pursuant to the requirements of 10CFR50.73(a)(2)(i)(B), as a condition or operation prohibited by the plant's Technical Specifications. The primary cause of the missed TS Surveillance was not including conditional surveillance triggering mechanisms in cooldown and containment purge procedures, and inadequate management of the transfer of responsibilities for the performance of TS conditional surveillances. The performance of the containment purge without having the minimum number of radiation monitoring channels operable, was attributed to an improper interpretation of the Limiting Condition for Operation (LCO) ACTION Statement. On June 27,1995, a TS change package was prepared and submitted to remove the ACTION statement ambiguity and clarify the intent. This change was approved and implemented on June 27, 1996. Additionally, conditional surveillance triggering mechanisms will be incorporated into the operational cooldown and the containment purge procedures by September 1, 1997.
4231997045 | Millstone 3 | 06/16/1997 | 08/01/1997 | 9708130320 | <strong>Reactor Trip System Response Time Testing Not in Verbatim Compliance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 16, 1997, with the unit in Mode 5, a Configuration Management Program (CMP) review identified a discrepancy between the Final Safety Analysis Report (FSAR) and the Technical Specification (TS) definitions of the Reactor Trip System (RTS) Response Time. This condition was determined reportable on July 3, 1997. The end point of reactor trip system response time testing as defined by TS exceeds the end point as defined by the FSAR by the amount of time it takes for the magnetic field In the stationary gripper coil to decay and with it the voltage produced by the coil because of the decay of the field. This difference has been specified by the manufacturer to be approximately 150 milliseconds. Evaluation of the combined response time testing, demonstrated that the RTS response time falls within the TS response time allowance. However, the unit is not in verbatim compliance with the Technical Specification definition for RTS response times. Therefore, this condition is reportable pursuant 10 CFR 50.73(a)(2)(i)(B), as a condition or event not in compliance with the Technical Specifications. This is an historical event and the cause is indeterminate. There was a misconception that performing the response time testing in accordance with the FSAR met the intent of the TS requirement. A causal factor in this lack of understanding was that management expectations and guidance regarding literal compliance with TS were neither clear nor adequately communicated throughout the organization. The Final Safety Analysis Report definition of Reactor Trip System response time testing will be changed to match the definition within the Technical Specifications, and the Reactor Trip System response time surveillance test procedure will be revised to comply with the Technical Specification RTS response time definition.
4231997046 | Millstone 3 | 07/11/1997 | 08/08/1997 | 9708190100 | <strong>Containment Recirculation Spray System Cubicle Flood Potential</strong><br /><i>Abstract:&nbsp;</i>On May 23, 1997, with the unit in Mode 5, a Configuration Management Program (CMP) review revealed that inleakage of groundwater results in a potential to flood the Recirculation Spray System (RSS) pump cubicles in the Engineered Safety Features Building (ESF), if the non-safety related sump pumps should fail to operate. On July 11, 1997, upon further investigation into the event, it was determined that this situation could result in the loss of both trains of RSS. The RSS cubicle non-safety related sump pumps are not fed from vital AC power. Being non-safety related, the RSS cubicle sump pumps cannot be credited as available, post-accident. Therefore, groundwater inleakage could accumulate in each of the RSS cubicle sumps which are connected to the drainlines under the Containment basemat. If the sumps are not pumped out, the groundwater could eventually affect both trains of the RSS. This is an unanalyzed condition which could lead to loss of both trains of RSS and is reportable pursuant to 10CFR50.73(a)(2)(v)(D), as any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This is a historical event. The cause of this condition was a design deficiency. The potential impact on RSS operability of inleakage into the sumps in the RSS Pump cubicles was not recognized during initial plant design. This condition was identified as part of the Configuration Management Program review process. The Recirculation Spray System is required to be operable in Modes 1 through 4. Consequently no immediate corrective action is required with the unit in Mode 5. Prior to entry into Mode 4, a design modification will be implemented to address the Recirculation Spray System cubicle sumps groundwater inleakage condition.
4231997047 | Millstone 3 | 08/15/1997 | 09/15/1997 | 9709240137 | <strong>Failure to Completely Test the Thermal Overload Bypass Protection Logic of Safety Related Motor Operated Valves that Receive Multiple Actuation Signals</strong><br /><i>Abstract:&nbsp;</i>On August 13, 1997, with the unit in Mode 5, it was identified that the testing of the safety-related motor operated valves (MOVs) which receive multiple actuation signals, may not have been adequately tested to ensure that the thermal overload protection, was bypassed for each actuation signal as required by Technical Specification (TS) 3.8.4.2.1, "Electrical Power Systems, Motor-Operated Valve Thermal Overload Protection". On August 15, 1997, it was determined that the testing performed was not adequate, and that this condition was reportable. This condition was discovered and described in accordance with the Millstone Corrective Action program via Condition Report M3-97-2613. Because proper operation of the thermal overload bypasses was not demonstrated, and this situation existed when the MOVs were required to be OPERABLE, this resulted in performance of inadequate (or incomplete) surveillances, which are equivalent to missed TS surveillances. TS 4.0.3 states, "Failure to perform a Surveillance Requirement within the allowed surveillance interval, defined by Specification 4.0.2, shall constitute noncompliance with the OPERABILITY requirements for a Limiting Condition for Operation." This is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition or operation prohibited by the unit's TS. Although, direct verification that the thermal overload protection would be properly bypassed upon receipt of each individual signal was not performed, there were no safety consequences involved in that the portions of the circuits, which function as the thermal overload bypass circuitry, are tested during loss of power and slave relay surveillance testing. This is a historical event and the cause is indeterminate. By inspection, the root cause is considered to be inadequate initial development of the applicable surveillance test procedures. Prior to entry into Mode 4, surveillance testing procedures will be revised and testing performed such that the thermal overload bypass function is tested for Reactor Plant Component Cooling Water valves 3CCP*MOV222 through 229 and Service Water System valves 3SWP*MOV115A and B.
4231997048 | Millstone 3 | 08/06/1997 | 09/05/1997 | 9709120212 | <strong>Oversized Primary Grade Water System Pump Impeller Could Result in Boron Dilution Event</strong><br /><i>Abstract:&nbsp;</i>On August 6, 1997, with the unit in Mode 5, it was identified during an engineering review of the Primary Grade Water System (PGS) pump flow rate calculation, that a non-representative pump curve had been used to determine the maximum boron dilution flow rates. This condition was discovered and described in accordance with the Millstone Corrective Action Program via Condition Report M3-97-2539. Prior to initial unit startup in 1986, a number of efforts were conducted to address the inability of the PGS pumps to attain their design flow rate. A review of historical engineering and design coordination reports identified several system modifications that were implemented at that time to increase the flow rates. These included replacing the original 7-inch pump impellers with 7.5-inch impellers. However, this design change was not addressed in the PGS flow rate calculation used for the Boron Dilution Event Safety Analysis. Design engineering has estimated that the pump flow rate with the larger 7.5-inch impellers would be approximately 154 gpm and 170 gpm for one and two pumps operating, respectively. The use of the larger diameter impeller for both one and two pump operation, results in estimated dilution flow rates greater than those assumed within the safety analysis. Consequently, this is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B), as any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded, or that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. The cause is attributed to insufficient configuration control within the design control program. During the timeframe when the system was modified, there was an incomplete evaluation of the impact of the changes on the boron dilution event analysis. As a compensatory action, the valves used to isolate the dilution path ways have been administratively locked closed to preclude the possibility of uncontrolled boron dilution of the RCS. Prior to entry into Mode 4 and, before using the PGS for reactor coolant system makeup, the system will comply with the flow rate limits of the boron dilution event analysis.
4231997049 | Millstone 3 | 09/10/1997 | 10/14/1997 | 9710210149 | <strong>Inadvertant Reactor Coolant System Positive Reactivity Addition While Entered into the Limiting Condition for Operation Action Statement is a Violation of the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1997, with the unit in Mode 5, while performing a test start of the "C" Charging System (CHS) Pump to verify proper breaker alignment, approximately 30 gallons of Refueling Water Storage Tank (RWST) water was inadvertently added to the Reactor Coolant System (RCS). The boron concentration of the water was 14 ppm lower than that in the RCS (2763 verses 2777 ppm). At the time of the RCS water addition, the unit had previously entered the action statements for Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.2.1 and 3.1.2.3 due to a surveillance test failure of a charging pump sealing and lubrication temperature control valve. While in Mode 5, LCO 3.1.2.1 requires that a boron injection flow path be available while LCO 3.1.2.3 requires that one charging pump in that boron injection flow path (required by LCO 3.1.2.1) be operable. The LCO ACTION statements for both prohibit core alterations or positive reactivity additions. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications. The apparent cause of this event was inadequate verification and validation of the system configuration prior to conducting the pump test. Operations department shift personnel will be counseled on management expectations for plant configuration changes during procedural usage (adequate pre-job brief and flow path validation, etc.), and expectations for configuration changes, by December 15, 1997. In addition the operators will be trained in fundamental human performance error reduction techniques by March 15, 1998.
4231997050 | Millstone 3 | 10/17/1997 | 11/15/1997 | 9711250345 | <strong>Non-Environmentally Qualified Parts Installed in Safety Related Components</strong><br /><i>Abstract:&nbsp;</i>On October 17, 1997, with the unit in Mode 5, it was determined that unqualified replacement parts that affected the equipment's historical operability, had been installed in the unit's four (4) feedwater isolation valves (FWIVs). The non-qualified parts were purchased and were installed in the valves during previous FWIV service overhauls. There is no documentation to support the environmental qualification of these parts. Under harsh environmental conditions, failure of the non-Electrical Environmental Qualification (EEQ) parts could potentially prevent the valves from performing their safety function. Consequently, this condition is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the design basis of the plant. The cause of this event was a program deficiency, in that the program lacked the detail and definition required to properly identify and maintain technical parts information. There were no safety consequences as a result of the event in that the FWIVs have not failed to operate when required. Additionally, safety-related Feedwater Flow Control and Bypass Level Control valves located upstream of the FWIVs automatically close on a feedwater valve isolation signal and provide another means to isolate the feedwater system should the FWIVs fail to close. The FWIVs will be inspected and unqualified parts will be replaced. Work orders will be reviewed for similar conditions and corrected as necessary. The EEQ programmatic issues that led to the non-qualified parts being installed in the FWIVs are being addressed within the Millstone Corrective Action Program.
4231997051 | Millstone 3 | 10/07/1997 | 11/05/1997 | 9711140274 | <strong>Design Deficiency for 4.16 Kilovolt Feeder Fault Clearing Times</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1997, with the unit in Mode 5, it was identified that the overcurrent protection design for 4.16kV feeder circuits (non-Class 1E and Class 1E) does not clear a short-circuit in sufficient time to provide adequate cable protection for short-circuit conditions. The overcurrent protection design is relied upon implicitly to respond to a short circuit within the Fire Protection and Appendix R Program analysis bases. This condition is reportable pursuant to 10 CFR 50.73 (a)(2)(ii)(B), as a condition outside the unit design basis. The cause for this condition was an inadequate design control process during original design implementation. This condition includes a lack of verification and validation of calculation design inputs by the Architect/Engineer and the utility engineering organizations during construction. There were no adverse safety consequences from this condition. However,this condition is significant in that it is contrary to the Fire Protection and Appendix R Program analysis bases. The electrical protection relaying scheme for the individual 4.16kV affected circuits will be restored to conformance with the design basis.
4231997052 | Millstone 3 | 10/14/1997 | 11/12/1997 | 9711210302 | <strong>Deficiencies Identified in the Performance of Surveillances for PORV Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1997, with the Unit in Mode 5, it was identified that the Channel 1 and 3 Pressurizer Pressure Narrow Range channel calibration Technical Specification (TS) surveillance procedures do not test the controller card and the Manual /Auto (M/A) station components which provide a pressurizer high-pressure signal input to the "A" Train Power Operated Relief Valve (PORV) logic. This condition was determined reportable on October 14, 1997. Review of the preventative maintenance (PM) history indicates that the control circuitry (controller card and M/A Station input) was last calibrated in September 1993. The 18 month recalibration should have been performed prior to July 1995. This could not be verified to have occurred. This constitutes a lapsed TS surveillance. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications. The cause of this event was a procedural deficiency. The root cause was a failure to establish the correct calibration standard for the "A" Train pressurizer pressure narrow range channels. Preventative maintenance records indicate satisfactory calibration of the controller card circuitry in September 1993 and again in October 1997. This provides reasonable assurance that the controller card and M/A station input to the controller card was operable between the July 1995 through March 1996 timeframe and would have functioned appropriately. Prior to entering Mode 3, the Manual / Auto Station component will be individually calibrated, applicable surveillance procedures will be revised to include the omitted pressurizer pressure narrow range channel calibration components, and a review of surveillance procedures will be conducted to determine if there are other missed occurrences of Technical Specification components actuated by control cabinet circuitry.
4231997053 | Millstone 3 | 10/24/1997 | 11/24/1997 | 9712030010 | <strong>Channel Check Surveillance Requirements not in Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1997, with the unit in Mode 5, a reportable condition was determined as a result of a Technical Specification (TS) procedure validation review, that Steam Generator [SG] Blowdown Effluent Line flow rate Channel Checks had not been performed as required. On November 4, 1997, other reportable conditions were determined from this review, that Channel Checks had also not been performed for the Turbine Building Floor Drains Flow Rate Measurement Device, the Unit 3 Vent Stack (Turbine Building) Stack Flow Rate Monitor and Sampler Flow Rate Monitor, and the Engineered Safeguards [ESF] Building Monitor Discharge Flow Rate Monitor and Sampler Flow Rate Monitor as required by TS 3.3.3.9, "Radioactive Liquid Effluent Monitoring Instrumentation Surveillance Requirements" and TS 3.3.3.10, "Radioactive Gaseous Effluent Monitoring Surveillance Requirements." These conditions are reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as events or conditions prohibited by the TS. This condition was found during an ongoing investigation into Technical Specification implementing procedure deficiencies. Additionally, a common cause analysis has been performed regarding the implementation and scheduling of Technical Specification requirements within surveillance procedures. There was no safety significance or consequences from these conditions. The failure to perform the specified Channel Checks has not resulted in any loss of function for this instrumentation. Parameter Limit verifications while not completely equivalent to Channel Checks were performed and provide some indication of Operability. Procedures will be corrected to reflect Channel Check Surveillance Requirements consistent with the TS.
4231997054 | Millstone 3 | 10/29/1997 | 06/19/1998 | 9806290378 | <strong>Westinghouse Fuel May Exceed 10 CFR 50.46 Maximum Cladding Design Criteria</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1997, with the unit in Mode 5, Westinghouse informed Millstone Unit 3 that a developmental fuel rod performance modeling computer code indicated that in very limiting cases for high power, high burnup Integral Fuel Burnable Absorber fuel rods, that the calculated pressures within the rod could be in excess of the fuel rod design criterion and the pellet-to-clad gap could re-open. This could result in the 17 percent (%) maximum cladding oxidation limit, defined in 10 CFR 50.46, potentially being exceeded following a postulated Loss of Coolant Accident (LOCA). On October 29, 1997, this condition was reported as an event or condition outside the design basis of the unit pursuant to 10CFR50.72(b)(1)(ii)(B). During performance of the Cycle 6 gap re-opening evaluation, one fuel assembly was predicted to exceed the maximum cladding oxidation limit by the end of the current cycle. This condition was identified by Westinghouse. Preliminary, generic reviews revealed that the modeling criteria assumptions may be potentially non-conservative regarding fuel rod internal pressures, cladding corrosion rates, and gap re-opening limits for certain combinations of fuel design features and operating conditions. There were no adverse safety consequences as a result of this condition. Westinghouse has performed a plant specific evaluation for Millstone 3 Cycle 6. This evaluation concludes that none of the fuel assemblies in the Cycle 6 core have the combination of design features which make them susceptible to the gap re-opening scenario. Administrative controls will be in place to ensure that the limiting fuel assembly is in compliance with the 17 % limit for maximum cladding oxidation.
4231997055 | Millstone 3 | 11/05/1997 | 12/05/1997 | 9712160135 | <strong>Historical Event: Area Temperature Monitoring Element Mounted in Wrong Location Resulting in No Area Temperature Monitoring Within The B and D Pump Recirculation Spray System Cubicle</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1997, it was identified that area temperature monitor (3ECS-TE098) utilized to fulfill the weekly area temperature monitoring requirement of Surveillance Requirement 4.7.14 of Technical Specification (TS) 3.7.14, "Area Temperature Monitoring," was not installed within the area intended to be monitored. TS 3.7.14 requires monitoring within the Engineered Safeguards Building (ESF) Recirculation Spray System (RSS) pump cubicles (Environmental Zone ES-05). This area temperature monitor was actually located within the Heating Ventilation and Air Conditioning and Motor Control Center Area (Environmental Zone ES-01) on the wall adjacent to the ESF Building RSS B and D pump cubicle. Failure to perform area temperature monitoring within the B and D RSS pump cubicle is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's TS. This is a historical event. The cause of this condition was human error and inadequate validation by the Architect/Engineer and Northeast Nuclear Energy Company (NNECO) of design documents. A physical location drawing within the design document located the monitor within environmental zone ES-01 rather than on the other side of the wall within the B and D RSS pump cubicle environmental zone (ES-05). The average temperature experienced within the A and C RSS pump cubicle during the period from January 1, 1991, to December 31, 1994, was less than the average temperature assumed in the qualified life evaluation. Assuming the B and D RSS pump cubicle temperatures were similar to the A and C RSS pump cubicle temperatures, the qualified life of the equipment in the B and D RSS pump cubicle has not been compromised. Area temperature monitor 3ECS-TE098 will be moved to within the B and D RSS cubicle prior to entry into Mode 4.
4231997056 | Millstone 3 | 11/07/1997 | 12/05/1997 | 9712150028 | <strong>Service Water System Drainage Following a Containment Depressurization Actuation and Loss of Power Could Result in a Condition Outside the Design Basis of the Unit</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1997, with the unit in Mode 5, during a review of original construction era Service Water System (SW) Design Deficiency Reports, it was determined that following the initiation of a Containment Depressurization "A" (CDA) signal coincident with a loss of offsite power (LOP), SW System pressures may not be sufficient to refill the SW supply piping to the control building air conditioning (A/C) condensers. Although SW flowrates are tested at each refueling outage, the test does not replicate design basis conditions, e.g., a degraded SW pump, high SW strainer differential pressure and a low intake water level as well as a LOP. If SW cooling water flow to the control building A/C condensers is lost, air temperatures could ultimately rise high enough to adversely affect the operability of safety-related equipment contained within the control building. However, there have been no adverse safety consequences as a result of this condition in that the unit has not experienced a CDA coincident with a LOP accident. This is a condition outside the design basis of the plant and is being reported pursuant to 10CFR50.73(a)(2)(ii)(B). The event is historical and is attributable to a design deficiency in the Service Water System. A design modification will be implemented to ensure that sufficient Service Water system pressure is available to refill the control building A/C condensers following a design basis accident.
4231997057 | Millstone 3 | 11/13/1997 | 12/18/1997 | 9712310359 | <strong>"A" Emergency Diesel Generator Inoperable Due To Ventilation Alignment Prohibiting Tornado Recovery</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1997, with the unit in Mode 5, it was identified that the "A" Emergency Diesel Generator (EDG) may have been inoperable from October 11, 1997. On October 11, 1997, the air intake damper for the Emergency Ventilation System serving the "A" EDG cubicle failed open. The exhaust dampers had been failed in the full open position as part of temporary modifications to provide cooling to support EDG operation in the event of an emergency because replacement parts could not be readily obtained. A review on November 13, 1997, of the associated safety and engineering evaluations, identified that credit had been taken for placing the EDG Emergency Ventilation System in full recirculation in order to be able to re-open the exhaust tornado dampers. This condition was determined reportable on November 18, 1997. The cause of this event was an inadequate development and review of the safety and technical evaluations associated with a temporary modification to fail open the 'A' EDG Cubicle ventilation dampers. Actions to alert personnel that a failure of the air intake damper could result in invalidating the tornado recovery actions specified within AOP 3569 'Severe Weather Conditions' were not explicitly identified and compensatory actions were not put in place. The ability of the EDG to provide emergency power in order to mitigate the consequences of an accident was not challenged during this time period. There were no safety consequences as result of this condition. However, the failure to recognize and prevent the circumstances leading to this degraded condition is safety significant. The actuator for the "A" Emergency Ventilation System air intake damper has been replaced with a functional actuator.
4231997058 | Millstone 3 | 11/22/1997 | 12/19/1997 | 9712310367 | <strong>Inadequate Technical Specifications Surveillances of the Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1997, with the unit in Mode 5, it was identified that a potential deficiency existed in the way certain logic circuits for the Solid State Protection System (SSPS) are tested at Unit 3. This concern was initially identified by Duke Energy Power Services and reported to the rest of the industry via the Institute of Nuclear Power Operations Nuclear Network. On November 22, 1997, it was confirmed that a similar condition existed at Unit 3. Three functions are inadequately tested and involve the Source Range High Voltage and Feedwater Isolation on P-14 Steam Generator Hi-Hi Level and Safety Injection. For these circuits, an internal card failure could be postulated which would not be detected by the current testing practices. The unit has operated in an operational mode without completely demonstrating the operation of these functions resulting in the performance of inadequate (or incomplete) surveillances, which are equivalent to missed Technical Specification surveillances. This is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition or operation prohibited by the unit's TS. This condition is historical and has existed since initial plant startup. As a result, the bimonthly Actuation Logic Test surveillance requirements have not been met for these functions. There was no safety significance as a result of this condition since the circuits in question have been actuated during plant operation providing reasonable assurance that the unit has not operated with an undetected failure. As a corrective action, the Solid State Protection System test procedures will be revised to include additional testing steps, and these functions retested to assure the integrity of the logic circuits.
4231997059 | Millstone 3 | 09/10/1997 | 12/22/1997 | 9801050019 | <strong>Spurious Operation of Auxiliary Feedwater Pump Turbine Exhaust Condensate Drain Line Isolation Valve During Certain Fire Scenarios May Impact Safe Shutdown Capability</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1997, with the unit in Mode 5, during preparation of a design change to upgrade the pilot solenoid valve associated with the auxiliary feedwater turbine exhaust condensate drain line, an error was identified in the BTP 9.5-1 (Appendix R) Compliance Report. Upon system actuation, the turbine exhaust drain isolation valve must close and remain closed to prevent turbine exhaust steam from entering the room, potentially impacting proper operation of the turbine. The Compliance Report identifies that this valve is not required for shutdown, based on the assumption that failure of the valve would not prevent proper operation of the turbine. Because of this classification, the consequences of spurious valve operation due to fires were not evaluated. As a result, the ability to achieve and maintain safe shutdown could not be assured for fire areas where cables associated with this pilot solenoid valve are routed and the turbine driven auxiliary feedwater pump is credited for safe shutdown. There have been no adverse safety consequences as a result of this condition in that the unit has not experienced the postulated fire damages. On November 25, 1997, this condition was identified outside the design basis of the plant and reportable pursuant to 10CFR50.73(a)(2)(ii)(B). The condition is attributable to a design deficiency introduced during construction, when it was decided to divert this condensate drain line from a drain header to the open floor drain. A design modification has been implemented to tie this exhaust condensate drain line to the existing drain header, thereby preventing exhaust steam from entering the room in the event that the valve fails to close or spuriously opens.
4231997060 | Millstone 3 | 12/09/1997 | 05/15/1998 | 9805270403 | <strong>Ineffective Implementation of the Post Accident Sampling System Program</strong><br /><i>Abstract:&nbsp;</i>On November 25, 1997. with the unit in Mode 5, a Nuclear Oversight audit finding identified several Post Accident Sampling System (PASS) program weaknesses which questioned the functionality of the system and the capability of sampling personnel to obtain and analyze reactor coolant, containment atmosphere, and containment recirculation sump samples, following a design basis accident. The audit identified specific PASS programmatic weaknesses in the areas of technician training, maintenance of equipment and supplies, instrumentation calibration and preventive maintenance activities, and PASS emergency plan drill performance. On April 15, 1998, results of a February 23-26, 1998, Nuclear Regulatory Commission (NRC) assessment inspection of the PASS identified several additional emergency response related program deficiencies that had not been previously addressed in the original report submittal (ref. LER 97-060-00). These deficiencies called into question the effectiveness of the PASS program and the ability to "ensure the capability" to obtain and analyze post-accident samples "under accident conditions." This is a failure to comply with TS 6.8.4.d and is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition or operation prohibited by the unit's Technical Specifications. The cause of this condition is attributed to a failure of management to implement an effective PASS program that ensured compliance with Technical Specification requirements. Although the ability of the PASS system to function in compliance with the TS requirements could not be assured, alternate sources could be utilized to make appropriate post-accident mitigation and protective action recommendations. There were no safety consequences as a result of this event. The corrective actions associated with these identified deficiencies have been completed with the exception of a corrective action to conduct surveillances that will verify that PASS samples can be analyzed to satisfy acceptance criteria.
4231997061 | Millstone 3 | 12/18/1997 | 01/17/1998 | 9801230362 | <strong>Technical Specification 6.8.4 leakage Reduction Program Does Not Address All Leakage Paths</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1997, with the unit in Mode 5, a Nuclear Regulatory Commission (NRC) inspection team questioned the adequacy of the Millstone Unit 3 (MP3) leakage reduction program, as required by Technical Specifications (TS) 6.8.4.a, and specifically, that present surveillances and programs may not address some possible leak paths. A recent investigation confirmed that additional leakage pathways existed that were not previously considered. On December 18, 1997, this condition was determined to be reportable and is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications. This condition is historical. An ongoing Technical Specifications (TS) Section 6.0 review attributes this condition to a failure to clearly assign ownership for the implementation of Section 6.0 programs. This lack of ownership did not foster continued improvement as rising standards were being adopted by the nuclear industry and resulted in narrowly focused corrective actions for problems with TS Section 6.0 programs. Although the ability of the leakage reduction program to minimize leakage outside of containment to as low as practical levels could not be assured, there were no safety consequences in that the unit has not experienced a design basis accident that challenged the effectiveness of the TS 6.8.4.a leakage reduction program. Corrective actions include confirmation that the program meets the licensing basis for offsite dose, testing potential leak paths and preparation/implementation (illegible print) program document. In addition, programs in TS Section 6.0 "Administrative Controls," are being reviewed as part of a separate condition report investigation.
4231997062 | Millstone 3 | 12/19/1997 | 02/11/1998 | 9802200073 | <strong>Failure to Meet Technical Specification Definition of Analog Channel Operational Test</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1997, with the unit in Mode 5, the method used to satisfy the Technical Specification (TS) Channel Functional test for digital radiation monitors was found to be out of compliance with the TS definition. The Analog Channel Operational Test (ACOT) by TS definition includes adjustments, as necessary, of the alarm, interlock and/or Trip Setpoints such that the setpoints are within the required range and accuracy. The radiation monitors that are affected are those where the ACOT was implemented by performing a source check, and then increasing the conversion factor until the alarm trips. The setpoints are not verified within a required range and accuracy using a simulated signal; and as such, verbatim compliance with the TS definition for performance of the ACOT is not achieved. On January 12, 1998, a review found that an ACOT surveillance on the 3HVR*RIY10B that was performed with a procedure revised to correct the condition remained out of compliance with the TS definition. Upon discovery of this condition the monitor was declared inoperable on January 12, 1998. This condition was determined reportable pursuant to 10CFR50.73(a)(2)(i) as a condition prohibited by TS. The apparent cause of this condition is that the test methods were historically considered in compliance with the intent philosophy behind the TS definition for the ACOT. The cause of a failure to adequately revise the procedure for 3HVR*RIY10B was personnel error and inadequate written and verbal communication. This condition has no safety significance since the testing performed was adequate to demonstrate the function of the affected instruments and no equipment failure is indicated. Radiation Monitoring ACOT procedures will be revised and surveillance tests performed to comply with verbatim interpretation of the TS definition for performance of ACOT.
4231997063 | Millstone 3 | 12/31/1997 | 06/03/1998 | 9806100085 | <strong>Inadequate Operator Response Time for Inadvertent Safety Injection (SI) Event</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1996, Unresolved Item Report (UIR) 1068 was initiated for a potential issue related to the plant operators' ability to meet the operator response time of 10 minutes assumed in Chapter 15 of the Final Safety Analysis Report (FSAR) for termination of an Inadvertent Safety Injection (SI) event. On December 31, 1997 it was determined that the assumptions contained within the FSAR could not be consistently met. This determination was made on the basis that one of ten crews had previously failed to prevent a solid water condition from occurring and that no crew met the required Inadvertent SI termination response time during simulator exercises. Because it can not be shown that the operators can consistently terminate an Inadvertent SI event within 10 minutes as described in the FSAR, and because it could not be conclusively shown that the Condition II criteria will not be exceeded, this condition is reportable pursuant to 10CFR50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. Probable causal factors identified were conflicting program requirements and lack of commitment to program implementation. These causal factors are historical in nature and further evaluation would provide no additional insight into the cause of the condition. This condition is significant to the safety of the plant. Mitigating the significance of this condition is the fact that the resulting transient is bounded by the SBLOCA analysis. Additionally, five of the six operating crews have demonstrated, on a plant specific simulator, the ability to terminate SI prior to a solid water condition occurring. There have been no adverse safety consequences as a result of this condition since the plant has not experienced an inadvertent SI while operating with a PORV block valve closed.
4241997001 | Vogtle 1 | 01/09/1997 | 02/06/1997 | 9702110341 | <strong>THERMAL OVERLOAD BYPASS JUMPER CONNECTION RENDERS ECCS VALVE INOPERABLE</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Walkdowns performed by NRC resident inspectors found the thermal overload bypass jumper for valve 1HV-8802A improperly connected. This valve is normally closed, but must be opened post-LOCA to initiate hot-leg recirculation. Technical Specification 3.8.4.2 requires the thermal overload protection to be bypassed for this valve. Within 3 hours of this discovery on January 9, 1997, the jumper was connected to the correct location. An investigation found that the last time work had been performed affecting this jumper was during the refueling outage in March 1996. The jumper had been removed and subsequently reinstalled during valve testing at that time. Due to a lack of evidence to the contrary, it was determined that the jumper must have been incorrectly installed following this valve testing. Therefore, the cause of this event was cognitive personnel error on the part of the electricians involved. The electricians were counseled regarding attention to detail, proper installation of lifted leads, and the value of independent verification. Also, this event will be addressed for maintenance personnel in 1997 continuing training.
4241997002 | Vogtle 1, Vogtle 2 | 01/22/1997 | 03/03/1998 | 9803100241 | <strong>P-4/TURBINE TRIP AND OTHER CIRCUITS NOT SURVEILLANCE TESTED</strong><br /><i>Abstract:&nbsp;</i>Following a discussion at an owners group meeting, an instruments and controls (I&C) assistant team leader (ATL) began to review testing for trip logic. On January 22, 1997, at 1700 EST, the assistant team leader discovered that a specific portion of the reactor trip breaker (RTB) contacts and wiring that generate a turbine trip were not being tested as required by Technical Specification (TS) Table 4.3-2, Item 9.b. This circuit is a part of the P-4 interlock which generates a turbine trip from a reactor trip. The control room was notified and limiting conditions for operation (LCOs) were entered per TS 3.3.2 and per TS 3.0.3 for both Train A and Train B in each unit. TS 4.0.3 was invoked to allow 24 hours for completion of the required testing. Test procedures were revised, the appropriate testing was completed satisfactorily, and LCOs were exited by 1443 EST, on January 23, 1997. The cause of this event was an inadequate review of surveillance testing requirements prior to initial plant startup. Surveillance procedures were revised and tests were successfully completed. As a result of further corrective action to continue reviewing safety related logic circuits per Generic Letter 96-01, on June 30, 1997, and on July 9, 1997, inadequate testing of other circuits was found as described herein. Appropriate testing was completed satisfactorily.
4241997003 | Vogtle 1, Vogtle 2 | 02/13/1997 | 03/11/1997 | 9703180033 | <strong>UNLATCHED DOORS ON MOTOR CONTROL CENTERS CHANGES SEISMIC QUALIFICATIONS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On December 5, 1996, an NRC inspector and a system engineer performing a walkdown discovered unlatched doors on Unit 2 motor control center (MCC) cubicles. The control room was notified and the doors were properly secured. Follow-up inspections found other unlatched MCC doors in both Unit 1 and Unit 2 that were also secured. On February 13, 1997, an evaluation of the unlatched MCCs found by the NRC inspector and the system engineer determined that a seismic event could cause the unlatched doors to these MCCs to impact interlocks and lead to breaker tripping or misoperation of other sensitive equipment. It was determined that this and other unlatched doors on safety related MCCs represented a condition that alone could have prevented the fulfillment of a safety function of a system needed to control the release of radioactive material. The cause of this event was the failure to maintain MCC doors secured. The affected MCC doors were secured as necessary. In addition, operators inspected all other class 1E MCCs and switchgear in both Unit 1 and Unit 2 to ensure that other doors were properly secured.
4241997004 | Vogtle 1 | 03/22/1997 | 04/16/1997 | 9704210214 | <strong>UNQUALIFIED CABLING RENDERS ATMOSPHERIC RELIEF VALVES INOPERABLE</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Two atmospheric relief valves (ARVs) were found to have cable splices that were not fully jacketed. The use of this cabling meant that the ARVs involved may not have been able to perform their intended safety function in the harsh environment of accident conditions. Two other ARVs with environmentally qualified cabling had remained in service, except for brief periods of maintenance. However, the unit operated in a condition prohibited by the Technical Specifications (TS), because TS 3.7.4 requires three ARVs to be operable when the unit is in Modes 1, 2, or 3. This requirement went into affect in January 1997 with the institution of the improved TS. The cause of this event was the installation of cable splices that were not environmentally qualified because the conductors were not fully jacketed. Due to the length of time since the work was performed in 1993 and 1994, an investigation was unable to determine the reason(s) that the splices were improperly installed. The ARV splices were repaired. All remaining ARVs in both Unit 1 and Unit 2 were inspected with no unqualified splices found.
4241997005 | Vogtle 1 | 08/04/1997 | 08/25/1997 | 9709050090 | <strong>TEST PROCEDURE INADEQUACY RESULTS IN AUXILIARY FEEDWATER ACTUATION</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1997, personnel were performing turbine driven auxiliary feedwater pump (TDAFWP) response time testing. At 1255 EDT, control room operators noticed a slight increase in reactor power and saw that the TDAFWP discharge valves were open, sending auxiliary feedwater (AFW) to the four steam generators. The discharge valves were subsequently closed and reactor power was stabilized at 100 percent. The cause of this event was a procedure inadequacy. The test procedure had recently been changed to remove a step for closing a manual valve that would have prevented the addition of auxiliary feedwater to the steam generators. The procedure will be revised by September 15, 1997, and this event will be discussed with all individuals involved in the preparation, review, and approval of Operations department procedures.
4241997006 | Vogtle 1 | 08/30/1997 | 09/26/1997 | 9710010026 | <strong>HYDROGEN MONITORING SYSTEM TRAIN RENDERED INOPERABLE</strong><br /><i>Abstract:&nbsp;</i>On August 30, 1997, personnel were performing a quarterly surveillance test on the Train A hydrogen monitor. They were unable to establish flow through the monitor and troubleshooting found that a manual isolation valve on the monitor inlet line was closed. Personnel opened the valve and completed the test successfully. An investigation found that this valve may have been closed for as long as 39 days. This represents a violation of the Technical Specification 3.3.3, condition B, requirement that allows one train of hydrogen monitoring to be inoperable for up to 30 days. The cause of this event was a cognitive personnel error by unknown personnel. Tests conducted during the period of time involved were reviewed. These tests do not manipulate the inlet line valve and no plausible reason for its closure could be discerned. This event will be reviewed in continuing training for appropriate personnel.
4241997007 | Vogtle 1, Vogtle 2 | 09/12/1997 | 10/10/1997 | 9710160169 | <strong>CONTAINMENT PENETRATION ELECTRICAL OVERCURRENT PROTECTION NOT TESTED</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1997, a system engineer was reviewing sections of an equivalency determination being developed by design engineering for replacing 125 volt DC non-1E circuit breakers for reactor coolant pump (RCP) control power. During the review, it was determined that the breakers provided power through containment penetrations to RCP lift oil pump pressure switches, in addition to providing power to control circuits outside of the containment. It was also found that the breakers are not tested in accordance with either the Technical Requirements Manual (TRM) surveillance requirements or the previous Technical Specification (TS) surveillance requirements which were replaced by the TRM requirements. The failure to perform containment penetration conductor protection (circuit breaker) surveillance testing represents unit operation in a condition prohibited by the previous TS surveillance requirements which were in place before January 23, 1997. The unit shift supervisors were advised and appropriate actions were taken. The cause of this event was failure to adequately document all of the containment electrical penetration circuits requiring surveillance testing during original plant startup and include these circuits in a testing procedure.
4241997008 | Vogtle 1 | 10/11/1997 | 11/10/1997 | 9711170062 | <strong>TURBINE STOP VALVES' CLOSURE SETPOINTS NOT PROPERLY SET</strong><br /><i>Abstract:&nbsp;</i>On October 11, 1997, a technician was performing an 18 month surveillance for verifying the actuation setpoint for the #1 main turbine stop valve limit switch. The function of the turbine stop valves' limit switches is to initiate an anticipatory reactor trip when four out of four stop valves close above 49 percent reactor power. The limit switch was found to be set at approximately 95 percent of valve opening instead of the 96.7 percent of valve opening required by Technical Specifications (TS). Further investigation found that the previously performed setting had been accomplished as the valve was opening. However, the trip signal is generated as the valve closes. Therefore, the previously performed surveillance to adjust the actuation setpoint was inadequate to ensure compliance with the TS setpoint. The failure to adequately perform this TS surveillance resulted in unit operation in a condition prohibited by the TS. The other three main turbine stop valve limit switches were found to be similarly out of adjustment. The cause of this event was a procedure inadequacy. The procedure used to calibrate the limit switches did not specify that the adjustment should be made as the valve closes. The limit switches were readjusted utilizing the methodology of adjusting the trip setpoint while the valve closes.
4241997009 | Vogtle 1 | 10/14/1997 | 11/05/1997 | 9711120097 | <strong>CONTAINMENT VENTILATION ISOLATION WHEN RAD MONITOR NOT BLOCKED</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1997, personnel were removing a used control rod drive shaft from the containment building. As it was taken out of the reactor refueling cavity, a containment ventilation isolation (CVI) signal was generated from radiation monitor 1RE-0002 at 0318 EDT. The CVI actuation signal from 1RE-0002 had not been blocked as planned. 1RE-0002 had been set to actuate a CVI at 15 mr/hr and the actual dose rate was 25 mr/hr. Control room personnel verified that all valves and dampers actuated as expected. The drive shaft was placed in a handling container and moved into the fuel handling building for storage in the spent fuel pool. The CVI signal and all affected components were reset. The cause of this event was a cognitive personnel error on the part of a vendor representative who failed to notify the control room when movement of the drive shaft commenced, as had been previously planned. The control room was to block the CVI actuation signal when notified. The individual involved was counseled regarding the importance of performing his assigned duties.
4241997010 | Vogtle 1 | 10/19/1997 | 11/14/1997 | 9711260107 | <strong>MANUAL REACTOR TRIP DURING CONTROL ROD DROP TIME TESTING</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1997, personnel were conducting control rod drop time testing utilizing digital rod position indicator (DRPI) in data A + B mode. As shutdown bank A rods were withdrawn, a DRPI urgent alarm sounded when rod M2 indicated being out of step by 8 steps, in contrast to the rest of the bank. When rod movement stopped, the alarm cleared and rod withdrawal was resumed. A rod deviation alarm then sounded and M2 was found to be indicating 18 steps out from the rest of the bank. A manual reactor trip was initiated at 1717 EDT. All rods inserted as designed. Because the reactor was not critical, there was no power transient. Troubleshooting indicated there were no actual rod deviations and that data B coils were the probable cause. Following troubleshooting, control rods were later withdrawn in data A only with no valid rod deviations indicated, and control rod drop time testing resumed. The cause of this event was a failed detector/encoder card in the DRPI B data cabinet. The failed card was replaced and this event will be reviewed in continuing training with appropriate personnel during the first requalification training segment in 1998.
4241997011 | Vogtle 1 | 10/19/1997 | 11/14/1997 | 9711250029 | <strong>PROCEDURE DISCREPANCY RESULTS IN OPERATION OUTSIDE OF TECH. SPECS. CONDITIONS</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1997, the unit operated in a condition prohibited by the Technical Specification (TS) per TS 3.0.3, when a condition existed that is not allowed by the TS. Safety injection (SI) valves that isolate pump discharge to the reactor coolant system (RCS) hot legs, 1HV-8802A and 1HV-880213, were opened. These valves are required to be closed with the power lockout switch in the lockout position by Surveillance Requirement (SR) 3.5.2.1 of TS 3.5.2. TS 3.5.2 is applicable in Modes 1, 2, and 3, and the valves were closed in accordance with SR 3.5.2.1 upon entry into Mode 3. However, a procedure discrepancy resulted in these valves being re-opened after entry into Mode 3. This would not have impacted emergency core cooling system (ECCS) operability because TS 3.5.2 allows the SI pumps to be inoperable for up to 4 hours after entry into Mode 3 or until reactor coolant system (RCS) temperature exceeds 375 degrees F, whichever comes first. However, after the valves were re-opened, RCS temperature exceeded 375 degrees F, thereby requiring the SI pumps to be operable. The condition of the subject valves being open rendered both trains of ECCS inoperable, and 100 percent flow equivalent to a single operable train could not be guaranteed. The cause of this event was a procedure error that specified opening valves 1HV-8802A and 1HV-8802B after entry into Mode 3. The valves were closed using a system operating procedure and the other procedure was corrected.
4251997001 | Vogtle 2 | 02/13/1997 | 03/13/1997 | 9703190079 | <strong>SURVEILLANCE NOT PERFORMED FOR UNLOCKED VALVES</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Technical Specification (TS) surveillance 3.7.5.1 requires that auxiliary feedwater (AFW) valves in water flow paths, which are not secured in position, be verified to be in the correct position every 31 days. On February 13, 1997, it was discovered that six auxiliary feedwater (AFW) valves had been neither secured nor surveilled to verify their positions since their installation during the Fall 1996 refueling outage. This failure to comply with a surveillance requirement represented unit operation in a condition prohibited by the TS. The valves were locked and added to the safety related locked valve verification checklist. In addition, TS surveillance 3.7.14.1 requires safety related chilled water system valves to be either secured or surveilled every 31 days. It was determined that a valve on the chilled water supply line to a piping penetration area cooler had not been locked since its return to service following a refueling outage in October 1996. The valve was found to be opened, as required. The cause of the AFW valves not being properly secured was the failure of engineering and operations personnel to ensure appropriate TS surveillance requirements were met upon completion of a design change. The cause of the chilled water supply line valve not being properly secured was the failure of operations personnel to properly secure the valve and verify it being secured as required by plant procedures. Lessons learned from these events will be reviewed by the appropriate personnel by April 29, 1997.
4401997001 | Perry | 01/07/1997 | 02/06/1997 | 9702100405 | <strong>Nonlicensed Operator Electrical Switching Error Results in Reactor Protection System and Other Engineered Safety Feature Actuations.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 7, 1997, at 0533 hours, the Perry Nuclear Power Plant, Unit 1, automatically scrammed from 100 percent rated thermal power, due to a loss of electrical power to the Feedwater Control system which resulted in a Reactor Protection system actuation on low reactor water level. The High Pressure Core Spray system, the Division 3 Diesel Generator, and associated support systems including Division 3 Emergency Service Water (ESW), the Reactor Core Isolation Cooling system, the Division 1 ESW system, and the Nuclear Steam Supply Shutoff system also actuated during the event. The cause of this event is personnel error; a Nonlicensed Operator failed to utilize self-checking and performed an inappropriate procedural step which resulted in the loss of electrical power to the vital loads. The pre-job briefing conducted for the switching activity did not contain sufficient detail to ensure successful completion of the switching activity. A Standing Instruction was issued to inform the operating crews of the event, to communicate expectations concerning in-field supervision and pre-job briefings, and to detail missed opportunities for preventing the event through self-checking and checking of others. Procedural enhancements are being evaluated and programmatic improvements are being developed. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv). This report is also being submitted to fulfill the requirements of Operational Requirements Manual, Special Reports, Emergency Core Cooling System Injection, Section 7.6.2.1.
4401997002 | Perry | 02/11/1997 | 03/13/1997 | 9703180227 | <strong>Breaker Trip Causes Loss of Electrical Power to Non-Class 1E Bus and Results in Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 11, 1997, at approximately 0349 hours, the Perry Nuclear Power Plant, Unit No. 1, was operating at 100 percent of rated thermal power when a non-class 1E feeder breaker to a 13.8kV/480V transformer tripped due to spurious actuation of the breaker ground fault relay. Consequently, the associated non-class 1E 480V bus was de-energized resulting in a loss of power to the Reactor Protection system (RPS) motor-generator 'B' causing a RPS half scram and Division 2 Nuclear Steam Supply Shutoff system actuation signals resulting in Balance-of-Plant, Main Steam Line Drain, and Reactor Sampling isolations. Reactor power was subsequently reduced to approximately 58 percent due to loss of power to an isolated phase bus duct cooling fan in conjunction with failure of the standby fan to continue to provide replacement cooling. Following troubleshooting and rework, the plant was returned to 100 percent of rated thermal power at approximately 1736 hours on February 11, 1997. Engineering investigation indicates that the event was caused by the isolated random component failure (i.e., the ground fault relay). The ground fault relay was replaced and tested prior to return to service. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv) as an event that resulted in the automatic actuation of an engineered safety feature.
4401997003 | Perry | 03/22/1997 | 04/21/1997 | 9704240094 | <strong>Loss of Electric Power to Protection Systems Bus Due to Electrical Protective Assembly Trip Results in Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 22, 1997, at approximately 1938 hours, the Perry Nuclear Power Plant, Unit No. 1, was operating at 1 00 percent of rated thermal power when electrical power from the Reactor Protection system (RPS) motor generator (MG) set 'B' to RPS bus 'B' was lost. As a result, RPS 'B' electrical power was removed from Division 2 and 4 RPS logic as well as Division 2 Nuclear Steam Supply Shutoff system (NSSSS) isolation logic. Subsequent to the loss of RPS 'B' electrical power, an RPS B and D channel half scram and the expected annunciations were received. The loss of RPS 'B' electrical power to the Division 2 NSSSS; isolation logic resulted in the initiation of Balance of Plant isolation, Reactor Water Cleanup isolation, Residual Heat Removal isolation, Main Steam Line Drain isolation, and Reactor Sampling isolation actuation signals. RPS bus 'B' was aligned to its alternate power source, the half scram and Division 2 NSSSS isolation signals were reset, and plant operators restored from the event in accordance with plant procedures. The event resulted from the trip of an Electrical Protective Assembly (EPA) due to random failure of the associated logic control board. Results of the failure analysis by the vendor indicate that integrated circuit chips associated with the undervoltage and underfrequency trip circuitry were found to be in a defective/degraded condition. The logic control board for the EPA was replaced with an updated board. Additionally the eight logic control boards currently installed in the plant are scheduled to be replaced with a newer designed logic control board.
4401997004 | Perry | 05/16/1997 | 06/26/1997 | 9707020412 | <strong>Invalid High Suppression Pool Level Signal Results in Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1997, with the plant in Mode 1 at 100 percent of rated thermal power during a scheduled Division 3 High Pressure Core Spray (HPCS) system maintenance outage, a test instruction was being performed to collect and analyze motor operated valve test data with the HPCS system operating in the Condensate Storage Tank (CST) to CST test mode. The manual containment isolation valves associated with the HPCS Suppression Pool Water Level-High transmitters were tagged closed to accommodate other Division 3 outage activities. At 2219 hours, after approximately 8 minutes of HPCS pump operation, the HPCS pump suction path automatically realigned from the CST to the suppression pool. HPCS Suppression Pool Water Level-High instrumentation indicated tripped on high water level although the actual suppression pool level was not high. The cause of the event is a procedural weakness. The tagout guidance is not adequate to ensure that when instrument loops are mechanically isolated, the electrical logic functions associated with the equipment are also verified, reviewed, and defeated if required. Ambient temperature increase due to heat from the pump motor operation resulted in a small pressure increase within the isolated high pressure sensing line of the transmitters. The small pressure increase was sufficient to trip the instrumentation and initiate the suction transfer. Appropriate administrative guidance will be revised to address potential problems when instrument loops are isolated during operation of associated system equipment.
4401997005 | Perry | 06/05/1997 | 07/07/1997 | 9707140117 | <strong>Automatic Reactor Scram Following Auxiliary Transformer Trip</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1997 at 1050 hours, the Perry Nuclear Power Plant (PNPP), Unit No. 1, was operating at 100 percent rated thermal power, when an automatic reactor scram occurred due to a 13.8 kV cable termination bus bar support fault at the auxiliary transformer, and subsequent auxiliary transformer phase differential relaying, generator lockout, turbine trip, and turbine control valve fast closure. The event was initiated when a three phase ground fault occurred on the 13.8 kV supply side termination compartment of the auxiliary transformer. It was determined the fault developed when electrical tracking established a conduction path across the 13.8 kV bus bar support/insulator to ground, apparently as a result of an accumulation of moisture and dust which entered the termination compartment housing at the location where a piece of gasket material was missing from the compartment housing sealing surface. Safety-related electrical loads were being supplied by the inservice start-up transformer. The nonsafety electrical loads automatically transferred to the start-up transformer, 200-PY-B, with the exception that the nonsafety bus that was locked out. This event had minimal safety significance since the safety-related loads were not affected, and the plant was stabilized within the bounds of plant operating procedures. The corrective actions for this event include: rework the 13.8 kV terminations and auxiliary transformer testing; periodic inspections of transformer termination compartments; additional training of transformer maintenance personnel; and, inspection/testing of protective relays for Unit 1 and Unit 2 startup transformers. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an automatic actuation of the Reactor Protection System.
4401997006 | Perry | 06/10/1997 | 07/09/1997 | 9707160011 | <strong>Technician Error Results in High Pressure Core Spray System Actuation Without Injection Into The Reactor Pressure Vessel</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1997, at 1831 hours, with the plant in Mode 4, a technician error occurred during the return of a reactor pressure vessel (RPV) water level instrument reference leg purge panel to service which resulted in an inadvertent High Pressure Core Spray (HPCS) system actuation. The error caused a pressure spike in the reference leg which resulted in an invalid Reactor Water Low Level signal being sensed by the level transmitters associated with the reference leg. The HPCS pump and Division 3 Diesel Generator started; however, because reactor water level was being maintained above the HPCS injection valve closure setpoint, the HPCS injection valve did not open and the HPCS system did not inject into the RPV. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in an automatic actuation of an Engineered Safety Feature. The cause of the event is personnel error, failure to follow procedure. The Instrumentation and Controls (I&C) technicians received unexpected flow indications while performing steps of the purge panel restoration procedure. Instead of stopping activities, the technicians reperformed steps which induced a pressure spike into the associated reference leg and transmitters. The technicians involved with the event received disciplinary action in accordance with company policy. The event is being reviewed by I&C supervisors and technicians with emphasis placed on procedural compliance.
4401997007 | Perry | 07/13/1997 | 08/12/1997 | 9708190316 | <strong>Loss of Electrical Power to Reactor Protection System Bus Due to Electrical Protective Assembly Trip Results in Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1997, at approximately 1158 hours, the Perry Nuclear Power Plant, Unit No. 1, was operating at 100 percent of rated thermal power when electrical power from the Reactor Protection system (RPS) "B" motor generator (MG) set to RPS bus "B" was lost. As a result, the RPS "B" electrical power was removed from Division 2 and 4 RPS logic as well as Division 2 Nuclear Steam Supply Shutoff system (NSSSS) isolation logic. Subsequent to the loss of RPS "B" electrical power, an RPS B and D channel half scram and the expected annunciations were received. The loss of RPS "B" electrical power to the NSSSS isolation logic resulted in the initiation of Balance of Plant isolation, Reactor Water Cleanup isolation, Residual Heat Removal isolation, Main Steam Line Drain isolation, and Reactor Sampling isolation actuation signals. After equipment checks, RPS bus "B" was re-energized by the RPS "B" MG set, the half scram and Division 2 NSSSS isolation signals were reset, and plant operators restored from the event in accordance with plant procedures. The event resulted from the trip of an Electrical Protective Assembly (EPA) due to spurious actuation of the associated logic control board. The EPA logic control board was replaced with a board of updated design and the associated molded case circuit breaker was replaced. The equipment was calibrated and is being tested in accordance with plant procedures prior to return to service. Additionally, the remaining EPA logic control boards currently installed in the plant are scheduled for replacement with boards of the updated design.
4401997008 | Perry | 08/07/1997 | 04/02/1998 | 9804100312 | <strong>Technical Specification Limit for Reactor Coolant System Heatup/Cooldown was not Exceeded due to Conservative use of Reactor Pressure Vessel Bottom Head Drain Temperature as an Indicator of Heatup/Cooldown Rate</strong><br /><i>Abstract:&nbsp;</i>On August 7, 1997, at approximately 1926 hours, PNPP conservatively made a non-emergency notification (Event No. 32737) to the Nuclear Regulatory Commission (NRC), as required by PNPP, Unit No. 1, Facility Operating License, Section 21, that during plant transients on September 10, 1992, and March 26, 1993, the Reactor Coolant system (RCS) Technical Specification (TS) heatup/cooldown limit of 100 degrees Fahrenheit (F) per hour was exceeded without performing an evaluation to determine the effects of the out-of-limit condition on the structural integrity of the RCS and that the RCS remained acceptable for continued operations. This was reported in Licensee Event Report (LER) 97-008 on September 5, 1997, in accordance with 10 CFR 50.73(a)(2)(i)(B). When LER 97-008-00 was submitted, this condition had been determined to be reportable based on PNPP's conservative use of the Reactor Pressure Vessel (RPV) bottom head drain temperature as a measure of RPV bulk coolant temperature and indication of RCS heatup/cooldown rate. This was based on information obtained from the investigation of a reactor scram transient that occurred on January 7, 1997 (LER 97-001). Preliminary results indicated that natural circulation caused flow through the bottom head drain and therefore drain line temperature was a valid indicator of bulk coolant temperature. Based on the results of a December 1997 evaluation, PNPP has determined that the use of the bottom head drain temperature was not appropriate because it is not a valid indicator of RPV bulk coolant temperature. Therefore, the TS heatup/cooldown limit of 100 degrees F per hour was not exceeded during the September 10, 1992, and March 26, 1993 transient events. A retraction of Event Notification No. 32737 was made to the NRC on April 1, 1998. This Voluntary Report is being submitted to provide useful information to other utilities and the NRC. This report supersedes and replaces the preliminary information in LER 97-008.
4401997009 | Perry | 08/19/1997 | 09/18/1997 | 9709240143 | <strong>Operator Error Causes Invalid Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1997, with the plant in Mode 1 at 100 percent of rated thermal power, the shift operating crew was performing a tag-out instruction in preparation for scheduled Division 1 Emergency Diesel Generator (EDG) system quarterly maintenance activities. After placing the EDG in a secured status, at approximately 0357 hours, a non-licensed operator inadvertently removed a fuse that was not listed on the tag-out instruction causing a loss of power to safety bus EH11. The loss of power to safety bus EH11, resulted in an Engineered Safety Feature (ESF) actuation when the Division 1 Plant Radiation Monitoring (D17) system's drywell outboard isolation valves, F071A and F079A, automatically closed. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in an automatic actuation of an ESF. The cause of the event is personnel error, failure to maintain an appropriate level of attention to detail and failure to utilize self-checking practices. The tag-out was immediately removed and the plant was restored to a normal configuration. The individual involved has been counseled to address the deficient work practices. Additionally, the event was reviewed by other Operations Section personnel with emphasis on maintaining an appropriate level of attention to detail and ensuring self-checking practices are utilized at all times.
4401997010 | Perry | 09/11/1997 | 10/23/1997 | 9710280293 | <strong>Loss of Electrical Power to Reactor Protection System Bus Due to Electrical Protective Assembly Trip Results in Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1997, at approximately 2307 hours, the Perry Nuclear Power Plant, Unit No. 1, was operating at 21 percent of rated thermal power when electrical power from the Reactor Protection System (RPS) "A" alternate electrical feed to RPS bus "A" was lost. As a result, the RPS "A" electrical power was removed from Division 1 and 3 RPS logic as well as Division 1 Nuclear Steam Supply Shutoff System (NSSSS) isolation logic. Subsequent to the loss of RPS "A" electrical power, an RPS "A" and "C" channel half scram and the expected annunciations were received. The loss of RPS bus "A" electrical power to the NSSSS isolation logic resulted in the initiation of Balance of Plant isolation, Reactor Water Cleanup isolation, Residual Heat Removal isolation, Main Steam Line Drain isolation, and Reactor Sampling isolation actuation signals. After equipment checks, RPS bus "A" was reenergized by the RPS "A" MG set (normal power supply), the half scram and Division 1 NSSSS isolation signals were reset, and plant operators restored from the event in accordance with plant procedures. The event resulted from the trip of an Electrical Protective Assembly (EPA) due to spurious actuation of the associated logic control board. The EPA logic control board was replaced with a board of updated design and the associated molded case circuit breaker was replaced. The equipment was calibrated and tested in accordance with plant procedures prior to return to service. Additionally, the remaining EPA logic control boards currently installed in the plant will be replaced with boards of the updated design prior to the end of Refueling Outage 6.
4401997011 | Perry | 09/21/1997 | 10/21/1997 | 9710280165 | <strong>Technical Specification Surveillance Test Performance Results in Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1997, at approximately 0453 hours, with the plant shutdown in Mode 5, surveillance activities associated with Reactor Pressure Vessel (RPV) level instrument check valve operability and seat leakage testing resulted in a pressure transient being induced in an instrument sensing line which caused the generation of an invalid Division 2 RPV water level low (Level 1) signal and the associated engineered safety feature Containment/Drywell Group 2B and Stub Bus XH12 isolation actuations, as well as the automatic start of the Division 2 Emergency Service Water and Emergency Closed Cooling Water subsystems. The cause of the event is procedure weakness. The associated surveillance instructions did not contain provisions to address the potential of a pressure transient being induced while valves connecting the Reference Leg Purge Panel to the Reactor Reference leg are being manipulated. The associated surveillance instructions will be revised to reduce the likelihood that a testing induced pressure transient in any of the four reference legs will result in an ESF actuation. The revisions are scheduled to be completed by January 30, 1998. These instructions are being administratively controlled to preclude use prior to their revision.
4401997012 | Perry | 09/23/1997 | 10/23/1997 | 9710290068 | <strong>Insufficient Procedural Guidance Results in Reactor Protection System Actuation.</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1997, at 0016 hours, the Perry Nuclear Power Plant, Unit 1, received a Reactor Protection system (RPS) actuation due to the Reactor Mode Switch being repositioned from the "REFUEL" to the "STARTUP/HOT STANDBY" position while the Scram Discharge Volume was full of water. At the time of the event the plant was in Mode 5 with the reactor shut down. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in an RPS actuation. The cause of the event is insufficient procedural guidance. The full impact of repositioning the Reactor Mode Switch could not be determined with readily available documentation. The RPS system operating instruction will be revised to include a table/checklist of Reactor Mode Switch positions and their effects on RPS signals. Licensed operators will be trained on the lessons learned from this event.
4401997013 | Perry | 10/09/1997 | 11/10/1997 | 9711170041 | <strong>Control Rod Drive Hydraulic System Maintenance Activities Result in Reactor Protection System Actuations</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1997, at 0440 hours, with the plant shut down in Mode 5 (Refueling), Control Rod Drive Hydraulic (CRDH) system tagout restoration activities resulted in a Reactor Protection system (RPS) actuation due to a high Scram Discharge Volume (SDV) water level trip. Additionally, on October 11, 1997, at 1520 hours, with the plant in Mode 4 (Cold Shutdown), CRDH system tagout implementation activities resulted in an equipment alignment which allowed water to drain from the reactor pressure vessel (RPV) through control rod drive seals, through the SDV to the suppression pool. Control room personnel observed a decrease in RPV water level and determined that the decrease was caused by the tagout activities. The Reactor Operator initiated an RPS actuation to terminate the RPV level decrease. For both events, all control rods were already inserted and the CRDH system had been removed from service; therefore, no control rod movement occurred. The events are the results of work activity review and preparation errors. Weaknesses were identified in the processes in place for refuel outage tagout preparation. The Senior Reactor Operator responsible for the clearance of the tagout for the October 9, 1997, event was counseled regarding authorization responsibilities. Information concerning the importance of sequencing of tags for the CRDH system was added to the tagout database. Process enhancements will be developed to ensure that refueling outage work orders will receive a detailed operational review, which includes an enhanced review for equipment removal adequacy, similar to that presently performed for "on-line" work orders.
4401997014 | Perry | 10/14/1997 | 11/13/1997 | 9711180020 | <strong>Withdrawal of Inoperable Control Rod Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1997, at approximately 1930 hours, with the reactor shut down in Mode 4, an inoperable control rod was partially withdrawn from the reactor core and reinserted during control rod testing. The control rod inoperability was identified at approximately 2203 hours, when the associated scram accumulator leak detection instrumentation was found to be removed from service and the scram accumulator pressure below the required value. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) and the requirements of the PNPP, Unit No. 1, Facility Operating License, Section 2.F., as operation prohibited by the plant's Technical Specifications (TS), specifically TS Limiting Condition for Operation 3.10.4. The primary cause of the event is that the Senior Reactor Operator (SRO) directly supervising control rod movement activities did not ensure that the Reactor Operator (RO) performing rod movements was made aware of the status of the inoperable accumulator/control rod and did not provide appropriate controls to ensure that the control rod was not moved. A contributing cause was due to the RO not appropriately questioning the control rod accumulator fault indication and control rod operability. The SRO in charge of control rod stroking activities and the RO were coached and counseled with focus on the importance of ensuring adequate controls and questioning equipment conditions are utilized to prevent the use of inoperable equipment. Additionally, involved control room personnel were coached and counseled with focus on factors contributing to the event.
4401997015 | Perry | 10/19/1997 | 11/18/1997 | 9711240284 | <strong>Containment Penetration Leak Rate Test Failure</strong><br /><i>Abstract:&nbsp;</i>During the sixth refueling outage, a containment penetration "as found" leakage exceeded LLRT failure criteria for non-Main Steam Isolation Valve leakage. A Nuclear Closed Cooling (NCC) system containment penetration could not be pressurized; therefore, the penetration leakage was unquantifiable. Consequently, the "as found" minimum pathway leakage exceeded the allowable leak rate limits for Types B and C valves (0.6 L sub a) and secondary containment bypass (0.0504 L sub a). The penetration failure was identified during routine surveillance testing and during a MODE (i.e., Refueling) for which the TS Surveillance Requirements on leakage rates did not apply. On October 19, 1997, because it was not positively concluded that this condition did not exist during MODES 1, 2, or 3, the event was conservatively reported to the NRC under 10 CFR 50.72(b)(2)(i) and 10 CFR 50.72(b)(2)(iii). At the time the event was determined to be reportable, the plant was in MODE 4 (Cold Shutdown). The reactor pressure vessel was at approximately atmospheric pressure with reactor coolant temperature being maintained between 100 and 140 degrees F. The inboard isolation check valve failed due to corrosion and pitting on the valve body seat which occurred due to elevated oxygen levels in the NCC water. The outboard isolation valve failed due to an inadequate seal between the valve disc and valve body seat which was attributed to seal wear. Following repairs, the post maintenance test verified penetration operability.
4401997016 | Perry | 12/19/1997 | 01/20/1998 | 9801230398 | <strong>Vibration-Induced Turbine Electro-Hydraulic Control System Fluid Leak Results in Reactor Protection System and Engineered Safety Features Actuations.</strong><br /><i>Abstract:&nbsp;</i>On December 19, 1997, at 0939 hours, the Perry Nuclear Power Plant, Unit 1, automatically scrammed from 100 percent of rated thermal power, due to a Turbine Electro-Hydraulic Control (EHC) system tubing fluid leak which resulted in a turbine trip, Reactor Protection system (RPS) actuation, and subsequent Residual Heat Removal isolation logic actuation. Operators responded to the event in accordance with the appropriate procedures and the plant was safely shut down. The cause of this event is a vibration-induced fatigue failure of a section of turbine control valve (TCV) EHC system tubing. The vibration is the normal result of the pressure transients within the system during operation. Contributing causes to the tubing failure were the design application of the tubing fitting used to connect the EHC tubing to the TCV, and the support scheme of the tubing. The EHC tubing compression fittings for the applicable hydraulic lines at the four TCVs were replaced with welded flare fittings. Additional EHC tubing hangers were added to two of the four TCVs to provide additional tubing support closer to the fittings. A design modification to install an accumulator in the applicable TCV ,hydraulic lines to dampen the vibration is being evaluated. The applicable tubing and fittings at the TCVs are being monitored, as plant conditions permit, until an appropriate design modification is implemented.
4401997017 | Perry | 07/15/1997 | 01/22/1998 | 9801280093 | <strong>High Suppression Pool Level Signal Results in Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1997, at approximately 2300 hours, operation of the Containment Vessel and Drywell Purge (CVDWP) system caused an increase in suppression pool water level and resulted in a High Pressure Core Spray (HPCS) Suppression Pool Water Level-High logic actuation. No actual valve movement associated with the logic actuation occurred because the HPCS pump suction had been previously aligned to the suppression pool. The cause of the event is incomplete assessment of suppression pool level instrumentation channels prior to the CVDWP system startup. The senior reactor operators (SROs) utilized the Emergency Response Information System (ERIS) indication, which averages multiple instrument inputs, when assessing the potential for the evolution to cause a suppression pool level increase of sufficient magnitude to result in the HPCS Suppression Pool Water Level-High logic actuation. One channel of the HPCS Suppression Pool Water Level-High instrumentation was reading higher (but still within specifications) than the ERIS indication evaluated by the SROs. Due to the margin that appeared to exist with the ERIS indication, the SROs did not anticipate the actuation of the logic and so did not document the evolution as pre-planned. The event and its cause, as well as management expectations concerning the documentation of expected actuations, were discussed with the SROs involved in the event and with other on-shift SROs.
4431997001 | Seabrook | 01/09/1997 | 02/10/1997 | 9702200170 | <strong>Seabrook Station Design Basis Flooding Analysis</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. The Seabrook Station design basis flood analysis is documented in Section 2.4 of the Updated Safety Analysis Report (UFSAR). The UFSAR addresses two flooding scenarios: a probable maximum hurricane (PMH)/Probable Maximum Flood (PMF) event and local intense probable maximum precipitation(PMP). The limiting event identified in the UFSAR is the PMH/PMF event which was analyzed to produce flood levels on the Seabrook Station site to an elevation of 21' mean sea level (msl) or less. Flooding associated with the PMH/PMF occurs primarily as a result of waves overtopping the vertical seawall. A critical assumption in the analysis is that the flood water will flow off the site via several flow paths that are specified in the UFSAR. North Atlantic has identified that certain obstructions to the flow of flood water off the site may produce site flood levels exceeding the elevations specified in the UFSAR. This condition was reported to the NRC on January 9, 1997, pursuant to 10CFR50.72(b)(1)(ii)(B), as a condition that is outside the design basis of the plant. An operability determination was performed to provide the basis for continued operation. Modifications to the flow obstructions will be implemented and the flooding analyses will be updated. The cause of this event has been determined to be a misapplication of design inputs and inadequate independent review.
4431997002 | Seabrook | 01/28/1997 | 02/12/1997 | 9702190316 | <strong>CONTAINMENT PENETRATION PIPING OVERPRESSURE POTENTIAL (GL 96-06)</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. In response to NRC Generic Letter 96-06 North Atlantic Energy Service Corporation (North Atlantic) completed an evaluation of the three issues outlined in GL 96-06. North Atlantic reported to the NRC in its response to GL 96-06 that Seabrook Station's containment air cooler cooling water system was not susceptible to either waterhammer or two phase flow. North Atlantic also reported that the containment penetrations themselves were not susceptible to thermally induced overpressurization. However, several containment isolation valves were found to have the potential for overpressurization due to the heatup of trapped fluid in the piping inboard of the inner containment isolation valve. Corrective actions were initiated to ensure that the affected containment isolation valves are not challenged by overpressure conditions and would remain capable of performing their intended safety function. North Atlantic initiated non-emergency one hour reports on January 13 and 24, 1997, due to the potential for containment bypass. The postulated bypass scenario is one in which the inner containment isolation valve fails as a result of the overpressure condition and the outer containment isolation valve does not close upon receipt of an automatic closure signal (single failure condition). There are two systems that have inside containment isolation valves that are susceptible to the thermally induced overpressure and bypass condition. The two systems are the Safety Injection System [BQ] test line and accumulator fill line, and the Waste Liquid System [WK]. A vent valve in each system was opened to provide a controlled relief path should the postulated condition develop.
4431997003 | Seabrook | 01/13/1997 | 02/12/1997 | 9702190321 | <strong>MISSED SURVEILLANCE TURBINE TRIP ON REACTOR TRIP</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. Technical Specification 4.3.2.1, Table 4.3-2. Functional Unit 10.b, 'Reactor Trip, P-4' Engineered Safety Features Actuation System (ESFAS) [JE] Interlock states that an Actuation Logic Test be performed on a Refueling Interval. The functions associated with the P-4 interlock are: actuation of turbine trip, feedwater isolation on low Tavg, seal-in of feedwater isolation on SI or Hi-Hi S/G level, SI manu reset and block, and steam dump control logic. The actuation of a turbine trip on P-4 interlock is not identified as a Seabrook Statio ESFAS system, however it was identified in the NRC Safety Evaluation Report (SER) as a function that should meet the criteria applicable to a safety function. It is apparent from review of original licensing documentation that it was intended that the turbine trip on P-4 circuitry would be tested. requirement, turbine trip on P-4 testing has not been performed on the required Refueling Interval due to lack of specific testing requirements in licensing documentation. A licensee-initiated Design Bases Review discovers this condition. Operability of the turbine trip on P-4 Interlock circuits were verified by confirming indication of actuation of the primary an backup turbine trip circuits during the plant trip on 1/27/96. This plant trip was within the required surveillance interval. There were no adverse safety consequences as a result of this event. An additional reportable event was identified during the evaluation of the event and is described in the Similar Events section.
4431997004 | Seabrook | 02/06/1997 | 03/07/1997 | 9703170073 | <strong>REMOTE SHUTDOWN SYSTEM CIRCUITS NOT TESTED COMPLETELY</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 6, 1997, North Atlantic Energy Service Corporation (North Atlantic) identified four Remote Shutdown System [JL] (RSS) circuits that were not being completely tested as required per Technical Specification (T.S.) 4.3.3.5.2. North Atlantic identified the condition during a review of Technical Specifications in support of a License Amendment Request to extend the cycle duration to twenty-four months. The circuits were declared inoperable and subsequently tested satisfactorily within the Allowed Outage Time. The intent of T.S. 4.3.3.5.2 is to verify that individual circuits of systems required to remotely shut down the plant from outside the control room are operable. This testing includes verifying that the RSS control circuits can be electrically isolated from the control circuits on the Main Control Board (MCB) and that their remote shutdown function is operable. These features are required per 10 CFR Part 50 Appendix R. The RSS transfer switches that are operated to select local or remote control are all GE Type SB1 switches. The design of the switch is such that the multiple contacts in the switch are individually operated by separate cams. Four of the RSS circuits have auxiliary relays which are operated by the SB1 switch contacts. The relays are relied upon to perform an electrical isolation or a remote shut down function, which is back-up fuse insertion into the local control circuit. The primary fuses are assumed to be damaged during the postulated fire and the back-up fuses ensure local operation is available. It is these relays that were not verified to have properly functioned. Since neither of the two functions of the relays had ever been verified, reasonable assurance of their operability did not exist. The subsequent testing provided assurance that all the RSS circuits are operable and capable of performing their intended safety function. Long term corrective actions are to enhance the surveillance test procedure to require relay testing and MCB indicating light verification to ensure the RSS circuit is operable.
4431997005 | Seabrook | 03/14/1997 | 05/27/1997 | 9706050024 | <strong>MISPOSITION OF MAIN STEAM LINE RADIATION MONITORS</strong><br /><i>Abstract:&nbsp;</i>On March 14, 1997 North Atlantic Energy Service Corporation (North Atlantic) discovered that the four Main Steam Line Radiation Monitors [IL] (MSLRM) were positioned downstream of the pipe branches to the atmospheric steam dump valves (ASDV) contrary to the UFSAR piping and instrumentation diagrams for the Main Steam System. With the MSLRMs located downstream of the ASDV pipe branches, radioactive steam releases through these valves under steam generator tube rupture accident conditions would not have been correctly quantified and non-conservative input data could have been used by the emergency plan dose projection models. For the period from full power license issuance in March 1990 to March 20, 1997, as a result of the mispositioning of the MSLRMs, non-conservative input data could have been used by the dose projection models which could have resulted in an underestimation of offsite radiation doses, and inappropriate protective action recommendations. The condition described in this LER is limited to a steam generator tube rupture accident. It would not have affected emergency classifications or protective action recommendations initiated based on plant Critical Safety Function conditions, field monitoring results, or radioactive releases from the plant vent. During normal operation, steam releases from the ASDVs are quantified as to radiological content by sampling and analysis of the Main Steam System. This condition was discovered during a system walkdown performed as part of operator training. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i). The causes of this event are attributed to (1) human errors involving inadequate instrument plan drawings, installation details and P&ID walkdowns and (2) misjudgment errors during the preparation of a minor modification. The MSLRMs were declared inoperable on March 14, 1997. The MSLRMs were repositioned upstream of the pipe branches to the ASDVs and the dose projection models revised to reflect the new location. The MSLRMs were declared operable at 1750 on March 20, 1997.
4431997006 | Seabrook | 04/07/1997 | 05/07/1997 | 9705150025 | <strong>NON-CONSERVATIVE FUEL HANDLING ACCIDENT ANALYSIS ASSUMPTIONS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 7, 1997, North Atlantic Energy Service Corporation (North Atlantic) initially determined that a potential fuel handling accident in Containment could result in radiological consequences to Control Room personnel being more severe than currently described in the Seabrook Station Updated Final Safety Analysis Report (UFSAR). The current UFSAR assumption for a fuel handling accident inside containment assumes that the accident takes place near the center of the refueling cavity or approximately 10 feet from the Containment Air Purge (CAP) exhaust duct. However, irradiated fuel assemblies are routinely moved in close proximity to the CAP exhaust ducts. Under these circumstances the CAP containment isolation valves may not have sufficient time to close before contaminated gas was released from Containment. A dropped fuel assembly adjacent to the CAP exhaust duct and operating exhaust fan would essentially result in the activity being released prior to the automatic isolation of the 36 inch butterfly valves. North Atlantic reported this condition to the NRC on April 7, 1997, pursuant 10CFR50.72(b)(1)(ii)(B) as .a condition that is outside the design basis of the plant.' Subsequent evaluations concluded that doses to control room personnel remained within UFSAR and General Design Criteria 19 limits. However, this more limiting fuel assembly drop location could represent 'a condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactivity. This condition is reportable pursuant 10 CFR 50.73 (a)(2)(v)(C). The apparent cause of this event was determined to be due a non-conservative assumption in the Fuel Handling Accident analysis. This is a knowledge-based error that is due to insufficient site-specific knowledge of fuel handling operations. North Atlantic has reevaluated the Control Room Makeup Air and Filtration System (CBA) Chapter 15 accident analysis and concluded the projected dose rates to control room personnel will remain less than GDC 19 and UFS AR limits. North Atlantic reviewed the Fuel Handling Accident Analysis for the Fuel Storage Building for potential similar non-conservative assumptions. Additionally, North Atlantic is evaluating corrective action options to be implemented prior to refueling operations during Seabrook Station's upcoming refueling outage.
4431997007 | Seabrook | 04/25/1997 | 05/27/1997 | 9706020302 | <strong>Environmental Protection Program Non-Compliance</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1997, during the preparation of the 1996 Annual Environmental Operating Report, it was discovered that North Atlantic was not in compliance with the requirements of Appendix B to the Facility Operating License (FOL) for Seabrook Station, Environmental Protection Plan (EPP). In accordance with the requirements of Section 2.G of the FOL, an initial notification was made to the NRC Operations Center via the Emergency Notification System on April 25, 1997. Three deficiencies of the EPP were identified in that notification. The causes of this event are attributed to: 1) Lack of commitment to program implementation, 2) Insufficient programmatic detail, and 3) Inadequate program monitoring or management. Corrective actions include: 1) Establish an Environmental Protection Program that coordinates and controls the various environmental subprograms, 2) Designate responsibility for the implementation of the Environmental Protection Program, 3) Reexamine and improve the Environmental Protection Plan subprogram implementation details and management expectations, and 4) Increase the frequency and rigor of self-assessment and independent oversight of the EPP. There were no adverse safety consequences nor were there adverse non-radiological environmental impacts as a result of this event. This is the first event of this type at Seabrook Station.
4431997008 | Seabrook | 05/10/1997 | 06/09/1997 | 9706170060 | <strong>AUTOMATIC REACTOR TRIP AND FEEDWATER ISOLATION</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1997, at 0211 EDT during a routine shutdown to begin the fifth refueling outage, an automatic reactor trip and subsequent feedwater isolation occurred at approximately 8% Rated Thermal Power (RTP). The reactor trip was initiated by one of two Intermediate Range Neutron Flux Instrumentation (IR NI)[IG] channels. The high flux trip signal (set for 25% RTP) occurred when the IR NI high flux trips were automatically unblocked at 8% reactor power. The IR NI trip bistable for Channel N35 had not reset prior to unblocking the IR NI trips below the P-10 reset setpoint of 8% reactor power and thus initiated a trip signal when unblocked. Both IR NI channels, N35 and N36, had been affected by a significant shift in radial power distribution and channel N35 had experienced power supply degradation problems during the operating cycle. The cumulative effect of these two factors on the IR NI channels caused the trip signals to stay actuated below the power levels at which they should have normally reset. The four power range nuclear instruments indicated approximately 8% reactor power just prior to the trip. The IR NI reactor trip bistables should have reset at 12.5% RTP. This event was reported to the NRC at 0321 May 10, 1997, as a non-emergency event pursuant to 10CFR50.72(b)(2)(ii), automatic actuation of the Reactor Protection System [JC] and Engineered Safety Feature System [JE]. The causes of this event are: 1) the inadequate monitoring and trending of the intermediate range channels power supplies, 2) a collective lack of knowledge about the effects that changing IR NI detector currents have on IR NI reactor trip and reset setpoints, and 3) inadequate procedural guidance in the plant shutdown procedure regarding verification that the intermediate range neutron flux trips were reset prior to decreasing power below the P-10 setpoint. Corrective actions include improved monitoring of IR NI channels, enhanced plant shutdown procedures and operator and technical training on this event.
4431997009 | Seabrook | 05/31/1997 | 07/30/1999 | 9908090073 | <strong>Degraded Fuel Rods Identified in Westinghouse Fuel Assemblies</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1996, during Cycle 5, Seabrook Station experienced a step increase in Reactor Coolant System (RCS)[AB] activity that was subsequently attributed to fuel cladding degradation. The increased activity levels were within Technical Specification allowable limits. Fuel sipping and ultrasonic testing during the refueling outage in May of 1997 identified five degraded fuel rods in four different fuel assemblies. The degraded fuel assemblies were Westinghouse Vantage 5H, with 1 28 Integral Fuel Burnable Absorber (IFBA) rods per assembly. The four degraded fuel assemblies had been in the core for one operating cycle. This condition was reported pursuant to 10 CFR 50.72(b)(2)(i) on May 31, 1997. The root cause of this condition is localized corrosion of the fuel cladding. Factors contributing to the localized cladding corrosion included crud deposition, high cycle average rod powers, and local flow effects. The four degraded fuel assemblies were replaced with new assemblies. The new assemblies and similar intact Vantage 5H, 128 IFBA assemblies were relocated to low power regions of the core for Cycle 6. An extended Mode 4 RCS clean-up prior to start-up following the fifth refueling outage was completed, and the RCS chemistry was modified during Cycle 6. Both the extended cleanup and the RCS chemistry changes were to reduce crud deposition on fuel rod cladding surfaces early in core life. The Cycle 6 core loading pattern prevented long term power peaking in any one set of fuel assemblies.
4431997010 | Seabrook | 06/05/1997 | 07/03/1997 | 9707110360 | <strong>Containment Building Spray Penetration Check Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1997 an inspection of the Train B Containment Building Spray (CBS) System containment isolation penetration (X-15) was performed to determine the cause of a local leak rate test failure that occurred on May 17, 1997. The inspection revealed that the check valve disc was stuck in the open position. Penetration X-15 consists of a motor operated valve (CBS-V17) outside reactor containment and a swing check valve (CBS-V18) inside reactor containment and is normally isolated by CBS-V17 during plant operation. The check valve (CBS-V12) associated with Train A penetration X-14 was found in the closed position but is also susceptible to similar sticking. This condition was reported to the NRC on June 10, 1997, pursuant to 10 CFR 50.72(b)(2)(i) as an event, found while shut down, that had it been found while the reactor was in operation, would have resulted in the nuclear power plant, including its principal safety barriers, being seriously degraded or being in an unanalyzed condition that significantly compromises plant safety. A root cause evaluation determined that this condition was caused in 1986 by the installation of an incorrect disc hanger in valves CBS-V18 and CBS-V12. As a result of the mechanical binding associated with CBS-V18, the valve discs on CBS-V18 and CBS-V12 have been machined/modified. The maintenance procedure associated with this type of check valve will be revised to provide guidance regarding abnormal indications found on the valve discs during future inspections.
4431997011 | Seabrook | 06/11/1997 | 07/11/1997 | 9707220136 | <strong>Containment Building Spray Sump Suction Valve Encapsulations</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1997 a local leak rate test of the "A" train containment recirculation sump isolation valve encapsulation tank indicated that the encapsulation tank was unable to maintain the required test pressure of 52 psig and thereby exceeded the established local leak rate acceptance criteria. Testing was subsequently performed on the "B" train encapsulation tank with similar results. The encapsulations are not required to be in place to ensure containment integrity, but rather to ensure that leakage from the ECCS recirculation sump isolation valves or piping is not released to the environment during design basis accident conditions. The unacceptable as-found local leakage rates of the encapsulation tanks was reported on June 11, 1997, pursuant to 10 CFR 50.72 (b)(2)(i). The cause of this condition was determined to be inadequate corrective actions taken to address design/manufacturing problems with the encapsulation tank seals. A design change has been implemented which enhances the sealing capability of the encapsulation tanks.
4431997012 | Seabrook | 06/13/1997 | 07/12/1997 | 9707220120 | <strong>REACTOR TRIP AND ESF ACTUATION ON LO-LO STEAM GENERATOR LEVEL</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1997 the "C" Steam Generator was inadvertently drained from 38% Narrow Range (NR) level to 13% NR level causing SG Lo-Lo Reactor Protection System [JC] and ESF [JE] Actuation signals to be generated (Reactor Trip and EFW actuation). This event was reported pursuant to 10 CFR 50.72(b)(2)(ii). 14% NR level is the Reactor Trip and Emergency Feed Water actuation setpoint. The Reactor Trip breakers were racked out and the EFW pumps were removed from service for maintenance so these components did not change state as a result of the actuations. The draining occurred when the "C" SG Feedwater Isolation Valve, FW-V48, was stroked open for testing and the SG water drained to a sump through a normally closed drain valve. The drain valve was open to assist workers re-packing a separate feedwater system valve. After stroking open FW-V-48, control room operators noticed the decreasing "C" SG level and re-closed FW-V-48. The "C" SG reached 13% NR level and stopped decreasing when FW-V-48 reached its full closed position. Corrective actions include presentations of this event, as well as reinforcement of error reduction techniques, by Operations management to the operators during future training sessions and incorporating the lessons learned into future outage planning.
4431997013 | Seabrook | 07/28/1997 | 08/26/1997 | 9709030257 | <strong>INOPERABLE TURBINE GLAND SEAL CONDENSER EXHAUST RADIOACTIVE GASEOUS EFFLUENT MONITOR</strong><br /><i>Abstract:&nbsp;</i>The Turbine Gland Seal Condenser Exhaust [TC] radioactive gaseous effluent monitor [IL] particulate sampler filter paper was torn during sampler installation. As a result, two representative particulate weekly samples were not collected and analyzed as required by Technical Specification 3.3.3.10, Table 3.3-13. The technicians who installed the sampler did not know that the recently replaced sampler sealing O-rings created tighter fit-up tolerances that necessitated sampler installation using a different technique to preclude tearing the filter paper. A limited particulate sample was collected from the torn filter paper and no detectable particulate activity was identified. A separate limited particulate analysis was performed using the in-line Iodine charcoal filter cartridge since this cartridge is also capable of capturing some particulate. No radioactive particulate was detected in the cartridge for either of the weekly samples when the particulate filter paper was torn. Additionally, the Iodine and Noble Gas sample results for the two sampling periods were less than minimum detectable. It is believed that no radioactive particulate was discharged during the period when the filter paper was torn. Corrective actions include briefing Chemistry Department personnel on the proper method of aligning and installing the sampler to preclude tearing the filter paper, and replacing the sampler's outlet line with flexible tubing to facilitate sampler alignment and installation.
4431997014 | Seabrook | 09/23/1997 | 10/23/1997 | 9710290130 | <strong>NON-CONSERVATIVE RHR VALVE LOW PRESSURE OPEN PERMISSIVE BISTABLE SETTING</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1997, a review of the Reactor Coolant System (RCS) wide range pressure channel calibration procedures concluded that the Residual Heat Removal System (RHR) Low Pressure Interlocks (LPI) reset on increasing pressure such that the RHR isolation valves can be opened with an RCS pressure as high as 394 psig. This is above the 365 psig Technical Specification limit and is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B), as a condition prohibited by the plant's technical specifications. There were no adverse safety consequences as a result of this condition. Existing administrative controls ensured that the RHR suction isolation valves could not have been opened between 365 and 395 psig. This condition was caused by the acceptance of a Technical Specification surveillance requirement for the RHR LPI's that did not consider the dead-band between the vendor recommended bistable setpoint of 365 psig and the reset point of 395 psig. This condition occurred when the Technical Specifications were developed before plant startup. The Seabrook Station Technical Specifications will be revised to ensure that the RHR system LPI surveillance requirements consider the dead-band between the vendor recommended bistable setpoint of 365 psig and the reset point of 395 psig.
4431997015 | Seabrook | 10/28/1997 | 11/26/1997 | 9712020177 | <strong>POTENTIALLY NON-CONSERVATIVE WESTINGHOUSE FUEL ROD PERFORMANCE MODEL</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, Westinghouse informed North Atlantic Energy Service Corporation (North Atlantic) that a developmental fuel rod performance model could calculate reduced fuel rod internal pressure margins when compared to the previously licensed computer code. Westinghouse has determined that in very limiting cases for high power, high burnup Integral Fuel Burnable Absorber (IFBA) fuel rods, calculated pressures are in excess of the fuel rod design criterion that the fuel rod pellet to clad gap shall not reopen. Additionally, if the no gap re-opening criterion is exceeded, the 17% clad oxidation limit following a postulated LOCA event, as defined in 10 CFR 50.46, could potentially be exceeded. This condition is the result of a Westinghouse fuel rod performance computer code that is potentially non-conservative. North Atlantic reported this condition on October 28, 1997 pursuant to 10CFR50.72(b)(ii)(B) as a condition outside the design basis of the plant. There are no adverse safety consequences as a result of this condition. Westinghouse has analyzed a hypothetical limiting case scenario and North Atlantic has concluded that Seabrook Station's specific core region criteria are more conservative than those assumed in the limiting case scenario. Westinghouse has informed North Atlantic that it is currently planning to perform plant-specific analyses to determine the applicability of this condition to Seabrook Station.
4431997016 | Seabrook | 11/05/1997 | 02/09/1998 | 9802190108 | <strong>NON-CONSERVATIVE AMSAC ARMING SETPOINT</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1997, North Atlantic determined that the ATWS mitigating system actuation circuitry (AMSAC) C-20 interlock setpoint was non-conservative in that it enabled AMSAC at 40 percent turbine power rather than at 40 percent reactor power as assumed in the Westinghouse ATWS analysis. At that time, North Atlantic did not have an analysis that determined the effect of voiding in the reactor vessel at 44 percent reactor power, which is estimated to correspond to approximately 40 percent turbine power under steady state conditions. On November 5, 1997, North Atlantic reported this as a condition that is outside the design basis of the plant pursuant to 10 CFR 50.72(b)(1)(ii)(B). Subsequent Westinghouse analysis determined that arming AMSAC at the C-20 interlock based on 40 percent turbine power remains appropriately conservative. As a result, on February 5, 1998, North Atlantic retracted the November 5, 1997 report made pursuant to 10 CFR 50.72(b)(1)(ii)(B). This condition was caused by the lack of a precise definition of the required power level for the C-20 interlock in the applicable WCAPs. This condition did not create any significant adverse safety consequences. North Atlantic issued a Standing Operating Order to promptly reduce reactor power to less than 40 percent if the C-20 interlock status light deenergizes due to turbine power being less than 40 percent while reactor power is above 40 percent. Subsequently, a design change was implemented to revise the AMSAC C-20 interlock setpoint to reflect a turbine impulse pressure equivalent to 20 percent reactor power, thus ensuring that AMSAC is armed prior to reaching 40 percent reactor power.
4431997017 | Seabrook | 11/18/1997 | 12/18/1997 | 9801050334 | <strong>Inadequate SSPS Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1997 during a review of industry operating experience, North Atlantic Energy Service Corporation (North Atlantic) determined that the current Solid State Protection System (SSPS) [JG] surveillance testing did not adequately test certain logic circuits. The circuits involved use universal logic boards in a memory configuration. There are three functions which are inadequately tested: Source Range Automatic P-10 Block, Feedwater Isolation on P-14 Steam Generator Hi-Hi Level and Feedwater Isolation on a Safety Injection. The cause of this condition was determined to be an inadequacy of the internal logic test scheme of the SSPS as supplied by the vendor. North Atlantic utilized guidance provided by the vendor during the initial development of the logic circuit surveillance procedures. The testing inadequacy was not identified during the initial surveillance procedure development nor during subsequent procedure reviews. The inadequate surveillance was determined to be a missed surveillance. The plant entered Technical Specification 4.0.3, which provided 24 hours to complete the surveillance. The surveillance procedures were revised to incorporate the additional testing, and both trains of SSPS were tested satisfactorily.
4431997018 | Seabrook | 12/16/1997 | 01/15/1998 | 9801230325 | <strong>Control Room Air Conditioning Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1997, the plant entered Technical Specification 3.0.3 due to both trains of Control Room Emergency Makeup Air and Filtration Subsystems (CREMAFS)[VI] being inoperable per Technical Specification 3.7.6. On December 15, 1997 CBA-AC-5B was declared inoperable due to a compressor failure. On December 16, 1997 CBA-AC-5A was declared inoperable due to degrading system performance. At the time of the event the plant was in Mode 4 and commenced a plant shutdown to Mode 5, where Technical Specification 3.7.6 has an applicable ACTION for both trains of CREMAFS inoperable. The compressor failure mechanisms have been attributed to liquid refrigerant carryover to the suction of the compressors. In addition to the mechanical failure mechanisms the following causes degraded the system performance: inherent control room air conditioning (CRACS) design deficiencies, corrective actions for previous events being too narrowly focused, design modifications not implemented in a timely manner and the failure of the corrective action program to promptly correct deficiencies that were significant conditions adverse to quality. A root cause evaluation will be performed to investigate the corrective action aspects of this event. As a result of the CRACS compressor failures, a team was tasked with identifying historical problems associated with the CRACS and evaluating whether the planned actions to increase the reliability of the systems would be effective. Design changes have been implemented to address the inherent design deficiencies. Based on the teams recommendations the following actions will be taken: monitoring CRACS performance criteria at the "train" level and evaluation of further design changes to enhance the performance of the CRACS.
4451997001 | Comanche Peak 1, Comanche Peak 2 | 01/24/1997 | 03/05/1997 | 9703120055 | <strong>IDENTIFIED SINGLE FAILURE OUTSIDE OF THE DESIGN BASIS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 24, 1997, at approximately 6:00 p.m. CST, a condition was identified with the potential to be a more limiting single failure for the Main Steam Line Break (MSLB) and Feedwater Line Break (FLB) accidents at Comanche Peak Steam Electrical Station (CPSES) Units 1 and 2. On February 3, 1997, TU Electric Engineering concluded that the postulated scenario of a FLB occurring to an 'A' Train Steam Generator (SG) coincident with the single active failure of the 'B' Train Solid State Protection System (SSPS) was considered outside of the CPSES design basis. A similar evaluation concluded that the MSLB remained conservative. TU Electric believes that the cause of this condition was the failure to identify this event as a credible scenario during the design of the facility. Analysis of this condition has determined that the Auxiliary Feedwater system remains OPERABLE. However, corrective action will be implemented by completion of design modification to restore the original design basis of the plant by the end of the next refueling outage for each unit.
4451997002 | Comanche Peak 1, Comanche Peak 2 | 03/19/1997 | 08/15/1997 | 9708220183 | <strong>INVALID ASSUMPTION FOR CONTAINMENT SPRAY SWITCHOVER FROM THE REFUELING WATER STORAGE TANK</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1997, at approximately 10:40 a.m. CST, a condition was identified where the time for containment spray switchover from the Refueling Water Storage Tank (RWST) to the containment sump could take longer than the time assumed in the supporting calculation: thus resulting in insufficient water to supply containment spray. On March 19, 1997, a TU Electric engineer (utility, non-licensed), conservatively concluded that the postulated scenario for the analyzed time for containment spray switchover from the RWST to the sumps compared to the available volumes in the RWST was considered outside of the CPSES design basis. TU Electric believes that the cause of this condition was a failure of contract engineering to verify the assumption of valve stroke times assumed in the design of the facility. Analysis of this condition has determined that the containment spray system remained operable. TU Electric is revising calculations, including level setpoints as appropriate, and the FSAR to reflect the capability to complete containment spray switchover without interruption of flow. Although the current emergency operating procedures should result in switchover without interruption of flow under realistic scenarios, the procedures are being revised to assure the operator can complete the switchover without interruption of flow under design basis accident conditions including the worst single active failure.
4451997003 | Comanche Peak 1, Comanche Peak 2 | 05/14/1997 | 06/13/1997 | 9706190257 | <strong>THE SYSTEM INTERACTION PROGRAM DID NOT ADEQUATELY CONSIDER ALL ENVIRONMENTAL EFFECTS RESULTING FROM POSTULATED MAIN STEAM AND FEEDWATER LINE CRACK</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1997, TU Electric Engineering personnel (utility, non-licensed) were performing a 10CFR50.59 safety screen on a condition described in a Comanche Peak Steam Electric (CPSES) deficiency document. The condition being reviewed involved air flowing out of floor drains. During the safety screen Reactor Engineering noted a Unit1/Unit2 difference which could impact the environmental analysis on the Main Steam (MS) (EIIS:(SB)) and Feedwater (FW) (EIIS:(SJ)) outside containment penetration areas. TU Electric believes the cause of this condition was that implementation of the System Interaction Program (SIP) did not adequately consider the direct communication paths between multiple rooms in the Safeguard Building through interconnecting floor drains when evaluating the effects of a postulated one square foot pipe crack in the break exclusion zones of main feedwater and steam system piping. Compensatory action has been taken to plug the drains in the MS and FW outside containment penetration areas of both units to mitigate the consequences of the postulated line breaks. This condition is being further analyzed by Engineering. The identified condition does not impact OPERABILITY per the CPSES Technical Specifications (TS), since these breaks are not part of the bases for the TS. Additionally, the compensatory action eliminated postulated adverse effects which could have exceeded the CPSES design.
4451997004 | Comanche Peak 1, Comanche Peak 2 | 06/24/1997 | 05/08/1998 | 9805180015 | <strong>ISSUES DISCOVERED DURING THE REVIEW OF GENERIC LETTER 96- 01 ASSOCIATED WITH TECHNICAL SPECIFICATION SURVEILLANCES</strong><br /><i>Abstract:&nbsp;</i>EVENT 1 On June 24, 1997, at approximately 11:00 a.m., during a review of surveillance procedures involving testing of safety-related logic circuits, it was determined that plant surveillance procedures did not adequately test, on a quarterly basis, the Solid State Protection System (SSPS) P-11 input relays during Analog Channel Operational Tests (ACOTs). The cause of this condition is attributed to an incorrect previous interpretation of the Licensing Basis requirements related to testing for the SSPS P-11 input relays. Corrective actions taken include declaring the P-11 interlock inoperable, revising procedures to perform the quarterly surveillances, and performing all of the SSPS P-11 quarterly surveillances required by the Technical Specifications.
4451997005 | Comanche Peak 1, Comanche Peak 2 | 10/04/1996 | 09/15/1997 | 9709220209 | <strong>MAIN STEAM SAFETY VALVES WERE DECLARED INOPERABLE WHEN THEY FAILED THEIR TECHNICAL SPECIFICATION SURVEILLANCE TESTING (T/S 4.0.5)</strong><br /><i>Abstract:&nbsp;</i>On October 4 and 5, 1996, surveillance testing of Main Steam Line code safety valves, in accordance with Technical Specification 4.7.1.1, was conducted. During this testing one Main Steam Safety Valves (MSSV)(EIIS:(RV)(SB)) 1MS-0024 initial lift pressure was found to be outside the Technical Specification (TS) limits of plus/minus I percent. As a result of this test failure, several other valves were tested. Five valves were found to be outside the TS limits of plus/minus 1 percent, which led to retesting of all MSSVs in CPSES Unit I which were subsequently declared operable. The MSSVs failed their initial lift pressure test on October 4 and 5, 1996. The required Technical Specification actions, including testing of additional valves, were met. However, the need for a LER to the NRC pursuant to the requirements of 10CFR50.73(a)(2)(vii) was not recognized until August 15, 1997. Corrective actions were to initiate a plant incident report to capture this matter as a missed opportunity to report a condition pursuant to the requirements of 10CFR50.73. The corrective actions of this PIR will be lessons learned which will be promulgated to personnel involved with this issue.
4451997006 | Comanche Peak 1, Comanche Peak 2 | 08/28/1997 | 10/18/1997 | 9710210171 | <strong>CONTROL ROOM HVAC EMERGENCY PRESSURIZATION UNIT WAS FOUND TO BE OUTSIDE TECHNICAL SPECIFICATION LIMITS</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.7.7.1j, for the Control Room Filtration/Pressurization System Train requires the Train to maintain a positive pressure of equal or less than 0.125 inches of water gauge. On August 28, 1997, two occurrences were identified where the "as left" flows from the related pressurization unit surveillance tests required by Comanche Peak Technical Specifications 4.7.7.1d.(1), 4.7.7.1g and 4.7.7.1h were in excess of 800 cfm. These related surveillance test conditions require 800 cfm plus or minus 10 percent. Immediate corrective actions were taken to reduce the airflow below 800 cfm. Test procedures are being revised so that each surveillance measures the system flow rate and that the "as left" conditions for each test satisfy all the applicable surveillance requirements of the other related surveillances. During the time period that the plant was outside the Technical Specification value of 800 cfm on each occasion, the opposite Train was taken out of service for a total of 6 days, 1 hour and 41 minutes.
4451997007 | Comanche Peak 1, Comanche Peak 2 | 08/20/1997 | 09/26/1997 | 9710010014 | <strong>POST WORK TESTING FOR A CONTAINMENT ISOLATION VALVE WAS NOT PERFORMED AFTER MAINTENANCE</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1997, during a review of a Comanche Peak Steam Electric Station (CPSES) deficiency document, control room personnel discovered that the required post work testing was not completed for a containment isolation valve. Upon discovery, the required post work test was immediately performed with satisfactory results. To prevent recurrence, additional guidance is being provided to the responsible work organizations concerning the testing requirements for the subject valves.
4451997008 | Comanche Peak 1, Comanche Peak 2 | 10/02/1997 | 02/27/1998 | 9803050249 | <strong>MINIMUM GAP FOR COLD LEG INJECTION ECCS THROTTLE VALVES NOT IN ACCORDANCE WITH DESIGN</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1997, at approximately 1:00 p.m. CDT, a condition was identified with the potential to prevent multiple Emergency Core Cooling System (ECCS) lines from performing their intended design function following a Loss of Coolant Accident (LOCA). The as found condition was that the containment recirculation sump screen mesh size was greater than the available gap in more than one ECCS injection throttle valve. This condition could potentially result in the interruption of ECCS flow for the affected lines. On October 2, 1997, at approximately 4:43 p.m. CST, TU Electric concluded that the postulated scenario was credible and a condition that resulted in the plant being outside of the design basis did exist. TU Electric believes that the cause of this condition was the failure to identify the severely throttled valve position and the internal valve design which resulted in an available gap size of less than the containment sump screen mesh size. This condition existed within the original configuration of the plant after ECCS flow balancing to Westinghouse supplied criteria. Analysis of this condition has determined that the ECCS remains OPERABLE. However, corrective action will be implemented by completion of design modifications to restore the original design basis of the plant by the end of the seventh refueling outage for Unit 1 (1RF07) and the next available refueling outage for Unit 2 (2RF04).
4451997009 | Comanche Peak 1, Comanche Peak 2 | 10/27/1997 | 11/25/1997 | 9712030030 | <strong>SLOW OPENING OF THE UNIT 1 EAST BUS SUPPLY RESULTED IN TURBINE TRIP AND SUBSEQUENT REACTOR TRIP</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1997, at approximately 10:44 a.m. Comanche Peak Steam Electric Station Unit 1 experienced a reactor trip initiated due to a main turbine generator trip. Prior to the event, testing of the high voltage switchyard east bus lockout relays was being performed. Slow opening of the Unit 1 generator east bus supply breaker during the testing caused the backup bus protection relay to actuate and tripped the Unit 1 generator west bus supply breaker. This resulted in a Unit 1 loss of load and an automatic turbine and reactor trip. All systems responded normally on the reactor trip and auxiliary feedwater was manually initiated. The cause of the event was the slow operation of the Unit 1 east bus supply breaker. Additionally, it was determined that the work instructions provided insufficient detail to defeat the backup relay protection during the performance of the test.
4451997010 | Comanche Peak 1, Comanche Peak 2 | 12/12/1997 | 01/12/1998 | 9801200097 | <strong>TECHNICAL SPECIFICATION REQUIRED SHUTDOWN DUE TO INOPERABLE SOLID STATE SAFEGUARDS SEQUENCER</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1997, at 11:27 p.m., the Control Room staff (utility, licensed) noted an output relay coil continuity failure in the Solid State Safeguards sequencer. After some trouble shooting the Train B Solid State Safeguards Sequencer was declared inoperable. At 4:03 a.m., December 13, 1997, the control room staff commenced shutdown of CPSES Unit 1, as required by CPSES Technical Specification 3.3.2 Action Statement 26. The Train A Solid State Safeguard Sequencer remained operable throughout this condition. The cause of the event was an output relay coil continuity failure, troubleshooting identified a failed lamp in the optical isolator. The open lamp caused the test to fail. The failed lamp was replaced and the system was declared operable on December 13, 1997, at 7:02 p.m.
4461997001 | Comanche Peak 2, Comanche Peak 1 | 04/15/1997 | 05/15/1997 | 9705210044 | <strong>AUXILIARY FEEDWATER STEAM ADMISSION VALVE FAILED OPEN DUE TO A RUPTURED DIAPHRAHM</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 15, 1997, at approximately 12:37 a.m., while CPSES Unit 2 was in Mode 1 at 100% reactor power, the auxiliary feedwater turbine steam admission valve, 2-HV-2452-2, failed open due to leakage through the valve diaphragm, starting the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) 2-01. Water flowed from the TDAFWP to all four steam generators for approximately 30 - 40 seconds until the flow control valves were closed. On April 20, 1997, at approximately 12:03 p.m., 2-HV-2452-2 came off its closed seat due to leakage through a newly replaced diaphragm. No water flowed into the steam generators. The TDAFWP speed control annunciator alerted the Control Room Staff to a start of the TDAFWP for both the events. TU Electric believes that the cause of this condition was that new 'thick' replacement diaphragms developed by the valve vendor were susceptible to under torquing (pullout) and over torquing (crush). The auxiliary feedwater system remained capable of performing its intended safety function throughout the event. A replacement 'thin' diaphragm (original design) has been obtained and installed in the auxiliary feedwater turbine steam admission valve, 2-HV-2452-2. This report also includes reporting data pursuant to the requirements of 10CFR21.
4461997002 | Comanche Peak 2, Comanche Peak 1 | 10/25/1997 | 11/24/1997 | 9712020151 | <strong>MANUAL REACTOR TRIP DUE TO FAILURE OF ROD CONTROL SYSTEM</strong><br /><i>Abstract:&nbsp;</i>On October 25, 1997, Comanche Peak Steam Electric Station Unit 2 was in Mode 1 and had commenced a Unit shutdown in preparation for the third refueling outage. At approximately 12:17 a.m., prior to the event, troubleshooting efforts were in progress for a phase failure indication associated with the moveable coils for control rod Bank C. At approximately 4:04 a.m., attempt was made to move Bank C. When the Reactor Operator (Utility, Licensed) placed the In-Hold-Out switch to the "out" position, a Rod Control Urgent Failure alarm was received and an indication of four dropped rods. The Reactor Operator manually tripped the reactor based on the indication of 4 dropped rods. All rods fully inserted when the Reactor Trip Breakers opened. TU Electric concluded that a failure of phase sensing transformer T2 within the rod control cabinet 2AC generated the first fault resulting in an urgent failure alarm. Subsequent troubleshooting resulted in replacement of regulation card. The replaced regulation card had a bent pin which caused the actual dropped rods. The bent pin was possibly caused during insertion of the regulation card. The Phase Sensing Transformer T2 has been replaced. Additional corrective actions including inspection/refurbishment of the rod control system with respect to rod control system are complete.
4461997003 | Comanche Peak 2, Comanche Peak 1 | 11/08/1997 | 12/08/1997 | 9712150237 | <strong>CORE ALTERNATIONS PERFORMED BEFORE COMPLETING ALL THE PREREQUISITES</strong><br /><i>Abstract:&nbsp;</i>On November 8, 1997, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 6, during its third refueling outage (2RF03) and in preparation of core offload. Following the upper internal removal in preparation for the core offload the fuel handling supervisor (Utility, Licensed) directed personnel in the area to position the lights in the vessel for core offload. By CPSES Technical Specifications this action is a core alteration. The fuel handling supervisor overlooked the requirements for core alterations. It was determined that core alterations had been conducted without all of the Technical Specification requirements in place. Self checking was determined to be less than adequate when the Fuel Handling Supervisor nor the remainder of the refueling crew stopped and examined whether the activity about to be conducted was consistent with plant conditions and governing requirements. The core alterations were suspended, prerequisites were completed and core offload was resumed.
4461997004 | Comanche Peak 2, Comanche Peak 1 | 11/08/1997 | 06/08/1998 | 9806120041 | <strong>GAPS IN STRUCTURAL COMPONENTS OF THE CONTAINMENT SUMP TRASH RACKS</strong><br /><i>Abstract:&nbsp;</i>On Saturday, November 8, 1997, while performing a coating inspection inside Unit 2 containment, the coating inspector (utility non-licensed), observed some gaps in the Unit 2 containment sump trash rack support structures that appeared to be larger than the system description specified in Section 6.2.2.2.1, "Component Description," of the FSAR (0.115 inches). Since the sump screens still met the prescribed design basis of Regulatory Guide 1.82 and Section 6.2.2.1 of the FSAR, "Design Basis," and structural gaps were smaller than those bounding sizes that would adversely affect the recirculation lines and system components, operability was not affected. Sump structural gaps is a condition which was initially identified in November of 1994 for which corrective action was previously performed. Immediate actions included verifying that this condition does not negatively interact with the condition reported in CPSES Unit 1 LER 445/97-008-00 to prevent ECCS recirculation in the event of an accident. The gaps in the Unit 2 containment sump trash racks were repaired. Unit 1 containment sump trash racks were inspected prior to startup of the next refueling outage. This is a voluntary LER.
4461997005 | Comanche Peak 2, Comanche Peak 1 | 11/10/1997 | 12/10/1997 | 9712170381 | <strong>CONTAINMENT PERSONNEL AIRLOCK RENDERED INOPERABLE DURING CORE ALTERNATIONS</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1997, at approximately 10:10 P.M., following discovery that maintenance was in progress on the inner door operating system of the Unit 2 Containment Personnel Airlock (PAL) with the door open, the PAL System Engineer determined that the Unit 2 PAL outer door hydraulic equalization valve was not fully closed and would not fully close when the outer door was manually closed. This could have prevented establishing containment integrity if needed during core alterations. The cause of this condition was less than adequate procedures governing PAL operation and containment integrity verification related to the PAL during refueling operations. Corrective actions taken include revising procedures and reperforming the containment integrity surveillance required by the Technical Specifications for refueling operations.
4541997001 | Byron 1, Byron 2 | 01/31/1997 | 03/01/1997 | 9703100244 | <strong>Hydros on the DG not Performed Due to Surveillance Tracking Error</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 097%. On 09/07/95 Surveillance (SURV) procedures 1/2 BVS 4.10-5 were suspended from the General Surveillance (GSRV) tracking system. Following the suspension, it was discovered that Technical Specification (TS) 3/4.8.1.1.2.h.2 had been covered under the suspended SURV. On 04/18/96 it was felt the TS SURV requirements were within frequency. On 01/31/97 it was determined that Byron had not performed the Unit 1 A train SURV in the time frame required under the TS. On 02/01/97 it was determined that the Unit 2 A and B train SURV were not performed in accordance with the TS. On 02/01/97, it was determined that TS 4.0.3 had not been invoked earlier, when it should have been. Missing the 1A, 2A, and 2B SURV requirements was the result of an inadequate tracking mechanism. Missing the 1 hour implementation of the appropriate TS action requirement was the result of an unclear understanding of section 4.0.3 of the TS. Corrective actions include satisfying the TS SURV requirements, and developing a SURV requirements matrix and requiring its review before suspensions from GSRV. Other actions include enhancing the written TS interpretation and LCOAR pages, and providing training to SROs. These events are reportable per 10CFR50.73(a)(2)(i)(B) - any operation or condition prohibited by the plant's Technical Specifications. Surveillance requirements for Technical Specification 3/4.8.1.1.2.h.2 were missed for the 1A, 2A, and 2B diesel generators.
4541997002 | Byron 1, Byron 2 | 02/11/1997 | 03/12/1997 | 9703190169 | <strong>480 Vac Breakers Found in Remove Position Instead of the Qualified Disconnect Position</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 097%. During Operator On The Job Training (OJT) walkdowns on 02/11/97, several Non-Safety Related 480 volt Air Circuit Breakers [BKR] (ACBs) were identified in the remove position within their cubicles. An investigation was immediately initiated to walkdown all Safety Related and Non-Safety Related 480 volt [EC] ACBs. were found in the remove position and were returned to their disconnect position on 02/11/97. qualified with the breakers in the connect and disconnect positions but are not seismically qualified with the breakers in the remove position. On 02/13/97, a 'B' operator (non-licensed) noticed Safety Related ACB 131Z-3B installed in the remove position. The ACB had been taken out-of-service and removed from its cubicle for repair by maintenance prior to the walkdown on 02/11/97 and returned to the cubicle after the walkdown. ACB 131Z-3B was returned to the disconnect position. The cause of this event was failure of management to implement measures to assure work practices were maintained over time. Maintenance and Operating personnel have been briefed on the proper positioning of 480 volt ACBs. Electricians will be trained on how to correctly position ACBs. Procedures associated with positioning ACBs are being revised to assure they are left in disconnect or connect. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. This event is reportable per 10CFR50.73(a)(2)(ii)(B)- any condition that was outside the design basis of the plant.
4541997003 | Byron 1, Byron 2 | 02/18/1997 | 03/19/1997 | 9703260123 | <strong>Equipment Hatch Gallery Not Properly Attached to the Containment Structure</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. During a Unit 1 Containment [NH] walkdown on February 18, 1997, site personnel determined the access gallery for the equipment hatch was not secured to the containment structure. Due to this discovery on Unit 1, an at power containment entry was made for Unit 2 and determined all but one access gallery attachment to the containment structure was in place. On 02/24/97, the Unit 1 access gallery was attached to the containment structure. Not all attachments to the structure were able to be installed. Operability assessment 97-019 was performed and determined that in the event of seismic acceleration, the gallery will remain intact and secured to the containment structure. Operability assessment 97-017 was performed for the Unit 2 Containment Equipment Hatch Access Gallery and determined that in the event of seismic acceleration, the gallery will remain intact and secured to the concrete structure. The cause of the Unit 1 event was inadequate procedural direction and a lack of questioning attitude. The cause of the Unit 2 event was an original construction deficiency. Containment Equipment Hatch Removal and Installation Procedure BMP 3300-1 and the Maintenance Procedure Writers Guide BAP 400-19 will be revised. A heightened level of awareness review for plant equipment design requirements will be performed with all maintenance personnel. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. This event is reportable per 10CFR50.73(a)(2)(ii)(B)-any condition that was outside the design basis of the plant.
4541997004 | Byron 1, Byron 2 | 02/15/1997 | 03/15/1997 | 9703240151 | <strong>Thrust Bearings Installed Backward on the RH and CS Pumps Due to Lack of Specific System/Component Knowledge</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 15, 1997, at 1432 hrs. the 1A Residual Heat Removal (RHR) pump was placed in shutdown cooling in preparation for the upcoming B1F17 outage. At 1620 hrs., an Equipment Attendant (EA) reported a steam leak in the 1A RHR pump room. The 1A RHR pump was shut down at 1635 hrs. Investigation showed that the 1A RHR pump seal was leaking. Preliminary indications were that an increased load was placed on the seal faces due to the shaft seal not being properly loaded. The cause was due to the incorrect installation of the lower motor bearing which allowed excessive end play. Excessive end play allowed the motor to thrust upward, causing an increased load on the seal faces resulting in seal failure. Subsequently, a review of the RH and CS pump/motors maintenance work history was completed. It was determined the 1B RHR pump and the 1A and B Containment Spray (CS) pumps should be inspected to check axial end play. Both Unit 1 CS pumps showed excessive end play. Unit 1 CS pump motor bearings were replaced and an axial end play check to verify correct installation was performed. Since the 1985/86 time frame, the 1A RH and 1B CS pumps were considered to be inoperable due to the results of this investigation. There have been cases when the 1B RH and 1A CS trains were taken out-of-service for other activities. However, based upon operating history, i.e., ASME pump runs, surveillances and required operation of the 1A RH and 1B CS pumps, the pumps were considered available. The cause of this event was lack of specific system or component knowledge which lead to both RH and CS pump/motor bearings being installed wrong by vendor supervision. We are reporting this event because it is a condition that was outside the Design Basis of the Plant. This issue is reportable per 10CFR50.73 (a)(2)(ii)(B) - any condition that was outside the design basis of the plant.
4541997008 | Byron 1, Byron 2 | 04/03/1997 | 05/29/1997 | 9706050131 | <strong>INADEQUATE MANUFACTURER BREAKER REPAIR PROGRAM ALLOWED WRONG PARTS TO BE INSTALLED</strong><br /><i>Abstract:&nbsp;</i>During offsite refurbishment of Safety Related Westinghouse [W120] DS-206 breakers [BKR], the manufacturer inadvertently replaced the breaker closing springs with heavier duty closing springs. Byron Station was notified by the manufacturer, that five (5) DS-206 breakers had been refurbished with the wrong closing springs. Two (2) of the defective breakers had been installed in the Ultimate Heat Sink (UHS) Essential Service Water (SX) [BI] High Speed Fan Breaker Cubicles after being returned to the Station. Upon discovery, the defective breakers were taken out of service, replaced with fully qualified breakers and the defective breakers were placed on hold for return to the manufacturer. The cause of the event was the manufacturer did not have an adequate quality process in place to control the repair of Safety Related breakers. The manufacturer issued a stop work order prior to the discovery of this event to stop the repair of breakers at their Lansing, IL. Facility. Westinghouse has redirected their focus and attention in establishing a high quality breaker refurbishment program, at the Lansing facility. Historically, due to the temporary declaration of inoperability for the two SX fans, it was determined that on three (3) occasions, Byron Station had more than the Technical Specification (TS) allowed number of SX fans inoperable at a given time. It was determined by Byron Station that this event is reportable per 10CFR50.73(a)(2)(i)(B)-any operation or condition prohibited by the plants Technical Specification. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. (p:\regassur\pifler\ler\wp9601r.wpf\052097)
4541997009 | Byron 1, Byron 2 | 05/22/1997 | 06/23/1997 | 9706300036 | <strong>MISSED TECHNICAL SPECIFICATION SURVEILLANCE</strong><br /><i>Abstract:&nbsp;</i>Pursuant to Technical Specification (TS) 4.5.2, ECCS Subsystems, venting the Chemical and Volume Control System {CB} (CV) pump casings and discharge piping high points outside of containment is required to be performed every 31 days. However, the monthly surveillance procedure used to meet this TS criterion does not require the applicable high head injection (CV) system components to be vented. This deficiency was attributed to managerial methods allowing the approval of a document, surveillance 1 BOS 5.2.b-1 / 2 BOS 5.2.b-1, without adequate critique or technical review. The procedure was approved without the requirement of venting the CV high head injection components, primarily because the CV pumps are designed to be self venting (i.e. the pumps do not have vents on the pump casings). Corrective actions included weekly Ultrasonic examinations (UT) of piping, issuance of a Daily Order to Operators, discussion of gas accumulation in stagnant lines, an exigent Technical Specification change and, a procedure revision to include the monthly UT examinations and the 1RH027 valve into the Unit 1 Monthly ECCS Venting Surveillance. 10 CFR 50.73 (a)(2)(i) requires Licensee to report operations or conditions prohibited by the plant's Technical Specifications. The surveillance requirements for 4.5.2.b-1 had not been completed and the equipment was inoperable for more than the LCO allowable time. (p-\regassur\pifler\ler\wp9598r.wpf\061397)
4541997010 | Byron 1, Byron 2 | 05/27/1997 | 06/26/1997 | 9707030025 | <strong>Faulty Review Causes Failure to Test Relays and Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>Letdown containment isolation valve slave relay contacts were not tested on a quarterly basis as required by Technical Specifications. This was found during a senior management review of outstanding issues. The failure to test containment isolation valve relays caused both units to enter Tech Spec 3.0.3 with a 24 hour extension per Tech Spec 4.0.3. The relay contacts were properly tested on 5/27/97. Further review found a similar concern with the letdown orifice block valves. The block valve relay contacts were tested on 5/28/97. In September, 1990, Westinghouse [W120] recommended preventing the valves from closing to minimize thermal transients. The cause of the improper testing was a deficient 1990 Onsite Review that allowed electrical jumpers to be used to prevent closure of the containment isolation valves. The time elapsed since the 1990 Onsite Review prevented definitive corrective actions, however improvements made since 1 994 minimize probability of recurrence. A contributing cause was delaying a modification based on a pending Technical Specification change and then repeatedly extending the due date. The event had minimal safety impact due to procedures in place to mitigate low probability multiple relay failures. The event is reportable per 10 CFR 50.73(a)(2)(i), Operation Prohibited by Technical Specifications. (p:\regassur\pifler\ler\wp9594r.wpf\062497)
4541997012 | Byron 1 | 05/29/1997 | 06/30/1997 | 9707090030 | <strong>Plant Shutdown Required Within 48 Hours Per Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On 05/29/97, Unit 1 was at 97 percent reactor power. System Engineering was performing 1BVS 7.1.5-2, Unit 1 Main Steam Isolation Valves Partial Stroke test, on the 1A Main Steam [SB] Isolation Valve (MSIV). The surveillance failed when the active train of the 1A MSIV failed to recharge properly at 1114. Operations entered action requirement for Technical Specification 3.3.2.c, Table 3.3-3, Action 22. The stand-by train of the 1A MSIV remained operable. The air/oil pump was replaced. Electrical Maintenance personnel were sent to replace the "C" and "D" solenoids. After initial replacement of the solenoids, it was identified the "D" solenoid as not being the proper solenoid and a new "D" solenoid was installed. The active train accumulator still did not pressurize. The MSIV was not repaired within a forty-eight hour time limit and Unit 1 was required to shutdown according to Technical Specification 3.3.2.c., which requires restoration of the inoperable channel to OPERABLE status within 48 hours. On 05/31/97, the turbine was tripped and Unit 1 entered Mode 2 at 1453, and Mode 4 at 2229. The four-way valve was replaced. The removed four-way valve was disassembled and the removed solenoids were benched tested. No apparent problem was found with either the four-way valve or the solenoids. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. This event is reportable per 10CRF 50.73 (a)(2)(i) (Completion of any nuclear plant shutdown required by the plant's Technical Specification). Corrective action: The Unit was shutdown as required by Technical Specifications. The four-way valve was replaced and stroke tested successfully. No previous occurrences were found. (p:\regassur\pifler\ler\wp9595r.wpf\062397)
4541997013 | Byron 1 | 05/22/1997 | 06/20/1997 | 9706250420 | <strong>VALVE MISTAKENLY OPENED CAUSES POST-LOCA LEAKAGE TO EXCEED LIMIT</strong><br /><i>Abstract:&nbsp;</i>The 1B Safety Injection pump suction vent valve was found open on operator rounds and was promptly closed. Difficulties had occurred with pump venting on the previous day. The last time the valve was known to have been operated was 20 hours earlier to support troubleshooting. Had a design LOCA occurred with the vent open, the non-seismic piping downstream of the vent is assumed to fail. The resulting leakage of contaminated sump water could cause offsite doses to substantially exceed regulatory limits. This exceedance would occur during recirculation when the Residual Heat Removal pump pumps containment sump water to the Safety Injection pump suction. The cause of the valve being open is unknown. Work activities in the area were reviewed and none were found that manipulated the valve. An evaluation will be done to increase awareness/strengthen controls on components that could increase post-LOCA ECCS leakage. Based on evaluations of pump operability by the vendor, flooding impact, effects on ECCS flow and realistic dose estimates, this event did not pose a threat to the health and safety of the public or plant personnel. This event is reportable under 10 CFR 50.73(a)(2)(ii)(B), Operation Outside the Design Basis. (p:\regassur\pifler\ler\wp9597ra.wpf\061797)
4541997014 | Byron 1, Byron 2 | 06/12/1997 | 07/14/1997 | 9707230302 | <strong>TESTING OF P-11 PERMISSIVE MISSED DUE TO INADEQUATE PROCEDURE</strong><br /><i>Abstract:&nbsp;</i>On 6-12-97, during a review of an industry Operating Experience which identified a lack of proper testing of the P-11 interlock circuitry, it was determined that the same situation existed at Byron. Performing the customary verification of the associated Solid State Protection System input relays does not properly check the P-11 input relays. Because of this deficiency a valid test of the entire channel, for the P-11 function, as defined by technical specifications was not met. Station personnel held an Onsite Review and completed Action 20 of Technical Specification Table 3.3-3. Later that day the action statement was exited when a review of plant data indicated the proper operation of the P-11 Permissive during two recent shutdowns of Units 1 and 2. The cause of this event is due to improper development of the Instrument Maintenance Department (IMD) surveillance procedure to properly test the P-11 function as it leaves the process protection system instrumentation and inputs into the Solid State Protection System. This event had minimal safety significance because the P-11 interlock was found to be operating correctly in response to plant conditions. The IMD procedures were revised to test the input relays at power. The revised procedures were performed on both units. There were two previous events that were similar to this event. The corrective actions from these events would not have prevented this event. This event is reportable under 10CFR50.73(a)(2)(i)(B) as any operation or condition prohibited by the Technical Specifications. (p:\regassur\pifler\ler\wp9592r.wpf\070297
4541997015 | Byron 1, Byron 2 | 08/13/1997 | 09/10/1997 | 9709160077 | <strong>CONTAINMENT PENETRATION TEST, VENT AND DRAIN VALVES NOT SURVEILLED WITHIN 31 DAYS DUE TO DIFFERENCE IN INTERPRETATION</strong><br /><i>Abstract:&nbsp;</i>In 1995, the Byron Station procedures governing this test (1/2BOS 6.1.1.a-1, "Primary Containment Integrity Verification of Outside Containment Isolation Devices," and 1/2BOS 6.1.1.a-3, "Primary Containment Integrity Verification of Outside Containment Isolation Devices In Cold Shutdown") were revised under the provisions of 10CFR 50.59 to change the test frequency for the test, vent and drain valves from 31 days to once per entry into cold shutdown if not done within the previous 92 days. The NRC issued "Safety Evaluation by the Office of Nuclear Reactor Regulation Catawba Containment Integrity Positions (Region II TIA 96-015)." Byron became aware of this issue on 8/1 3/97 and recognized its significance to plant surveillances. Included in this evaluation was NRC's position on containment penetration test, vent and drain valves. NRC stated that these valves are for containment isolation and, therefore, their position must be verified every 31 days. The affected valves were verified to be in their proper position and will be verified every 31 days. The affected valves were verified to be in their proper position and will be verified every 31 days. (p:\regassur\pifler\ler\wp9576r.wpf\090497)
4541997016 | Byron 1 | 10/07/1997 | 11/05/1997 | 9711100080 | <strong>Projected Steam Generator Leak Rate Combined with Technical Specification Limit for Dose Equivalent Iodine Creates Potential for Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>The operability of the steam generators is determined through an augmented in-service inspection program and application of Technical Specification (TS) listed acceptance criteria. As part of the requirements for voltage based repair criteria for steam generator tubing with Outer Diameter Stress Corrosion Cracking (ODSCC), potential leakage during a Main Steam Line Break accident with containment bypass must be calculated. This calculated leak rate value is then compared to the site allowable accident leakage limit. The site allowable accident leakage limit results in a dose corresponding to 10% of 10 CFR Part 100 assuming maximum TS allowable Reactor Coolant System Dose Equivalent (DE) Iodine-131. The current licensing basis maximum site allowable leakage limit for Byron Unit 1 Cycle 8 (BY1C8) is 36.5 gpm. This leakage limit value is given at operating conditions. Calculations indicate that the total Predicted Accident tube leakage at the end of BY1C8 is 63.1 gpm which exceeds the current licensing basis value of 36.5 gpm. A TS amendment request was submitted 1/97 to lower the DE Iodine-131 limit to allow an increase in the site allowable accident leakage limit. The projected accident leak rate exceeded 36.5 gpm on 10/7/97. Approval of the TS amendment request to lower the DE Iodine-131 limit was not received prior to the projected accident leak rate exceeding the limit. An operability assessment was performed to justify continued operation. This event is reportable per 10 CFR 50.73(a)(2)(ii). (p:\regassur\pifler\ler\wp9567r.wpf\102797)
4541997017 | Byron 1 | 10/09/1997 | 08/31/1998 | 9809040275 | <strong>Completion of Shutdown Initiated due to Degraded Condition of Safety Injection System Found Monthly Venting Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 10/09/97 an excessive amount of gas was noted as coming out of solution while venting from the Safety Injection [BQ] (SI) discharge piping vents. While venting the discharge piping, the 1C SI accumulator level and pressure decreased. Venting was halted and the accumulator level and pressure stabilized. The excessive gas in solution in the SI discharge piping was the result of the Reactor Coolant System [AB] (RCS) cold leg back-up check-valve leaking by, allowing nitrogen saturated water from the 1C SI accumulator to reach the vent location. The leak-rate, as measured in terms of accumulator level decrease over time, while venting, exceeded the Technical Specification limit of 1 gallon per minute. A unit shutdown was initiated and completed. Corrective action was to replace the 1C Safety Injection accumulator cold leg check valve. No previous events were found where corrective actions were specifically applicable to this event. The safety of the plant and the public was not affected by this event. This event is reportable per 10 CFR 50.73(a)(1), 50.73(a)(2)(ii), and 50.73(a)(2)(i)(A).
4541997018 | Byron 1, Byron 2 | 10/23/1997 | 11/21/1997 | 9711280104 | <strong>Missed ECCS Venting Surveillance due to Ineffective Supervisory Methods</strong><br /><i>Abstract:&nbsp;</i>On October 23, 1997, during review of the Emergency Core Cooling System Monthly Venting Surveillance procedure and field walkdown, it was discovered that two Unit 1 vent valves were not included in the procedure. This resulted in entrance into Technical Specification 4.0.3. Corrective actions following an event on May 22, 1997 (LER 97-009) were not effectively implemented due to failure to implement supervisory methods to control time pressure and distractions affecting the system engineers during performance of corrective actions. Unit 1 and 2 Residual Heat Removal [BP] (RH), Chemical and Volume Control [CB] (CV), and Safety Injection (Low Head) [BP] (SI) piping isometrics were reviewed to ensure that no other vent valves existed that were not included in the venting procedure. A Temporary Procedure Change Request was initiated to add the vent valves to the surveillance procedure. The system was vented through the two vent valves, and no air was discovered at either location. This report was reviewed by the involved System Engineer and Supervisor for lessons-learned. A refresher of Human Error Reduction techniques for managing time pressure and work-place distractions shall be conducted with the System Engineering Department. Plant and public safety was not affected by this event. The SI system was fully capable of performing its design function, including mitigation of design basis accidents. This event is reportable per 10 CFR 50.73(a)(2)(i)(B). (p:\regassur\pifler\ler\wp9563r.wpf\110797)
4541997019 | Byron 1, Byron 2 | 10/28/1997 | 12/21/1997 | 9801050080 | <strong>Potential Failure of Westinghouse Fuel Caused by Inadequate Design Code</strong><br /><i>Abstract:&nbsp;</i>Westinghouse analysis shows that for high power, high burnup assembly Integral Fuel Burnable Absorber fuel rods, calculated rod internal pressures are in excess of the Westinghouse fuel rod design criterion that "the fuel rod pellet-to-clad gap shall not re-open." Additionally, if the "no gap re-opening" criterion is exceeded, the 17% clad oxidation limit following postulated Loss of Coolant Accident event, as defined in 10CFR50.46, can likewise be exceeded. Westinghouse has since determined that all currently operating plants are in compliance with 10CFR50.46. Westinghouse has completed the Byron Unit 2 analyses using plant specific conditions which conclude there is no gap re-opening and the 17% post-LOCA clad oxidation limit is not exceeded. All fuel design limits and 10CFR50.46 criteria are met. Cause of the issue was that Westinghouse used inadequate methods and incorrect assumptions in the fuel rod design code. Corrective actions are: Westinghouse to review and improve analytical models; gather additional data; and perform plant by plant assessments. Byron Station will address this issue in the Byron Unit 1 Cycle 9 safety evaluation. A search of the Nuclear Station Regulatory Assurance database found no previous occurrences. The fuel rod design issues potentially result in a condition outside the design basis reportable per 10CFR73(a)(2)(ii). (p:\regassur\pifler\ler\wp9554r.wpf\121597)
4541997020 | Byron 1, Byron 2 | 09/30/1997 | 11/24/1997 | 9712020154 | <strong>Excessive Operator Response Times due to Inadequate Analysis Implementation</strong><br /><i>Abstract:&nbsp;</i>During a Steam Generator Tube Rupture (SGTR) procedure review, a condition was found where operators would be sent to a procedure not in the time-validated sequence, resulting in steam generator overfill for a SGTR. This transition would result from a large drop in coolant temperature that had not been addressed in the SGTR procedure. The plant-specific analysis that showed the temperature drop was not properly incorporated in the procedure. If a steam generator overfill had occurred the resulting doses would be bounded by existing analyses. The SGTR procedure was revised to address the temperature drop. Other plant-specific analyses will be reviewed for similar problems. A more formal interface between the procedure writers and the accident analysis group will be evaluated. There were no previous occurrences of a similar nature. This is reportable under 10CFR50.73(a)(2)(ii). (p:\regassur\pifler\ler\wp9562r.wpf\111797)
4541997021 | Byron 1, Byron 2 | 10/28/1997 | 11/25/1997 | 9712020170 | <strong>Operation Outside Ventilation Design Basis due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>A control room door was removed and a non-seismically qualified structure was relied on to maintain the control room pressure boundary. Investigation found that previous maintenance activities had also relied on non-seismic structures. The process for impairing ventilation barriers was found to be inadequate in that no direction was given to review for impact on seismic qualifications of the impaired structure and to ensure the compensatory measures were inclusive of seismic concerns. An immediate action was to provide a temporary barrier, As an interim measure, personnel involved with door maintenance have been told of the sensitivity of ventilation barriers. As a long-term corrective action, administrative controls will be strengthened to provide clear direction for ventilation barriers. This revision will be broad-based and not just limited to seismic issues. This is being reported per 10CFR50.73 (a)(2)(ii). p:\regassur\pifler\ler\wp9559r.wpf\112097)
4541997022 | Byron 1, Byron 2 | 11/14/1997 | 12/08/1997 | 9712180062 | <strong>SSPS Logic Testing Not Performed Due to Inadequate Testing Design</strong><br /><i>Abstract:&nbsp;</i>On November 14, 1997, Byron Station Unit 1 had entered refueling outage B1R08, was in Mode 5, and proceeding with scheduled activities to enter Mode 6. Byron Station Unit 2 was at full power operation with all safety systems available. During a review of Generic Letter 96-01 (Testing of Safety Related Logic Circuits), a discovery within the industry revealed current Solid State Protection System (SSPS) [JE] [JG] testing was inadequate. Byron and Braidwood Stations determined current SSPS testing did not test all functions of some memory logic circuits. As such, a missed surveillance condition was determined to exist. The cause for this event was that the original testing design prescribed by the vendor did not fully verify proper operation of the SSPS logic cards. Corrective action to resolve the inadequate testing is to add new testing criteria to the SSPS Bi-monthly surveillance procedures. Unit 2 Train A/B SSPS Bi-Monthly testing was successfully performed on 11/14/97. Unit 1 Train A/B SSPS Bi-Monthly testing will be performed prior to Unit 1 entering Mode 4 while returning to power operation from refueling outage B1R08. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. This event is reportable per 10CFR50.73(a)(2)(i)(b)-any operation or condition prohibited by the plant's Technical Specifications. (p:\regassur\pifler\ler\wp9556r.wpf\120197
4541997023 | Byron 1 | 12/29/1997 | 03/04/1998 | 9803090393 | <strong>1B Diesel Generator Control Power Wiring Discrepancy due to a Modification Installation Error and Programmatic Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On December 29, 1997, during the performance of Special Procedure 97-033, it was discovered that the 1B Emergency Diesel Generator (DG) was wired in such a configuration that it may not have continued to operate if a fire had occurred in fire zones 11.5-0 or 11.6-0. A wiring error occurred in May of 1996 during the installation of a design change which re-powered vital components to the credited DC control power supply relied upon for the 1B DG. A normally connected wire was mistakenly removed and the intended wire which remained resulted in both DG DC control power supplies being cross-tied. A fire in zone 11.5-0 or 11.6-0 could have resulted in the loss of both control power circuits for the 1B DG. The DG control circuit was not impacted in any way by the incorrectly removed wire. The cause of the wiring problem was both an error on the part of the technician installing the design change and a programmatic deficiency in that the installation process did not provide for independent verification. The corrective actions include counseling the technician involved in the installation error by management and initiating programmatic changes to require independent verification for all Safety Related and Regulatory Related design changes which involve wiring termination/determinations. In addition, a comprehensive wiring verification was performed in all four DG local panels to confirm the as-built configuration of the wiring against design drawings. This event is reportable per 10CFR50.73(a)(2)(ii). (p:\regassur\pifler\ler\wp9545r.wpf\022598)
4551997001 | Byron 2 | 03/15/1997 | 04/17/1997 | 9704220096 | <strong>UNIT 2 CONTAINMENT DRAIN SYSTEM CLOGGED DUE TO DEBRIS</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. ABSTRACT On March 15, 19 97, Unit 2 was cooling down and entering maintenance outage B2F18. The Unit 2 containment floor drains were found full of water during the Mode 3 walkdown. It was determined that debris had clogged the flow control device. This blockage would not allow the weir box to dete ct a one gallon per minute leak in containment. A water hose was used t o blast the blockage clear at the flow control device and all drains op ened up. An at p ower containment entry was made for Unit 1 to check the contai nment drains on March 19, 1997, which found no drains blocked The root cause for this blockage was the concrete and bar grating to the ent rance of the drain system was not installed in accordance with design sp ecifications. This allowed debris to enter the drain system and become l odged in the flow control device. Operability assessment 97-027 was performed for the Unit 2 leak detection system[BD] for the deficiency in the bar gratings. There have been no previous occurrences of this event. To prevent recurrence, a new bar grating design will be installed. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. This even t is reportable per 10CFR50.73(a)(2)(ii)(B) -any condition that was outs ide the design basis of the plant.
4551997003 | Byron 2 | 10/10/1997 | 11/04/1997 | 9711100093 | <strong>Reactor Trip Due to Age-Related Failures of Redundant Rod Drive Power Supplies</strong><br /><i>Abstract:&nbsp;</i>A Unit 2 reactor trip occurred at 1112 on 10/10/97 following the failure of redundant Rod Drive Power cabinet power supplies. One or more rods fell into the core, causing a trip on high negative flux rate. The day before, a local Power Supply Failure alarm was noted. Troubleshooting on the day of the trip found voltage on both supplies dropping. As an attempt was being made to install a temporary supply, the conditions finally reached the point where one or more gripper coils released their respective rods. Testing of all Rod Drive power supplies found 4 more failures between both units. The average age of all failed supplies was 76 months. A search of Operating Experience only found one occurrence relating to age concerns of Lambda power supplies. This was a 1995 report stating a 5 year life for Lambda power supplies. Pending confirmation from offsite testing, the failure of the power supplies is age-related. A contributor was the failure of the alarm to annunciate the first power supply failure. This vulnerability was pointed out in a 1987 vendor bulletin. Due to the low failure rate in 1987, the station chose to inspect the power supplies instead of modifying the alarm circuit. Corrective actions will be to periodically replace the power supplies and evaluate changes to the alarm circuit. This event is reportable per 10CFR50.73(a)(2)(iv). (p:\regassur\pifler\ler\wp9565r.wpf\102997)
4551997004 | Byron 2 | 09/12/1997 | 11/19/1997 | 9711280302 | <strong>Reverse Functioning Control Switch Due to Improper Actuator Installation and Failure to Recognize Reportability of the Issue</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1997, during the performance of BOP SI-21, it was determined that the control switch for the valve 2SI8964 was functioning backwards. The valve was declared inoperable and LCOAR 6.3-1a was entered. The control switch had maintenance performed on it six days prior to the discovery that it was functioning backwards. An action request was written to have the control switch fixed. The cause of the switch problem was an inadequate procedure for working on this type of switch. Also, pertaining to the work request for maintenance on the switch, errors were made by a maintenance supervisor. Initial screening of the problem failed to recognize the reportability of this event. The failure to recognize this event as reportable was due to an error by the root cause investigator. The corrective actions are to counsel the individuals involved and change the affected maintenance procedure. There were no previous occurrences of this type of event identified. There were no adverse affects on nuclear safety because of this event. This event is reportable per 10CFR50.73(a)(2)(i).
4561997001 | Braidwood 1, Braidwood 2 | 04/17/1997 | 05/14/1997 | 9705230006 | <strong>Both Main Control Room Chillers Inoperable Due to Equipment Failure and Surveillance Testing Resulting in Entry Into 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On 4/17/97, the 1A diesel generator sequencing test (1BwVS 8.1.1.2.F-19, 1A DG 5500 KW Load Rejection and Simulated Safety Injection in Conjunction with Under Voltage During Load Testing) was being completed. The 0A Main Control Room chiller breaker was in equipment test for the surveillance rendering it inoperable, and the appropriate LCOAR (7.6-1A) had been entered. In order to exit the LCOAR for the 0A Main Control Room chiller, it was necessary to shutdown the running 0B Main Control Room chiller and start the 0A Main Control Room chiller and declare it operable. The 0A Main Control Room chiller control switch was placed in pull-to-lock and the breaker was racked in to the connect position. At approximately 1413, the 0B Main Control Room chiller was shutdown. Valve 0SX063B started to close but indication was lost before the valve showed fully closed. Inspection of the breaker indicated that the thermal overloads had tripped. The 0B Main Control Room chiller was declared inoperable and LCOARs 7.6-1A and 3.0.3 were entered. The thermal overloads were reset and indication (dual) was restored. At 1420 the Unit 1 NSO started the 0A Main Control Room chiller with no abnormal indications. The 0A Main Control Room chiller was then declared operable and LCOARs 3.0.3 and 7.6-1A (for the 0A chiller) were exited. On 4/18/97 at CS30, the 0B VC chiller was declared operable and LCOAR 7.6-1A was exited. The cause of the event was equipment failure of the electrical valve operator. This event had minimal safety significance. Planned corrective actions include an overhaul of the actuator, replacement of the motor, and inspection of the 0SX063A valve.
4561997002 | Braidwood 1 | 04/21/1997 | 05/21/1997 | 9705230294 | <strong>Unit 1 Steam Generators declared Category C-3 per Tech. Spec Table 4.4-2 During the A1R06 Refuel Outage</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. A Steam Generator (SG) Tube Inservice Inspection performed on Braidwood Unit 1 (Westinghouse Model D-4 Steam Generators) revealed SGs 1A, 1B, 1C, and 1D as Category C-3 with greater than one percent of the inservice tubes being defective. Per Technical Specification 4.4.5.2, a SG will be classified in Category C-3 if more than 10 of the total tubes inspected are degraded or more than 1% of the total tubes inspected are defective. The primary cause of this event is circumferential outside Diameter Stress Corrosion Cracking (ODSCC) at the top-of-tubesheet roll transition region and axial ODSCC at the tube-to-Tube Support Plate intersections. Corrective actions include plugging or sleeving the repairable indications, the continuation of methoxypropylamine injection with review of other alternate amines, and the continuation of the elevated hydrazine program. Two tubes were removed from the 1A Steam Generator to evaluate the axial indications at the tube-to-Tube Support Plate as is required by Generic Letter 95-05. Sixteen tubes, with the largest indications, were insitu pressure and leak tested which verified structural and leakage integrity of the defective tubes. Circumferential indications were also identified at the top of the tubesheet in SG tubes that were not inservice. These tubes were unplugged to support inspections of the locks installed during A1R05. Forty-nine of the eighty-five SG tubes unplugged contained circumferential indications at the top of the tubesheet. A Westinghouse Laser Welded Sleeve was installed in 100% of the Locked tubes. Testing was performed that demonstrated that these tubes would have performed their function during an accident. This is the fifth Braidwood Unit 1 inspection with SGs being classified as Category C-3. The SGs have not exceeded their design plugging levels.
4561997003 | Braidwood 1 | 05/24/1997 | 06/23/1997 | 9706260321 | <strong>Manually Opened Reactor Trip Breakers Due to a Control Rod Drive Bank Overlap Malfunction</strong><br /><i>Abstract:&nbsp;</i>On 5/19/97, surveillance BwVS 500-2, Checkout of the Bank Overlap Unit, was successfully performed by the system Engineering Department. The purpose of this surveillance is to verify that the Bank Overlap Function and the Non-Urgent Alarms of the Rod Control System (AA) are operational. At 1728 on 5/24/97, surveillance BwVS 500-4, Initial Criticality After Refueling and Nuclear Heating Level, was initiated in conjunction with procedure 1BwGP 100-2, Plant Startup. During the reactor startup, manual rod movement occurred as expected until approximately 2225 when the Nuclear Station Operator (NSO, Licensed) was manually withdrawing Control Bank C and D. It was observed that Control Bank C was not moving as expected in response to its demand signal from the bank overlap unit. Annunciator 1-10-A7, Rod Deviation Power Range Tilt, alarmed; at 2310 the reactor was manually tripped by the NSO. The cause of the improper rod bank overlap was determined to be a failure of the thumbwheel switches due to dirty contacts. The safety significance of this event is minimal since the Rod Control System is a control system not required for safety. Corrective actions for this event included stopping rod withdrawal, and manually initiating a Reactor Trip; all rods fully inserted. Subsequently, the contacts were cleaned. The bank overlap surveillance procedure will be revised to include additional verifications.
4561997004 | Braidwood 1 | 05/23/1997 | 06/18/1997 | 9706300087 | <strong>Missed Tech Spec Surveillance Due to Clerical Error, a Weakness in the Tracking Program and Unclear Management Expectations</strong><br /><i>Abstract:&nbsp;</i>On 5/23/97, an incorrect "calculation type" was discovered in the surveillance program for Operations Surveillance 1BWOS 8.2.1.2.A-1, 125 volt D.C. Battery Bank and Charger Bus 111 Operability Surveillance. It was determined at this time that the surveillance had exceeded the allowed Tech Spec frequency on 5/22/97. Investigation of the event determined that the "calculation type" had been inadvertently changed as a result of a typographical error that occurred on 4/25/97. This event was determined to be the result of a skill based error by a data entry clerk. Inadequate management expectations for review of the daily exceptions report allowed the error to go undetected. Upon identification of the error, Operations was immediately informed and the surveillance was successfully completed. Corrective actions include the generation of a separate new report to ensure Tech Spec surveillances contain the proper "calculation type". The COMED corporate predefine users group is evaluating changes to the surveillance program which will protect critical database fields from being inadvertently changed. There were no safety consequences as a result of the missed surveillance as the prior and subsequent surveillances were successfully completed, redundant equipment was operable and cross-tie capability was available.
4561997005 | Braidwood 1, Braidwood 2 | 06/12/1997 | 07/09/1997 | 9707160075 | <strong>Inadequate P-11 ACOT/Channel Calibration Due to Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On 6-12-97, during a review of an industry operating Experience which identified a lack of proper testing of the P-11 interlock circuitry, it was determined that the same situation existed at Braidwood. Performing the customary verification of the associated Solid State Protection System input relays does not properly check the P-11 input relays. Because of this deficiency a valid test of the entire channel, for the P-11 function, as defined by technical specifications was not met. At 1530 on 6-12-97, the P-11 function for Braidwood Unit 2 was declared inoperable and required actions directed by the Limiting Conditions for Operations stated in Technical Specifications were taken. The declaration of an inoperable P-11 function for Braidwood Unit 1 was not made because it was verified that the input relays were functional after reviewing data from a recent startup which occurred since the last surveillance was performed on the associated channels. The cause for this event is due to improper development of the surveillance procedure to properly test the P-11 function as it leaves the process protection system instrumentation and inputs into the Solid State Protection System. This event had minimal safety significance because the P-11 interlock was found to be operating correctly in response to plant conditions. Planned corrective actions include revision of surveillance procedures to properly verify the P-11 function to the point of input into the Solid State Protection System. There have been three (3) previous events involving inadequate surveillances. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
4561997006 | Braidwood 1, Braidwood 2 | 05/22/1997 | 06/21/1997 | 9706270077 | <strong>Tech Spec entry in 3.0.3 and Unit 1 Cooldown due to ECCS Venting Issue</strong><br /><i>Abstract:&nbsp;</i>Pursuant to Technical Specification 4.5.2, ECCS Subsystems, venting to the Chemical and Volume Control System pump casings and discharge piping high points outside of containment is required to be performed every 31 days. However, the monthly surveillance procedure required to meet this criterion does not require the applicable high head injection system components to be vented. Unit 1 cooled down and depressurized to 511 degrees and 1650 psig due to this event. This deficiency was attributed to a management deficiency which credited system operation, e.g. dynamic venting, with meeting the requirement of T.S. 4.5.2. The procedure was approved without the requirement of venting the high head injection components primarily because the charging pumps are designed to be self venting (i.e. the pumps do not have vents on the pump casings). Corrective actions included weekly ultrasonic examinations of piping until the Technical Specification is changed, issuance of a Daily Order and a verbal briefing to Operators on gas accumulation in stagnant lines, an exigent Technical Specification change, and procedure revision to include the monthly ultrasonic examinations in a Monthly Venting Surveillance, once the Technical Specification is approved.
4561997007 | Braidwood 1, Braidwood 2 | 10/27/1997 | 11/21/1997 | 9712020113 | <strong>Excessive Operator Response Times due to Inadequate Analysis Implementation</strong><br /><i>Abstract:&nbsp;</i>During a Steam Generator Tube Rupture (SGTR) procedure review at Byron in February 1996, a condition was found where operators would possibly be sent to a procedure not in the time-validated sequence, which could result in steam generator overfill for a SGTR. This transition would result from a large drop in indicated coolant temperature that had not been addressed in the SGTR procedure. The plant specific analysis showed the indicated temperature drop was not properly incorporated in the procedure. If a steam generator overfill had occurred the resulting doses would be bounded by existing analyses. The SGTR procedure was revised to address the indicated temperature drop. Other plant-specific analyses will be reviewed for similar problems. A more formal interface between the procedure writers and the accident analysis group will be evaluated. There were no previous occurrences of a similar nature. This is reportable under 10CFR50.73(a)(2)(ii).
4561997008 | Braidwood 1 | 10/10/1997 | 11/07/1997 | 9711120203 | <strong>Projected Steam Generator Leakrate Combined with Technical Specification Limit for Dose Equivalent Iodine Creates Potential for Operation Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>The operability of the steam generators is determined through an augmented in-service inspection program and application of Technical Specification (TS) listed acceptance criteria. As part of the requirements for voltage based repair criteria for steam generator tubing with Outer Diameter Stress Corrosion Cracking (ODSCC), potential leakage during a Main Steam Line Break accident with containment bypass must be calculated. This calculated leak rate value is then compared to the site allowable accident leakage limit. The site allowable accident leakage limit results in a dose corresponding to 10% of 10 CFR Part 100 assuming maximum TS allowable Reactor Coolant System Dose Equivalent (DE) Iodine-131. The current licensing basis maximum site allowable leakage limit for Braidwood Unit 1 Cycle 7 is 26.8 gpm. This leakage limit value is given at operating conditions. Calculations indicate that the total Predicted Accident tube leakage at the end of Unit 1 Cycle 7 is 87.7 gpm which exceeds the current licensing basis value of 26.8 gpm. A TS amendment request was submitted September 2, 1997 to lower the DE Iodine-131 limit to allow an increase in the site allowable accident leakage limit. The projected accident leak rate exceeded 26.8 gpm on 10/10/97. Approval of the TS amendment request to lower the DE Iodine-131 limit was not received prior to the projected accident leak rate exceeding the limit. An operability assessment was performed to justify continued operation. This event is reportable per 10 CFR 50.73(a)(2)(ii).
4561997009 | Braidwood 1, Braidwood 2 | 10/28/1997 | 03/19/1998 | 9803270261 | <strong>Potential Failure of Westinghouse Fuel Rod Design Criteria discovered by Westinghouse while updating PAD code.</strong><br /><i>Abstract:&nbsp;</i>Westinghouse analysis shows that for high power, high burnup assembly Integral Fuel Burnable Absorber fuel rods, calculated rod internal pressure are in excess of the Westinghouse fuel rod design criterion that "the fuel rod pellet-to-clad gap shall not re-open." Additionally, if the "no gap reopening criterion is exceeded, the 17% clad oxidation limit following postulated Loss of Coolant Accident event, as defined in 10CFR50.46, can likewise be exceeded. Westinghouse has since determined that all currently operating plants are in compliance with 10CFR50.46. Cause of the issue was Westinghouse used inadequate methods and incorrect assumptions in fuel rod design code. Corrective actions: Westinghouse completed plant-specific analyses on March 6, 1998. These analyses indicate that gap re-opening occurs during Braidwood 1 Cycle 7 operation, but that the 10 CFR 50.46 cladding oxidation criterion continues to be met. The criterion will be met through the cycle's End of Life (EOL) burnup of 20,000 MWD/MTU. In addition, all analyses supporting the conclusions of the Cycle 7 Reload Safety Evaluation demonstrate that operation until EOL is valid. Braidwood System Engineering and Nuclear Fuel Services have reviewed the results of these analyses and concur with the conclusion. A search of the Nuclear Station Regulatory Assurance database found no previous occurrences.
4561997010 | Braidwood 1, Braidwood 2 | 11/14/1997 | 12/12/1997 | 9712160206 | <strong>SSPS LOGIC TESTING NOT PERFORMED DUE TO INADEQUATE TESTING DESIGN</strong><br /><i>Abstract:&nbsp;</i>On November 14 1997, Braidwood Unit 1 was at full power operation with all safety systems available. Braidwood Station Unit 2 was in refueling outage A2R06, Mode 3 with all safety systems available, and preparing for reactor startup. During a review of Generic Letter 96-01 (Testing of Safety Related Logic Circuits a discovery within the industry revealed current Solid State Protection System (SSPS) testing was inadequate. Braidwood and Byron Stations determined current SSPS testing did not test all functions of some memory logic circuits. As such, a missed surveillance condition was determined to exist. The cause for this event was that the original testing design prescribed by the vendor did not fully verify proper operation of the SSPS logic cards. Corrective action to resolve the inadequate testing is to add new testing criteria to the SSPS Bi-monthly surveillance procedures. Unit 1 Train A/B SSPS Bi-Monthly testing was successfully performed on 11/14/97. Unit 2 Train A/B SSPS Bi-Monthly testing was successfully performed on 11/19/97. There were no adverse consequences to the health and safety of the general public or plant personnel as a result of this event. There have been four (4) previous events involving inadequate surveillances. This event is reportable per 10CFR50.73(a)(2)(i)(B) - any operation or condition prohibited by the plant's Technical Specifications.
4571997001 | Braidwood 2 | 09/16/1997 | 10/16/1997 | 9710300078 | <strong>Two Extraction Steam Non-Return Check Valves Made Inoperable By Installed Scaffolding As A Result Of Knowledge Deficiencies, Improper Assumptions and Not Adhering To Procedures</strong><br /><i>Abstract:&nbsp;</i>At 18:13 on 9/16/97, Operating personnel identified that scaffolding had potentially blocked the weighted lever arm on Extraction Steam Non-Return Check Valve 2ES015C from full movement, and entered Limiting Condition for Operations Action Requirement (LCOAR) 3.4-1a. Following adjustment of the scaffold, Operating Surveillance 2BwOS 3.4.2.c-1, Turbine Overspeed Protection Systems Monthly Surveillance (partial for 2ES015C), was satisfactorily performed to demonstrate the operability of valve 2ES015C. At 19:36, LCOAR 3.4-1a was exited. At 11:30 on 9/17/97, a Stop Work Order was issued for scaffold erections. At 17:20, Operations identified that the operation of Extraction Steam Non-Return Check Valve 2ES017B also appeared to be restricted from free movement and entered LCOAR 3.4-1a. Maintenance was immediately notified and a pole was removed to ensure adequate clearance was available for valve movement. Operations remained in the LCOAR until surveillance 2BwOS 3.4.2.c-1 was performed on all extraction steam non-return check valves to ensure no other valves were prevented from free travel. At 2152, surveillance 2BwOS 3.4.2.c-1 was completed with no additional problems, and LCOAR 3.4-1a was exited. These events were determined to be the result of Knowledge Deficiencies, Improper Assumptions and Not Adhering To Procedures. Corrective Actions for these events included the inspection of all scaffolds erected but not yet inspected, tailgating of expectations to all personnel involved in scaffold erection, and clarifying the expectation for Operations personnel to inspect scaffold erection sites with a potential to affect operating equipment prior to commencing installation work. There were no safety consequences as a result of these events as no credit is taken for the operability of these valves in any Braidwood Safety Analysis. There have been no previous Licensee Event Reports where equipment was made inoperable by improper scaffold installations. This event is being reported pursuant to 10CFR 50.73(a)(2)(i), a condition prohibited by Technical Specifications.
4571997002 | Braidwood 2 | 09/27/1997 | 10/24/1997 | 9710300137 | <strong>Manually Opened Reactor Trip Breakers Due to Decoder And Encoder Control Card Failure</strong><br /><i>Abstract:&nbsp;</i>On 9/27/97, Unit 2 was in Mode 3 at 2235 pounds per square inch gauge and 557 degrees during a scheduled refuel outage. Digital Rod Position Indication Operability Surveillance, 2BwOS 10.5-1, was in progress with the reactor trip breakers closed. While control rod bank C was being withdrawn with demand group step counters at 48 steps, the Digital Rod Position Indication for control rod B-8 jumped up to 96 steps. Procedure 2BwOS 10.5-1 requires opening the reactor trip breakers if, at any time during control rod movement, the Digital Rod Position Indication versus demand indication disagrees by >/= 24 steps. Immediate actions taken included opening the reactor trip breakers. Limiting Condition For Operating Requirement 1.3.3-1a was entered and 4 hour Event Notification, Emergency Notification System (ENS) notification was made due to manually opening the reactor trip breakers. All Operator actions were appropriate. The subsequent investigation determined that a circuit board on the Digital Rod Position Indication Train B Decoder and Encoder Control had failed. Cause of the circuit board failure is unknown at the present time. No visual indication is evident. A failure analysis for the circuit board will be performed and tracked by our Nuclear Tracking System (NTS). Corrective actions include replacing the defective card and re-performing the surveillance prior to Unit start-up. No previous LERs concerning manually opening of reactor trip breakers due to the failure of the Decoder and Encoder Control Card have occurred. 1
4571997003 | Braidwood 2 | 10/17/1997 | 11/14/1997 | 9711200209 | <strong>Incorrect setpoints were entered into 2AR012J Radiation Monitor as a result of a combination of programmatic deficiencies in the controlling procedures and personnel failing to follow procedures.</strong><br /><i>Abstract:&nbsp;</i>On 10/17/97 at 23:29, operations identified a discrepancy between the setpoints of redundant Containment Area Radiation Monitors 2AR011J and 2AR012J. Operations immediately secured a containment release in progress and terminated the event. Technical Specification 3.3.3.1 requires the containment purge valves be maintained closed if both monitors are not operable. The event investigation determined that incorrect Alarm setpoints were inadvertently entered into monitor 2AR012J during the course of maintenance work. At the completion of this work, the monitor was erroneously declared operable and returned to service at 20:05 on 10/16/97. This event was determined to be caused by a combination of programmatic deficiencies in the controlling procedures and by personnel failing to follow procedures. Corrective actions to prevent recurrence include revising the process and procedures used to control radiation monitor setpoints to eliminate identified weaknesses, counseling, and training the responsible personnel and departments. The safety consequences as a result of this event were minimal because redundant monitor 2AR011J was operable. The actual exposure difference between the actual and the correct 2AR012J setpoints were </= 0.052 Rem/hour. Additionally, sufficient monitoring capability was available to allow manual isolation. This event is being reported pursuant to 10CFR 50.73(a)(2)(i)(B), a condition prohibited by Technical Specifications.
4571997004 | Braidwood 2 | 10/14/1997 | 11/12/1997 | 9711180045 | <strong>Containment Fuel Handling Incident Radiation Monitor 2AR11J Alarm Setpoints Were Set Incorrectly Due to Personnel Error Resulting in an Inadvertent Containment Vent Isolation</strong><br /><i>Abstract:&nbsp;</i>On 10/14/97, preparations were being made to reload fuel into Unit 2. Alarm setpoints for the Containment Fuel Handling Incident Radiation Monitors were being changed for loading fuel into the reactor vessel. A containment release was in progress. When the Nuclear Station Operator (licensed reactor operator) entered the change for the first radiation monitor he entered an incorrect (more conservative) value resulting in a High Alarm for the radiation monitor and a containment vent isolation. All required isolation valves closed and the release was automatically secured. The cause of the event was personnel error due to inattention to detail and a failure to self-check. Corrective actions included verifying proper response of equipment to the containment vent isolation signal, entering the correct setpoints, counseling the operator, tailgating the event with operating crews, and initiating a procedure for the evolution. There has been one previous event involving incorrect setpoints for these monitors. There were no safety consequences for this event. The monitor alarm setpoints were set more conservatively resulting in a containment vent isolation thereby preventing an unmonitored release. This event is being reported pursuant to 10CFR50.73(a)(2)(iv).
4571997005 | Braidwood 2 | 11/06/1997 | 06/25/1998 | 9806300169 | <strong>Violation of Technical Specifications Due to Safety Injection Relief Valves Lifting and Failing to Reseat Due to a System Design Deficiency..</strong><br /><i>Abstract:&nbsp;</i>On 11/6/97, during the performance of a check valve leakage surveillance, relief valve 2SI8851 lifted and failed to reseat with indications of bellows failure when a Safety Injection (SI) [BQ] pump was started. This valve had been replaced with a rebuilt valve during the refueling outage due to a failure in July 1996. Both trains of SI were declared inoperable and LCO 3.0.3 was entered. At 1815 an ENS phone call was made. The plant was cooled down to < 350 degrees, Mode 4 was entered, and at 2215 LCO 3.0.3 was exited. On 11/7/97, the 2SI8853A/B relief valves were operationally tested using the SI pumps and the 2SI8853B valve lifted and failed to reseat with indications of bellows failure. This valve had also been replaced during the refuel outage. Both valves were replaced with new valves and during subsequent testing the replacement valve for 2SI8851 also lifted and did not reseat until the pump was secured. The 2SI8851 valve was again replaced with a third new valve and operationally tested with no further failures. Bench testing of the failed relief valves indicated that the setpoints were below the correct 1750 psig setpoint. on 11/8/97, Unit 2 was returned to Mode 3. The cause for the relief valves lifting was due to a limited margin between the pump start pressure transient and the valve setpoints. Subsequent investigation determined that the setpoints for the valves that actuated were 70 to 165 psig below the specified 1750 psig setpoint. The bellows failures were determined to be due to excessive differential pressure. Corrective actions include revising procedures, evaluating setpoint tolerance, reviewing testing methodology, evaluating the valve application for the system, evaluating the system for backpressure problems, and sending the bellows off-site for evaluation. There was one previous LER involving failure of SI relief valves. Safety consequences for this event were minimal. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4581997001 | River Bend | 05/06/1997 | 06/05/1997 | 9706110058 | <strong>Manual Reactor Scram on Lowering Vessel Level due to Cut Cable</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1997, at 9:01 AM, with the plant in mode 1 (power operation) and the reactor at 99% power, contract insulators severed and shorted two wires inside a cable (*CBL*) while removing low density silicon elastomer (LDSE) from a floor penetration in the turbine building. This resulted in a trip of three electrical breakers de-energizing the 4.16kV safety-related bus "B", and the 4.16 kV and 13.8kV non-safety-related bus "B", resulting in a loss of two of three reactor feedwater pumps. The reactor operator initiated a manual scram at 9:02 AM on lowering water level in anticipation of an automatic scram at reactor vessel level 3. The loss of electrical busses also resulted in the loss of reactor protection system "B" and subsequent containment isolations. In addition, the inboard main steam isolation valves (MSIV) isolated on high temperatures in the turbine building and main steam tunnel. The primary causes of the cut cable event were determined to be: site standards, procedures, and formal guidance for breaching penetrations was less than adequate, and tools and techniques used for the work need improvement. The cause of the MSIV isolation was determined to be human engineering. Corrective actions include repairing the cut cable, developing expectations for breaching penetration seals, and evaluating measures to reduce vulnerability to isolations caused by ambient area temperatures. The reactor safely shut down and the main turbine trip occurred in accordance with plant design. Engineered safety feature (ESF) systems performed their safety function per design. These events are reportable pursuant 10CFR50.73 (a)(2)(iv) as a manual reactor protection system actuation and automatic ESF actuations.
4581997002 | River Bend | 05/06/1997 | 10/27/1997 | 9711030229 | <strong>Through-Wall Linear Indication in a Weld on a Reactor Recirculation System Vent Valve</strong><br /><i>Abstract:&nbsp;</i>On May 06, 1997, with the plant in Mode 3 (Hot Shutdown) and the reactor at 0% power, during the drywell walkdown subsequent to a manual scram initiated for unrelated reasons, a small leak was noted spraying from the weld at the inlet of the vent valve for Reactor Recirculation System Flow Control Valve B. This valve and weld are part of the Reactor Coolant Pressure Boundary (RCPB). This portion of the Reactor Recirculation system can be isolated using maintenance valves which are installed on each side of the flow control valve. A through-wall crack was found approximately 180 degrees around the pipe through the weld (i.e., not between the weld and the base metal). The underlying causal factor is low stress, high cycle fatigue induced by vibration. The valve was replaced prior to returning to power operations. Appropriate modifications were made to the socket weld configuration to markedly reduce the susceptibility of these two vent valves to this type of failure. The subject vent line is 3/4 inch pipe, which vents a 1/4 inch vent port. Had the line completely sheared, the leakage would have been within the normal make-up capacity of plant systems. Therefore, this specific condition was of low safety significance.
4581997003 | River Bend | 07/22/1997 | 08/21/1997 | 9708260448 | <strong>Relay Failure Resulting in a High Pressure Core Spray Pump Breaker Trip During Testing</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1997 at approximately 8:30 PM, with the plant in mode 1 (power operation) and the reactor at 100% power, the high pressure core spray (HPCS)(*BG*) pump output breaker tripped open during an attempted pump start for testing. The cause of the breaker trip was determined to be the failure of the "A" phase time overcurrent relay. The defect appears to be internal to the wound coil. This could have been caused by a thin insulation coating or a manufacturing defect. The "B" and "C" phase time overcurrent relays were tested and found acceptable. Corrective actions include replacing the failed relay and evaluating the HPCS relay testing procedure. The failure of the HPCS system is bounded by the safety analysis. Therefore, this event is of minimal safety significance. This report is submitted pursuant to 10CFR50.73(a)(2)(v)(D) as a condition alone that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
4581997004 | River Bend | 07/24/1997 | 08/25/1997 | 9709030332 | <strong>Inadequate Surveillance of the Division III Battery Due to Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1997, with the plant in Mode 1 (Power Operation) and the reactor at 100 % power, a design engineering review identified a failure to conduct an adequate surveillance on the Division III battery. A revised calculation of the Division III battery profile shows the allowable values in the Technical Specifications to be non-conservative. Since these values were yet to be determined, previous performances of this surveillance did not verify the values from the revised calculation. Therefore, failure to meet the correct surveillance acceptance criteria during past operation constitutes a condition prohibited by the plant's Technical Specifications which is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The primary cause of the inadequate surveillance testing was non- conservative design analysis methods by a vendor. The revised Division III battery service discharge test procedure has been performed using the correct battery profile and acceptance criteria as defined in the revised calculation. The battery service test performed on July 28, 1997 demonstrated that the battery was capable of providing its safety related function. Therefore, failure to test the battery to the correct load profile had no actual safety significance for the current Division III battery which has been installed since 1994. Prior to 1994, the historical surveillance test results are being reviewed to determine the past performance capabilities of the Division III battery.
4581997005 | River Bend | 08/22/1997 | 09/22/1997 | 9709290049 | <strong>Reactor Scram Due To Failure Of A Connector To The Electrical Trip Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On August 22, 1997, at 00:27, with the plant in mode 1 (power operation) and the reactor power at 92.9% power, a turbine stop and control valve closure occurred resulting in an automatic reactor scram. The turbine trip and monitor panel indicated the stop and control valve closure was due to low emergency trip system fluid pressure. The valve closure was due to a Turbine Emergency Trip System signal caused by a short circuit in a connector for the Main Turbine Electrical Trip Solenoid Valve. The short was due to the formation of a conductive bridge, containing elements of solder flux and solder spatter, between the connector conductors. The connector had been installed as part of a plant modification in June, 1994. The condition was discovered during troubleshooting performed subsequent to the August 22, 1997, scram. Immediate corrective action was to replace the connector prior to start-up. Additional corrective actions will be implemented to ensure maintenance personnel are knowledgeable and adequately trained on soldering skills, and to evaluate the installation of the new connector. An evaluation determined that operator actions during the scram were appropriate and that safety systems functioned as designed
4581997006 | River Bend | 09/13/1997 | 10/14/1997 | 9710210092 | <strong>Unplanned Mode Change During Initial Test of New Alternate Decay Heat Removal Function Due To Inadequate Average Coolant Temperature Monitoring</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1997, approximately thirty-six hours after a planned reactor shutdown for a scheduled refueling outage at River Bend Station (RBS), an unplanned mode change occurred. The change from Mode 4 (Cold Shutdown - average coolant temperature less than or equal to 200 degrees F) to Mode 3 (Hot Shutdown average coolant temperature greater than 200 degrees F) occurred during the post modification testing of the alternate decay heat removal function of the existing Suppression Pool Cooling and Cleanup System. Engineering evaluations concluded that average reactor coolant temperature reached a maximum of approximately 205 degrees F. The most direct contributors to this event were: (1) the failure to reference and use the "time-to-boil" curves, and (2) the failure to recognize that RWCU temperature was not representative o average reactor coolant temperature under the existing plant conditions. Operators immediately increased cooling flow to return the plant to Mode 4. Existing procedural guidance regarding use of temperature monitoring instruments will be enhanced. Throughout the event, several means of reactor pressure and level control were available. Both divisions of the Residual Heat Removal System were available to assist in decay heat removal. There was no risk to the health and safety of the public. Since the mode change was unplanned, it resulted in a failure to meet Technical Specification 3.0.4 requirements in that several Mode 3 Limiting Conditions for Operations (LCOs) requiring shutdown were not met. This event is being reported under 10CFR50.73 (a)(2)(i)(B) as an "operation or condition prohibited by the plant's Technical Specifications".
4581997007 | River Bend | 09/26/1997 | 10/23/1997 | 9711040085 | <strong>Cracked Emergency Diesel Generator Valve Adjusting Screw Assembly Swivel Pads</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1997, at 1715 hours, with the plant in mode 5 (refueling) and the reactor at 0% power, the Division I (Div I) and Division II (Div II) emergency diesel generators (EDGs) were declared inoperable. Multiple valve adjusting screw assembly swivel pads (VASASPs) in the Div I EDG were found to be cracked, and was attributed to a manufacturing defect. Although the EDG would have been able to start and run following a loss of offsite power, an engineering evaluation conservatively postulated that in the event of a gross failure of the VASASP, the EDG may not have be able to run for the 30 days assumed in the accident analysis. Since the VASASPs in both the Div I and the Div II EDGs were manufactured from the same material lot, the condition was suspected to exist in both EDGs. Subsequent inspection of the Div II EDG on September 28, 1997, confirmed that four VASASPs were cracked. Based on the results of this inspection, the condition was reported at 1000 hours pursuant to 10 CFR 50.72(b)(2)(iii) as a condition which alone could have prevented the fulfillment of a safety function. This report is submitted pursuant to 10 CFR 50.73(a)(2)(v). Because the same manufacturing defect caused the VASASP cracks in both EDGs, this event is also reportable pursuant to 10 CFR 50.73(a)(2)(vii). Core alterations were suspended while both EDGs were inoperable, and the VASASPs in the Div I and Div II EDGs were replaced with improved components. VASASPs removed from the two EDGs will be returned to the vendor for analysis. A review of the vendor's failure analysis report will be performed to determine the need for additional corrective actions. Because the EDGs did not experience a gross failure of the VASASPs, the safety significance of this event is considered low.
4581997008 | River Bend | 10/04/1997 | 11/03/1997 | 9711130107 | <strong>Inadvertent Closure of Residual Heat Removal Shutdown Cooling Inboard Isolation Valve due to Less Than Adequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1997 at 2114 hours, with the reactor in Mode 5 (refuel) for a scheduled refueling outage with residual heat removal "A" in shutdown cooling, an operator closed a supply breaker for the residual heat removal shutdown cooling inboard isolation valve, causing to it to stroke closed. The close signal for the valve existed because the leak detection isolation logic power for that valve had been previously de-energized. The valve isolation resulted in a 17 minute loss of Shutdown Cooling, during which time the vessel increased in temperature from 97.0 degrees F to 100.4 degrees F. The valve was manually re-opened and shutdown cooling was restored. A root cause analysis was conducted. Administrative controls, supervision, and work practices were determined to be less than adequate. Other corrective actions include revising necessary procedures and conducting training. The time after shutdown and reduced decay heat in the core mitigates the potential consequences of this event. Additionally, the alternate decay heat removal system was available as a backup means of decay heat removal. This event had minimal safety significance and did not impact the health add safety of the public. This event is being reported per 10CFR50.73 (a)(2)(iv) as an automatic actuation of an Engineered Safety Feature.
4581997009 | River Bend | 10/16/1997 | 11/17/1997 | 9712020082 | <strong>INADEQUATE PRESSURE TEST PERFORMANCES DUE TO PRESSURIZING THROUGH CHECK VALVES</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1997, while completing a refueling outage (RF-7), with the plant in mode 4 (cold shutdown) and the reactor at 0% power, investigation results identified potentially inadequate prior local leak rate testing (LLRT) for three valves. The inadequate prior test performances were caused by pressurizing with at least one check valve between the pressure source and the valves being tested. Differential pressure across the check valves may have reduced test pressures to less than the minimum required test pressure. The cause of the inappropriate testing lineups was determined to be insufficient technical knowledge regarding the effects of pressurizing an LLRT test boundary through a check valve. After recognition by the test engineers during RF-7, LLRT personnel, including contractors, were briefed on the potential effects of check valves on LLRTs. Applicable procedures will be revised to remove the check valves from the test configurations. A caution will be placed in the controlling procedure regarding the effects of check valves on leak tests. Immediate corrective actions included leak rate testing utilizing revised pressure pathways which do not include check valves. All three valves passed the revised testing method. Also, each penetration contains at least one additional containment isolation valve in series that was tested satisfactorily. No safety significance is associated with this event. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(B) as an operation prohibited by the plant's Technical Specifications.
4581997010 | River Bend | 11/11/1997 | 02/26/1998 | 9803040205 | <strong>High Pressure Core Spray Minimum Flow Valve Discovered In Closed Position Due To Air In Transmitter Sensing Lines</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1997, at 1713 hours during testing of the High Pressure Core Spray System (HPCS) (*BG*) the minimum flow valve was discovered to be closed while the pump was running. No other discharge path for the pump was open at the time. Upon discovery of the closed valve condition, the operator took immediate action to open the minimum flow valve, and the test was completed. The HPCS minimum flow valve and the HPCS system were declared inoperable. The root cause for the initial minimum flow valve failure was determined to be air in the flow transmitter sensing line high point due to a failure to properly vent those lines. The sensing line from the HPCS pipe to the flow transmitter was vented at the high point vent. The HPCS pump was tested and no abnormalities noted. Low pressure emergency core cooling systems and the reactor core isolation cooling system were verified to be operable and capable of performing their safety function at the time of the event. Corrective action includes developing procedural guidance to specify the appropriate venting requirements for instrument line high point vents. This event has minimal safety significance. It was subsequently determined that this condition would not have prevented the fulfillment of a safety function of a system needed to mitigate the consequence of an accident and is not reportable. This report is being revised to reflect a voluntary submittal and contains no commitments.
4611997001 | Clinton 1 | 01/03/1997 | 01/28/1997 | 9702030199 | <strong>Failure of Nuclear Fuel Supplier to Analyze Turbine Pressure Regulator Downscale Failure Event in the Off- Rated Condition Results in Operation in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. Because of a nuclear fuel supplier error, the Turbine Pressure Regulator Downscale Failure (PRDF) event for 40 to 80 percent of rated thermal power had not been quantitatively analyzed during past operation. The fuel supplier issued a revision to the power-dependent operating limit for the cycle 7 Minimum Critical Power Ratio (MCPR) to correct the previous limit which was not adequate for conditions between 40 and 80 percent of rated thermal power for the PRDF event. Utility engineers reviewing the documentation identified that there was some potential to exceed the Safety Limit MCPR if the PRDF event had occurred during any of the past 5 fuel cycles. The engineers identified that the plant had operated in an unanalyzed condition during fuel cycle 6 and may have operated in unanalyzed conditions during fuel cycles 2, 3, 4, and 5. The cause of this event is attributed to an error by the nuclear fuel supplier in determining which events were the limiting anticipated operational occurrences that required analysis for the fuel design. Corrective action includes implementing corrected power-dependent operating limits for the MCPR. This event is also reportable under 10CFR, Part 21.
4611997002 | Clinton 1 | 01/21/1997 | 08/28/1997 | 9709050004 | <strong>Failure to Complete Technical Specification 3.8.2 LCO Required Action B.4</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1997, the plant was in Mode 5 (REFUELING) and the Division II Emergency Diesel Generator (EDG) was available but inoperable. The Operations staff performed Clinton Power Station (CPS) procedure 9080.01, "Diesel Generator 1A(B) Operability-Manual and Quick Start Operability," on the Division I EDG which caused the EDG to be inoperable as a result of performing the prestart checks on the EDG. Technical Specification 3.8.2 Limiting Condition for Operation (LCO) Required Action BA requires that with the Division I and II EDGs inoperable, one EDG be restored to an operable status immediately when both Division I and II are inoperable. Not immediately restoring one EDG to an operable status during performance of CPS procedure 9080.01 was contrary to the Technical Specifications. The cause of this event was an error by the operations Shift Supervisor when the determination was made that making the EDG inoperable during the performance of CPS procedure 9080.01 was allowed by the Technical Specifications. The corrective action for this event includes training appropriate Operations Department personnel on this event and revising CPS procedure 9080.01 to not require barring over the EDG under these circumstances.
4611997003 | Clinton 1 | 01/28/1997 | 07/01/1997 | 9707090063 | <strong>Failure to Recognize the Impact of Disconnecting Division 1 Intermediate Range Monitor (IRM) Cable While Division 2 IRM Cable was Disconnected results in 2-out-of-4 Reactor Protection System Actuation Logic Being Satisfied</strong><br /><i>Abstract:&nbsp;</i>The plant was in REFUELING during the sixth refueling outage, the reactor mode switch was locked in the shut down Position, and all reactor control rods were fully inserted. A safety tagout was in place for reworking a cable connector assembly on the Neutron Monitoring system Division 2 intermediate range monitor (IRM) channel F. The channel F cable was disconnected from its detector causing an IRM trip signal to the reactor protection system (RPS) as expected. Additional safety tags were hung for the Division 1 IRM channel E to allow the channel E cable to be used in trouble shooting the channel F monitor. Disconnecting the channel E cable caused a second IRM trip signal to the RPS and satisfied the 2-out-of-4 RPS actuation logic. The off-normal procedure for reactor scram was entered and applicable portions completed. No control rods moved as a result of the RPS actuation. The cause of this event is attributed to personnel error. The impact of the safety tagout for IRM channel E was not recognized by the operations crew prior to hanging the tagout. Corrective action for this event included counseling the personnel involved in this event about adequate turnovers, questioning the impact of tagouts and recording the impacts on the tagout documentation.
4611997004 | Clinton 1 | 02/04/1997 | 03/06/1997 | 9703110084 | <strong>Inadequate Procedure Leads to Failure to Properly Implement Technical Specification Surveillance Requirement 3.6.5.3.3</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 4, 1997, the plant was in Mode 5 (REFUELING) when an engineer discovered that the drywell isolation valves 1E12-F073A and 1E12-F073B had not been verified Closed as required by the Technical Specifications. Engineers later determined that on at least one occasion the drywell bypass leak rate test did not adequately challenge 1E12-F073A and 1E12-F073B. The cause for these conditions could not be definitively determined. It is believed that the reason the valves were not properly verified closed may have been because the procedure preparer thought the valves were automatic valves and therefore, were not required to be verified Closed by the Technical Specifications. It is believed that the failure to properly perform the drywell bypass test was the failure of the test procedure preparer and reviewers to recognize that the discharge piping downstream of these valves may be submerged by water in the drywell weir well during the test. Corrective actions for this event include: revising the surveillance procedure to verify that the valves are closed and to either ensure the discharge piping is not submerged or account for the calculated potential leakage through these valves.
4611997005 | Clinton 1 | 09/29/1986 | 08/28/1997 | 9709050080 | <strong>Eighteen Containment Penetrations Susceptible to Thermally Induced Over-Pressurization Due to Unknown Cause Are Considered Outside Design Basis of Plant</strong><br /><i>Abstract:&nbsp;</i>The plant was in REFUELING during the sixth refueling outage. Engineers reviewing containment penetrations for impact of NRC Generic Letter 96-06 determined that 18 containment penetrations were susceptible to thermally induced over-pressurization during a.design basis Loss of Coolant Accident (LOCA). The 18 penetrations constitute a condition that is outside the design basis of the plant. A specific cause for this event could not be substantiated; however, the most likely cause appears to be an undocumented assumption that over-pressurization was not a concern at the expected temperatures. A contributing factor to the cause was a lack of guidance in the design specification for thermal expansion of fluid. Corrective actions include draining penetrations not required post-LOCA or during normal plant operation, modifying some penetrations, and revising the design specification.
4611997006 | Clinton 1 | 02/19/1997 | 08/06/1997 | 9708200087 | <strong>Lack of Coordination of 120 Volt Non-Safe Shutdown Circuit Breakers in Distribution Panels with Safe Shutdown Circuit Breakers Causes Plant to be Outside its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1997, the plant was in Mode 4 (Cold Shutdown) and reactor coolant temperature was being maintained between 95 and 105 degrees Fahrenheit, reactor pressure was atmospheric. An engineer discovered that there was a circuit breaker coordination problem between 120 volt circuit breakers and safety related 480 volt circuit breakers that supply 120 volt distribution panels. This is contrary to the design basis of the plant which requires that the 120 volt circuit breakers be coordinated with the 480 volt supply circuit breaker to the 120 volt distribution panel on electrical distribution systems that contain safe shutdown and non-safe shutdown equipment. Three occurrences of this condition were discovered. The cause of this event has been attributed to an error by the architect engineer for Clinton Power Station. Corrective actions for this event include modifying the three affected circuits and reviewing the electrical distribution scheme to ensure proper circuit breaker coordination.
4611997007 | Clinton 1 | 02/27/1997 | 03/27/1997 | 9704040204 | <strong>Lack of Procedural Guidelines for Maintaining Seismic Qualification Results in Division 3 Switchgear Outside Design Basis When GE 4160-Volt Magne Blast Breakers in Racked-Down (Disconnected) Position</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. With the plant in COLD SHUTDOWN, a System engineer recognized that a Probabilistic Risk Analysis (PRA) performed for General Electric Magne Blast breakers in Division 3 High Pressure Core Spray System switchgear in the racked-down (disconnected) Position was not valid for evaluating the seismic qualification and operability of the switchgear. Further, procedures were not adequate to prevent the breakers from being left in the breaker cubicle in the racked-down Position while performing on-line maintenance activities for an extended period of time. Leaving the breakers in the racked-down position in the cubicle for extended periods of time was a normal practice. The cause of this event is attributed to lack of procedural guidelines to maintain seismic qualification of the Division 3 breakers and switchgear. Corrective actions include verifying breakers were in the racked-in (connected) position, issuing an Operations Night Order requiring that racked-down breakers must be removed from the cubicle, performing a revised PRA, reviewing and revising as needed the seismic analysis, and revising procedures to address the acceptability of breaker configurations.
4611997008 | Clinton 1 | 04/08/1992 | 04/22/1997 | 9704280270 | <strong>Diesel Generator Undervoltage Relays Inoperable</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. In 1992, Illinois Power electrical design engineers raised a concern that the setpoints for second-level undervoltage relays in the Auxiliary Power system may not be correctly set to provide adequate voltage for proper equipment operation. In 1994, an extensive study of the AP system response under Loss of Coolant Accident (LOCA) conditions identified the minimum voltage required at all levels from the 4160-volt to the 120-volt levels and concluded that the second-level undervoltage relay minimum reset point of 3799 volts would not ensure sufficient voltages for all equipment fed from the 120-volt motor control center distribution panels following a postulated LOCA scenario. This condition was identified on Licensee Event Report (LER) 94-005. However, it was not recognized at that time that the relays must be considered inoperable. Corrective actions for LER 94-005 included a Main Control Room alarm, revising the annunciator procedure for operator guidance, training of operators to respond to an undervoltage condition, and modifications of the plant design to replace the existing plant equipment with more accurate undervoltage relays and regulating transformers. in March of 1997, the Improved Technical Specification requirements for power sources and instrumentation were reviewed to submit an amendment to the Facility Operating License No NPF-62. Based on that review, the operability requirements of the undervoltage relays were not being met, so the relays and the associated Emergency Diesel Generators were declared inoperable.
4611997009 | Clinton 1 | 03/26/1997 | 10/01/1997 | 9710060343 | <strong>Surveillance Procedure Does Not Adequately Consider Accuracy Of Installed Instrumentation in Meeting Technical Specification Requirements for Reactor Core Isolation Cooling Pump</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN and the sixth refueling outage in progress, a generic concern was identified that values in surveillance procedures used to assure that Clinton Power Station meets Technical Specifications (TS) may not have adequate consideration for the tolerances of the installed instrumentation. A plan was developed to review all TS Surveillance Requirements (SR) to assure indications observed by the operators will accurately reflect that the parameter is within the TS limits. During implementation of the plan, engineers were unable to confirm that some of the previous surveillance test data met the acceptance criteria of TS SR 3.5.3.3 for the Reactor Core Isolation Cooling (RCIC) system pump when potential instrumentation inaccuracies were applied. The failure to meet TS SR 3.5.3.3 constitutes a failure to meet the Limiting Condition for operation of TS 3.5.3, RCIC System. The cause of this event was a lack of rigor of documenting the original evaluations which created the TS limits. The corrective actions for this event include evaluation of approximately 146 TS SR parameters, preparation of formal calculations to document whether the margin for instrument accuracy has or has not been added and preparation of a TS bases change to reflect each parameter evaluated.
4611997010 | Clinton 1 | 04/08/1992 | 08/28/1997 | 9709050023 | <strong>Incorrect Voltage in Procedure for Verification of Off- Site Power Sources</strong><br /><i>Abstract:&nbsp;</i>Due to a concern raised throughout the nuclear industry about degraded voltage protection, Illinois Power (IP) engineers began a study of the effects of degraded voltage on safety-related equipment. This study involved, in part, a review of the calculations used to set the minimum bus voltage required to ensure proper operation of safety-related (Class 1E) 120-VAC equipment. In review of these calculations plant engineers determined a new minimum voltage value of 4030-VAC required to be present at the off-site power sources vice the previous value of 3744-VAC. Review of past voltage data during the first week of April, 1997, showed that fluctuations in bus voltages had resulted in voltage less than the new minimum value of 4030-VAC and that one of the offsite power sources should have been declared inoperable. It was determined that the required action as stated in the Technical Specifications (TS) section 3.8.2, "Initiate action to restore required off-site power circuit to OPERABLE status immediately," was not met. This event was personnel error in the failure to adequately review operability requirements of plant equipment. Corrective action will include a revision to the appropriate surveillance procedures that determine equipment operability.
4611997011 | Clinton 1 | 09/29/1986 | 05/08/1997 | 9705190035 | <strong>Failure to Verify Breaker Closed at 7-Day Frequency as Required by Technical Specifications Due to Omission of Breaker From Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. With the plant in COLD SHUTDOWN and the sixth refueling outage in progress, a review of procedures to verify procedure fidelity with the Updated Safety Analysis Report (USAR) and Technical Specifications (TS) identified that a circuit breaker was not included in surveillance procedures that verify correct breaker alignments and voltage to required electrical distribution subsystems as required by TS Surveillance Requirements. The breaker connects the Division 3 battery bus to the Division 3 125-volt direct current distribution bus and has not been verified to be in the closed position at a 7-day frequency since initial plant operation. The breaker was immediately verified to be closed. The cause of this event is attributed to inadequate procedures. procedures to include the omitted breaker. Additionally, the procedure to USAR and TS fidelity review is continuing in accordance with the Startup Readiness Action Plan. This event was not nuclear safety significant; if the breaker was open, plant annunciators would alarm to reveal it.
4611997012 | Clinton 1 | 09/29/1986 | 10/27/1997 | 9711050175 | <strong>Failure to Correct for Instrument Error During the Performance of Standby Gas Treatment System Surveillance Procedure Leads to Invalid Surveillance Results</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1997, the plant was in Mode 4 (Cold Shutdown), and engineers were reviewing correction curves in surveillance procedure CPS No. 9065.02 "Secondary Containment Integrity". These correction curves were used to correct measured air flow of the standby gas control system (VG) for the barometric pressure and temperature conditions observed at the time the surveillance procedure was performed. The engineers were unaware that the correction curves also accounted for flow measurement instrument error. Review of other VG surveillance procedures that measure air flow in the system disclosed that those surveillance procedures did not account for instrument error. Testing was conducted, and it was determined there was instrument error in the currently installed flow measurement instrumentation and that this instrument error was not accounted for in some surveillance procedures resulting in Technical Specification Surveillance Requirements 3.6.4.3.1 and 3.6.4.3.2 not being fully satisfied. This event resulted from lack of system ownership and procedural guidance for resolution of system problems prior to original issue of the procedure for the System Engineering Program. Corrective actions for this event included recalibrating the flow instrumentation and reperforming the applicable surveillance procedures.
4611997013 | Clinton 1 | 05/08/1997 | 06/04/1997 | 9706110095 | <strong>Failure to Adequately Verify No Trips Exist During Surveillance Test Results in Inadvertent Actuation of Standby Gas Treatment System</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1997, Control and Instrumentation (C&I) technicians were performing a routine surveillance per Clinton Power Station (CPS) procedure CPS 9532.61, "CRVICS Fuel Building Exhaust Radiation Monitor 1RIX-PR006A Channel Functional Test," when a "High Radiation Initiation Standby Gas Treatment System (SGTS) Division I & II" alarm actuated. An inadvertent isolation of the Fuel Building ventilation (VF) and an initiation of both trains of the SGTS (VG) occurred. Upon investigation, it was discovered that the local "trip" switch of Fuel Building Exhaust Division 2 radiation monitor 1RIX-PR006D was in the trip position. The trip logic was then completed when the technicians inserted a high signal into Division 1 radiation monitor 1RIX-PR006A as part of the surveillance test. The root cause of this event is personnel error. The technicians failed to properly perform a step in the surveillance procedure that verifies all four channels to be in a non-trip condition. A contributing factor was the failure to adequately restore the trip switch on monitor 1RIX-PR006D after the removal of a safety tagout on April 1, 1997. Corrective actions include revising procedure CPS 9532.61 to include an electrical lineup for the trip switches located in each monitor.
4611997014 | Clinton 1 | 04/26/1988 | 06/18/1997 | 9706250245 | <strong>Main Steam Isolation Valves Closure Time Out of technical Specifications Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN and the sixth refueling outage in progress a review of instrument accuracy for compliance with the Technical Specifications (TS) was being performed. During the review it was determined that Clinton Power Station procedure 9061.09, which satisfies TS Surveillance Requirement (SR) 3.6.1.3.6 governing Main Steam Isolation Valve (MSIV) closure time testing, was not adequate because it did not account for full valve travel. Faulty data from CPS 9061.09 was also used in procedure 9432.30 to satisfy TS SR 3.3.6.1.7 for MSIV system response time testing. Consequently, there have been several instances since April 26, 1988, where the MSIV valve and system closure times have not been within TS SR 3.6.1.3.6 and TS SR 3.3.6.1.7. The cause of this event was determined to be procedural inaccuracy. Corrective actions include revising CPS 9061.09 to account for full valve travel, verifying MSIV operability before plant start up, and training plant operators on the MSIV limit switch configuration and position indication.
4611997015 | Clinton 1 | 12/31/1996 | 07/09/1997 | 9707150011 | <strong>Inappropriate Use of a Solder Flux Due to Inadequate Control of a Consumable Material and Poor Workmanship During Rework of Main Control Room Neon Indicator Lights Sockets Results in Inoperable Safety Systems</strong><br /><i>Abstract:&nbsp;</i>An operability determination performed due to repetitive failures of main control room neon indicator light sockets in main control room panels identified that equipment associated with the light socket circuits was inoperable. The determination was based on the potential that light socket circuits could short to ground due to use of an incorrect solder flux during rework of the light sockets. The short to ground would cause control power fuses on affected components to open or trip coils to activate. This condition was determined to be applicable to various safety-related systems including the Residual Heat Removal system, Emergency core Cooling Systems, Emergency Diesel Generators, Main Steam Isolation and Control Rod Drive system. The causes of this event were a breakdown in the control of a consumable material (solder flux) and poor workmanship. Corrective actions for this event include replacing affected light sockets, clarifying the use of solder flux in the control of chemicals program, evaluating personnel qualifications, training personnel, revising required post maintenance testing, reviewing other uses of solder flux, designating the use of fluxes in the material tracking system, adding management oversight to rework of light sockets, revising procedures, and performing an assessment of the use of consumables.
4611997016 | Clinton 1 | 06/17/1997 | 06/30/1997 | 9707240165 | <strong>Failure to Provide Emergency Lighting for Safe Shutdown Equipment as Required by the Plant Design Basis</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1997, the plant was in mode 4 (Cold Shutdown), and the sixth refueling outage was in progress. A Quality Assurance Technical Specialist identified that the required fixed sealed beam lighting units with eight hour minimum battery supplies were not provided for one location where manual action is required to safely shutdown the plant by the Safe Shutdown Analysis (SSA). The requirement for eight hour emergency lights, which constitutes the design basis for emergency lighting, is specified in Branch Technical Position-APCSB 9.5-1 and 10CFR50 Appendix R section III J. The manual action that was required to be performed was to open valve 1E12-F024B locally because a hot short of the cables associated with valve 1E12-F006B could cause that valve to open which would actuate an interlock that prevents valve 1E12-F024B from opening. The cause of this event could not be determined. Corrective actions for this event include: preparing a modification and administrative controls to de-energize valve 1E12-F006B during modes when it is not necessary, this prohibits 1E12-F024B from being affected by a hot short and the subsequent requirement for emergency lights, and a review of other manual actions in the SSA to determine if there were other occurrences where adequate lighting were not provided as required by the plant design basis.
4611997017 | Clinton 1 | 06/13/1997 | 08/07/1997 | 9708200076 | <strong>Failure to Properly Calibrate Main Steam Line Radiation Monitoring</strong><br /><i>Abstract:&nbsp;</i>On June 13, 1997, the plant was in Mode 4 (Cold Shutdown), and the sixth refueling outage was in progress. A review of the calibration procedure for the main steam line radiation monitors revealed that the trip set point was not in accordance with the Operational Requirements Manual (ORM). These monitors are required to have a trip setpoint of less than or equal to 3.0 times full power background radiation levels. The monitors were initially calibrated, prior to initial plant startup, using 1.0 Rem per hour as the full power background radiation level. This value was included in a design document to allow calibration of the instruments prior to initial plant startup and achieving full power operation. The setpoints for these monitors were not changed to reflect actual plant full power background radiation levels. The cause of this event is that the design document that provided the setpoints to be used prior to plant startup did not address the need to recalibrate the monitors once full power was achieved. Corrective actions for this event include: determining actual full power background radiation levels, calibrating the main steam line radiation monitors with the new value, revising the calibration procedure to use the values determined from actual plant data.
4611997018 | Clinton 1 | 08/23/1997 | 09/19/1997 | 9709260278 | <strong>Inadequate Preventive Maintenance Leads to Possible Failure of Westinghouse DHP Circuit Breakers to Open on Demand</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1997, the plant was in Mode 4 (Cold Shutdown). Plant personnel were reviewing the results of the maintenance performed on three Westinghouse model DHP safety-related circuit breakers. During the review station personnel determined that the condition of the three circuit breakers was similar to the condition of two Westinghouse model DHP safety-related circuit breakers that failed to open an demand on July 22, and August 5, 1997. Because the condition of three of the circuit breakers was similar to that of the Westinghouse model DHP safety-related circuit breakers that had previously failed station personnel determined that the condition of the circuit breakers presented a condition that could have prevented the circuit breakers from fulfilling their safety function to shutdown the reactor and maintain it in a safe shutdown condition. The cause of the event was determined to be inadequate preventive maintenance (PM) performed on Westinghouse DHP circuit breakers. Corrective actions for this event include: performing preventive maintenance tasks on the circuit breakers to ensure circuit breaker operability, revise preventive maintenance procedures to provide better instructions for required maintenance, increase the frequency of the PM task on the circuit breakers from six to three years, and develop new PM task to periodically refurbish the circuit breakers.
4611997019 | Clinton 1 | 09/29/1986 | 08/07/1997 | 9708200081 | <strong>Switchgear Heat Removal System Fan Discharge Damper Control Circuit Routed Through Main Control Room (MCR) Is Not Per Design Basis Due to Design Error and Could Fail During a MCR Fire, Adversely Affecting Method 1 of Safe Shutdown Analysis</strong><br /><i>Abstract:&nbsp;</i>With the plant shut down for refueling, engineers identified that a fire in the Main Control Room (MCR) could prevent proper operation of the Division 1 Essential Switchgear Heat Removal System (VX) from the Remote Shutdown Panel (RSP). Remote Method 1 of the Safe Shutdown Analysis (SSA) relies on the RSP to be available during a fire in the MCR to provide alternate shutdown capability. The control circuit wiring for the VX supply air fan discharge damper is routed through the MCR to provide damper position indication. During a fire in the MCR the control circuit wiring could short circuit, blowing the control circuit fuse, and preventing the damper from proper automatic operation to provide a discharge flow path when the supply air fan is operated from the Remote Shutdown Panel. The SSA relies on the availability of VX to perform its function. A fire in the MCR could cause an evacuation of operators to the RSP, however, there is no capability to transfer control of damper 1VX03YA to the RSP. The circuit design is not in accordance with 10CFR50 Appendix R, Section III.G and the plant's design basis. The cause of this event is indeterminate, but most likely an oversight in original design. Corrective actions for this event include installing a temporary modification to disconnect the damper indication to the MCR, redesigning the control circuitry and reviewing other systems.
4611997020 | Clinton 1 | 07/15/1997 | 08/13/1997 | 9708190130 | <strong>Failure to Document Effect of Degraded Coatings in Containment on ECCS Pump NPSH and Properly Control Flexible Materials Leads to Potential Failure of ECCS Pumps Under Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>On July 15, 1997, Illinois Power (IP) personnel were reviewing the effect of degraded protective coatings in containment on the ability of the emergency core cooling system (ECCS) pumps to have the required net positive suction head (NPSH). IP personnel could not determine that these protective coatings would not fail during an accident and deposit on the ECCS pump suction strainers causing the pumps to not meet their design NPSH requirements. Also, the quantity of non-qualified flexible materials in the containment may have had similar effects during accident conditions on the ECCS NPSH. The cause of this event was the failure to recognize the impact of the degraded protective coatings on the ECCS pumps NPSH and the failure to implement better controls on the use of flexible material in the containment. Corrective actions include: removal of degraded coatings, periodic inspection and evaluation of the remaining protective coatings, testing of existing coatings, and providing additional procedural controls and training on the use of flexible materials in the containment building. In addition, excess flexible materials were removed.
4611997021 | Clinton 1 | 09/29/1986 | 08/25/1997 | 9709030329 | <strong>Control Circuit for Division 1 Emergency Diesel Generator Feed Breaker Does Not Meet Design Basis Due to Design Error and Could Prevent Power for Division 1 Safe Shutdown Equipment During a Main Control Room Fire with Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>Design of a control circuit fed from the 125 volts direct current (DC) control power fuse for the Division 1 Emergency Diesel Generator (EDG) feed breaker was not in accordance with the plant's Fire Protection Safe Shutdown Analysis (SSA). The circuit was routed through the Main Control Room (MCR), but did not include isolation contacts at the Remote Shutdown Panel (RSP) transfer switch to allow isolation of the MCR wiring/controls while operating from the RSP. During a MCR fire, concurrent with a Loss of Offsite Power, fire could damage the circuit, causing multiple (DC) ground faults, the loss of control power for the Division 1 EDG feed breaker, and a loss of power to Division 1 equipment. The lack of isolation contacts would prevent isolation of the faults when transfer/isolation of the breaker control circuit from the MCR to the RSP was attempted. The circuit design is not in accordance with 10CFR50, Appendix R, Section III.L, and the plant's design basis. The cause of this event is attributed to a design error. Corrective action for this event includes rewiring the circuit to add isolation contacts from the transfer switch at the RSP, and reviewing all circuits routed through the RSP to ensure that a MCR fire would not prevent operation of those circuits from the RSP. This condition is also reportable under the provisions of 10CFR21.
4611997022 | Clinton 1 | 09/29/1986 | 11/13/1997 | 9711210231 | <strong>Design of Diesel Generator Ventilation Subsystems Outside Design Basis as a Result of Failure to Include Minimum and Maximum Outside Air Temperature Extremes Due to Design Error</strong><br /><i>Abstract:&nbsp;</i>The diesel generator (DG) room ventilation system was designed based on an outside air temperature range of -2 degrees Fahrenheit (F), winter minimum temperature, and 96 degrees F, summer maximum temperature. The Updated Safety Analysis Report (USAR) identifies temperature extremes of -22 degrees F and 112 degrees F based on surrounding area temperature data. Analysis determined that the DG ventilation system is unable to maintain DG room temperature within the design limit during the area extreme high temperature identified in the USAR. The cause for this condition was design engineers, oversight. During the investigation, annunciator power supplies located in the DG rooms were identified as not meeting Class 1E qualification due to improper implementation of a design modification. Corrective actions include revising procedures, evaluating components for increased room temperature, installing a temporary modification to reduce temperature inside a control panel, design changes to the DG Direct Current (DC) electrical distribution system, reviewing other ventilation systems for the design deficiencies, correcting the USAR, correcting the DG DC annunciator power supply Class 1E deficiency, evaluating the effects of outside air temperature extremes and verifying Class 1E deficiencies do not exist in other control panels. This condition is reportable under 10CFR21.
4611997023 | Clinton 1 | 11/07/1997 | 12/05/1997 | 9712100047 | <strong>Inadequate Work Instructions Leads to Potential Overgreasing of the Motor Bearings Causing Potential Failure of Various Motors</strong><br /><i>Abstract:&nbsp;</i>On November 7, 1997, it was determined that all safety related motors that contain bearings requiring the periodic addition of grease, may potentially fail. The possible premature failure of the motors is due to the use of an incorrect method for adding grease to safety-related motor bearings. The incorrect method for adding grease to safety related motor bearings could cause the motor to fail due to overheating of the windings or bearing damage. Approximately seventy safety-related motors, in various systems, are potentially affected by this condition. The cause of this event is that inadequate job instructions were provided in the preventive maintenance tasks. Corrective actions for this event include: revising appropriate preventive maintenance tasks that add grease to motors to provide the necessary instruction to properly perform the task, briefing of electrical and mechanical maintenance supervisors on this condition, and inspection of safety-related and risk significant electric motors that are susceptible to this condition.
4611997024 | Clinton 1 | 08/30/1997 | 10/29/1997 | 9711070092 | <strong>Failure to Comply with the Technical Specifications Action Statement to Immediately Restore AC Power Sources Due to Inadequate Interpretation of the TS Action</strong><br /><i>Abstract:&nbsp;</i>On Labor Day weekend, August 30, 31, and September 1, 1997, Clinton Power Station (CPS) suspended work that Was ongoing to restore Westinghouse 4160 volt safety-related breakers to an operable status. Suspension of this work was later determined to be in conflict with the Technical Specification requirements (Action statements) to immediately initiate action to restore operability of the affected electrical bus(es), source(s), and/or components. The cause for this event was determined to be an organizational breakdown due to inadequate work prioritization and a lack of understanding of the CPS TS for an immediate action when applied to a long term condition. The corrective actions for this event include Licensing providing plant staff guidance on the application of immediate as it pertains to long term corrective actions, emphasizing to Plant Schedulers and the Work Control Team the expectation for working continuously around the clock on immediate actions required by the TS and distribution of a memo to site personnel describing the Operations Shift Supervisor's responsibility for leadership over plant activities.
4611997025 | Clinton 1 | 10/02/1997 | 10/28/1997 | 9711040287 | <strong>Design Deficiency Results in Plant Being Outside Design Basis for a Fire in the Main Control Room Potentially Damaging Valves Required in the Safe Shutdown of the Plant</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1997, the plant was in Mode 4, reactor coolant temperature was being maintained within a band of 100 to 120 degrees Fahrenheit and pressure was atmospheric. Engineering personnel were resolving a condition report written to investigate the potential for a fire in the Main Control Room causing hot shorts of circuitry for motor operated valves (MOV) required for safe shutdown of the plant from the remote shutdown panel. A hot short could potentially cause the MOV to spuriously operate bypassing the MOV control circuitry protective features. When the MOV control circuit protective features are bypassed, the potential exists for the valve to be damaged to the extent that the valve could not be operated either manually or electrically. This is contrary to the design basis of the plant described in 10CFR50 Appendix R, Section III.G. The cause of this design deficiency could not be determined. Approximately fifty valves are potentially affected by this condition. Corrective actions for this event include: analyze and modify, as required, each affected MOV circuit so that a fire in the Main Control Room will not affect the ability of the valve to operate so that the capability to achieve safe shutdown is assured, review of other component types for applicability, and revise the engineering review standards to require that changes to safe shutdown electrical circuits be reviewed for this condition.
4611997026 | Clinton 1 | 10/14/1997 | 03/03/1998 | 9803100122 | <strong>Excess Silt in Area of Shutdown Service Water Pumps Results in Shutdown Service Water Pump Inoperability</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1997, the plant was in Mode 4 (Cold Shutdown) for the sixth refueling outage (RF-6), reactor [RCT] coolant temperature was being maintained within a band of 100 to 120 degrees Fahrenheit and pressure was atmospheric. Plant engineers identified that the level of silt in the area of the shutdown service water system (SX) pump intake area exceeded the level required to ensure the operability of the Division I and II SX pumps. The cause of this event was attributed to the failure to perform an adequate inspection of the SX pump intake area. The inspection procedure for the plant service water screenhouse did not specifically require an inspection of the SX pump intake area and establish an acceptance criteria for the level of silt in the plant service water intake area. Corrective actions for this event include: cleaning of the plant service water intake structure, evaluating, inspecting or testing the Division I and II SX heat exchangers to determine operability, and revising the inspection procedure to include acceptance criteria for silt levels, trending of silt accumulation, and periodic inspection of the SX portion of the pump intake structure.
4611997027 | Clinton 1 | 08/03/1990 | 12/04/1997 | 9712100004 | <strong>Misinterpretation of 10CFR50.59 Results in Installation of Modification of the Residual Heat Removal (RHR) System that is Outside of the Plant's Design Basis</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1990, the plant was in Mode 1 (Power Operation) at approximately eighty-two per cent reactor power. Maintenance completed installation of the first portion of a modification to add interlocks to the RHR system. This modification allowed opening the residual heat removal (RHR) suppression pool suction and full flow test valves only when the respective RHR shutdown cooling suction valve is fully closed. on October 9, 1997, questions were raised concerning the safety evaluation prepared for this modification. Further review determined that the addition of a relay in two of the RHR loops increased the probability for an equipment malfunction which would affect the ability of the plant to use RHR in the suppression pool cooling mode of operation. Therefore, the addition of this relay resulted in an unreviewed safety question. The cause of this event was a misinterpretation of 10 CFR 50.59. The corrective action for this event is to modify the RHR system to eliminate the unreviewed safety question and maintain the interlocks added by the modification. Additionally, the current safety evaluation program procedure provides clear guidance that any increase in the probability of an equipment malfunction is an unreviewed safety question.
4611997028 | Clinton 1 | 11/26/1997 | 12/23/1997 | 9712290027 | <strong>Failure of ABB to Supply Properly Qualified Components Results In Inoperability of All In-Service Thirty-Three 480-Volt K-Line Safety Related Circuit Breakers</strong><br /><i>Abstract:&nbsp;</i>On November 26, 1997, the plant was in Mode 4 (Cold Shutdown) for the sixth refueling outage (RF-6). Engineering identified that the environmental qualification of the power shield trip units associated with all thirty-three inservice ABB 480-volt K-Line safety-related circuit breakers ware not sufficient to withstand the expected dose rates following a worst case lost of coolant accident. The cause of this event is that ABB can no longer assure Illinois Power that the power shield trip units associated with ABB-480-volt K-Line safety-related circuit breakers are qualified for the expected post lose of coolant accident radiation dose. Also, Illinois Power was not notified by ABB when they made the 10 CFR Part 21 notification of this condition. The corrective action for this event includes, either replace or repair the affected components in the inservice ABB 480-volt K-Line safety related circuit breakers with properly qualified components or evaluate that the installed power shield trip units on ABB 480-volt K-Line safety-related circuit breakers are acceptable for the expected environmental conditions, obtain and review a list of 10 CFR Part 21 notifications for ABB circuit breakers and relays to determine if Illinois Power was notified of applicable 10 CFR Part 21 notifications.
4611997029 | Clinton 1 | 11/13/1997 | 12/15/1997 | 9712190165 | <strong>Failure to Follow a Plant Procedure When Erecting Scaffold Results in a Safety-Related Area Cooler Becoming Inoperable Due to Seismic Qualification Concerns</strong><br /><i>Abstract:&nbsp;</i>On November 13, 1997, Illinois Power (IP) personnel were investigating an issue where a scaffold was found partially supported by the Low Pressure Core Spray (LPCS) [BO] room area cooler, 1VY01S [CLR]. The effect that this scaffold had on the room cooler could not be positively determined; therefore, the room cooler was concluded to be inoperable due to seismic qualification concerns. The 1VY01S room cooler is a support component for the LPCS system, therefore, inoperability of the room cooler causes the LPCS system to be inoperable. The scaffold was built in November, 1994, to perform preventive maintenance on the 1VY01S room cooler. Because of radiation dose rates in the area (but without proper consideration given to the impact of the scaffold), a decision was made to leave the scaffold up for future use to reduce worker radiation exposure. The cause for this event was a failure to comply with CPS procedure 8901.10, "Scaffold Erection/Use/Dismantling." The corrective actions for this event include modifying the scaffold in accordance with CPS procedure 8901.10 to ensure it does not affect the seismic qualification of plant equipment, briefing appropriate personnel on this incident and CPS procedure 8901.10, and performing a walkdown of existing scaffolds to ensure the requirements of CPS procedure 8901.10 are met.
4611997030 | Clinton 1 | 10/26/1997 | 12/17/1997 | 9712240167 | <strong>Failure to Verify the Reactor Water Cleanup System Was Available as an Alternate Means of Shutdown Cooling Due to Procedural Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1997, at approximately 0245 hours, with the plant in Mode 4 (COLD SHUTDOWN), the Operations Department discovered that Component Cooling Water (CCW) was not aligned to the "A" Reactor Water Cleanup (RWCU) non-regenerative heat exchanger (NRHX). At this time the plant was in the Technical Specification (TS) Limiting Condition for Operation (LCO), 3.4.10, "RHR-Shutdown Cooling (Cold Shutdown)." The Action Statement for TS LCO 3.4.10 required verification of an available alternate method of decay heat removal for each inoperable RHR shutdown cooling subsystem. The RWCU system was being credited as one of the alternate methods of decay heat removal, and because of the unknown CCW system alignment to the "A" RWCU NRHX, the TS LCO Action Statement for verifying an alternate method of decay heat removal had not been met. The cause of this event was procedural deficiency-inadequate scope. The corrective actions for this event include aligning the Component Cooling Water system to the "A" RWCU NRHX, revising CPS procedure 3303.01, "Reactor Water Cleanup (RT)," reviewing other procedures to ensure proper heat exchanger valve lineups, defining "available" as it pertains to support system adequacy including analyzing system procedures to ensure their adequacy in verifying a system available, and briefing appropriate personnel on this event.
4611997031 | Clinton 1 | 11/13/1997 | 11/18/1999 | ML99335007 | <strong>Inadequate Testing of Safety-Related Logic Circuits Results in Failure to Meet Technical Specification Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>
4611997032 | Clinton 1 | 09/29/1986 | 04/24/1999 | 9905050136 | <strong>Plant Outside Design Basis Due to Inadequate Tornado Missile Protection Caused by Design Error</strong><br /><i>Abstract:&nbsp;</i>ABSTRACT: On December 2, 1997, at approximately 1840 hours, Plant Operations determined that portions of the High Pressure Core Spray (HPCS) pump suction piping, Reactor Core Isolation Cooling (RCIC) pump suction piping, and RCIC storage tank level instrumentation standpipe, located outside of a missile protected building, were not designed to withstand missiles generated by a design basis tornado. The Updated Safety Analysis Report (USAR) identifies these components as designed to withstand the effects of tornado-generated missiles. An extent of condition evaluation was performed and determined that other portions of the plant were susceptible and not analyzed for damage due to tornado-generated missiles. Specifically, portions of the Shutdown Service Water system and Control Room Ventilation system are not missile protected as described in the USAR. The cause of this event was determined to be design engineering oversight. The corrective actions for this event include: analyzing the probability of increased risk due to missile damage from a design basis tornado, submitting a license amendment to change the CPS design basis, and revising the USAR to reflect this change upon NRC approval. This report also cancels 10CFR21 report 21-97-057. END OF ABSTRACT
4611997033 | Clinton 1 | 12/17/1997 | 01/16/1998 | 9801280140 | <strong>Misinterpretation of Technical Specification Bases Results in Failure to Meet Required Technical Specification Actions for Two Inoperable Emergency Core Cooling Subsystems</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1997, an Operations shift supervisor was reviewing a table of secondary containment isolation valves and dampers that required manual "Administrative Controls" to determine their required positioning for an upcoming divisional bus outage. The shift supervisor recognized that the Containment Building Fuel Transfer Pool Ventilation Plenum Exhaust Radiation monitors, which have been inoperable since October 18, 1997, impacted the status of some isolation dampers. These monitors isolate secondary containment and secondary containment bypass dampers on the detection of a high radiation condition. Administrative control was not in place to ensure isolation capability of these dampers. The cause of this event is due to a misinterpretation of the Technical Specifications, therefore the required actions for these monitors being inoperable were not taken. The corrective actions for this event are to issue a night order to the Operations Department emphasizing the requirement to review the applicable Technical Specification Bases for other required actions, to revise the operations procedure on Technical Specification tracking to add clarification on reviewing the Technical Specification Bases for any additional actions to be performed, and a review of the Technical Specifications references to instrumentation required during a shutdown.
4611997034 | Clinton 1 | 09/29/1996 | 04/03/1998 | 9804130273 | <strong>Incorrect Cable Resistance and Brake Horsepower Data Used in the Design of Divisions 1 and 2 Emergency Diesel Generator Vent Fans Results in design of Fan Motors Being Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>Station engineers determined that during degraded voltage conditions, the Divisions 1 and 2 emergency diesel generator (EDG) room vent fans, 1VD01CA and 1VD01CB, could cause off-site power supply breakers to trip on undervoltage during transient electrical bus loading conditions associated with a block start Loss of Coolant Accident (LOCA). Improper cable resistance values and brake horsepower ratings were used in the original design of the 1VD01CA and 1VD01CB vent fans. This condition is outside the design basis of the plant. The cause of this event was determined to be insufficient detail provided in a S&L standard and design engineer's oversight when determining the brake horsepower ratings of 1VD01CA and 1VD01CB. Corrective actions include revising calculations, developing a new cable impedance standard, providing required reading for appropriate individuals on the new cable impedance standard, verifying other S&L standards, and performing a plant modification to correct this condition. The cable resistance issue is also reportable under 10CFR21.
4611997035 | Clinton 1 | 09/29/1986 | 03/19/1998 | 9803250470 | <strong>Divisions 1 and 2 Battery Chargers Incapable of Supplying Full Rated Voltage and Current Flow at the Degraded Voltage Trip Setpoint in Accordance With the Plant's Technical Specifications and Design Basis</strong><br /><i>Abstract:&nbsp;</i>The plant was in COLD SHUTDOWN for a refueling outage and engineers were investigating degraded voltage margins and a cable impedance deficiency when they discovered that the Divisions 1 and 2 safety-related battery chargers had not been analyzed in the degraded voltage calculations. Further, the battery chargers may not be capable of supplying full rated voltage and current flow at the degraded voltage trip setpoint with the present battery charger transformer tap setting at 480 volts. In accordance with Technical Specification (TS) Surveillance Requirements, the battery chargers are required to meet a minimum battery terminal voltage of greater than or equal to 129 volts on float charge and a minimum current output of 300 amps at 125 volts. Degraded voltage input to the chargers could be as low as 426.1 volts; therefore, at the present transformer tap setting, the battery chargers may not provide the output required during degraded voltage conditions. The apparent cause of this event was a failure to include the battery charger minimum voltage requirement in the acceptance criteria for the degraded voltage transient calculation. Corrective action includes adjusting the transformer tap settings on the Divisions 1 and 2 battery chargers and, if needed, on the Division 4 battery charger.
4611997036 | Clinton 1 | 12/22/1997 | 01/19/1998 | 9801260201 | <strong>Failure of Cooling Unit Manufacturer to Install Motor Shaft Key Leads to Inoperability of Shutdown Service Water Pump Room Cooling Unit</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1997, Engineering completed an evaluation of a missing motor shaft key that connects the motor to the fan hub of the Division II shutdown service water pump room cooler. This evaluation determined that without the motor shaft key the Division II shutdown service water pump room cooler could not be considered operable. The inoperability of the room cooler causes the associated Division II shutdown service water pump to be inoperable. It is likely that the motor shaft key was not installed during initial manufacturing by Buffalo Forge. Corrective action for this event is to install the required motor shaft key. A review of the maintenance history at Clinton Power Station for similar fans manufactured by Buffalo Forge revealed that similar conditions with Buffalo Forge supplied cooling fans have not been previously identified. This event is reportable under 10 CFR Part 21.
4821997001 | Wolf Creek | 01/08/1997 | 09/12/1997 | 9709220191 | <strong>Failure To Comply With Surveillance Requirements to Test Certain Components at Shutdown</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1997, during a Quality Evaluations Audit, "Technical Specifications and Surveillance Testing," an auditor questioned whether the surveillance requirements for Technical Specification 4.7.3.b were being appropriately met. Surveillance requirement 4.7.3.b states, "At least two component cooling water loops shall be demonstrated OPERABLE: At least once per 18 months during shutdown..." It was determined that portions of this Technical Specification surveillance required to be performed "at least once per 18 months during shutdown" were being performed in Mode 1. Operations personnel have performed a review of surveillances requirements that are required to be performed at shutdown and found other occurrences. Additional examples of surveillances being performed at an incorrect frequency are being reported as supplements to 97-001-00. The root cause of these events is personnel error made in scheduling of Technical Specifications Surveillances and the surveillance requirements contained therein. Corrective actions included review of the scheduling database for similar scheduling errors and revision of applicable procedures.
4821997004 | Wolf Creek | 02/06/1997 | 03/07/1997 | 9703140095 | <strong>Failure to Accurately Perform the Containment Integrated Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On February 6, 1997, it was discovered that during the past performances of the Containment Integrated Leak Rate Test (ILRT) the valves associated with the Hydrogen Analyzer System penetrations (P-56, P-97, P-99 and P-101) were closed. Therefore, that portion of the system located outside of Containment was not leak tested as required by Technical Specification surveillance requirement 4.6.1.1. The root cause of this event was an incorrect start-up procedure which was developed as part of the Containment Leakage Rate Testing Program. Immediate corrective actions included revision of applicable procedures and performance of the required leak rate test to verify compliance with Appendix J requirements. Long term corrective actions include further procedure revisions, training of personnel, and a self assessment of the Containment Integrated Leak Rate Program.
4821997005 | Wolf Creek | 04/11/1997 | 05/08/1997 | 9705150179 | <strong>Violation of Technical Specification 3.8.1.1, "B" EDG Operability</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 10, 1997, the rear cover panel of the annunciator assembly in KJ122 ('B' Emergency Diesel Generator) was found unsecured and all fasteners were missing. It is possible that this cover could fall and damage components used to control the operation of Emergency Diesel Generator 'B'. This is in violation of Technical Specification 3.8.1.1.b, which requires two separate and independent diesel generators to be operable during Modes 1, 2, 3, and 4. This event is reportable to 10 CFR 50.73(a)(2)(i). This is being reported as a condition which could have caused inoperability of the 'B' EDG in a seismic event. This event is reportable to 10 CFR 50.73 (a)(2)(i). Immediate corrective actions included inspecting the wiring below the panel to determine that no damage occurred, and to reinstall the panel correctly. Additional corrective actions include a walk down to ensure that other panels in the plant are correctly installed, and training in prevention of human error.
4821997006 | Wolf Creek | 04/14/1997 | 05/13/1997 | 9705200222 | <strong>Failure To Comply With Regulatory Guide Requirements for Instrument Accuracy</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On April 14, 1997, during the review of a Setpoint Change Request for new recorders being installed at WCNOC's meteorological tower, it was identified that the existing setpoints for the 10 and 60 meter wind directions were contrary to, and non-conservative with, the requirements for accuracy in Regulatory Guide 1.23, 'Onsite Meteorological Programs.' This error was reflected in the corresponding procedures. Historically, Regulatory Guide 1.23 was stated in the bases section for Technical Specification 3.3.3.4, and operability of the instrumentation was based on meeting the requirements therein. The root cause of this event is personnel error in that procedural controls in place at the time should have caused the appropriate documents to be updated. Corrective actions include a historical review of Performance Improvement Requests to determine if generic issues exist, correction of the surveillance procedure which calibrates the instrumentation, and a review of the remaining Meteorological System components to ensure that all setpoint data and accuracy requirements are correct.
4821997007 | Wolf Creek | 05/01/1997 | 08/28/1997 | 9709050025 | <strong>Failure To Procure Test Gas for a Safety Related Component Through an Appendix B Program.</strong><br /><i>Abstract:&nbsp;</i>On May 1, 1997, while verifying prerequisite requirements for performance of a Surveillance Test Procedure, Instrumentation and Controls personnel discovered multiple test certificates with the Hydrogen calibration gas bottle installed for Containment Hydrogen Analyzer "B" when there should only have been one. There were inconsistencies with the information on the certificates which caused the technician to question the contents of the test gas bottles. The Hydrogen Analyzers were declared inoperable while verification and certification were being obtained. During the problem resolution, System Engineering questioned why the gas was classified as non-safety related and not procured pursuant to an Appendix B program. Engineering determined that the certification of the gas is a safety related function and should be performed through an approved Appendix B process. There is very little documentation available for certification of the test gas for the Hydrogen Analyzers, therefore the historical effect of the test gas used since initial start-up is indeterminate. Technical Specification Surveillance Requirements require the Hydrogen Analyzers to be calibrated and it is unknown if the calibration performed was correct. The root cause is failure to follow procedure requirements. Corrective actions include review of purchasing documents for similar issues, training, and procedure revision.
4821997008 | Wolf Creek | 05/20/1997 | 06/19/1997 | 9706300017 | <strong>Manual Reactor Trip Due To A Steam Leak in A Non-Safety Related Third Stage Extraction Steam Isolation Valve.</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, May 20, 1997, at 1402, valve AFLV0058C, a non-safety related sixteen inch third stage extraction steam isolation valve, developed a body-to-bonnet steam leak. The steam leak increased to the point that a manual plant trip was initiated at 1457. All rods inserted normally and fully, and all Engineered Safety Features equipment and Reactor Protection System equipment performed as designed. The leak was stopped by shutting the Main Turbine Stop valves. The body-to-bonnet gasket in AFLV0058C was replaced by a new corrugated iron gasket wrapped with graphite tape. No steam cutting or other damage was identified during the rework. The root cause of the event was the lack of guidance on how to determine minimum and maximum gasket seating stress and corresponding bolt torque values for sheet type gasket materials. Corrective actions included evaluation of other equipment for similar concerns, revision of procedures to provide guidance on providing the correct torque necessary to produce the required gasket stress, and training of Maintenance Planners.
4821997009 | Wolf Creek | 05/20/1997 | 08/06/1997 | 9708150304 | <strong>Failure To Comply with Technical Specification 4.5.2.c.2</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1997, during a forced outage, it was identified by Operations personnel that containment inspections required by Technical Specification (TS) 4.5.2.c.2, and by procedure STS EJ-001, Revision 10, "Containment Inspection," were not performed on May 20, 1997 after three containment entries. Technical Specification surveillance requirement 4.5.2.c.2 requires a visual inspection be performed at the completion of each containment entry when containment integrity is established. The root cause of this event is that though corrective actions following the concerns with the use of Technical Specification Clarifications addressed the need for verbatim compliance, several employees failed to meet Operations' performance expectations when addressing verbatim compliance. Corrective actions include procedure review and management meetings with employees.
4821997010 | Wolf Creek | 06/04/1997 | 06/30/1998 | 9807210363 | <strong>Deficient Surveillance Tests Identified During Generic Letter 96-01 Reviews</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1997, Wolf Creek Nuclear Operating (WCNOC) personnel, after receiving information about a Generic Letter 96-01-identified concern from another plant, reviewed the Wolf Creek Generating Station Engineered Safety Features Actuation System testing procedures, and determined that three procedures did not fully meet the quarterly Analog Channel Operational Test (ACOT) requirements of Technical Specification 4.3.2.1. The procedures did not provide for full overlap testing of the P-11 circuits. The on-duty Shift Supervisor was immediately notified. All three channels of Pressurizer Pressure P-11 were declared inoperable and the required Limiting Conditions for Operation entered. On June 12, 1997, the three channels were tested with newly revised procedures. On July 31, 1997, WCNOC identified two surveillance procedures that did not test all contacts of Slave Relay K643 on a quarterly basis, per Technical Specification 4.3.2.1. The procedures were revised and the relay contacts were successfully tested. On September 4, 1997, it was discovered that certain relay contacts have not been tested during performance of surveillance procedure, STS KJ-001 A/B, "Integrated Diesel Generator Safeguards Actuation Test Train A/B." The procedures were revised and the relay contacts were successfully tested. The root cause for all three events was inadequate or incomplete procedures due to misinterpreting, not understanding, or not clarifying technical specification requirements during writing or revising the procedures. No additional actions beyond the immediate actions taken were deemed necessary.
4821997011 | Wolf Creek | 05/25/1997 | 06/27/1997 | 9707030288 | <strong>Technical Specification Violation Occurred During Calorimetric Adjustments</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.3.1.1, Table 4.3-1, Power Range, Neutron Flux High Setpoint Note 2, states, "Comparison of calorimetric to excore power indication above 15 percent of RATED THERMAL POWER. Adjust excore channel gains consistent with calorimetric power if absolute difference is greater than 2 percent..." This Technical Specification was inadvertently violated when procedure changes were made contrary to this Technical Specification and then implemented during a return to power after a forced outage. The root cause is personnel error during the procedure revision and regulatory screening process. Corrective actions include revision of the procedure to concur with the Technical Specification and counseling of the individuals involved.
4821997012 | Wolf Creek | 06/05/1997 | 07/02/1997 | 9707090398 | <strong>Section 6.2.2 Technical Specification Violation Regarding Shift Compliment</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1997, it was identified that several active licensed Operators did not have corrective glasses that would fit inside self contained breathing apparatuses (SCBA). The operators in question are required per their license to wear corrective lenses while performing licensed duties. Two off-normal procedures require licensed operators to wear an SCBA. This is being reported as a violation of the administrative section of Technical Specifications which stipulates shift compliment requirements. The root cause of this event is lack of administrative controls to ensure SCBA compatible corrective lenses were available for licensed operators. Corrective actions included buying corrective glasses, development of a procedure regarding license restrictions, and adding the requirement to training.
4821997013 | Wolf Creek | 07/21/1997 | 08/20/1997 | 9708290063 | <strong>Section 3.7.3 Technical Specification Violation Regarding Two Independent CCW Loops</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1997, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel determined that the two Component Cooling Water (CCW) trains had been cross-tied on five different occasions using procedure SYS EG-202, "CCW Surge Tank Level Equalization." This action is contrary to Technical Specification 3.7.3 which requires "At least two independent component cooling water loops shall be operable" during Modes 1, 2, 3, and 4. The root cause is that WCNOC personnel failed to assure that adequate procedures were in place to prevent this Technical Specification violation from occurring. Corrective actions include the cancellation of STS EG-202, and a review of Operations' procedures.
4821997014 | Wolf Creek | 07/30/1997 | 08/28/1997 | 9709050001 | <strong>Waste Gas System Hydrogen/Oxygen Analyzers Not Operated in Accordance With Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 30, 1997, while performing a daily surveillance procedure, a Radwaste operator questioned the acceptability of operating a Waste Gas System compressor with both Hydrogen/Oxygen analyzer racks being out of service. USAR Technical Requirements 16.3.1.6 and 16.11.3.1 (previously Technical Specifications 3/4.3.3 and 3/4.11, respectively) require that the analyzers be in service at all times during Waste Gas Holdup System operation. Research into this issue determined that the system had been operated in a similar fashion when the requirements were in the WCNOC Technical Specifications. Therefore, this event is considered reportable in accordance with 10 CFR 50.73(a)(2)(i). The root cause of this event was inadequate administrative controls for ensuring the analyzers are in service during system operation. Corrective actions include revising applicable procedures to ensure the analyzers are in service whenever a compressor is in operation.
4821997015 | Wolf Creek | 08/19/1997 | 12/11/1997 | 9712180061 | <strong>Required 10-Year ISI VT-3 Examinations Not Performed on Pressurizer Safety Valves</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1997, at 1731 hours, WCNOC Engineering personnel determined that a 10-year Inservice Inspection (ISI) requirement for a VT-3 visual examination of the internal surfaces of a Pressurizer Safety Valve had not been performed during the first 10-year interval. As a result, the requirements of Technical Specifications 4.0.5 and 4.4.2.2 were not met and the pressurizer safety valves were declared inoperable. Technical Specification 4.0.3 was entered, allowing 24 hours to complete the required surveillance prior to taking the required actions of Specification 3.4.2.2. The required ISI VT-3 visual examination was completed satisfactorily, and the pressurizer safety valves were returned to OPERABLE status on August 19, 1997 at 2346 hours. The cause of this event was inadequate program to program interface between the ISI program and Maintenance work planning with respect to work activities which fall outside the scope of the WCNOC ASME Section XI Repair/Replacement program. Until necessary procedure revisions are complete, interim corrective actions ensure ISI engineer review of work activities on Code components which would be outside of the WCNOC Repair/Replacement Program. Revisions of the Pressurizer Code Safety Valve Operability procedure and the work package task planning procedure will be completed by February 3, 1998.
4821997016 | Wolf Creek | 09/03/1997 | 01/27/1998 | 9802050023 | <strong>Use of Fire Protection Pumps for Non-Fire Protection Purpose Constituted a Significant Degradation of Fire Protection System.</strong><br /><i>Abstract:&nbsp;</i>Testing performed on September 19, 1997, provided results which indicate that uses of the Fire Protection (FP) system water flow for non-fire protection purposes resulted in a significant reduction of FP system capability; however, adequate flow would have been available to achieve and maintain safe shutdown in the event of a fire. These uses constitute a violation of License Condition 2.C (5)(a); therefore, this event is being reported per the Wolf Creek Generating Station (WCGS) Operating License, Condition 2.F. The cause of this event is attributed to the inadequacy of Fire Protection Program management with respect to training of personnel and ensuring compliance with licensing requirements. WCGS has initiated interim actions to ensure no further uses of the fire protection system pumps would occur for non-fire protection purposes without Engineering evaluation and approval of the plant manager. A comprehensive procedure is being developed for FP system use. An assessment of the fire protection organization structure and program ownership will be completed by July 15, 1998.
4821997017 | Wolf Creek | 09/30/1997 | 10/30/1997 | 9711030209 | <strong>Spent Fuel Storage Facility Crane Surveillance Not Met</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1997, WCNOC personnel identified that Surveillance Test Procedure STS KE-003, Spent Fuel Bridge Crane Surveillance test, does not account for the weight of the scale in the steps used to check the overload cutout setpoint. This procedure, as written was not adequate to ensure that the cutout would occur consistent with the surveillance requirements (i.e., above the 2250 pound overload cutout requirement). Although these requirements are not currently in the WCNOC Technical Specifications (they were relocated to the USAR by Amendment 89, dated October 2, 1995), this practice existed during the time the Spent Fuel Bridge Crane requirements were in the WCNOC Technical Specifications. Therefore, this LER is being written to document a historical violation of the WCNOC Technical Specifications. The cause of this event is an inadequate procedure. Corrective actions were to revise STS KE-003 and satisfactorily perform the surveillance.
4821997018 | Wolf Creek | 10/01/1997 | 04/27/1998 | 9805050447 | <strong>Voluntary Report - Multiple Failures of "B" Residual Heat Removal Pump to Start</strong><br /><i>Abstract:&nbsp;</i>On October 1, 5, and 31, 1997, the "B" Residual Heat Removal (RHR) pump did not start because the RHR pump breaker failed to close. Following the October 31, 1997, breaker failure, an Incident Investigation Team was assembled. The cause of the failures was determined to be the 152/IS closing circuit interlock switch contacts in the breaker closing circuit not achieving continuity after the switch was actuated. Corrective actions included adjustment of the breaker's positive interlock roller, generic inspection of other similar breakers, identification of inadequacies in trouble shooting and handswitch performance, procedure revisions, and additional preventive maintenance. Independent laboratory testing was conducted to assist in identifying the cause of the contact failure. The laboratory results were inconclusive.
4821997019 | Wolf Creek | 10/14/1997 | 11/13/1997 | 9711180112 | <strong>Failure to Adequately Vent Emergency Core Cooling Pump Casings and Discharge Piping High Points in Accordance With Technical Specification Surveillance Requirement 4.5.2b.1)</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1997, after discussions with another utility and further reviews, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel determined that WCGS was not in compliance with Surveillance Requirement 4.5.2b.1). Technical Specification Surveillance Requirement 4.5.2b.1) requires verifying that the Emergency Core Cooling System (ECCS) piping is full of water by venting the ECCS pump casings and accessible discharge piping high points at least once per 31 days. A review of procedure STS BG-002, "ECCS Valve Check and System Vent," determined that the Centrifugal Charging pump and Residual Heat Removal pump casings were not being vented as required by the surveillance requirement. Additionally, WCNOC personnel determined that the surveillance procedure was deficient in providing the appropriate discharge piping high points. The root cause of this event is the initial procedure writers failed to clearly understand the requirements of the technical specifications before procedures were initially written or subsequently when they were revised. Corrective actions included submitting an exigent license amendment request and revising STS BG-002 to incorporate the RHR pump seal cooler line vent valves and additional high point vents.
4821997020 | Wolf Creek | 11/09/1997 | 05/26/1999 | 9906030266 | <strong>Failure to Meet Snubber Technical Specification LCO Requirements</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1997, during Refueling Outage 9 routine snubber inspections, a Residual Heat Removal (RHR) line snubber failed its functional test requirements. The root cause of this and other snubber failures identified during Refueling Outage 9 indicates that several snubbers were likely inoperable during the time frame when former Technical Specification 3.7.8 requirements were applicable; however, in no case was the system or subsystem rendered inoperable by the failures. Although snubber requirements are not currently in the WCGS Technical Specifications (they were relocated to the Updated Safety Analysis Report by Amendment 89, dated October 2, 1995), the Action Requirements of former Technical Specification 3.7.8 (i.e., restoring the snubber to operable status within 72 hours or declaring the affected system inoperable) may not have been met for the identified failures. Therefore, this LER is being written to document historical violations of the WCGS Technical Specifications. The causes of the snubber failures involved manufacturing errors, corrosion, hydraulic transient, check valve slamming, and system vibration. Corrective actions included performing system walkdowns, replacement and evaluations of the failed snubbers and associated piping sections, and additional snubber sampling. The root cause of snubber EJ01-R003 being found in a failed condition was determined to be a September 17, 1994 hydraulic transient.
4821997021 | Wolf Creek | 11/19/1997 | 12/19/1997 | 9801020055 | <strong>On November 19, 1997, During review of an INPO Operating Experience Report at another facility, Wolf Creek personnel determined that a similar inadequacy exists with respect to surveillance testing of two Technical Specification functions (Feedwater Isol</strong><br /><i>Abstract:&nbsp;</i>On November 19, 1997, during review of an INPO Operating Experience Report at another facility, Wolf Creek personnel determined that a similar inadequacy exists with respect to surveillance testing of two Technical Specification functions (Feedwater Isolation on P-14 S/G Hi-Hi Level and Safety Injection Feedwater Isolation) and one non-Technical Specification function (Source Range Automatic P-10 Block) associated with the Solid State Protection System (SSPS) at Wolf Creek. The plant was in a refueling outage at that time of discovery (Mode 5). None of the functions is required operable in Mode 5. An Equipment Out-of-Service Log Entry was made to establish a Mode 4 restraint on the SSPS for these functions. Test procedures were revised and appropriate testing completed on November 19 (Train A) and November 20, 1997 (Train B). The logic tested satisfactorily; therefore, there was no affect on public health and safety. This event was caused by an inadequate original testing design supplied by the vendor that did not fully verify operation of the circuits involving Universal Logic Boards in a memory configuration. The SSPS was reviewed for similar memory configurations of this unique logic circuit design (none were found).
4821997022 | Wolf Creek | 11/21/1997 | 12/22/1997 | 9801020039 | <strong>Turbine Trip Instrumentation Surveillance Testing not Performed Prior to Startup</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1997, Wolf Creek personnel determined that the Technical Specification requirements for performing Turbine Trip instrumentation surveillance testing prior to entering Mode 2 (startup) were not being met. The plant was in a refueling outage at the time of discovery (Mode 5). None of the functions are required to be operable in Mode 5. An Equipment Out-of-Service Log Entry was made to establish a Mode 2 restraint for these functions. Test procedures were revised, and appropriate testing completed, prior to entering Mode 2. Prior to properly scheduling these surveillances, testing was done after entering Mode 2. Although testing after entering Mode 2 does not meet Technical Specification requirements, the testing was being performed prior to the turbine trip actuations becoming armed; therefore, there was no affect on public health and safety. This event was caused by the historical mindset of personnel involved in the development and revision of the procedures with respect to literal compliance with the Technical Specification requirements. The Technical Specifications were reviewed for similar startup requirements. No other surveillance frequency violations were found.
4821997023 | Wolf Creek | 11/24/1997 | 12/23/1997 | 9801020147 | <strong>Failure to Maintain Both Containment Personnel Hatch Air Lock Doors Closed</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1997, with the plant in Mode 4, the Containment outer personnel air lock door was found open. Technical Specification Limiting Condition for Operation (LCO) 3.6.1.3 requires that, in Modes 1 through 4, each air lock door shall be OPERABLE with both doors closed, except when the air lock is being used for normal transit and exits through the Containment; then at least one air lock door shall be closed. Root cause of this event is inadequate communications due to insufficient detail in procedures. Corrective actions include closing of the outer airlock door and revision of procedures, GEN 00-002, "Cold Shutdown To Hot Standby," and GEN 00-006, "Hot Standby to Cold Shutdown," and FHP 02-001, "Refueling Operation." In addition, Training Lesson Plan TIN OP 12 032 00, "Containment Operations," will be revised to address this event and the appropriate procedure revisions.
4821997024 | Wolf Creek | 11/29/1997 | 12/23/1997 | 9801020149 | <strong>Engineered Safety Features and Reactor Protection System Actuations Due to a Spike on the Ex-Core Neutron Monitoring System (SE) Nuclear Instrument NI-35 Intermediate Range (IR) Channel.</strong><br /><i>Abstract:&nbsp;</i>On November 29, 1997, at 14:37 Central Standard Time a reactor trip occurred at the Wolf Creek Generating Station (WCGS). The plant was in mode one, at seven percent power, at the time of the trip. The Engineered Safety Features (ESF) and Reactor Protection System (RPS) performed as required. The automatic actuation of the reactor trip occurred as expected, with all rods inserting fully. Subsequent investigation revealed that the reactor trip was caused by a spike on the Ex-Core Neutron Monitoring System (SE) Nuclear Instrument NI-35 Intermediate Range (IR) Channel. The spike exceeded the Intermediate Range High Flux trip setpoint of the current equivalent of twenty-five percent Rated Thermal Power (RTP). The cause of the spike is indeterminate. Based on the investigations performed, no anomalies have been identified that can be confirmed to have caused the IR High Flux trip. Corrective actions included stabilizing the plant, and investigating causes.
4821997025 | Wolf Creek | 12/18/1997 | 01/15/1998 | 9801220096 | <strong>Failure to Meet Breaker Historical Technical Specification Frequency Testing Requirements Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On December 18, 1997, Wolf Creek Operating Corporation (WCNOC) personnel discovered that testing of two types of breakers did not meet the USAR testing requirements regarding sample size and rotating frequency of performance. USAR Section 16.8.1.1.1 (formerly Technical Specification [TS] 4.8.4.1) requires 10% of each breaker type be tested every 18 months on a rotating basis. One of the two types has only one breaker that is subject to this requirement; therefore, this breaker would have to be tested every 18 months to meet the requirement. The second type has two breakers, one of which must be tested every 18 months on a rotating basis to meet the requirements. Although the surveillances were current at the time of discovery, reviews indicate that historical performances of the surveillance did not meet past Technical Specification requirements. The root cause of this event is the failure of personnel to ensure that Technical Specification requirements were incorporated during the initial development of the listing of breakers in the surveillance test procedure. As indicated, surveillances were current for both breaker types at the time of discovery. One breaker was scheduled and tested prior to its January 10, 1998 expiration date. The breaker testing procedure has been revised to correct the testing frequency discrepancy.
4821997026 | Wolf Creek | 11/09/1997 | 11/24/1998 | 9812020021 | <strong>Heavy Loads Moved in Containment Outside of Heavy Load Analysis Requirements</strong><br /><i>Abstract:&nbsp;</i>During a review of Wolf Creek Nuclear Operating Corporation's (WCNOC) heavy load report, WCNOC personnel identified that during past outages heavy loads were moved in the Containment Building in a manner that was inconsistent with the heavy load analysis assumptions. Specifically, WCNOC's analysis assumes that both trains of Residual Heat Removal (RHR) will be operable in Modes 5 and 6, yet WCNOC Technical Specifications allows one train to be operable in Mode 5 if the loops are filled, and secondary side water level of at least two Steam Generators is >10% of the wide range. WCNOC met the Technical Specification requirements, but did not recognize the analysis assumptions for RHR when moving heavy loads in Containment. A review of the Control Room logs from Refuel IX, Fall 1997, confirmed that with one train of RHR inoperable in Mode 6, heavy loads were moved over the one operable train of RHR. The root cause is procedural inadequacy. Corrective action included revision of the controlling procedure to be consistent with the analysis.
4821997027 | Wolf Creek | 11/22/1997 | 06/04/1999 | 9906140052 | <strong>Missed Surveillance Due to Improper Circuitry Configuration and Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1999, Wolf Creek Generating Station (WCGS) personnel identified that Technical Specification Surveillance 4.3.3.5.2 had been missed for Auxiliary Shutdown Panel (ASP) controls during a 1997 refueling outage. Surveillance Requirement 4.3.3.5.2 requires that Auxiliary Shutdown Panel controls be demonstrated operable once every 18 months. However, the actual vendor wiring was not per design drawings for one contact and verification of 15 contacts was not adequately tested by the surveillance procedure. The contacts are associated with ASP control switch circuitry for the Letdown Line Isolation Valve, the Main Steam Supply Valves to the Turbine Driven Auxiliary Feedwater Pumps, the Motor Driven Auxiliary Feedwater Pump and/or the Turbine Driven Auxiliary Feedwater Pump, from the Auxiliary Shutdown Panel. The root cause of this event is attributed to human error by personnel involved with the procedure revisions. The root cause of the vendor wiring issue is historical in nature. This condition constitutes a reportable event in accordance with 10 CFR 50.73 (a) (2) (i) (B). The safety significance of this event was minimal because the configuration, although not per design, was identical in function; therefore, the systems would have functioned as designed. For those contacts and relays not included in the procedure, there is high confidence that the contacts and relays, along with their associated control switches, were capable of performing all of their safety related design functions based on successful subsequent testing. Corrective actions are work groups discussing PIR 99-1777 and revising procedure STS RP-004, "Auxiliary Shutdown Panel Control Switch Test."
4831997001 | Callaway | 02/28/1997 | 03/26/1997 | 9704010458 | <strong>Misinterpretation of Technical Specification 3.9.6 Refueling Machine Trip Limits</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On 2/28/97 Union Electric discovered Technical Specification (T/S) Interpretation (TSI) 25 resulted in the violation of UE FSAR (F/S) Specification 16.9.2.1, REFUELING OPERATIONS-REFUELING MACHINE. F/S Specification 16.9.2.1 replaced T/S 3.9.6. T/S 3.9.6 was violated when TSI 25 was used in refuel one, Spring of 1986 through refuel seven, Spring of 1995. F/S 16.9.2.1 requires the refuel machine primary automatic overload cutoff be set at less than or equal to 250 pounds above the indicated weight for wet conditions and the automatic load reduction trip setpoint be set less than or equal to 250 pounds below the suspended weight for wet conditions. TSI 25 allowed the automatic overload cutoff and load reduction trip weights to be set by the heaviest fuel assembly and lightest fuel assembly respectively. Differences in fuel assembly weights allowed the automatic overload cutoff 250 pound limit to be exceeded when lighter fuel assemblies than the one used to establish the setpoint were being moved and load reduction 250 pound trip limit to be exceeded when moving fuel assemblies heavier than the one used to establish the limit. This violation was caused by the incorrect interpretation of T/S 3.9.6. TSI 25 has been deleted. T/S Section 3.9.6 was relocated to the FSAR during December 1995. The FSAR is being revised to provide appropriate guidance for setting the automatic cutoff and automatic load reduction trip. Additional reviews of TSI's are being performed in conjunction with the ongoing T/S conversion process.
4831997002 | Callaway | 03/07/1997 | 04/04/1997 | 9704080246 | <strong>Missed Technical Specification 4.6.3.1 Surveillance of Containment Isolation Valves Following Maintenance Due to Cognitive Personnel Error</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (T/S) 4.6.3.1 requires that each containment isolation valve shall be demonstrated operable prior to returning the valve to service after maintenance, repair or replacement work is performed on the valve or its associated actuator, control, or power circuit by performance of a cycling test and verification of isolation time. On March 7, 1997, during an engineering review of completed work documents, it was determined that T/S 4.6.3.1 was inadvertently violated on November 9, 1992 and August 30, 1995. The Containment Hydrogen Control System (CHCS) hydrogen analyzer sample line Containment Isolation Valves (CIV) were returned to service on these dates without performance of a stroke time test following replacement of relays in the control or power circuits. Subsequently, on January 1, 1993 and October 16, 1995, the normal stroke testing required per T/S 4.6.3.3 verified that the valves met isolation time requirements. This event was caused by cognitive personnel error on the part of the utility individual determining the retests for the CHCS CIV relay replacements; the individual failed to adequately implement the requirements of PDP-ZZ-00011, "Retest Development". The applicable requirements have been discussed with the individual involved. This event will be reviewed with Planning Department personnel responsible for determining retests. The administrative program for identifying retests has been improved since the events occurred. Review of the retest program has determined that additional changes are not needed.
4831997003 | Callaway | 03/31/1997 | 04/28/1997 | 9705050003 | <strong>Tech Spec Table 3.3-3 Violation Due To Error In The Tech Spec Description for Turbine-Driven Auxiliary Feedwater Start Logic</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 3/31/97, a Utility Quality Assurance audit determined the 'Channels to Trip' description in Technical Specification (T/S) Table 3.3-3, 'Engineered Safety Features Actuation System Instrumentation' for starting the Turbine-Driven Auxiliary Feedwater Pump (TDAFP) on low-low Steam Generator (S/G) water level did not accurately describe plant design. The error in T/S Table 3.3-3 described the channels to trip as '2/stm. gen. in any operating stm. gen.' implying the TDAFP should automatically start on low-low level in any single S/G The table should read '2/stm. gen. in any 2 operating stm. gen.' since the TDAFP automatically starts on low-low level in any two S/Gs. On 3/31/97, at 1500, the TDAFP was declared inoperable and T/S 3.7.1.2, Action a was entered. All S/G level channels and the Motor-Driven AFPs were verified to be operable. The situation was discussed with the NRC and an emergency T/S amendment was requested per 10 CFR 5 0.91 (a)(5) to correct the T/S table. Approval was received on 4/2/97 and the TDAFP was declared operable at 1142 on 4/2/97. The inaccurate T/S table constitutes a condition prohibited by T/S and is reportable per 10 CFR 50.73 (a)(2)(i)(B). The plant was in Mode 1 at 100% power. The error was introduced when the Utility incorporated a design change to the S/G trip circuitry, developed by Westinghouse, into the T/S. The Utility did not identify the error in the updated T/S markups supplied for inclusion into the license amendment. implemented since the time this error occurred which provide increased assurance this type of error is not repeated.
4831997004 | Callaway | 04/04/1997 | 05/05/1997 | 9705130389 | <strong>MISSED TECHNICAL SPECIFICATION 4.3.2.1 TURBINE AND FEEDWATER PUMP TRIP SLAVE RELAY SURVEILLANCE DUE TO COGNITIVE PERSONNEL ERROR</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On 4/4/97 a Quality Assurance engineer discovered the Technical Specification (T/S) 4.3.2.1, Table 4.3-2-5a, Table Notation (3) slave relay test for Turbine and Feedwater Pump Trip Slave Relay K620 had not been performed each COLD SHUTDOWN exceeding 24 hours on one occasion. On 4/17/97, during a review of historical surveillance documents associated with T/S 4.3.2.1, utility engineers discovered the above referenced slave relay test for K620 and Containment Isolation System Phase 'A' Slave Relay K630 had been performed in Mode 1 versus refueling on several occasions. These events are being reported in accordance with 10CFR50.73 (a)(2)(i)(B). The cause of the missed K620 surveillance during the October 1995 shutdown is cognitive personnel error. The responsible individual initiated work authorizing documents without the proper conditional note. The decision not to perform the referenced K620 and K630 slave relay surveillance during 'refueling' was based on the assumption that since the surveillances had been performed in the previous 90 days, they were current and need not be repeated during the refuel outage. Work authorizing documents for the associated surveillances have been modified to ensure future T/S compliance. The responsible individuals were counseled on the importance of reviewing associated T/S surveillance requirements when revising implementing surveillance procedures.
4831997005 | Callaway | 06/04/1997 | 01/15/1998 | 9801280062 | <strong>Missed Technical Specifications 4.3.2.1 Emergency Safety Features Actuation System Missed Surveillance Due to Inadequate System Design and Inadequate Test Procedure</strong><br /><i>Abstract:&nbsp;</i>Technical Specifications (T/S) 4.3.2.1, Table 4.3-2 item 11.a requires a quarterly Analog Channel Operability Test (ACOT) of Engineered Safety Feature Actuation System (ESFAS) Pressurizer Pressure permissive, P-11. On 6/4/97, Utility Engineers (UE) found surveillance procedures did not fully meet the intent of the ACOT when performed in Mode 3 greater than 1970 psig or Modes 1 and 2. P-11 was declared inoperable. P-11 channel bistable lights were verified to be in the correct status. On 6/7/97, P-11 was restored following test completion. This event was caused by inadequate system design. Observation of a change in the status of the bistable has not been considered a requirement for successful test completion Procedures will be revised to incorporate a method proving overlap exists. Circuit cards will be reconfigured to allow acceptable ACOT of the P-11 interlock. Additional Technical Specification testing deficiencies were identified during the comprehensive Technical Specification testing program review required per NRC GL 96-01 and were reported as items 1-8.
4831997006 | Callaway | 07/19/1997 | 08/18/1997 | 9708220265 | <strong>Loss of Annunciators and Unusual Event Declaration Due to Lightning Strikes</strong><br /><i>Abstract:&nbsp;</i>On 7/19/97, at approximately 1600 CDT, two lightning strikes occurred in the Callaway Plant water treatment facility resulting in degraded field power supply voltages and a loss of several Main Control Board (MCB) annunciators. At approximately 1625, utility Instrument and Control (I&C) technicians discovered smoking connector cards in computer multiplexer cabinet RK045D1, rack M-7 and de-energized the rack, thus returning most MCB annunciators to a functional status. At approximately 2230 CDT, utility engineers determined that although the power supplies had not failed during the subject 25-minute period, it could not positively be determined that the majority of MCB annunciators had been functional from 1600 to 1625. Notification was made that conditions had existed between 1600 and 1625 which placed Callaway Plant in an Unusual Event. This report is being made voluntarily to address the root cause and corrective actions for a declared Unusual Event. The cause of the post event emergency declaration was inadequate procedural guidance. The utility Nuclear Engineering department will perform a comprehensive system design review to identify probable failure modes and potential design enhancements. Applicable procedures have been revised to more clearly define criteria for a "failed" power supply. Integrated training will be conducted on this event with utility personnel.
4831997007 | Callaway | 07/25/1997 | 07/25/1997 | 9709030004 | <strong>Main Steam Safety Valve Setpoint Drift Outside Design Basis Requirements</strong><br /><i>Abstract:&nbsp;</i>A review of Main Steam Safety Valve (MSSV) test data for Technical Specification (T/S) 4.6.1.1 and 4.0.5 tests conducted 3/22/95 to 3/24/95 indicates that 14 MSSVs were outside of the +/-1% lift setting tolerance allowed by T/S 3.7.1.1. In addition, it was determined that 4 of these valves were outside previously analyzed limits and 2 of the Main Steam Lines (MSLs) had more than 3 MSSVs outside of their +/-1% lift setting tolerance. A review of MSSV test data for Refuel 1 from 2/86 indicates 11 MSSVs were outside the T/S tolerance and 1 of the MSLs had greater than 3 MSSVs inoperable. A review of MSSV test data for Refuel 6 from 9/93 indicates 10 MSSVs were outside of the T/S tolerance and 1 MSL had greater than 3 MSSVs inoperable. The cause of the conditions found in 2/86 and 3/95 is believed to be setpoint drift or variance attributable to disc to seat surface adhesion. The cause of the condition found in 9/93 is believed to have been a decision to set the valves low in the tolerance band to compensate for the above referenced seat surface adhesion. In each case, the valves either tested satisfactorily during subsequent tests allowed by ASME guidance, were reset within the T/S required tolerance, or were reworked. In addition, an Operating License Amendment is being pursued to change the as found setpoint tolerance from (+/- 1%) to (+3 %,-1%).
4831997008 | Callaway | 09/09/1997 | 10/02/1997 | 9710080029 | <strong>A Senior Reactor Operator Was Not Present in The Main Control Room During Mode 1 Operations Contrary to Technical Specification 6.2.2.b Due to Personnel Error.</strong><br /><i>Abstract:&nbsp;</i>On 9/9/97, at 0116, the Field Supervisor (FS) left the Control Room (CR) before realizing that he had been the only licensed Senior Reactor Operator (SRO) left in the CR. The event is reportable per 10CFR50.73(a)(2)(i)(B) as an operation prohibited by Technical Specification 6.2.2.b which requires one licensed SRO be in the CR while the plant is in Modes 1, 2, 3, or 4. Additionally, this was a violation of 10CFR50.54(m)(2)(iii). The plant was in Mode 1 at 70 % power at the time of the event. There are normally two SROs assigned to the CR. The Control Room Supervisor (CRS) informed the FS that he was going to his locker to get a procedure for the FS to review. Subsequently, the FS exited the CR. The CRS left the CR at 0115. The FS left the CR at 0116. When the FS was in the hallway, he saw the CRS coming down the hall and realized that he had been the only SRO in the CR. He immediately badged back into the CR and notified the SS of the occurrence. The total time the FS was out of the CR was 13 seconds. The root cause of the event was a lack of effective communication between the CRS and FS. Corrective actions include: reminding Operations personnel of the need for formal communication, the establishment of a physical barrier used in conjunction with the security badge to prevent inadvertent CR exit and reviewing the event with Operations personnel in training.
4831997009 | Callaway | 10/14/1997 | 11/13/1997 | 9711180010 | <strong>High Head Safety Injection Pump Casings Were Not Being Vented Contrary to Technical Specification 4.5.2.b.1</strong><br /><i>Abstract:&nbsp;</i>At 1000 CST, on 10/14/97, with the Plant in Mode 1, at 70% power, Utility Engineers (UE) determined that Callaway Plant had not complied with the Technical Specification 4.5.2.b.1 requirement for venting the pump casings of the High Head Safety Injection (HHSI) Pumps (1)_/ since Plant startup. Technical Specification 4.0.3 was entered at 1000, on 10/14/97. Since the HHSI Pumps do not have pump casing vents, Utility Engineers (UE) performed an evaluation to determine the adequacy of the existing flushing connections off the discharge piping of the HHSI Pumps to vent the pump discharge piping - the pumps were already vented due their self-venting design. The evaluation determined that complete venting of the piping was not possible due to the piping configuration; however, the maximum possible void in the piping from this venting was bounded by a previous Westinghouse analysis. The HHSI Pumps were then vented using the flushing connections off the discharge piping of the pumps. Venting of the 'A' HHSI Pump completed at 1856, on 10/14/97. Venting of the 'B' HHSI System was completed at 2029, on 10/14/97. A plant modification is being implemented to add a vent line off the HHSI Pumps discharge piping to enhance the required venting of the pump casings. Upon completion of the vent installation, the surveillance procedure that vents the HHSI Pumps will be revised to use these new vent lines.
4831997010 | Callaway | 11/18/1997 | 12/15/1997 | 9801050385 | <strong>Inadequate Testing of Solid State Protection System (SSPS)</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 4.3.2.1-5.a requires a monthly actuation logic test of the Feedwater Isolation and Turbine Trip instrumentation. At 0830 CST, on 11/18/97, Callaway Plant Utility Engineers, reviewing a testing deficiency discovered at another nuclear plant, determined that Callaway Plant was not adequately testing certain logic circuits of the Westinghouse Solid State Protection System 1_/ (SSPS) in accordance with Technical Specification 4.3.2.1-5.a. There are three functions which are inadequately tested: Source Range Automatic P-10 Block, Feedwater Isolation on P-14 Steam Generator Hi-Hi Level, and Feedwater Isolation on a Safety Injection signal. The circuits affected by this concern are memory circuits which have multiple inputs jumpered together. In these circuits, the testing configuration results in an inconclusive determination of the operability of each input. Technical Specification 4.0.3 was entered at 0830 CST on 11/18/97. Work instructions were written to test the affected logic circuits of the SSPS and were performed with satisfactory test results. This testing was completed and Technical Specification 4.0.3 was exited at 1840 on 11/18/97. The SSPS surveillance procedures are being revised to adequately test the affected logic circuits of the SSPS.
4831997011 | Callaway | 10/29/1997 | 12/30/1997 | 9801060335 | <strong>Failure to Enter Technical Specification Action Statement 3.8.1.1.b During "A" Train Emergency Diesel Generator Heat Exchanger Test</strong><br /><i>Abstract:&nbsp;</i>At approximately 1430 CST, on 10/29/97, with the plant in Mode 1, it was discovered that a temporary differential pressure gauge was installed and valved-in on the Essential Service Water 1_/ (ESW) side of the "A" Train Emergency Diesel Generator 2_/ (EDG) Heat Exchangers. This differential pressure gauge had been installed on 10/28/97, at 2140, to support a performance test of the EDG Heat Exchangers. Since the test connection isolation valves are the seismic boundary for the ESW system, an engineering determination was subsequently performed and it was determined that the EDG should have been considered inoperable as a result of this test configuration (isolation valves open and unattended) and the appropriate actions from Technical Specification 3.8.1.1.b should have been performed. The differential pressure gauge was removed and the system test connections and valves were restored to their normal positions on 10/29/97, at approximately 1546. Temporary instructions were issued on 12/5/97 instructing the Shift Supervisor or designee that under no cicumstances should a temporary gauge be left valved in and unattended. Additionally, Preventive maintenance work instructions that require manipulation of plant equipment, including temporary instrumentation, without declaring the system/component inoperable are being evaluated to determine if there are any operability concerns associated with the activity. If any operability concerns are found, the work document will be revised to require the system/component to be declared inoperable while the component is out of its normal position or unattended.
4981997001 | South Texas 1, South Texas 2 | 01/16/1997 | 09/25/1997 | 9709300387 | <strong>Failure to fully meet the requirements of Technical Specification Surveillance Requirement 4.7.13 for ensuring monitored areas meet their temperature limits.</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1997 Unit 1 and Unit 2 were operating in Mode 1 at 100% power. An engineering evaluation determined the temperature switches used for area temperature monitoring to meet Technical Specification Surveillance Requirement 4.7.13 had incorrect tolerances such that the temperature limits of the areas monitored could have been exceeded without detection. Station programs have been strengthened over the years to detect, evaluate and correct instrument reliability problems. The review process required by these programs led to the discovery of the incorrect tolerances used in setting the temperature switch alarm setpoints. The cause of this occurrence was the supplier of the temperature switches used to meet Technical Specification Surveillance Requirement 4.7.13 provided the incorrect repeatability value and other factors affecting instrument uncertainty were not applied resulting in a non-conservative accuracy value used in determining the switch setpoint. Corrective actions include action taken to monitor area temperatures locally to meet technical specification surveillance requirements, application of a more rigorous Design Criteria for Instrument Loop Uncertainty and Setpoint Methodology for use in establishing instrument setpoint and scaling values, and an evaluation of setpoints for switches of similar type provided by the same supplier and used in other plant applications. e:\wp\nl\nrc-wk\LER-97\5703.wpw
4981997002 | South Texas 1, South Texas 2 | 01/15/1997 | 02/13/1997 | 9702210020 | <strong>Safety Injection System Logic Circuitry Not Fully Tested by Surveillance Procedures</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On January 15, 1997, both units were operating at 100 percent power. During a review of surveillance procedures in accordance with Generic Letter 96-01 and associated NRC clarifications, it was found that the quarterly actuation logic test for 'Automatic Switchover to Containment Sump' (Technical Specification 4.3.2.1, Table 4.3-2, Item 7.a) did not appear to have been satisfied. An operability/reportability review determined that the surveillance procedures were not fully satisfying the testing requirements. The cause of inadequate surveillance procedures was an unusual logic arrangement which was not recognized as being within the scope of the requirements for an actuation logic test. Corrective actions include testing the affected logic circuitry, reviewing similar actuation logic circuitry for other occurrences, revising the affected surveillance procedures, and completing the surveillance procedure review required by NRC Generic Letter 96-01
4981997003 | South Texas 1, South Texas 2 | 01/23/1997 | 02/24/1997 | 9703040049 | <strong>Liquid Waste Processing System line on each unit potentially susceptible to thermal expansion of fluid with resultant piping overpressurization</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. During an evaluation in response to Generic Letter 96-06, 'Assurance of Equipment Operability and Containment Integrity During Design-Basis Accident Conditions,' an engineering review identified a 3-inch Liquid Waste Processing System line on each unit that could potentially be susceptible to thermal expansion of fluid with resultant piping overpressurization in the event of a design-basis accident. Lines 3'WL-1009 (Unit 1) and 3'WL-2009 (Unit 2) are used to drain the Reactor Coolant Drain Tank to the Liquid Waste Processing System. Conservative analysis of the uninsulated line identified a potential overpressurization condition during a design basis accident that could result in piping stresses exceeding ASME Code allowable limits. To ensure that overpressurization of this piping would not occur, the affected section of the line was drained. Additional analysis showed that piping stress allowable limits would not be exceeded if the line were insulated. Subsequently, a design change installed insulation on the piping and the line was returned to service. No loss of containment integrity would have occurred as a result of this condition. The potential condition was reported in accordance with 10CFR50.72(b)(1)(ii) on January 23, 1997. This potential condition is also reportable accordance with 10CFR50.73(a)(2)(ii)(B), condition outside the design basis of the plant.
4981997004 | South Texas 1, South Texas 2 | 03/19/1997 | 04/17/1997 | 9704220364 | <strong>4160 Volt Bus Undervoltage Logic Circuitry Not Fully Tested by Surveillance Procedures</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 19, 1997, both units were operating at 100 percent power. During a review of surveillance procedures against Nuclear Regulatory Commission (NRC) Generic Letter 96-01 and associated NRC clarifications, the reviewer found that the surveillance testing for the 4160 volt Sustained Degraded Voltage and the Degraded Voltage Coincident with Safety Injection did not adequately test all logic contacts to fully meet the surveillance requirements (Technical Specification 4.3.2.1, Table 4.3-2, Items 8.b and 8.c). The cause of inadequate surveillance procedures was not recognizing that a failure in one actuation scheme could affect the ability to detect a failure in a parallel scheme. Corrective actions include testing the affected logic circuitry, revising the affected surveillance procedures, and completing the surveillance procedure review specified in NRC Generic Letter 96-01.
4981997005 | South Texas 1, South Texas 2 | 04/02/1997 | 05/01/1997 | 9705060278 | <strong>Main Steam Safety Valve Setpoints Discovered Outside Required Tolerance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 098%. On April 2, 1997, Unit 1 was in Mode 1 at 98% power. On April 21, 1997, Unit 2 was in Mode 1 at 98% power. Main Steam Safety Valve Inservice Testing was being performed in the respective units as part of a corrective action plan established following Unit 2 Main Steam Safety Valve testing in early February, 1997 and reported in South Texas Project Unit 2 Licensee Event Report 97-001. During the Unit 1 testing performed on April 2 and 3, 1997 and during the Unit 2 testing performed on April 21 and 22, 1997, two of twenty Main Steam Safety Valves tested in each unit were found with lift settings outside the Technical Specification allowable tolerance of +/- 3%. The lift settings were adjusted to within their required allowable tolerances. The remaining eighteen Main Steam Safety Valves in each unit were tested satisfactorily. The most probable cause of the high initial lift results of the Main Steam Safety Valves is an alteration of the nozzle seat and disc seat oxide layers. In addition to consideration of further testing and preconditioning lifting, South Texas is actively pursuing other activities to resolve this issue. Some activities being considered are evaluation of improved valve seat preconditioning techniques, evaluation of use of alternate valve disc materials and evaluation of metallurgical testing of valve discs.
4981997006 | South Texas 1, South Texas 2 | 05/08/1997 | 04/09/1998 | 9804220155 | <strong>Inappropriate Surveillance Procedure Monitoring Parameters</strong><br /><i>Abstract:&nbsp;</i>On May 7, 1997, Units 1 and 2 were operating at 100% power. During a review of requirements for controlling Reactor Coolant System average temperature at full power, a surveillance procedure was found to be inconsistent with Technical Specification surveillance requirements. Average temperature and pressurizer pressure limits for protection against departure from nucleate boiling used in the Operator Log surveillance procedure, which are required to be verified per Technical Specification surveillance requirement 4.2.5.1, did not take into account measurement instrument uncertainties. The concern is that these parameters were not being accurately monitored as required by Technical Specification surveillance requirements. This error in the Operator Log surveillance procedure resulted from a less than adequate review of changes to the Technical Specifications and Bases. The Operator Log surveillance procedure has been revised to include instrument uncertainty. Further review found no operability or reportability concerns associated with this issue for other Technical Specification surveillance requirements. However, additional historical review determined that measurement instrument uncertainties had not been properly considered for Reactor Coolant System average temperature and pressurizer pressure since issuance of the Unit 1 operating license. SHELLS\LER.RPT 04/07/98 (1:23PM)
4981997007 | South Texas 1, South Texas 2 | 06/19/1997 | 07/21/1997 | 9707250128 | <strong>Engineered Safety Features Actuation System Pressurizer Pressure System Interlock Not Fully Tested by Surveillance Procedures.</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1997, Units 1 and 2 were operating at 100% power. A determination was made that Technical Specification 4.3.2.1, Table 4.3-2 item 9a, which requires a quarterly Analog Channel Operability Test of Engineered Safety Features Actuation System Pressurizer Pressure Permissive P-11, had not been met. A review of an Operating Experience Report determined that the South Texas Project does not adequately test the P-11 function when in MODE 3 greater than 1985 psig or in MODEs 1 and 2. P-11 was declared inoperable and the channel permissive annunciator window indications were verified to be in the correct status for the existing plant Conditions as required by Technical Specifications Table 3.3-3 Functional Unit 9.a. action 21. The cause of this event was a failure to recognize that the testing circuitry did not include a necessary channel bistable light change when performing the Analog Channel pressures greater than 1985 psig. Observation of a change in the status of the considered a requirement for successful test completion. Procedures that test P-11 will be revised to incorporate a method for testing the entire circuit in all plant conditions. e:\wp\nl\nrc-wk\LER5694\wpw
4981997008 | South Texas 1, South Texas 2 | 08/11/1997 | 09/10/1997 | 9709170164 | <strong>Engineered Safety Features Containment Spray Actuation Relays Slave Relay Test Not Fully Tested by Surveillance</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1997, Units 1 and 2 were operating at 100% power. The Containment Spray engineered safety features system actuation logic was being reviewed against surveillance test procedures as requested in Nuclear Regulatory Commission Generic Letter 96-01, "Testing of Safety-Related Logic Circuits". During this review, it was determined that the requirements of Technical Specification Surveillance Requirement 4.3.2.1, Table 4.3-2, Item 2.c.7, "Containment Spray Actuation Relays Slave Relay Test", had not been met. Specifically, the implementing surveillance procedures did not test the Containment Spray Pump circuit breaker. Credit for running the Containment Spray Pump and testing the circuit breaker continuity had been taken during the quarterly inservice testing of the Containment Spray Pumps. The Containment Spray Pump inservice testing frequency was revised in mid 1994 without determining the effect of the change on the Containment Spray Actuation Relays Slave Relay Test requirements. The cause of this occurrence was a failure to fully understand the expectations regarding documentation of procedures to indicate when the procedure is used to partially satisfy technical specification surveillance requirements. Corrective actions include verification of the Containment Spray Pump operability, completion of surveillance test credit packages, generation of new surveillance tests to document the completion of the entire circuit continuity of the Containment Spray Actuation Relays Slave Relay Test, and training on lessons learned for surveillance procedure writers. e:\wp\nl\nrc-wk\LER_97\5740.wpw
4981997009 | South Texas 1, South Texas 2 | 09/02/1997 | 01/15/1999 | 9901260460 | <strong>Main Steam Safety Valve Setpoints Found Outside Required Tolerance</strong><br /><i>Abstract:&nbsp;</i>South Texas Project has previously submitted Unit 1 LER 97-005, LER 97-009, LER 97-009, Revision 1, and Unit 2 LER 97-001 with regards to the main steam safety valves testing outside lift tolerances due to a sticking phenomenon. This revision (Revision 2) submits our current position on this issue. South Texas Project's latest findings indicate the phenomenon is due to locking caused by hydraulic, oxide, or microbonding; material incompatibility; and maintenance activities. Corrective actions to resolve the main steam safety valve initial high lift phenomenon will include opening, inspecting, and refurbishing valves in Unit 1 that have had maintenance previously performed on the valves with the new preoxidized Inconel X750 discs and satisfactorily testing the reworked valves. A plan of action for the Unit 2 valves will be finalized by Unit 2's fall 1999 outage scope freeze. An effectiveness review will be performed to validate the corrective actions. In addition, South Texas Project will solicit collaboration from a users group sponsored by EPRI. e:\wp\nl\nrc-wk\ler-97\0149.doc
4981997010 | South Texas 1 | 09/20/1997 | 08/18/1998 | 9808240041 | <strong>Main Steam Safety Valve Discovered Not Meeting Required Relief Capacity</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1997, Unit 1 was in Mode 6 conducting refueling operations. During refurbishment of Main Steam Safety Valves 7430A and 7430B, it was found that each valve was previously set to a condition that did not compensate for thermal growth such that each valve would only pass approximately 93% of its required relief capacity. This condition resulted in an effective valve orifice size less than that specified in Technical Specification Table 3.7-2 for ensuring specified relief capacity is met. This condition was determined to have existed since the previous Unit 1 sixth refueling outage conducted in 1996 when maintenance was performed on these valves. The cause of this event was inadequate resolution of issues regarding valve reassembly during the Unit 1 sixth refueling outage. The issues involved a less than adequate questioning attitude regarding confusing requirements in the valve reassembly work procedure. Corrective actions include procedure revision, correct lift setting adjustment to the affected valves, and lesson learned training for Maintenance personnel. E:\wp\nl\nrc-wk\ler-97\0257.doc
4981997011 | South Texas 1 | 10/21/1997 | 11/20/1997 | 9711260106 | <strong>Pressurizer Safety Valve setpoints discovered outside required tolerances</strong><br /><i>Abstract:&nbsp;</i>On October 20 and 21, 1997, Unit 1 was in Mode 1 at 100% power following the unit's seventh refueling outage. Two of the three Unit 1 Pressurizer Safety Valves shipped to Wyle Laboratories for setpoint verification testing were found outside Technical Specification 3.4.2.2 required tolerance of +/- 2%. The valves were set to the required Technical Specification setpoint of 2485 psig +/- 1% prior to their initial installation in Unit 1 during the unit's sixth refueling outage. The remaining Pressurizer Safety Valve, PSV-3451, tested within the required Technical Specification 3.4.2.2 tolerance. The Pressurizer Safety Valves that had been removed during the Unit 1 seventh refueling outage for factory testing had been replaced during the refueling outage. The replacement Pressurizer Safety Valves which are currently installed in Unit 1 were set to the Technical Specification as left lift setting tolerance of +/- 1% prior to their installation. The observed setpoint drift on the South Texas Project Pressurizer Safety Valves is apparently the result of the inherent valve characteristics (i.e., the massive spring assembly). The setpoint drift of these components is a widely known industry problem. The two Pressurizer Safety Valves were adjusted to within their required allowable tolerance lift settings as corrective action. c:\wp\nl\nrc-wk\ler-97\0018.wpw STI: 30477293
4981997012 | South Texas 1 | 11/10/1997 | 12/10/1997 | 9712160392 | <strong>Reactor trip due to overtemperature/delta temperature actuation.</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1997, Unit 1 was in Mode 1 at 100% power. At approximately 1701 hours, an Overspeed Protection Control solenoid for the Unit 1 Main Turbine momentarily energized resulting in the closing and opening of the Main Turbine governor valves. This valve response was followed by a secondary system transient and oscillating Steam Generator levels. The oscillating Steam Generator levels resulted in main feedwater flow oscillation and deviations between steam flow and feedwater flow. The secondary system transient was reflected in the primary system as an increase in average Reactor Coolant System temperature. An automatic Reactor trip occurred on two of four Over Temperature/Delta Temperature signals to the Solid State Protection System. A Main Turbine trip followed the Reactor trip. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. During the response to the Reactor trip, the Engineered Safeguards Features System actuated the Auxiliary Feedwater System during the transition of Main Steam Dump system modes when Steam Generator levels momentarily dropped below the LOW-LOW level setpoint. The cause of the Reactor trip was the momentary energization of the Overspeed Protection Control solenoid due to failure of a solid state relay in the control circuitry. It was determined that the solid state relay was redundant and not required for the Overspeed Protection Control circuit to perform its function. Corrective actions included removal of the redundant solid state relay from both the Unit 1 and 2 Main Turbine Overspeed Protection Control circuits. STI: 30489212
4981997013 | South Texas 1, South Texas 2 | 11/11/1997 | 04/16/1998 | 9804220356 | <strong>Failure to meet the Technical Specification leak rate requirements for a Supplementary Containment Purge Supply Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1997, Unit 1 was in Mode 3. On November 11, 1997, a determination was made that containment penetration M-43, a Unit 1 Supplementary Containment Purge Supply Isolation Valve, exceeded the allowed Technical Specification leak rate on September 22, 1997. This condition existed without taking the required Technical Specification action for an inoperable Supplementary Containment Purge Supply Isolation Valve until October 30, 1997 when the penetration was retested and found within Technical Specification leak rate allowances. An evaluation determined that the methodology used to calibrate the flow measuring devices used in Local Leak Rate Testing was non-conservative. After applying conservative calibration correction factors, it was determined that current containment leak rate test results meet Technical Specification requirements. The cause of this occurrence was an inadequate process for developing measuring and test equipment calibration specifications. Corrective actions include ensuring all future local leakage testing is performed using leak rate measuring devices calibrated in accordance with required standards, evaluation of training to be performed on lessons learned from this event, and revising plant procedures to require end user review prior to implementation of new or revised calibration specification sheets. e:\wp\nl\nrc-ap\ler-98\0121,doc STI: 30579123
4991997001 | South Texas 2 | 02/05/1997 | 03/06/1997 | 9703120363 | <strong>Main Steam Safety Valve Setpoints Discovered Outside Required Tolerance</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 093%. On February 3, 1997, Unit 2 was in Mode 1 at 93% power conducting power ramp down operations in preparation for the Unit's fifth refueling outage. During the performance of the Main Steam Safety Valve Inservice Test, a Main Steam Safety Valve was found with its lift setting outside the Technical Specification allowable tolerance of +/- 3%. The test sample was expanded in accordance with ASME requirements. Upon testing completion on February 5, 1997, five of twenty Main Steam Safety Valves were found with the lift settings outside Technical Specification tolerances. The most probable cause of the high initial lift results of the Main Steam Safety Valves above and beyond previously documented setpoint drift is an alteration of the seat and disc oxide layers. Over time this mechanism tends to promote oxide locking and galling with subsequent bonding between the valve seat and disc. Corrective action included adjusting the lift settings to within their required allowable tolerances and inspecting two disassembled Main Steam Safety Valves found with the lift settings outside the allowable tolerance for root cause. South Texas Project plans to continue to actively participate with the industry in resolving the safety valve sticking issue.
4991997002 | South Texas 2 | 02/15/1997 | 03/13/1997 | 9703180257 | <strong>Steam Generators Classified as Category C-3</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 15, 1997, South Texas Project Unit 2 steam generator 2A eddy current inspection results fell into Category C-3 and the NRC was notified within four hours pursuant to 10CFR50.72(b)(2) and Technical Specification Table 4.4-2. Additionally, on February 17 and February 18, 1997, the inspection results for steam generators 2B, 2D, and 2C fell into Category C-3 and the NRC was notified within the required time. Eddy current inspections were conducted on 100% of in-service tubes on all four Unit 2 steam generators. As a result of these inspections, a total of 601 steam generator tubes were plugged in the four Unit 2 steam generators. All but 20 of the 601 tubes plugged were the result of outside diameter stress corrosion cracking at tube-to-tube support plate intersections. The cause may be summarized as improper selection of tube material and improper design of the tube-to-tube support plate intersection locations. A contributing factor is the high reactor coolant system hot leg temperature design values. South Texas will evaluate submitting a license amendment for application of the voltage-based repair criteria to Unit 2 per Generic Letter 95-05. For subsequent steam generator eddy current inspections on the currently installed generators conducted to satisfy Technical Specification surveillance requirements, the first sample will be a 100% bobbin examination of the full length of all in-service tubes.
4991997003 | South Texas 2 | 02/24/1997 | 04/28/1997 | 9705060363 | <strong>Failure to meet the requirements of Technical Specification 4.5.2.c regarding surveillance inspection of containment for loose debris.</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 000%. On February 24, 1997, Unit 2 was in Mode 3 following core refueling. It was determined that Technical Specification Surveillance Requirement 4.5.2.c, as defined in the Surveillance procedure, was not met when loose debris was discovered in the Reactor Containment Building. Additional discoveries of miscellaneous small items of loose debris were made on March 27, 1997 during numerous walk-downs following a reactor trip. All of the items discovered were immediately removed. The types of items discovered and the locations in which they were discovered are consistent with activities that were performed during the previous outage period. Based on this, these most recent discoveries are associated with the previous event. The corrective actions associated with the previous event are still ongoing and, when combined with the additional corrective action in this supplement, will prevent this type of event in the future. Evaluations performed for the previous discovery and these subsequent discoveries have determined that the Emergency Core Cooling System would not have been compromised during a design bases event with these items in containment. In all cases the Emergency Core Cooling System was operable.
4991997004 | South Texas 2 | 03/19/1997 | 04/17/1997 | 9704240017 | <strong>Unit trip During turbine testing</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 19, 1997, Unit 2 was in Mode 1 at 100% power. At approximately 1555 hours while performing main turbine testing, a unit trip occurred. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. All safety equipment operated as designed for a normal reactor trip. During post-maintenance testing on the Unit 2 Main Turbine Emergency Trip System, a condition developed that resulted in low Electro-Hydraulic Control System pressure causing a rapid closure of the main turbine throttle stop valves. The closure of the main turbine throttle stop valves resulted in a reactor trip followed by a main turbine trip. The cause of this occurrence was the intermittent failure of the inverter power supply for the channel two Automatic Stop Trip valve in the Electro-Hydraulic Control System. The inverter power supply was replaced and the condition of the other three inverters in the Electro-Hydraulic Control System were assessed and all were found to be in satisfactory condition.
4991997005 | South Texas 2 | 03/26/1997 | 04/24/1997 | 9704300253 | <strong>Manual unit trip due to lowering Steam Generator level</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 26, 1997, Unit 2 was in Mode 1 at 100% power. At approximately 2146 hours, a 2B Steam Generator feed flow/steam flow mismatch alarm was received. The 2B Main Feedwater Regulating Valve was discovered not responding in the automatic mode of control. After attempts to manually control the 2B Main Feedwater Regulating Valve were unsuccessful and with 2B Steam Generator level decreasing towards the automatic trip setpoint, Unit 2 reactor was manually tripped at 2147 hours. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. All safety equipment operated as designed for a normal reactor trip. Subsequent troubleshooting determined that the cause of this occurrence was the failure of a seal-in relay for one of the two solenoid controlled air valves used to operate the 2B Main Feedwater Regulating Valve. seal-in relay and verifying other seal-in relays affecting Main Feedwater Regulating Valves in both Unit 1 and 2 had proper coil resistances.
4991997006 | South Texas 2 | 04/30/1997 | 05/29/1997 | 9706050247 | <strong>Manual Reactor Trip due to Malfunctioning Main Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On April 30, 1997, Unit 2 was operating at 100% power in Mode 1. At approximately 2150 hours on April 30, 1997, feedwater flow oscillation to the 2D Steam Generator was observed. Attempts to manually control 2D Main Feedwater Regulating Valve resulted in erratic response. With 2D Steam Generator level at 35% and decreasing, the reactor was manually tripped at 2158 hours on April 30, 1997. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. All safety equipment operated as designed. The cause of this occurrence was a failure of two integrated circuits in the 2D Main Feedwater Regulating Valve automatic control circuit and a hairline crack in the solder run leading to a resistor in the manual control circuit. Corrective actions included replacing the 2D Main Feedwater Regulating Valve controller-driver card and testing the control circuit satisfactorily, and performing alignment checks of the Main Feedwater Regulating Valve controller-driver cards in each Unit 2 train prior to unit restart. e:\wp\n1\nrc-wk\LER-97\5650.wpw STI: 30279653
4991997007 | South Texas 2 | 11/21/1997 | 12/18/1997 | 9712220417 | <strong>Manual reactor trip due to a loss of inventory in Steam Generator 2D.</strong><br /><i>Abstract:&nbsp;</i>On November 21, 1997, Unit 2 was in Mode 1 at 100 percent power. At 0213 hours, multiple alarms were received the Unit 2 Control Room. The feedwater regulating valve to Steam Generator 2D was observed indicated closed Manual operation of the regulating valve electronic controls in the open direction was not effective. When Steam Generator 2D level approached 40 percent and decreasing, the reactor was manually tripped in accordance wit plant procedures. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected. Inspection of the 7300 system Process Control Cabinet 08, which provides control to the Steam Generator 2D feedwater regulating valve, determined a loss of power to the internal components of the cabinet existed. Troubleshooting determined a failed capacitor on the voltage to pulse converter circuit card had occurred and a capacitor mounting strap in the primary power supply had caused an internal short. It was determined that the fault protection design of the cabinet circuitry permitted a single circuit card capacitor failure to cause a loss of both the primary and secondary power supplies to the cabinet. The cause of the event was two separate failure mechanisms that combined to result in loss of power to the cabinet. Corrective actions include replacing the failed components associated with Process Control Cabinet 08, and initiation of evaluations to identify permanent modifications, as appropriate, to prevent failure recurrence. E:\wp\nl\nrc-ap\ler-97\0041.doc 12/18/97 (7:31AM)
5281997001 | Palo Verde 1 | 05/27/1997 | 06/19/1997 | 9707030068 | <strong>Reactor Trip Following Reactor Coolant Pump Load Shed from Non-Class 1E 13.8 kV Bus</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1997, at approximately 0034 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when an automatic reactor trip occurred on low departure from nucleate boiling ratio (DNBR) following the load shed of two reactor coolant pumps (RCP). The non-Class 1E 13.8 kV electrical bus (NAN-S01) performed a load shed of two of the four RCPs on an indicated undervoltage signal. The core protection calculator (CPC) generated a reactor trip on low DNBR due to low RCP speed. By approximately 0352 MST, the unit was stabilized in Mode 3 (HOT STANDBY) and the Shift Supervisor classified the event as an uncomplicated reactor trip. There were no engineered safety features (ESF) actuations and none were required. Required safety systems responded to the event as designed. The cause of the indicated undervoltage signal and subsequent load shed was attributed to a degraded fuse on the bus voltage potential transformer (PT). As corrective action, the fuse was replaced. NAN-S01's PT and connections were checked satisfactory. A transportability review was performed to check the remaining non-Class 1E 4.16 kV and 13.8 kV PT fuses in Unit 1 associated with load shedding and synchronizing. Similar fuses in Units 2 and 3 have been checked. A previous similar event was reported in LER 529/89-009-00.
5281997002 | Palo Verde 1 | 05/28/1997 | 07/07/1997 | 9707150361 | <strong>Surveillance Requirement for Core Protection Calculators not Performed due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On June 11 at approximately 1500 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION) operating at approximately 100 percent power when APS personnel identified that a Technical Specification (TS) Surveillance Requirement (SR) for Core Protection Calculators (CPC) (TS SR 4.3.1.5) was not performed during the unit restart on May 28, 1997. The TS violation was identified during a Nuclear Assurance Audit of Unit Operations, Technical Specifications, and License Conditions. A backend review of the SRs indicated that the CPCs were OPERATIONAL prior to and immediately following the event. A preliminary evaluation has determined that the apparent cause of the missed surveillance test was attributed to inadequate procedures. As corrective action, procedures have been revised to properly reflect the TS SR. No previous similar events have been reported pursuant to 10CFR50.73 in the last three years.
5281997003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 07/25/1997 | 08/25/1997 | 9709030203 | <strong>Construction Design Deficiency Resulted In Inadequate Protection Against Floodwater Migration</strong><br /><i>Abstract:&nbsp;</i>On July 25, 1997, at approximately 1200 MST, Palo Verde Units 1, 2, and 3 were in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when APS Engineering personnel identified that certain electrical conduit penetration fittings within safety related buildings had been in a condition which would have allowed the migration of flood water to other elevations and potentially render safety related equipment unable to perform its safety function. The cause of the condition was attributed to a construction design deficiency which did not consider the submergence characteristics of conduit fittings used for the penetrations. As corrective action, the fittings were sealed to prevent the migration of flood water to other elevations and equipment and appropriate drawings have been revised to provide for the current proper sealing of the penetration following maintenance, modifications, and new construction. No previous similar events have been reported pursuant to 10CFR50.73.
5281997004 | Palo Verde 1 | 09/25/1997 | 11/24/1997 | 9712010299 | <strong>Inverters for Class 1E 120 VAC Vital Buses not in Design Conformance</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1997, at approximately 1430 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel made appropriate Technical Specifications (TS) entries for two Class 1E 120 VAC vital instrument distribution buses (PNA-D25 and PNC-D27) being inoperable due to their associated inverters being non-seismically qualified. The inverters were missing seismic restraint clips on their cooling fan failure air flow alarm switches. At approximately 1705 MST, Control Room personnel exited TS following the installation of the restraint clips. On October 1, 1997, at approximately 1713 MST, Control Room personnel made TS entries for PNB-D26 and PND-D28 being inoperable due to their associated inverters being non-seismically qualified. The inverters were missing retaining nuts on the seismic restraint clips. At approximately 1758 MST, Control Room personnel exited TS following the installation of the retaining nuts. Based on investigation results, APS concluded that this event was attributed to an inadequate quality assurance program at Elgar Corporation which allowed the inverters to be manufactured and shipped without full design compliance. However, Elgar Corporation reviewed their shipping inspection records and noted no discrepancies concerning the restraint clips and retaining nuts. A seismic qualification evaluation subsequently determined that the inverters remained operable. The TS entries were retracted. Although the event does not meet the 10 CFR 50.73 reporting requirements, APS believes that the information provided in this voluntary LER might prove useful and be of generic interest to the nuclear industry.
5281997005 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/28/1997 | 12/22/1997 | 9712310097 | <strong>TS SR violation resulting from an inadequate procedural impact review of a TS amendment</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1997, at approximately 0500 MST, Palo Verde Units 1 and 3 were in Mode 1 (POWER OPERATION), operating at approximately 100 percent power and Unit 2 was in a refueling outage, with fuel off-loaded to the spent fuel pool, when Unit 3 Operations personnel discovered that the containment cleanliness inspection procedure did not appropriately implement Technical Specifications Surveillance Requirement (TS SR) 4.5.2.c.2 for daily containment debris inspection. On November 20, 1997, during an evaluation of the condition, Nuclear Regulatory Affairs personnel discovered that the TS SR for daily checks was not met in Unit 1 between May 27, 1997 and May 29, 1997 during containment entries when CONTAINMENT INTEGRITY was established. Therefore, the procedural discrepancy led to a reportable event under 10 CFR 50.73. A containment inspection was satisfactorily performed on May 29, 1997, prior to final containment closeout. The cause of the procedural discrepancy was attributed to an inadequate procedural impact review of a TS amendment approved on September 2, 1994. As corrective action, appropriate procedures were revised and additional TS changes were reviewed to verify proper procedural implementation. No previous similar events have been reported pursuant to 10CFR50.73.
5281997006 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 10/28/1997 | 02/05/1998 | 9802130064 | <strong>Missed TS 4.0.5 Surveillance requirement due to personnel error</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1997, Palo Verde Unit 2 was in Mode 3 (HOT STANDBY) when APS Engineering personnel discovered that the portions of the nuclear cooling (NC) system classified as ASME Code Class 3 had not received the periodic (3 1/2 year) pressure tests for Interval 1 Periods 1 and 2 as required by Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.9, Structural Integrity, and Surveillance Requirement (SR) 4.0.5. The omission was discovered during the performance of Unit 2's Interval 1 (10 year) ASME Section XI pressure testing. On October 28, 1997, applicable portions of Unit 2's NC system were satisfactorily pressure tested to meet the Interval 1 Period 3 requirements. On December 10, 1997, APS Engineering personnel determined that the same portions of the NC system in Units 1 and 3 had not received the Interval 1 Period 1 and 2 pressure tests as required by TS LCO 3.4.9 and TS SR 4.0.5. On December 10, 1997, applicable portions of Units 1 and 3's NC systems were satisfactorily pressure tested to meet the Interval 1 Period 3 requirements. A preliminary evaluation has determined that the apparent root cause is attributed to personnel error. The ISI pressure testing scope for Interval 1 Periods 1 and 2 was reviewed for all three units and concluded no systems within the ISI program scope other than NC were omitted. No previous similar events have been reported pursuant to 10CFR50.73.
5291997001 | Palo Verde 2 | 08/13/1997 | 09/10/1997 | 9709170295 | <strong>Single Main Steam Safety Valve Found Outside of TS Lift Setting</strong><br /><i>Abstract:&nbsp;</i>At approximately 0524 MST on August 13, 1997, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 85 percent power when Control Room personnel declared Steam Generator No. 2's main steam safety valve (MSSV) SGE-PSV-556 inoperable due to the as-found lift setting being greater than the 3 percent of the lift setting specified in Technical Specifications (TS) and entered TS 3.7.1.1 ACTION a. At approximately 0555 MST, the MSSV was declared operable after adjusting the lift setting within +/-1 percent of the TS lift setting and TS 3.7.1.1 ACTION a was exited. The provisions of TS 3.7.1.1 were met. Therefore, there was no condition prohibited by the plant's TS. MSSV SGE-PSV-556 was the only valve, out of twenty, determined to be outside of the lift settings specified in TS 3.7.1.1. A previous similar event was reported in LER 530/97-003-00 which describes a condition where seven MSSVs had as-found lift settings greater than the 3 percent of the lift settings specified in TS. An investigation associated with LER 530/97-003-00 is currently evaluating the cause of the MSSVs being outside of the TS lift settings.
5291997002 | Palo Verde 2 | 03/10/1997 | 04/07/1997 | 9704150078 | <strong>TS 3.0.3 Entry due to Non-compliance with TS 3.4.9 Structural Integrity for Charging Pump A</strong><br /><i>Abstract:&nbsp;</i>POWER LEVEL - 100%. On March 10, 1997, at approximately 0830 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.0.3 due to non-compliance with the structural integrity requirements of TS LCO 3.4.9 for an ASME Code Class 2 component. A small leak indicative of a cracked block had been discovered on charging pump A. The pump was isolated to comply with the requirements of TS LCO 3.4.9 ACTION b, and Control Room personnel exited TS LCO 3.0.3 at approximately 0900 MST. As corrective action, the charging pump block was replaced and Control Room personnel declared charging pump A operable at approximately 1630 MST on March 15, 1997. Following replacement, a visual inspection revealed a crack at the intersection connecting the number one plunger bore and its discharge check valve bore. Based on historical performance information, APS Engineering personnel determined that the most probable cause of the cracked pump block was high-cycle fatigue. A previous similar event was reported pursuant to 10CFR50.73 in LER 530/95-00100 and LER 530/94-004-00.
5291997003 | Palo Verde 2 | 09/07/1997 | 10/07/1997 | 9710150164 | <strong>Inadvertent Loss of Power and Emergency Diesel Generator Start Due to Procedural Error</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1997, at approximately 1923 MST, Palo Verde Unit 2 was in Mode 5 (COLD SHUTDOWN) in its seventh refueling outage when an inadvertent loss of power (LOP) of the Train B Class 1E 4160 V bus (PBB-S04) and a Train B emergency diesel generator (EDG-B) automatic start occurred during pretest staging for EDG-B and integrated safeguards (ISG) surveillance testing (ST) of the Train B LOP actuation. By approximately 1944 MST, PBB-S04 was restored to normal system lineup and EDG-B was stopped. This event is being reported because an engineered safety feature (EDG-B) actuation occurred during a preplanned test in a way that was not part of the planned procedure. The cause of the inadvertent line up was attributed to a procedural deficiency which caused Control Room personnel to close the alternate supply breaker (PBB-S04L) to PBB-S04 from the Control Room board as opposed to the local panel. This action caused the synchronizing switch interlock logic to automatically open the normal supply breaker (PBB-S04K) to PBB-S04 resulting in an inadvertent LOP of PBB-S04 and automatic start of EDG-B. All systems actuated as designed. There were no other ESF actuations and none were required. As corrective action, the EDG/ISG ST procedure was revised. No previous similar events have been reported pursuant to 10CFR50.73.
5291997004 | Palo Verde 2, Palo Verde 3 | 08/24/1997 | 09/19/1997 | 9709300314 | <strong>Missed Neutron Flux Power Daily Channel Checks Due to a Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>At approximately 2200 MST on August 24, 1997, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 76 percent power during a coast down into its seventh refueling outage, and Palo Verde Unit 3 was in Mode 1 operating at approximately 100 percent power, when Unit 2 Control Room personnel determined that incorrect acceptance criteria was used for the neutron flux power daily channel checks during periods of reduced power below 80 percent from August 21 through August 24, 1997. Following discovery, reactor power was surveilled and found to be in compliance with the appropriate acceptance criteria. A preliminary evaluation determined that the apparent root cause is attributed to a defective procedure that has been in effect since August 14, 1996. Therefore, the investigation team determined that, since August 14, 1996, incorrect acceptance criteria has been used in all three units for the neutron flux power daily channel checks during periods of reduced power below 80 percent. The investigation determined that this condition also resulted in a condition prohibited by Technical Specifications for Unit 3 on February 21, 1997 during periods of reduced power below 80 percent prior to its sixth refueling outage. Corrective actions included issuing a night order in all three units followed by a temporary procedural change pending a review and final modifications to the deficient procedure.
5291997005 | Palo Verde 2 | 09/23/1997 | 10/17/1997 | 9710300071 | <strong>Inadvertent Train B ESFAS Equipment Actuations and Emergency Diesel Generator Start Due to Component Failure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1139 MST on September 23, 1997, Palo Verde Unit 2 was in its seventh refueling outage with the core offloaded to the spent fuel pool when an inadvertent actuation of the Train B Engineered Safety Feature Actuation System (ESFAS) 1-3 leg equipment (e.g., valves with power available, control room essential air filtration unit, and essential chiller), the Train B Diverse Auxiliary Feedwater Actuation System (DAFAS), and an automatic start of the Train B emergency diesel generator (EDG-B) occurred during planned outage maintenance activities. ESF components are normally expected to actuate in the event of a full trip initiated by the plant protection system, not half-leg trips. By approximately 1459 MST on September 23, 1997, the Train B ESFAS half-leg trips and the Train B DAFAS trip were cleared, and EDG-B was stopped. Initial troubleshooting identified that an apparently non-detectable failed power supply in the Train B ESFAS cabinet caused the inadvertent Train B ESFAS 1-3 leg equipment to actuate, and the subsequent EDG-B start when combined with the outage-related deenergization of power to an auctioneered power supply. As corrective action, the faulty power supply was replaced. No previous similar events have been reported pursuant to 10CFR50.73.
5291997006 | Palo Verde 2 | 10/20/1997 | 11/12/1997 | 9711280051 | <strong>Manual reactor trip due to vibration and bearing temperature increases in reactor coolant pump</strong><br /><i>Abstract:&nbsp;</i>On October 20, 1997, at approximately 1050 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel initiated a manual reactor trip following vibration and bearing temperature increases in reactor coolant pump (RCP) 2B. No other safety system actuations occurred and none were required. At approximately 1051 MST, Control Room personnel secured and quarantined RCP 2B. The event was classified as an uncomplicated reactor trip. An engineering evaluation determined that the apparent root cause is attributed to a failed lower journal bearing. The most probable cause of the bearing failure was intrusion of debris. The source and composition of the debris is unknown. As corrective action, the bearing assembly was disassembled, inspected, and rebuilt. A metallurgical examination of the bearing pads, shaft protection sleeve, and debris collected from the bearing assembly is currently ongoing. No previous similar events have been reported pursuant to 10CFR50.73.
5291997007 | Palo Verde 2 | 10/06/1997 | 02/10/1998 | 9802190104 | <strong>TS violation due to inadequate shutdown cooling flow During Modes 5 and 6 operation</strong><br /><i>Abstract:&nbsp;</i>From September 30, 1997, at approximately 1455 MST to October 6, 1997, at approximately 1155 MST, Palo Verde Unit 2 was in Modes 5 and 6 (COLD SHUTDOWN and REFUELING), when shutdown cooling flow requirements specified in Technical Specification Limiting Condition for Operation (TS LCO) 3.4.1.4 and TS LCO 3.9.8 were not being met. Approximately 400 gpm of flow were bypassing the reactor core due to a shutdown cooling bypass valve not being fully seated when it was stroked closed on September 30, 1997 at approximately 1455 MST. Upon discovery, Control Room personnel closed the valve and initiated actions to reestablish the TS required shutdown cooling flow at approximately 1155 MST on October 6, 1997. Since Unit 2 had been shutdown for a refueling outage, the decay heat load was minimal and available shutdown cooling flow was more than adequate to remove decay heat under existing conditions. No previous similar events have been reported pursuant to 10CFR50.73.
5301997001 | Palo Verde 3 | 03/06/1997 | 04/03/1997 | 9704090153 | <strong>Loss of Spent Fuel Pool Level Procedure Requires Manual Fuel Building Essential Ventilation Actuation</strong><br /><i>Abstract:&nbsp;</i>On March 6, 1997, at approximately 0643 MST, Palo Verde Unit 3 was in its sixth refueling outage with the core offloaded to the spent fuel pool (SFP) when Control Room personnel manually initiated an Engineered Safety Feature Actuation System (ESFAS) actuation of the fuel building essential ventilation actuation system (FBEVAS) per an approved procedure for loss of SFP level. There was no increase in radiation levels during this event. Train A FBEVAS air filtration unit's (AFU) exhaust fan failed to start and the exhaust damper failed to open. The AFU was manually started using the Control Room handswitch. Control Room personnel entered Technical Specification Limiting Condition for Operation (TS LCO) 3.9.12 ACTION a for an inoperable Train A FBEV system. The Train B FBEV system remained operable and capable of being powered from the operable Train A Emergency Diesel Generator. At approximately 0705 MST, Operations personnel determined that leakage was occurring from the SFP to the fuel transfer canal through the gate seal. Air pressure was restored to the gate seal and the SFP level proceeded to increase. By approximately 2245 MST, both trains of FBEVAS had been reset and TS LCO 3.9.12 ACTION a was exited at approximately 2100 MST on March 7, 1997. There were no automatic ESFAS actuations and none were necessary. There have been no previous similar events reported pursuant to 10CFR50.73.
5301997002 | Palo Verde 3 | 05/31/1997 | 06/13/1997 | 9706190233 | <strong>Reactor Trip Following Spurious Opening of All Four Reactor Trip Switchgear Breakers</strong><br /><i>Abstract:&nbsp;</i>On May 31, 1997, at approximately 2312 MST, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when a reactor trip occurred following the spurious opening of all four reactor trip switchgear (RTSG) breakers. The core protection calculator (CPC) generated a low departure from nucleate boiling ratio (DNBR) signal due to all control element assemblies (CEA) inserting. By approximately 2325 MST, the unit was stabilized in Mode 3 (HOT STANDBY) and the Shift Supervisor classified the event as an uncomplicated reactor trip. There were no engineered safety features (ESF) actuations and none were required. Required safety systems responded to the event as designed. The preliminary cause of all four RTSG breakers spuriously opening, and the subsequent reactor trip was attributed to a combination of two incorrectly assembled ring-tongue terminals, in conjunction with a missing jumper on the spare trip parameter, all within the BD matrix logic of the plant protection system (PPS). Maintenance and engineering personnel were troubleshooting previous spurious RTSG breaker openings at the time of the reactor trip. The wiring error and termination deficiencies are believed to have occurred during original construction by Combustion Engineering/Electro-Mechanics. The lugs were replaced and the jumper was installed. The other 5 matrices in Unit 3 were visually verified to have their jumpers installed. No previous similar events have been reported pursuant to 10CFR50.73.
5301997003 | Palo Verde 3 | 02/15/1997 | 09/26/1997 | 9710060403 | <strong>Seven Main Steam Safety Valves Found Out of Tolerance Prior To Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>Between February 11, 1997, and February 15, 1997, Palo Verde Unit 3 was in Mode 1 (POWER OPERATION) operating at between 86 and 83 percent power, when control room personnel were notified of trevitest activities indicating that a total of seven MSSVs had as-found lift set pressures greater than the 3 percent allowed by TS 3.7.1.1. Six of the seven valves were adjusted and/or retested in accordance with APS procedures and were returned to an operable status on-line. Because MSSV SGE-PSV-691 did not lift at 5.8 percent of the rated lift set pressure, testing was suspended and the valve was quarantined until a root cause investigation could be performed during the upcoming refueling outage. An independent investigation of this event has been conducted in accordance with the APS Corrective Action Program. As part of the investigation a safety analysis was performed based upon the as-found MSSV data which demonstrated that the MSSVs would have performed their intended safety function. The analysis concluded that the condition would not have resulted in the secondary system pressure exceeding 110 percent of the design pressure limit. Between February 22, 1997 and March 31, 1997 six MSSVs were replaced with spare valves from warehouse inventory and one valve was adjusted to within +/-l% of the nameplate set pressure and left in place. The six removed MSSVs will be rebuilt and recertified prior to being returned to service. A previous similar event was reported LER 50-530/94-002-01.