## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2061999001 | San Onofre 1, San Onofre 2, San Onofre 3 | 08/08/1999 | 08/31/1999 | 9909030028 | <strong>Unattended Security Weapon Inside Protected Area</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1999, at 0630 PDT during routine security communication checks, a Security officer, who assumed dayshift armed responder duties inside the Protected Area (PA) at approximately 0600 PDT, did not respond to radio transmissions. Another Security officer was dispatched and at 0642 PDT (discovery time) found the posted officer apparently asleep inside a Vital Area (VA). The responding officer assumed custody of the response weapon, and awakened the officer (Reference: AR990800394). SONGS Security procedure SO123-IV-11.2 conservatively requires Southern California Edison (SCE) to make a 1-hour notification whenever a weapon is found "out of the control or physical custody of security personnel." Consequently, SCE made a 1-hour notification for this event (NRC Log Event Number 360080), and is providing this voluntary written follow-up. SCE has determined this event does not meet any NRC reporting requirements because: • 10CFR73, Appendix G, Section 11(a) and the guidance provided by Generic Letter (GL) 91-03, under the heading "Examples of Safeguards Events That Do Not Need To Be Reported To The NRC Within 1 Hour of Discovery," require the discovery of a sleeping or inattentive Security guard performing "compensatory measures" to be logged. a. The Security officer in this report was not at a compensatory post for a degraded security system. b. Under the assumption that a Security officer is armed, the NRC's guidance does not require a separate log entry or report for an "unattended weapon." Therefore, this would not be reportable or loggable under 10CFR73, Appendix G, Section 11(a) or GL 91-03. • Regulatory Guide (RG) 5.62, Section 2.2, Item 24, requires the loss of a security weapon be reported within 1 hour of discovery that a weapon has been lost. However, the weapon in question was not lost, but was next to the sleeping officer. The location of the weapon was always known. • Guidance provided in draft RG DG-5008, Section 2.4, Example 13, indicates the loss of a security weapon which is retrieved within 1 hour of the discovery of the loss should be logged only. For this event, the weapon was retrieved by another Security officer at the time of discovery.
2131999001 | Haddam Neck | 01/05/1999 | 03/31/1999 | 9904070079 | <strong>Main Stack Radiation Monitor R-14A Pressure Compensating Signal Not Calibrated</strong><br /><i>Abstract:&nbsp;</i>On January 5, 1999, with the plant permanently defueled, while reviewing radiation monitoring system (RMS) design issues, it was determined that main stack radiation monitor R-14A utilizes a pressure compensating signal and that calibration of the pressure transmitter had not been included in the instrument calibration surveillance procedure from the time the monitor was installed in August 1996. The apparent cause is that personnel preparing the R-14A calibration and functional test procedures did not identify the need for the pressure transmitter calibration. This event is believed to have low safety significance since the error introduced by the uncalibrated pressure transmitter is offset by conservative instrument setpoints. Corrective action consisted of revising the calibration procedure to include calibration of the pressure transmitter and ensuring the pressure transmitter signal is bypassed during calibration of the radiation detector. The pressure transmitter was calibrated on January 27, 1999. The as-found data was within the min/max pressure range specified within the calibration procedure. This supplemental LER provides the results of the calibration.
2191999001 | Oyster Creek | 02/08/1999 | 07/29/1999 | 9908030239 | <strong>Prolonged Operations of the Turbine Building with Condenser and Heater Bay Pressure less than Design</strong><br /><i>Abstract:&nbsp;</i>The Final Safety Analysis Report, Update 11, required that differential pressure in the Turbine Building be maintained at approximately -0.25 inches water gauge or greater during normal plant operations. A review of equipment operator tour sheets revealed that the Turbine Building had been operated at less than the design basis negative differential pressure for an extended period. This condition was determined to be reportable under 10 CFR 50.73(a)(2)(ii). The root cause for this condition was a lack of a clearly documented design description of the unique Turbine Building ventilation envelope to which this negative pressure applied. As a result, the Oyster Creek staff did not establish the appropriate procedural and administrative controls to prevent the Turbine Building from being operated in a pressure condition outside the design bases. On January 1, 1999, immediate corrective actions were taken to place the alternate exhaust fan in service. Due to the larger capacity of this fan, greater negative pressures were achieved and maintained. As maintaining this negative pressure is not credited in any of the plant accident analyses, this pressure and the FSAR have been revised. The safety significance of this discovery is minimal. The Turbine Building pressure was maintained negative. Therefore, no significant exfiltration could have occurred.
2191999002 | Oyster Creek | 03/30/1999 | 04/29/1999 | 9905110283 | <strong>Fire Protection Deluge System Isolation Valve Found out of Position</strong><br /><i>Abstract:&nbsp;</i>On March 30, 1999, an Operator found Fire Protection System deluge valve V-9-151 closed. This is the main isolation valve for one half of the non-redundant water deluge system in the Lower Cable Spreading Room. There were no compensatory measures in place. Upon discovery of the mispositioned valve, the Operator reported this condition to the Control Room. He was directed to place the valve in the locked open position, as required. A walkdown was performed on other Fire Protection System valves in the Reactor Building, Turbine Building, and Main Office Building. No other valves were found out of position. A technical assessment of this occurrence was performed. The assessment was subsequently turned over to the Corporate Internal Investigations Department for further investigation. Although no indication was discovered which would indicate deliberate mispositioning, the investigation could not rule out tampering. If any additional information is obtained, a revision to this LER will be submitted.
2191999003 | Oyster Creek | 04/02/1999 | 04/30/1999 | 9905110271 | <strong>Cable Trays Did Not Meet Criteria due to Inadequate Engineering Review</strong><br /><i>Abstract:&nbsp;</i>On April 2, 1999, it was discovered that the New Cable Tray System, located in the Reactor Building, did not meet the cable separation criteria which were used in the original design. The New Cable Tray System was installed in 1981 for future use. The tray installation package indicated that the use of covers, where appropriate, would be required when cables were installed. However, during subsequent modifications when new cables were installed, covers were not installed. The apparent cause of this occurrence was determined to be a failure to translate the original design criteria into the Cable Installation Standard. The significance of this discovery is minimal as the trays are lightly loaded and the cables involved carry only instrumentation and control cables. The cables meet appropriate industry standards for fire retardance. A fire watch was stationed immediately upon this discovery as a compensatory measure. Long term corrective actions include a plant walkdown and a revision to the Cable Installation Standard.
2191999004 | Oyster Creek | 05/10/1999 | 12/21/1999 | ML99363034 | <strong>Two Spent Fuel Pool Cooling System Piping Supports Do Not Meet Design Requirements Due to Inadequate Analysis</strong><br /><i>Abstract:&nbsp;</i>In May 1999, it was determined that the configurations of 2 pipe supports in the Spent Fuel Pool Cooling System (SFPCS) do not meet their design requirements for deadweight loads. One of these pipe supports is in the seismic class I portion of the system, and therefore, also does not meet its design requirements for load combinations of deadweight plus thermal plus seismic load. This condition is reportable under 10 CFR 50.73(a)(2)(ii). The root cause of the design basis deviations found was inadequate structural analysis performed during construction of the plant and when the augmented fuel pool cooling system was installed in 1977. The safety significance of the non-conforming conditions has been determined to be minimal as the supports meet operability criteria, the piping meets the design criteria and neither the pipe nor pipe supports would fail during any design basis event. This discrepancy in structural analysis is believed to be isolated to this system at this time. The appropriate design code for the augmented Spent Fuel Pool Cooling System has been determined and two of six segments have been re-analyzed and found acceptable. Two pipe supports will be upgraded to meet their design criteria and the remaining analyses will be completed by the end of the upcoming refueling outage.
2201999001 | Nine Mile Point 1 | 01/25/1999 | 02/24/1999 | 9903050270 | <strong>NMP1 Outside Design Basis Due to Failure to Revise Satellite Pre-Fire Plans</strong><br /><i>Abstract:&nbsp;</i>At 1500 hours on January 25, 1999, with Nine Mile Point Unit 1 (NMP1) in full power operation, an NRC Resident Inspector questioned Niagara Mohawk Power Corporation (NMPC) Fire Protection personnel concerning commitments that NMPC had made in its November 6, 1998, request for exemption from the requirements of 10CFR70.24(a), "Criticality Accident Requirements." When NMPC Operations personnel reviewed the commitments to answer the resident inspector's inquiry, they determined that the NMPC Fire Protection Supervisor had not adequately implemented the commitments made in NMPC's application for exemption to 10CFR70.24 (and as granted by the NRC on December 10, 1998). Therefore, NMP1 operated outside its design basis from January 12, 1999, when new fuel was first placed in the NMP1 new fuel storage vault, to January 25, 1999, when the revisions of the satellite Pre-Fire Plans were satisfactorily implemented. The root cause of the event is that the Fire Protection Supervisor failed to implement the required change to the Pre-Fire Plans. While the Fire Protection Supervisor did revise the master copy of the Pre-Fire Plans, the supervisor did not properly implement the change to the satellite copies of the Pre-Fire Plans. Corrective actions included revising the satellite copies of the Pre-Fire Plans, ensuring that all Fire Protection personnel were made aware of the basis for and importance of the change, revising the site services administrative procedure for control of Pre-Fire Plans, and counseling the Fire Protection Supervisor.
2201999002 | Nine Mile Point 1 | 02/17/1999 | 03/19/1999 | 9903300045 | <strong>ASME Code Pre-Service Examinations Not Performed On Emergency Condensers</strong><br /><i>Abstract:&nbsp;</i>On February 17, 1999, Niagara Mohawk Power Corporation (NMPC) determined that Nine Mile Point Unit 1 (NMP1) Technical Specification (TS) 3.2.6.a. 1 had not been met when the Emergency Cooling System (ECS) Emergency Condenser (EC) tube bundles were replaced during the fourth quarter of 1997. The ASME preservice examination had not been completed in strict compliance with the American Society of Mechanical Engineers (ASME) Code. On March 15, 1999, NMPC also determined that records could not be found to confirm that between June 20, 1986, and March 12, 1999, that the Containment Spray (CS) heat exchangers, which had been replaced in 1986, were in compliance with ASME Code requirements. The cause of both missed TS requirements is that engineers involved with the EC tube bundle replacement and the CS heat exchanger replacements misinterpreted the ASME Code requirement. Corrective actions for the ECS were to complete the inspections and to evaluate the extent of condition. During the extent of condition evaluation CS heat exchangers were identified as not having had proper preservice examinations performed. Prior to concluding that the CS heat exchangers had not had proper preservice examinations, preemptive inservice examinations were performed as required by ASME Code. In addition, mechanical engineering personnel at both NMP1 and 2 have been trained on ASME Code interpretation expectation.
2201999003 | Nine Mile Point 1 | 03/20/1999 | 04/22/1999 | 9905030146 | <strong>Thermal Limit Exceeded the Requirements of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Between March 20 and March 23, 1999, Nine Mile Point Unit 1 operated with the average planar linear heat generation rate exceeding the limits specified in Technical Specification Limiting Condition for Operation 3.1.7.a. Niagara Mohawk Power Corporation determined the root cause to be inadequate interface design between the color graphics terminals and the 3D-Monicore system, which led to an inadvertent entry of a command to reprocess a traversing in-core probe case. The reprocessed traversing in-core probe case altered the 3D-Monicore calculated core power distribution. This calculated power distribution change was not detected and subsequently resulted in a core thermal limit being exceeded. Corrective actions included lowering reactor power to restore compliance with the Technical Specification limit and disabling the color graphics terminals. The preventive action is to modify the color graphics terminals to disable any commands that could potentially affect the accuracy of the 3D-Monicore system upon an inadvertent operation.
2201999004 | Nine Mile Point 1 | 07/23/1999 | 08/23/1999 | 9908300301 | <strong>Reactor Scram Due to Mechanical Pressure Regulator Suppressor Valve Failure and Mode Switch Position not in Conformance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1999, at 1558 hours, during post maintenance testing of the turbine mechanical pressure regulator controls, the Nine Mile Point Unit I reactor automatically scrammed from full power from a high neutron flux signal on Channel 11 and Channel 12 of the reactor protection system. Following the reactor scram, operators moved the mode switch through the "Shutdown" position, to the "Refuel" position. The operators did not subsequently reposition the mode switch to "Shutdown" as required by Special Operating Procedure N1-SOP-1, "Reactor Scram." This was a nonconformance with Nine Mile Point Unit 1 Technical Specifications, which permitted the mode switch to be positioned in "Refuel" above 212 degrees F reactor coolant temperature only during reactor coolant system pressure testing, control rod scram timing, and for scram recovery. Niagara Mohawk Power Corporation determined that the cause of the reactor scram was internal blockage in the pressure suppressor valve in the mechanical pressure regulator feedback loop. The vendor had treated the valve with excessive corrosion inhibitor, and the excessive corrosion inhibitor blocked internal passages. The cause of the inappropriately positioned mode switch was ineffective change management, with contributing factor of inadequate corrective actions for a previously identified issue. Corrective actions for the reactor scram included placing the plant in a stable condition, cleaning the pressure suppressor valve, and providing guidance for valve disassembly and inspection. Corrective actions for the mispositioned mode switch included revising procedures, and conducting training.
2201999005 | Nine Mile Point 1 | 08/01/1999 | 11/18/1999 | ML99341030 | <strong>Reactor Trip During Plant Startup on Intermediate Range Monitor Spiking Caused by Electro-Magnetic Interference</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1999, at 2:20 p.m., Nine Mile Point Unit 1 automatically tripped during plant startup on invalid intermediate range monitor signals. Just prior to the trip, a normal reactor startup was in progress. When the reactor operator changed the Intermediate Range Monitor 11 range switch from range 2 to 3 as required, a reactor trip occurred. All systems responded as expected following the reactor trip. The cause of the reactor trip was degraded contacts on the range switch. When the switch was moved, a relay in the downscale rod block circuitry chattered, which in turn, produced electro-magnetic interference. The electro-magnetic interference caused Intermediate Range Monitors 12, 15, and 16 to spike, which resulted in the reactor trip signal. A contributing cause is the sensitivity of the intermediate range monitor circuitry to electro-magnetic interference. Corrective actions included: inspecting, cleaning, burnishing, and testing Intermediate Range Monitor 11 range switch, inspecting the remaining intermediate range monitor range switches, and installing circuitry to reduce the magnitude of the electro-magnetic interference from relays in all Intermediate Range Monitors downscale rod block circuitry. An action plan will be developed and implemented to further reduce the effect of electro-magnetic interference on the intermediate range monitor circuitry.
2201999006 | Nine Mile Point 1 | 04/03/1995 | 12/09/1999 | ML99355029 | <strong>Shutdown Cooling Water Seal not Established as Required by Technical Specification 3.3.0</strong><br /><i>Abstract:&nbsp;</i>On November 9, 1999, with the plant shutdown, Niagara Mohawk Power Corporation identified that beginning on April 3, 1995, for approximately eight days, the breakers associated with the shutdown cooling system isolation valves were not placed in the open position and racked out. When both of these events occurred, the plant condition required primary containment integrity to be in effect, which includes having the shutdown cooling isolation valves closed and the associated breakers for the valves racked out to maintain a water seal. These two events resulted in Technical Specification 3.3.0 not being met. The causes of these two events were determined to be inadequate training and review of procedures affected by the water seal modification. Procedures were revised to provide additional controls and guidance on when shutdown cooling water seal is required to be established. Licensed operators were given additional training on primary containment integrity and the shutdown cooling system water seal. Additionally, new controls will be evaluated and added, if appropriate, to the modification process for training and procedure revisions. Until this is done, training and procedure revisions requi4red for design changes will require an independent verification to ensure the procedure changes and training are adequate.
2371999001 | Dresden 2 | 01/15/1999 | 02/10/1999 | 9902230147 | <strong>Unit 2 Loss of Drywell to Torus dP During Quarterly Valve Timing due to Poorly Structured Technical Procedural Step</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1999 at approximately 0100 hours, The Unit 2 Nuclear Station Operator (NSO) was performing DOS 1600-03, Quarterly Valve Timing, in accordance with the station schedule. The NSO was performing the next block of valves, which time the movement of the 2-1601-55, 56, 21 and 22 valves. The surveillance directed him to perform either step I.4 or I.5, based upon plant conditions. The NSO reviewed steps I.4 and I.5 and chose to perform step I.5. The NSO timed the 2-1601-55 valve closed then reopened the valve, timed the 2-1601-56 valve closed and reopened it, timed the 2-1601-22 closed pd left closed (normal position) then opened the 2-1601-21 valve so that it could be timed in the closed direction. When the 21 valve opened it created an equalization path between the Drywell (DW) to Torus via the open 2-1601-56 valve. Numerous alarms were received on Unit 2, one of which being the 902-4 B-15 "DW to Torus dP Hi/Lo" alarm. At the time the DW to Torus differential pressure (dP) alarm was received, it was noted by both Unit 2 NSO's and the Unit Supervisor that dP had decreased to 0.85 dP, dropping below the Tech Spec required 1.0 dP. The NSO immediately closed the 2-1601-21 valve and proceeded to reestablish dP. The Shift Manager was notified and a prompt investigation was initiated. The investigation determined that the stated criteria for determining whether to perform step I.4 or I.5 caused this event. The procedural steps each stated a compound set of plant conditions which mislead the NSO during selection of the appropriate action to be taken. This event was determined to be reportable per 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. Corrective Actions include presenting the event and lessons learned to Operations personnel, reviewing and revising procedures with similar problems, and a review of fundamental operator training and system response. The Nuclear Safety Significance of this event was determined to be minimal.
2371999002 | Dresden 2 | 02/04/1999 | 03/04/1999 | 9903180238 | <strong>Reactor Protection System Electrical Protection Assembly CHANNEL FUNCTIONAL TEST Requirement Not Met due to Inadequate Review of Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1999, during a routine review of vendor technical material relating to the Reactor Protection System (RPS) Electrical Protection Assembly (EPA) [ED], it was discovered that a Dresden procedure used to perform channel functional testing requirements on RIPS EPAs (DTS 0500-02) used a testing methodology that did not satisfy the requirements of the Technical Specification 4.9.G.1. Technical Specification 4.9.G.1 requires a CHANNEL FUNCTIONAL TEST of the EPAs be performed when the plant is in cold shutdown for greater than 24 hours, unless it has been performed in the last 6 months. However, Dresden also uses another procedure (DTS 0500-03) to perform EPA channel calibrations every 18 months. A review of this procedure determined its performance satisfied the requirements of the CHANNEL FUNCTIONAL TEST specified in T.S.4.9.G.1. At the time of discovery, both Units were in compliance with 4.9.G.1 due to the satisfactory completion of DTS 0500-03. However, a review of past operating and surveillance history determined that several times in the past, the requirements of T.S.4.9.G.1 were not met due to the use of an inadequate procedure. This report documents historical operability issues pursuant to 10 CFR 50.73(a)(2)(i)(B). This event was the result of an inadequate review of the test procedure. Corrective actions include enhancing the review of applicable procedures to require the appropriate disciplines and reviewing similar procedures to ensure technical specification requirements are met.
2371999003 | Dresden 2 | 03/20/1999 | 04/19/1999 | 9904270041 | <strong>Unit 2 rod Block Monitor Inoperable due to Failed Diode</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1999, during routine Control Rod Drive (CRD) exercising on Unit 2, it was observed that the four-rod display on panel 902-5 indicated an improper number of Local Power Range Monitor (LPRM) inputs to the Rod Block Monitor (RBM) for the rod selected. Troubleshooting revealed that a diode had shorted, preventing proper operation of the Count Circuit and providing an improper number of LPRM inputs when some rods were selected. The cause of the diode failure is unknown. The corrective action was to replace the diode. The safety consequences of this event are minimal. This report is submitted pursuant to 10 CFR 50.73(a)(2)(vii)(D).
2371999004 | Dresden 2 | 05/15/1999 | 09/17/1999 | 9909290112 | <strong>Supplement to Control Room HVAC System Emergency Zone Refrigeration Control Unit Inoperability</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1999, at 0456 hours, during the performance of Dresden Operating Surveillance procedure (DOS) 5750-04, "Control Room B Train Heating, Ventilation and Air Conditioning and Air Filtration Unit Surveillance", for the post maintenance testing of the air filtration unit booster fan 2/3-9400-104A, the Refrigeration Control Unit (RCU) tripped after starting. The RCU was unavailable from 0456 hours on May 15, 1999 until 2232 hours on May 16, 1999. The RCU was determined to be OPERABLE after the satisfactory completion of DOS 5750-04, at 0900 hours on May 17, 1999. The cause has been determined to be inadequate procedures and instructions to perform specified work and testing on Westinghouse Overload relays. Corrective actions have been developed to include a Westinghouse Motor Control Center (MCC) assemblies procedure, job/task analysis, required training based on the job/task analysis, revision of work request models to include Westinghouse overload relays and a review of all Westinghouse MCC assemblies to prevent recurrence. This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(v). The "A" Train HVAC System Air Handling Unit (AHU), Return Air Fan and refrigeration control units were available for Control Room Habitability requirements and calculated sensible and latent heat loads for the design specifications of the "A" Train System are equal to the "B" Train heat load calculations. In addition, the "A" train, if required, is available on loss of offsite power via an alternate power source. Therefore, the safety significance of this condition is minimal.
2371999005 | Dresden 2 | 10/19/1999 | 04/14/2000 | ML99363034 | <strong>Inadvertent Reactor Vessel Drain Down Through an Electromagnetic Relief Valve Caused by Procedure Non-Adherence Due to Inadequate Supervision and Ownership of Work</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1999, at approximately 1715 hours, following removal of the Main Steam Line (MSL) "B" plug by station personnel, an inadvertent draindown of the Unit 2 Reactor Cavity commenced. Operations personnel immediately recognized the event in progress, and took appropriate actions to terminate the event. Control Room personnel manually started the 2B Core Spray Pump to restore and control cavity water level. The Outage Control Center (OCC) was notified of the event and station personnel were directed to reinstall the MSL plugs that had been removed. At approximately 1750 hours, management personnel entered the Unit 2 Drywell and identified that water was flowing through the "E" Electromatic Relief Valve (ERV). The "E" ERV closed following mechanical agitation of its associated pilot valve assembly, terminating the event. This LER is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv), which states the licensee shall report any event or condition that resulted in manual or automatic actuation of any Engineered Safety Feature (ESF). Based upon physical inspection of the ERV pilot valve, review of the maintenance work packages and interviews with maintenance personnel, the investigation concluded that the cause for the event was failure to follow and complete procedures as written due to inadequate supervision and ownership of the work. An Evaluation of the event concluded that fuel integrity was never challenged and core submergence maintained. As a result, the Nuclear Safety Significance of the event was minimal. A review of Station events since 1995 did not identify any similar events.
2371999006 | Dresden 2 | 12/22/1999 | 01/21/2000 | ML00367946 | <strong>Recirculation Loop Temperature Thermocouple Failuire Cause Shutdown Cooling Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1999 at approximately 1356 hours the "B" Reactor Recirculation Loop temperature recorder and electronic temperature switch failed upscale due to a degraded connection in the temperature measurement loop. This failure would have prevented the operation of the Shutdown Cooling (SOC) System in the event of a unit scram or shutdown. Operations entered the appropriate Technical Specifications Limiting Conditions for Operation (LCO). This connection was immediately repaired. The loop calibration was checked and found satisfactory. During trouble shooting, all other connections for the loop components were verified to be satisfactory. Operations exited the LCO at approximately 2020 hours. The overall safety significance of this event was minimal. This event is being reported pursuant to 10 CFR 50.73 (a) (2) (v), which requires the reporting of any event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to Remove Residual Heat.
2441999001 | Ginna | 02/22/1999 | 06/21/1999 | 9906290303 | <strong>Deficiencies in NSSS Vendor Steamline Break Mass & Energy Release Analysis results in Plant Being Outside its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1999, Ginna Station was notified by its NSSS vendor (Westinghouse) of two modeling errors in the analysis for a main steamline break inside containment with an assumed single failure of a main feedwater regulating valve. These errors had a nonconservative impact on calculated peak containment pressure. The first error involved the omission of a previously unaccounted for volume of high temperature feedwater. The second error resulted in an incorrect feedwater isolation time. The consequences of these two modeling errors previously created the potential for containment to exceed its design basis value of 60 psig for a main steamline break with a concurrent failure of a main feedwater regulating valve for R.E. Ginna Cycles 12 through 25. The cause of the plant being in a condition that was outside the design basis of the plant from Cycle 12 to Cycle 25 was deficiencies in the Westinghouse main steamline break mass and energy release analysis. Immediate corrective action for Cycle 27 was to place a temporary administrative restriction of 40 degrees Fahrenheit maximum on screenhouse bay temperature, a measure of Service Water / Containment fan cooler heat removal and pressure reduction capability, for Modes 1 through 4 (when containment is required to be operable) to ensure adequate post-accident environmental conditions margin existed. Corrective action to justify return to power for Cycle 28 included a cycle-specific analysis showing peak containment pressure less than 60 psig. Corrective action to prevent recurrence is outlined in Section V.B.
2441999002 | Ginna | 02/27/1999 | 03/29/1999 | 9904080022 | <strong>Surveillance Not Performed, due to Personnel Error, Resulted in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1999, at approximately 1600 EST, the plant was in coastdown prior to the 1999 refueling outage, in Mode 1 at approximately 70% steady state reactor power. It was discovered that a surveillance had not been performed at the frequency required by the plant's Technical Specifications. This constituted a missed surveillance, which is a condition prohibited by the plant's technical specifications. Control Room operators verified that the plant was currently in compliance with these surveillance requirements. No immediate corrective action was needed. The underlying cause of not performing this surveillance was a personnel error. Corrective action to prevent recurrence is outlined in Section V.B.
2441999003 | Ginna | 03/01/1999 | 03/31/1999 | 9904080027 | <strong>Two Valves Declared Inoperable Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1999, at approximately 1707 EST, it was determined that the required torque to initiate valve disc closure for the two main steam non-return check valves was greater than the acceptance criteria specified in plant test procedures. Immediate corrective action was to declare both valves inoperable and enter Technical Specification Limiting Condition for Operation 3.0.3. Following an evaluation of the test data by Nuclear Engineering Services, it was determined that the valves were operable. The plant exited Limiting Condition for Operation 3.0.3. The underlying cause of the event was changes in the methodology and materials for packing these valves, which resulted in a greater than anticipated shaft breakaway torque. Corrective action to prevent recurrence is outlined in Section V.B.
2441999004 | Ginna | 04/12/1999 | 08/24/1999 | 9909010030 | <strong>Containment Recirculation Fan Moisture Separator Vanes In Plant Being Outside Its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1999, at approximately 1600 EDST, the plant was shutdown in Mode 5. It was discovered that the containment recirculation fan chevron moisture separator vanes were installed backwards, so that the path for air flow was less tortuous, decreasing moisture separation effectiveness. Corrective action was to remove the vanes and install them in the proper orientation. The incorrect installation was a result of improper assembly by the manufacturer in the 1960's. The original moisture removal equipment consisted of an assembly made up of the chevron type vanes and fiberglass moisture removal pads. This equipment was shop-assembled and shipped to Ginna Station. Vendor photographs taken during original shop assembly show the vanes installed in a manner now known to be incorrect. Corrective action to prevent recurrence is outlined in Section V.
2441999005 | Ginna | 04/13/1999 | 05/13/1999 | 9905190187 | <strong>Undervoltage Signal on Safeguards Bus During Testing Results in Automatic Start of "B" Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1999, at approximately 1525 EDST, the plant was shutdown in Mode 5 for the 1999 refueling outage. A Refueling Shutdown Surveillance Procedure was in progress. During this surveillance (test), the "B" Emergency Diesel Generator, which had been locked out for the test, was reset with an undervoltage signal present on safeguards bus 17. The "B" Emergency Diesel Generator automatically started and reenergized bus 17 as per design. The cause of the reset was a personnel error. Immediate corrective action was to verify that the "B" Emergency Diesel Generator had started and reenergized bus 17. When the cause of the undervoltage signal on bus 17 was identified, normal offsite power was restored to bus 17. Corrective action to prevent recurrence is outlined in Section V.B.
2441999006 | Ginna | 04/21/1999 | 05/21/1999 | 9905280059 | <strong>Valve in Unexpected Position Results in Start of Turbine-Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1999, at approximately 1947 EDST, the plant was in Mode 2 at approximately 2% reactor power with the reactor coolant system being maintained at a temperature of 549 degrees F and a pressurizer pressure of 2235 PSIG. Testing of a motor-operated valve which isolates steam to the turbine-driven auxiliary feedwater pump was being completed, and the valve was left in the open position. The manual isolation valve was then opened, admitting steam to the turbine-driven auxiliary feedwater pump. This started the turbine-driven auxiliary feedwater pump. Immediate action was to isolate auxiliary feedwater flow from the turbine-driven auxiliary feedwater pump and close the manual isolation valve to secure steam to the pump. The underlying cause of this event was the motor-operated valve was left in the open position following diagnostic testing. This event occurred at a time when the valve would normally have been expected to be closed. Corrective action to prevent recurrence is outlined in Section V.B.
2441999007 | Ginna | 04/23/1999 | 07/23/1999 | 9908020082 | <strong>Personnel Error Causes Two Channels to be in Tripped Condition, Resulting in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1999, at approximately 0748 EDST, with the plant in Mode 1 at approximately 35% reactor power and a power escalation in progress after the 1999 refueling outage, Instrument and Control technicians inadvertently pulled fuses from the wrong nuclear instrument channel, causing a reactor trip due to high range flux trip. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. The underlying cause of the reactor trip was a personnel error, in that fuses were pulled on the wrong nuclear instrument channel. Further evaluation of the event has resulted in more accurately categorizing the root causes. Immediate corrective action was taken to stabilize the plant in Mode 3. Corrective actions to prevent recurrence are outlined in Section V.B.
2441999008 | Ginna | 04/27/1999 | 05/27/1999 | 9906040057 | <strong>Faulted Bistable During Calibration of Redundant Channel results in Overtemperature Delta T Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 27, 1999, at approximately 1248 EDST, with the plant in Mode 1 at approximately 90 percent reactor power and a power escalation in progress after the 1999 refueling outage, Instrument and Control technicians had placed one channel of the reactor protection system in the tripped condition for calibrations. A bistable in a different channel entered the tripped condition, resulting in two channels tripped and causing a reactor trip due to Overtemperature Delta T. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all systems operated as designed, and the reactor was stabilized in Mode 3. The underlying cause of the reactor trip was a faulted bistable. Immediate corrective was taken to stabilize the plant in Mode 3. The faulted bistable was subsequently replaced. Corrective action to prevent recurrence is outlined in Section V.B.
2441999009 | Ginna | 05/03/1999 | 06/02/1999 | 9906080307 | <strong>Instrumentation Declared Inoperable in Multiple Channels Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 3, 1999, the plant was in Mode 1 at approximately 90 percent steady state reactor power. It had previously been determined that Overtemperature Delta T and Overpower Delta T bistable trip setpoints were potentially nonconservative on three out of four reactor protection system channels, and an evaluation was in progress. At approximately 2330 EDST, instrumentation for these three channels was declared inoperable. Immediate corrective action was to enter Technical Specification Limiting Condition for Operation 3.0.3, and take actions to restore the channels to operable status. Following replacement of the affected bistables with bistables of a different design, the bistable trip setpoints were recalibrated and three of four channels were declared operable. The plant exited Limiting Condition for Operation 3.0.3. The underlying cause of the event was an unanticipated high frequency AC voltage ripple on the Delta T signals that adversely affected the trip setpoints for the bistables. Corrective action to prevent recurrence is outlined in Section V.B.
2441999010 | Ginna | 06/15/1999 | 07/15/1999 | 9907220014 | <strong>Radiation Monitor Alarm, Due to Higher than Normal Radioactive Gas Concentration, Results in Auxiliary Building Ventilation Isolation</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1999, at approximately 0356 EDST, the plant was in Mode 1 at approximately 100% steady state reactor power. Reactor coolant activity was higher than normal due to a suspected leaking fuel assembly. During activities associated with draining a CVCS holdup tank containing radioactive fluid, radioactive gas was released from the tank and radioactive gas concentration increased within the auxiliary building, where the tank is located. A ventilation isolation of the auxiliary building occurred when auxiliary building gas radiation monitor R-14 reached its high alarm setpoint. Immediate operator action was to perform the applicable actions of alarm response procedures. Corrective action to prevent recurrence is outlined in Section V.B.
2441999011 | Ginna | 08/23/1999 | 09/22/1999 | 9909290014 | <strong>Small Breach in Ventilation System Results in Plant Being Outside Design Limits</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1999, the plant was in Mode 1 at approximately 100% steady state reactor power. At approximately 10:15 EDST, small tears were discovered in the flexible duct work connector at the inlet of the Control Room HVAC System Return Air Fan (AKF08). The plant entered Technical Specification Limiting Condition for Operation 3.0.3 for approximately 48 minutes while temporary repairs were made. Subsequently, it was determined that the openings could have caused an in-leakage greater than that assumed in the accident analysis, placing the plant in a condition outside its design basis. This was reported to the NRC within one hour of the determination per 10CFR50.72 (b)(1)(ii)(B). Corrective action to prevent recurrence is listed in Section V.B.
2441999012 | Ginna | 11/24/1999 | 12/23/1999 | ML00367052 | <strong>Opening Control Room Ventilation System for Filter Replacement Resulted in Plant Being Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1999, the plant was in Mode 1 at approximately 100% steady state reactor power. As part of the Work Control System process, Work Order #9902102 was reviewed by the Shift Supervisor prior to authorizing the start of the work. This work order consisted of inspecting and replacing, as necessary, the Control Room HVAC air filters. In order to inspect these filters, small access covers in the side of the HVAC unit have to be removed. During this pre-job review on November 24, it was discovered that performing this work would cause a breach in the integrity of the Control Room HVAC system ductwork. The Shift Supervisor denied permission to perform the work on the basis that removing the filter bank access covers would be equivalent to opening the Control Room HVAC system envelope. At valrious times in the past such a breach was permitted to occur when this work was performed. This breach could have allowed in-leakage in excess of the assumed leak rate listed in the Ginna Station Updated Final Safety Analysis Report. It was concluded that the system may have been outside the design basis at those times in the past, and that it had not been recognized that the plant was outside its design basis during those times. The cause of the occasional breaches in the integrity of the Control Room HVAC system ductwork was inadequate procedural guidance for conformance with requirements of Technical Specifications. Corrective action to prevent recurrence is outlined in Section V.B.
2451999001 | Millstone 1 | 08/10/1999 | 09/08/1999 | 9909170045 | <strong>Stack Flow Monitor 4 Hour LCO Action Statement Not Met</strong><br /><i>Abstract:&nbsp;</i>On August 10, 1999 at 1200, with the stack flow rate monitor inoperable due to a lightning strike, it was discovered that a conditional Technical Specification Limiting Conditions for Operation (LCO) action for estimating the stack flow rate every 4 hours was not performed within the required frequency. Technical Specification LCO for all three Millstone units require a minimum of one stack flow rate monitor channel be operable and in service on a continuous, uninteruptable basis. The Technical Specification action statement for stack flow rate monitor inoperability states that with the number of channels operable less than required, effluent releases may continue provided that the flow rate is estimated once per 4 hours. On August 10, 1999, the stack flow rate was required to be estimated at 1145 and was not completed until 1205, therefore exceeding the 4 hour interval specified in the Technical Specifications for all three Millstone Units. Although the 4 hour interval was exceeded, there was no safety significance associated with performing the estimate 20 minutes late as there were no evolutions in progress during the 4 hour 20 minute time interval that would have impacted stack releases. The event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications. The cause of the event was attributed to personnel error in that plant personnel failed to perform verification of the next required reading as listed on the conditional LCO surveillance attachment to the Control Operators Log. The frequency of the LCO action was increased to ensure that it was completed every 3 hours and shift personnel involved received coaching and counseling. The Control Operators Log was revised to maintain a margin to the frequency for LCO action statements where applicable. Unit 1 Operations management has reinforced the need to be aware of error likely situations and maintaining proper focus on the operation of the unit.
2471999002 | Indian Point 2 | 01/22/1999 | 02/22/1999 | ML10043117 | <strong>Potential Containment Penetration Leakage Path via Weld Channel Supply/Vent Solenoid Valves</strong><br /><i>Abstract:&nbsp;</i>At approximately 12:10 hours on January 22, 1999 with the unit at 99 percent power, it was determined that, if a single failure occurred during containment pressure relief operations, the containment isolation function could be outside of its design basis. This would occur because of a potential vent path via containment isolation valve PCV-1190 through the Weld Channel and Containment Penetration Pressurization System solenoid vent port out to the piping penetration area in the PAB Thus, during containment pressure relief, a single failure of PCV-1190 to close on a containment isolation signal would result in opening a vent path to the piping penetration area in the PAB. This would be a monitored release path and filtered by the PAB exhaust system. This condition resulted, during containment pressure relief operations, in Indian Point 2 being outside the plant design basis for containment isolation. The most likely cause of the identified design deficiency was improper evaluation of the single failure associated with the interlock between valve PCV-1190 and SOV-1280 in the original design. Immediate corrective action was taken to administratively control (close) a manual valve located in series with the weld channel during pressure relief operation. The event had no actual affect on the health and safety of the public.
2471999003 | Indian Point 2 | 02/19/1999 | 03/22/1999 | ML10043117 | <strong>Missed Technical Specifications Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>On February 19, 1999, with the unit at approximately 99 percent power, it was discovered that the surveillance test for PT-M72, Liquid Process Radiation Monitor Functional Test, had not been performed in its entirety and two monitors (R-39, liquid effluent monitor for Service Water from the Component Cooling Water heat exchanger outlet and R-59, house service boiler condensate return line) had exceeded the surveillance test interval specified by Technical Specification. Further, the subsequent investigation revealed that R-8, an area radiation monitor for the Unit 2 Drumming Station, also exceeded the surveillance test interval specified by Technical Specification. Subsequently, the required surveillances for R-39 and R-59 were performed successfully, and the limiting condition of operation was exited. R-8 currently remains out of service pending completion of repairs to the drumming station door which is difficult and unsafe to operate. The door inoperability results in the door being maintained in the closed position thereby making entry and completion of the R-8 surveillance test not practicable. A Request for Engineering Services (RES) has been made to permanently retire the R-8 area radiation monitor. Human error has been cited as the cause of the test completion being incorrectly reported. Process enhancements to be implemented include reinforcing the expectations of test performance with the organizations that perform these tests ensuring that any deviations from the test scope are approved by the Test Engineer and Shift Watch Supervisor (SWS), and accurately reported.
2471999004 | Indian Point 2 | 03/05/1999 | 07/16/1999 | ML10043118 | <strong>EEQ Deficiency in Acoustic Monitors</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1999, a potential Equipment Qualification (EQ) deficiency was identified in the Acoustic Monitoring System. The station EQ file for this system did not contain any requirement to use RTV sealant around the hardline cable to accelerometer connection. Based on discussions with other utilities during an EQ self assessment, the need for sealing the hardline connectors was recognized. This was confirmed with the acoustic monitor manufacturer. Upon inspection of the connectors in question, it was verified that the hardline cable to accelerometer connectors did not have RTV sealant applied to them. The other ends of the hardline cables were covered with Raychem tubing which exceeds the sealing capabilities of RTV sealant. RTV sealant was subsequently applied to two of the three hardline cable to accelerometer connectors. The cable to the third connector was found to be broken. The cable and connectors were replaced, and the connectors at both ends of the cable were properly sealed. The cause of EQ deficiency was determined to be the omission from the manufacturer's test report, which was used to qualify the acoustic monitors, of any reference to applying RTV sealant on the hardline cable to accelerometer connectors. The manufacturer stated t & the RTV sealant requirement was in their installation procedure.
2471999005 | Indian Point 2 | 03/17/1999 | 04/16/1999 | ML10043117 | <strong>Failure to Declare Automatic Containment Isolation Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1999, with the unit operating at 99% power, the switches for Solenoid Operated Valves (SOV) EW-1 and EW-2, "WCP Air Supply to Cont. Isolation Valves," in the Weld Channel (WCCPPS) for the Post Accident Containment Ventilation System were found in the closed position contrary to the requirements of Check Off List 10.9.1, Post Accident Hydrogen Removal System. Valves EW-1 and EW-2 are maintained open to pressurize Weld Channel Zone 4 to 47 PSI. At 1150 A.M., upon discovery of the mispositioning of EW-1 and EW-2 switches, the seven day action statement was entered per Technical Specification 3.3.D.1.a for a portion of Zone 4 WCCPPS being inoperable. On March 17, 1999, at 1235 P.M. the switches for EW-1 and EW-2 were placed in the open position and Technical Specification 3.3.D.1.a action statement was exited. The design basis of the system is to prevent containment out-leakage, during a design basis Loss of Coolant Accident, by maintaining a higher external pressure on the liner welds and penetrations than containment pressure. This system is not required to meet the 10 CFR 100 offsite dose limits. Public health and safety were not affected by this event.
2471999006 | Indian Point 2 | 04/13/1999 | 05/13/1999 | ML10043118 | <strong>Plant Operation in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1999, while reviewing a surveillance test, PT-M48, "480 Volt Undervoltage Alarm," in preparation for scheduled work the following day, the Senior Watch Supervisor reviewed the Technical Specifications to determine if any limiting conditions of operation (LCOs) were potentially applicable to the performance of this test. The test requires the actuation of a test switch that results in bypassing the two degraded voltage relay contacts that provide degraded voltage protection for the associated 480-volt bus supply breaker. Technical Specifications require at least one degraded voltage channel on each 480-volt bus be operable when the plant is above cold shutdown. This 480-volt alarm test had been performed on a monthly basis for each of four 480-volt buses since 1984. Since this 480-volt alarm test bypassed both degraded voltage channels by bypassing the two degraded voltage relay contacts, the plant operated in a condition prohibited by Technical Specifications for approximately ten minutes each time the test was performed with the plant above cold shutdown. The surveillance test was postponed, and it was subsequently revised to test only the low voltage alarm, as required by Technical Specifications, which can be tested without disabling the degraded bus voltage relays.
2471999007 | Indian Point 2 | 04/21/1999 | 05/21/1999 | ML10043118 | <strong>Failure of 480V Bus 2A DC Control Power Transfer Switch</strong><br /><i>Abstract:&nbsp;</i>At approximately 2100 hours on April 21, 1999, with the IP2 station operating at approximately 99% power, surveillance tests were being conducted to verify that the 125 VDC control power to various 480 VAC safeguards busses could be transferred from their normal DC supply to their alternate DC supply. During performance of these tests, an automatic transfer switch failed at mid position leaving 480 VAC Bus 2A without DC control power. Due to the loss of DC control power to Bus 2A, Technical Specification (TS) 3.0.1 was entered. The immediate corrective action taken by the operator was to restore control power by manually moving the transfer switch to its "normal" position. Once the 125 VDC control power was restored, which occurred about 30 seconds into the event, TS 3.0.1 was exited and pursuant to 10 CFR 50.72(b)(1)(ii)(B), the NRC was notified. An operability determination of the transfer switch was performed after which the transfer switch was declared operable in its "normal" position. It will remain in that position until repaired. The apparent cause of the failure to transfer was malfunction of mechanical limit switches internal to the automatic transfer switch. The event had no effect on the health and safety of the public or plant personnel.
2471999008 | Indian Point 2 | 04/28/1999 | 05/28/1999 | ML10043118 | <strong>Deficiency in Respirator Qualification</strong><br /><i>Abstract:&nbsp;</i>While conducting Self Contained Breathing Apparatus (SCBA) training with nuclear plant operators (NPO), it was brought to the trainer's attention that some individuals may not be presently qualified to wear respirators. The trainer then asked the Respiratory Protection Section to provide a list of individuals in Operations and their current respirator qualification status. The list was provided on the morning of April 28, 1999. The list indicated that eighteen (18) Central Control Room (CCR) operators lacked respirator qualifications (16 due to respirator fits, 2 due to respirator medicals). Under certain emergency conditions CCR operators might be required to wear respirators. This report is being made per 10CFR50.73(a)(2)(ii)(C), because the expired operator respirator qualifications is a condition not covered by the plant's operating and emergency procedures. The health and safety of the public was not affected by this event.
2471999009 | Indian Point 2 | 05/11/1999 | 06/10/1999 | ML10043118 | <strong>Toxic Gas Monitor setpoint drift caused Technical Specification limit to be exceeded</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1999, with the unit at approximately 99 percent power, an engineering evaluation of the Toxic Gas Monitor setpoints determined that ammonia monitor drift could cause the Technical Specification limits on detectability to be exceeded. Both ammonia monitors (AC-5092 and AC-5095) in the Toxic Gas Monitoring system were declared inoperable. Accordingly, the declaration was based on the conclusion that both channels of ammonia monitors could have failed to detect a concentration of 25 ppm as required by Technical Specification 3.3.H.3. Subsequently, the ammonia channel set point calculation was revised to document the as-found allowance for the monthly and quarterly set point based on drift such that the Technical Specification limit on detectability of 25 ppm would not be exceeded. A modification was implemented to affect this set point change and the Toxic Gas Monitor ammonia channels were declared operable. The threshold limit value for ammonia is 25 ppm and signifies that a worker can be exposed to this concentration for 40 hours per week without detrimental effect. According to Regulatory Guide 1.78, the toxicity limit for ammonia is 100 ppm. Sufficient time was available for the donning of Self Contained Breathing Apparatus. Therefore, the health and safety of the public were not adversely affected by this event.
2471999010 | Indian Point 2 | 05/14/1999 | 06/14/1999 | ML10043118 | <strong>Emergency Diesel Generator Air Compressor Non-Conservative Alarm Response Procedure Operation</strong><br /><i>Abstract:&nbsp;</i>While preparing for a planned maintenance activity on the Emergency Diesel Generator (EDG) starting air system, a concern was identified regarding the consequence of cross-connecting two of the starting air receivers. Whenever one of the three EDG starting air compressors are taken out of service, the starting air receiver associated with that air compressor is cross-tied to one of the remaining two air compressors. The local alarm response procedure for low EDG starting air pressure directs the operator to open the starting air tie valve to restore pressure to design limits. With EDG starting air systems cross-tied, a potential exists to lose adequate pressure to two EDGs in the event of a system component failure, such as failure of a relief valve in its open position. The operability of two (2) of the three (3) EDGs is required for minimum safeguards. At the time of discovery no starting air systems were cross connected; however, the starting air systems may have been cross connected in the past. This report is being made per 10CFR50.73(a)(2)(ii)(B), since "Any event or condition that resulted in the condition of the nuclear power plant, including its principle safety barriers, being seriously degraded; or that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant" is reportable. The health and safety of the public were not affected by this event.
2471999011 | Indian Point 2 | 06/16/1999 | 11/01/1999 | ML99342021 | <strong>Overload of MCC Breaker Causes Loss of Rod Position Indication and Turbine Runback.</strong><br /><i>Abstract:&nbsp;</i>At 0211 on June 16, 1999, with Indian Point No.2 (IP2) operating at 99 percent power, the supply breaker to Motor Control Center (MCC) 24 tripped open. This caused loss of power to all loads on MCC 24. Loss of power to the Rod Position Indication System (RPIS) initiated a turbine runback. The turbine automatically ran back and reduced reactor power level by approximately 4.2 percent. The expected power reduction from a dropped rod runback is approximately 15 percent. Due to loss of power to the RPIS, the plant entered Technical Specification 3.0.1 for circumstances in excess of those addressed in Technical Specification 3.10.6.2 for inoperable RPI channels. The operators determined a few minutes into the vent, by using alternate instrumentation to rod position indication (Excore Nuclear Instrumentation System (MS) indication and RCS temperature), that there was no evidence of an actual rod drop event. The immediate corrective action was to restore power to the RPIS. After approximately 19 minutes power was restored to the RPIS. With RPIS operational Technical Specification 3.0.1 was exited. Pursuant to 10 CFR 50.72 (b)(1)(ii)(B) the NRC was notified. Over the next few hours important loads on MCC 24 were reestablished and power was reduced to 85 percent to prevent another turbine runback transient from occurring during circuit troubleshooting efforts. The apparent cause of the trip of MCC 24 was overload of its supply breaker. There was no danger to the health and safety of the public or plant personnel due to this event. There was no indication of control rod misalignment prior to or following the restoration of MCC-24.
2471999013 | Indian Point 2 | 08/19/1999 | 09/20/1999 | ML10043119 | <strong>Design Anomaly Identified in Emergency Diesel Loading Sequence</strong><br /><i>Abstract:&nbsp;</i>On August 19, 1999, with the unit at 99% power, during an assessment of engineered safety features and emergency diesel generator testing, a postulated single failure on either Train A or Train B that could affect the emergency diesel loading sequence for both trains was identified. The postulated single failure of either Train A or Train B logic sequence (such as a loss of 125VDC control power) could result in certain sequencing relays to start timing on initiation of the "loss of offsite power with unit trip and no safety injection" signal, rather than when the emergency diesel restores power to the 480V bus. This could result in the emergency diesel having to assume a large 480V motor load (such as a 250HP pump) upon connection to the 480V supply bus. An operability determination was made on the emergency diesels that showed that any one of the diesels can assume a large motor load upon connection to the supply bus. As a result, this circumstance has no adverse impact on safety. Only the loading sequence for a loss of offsite power with a unit trip without safety injection is affected by the identified condition. This condition does not affect the emergency diesel loading sequence with safety injection. This condition is part of the original plant-design. Recommended solutions for this situation are being evaluated.
2471999014 | Indian Point 2 | 08/25/1999 | 09/24/1999 | ML10043119 | <strong>Failure to Meet Technical Specification Minimum Degree of Redundancy</strong><br /><i>Abstract:&nbsp;</i>On August 25, 1999, with the unit operating at 99 percent power, a review of surveillance tests PT-Q62 "Hi Steam Flow/1st stage Pressure Bistable" completed on February 26, 1999 and June 30, 1999 indicated the number of operable Hi Steam Flow Bistables, for both tests, did not meet the minimum degree of redundancy required by Technical Specifications Table 3.5-3 "High Steam Flow in 2/4 Steam Lines Coincident with Low T sub a v e or Low Steam Line Pressure." The as found setpoints for the High Steam Flow bistables were above the Administrative Limits specified in WCAP-13871 "Westinghouse Setpoint Methodology for Protection and Control Systems Indian Point Unit 2". On February 26, 1999 the setpoints for two channel "A" and two channel "B" bistables, each for different steam lines, were above the Administrative Limits and on June 30, 1999 all channel "B" and two channel "A" bistables in different steam lines were set above the Administrative Limits. In addition, three occasions were identified with similar setpoint issues where both bistables associated with a single steam line were above the Administrative Limit. Thus, the minimum degree of redundancy (two) required by Technical Specification Table 3.5-3 could not be established. Procedure PC-R19 for the calibration of the Turbine First Stage Pressure Computers and Hi/Lo Limiters and PT-Q62 for bistable setpoints were revised to increase the adjustment span and setpoints for the Hi Steam Flow bistables. On August 28, 1999 the High Steam Flow bistable setpoints were adjusted to within the required administrative values.
2471999015 | Indian Point 2 | 08/31/1999 | 09/30/1999 | ML10043119 | <strong>Reactor Trip, ESF Actuation, Entry into TS 3.0.1, and Notification of Unusual Event.</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1999 the Instrument and Control (I&C) group was replacing a defective bi-stable PC-457A, the pressurizer low pressure trip bi-stable for Protection Channel 3. To support this maintenance, the Over Temperature Delta Temperature (OTDT) channel trip for Protection Channel 3 was placed in the trip position. A spurious electrical spike occurred on the OTDT Protection Channel 4. This made up the "two out of four" reactor trip logic causing an OTDT reactor trip. After the reactor tripped, a sustained undervoltage condition on 480 VAC bus 5A or 6A caused the station blackout logic matrix to generate a blackout signal, stripping the 480 VAC buses and reloading them onto the emergency diesel generators (EDG). Bus 6A loaded onto its EDG and then tripped off due to an over-current trip on the EDG output breaker. Battery Charger 24 is powered from bus 6A. The battery supported the DC loads for approximately 7.4 hours. During that period of time, power was not restored to Battery Charger 24. Subsequently Instrument Bus 24 was lost when the voltage on DC bus 24 became too low for Inverter 24 to provide AC power to the instrument bus. As a result, a Notification of Unusual Event (NUE) was declared based on Emergency Action Level (EAL) 7.3.1 due to an unplanned loss of approximately 75% safety system annunciators for greater than 15 minutes. The NUE was exited at 03:30 hours on September 1, 1999 when power was restored.
2471999016 | Indian Point 2 | 09/17/1999 | 10/18/1999 | ML99306008 | <strong>Engineering review of field conditino revealed a missing jumper wire.</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1999 during the installation of a modification to the facility, consisting of new timing relays in a Motor Driven Auxiliary Feedwater Pump breaker control circuit, variations between the design documents and the actual field conditions were discovered. Specifically, jumper wires indicated on the design drawings did not physically exist in the installed circuitry for the two Motor Driven Auxiliary Feedwater Pumps. A preliminary investigation determined that this condition could have rendered the automatic start feature from the breaker control circuitry to the 21 Auxiliary Feed Water Pump (21AFWP) inoperable during certain scenarios. Specifically, in the event of a loss of power to 480 VAC bus 3A only, the anti-pump" feature of the 21 AFWP breaker would require operator action to start the pump for a low-low steam generator water level signal or an Anticipated Transient Without Scram ATWS) Mitigation System Actuation Circuitry (AMSAC) signal. The circuitry for all of the automatic start features for the 23 Motor Driven Auxiliary Feedwater Pump remained operable. Further, the automatic start features for both Motor Driven Auxiliary Feedwater Pumps remained operable for both Safety Injection (SI) and reactor trip with station blackout signals.
2471999017 | Indian Point 2 | 09/21/1999 | 10/21/1999 | ML99316027 | <strong>Fire Protection System Design Deficiency Resulting in Potential Flooding</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1999 with the unit in hot shutdown condition, an ongoing review of the Fire Protection (FP) system identified the existence of a design deficiency associated with one (1) Victaulic pipe coupling which could, in certain postulated seismic circumstances, have resulted in flooding concerns to safety-related equipment. It was determined that predicted high impact loads due to pipe movement and as-found clearances during a postulated seismic event, could have resulted in piping failure and localized area flooding within the Primary Auxiliary Building (PAB). The potentially affected flooding area was in the lower level of the PAB, which includes safety-related equipment such as the Residual Heat Removal (RHR) pumps. To correct this design deficiency, additional piping supports were installed to limit pipe movement in the affected area. This report is being made per 10CFR50.73(a)(2)(ii)(B), as a condition found to be outside the design basis of the plant. The health and safety of the public was not affected by this event.
2471999018 | Indian Point 2 | 10/06/1999 | 11/04/1999 | ML99325003 | <strong>Plant Operation in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1999, with the unit at hot shutdown, 125VDC control power for 480V Bus 2A was interrupted during the installation of a temporary facility change on the 125VDC transfer switch associated with Bus 2A. This rendered breaker control inoperable for the Bus 2A supply and load breakers for approximately one minute. During this interval, Bus 2A degraded voltage actuation channels were inoperable due to the lack of 125VDC power. This was contrary to the requirements of Technical Specification Table 3.5-3, Item 3.b. Throughout this event, bus and load fault protection was available through the amptector current sensing devices. No operating loads supplied by Bus 2A were tripped as a result of this event. The temporary facility change was implemented to allow repair of the Bus 2A 125VDC transfer switch. The 125VDC power supply for Bus 2A was returned to its original design configuration upon completion of repairs to the transfer switch. The root cause of this event is presently still under investigation. Insufficient planning and lack of communication in the implementation of the temporary facility change have been preliminarily identified as apparent causes of this event. This report will be supplemented upon completion of the root cause investigation and the determination of appropriate corrective action.
2471999019 | Indian Point 2 | 10/28/1999 | 11/17/1999 | ML99340039 | <strong>Inadvertent Disabling of Rod Position Plant Computer Program</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1999, with the unit at 99% power during surveillance testing, the alarm limits for the control rod position deviation (Rod-vs-Bank) alarm were discovered to be plus or minus 24 steps. The design alarm limits are plus or minus 12 steps (or plus 17 or minus 12 steps If above 211 steps) In accordance with Technical Specification requirements for power levels above 50%. T here was no plant operation outside of Technical Specifications because the Technical Specification action statement concerning an Inoperable rod position monitor was followed for the duration that the alarm limits were outside the acceptable range. However, this report is being made as a management discretion because of the potential significance of an incorrect rod position alarm setting. The rod position monitoring plant computer program had been erroneously allowed to be disabled due to lack of proper software configuration control of software upgrades related to the Y2K Issue. On October 29, 1999, the program was returned to service. In January 1998, as part of the initial Y2K assessment of PROTEUS, a test had been performed that demonstrated the Y2K compliance of the overall PROTEUS system with this program intact. A further detailed code review that confirms this program is not date-sensitive and, therefore, not subject to Y2K concerns, was performed on November 3, 1999.
2471999020 | Indian Point 2 | 12/23/1999 | 01/24/2000 | ML00368158 | <strong>Failure of Cable Spreading Room Fire Dampers to Close During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1999, with the unit at 99 percent steady state power, approximately one-half of the Cable Spreading Room (CSR) fire dampers failed to close upon receipt of a halon fire suppression system actuation signal which was transmitted while performing surveillance test PT-EM19, "Cable Spreading Room Halon System." The affected fire dampers were FD-01, FD-02, FD-03, FD-0 6 and FD-07. Proper closure of the CSR fire dampers upon halon system actuation is necessary to ensure that the required halon concentration is achieved within the CSR in the event of a fire. The cause of this failure has been attributed to incorrectly wired electrical controls for the damper closure circuit. These incorrectly wired electrical circuits were corrected and the associated fire dampers re-tested successfully. An investigation to determine the root cause of this event has been initiated. This report is being made per 10 CFR 50.73(a)(2)(ii)(S) as a condition found to be outside the design basis of the plant. Pursuant to 10 CFR 50.72(b)(1)(ii)(B), this event was reported to the NRC on December 23, 1999. The health and safety of the public was not affected by this event.
2491999001 | Dresden 3 | 02/20/1999 | 03/19/1999 | 9903250359 | <strong>Unit 3 Shutdown Cooling Isolation from an invalid Low Reactor Water Level Signal due to Procedural Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 0414 hours on February 20, 1999, Operations had successfully completed DOS 0201-02, Unit 3 ASME B & PV Code 1000 psi System Leakage Test / Hydrostatic Test. Following the testing, the two Equipment Attendants were tasked with the return to service of various reactor pressure instruments on the 2203-5 rack, located in the Unit 3 Reactor Building. As the two Equipment Attendants valved in the reactor pressure instruments, a reactor scram signal and Groups 2 and 3 isolations occurred causing a Shutdown Cooling (SDC) isolation for sixteen minutes. The Equipment Attendants were contacted by radio, work was stopped and an investigation initiated. A lack of backfill pressure in the instrument reference line, between the instrument isolation valve and the actual instrument, had caused a momentary oscillation in reference leg pressure. The reactor pressure instruments being returned to service share a common sensing line with reactor level instruments. As a result of the small pressure oscillation seen when the isolation valve was opened, the level instruments sensed the momentary low level condition resulting in initiation of the reactor scram and Groups 2 and 3 Isolations from low reactor water level. Actual reactor level remained at +32 inches for the duration of the event. The cause was determined to be a procedural deficiency, evident by the failure for the governing procedure to adequately control sequencing of the task. Corrective actions include revision to Unit 2 and 3 hydro, procedures, evaluation of the feasibility of electronically isolating the pressure switches in lieu of manual valving out of the pressure switches, review of similar procedures for related issues, and evaluation of the event for future training. This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(iv), which requires the reporting of any event or condition that results in manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection system (RPS). Based on plant conditions at the time of the event, the safety significance was determined to be minimal.
2491999002 | Dresden 3 | 03/05/1999 | 04/02/1999 | 9904070407 | <strong>Inadequate corrective actions contributed to invalid Recirculation Loop Temperature Signal which causes Unit 3 Shutdown Cooling Isolation</strong><br /><i>Abstract:&nbsp;</i>At 1354 hours on February 01, 1999, while Unit 3 was in Mode 5 a spurious 350 degrees F isolation of the Shutdown Cooling System (SDC) occurred. Operations personnel performed steps in accordance with Dresden Operating Abnormal (DOA) 1 000-1 and entered the appropriate Technical Specification (TS) Action Statement. The isolation was due to a spurious 350 degrees Recirculation loop temperature isolation signal. The isolation was immediately reset and SDC was restarted at 1402. TS Action statement exited at that time, as well as, DOA. Following the isolation, TS 3.2.A-1 was reviewed and the 350 degrees isolation function was bypassed in accordance with the guidance in DOA 1000-1. A procedure change was initiated and revised Dresden Operating Procedure (DOP) 1000-03 to disable the trip function since this function is only required to be operable in modes 1, 2 and 3. As a part of the follow-up actions, Operations personnel reviewed reportability requirements in accordance with the ComEd Reportability Manual. The Reportability Manual states that this event is not reportable, therefore no ENS call was made. Subsequent review of deficiency documents revealed that the Reportability Manual was in error and the event should have been reported. An ENS call was made on March 05, 1999 at 1840 hours. A revision request to the reportability manual was issued to correct the manual. Based on a review of the event, several previous occurrences were identified. However, no evidence could be obtained which indicated that actions were taken to prevent recurrence. The cause of the isolation is attributed to inadequate corrective actions due to management oversight. This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(iv), which requires the reporting of any event or condition that results in manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection system (RPS). The system was not in operation for approximately eight minutes. There was no temperature increase during the time that the system was not in operation.
2491999003 | Dresden 3 | 03/21/1999 | 10/27/2000 | ML00376563 | <strong>Supplement to Reactor Recirculation B Loop, High Pressure Flow Element Venturi Instrument Line Steam Leakage Results in Unit 3 Shutdown Due to Fatigue Failure of Socket Welded Pipe Joint</strong><br /><i>Abstract:&nbsp;</i>On March 21, 1999, at approximately 0900 hours, during an inspection of the drywell for the source of a previously detected increase in unidentified leakage, a steam leak was discovered on a socket weld at a 1 inch tee fitting on the high pressure instrument line for the Reactor Recirculation pump Loop B venturi flow element. A Unit 3 shutdown was performed in accordance with the pre-approved inspection plan, as required by Technical Specification 3.6.H for primary pressure boundary leakage. A detailed analysis of the failed tee weld indicated the failure was attributed to vibration induced fatigue cracking accelerated by the presence of a weld defect due to lack of fusion in the root of the socket weld. This same tee weld had previously failed in November 1997 (ref. LER 97-012-00). No detailed material analysis was performed after that failure. A root cause investigation has been performed to determine the reasons the corrective actions implemented after the November 1997 weld failure did not prevent recurrence. A modification for Unit 3 has been developed and it was determined that a modification to the Recirculation Lines for Unit 2 is not required as the Unit 2 configuration and support system is significantly more rigid than Unit 3 (without the tie-back supports) making it less susceptible to the flow induced vibration. The overall safety significance of the event was minimal. This report is submitted pursuant to 10 CFR 50.73(a)(2)(i)(A).
2491999004 | Dresden 3 | 05/03/1999 | 04/12/2001 | ML01107053 | <strong>Enforcement discretion Required for Target Rock Safety/Relief Valve Inoperability</strong><br /><i>Abstract:&nbsp;</i>At approximately 1951 hours on May 3, 1999, an annunciator, indicating a possible pilot valve bellows failure for the Target Rock safety relief valve, was received in the Unit 3 control room. The failure of the pilot valve bellows prevents the Target Rock from functioning as a safety valve. Although the pressure safety function is inhibited, the pressure relief capability was not impacted. The action statement associated with an inoperable safety valve required that the unit be in hot shutdown within 12 hours and cold shutdown within the next 24 hours. Preparation for a plant shutdown was commenced. Concurrently, the Notice of Enforcement Discretion (NOED) process was also initiated. At approximately 0215 hours on May 4, 1999, the NRC granted verbal approval of the NOED. The NOED request was docketed on May 4, 1999. Although a NOED was granted, which allows continued operation, current Technical Specification 3.6.E requires the plant to be in hot shutdown in 12 hours and cold shutdown in 24 hours. Unit 3 did not reach hot shutdown in the 12-hour time duration. Corrective actions included submittal of an Exigent Technical Specification Amendment. The Target Rock safety relief valve was removed from Unit 3 in D3R16, packaged and shipped offsite. The valve underwent bellows leak testing with steam and nitrogen. Both tests confirmed the bellows was intact and no leak existed. Confirmation of pressure switch malfunction could not be obtained as the switch was replaced and the old switch discarded. Based on the bellows leaking testing of the Target Rock valve, it is concluded that the valve safety function was available and the alarm was caused by a faulty pressure switch. This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B), which requires the reporting of any operation or condition prohibited by the plant's technical specifications. The Target Rock Valve is not assumed to operate in the Plant's Transient Analysis. Therefore, the safety significance of this condition is minimal.
2491999005 | Dresden 3 | 07/10/1999 | 08/09/1999 | 9908160045 | <strong>Isolation Condenser Inoperable Due to Valve Actuator Motor Pinion Key Becoming Dislodged</strong><br /><i>Abstract:&nbsp;</i>On July 10, 1999 at 1555 hours, the Dresden Operations Department was performing Quarterly valve timing on valve 3-1301-4, Isolation Condenser Condensate Return Valve, when it was discovered that the valve could not be electrically opened. The valve, which is normally open, had been cycled earlier in the day in order to support the testing. In response to the valve's failure to open, Operations electrically deenergized the valve at the breaker, in accordance with Dresden Operating procedure (DOP) 0040-01, electronically isolating the valve in the closed position until troubleshooting could be performed. On July 17, 1999, a drywell entry was made at power to perform additional trouble shooting and repairs to the valve. The valve's motor was removed, and a visual inspection revealed the motor pinion gear was loose on the shaft and the drive key had fallen out of the keyway. The motor pinion gear drive key was replaced, and the pinion gear was reinstalled and staked in accordance with Dresden Electrical Procedure (DEP) 0040-09 revision 8, Limitorque Valve Operator Maintenance. The valve was tested and declared operable at 0715 hours on July 17, 1999. The primary cause for the event was determined to be human error by employee's failure to complete work steps contained within Station Procedures. The On-line Safety Assessment Program has previously determined that the loss of the Isolation Condenser has a relatively low Safety Significance. All of the Unit 3 High Pressure Emergency Core Cooling Systems (ECCS) were fully operable during the entire period, from first cycling of the 3-1301-4 valve on July 10, 1999, until its repair on July 17, 1999. The Unit 3 ECCS systems were fully capable, by design, to provide reactor decay heat removal, pressure control, and inventory control under all design basis accident conditions. The Isolation Condenser was returned to operable status within 7 days, approximately half of its Limiting Condition of Operation (LCO) statement of 14 days. Therefore, the safety significance of this event was minimal. This event is reportable per 10 CFR 50.73 (a) (2) (v), which requires the reporting of any event or condition that alone could have prevented the fulfillment of the safety function of structure or systems to remove residual heat.
2491999006 | Dresden 3 | 12/11/1999 | 01/10/2000 | ML00367704 | <strong>Reactor Scram from Main Turbine Stop Valve Closure due to Turbine Trip Caused by Lockout Valve Solenoid De-energization During Weekly Overspeed Oil Trip Testing</strong><br /><i>Abstract:&nbsp;</i>On December 11, 1999, at 0111 hours, operations personnel were performing the Main Turbine weekly surveillances per DOS 5600-02, "Weekly Turbine Checks." The Unit 3 tripped from Main Turbine Stop Valve closure initiated by the turbine overspeed test circuits. The cause of this event was determined to be a faulty XK3 relay socket that resulted in the turbine lockout solenoid being de-energized during the oil trip testing. The de-energization of lockout valve caused the Electro Hydraulic Control (EHC) Emergency Trip System (ETS) hydraulic pressure to bleed off from the system pressure. This cause was determined through the measurement of AC voltages before the Xk3 relay contact and after the contact that supplies voltage to the lockout valve. The cause of this event was the failure of the XK3 relay socket. Corrective actions included replacement of the defective socket for the XK 3 relay. The overall safety significance of this event was minimal. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv), which requires the reporting of any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS).
2501999001 | Turkey Point 3 | 06/23/1999 | 07/20/1999 | 9907270053 | <strong>Manual Reactor Trip from 100% Power Following Multiple Control Rod Drops</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1999, FPL's Turkey Point Unit 3 was operating in Mode 1 at 100% power. At approximately 11:38 AM, Shutdown Bank B, Group 1 rods (4 control rods) dropped to the bottom of the core. The Reactor Control Operator (RCO) manually tripped the reactor approximately 8 seconds after receipt of rod drop indications. The remaining rods inserted as expected when the reactor trip breakers were opened. The immediate cause of the reactor trip was manual action taken by the RCO in response to indications of more than two control rods dropped in the core. The underlying cause of the trip was failure of a Stationary Gripper Regulating circuit card in the Rod Control System. The card failure was due to fracture of an uninsulated solder terminal post. The terminal post fracture was located flush with the top of the circuit board below a resistor lead solder joint. Failure of the card caused the group 1 rods in Shutdown Bank B to be released by their Stationary Gripper Coils, allowing the rods to drop into the core. Corrective actions included inspections and repairs of Stationary Gripper Regulating cards, and post maintenance testing.
2541999001 | Quad Cities 1 | 07/15/1997 | 05/12/1999 | 9905200120 | <strong>A Technical Specification Surveillance for Primary Containment Isolation Valves was Not Met when Three Spare manual Isolation Valves were Inappropriately Deleted from the Surveillance Procedure due to Inadequate Procedure Revision Review</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1999, three spare valves were determined to require monthly verification in accordance with Technical Specification (TS) Surveillance Requirement 4.7.A.2. TS 4.7.A.2 requires monthly verification of accessible primary containment penetration valves. These valves were not included in revision 2 of QCOS 1600-33, "Monthly Primary Containment Integrity Surveillance," implemented on June 20, 1997. The change that resulted in revision 2 of QCOS 1600-33 removed a number of valves from the procedure that did not require monthly verification. The revision was inadequate in that it also deleted the verification of three spare valves that did require monthly verification. The cause of this event was an inadequate review of a procedure revision. A contributing cause was the fact that these spare valves were not shown in controlled drawings and were not listed in the Updated Final Safety Analysis Report (UFSAR). Corrective actions included immediately verifying the valves were lock-wired closed, revising tile surveillance to ensure continued compliance, implementing additional reviews for TS related procedure revisions, revising drawings, revising the UFSAR, and training on the event. The review for events involving previously reported inadequate TS procedures identified that corrective actions from these previous events were not yet in place when this procedure error occurred. This event was not safety significant because the spare valves were identified to be lock-wired closed with threaded pipe caps installed. There was no impact to the health and welfare of the public or onsite personnel.
2541999003 | Quad Cities 1 | 09/07/1999 | 12/08/1999 | ML99351010 | <strong>High Pressure Coolant Injection (HPCI) Inoperable due to Manual Closure of a HPCI Steam Supply Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On September 7, 1999, and on October 4, 1999, while at 100% power, the Unit 1 High Pressure Coolant Injection (HPCI) steam supply outboard containment isolation valve failed to close from the control room control switch. In accordance with Technical Specification (TS) 3.7.D, "Primary Containment Isolation Valves," Action 1, the redundant HPCI steam supply containment isolation valve was maintained closed, rendering HPCI inoperable. Following replacement of the HPCI steam supply isolation valve control switch on September 7, 1999, HPCI was declared operable. Following contactor replacement on October 7, 1999, HPCI was again declared operable. The root cause of these events were inadequate instructions in the procedure used to refurbish this type of breaker, resulting in a failed close contactor at the valve breaker. For each event, an ENS notification was made under l0CFR50.72(b)(2)(iii)(D). The safety significance of this event was minimal. The redundant (inboard) HPCI steam supply isolation valve was operable during these events and primary containment isolation would have occurred upon receipt of an isolation signal. In each case, HPCI was inoperable for less than the TS allowed outage time, and the Automatic Depressurization System (ADS) and all low pressure core cooling, as well as the Reactor Core Isolation Cooling system, were operable throughout the event.
2541999004 | Quad Cities 1, Quad Cities 2 | 09/10/1999 | 12/08/1999 | ML99351011 | <strong>Control Room Emergency Ventilation System Air Filtration Unit Inoperable due to Airflow Rate in Excess of Technical Specifications Allowable</strong><br /><i>Abstract:&nbsp;</i>At approximately 1445 hours on September 10, 1999, with Unit 1 and Unit 2 at 100% power, the Control Room Emergency Ventilation System (CREVS) Air Filtration Unit (AFU) was declared inoperable, when the AFU airflow rate was found to have exceeded the maximum allowed by Technical Specifications (TS). Initial investigation identified that the high AFU airflow rate was caused by the incorrect setting of a damper following a maintenance activity conducted on September 1, 1999. The damper was set incorrectly due to an incorrect measurement of the AFU airflow which resulted in the AFU inlet damper being throttled open to far. This situation went undetected until the Control Room (CR) Emergency Filtration Monthly Test was performed nine days later. Upon discovery, the damper was repositioned and the airflow rate was returned to within the TS band. The safety significance of this event was minimal. The CREVS was capable of performing its safety function. Had a Loss of Coolant Accident occurred, the CREVS was capable of meeting the CR dose requirements with the high AFU airflow rate condition. The health and safety of the general public and CR personnel were not affected. The root cause of this event was the inaccurate AFU airflow measurement taken during the post-maintenance testing conducted on September 1, 1999. This resulted in the AFU inlet damper being set incorrectly.
2541999005 | Quad Cities 1 | 12/13/1999 | 01/12/2000 | ML00367705 | <strong>"B" Control Room HVAC Inoperable Due to Refrigeration Control Unit Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>At 2045 hours on December 13, 1999, with Unit 1 and Unit 2 at 100% power, the B Control Room Heating Ventilation Air Conditioning (B HVAC) System was declared inoperable when the Refrigeration Control Unit (RCU) breaker unexpectedly tripped while its control switch was being placed in the off position. The root cause of the breaker trip was a malfunction of the switch cam follower. The safety significance of this event was minimal. The Control Room Emergency Ventilation System filtration capability was not lost and the Control Room temperature was adequately maintained during this event. Corrective actions taken include installation of a new contact assembly, proper alignment and adjustment of the cam follower.
2551999001 | Palisades | 03/10/1999 | 04/09/1999 | 9904200107 | <strong>Failure to Perform Technical Specification Surveillance Channel Check of Auxiliary Feedwater Flow Indication</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1999, an audit revealed that the channel check of Auxiliary Feedwater (AFW) [BA] flow indication specified in Technical Specification Table 4.17.6, item 6 was not being performed as required by Technical Specification 3.17.6. This channel check is specified to be performed every 12 hours when the PCS temperature is greater than 300 degrees F. However, due to a misinterpretation of the definition of a channel check, the channel check was inappropriately specified in the implementing procedure to be performed only when the AFW system was in operation. Since the AFW is not normally in operation, the 12 hour channel check was regularly not performed. There are no safety implications associated with this occurrence since AFW flow indication is utilized during several periodic surveillance tests of the AFW system which routinely demonstrate its operability. The implementing procedure has been revised.
2551999002 | Palisades | 07/22/1999 | 08/20/1999 | 9908310259 | <strong>Technical Specification Surveillance Not Completed Within Specified Frequency</strong><br /><i>Abstract:&nbsp;</i>On July 22, 1999, with the plant at 99.9% power, during an internal audit of completed Technical Specification surveillance packages, it was discovered that a past performance of Technical Specification surveillance procedure RI-38, "SIRW Tank Level Indication", was not completed within the required 18 month interval plus allowable extension. RI-38 performs the channel calibration surveillance for Safety Injection' and Refueling Water (SIRW) Tank Level, which is required in accordance with TS Section 4.17.5, Item 12. RI-38 was completed on May 25, 1993. Based on an 18 month interval plus allowable extension, RI-38 should have been completed by April 15, 1995; but was not completed until May 19, 1995. This exceeded the required 18 month interval plus allowable extension by 34 days. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B).
2551999003 | Palisades | 10/31/1999 | 03/23/2000 | ML00369605 | <strong>Reduction in Service Water Flow through Containment Air Coolers VHX-1 and VHX-2</strong><br /><i>Abstract:&nbsp;</i>On October 31, 1999, with the plant in Refueling Shutdown, the Containment Air Cooler (CAC) service water discharge check valves associated with CRCs VHX-1, VHX-2 and VHX-3 were discovered to have incurred severe damage to their internal components, including detachment of the check valve disc from the disc arm. For CACs VHX-1 and VHX-2, the disc itself was found in both cases to be wedged in the respective check valve outlet port in an orientation which was largely obstructing the outlet. For CAC VHX-3, the disc was found in the bottom of the valve, and did not restrict flow or affect operability of this CAC. As a result of the associated reduction in service water flow, CACs VHX-1 and VHX-2 may have been inoperable for a period of time in excess of the Technical Specification allowed outage time for this equipment. In accordance with this assumption, this occurrence is reportable pursuant to 10CFR50.73 (a)(2)(i)(B), as a condition prohibited by Technical Specifications. The excessive wear of the check valve internals was caused by disc fluttering as a consequence of the relatively low service water flow through the check valves which is experienced during normal plant operation. Each of the check valves has been refurbished and enhancements have been incorporated to provide a high degree of confidence that the check valves will remain intact for the duration of the forthcoming operating cycle. An operating change has been implemented to increase service water flow through the check valves to minimize fluttering of the internals and reduce the potential for excess wear.
2551999004 | Palisades | 11/02/1999 | 11/08/2000 | ML00376964 | <strong>Control Rod Drive Seal Housing Leaks and Crack Indications</strong><br /><i>Abstract:&nbsp;</i>On October 16, 1999, following shutdown of the reactor for the 1999 refueling outage, inspection of reactor head components revealed the presence of moisture and/or boric acid deposits on the exterior surfaces of three Control Rod Drive (CRD) [DRIV] seal housings. The CRD seal housing assemblies comprise a portion of the ASME Class 1 Primary Coolant System [AB] pressure boundary. The affected seal housings were removed when plant conditions permitted, and on November 2, 1999, two of the three were determined to have small through-wall cracks. All 45 seal housings were ultimately removed from the head and inspected utilizing visual, dye penetrant and eddy current examination techniques. The inspections revealed that 30 of the 45 seal housing assemblies contained small circumferential cracks. Three seal housing tubes also contained small axial cracks. Examination of spare housings showed similar crack indications. The cracking has been determined to be transgranular stress corrosion cracking, probably resulting from inadequate post-weld heat treatment which left residual stresses of sufficient magnitude to support cracking. 45 seal housing assemblies were repaired as necessary for reuse during the next operating cycle.
2551999005 | Palisades | 11/06/1999 | 12/06/1999 | ML99348023 | <strong>Charcoal Filter Not in Service During Movement of Irradiated Fuel Assemblies</strong><br /><i>Abstract:&nbsp;</i>At approximately 0845 hours on November 6, 1999 with the plant in refueling shutdown, it was discovered that the Charcoal filter [FLT] associated with the ventilation system [VG] in the fuel storage building was not in operation during fuel handling activities. Technical Specification 3.8.4 requires that the ventilation system and charcoal filter in the fuel storage building be in operation during fuel handling. This occurrence is reportable to the NRC in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Checklists are performed to ensure the ventilation equipment status meets the requirements for fuel handling activities. The event was caused by the licensed operator prematurely completing the general checklist before the ventilation requirements for fuel handling activities were met, and a lack of communication to the crew by the control room supervisor when fuel moves were authorized. There was no safety significance associated with this occurrence.
2551999006 | Palisades | 11/23/1999 | 12/22/1999 | ML99364009 | <strong>Failure to Perform Technical Specification Surveillance of Fuel Oil Storage Tank Level</strong><br /><i>Abstract:&nbsp;</i>At approximately 1745 hours on November 23, 1999, with the plant in refueling shutdown, it was discovered that the daily surveillance of fuel oil storage tank level specified by Technical Specification 4.7.3.1 had not been performed within its specified interval plus allowable extension. This occurrence is reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. Performance of the surveillance was late by approximately 12 hours. Upon discovery, the surveillance was promptly completed with satisfactory results. There was no safety significance associated with this occurrence since at all times the amount of oil stored in the tank met requirements.
2551999007 | Palisades | 12/04/1999 | 12/30/1999 | ML00367287 | <strong>Steam Generator Temperature Greater Than Indicated Primary Coolant System Temperature When Forced Circulation Was Initiated</strong><br /><i>Abstract:&nbsp;</i>Technical Specification 3.1.1.h requires that steam generator temperature be less than or equal to Primary Coolant System (PCS) loop Tcold temperature when forced circulation is initiated in the PCS; in order to ensure that an energy addition caused by heat transferred from the secondary system to the PCS will not occur. Contrary to the above, a subsequent review of steam generator and Tcold temperature indication revealed that the required steam generator temperature relationship to PCS loop Tcold temperature was satisfied on only three of four loops. With respect to one loop, steam generator temperature was approximately 7 degrees F greater than the indicated loop Tcold temperature when forced circulation was initiated. This occurrence is reportable to NRC in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. There was no safety significance associated with this occurrence. PCS pressure lowered slightly with the initiation of forced circulation, indicating that bulk steam generator temperature was less than bulk PCS temperature, and no energy addition from the secondary system to the PCS occurred.
2591999001 | Browns Ferry 1, Browns Ferry 2 | 01/15/1999 | 02/12/1999 | 9902250070 | <strong>Inoperable Control Room Emergency Ventilation System During Post Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1999, at approximately 0630 hours, Central Standard Time (CST), it was determined that both trains of the Control Room Emergency Ventilation System (CREV) were inoperable. At approximately 1305 hours CST on January 14, 1999, post maintenance operability testing following the replacement of two charcoal trays in accordance with Control Room Emergency Ventilation Unit B Flow Rate and Filter Testing Program resulted in the CREV System Priority Selector Switch being placed in the B CREV train position and B CREV train started. During the review of the conditions established by the post maintenance test activity, the Unit Supervisor questioned the fact that the switch alignment may have left A CREV train incapable of automatically starting on a valid initiation signal and, thus inoperable. The root cause of this event was failure of the procedure writers and reviewers to adequately address operation the CREV System Priority Selector Switch during system operation. Immediate corrective actions included returning A CREV to an operable state and revising applicable B CREV train procedures. This was followed by successful completion of post maintenance testing on the B CREV train. To prevent recurrence, those involved in the preparation of the CREV procedures will be counseled. Appropriate personnel will be briefed on the unique features of the CREV System Selector Switch. Other procedures involving CREV System Selector Switch operation will be revised. This report is submitted pursuant to 10 CFR 50.73 (a) (2) (i) (B) as any operation or condition prohibited by the plant's Technical Specifications.
2601999001 | Browns Ferry 2, Browns Ferry 3 | 03/08/1999 | 04/07/1999 | 9906210061 | <strong>Two Trains of Standby Gas Treatment Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 8, 1999, at approximately 2042 hours Central Standard Time (CST), it was determined that two trains of Standby Gas treatment (SGT) were inoperable. Prior to the event, on March 8, 1999, at approximately 0518 hours CST, B SGT train was removed from service for planned maintenance activities. The appropriate seven day Technical Specification (TS) Limiting Condition for Operation (LCO) for one inoperable SGT train was entered. At approximately 2038 hours CST, B SGT train was placed in service to support planned post maintenance testing activities. At 2042 hours CST, C SGT was declared inoperable due to a tripped blower motor breaker and, TS LCO 3.0.3 was entered for Units 2 and 3. Operations commenced a TS required shutdown of both operating Units 2 and 3. At 2237 hours CST, C SGT was declared operable and TS LCO 3.0.3 was exited. The cause of this event was a trip of the C SGT blower motor breaker. Subsequent testing of the tripped breaker revealed no definitive cause for the trip of the C SGT train blower breaker. This report is submitted in pursuant to 10CFR50.73 (a) (2) (i) (B) as any operation or condition prohibited by the plant's Technical Specifications.
2601999002 | Browns Ferry 2 | 05/01/1999 | 06/14/1999 | 9906210092 | <strong>Surveillance Requirements For Single Control Rod Withdrawal During Cold Shutdown Not Adequately Implemented</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1999, an inadequate implementation of a Technical Specification surveillance requirement (SR) was discovered in the performance of 2-SR-3.10.4, Verification of Surveillance Requirements for Single Control Rod Withdrawal - Cold Shutdown. During control rod drive (CRD) system testing, the SR for verification that all control rods, other than the control rod being withdrawn, are fully inserted was not performed at the required frequency. The verification was performed at the beginning of the CRD testing evolution. However, it was not subsequently performed at the required 24 hour frequency during the evolution. Although the plant surveillance instruction was written to apply to the withdrawal of one single control rod, the instruction was improperly used to document multiple withdrawals of single control rods during the testing evolution. The root cause of this event is procedural inadequacy which lead to a misinterpretation of the plant surveillance instruction 2-SR-3.10.4. Recurrence control will include revising the applicable plant surveillances to address multiple individual control rod withdrawals for testing and maintenance. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(I)(B) as a condition prohibited by the plant's Technical Specifications.
2601999003 | Browns Ferry 2 | 05/15/1999 | 06/14/1999 | 9907010262 | <strong>Automatic reactor scram due to a turbine trip</strong><br /><i>Abstract:&nbsp;</i>On May 15, 1999, at 1456 CDT, Unit 2 received an automatic scram from 100 percent reactor power due to a turbine trip that occurred during routine turbine overspeed testing. The reactor scram caused reactor water level to go below the low level setpoint (level 3) which generated a redundant scram signal and initiated the Primary Containment Isolation System, as expected. The low reactor water level signal also initiated the Standby Gas Treatment and Control Room Emergency Ventilation Systems. All systems responded as expected and all control rods fully inserted. The cause was of the turbine trip was failure of the mechanical trip cylinder to latch when hydraulically reset. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an automatic actuation of an engineered safety feature, including the reactor protection system. This report was initially submitted on June 14, 1999, as 50-260/1999001. The number has been corrected and this report is being re-submitted as 50-260/1999003.
2601999004 | Browns Ferry 2 | 05/30/1999 | 06/28/1999 | 9907070275 | <strong>Reactor Protection System Trip Resulting In Safety Feature System Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1999, at 0522 central daylight time CDT, Unit 2 received an unexpected channel 2B reactor protection system (RPS) actuation when power was lost to the 2B RPS bus. The RPS actuation resulted in the automatic actuation or isolation of primary containment isolation system (PCIS) groups 2, 3, 6, and 8. The loss of power also resulted in the initiation of stand by gas treatment (SGT), and control room ventilation (CREV). At approximately 0527 hours CDT the 2B RPS was placed on the alternate feed and the half scram was reset and the affected PCIS groups were returned to their pre-event configuration. The SGT and CREV systems were also returned to pre-event configuration. The cause of the event was the loss of the 2B RPS bus when the 2B RPS MG set shutdown. The root cause of this event was a failure of the MG set AC drive motor starter contactor coil. The failed motor starter coil on the 2B RPS MG set AC drive motor was replaced. The plant response to this event was uncomplicated and the affected systems responded as designed during the loss of power to the 2B RPS bus. Also, there were no ongoing plant activities that could have led to the RPS actuations. The RPS is designed to fulfill this safety function upon loss of initiating logic power. In this event, the loss of power was to RPS bus 2B, and because RPS bus 2A remained energized throughout the event a full scram was not initiated. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in an automatic actuation of an engineered safety feature.
2601999005 | Browns Ferry 2 | 06/17/1999 | 07/12/1999 | 9907190071 | <strong>Engineered Safety Feature (ESF) Actuation and High Pressure Coolant Injection (HCPI) Inoperable Due To Personnel Error During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1999, at approximately 1337 hours Central daylight Time (CDT) during the performance of a regularly scheduled surveillance on a Unit 2 Core and Containment Cooling System Analog Trip Unit (ATU), an unexpected isolation of the HPCI System occurred. The HPCI system was immediately declared inoperable. Upon investigation, it was determined that the isolation was due to personnel error. Specifically, contact inhibits (boots) were incorrectly placed on a relay during the surveillance. Section 7.15 of this procedure was being performed which is used to demonstrate operability of the HPCI isolation function on high steam line flow. The inhibits were removed, the HPCI isolation was reset and the system was returned to operable status. During this event, HPCI was inoperable less than 1/2 hour of the 14 days allowed by the Technical Specification LCO. Also, during the period the HPCI system was inoperable, all other required alternate safety systems were operable and would have performed their design function if called upon. Accordingly, there was no significant reduction in the degree of protection provided to public health and safety. Furthermore, the safety of the plant, its personnel, and the public was not compromised. This report is submitted pursuant to 10 CFR 50.73 (a) (2) (iv) as an event or condition that resulted in an automatic actuation of an engineered safety feature (ESF) and 10CFR50.73(a)(2)(v) as a condition that alone could have prevented the fulfillment of the safety function of a structure or system needed to mitigate the consequences of an accident.
2601999006 | Browns Ferry 2 | 06/18/1999 | 07/19/1999 | 9907260078 | <strong>Main Steam Safety/Relief Valves Exceeded the Technical Specifications Setpoint Tolerance Due to Pilot Valve Disc/Seat Bonding</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1999, Wyle Laboratories notified TVA that 5 of the 13 Unit 2 main steam safety/relief valves (SRV) pilot cartridges removed during the Unit 2 Cycle 10 refueling outage bench tested outside the Technical Specifications (TS) setpoint tolerance of +/- 3 percent. The Unit 2 SRV pilot cartridges were installed during the previous refueling outage and were in service from October 1997 to April 1999. The cause was attributed to SRV pilot disc/seat corrosion bonding at the two-stage SRV pilot disc/seat interface which resulted in drifting of the SRV setpoints. Setpoint drift is a generic concern experienced by many utilities using Target Rock Two-Stage SRVs (Model No. 7537F) in boiling water reactors and is being investigated by the Boiling Water Reactor Owners Group (BWROG) SRV Drift Fix Development Committee and the valve manufacturer. A modification was implemented in October 1998 that installed pressure switches to ensure the opening of any SRV should it fail to open at its setpoint. TVA will continue to participate in the BWROG evaluation of the long-term solution for the SRV setpoint drift problem. Based on the as-found data, the previous sensitivity evaluations, and the transient analysis, the SRV drift would not have resulted in exceeding any safety limit. Therefore, the protection afforded the health and safety of the public was not significantly reduced by this event. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS.
2601999007 | Browns Ferry 2, Browns Ferry 3 | 06/23/1999 | 07/20/1999 | 9907270243 | <strong>Surveillance Requirement Not Met For Monitoring of Primary Containment Oxygen Concentration</strong><br /><i>Abstract:&nbsp;</i>The Surveillance Requirements (SR) of Technical Specification (TS) 3.6.3.2, Primary Containment Oxygen Concentration require the primary containment oxygen concentration be verified below four percent by volume to ensure the containment remains inerted. Each unit has two oxygen analyzers, one that is normally aligned to the drywell and the other aligned to the suppression chamber. The 3B oxygen analyzer had become inoperable and in order to satisfy the SR, plant procedures require the operable monitor be manually aligned to verify both the drywell and suppression chamber are within limits as required on a seven day frequency. However on June 23, 1999, it was discovered that the SR was not being met since the operable analyzer was aligned to the drywell and no valid data had been collected or recorded for the suppression chamber in the past seven days. Further investigation revealed the same SR was not being met on Unit 2 since the operable analyzer had not been aligned to the suppression chamber within the last 7 days. Upon discovery of the failure to meet the requirements of SR 3.6.3.2.1, a 24 hour TS Limiting Condition for Operation (LCO) was entered for each unit until a valid sample was obtained. The root cause of the event was failure of the operators (utility-licensed) to adequately communicate and track the status of the inoperable oxygen sample pumps. There were no actual or potential safety consequences as a result of this event nor did this event adversely affect the safety of plant personnel or the public. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2601999008 | Browns Ferry 2 | 09/05/1999 | 10/08/1999 | 9910200172 | <strong>High Pressure Coolant Injection (HCPI) Inoperable due to a Failed Flow Controller</strong><br /><i>Abstract:&nbsp;</i>On September 8, 1999, at approximately 0610 hours Central Daylight Time (CDT) during a routine control room board-walkdown, the Unit 2 Operator observed that the HPCI flow controller output signal indication was downscale. The HPCI system was immediately declared inoperable. The HPCI controller was replaced, HPCI operability testing was completed satisfactorily, and the system was returned to an operable status at approximately 1520 hours CDT on September 8, 1999. Upon investigation of data taken from the plant's Integrated Computer System history, it was determined that the controller began experiencing an erratic signal at approximately 1248 hours CDT on September 5, 1999. At approximately 1320 hours CDT on September 5, 1999, the controller lost power. During this event, HPCI was inoperable for a period of approximately three days out of the fourteen days allowed by the Technical Specifications Limiting Condition for Operation. During the period of time that HPCI was inoperable, all other required safety systems were operable and would have performed their design function if called upon. Accordingly, there was no significant reduction in the degree of protection provided to public health and safety. This report is submitted pursuant to 10CFR50.73 (a)(2)(v) as a condition that alone could have prevented the fulfillment of the safety function of a structure or a system needed to mitigate the consequences of an accident.
2601999009 | Browns Ferry 2 | 09/15/1999 | 10/14/1999 | 9910200198 | <strong>Manual Reactor Scram due to an EHC leak</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1999, at 1825 CDT, Unit 2 operators manually scrammed the reactor from 54 percent power due to an Electro-Hydraulic Control (EHC) [TG] leak that could not be isolated. The reactor had been at 100 percent power prior to the leak. As expected, the reactor scram caused reactor water level to go below the low level setpoint (level 3) which generated a redundant scram signal and initiated Primary Containment Isolation, Standby Gas Treatment, and Control Room Emergency Ventilation Systems. All systems responded as expected and all control rods fully inserted. The cause of the leak was failure of a stainless steel tubing connection that was installed for the power uprate modification package to measure pressure perturbations in the EHC system. The damaged tubing was removed and the connection plugged. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in a manual actuation of an engineered safety feature, including the reactor protection system.
2601999010 | Browns Ferry 2 | 09/17/1999 | 10/15/1999 | 9910260031 | <strong>Reactor Scram due to Moisture Separator High Level</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1999, at 1702 Central Daylight Time, during reactor startup operations at 30 percent power, a high water level in main steam moisture separator 2C2 caused a Unit 2 main turbine trip. This resulted in an automatic reactor scram on turbine stop valve closure. Safety systems responded as expected and all control rods fully inserted. The cause of the high level in the moisture separator was a failed high level controller for the 2C2 moisture separator drain reservoir. The 2C2 reservoir level transmitter and relays were replaced and tested satisfactorily. Unit 2 was restarted on September 18, 1999. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in an actuation of an engineered safety feature, including the reactor protection system.
2601999011 | Browns Ferry 2 | 11/18/1999 | 12/17/1999 | ML99363046 | <strong>High Pressure Coolant Injection (HPCI) Inoperable Due to Oil System Breach</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1999, at approximately 1700 hours Central Standard Time (CST) work was begun to replace the Unit 2 High Pressure Coolant Injection (HPCI) System Oil Cooler Discharge Temperature Switch TS-73-52. This switch is used to monitor the HPCI System oil temperature and actuates a control room alarm if HPCI system oil temperature reaches the alarm set point. During the switch replacement, the switch cover was removed, the wires were lifted and the switch was extracted. Instrument Maintenance (IM) craftsmen then noticed the presence of oil on the switch. Inspection of the mounting location for the switch revealed that the oil system had been unexpectedly breached. Contrary to the Unit 3 drawing provided in the work package and a local tag that indicated the presence of a thermo-well, there was no thermo-well in place for mounting the switch. The Unit 2 drawing correctly indicated no thermo-well. The IM craftsmen installed the new switch, obtained the necessary pipe sealant and sealed the penetration. The HPCI oil system was breached for approximately 5 minutes. The event was caused by inattention to detail during the planning of the activity. On November 22, 1999, it was determined that HPCI had been inoperable during the time the oil system was breached. This condition was reported to the NRC pursuant to 10 CFR 50.72 (b)(iii)(D). This report is submitted pursuant to 10CFR 50.73 (a) (2) (v) as a condition that alone could have prevented the fulfillment of the safety function of a structure or a system needed to mitigate the consequences of an accident.
2611999001 | Robinson 2 | 09/27/1999 | 12/17/1999 | ML00367286 | <strong>Inadvertent De-energization of 480 Volt Bus Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1999, at approximately 2233 hours EDT with the plant in cold shutdown conditions, preventive maintenance was being conducted on a breaker for Circulating Water Pump B in the 4160 volt (V) Bus room. An electrician inadvertently contacted the trip/close switch for 4160 V breaker 52/15. This de-energized the transformer that normally feeds 480 V Bus E-2. The "B" Emergency Diesel Generator automatically started, as a result of an under-voltage condition, as designed and loaded to the bus, restoring power to Bus E-2. The operating "B” Residual Heat Removal (RHR) pump, stopped as a result of the loss of power to bus E2. RHR pump "A" was manually started by the operators which restored shutdown cooling within two minutes. The temperature of the Reactor Coolant System was estimated to have risen </= two degrees Fahrenheit. The cause of this event has been determined to be the technician's inattention to detail relative to his surroundings. The individual involved was counseled regarding inattention and the need for awareness of his surroundings. Corrective actions have been implemented to heighten worker awareness prior to the job and add visual reminders in the form of barrier markers with warning signs at the entrances to the area. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an event that resulted in an automatic actuation of an engineered safety feature.
2611999002 | Robinson 2 | 10/04/1999 | 11/24/1999 | ML99335005 | <strong>Incorrect Gain Settings for Delta-Temperature Trips</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1999, at approximately 1900 hours, the H.B. Robinson Steam Electric Plant, Unit No. 2 was in the defueled condition. The calibration data sheets for the Overpower Delta-Temperature (OPDT) trip setpoint were found to contain non-conservative gain settings for dynamic compensation of the setpoint. The cause was a failure to incorporate gain settings from scaling calculations for the OPDT setpoint into calibration procedures. Additionally, it was discovered that scaling calculations for the Overtemperature Delta-Temperature (OTDT) trip setpoint were not incorporated correctly into procedures and contained an error. As a result, the dynamic compensation for the OTDT setpoint was non-conservative below about 65 percent reactor power. Both conditions have been found to be bounded by the safety analyses. The scaling calculations, calibration procedures, and gain settings for the Delta-Temperature trip setpoints have been corrected. A change to the calculation control procedure will be made to require an impact review when calculations are changed. This event is reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2631999001 | Monticello | 02/15/1999 | 03/17/1999 | 9903240141 | <strong>HPCI High Steam Flow Isolation During Quarterly Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>During the performance of the quarterly High Pressure Coolant Injection (HPCI) surveillance test, a high steam flow signal isolated the steam to the HPCI turbine. The surveillance test was terminated. The high steam flow signal was not caused by any piping integrity problems. The cause of this event is an inadequate surveillance procedure. The surveillance procedure steps did not ensure that the high steam flow setpoint would be avoided. The surveillance procedure has been revised. Other procedures have been reviewed and changed as necessary. A means of identifying that steam flow is greater than the high steam flow setpoint will be investigated. Training on the lessons learned from this event will be provided to the engineering technical staff and operations personnel.
2631999002 | Monticello | 03/29/1999 | 05/11/1999 | 9905200087 | <strong>Procedures Did Not Require an LCO Entry During Suppression Pooling Cooling</strong><br /><i>Abstract:&nbsp;</i>The condition involves an event sequence that results in available Emergency Core Cooling Systems (ECCS) being reduced to less than that assumed in the current USAR safety analysis. The sequence is: one division of Residual Heat Removal (RHR) System is in suppression pool cooling mode, a large break loss of coolant accident occurs, offsite power is lost, and the same division's emergency diesel generator fails. In this sequence, the suppression pool cooling valves receive a close signal, but the failure of that division's emergency diesel generator would prevent the valves from closing. Part of the Low Pressure Coolant Injection (LPCI) flow would therefore be diverted to the suppression pool. Original design of RHR did not consider single failure vulnerabilities during accidents when initiated from a secondary mode of operation. The event sequence above had not been previously recognized to reduce the complement of ECCS pumps to below the minimum number of pumps assumed in the USAR safety analysis. Therefore, plant procedures did not require that a limiting condition for operation (LCO) be entered during operation of RHR in suppression pool cooling. Operating procedures were changed to require that the LPCI function be declared inoperable when in the suppression pool cooling mode. ECCS systems have been reviewed for similar problems.
2631999003 | Monticello | 04/12/1999 | 05/12/1999 | 9905180150 | <strong>Emergency Service Water Pump Failure Causes HPCI Inoperability</strong><br /><i>Abstract:&nbsp;</i>The #13 Emergency Service Water pump failed to start during the quarterly surveillance test. High Pressure Coolant Injection and Division I Emergency Core Cooling System equipment were declared inoperable since the #13 Emergency Service Water pump provides the backup room cooling water. Due to a problem with the emergency service water pump discharge check valve, service water had been flowing in the reverse direction. This flow deposited silt in the pump internals and prevented the pump shaft from rotating freely. The pump shaft was mechanically freed and the check valve was repaired. The pump was successfully re-tested. The surveillance frequency for the emergency service water pumps has been temporarily increased. The preventive maintenance frequency for the discharge check valve will be reviewed to determine if more frequent maintenance is appropriate. Other pumps in the intake structure will be evaluated for this type of vulnerability.
2631999004 | Monticello | 04/22/1999 | 05/24/1999 | 9906040173 | <strong>Feedwater Controller Power Supply Failure Causes Low Reactor Water Level Scram and Group 2 & 3 Isolations; Subsequent Events Cause HPCI to become Inoperable</strong><br /><i>Abstract:&nbsp;</i>Failure of a digital feedwater control system (DFCS) power supply caused one feedwater regulating valve to close and the other to lock-up in its pre-existing condition. Attempts to manually control reactor water level failed due to the DFCS failure, resulting in an automatic reactor low water level scram. Subsequently, steam lines for the main steam system, High Pressure Coolant Injection system (HPCI) and Reactor Core Isolation Cooling system (RCIC) were overfilled, causing HPCI and RCIC to become inoperable for about 1/2 hour. Water level was restored to shutdown normal conditions approximately one hour later. The DFCS power supply failure was due to an oxidized connection in a plus 5 volt power supply. The overfill was caused by the failed level indications and misleading Safety Parameter Display System (SPDS) indications. Concern about using reactor water level indications led to bypassing the Reactor Feedwater Pump (RFP) high water level trip. Three power supplies were replaced and all associated connections cleaned. Several operating procedures were revised, temporary monitoring instrumentation was added and extensive testing was performed. Operator training was provided on several topics.
2631999005 | Monticello | 05/08/1999 | 06/07/1999 | 9906140198 | <strong>Manual Scram Inserted When Pressure Transient Closes Air Ejector Suction Isolation Valves and Trips Off-gas System</strong><br /><i>Abstract:&nbsp;</i>A rapid recombination of hydrogen and oxygen in the Off-gas system caused a pressure transient that initiated an isolation of valves between the main condenser and the air ejectors. With no means of removing off-gas, operations personnel reduced power and manually scrammed the reactor. Following the reactor scram, low steam line pressure caused a Group 1 containment isolation which closed the main steam isolation valves. Three safety relief valve openings occurred while the main steam isolation valves were closed. The main steam isolation valves were reopened, and the plant was placed in cold shutdown. The rapid recombination of hydrogen and oxygen was caused by recombiner catalyst migration. The Group 1 containment isolation was caused by the reactor mode switch being in RUN when the steam line pressure decreased to the Group 1 low pressure set point. All safety systems performed as designed. Catalyst has been removed from the off-gas piping up to the recombiner. A time delay was added to the high pressure trip for the air ejector suction isolation valves. Training was provided to all licensed operators.
2631999006 | Monticello | 06/02/1999 | 07/02/1999 | 9907090279 | <strong>During Quarterly Surveillance HPCI Delcared Inoperable Due to Drain Pot Alarm</strong><br /><i>Abstract:&nbsp;</i>High Pressure Coolant Injection was declared inoperable upon receipt of a high drain pot level alarm on the steam supply line. A malfunctioning steam trap was not properly removing water from the drain pot. Steps were taken to provide assurance that the steam supply system is effectively removing condensate from the steam supply line while HPCI is in standby. The HPCI surveillance test procedure will be revised. The steam trap will be replaced. The scope, frequency and content of the current safety related steam trap preventive maintenance program will be evaluated.
2631999007 | Monticello | 06/10/1999 | 07/09/1999 | 9907160034 | <strong>HPCI Test Return Valve Unable to Close Against Maximum Expected Differential pressure</strong><br /><i>Abstract:&nbsp;</i>While responding to issues raised by Generic Letter 96-05 (Periodic Verification of Design-Basis Capability of Safety-Related Motor-Operated Valves), it was determined that the thrust required to close the High Pressure Coolant Injection test return valve against the maximum expected differential pressure exceeds the maximum allowable valve thrust. The valve is open during HPCI surveillance testing or when HPCI is used in pressure-control or level-control mode. It receives a signal to close in the event of an Emergency Core Cooling System (ECCS) initiation. In this situation, it could experience the maximum differential pressure, fail to fully close, and prevent HPCI from achieving the required injection flow. Analytical methods used in the original plant design did not accurately predict valve performance. Procedures have been revised to declare HPCI inoperable whenever the valve is open. All other safety related motor-operated valves have been evaluated as required by Generic Letter 96-05. These evaluations have resulted in either confirming the valve performance capability or requiring that the valve be declared inoperable when not positioned to support its safety function. These evaluations will be verified.
2631999008 | Monticello | 10/19/1999 | 11/18/1999 | ML99330018 | <strong>Loss of Speed Control for Reactor Core Isolation Cooling System Turbine Due to Loose Gasket Material Preventing Closure of Governor Valve</strong><br /><i>Abstract:&nbsp;</i>During performance of Reactor Core Isolation Cooling (RCIC) System tests, with reactor pressure at rated conditions, it was found that RCIC flow and turbine speed could not be lowered using the flow controller in either automatic or manual mode. The turbine was tripped manually. Investigation determined that the cause of this condition was obstruction of the turbine governor valve with material from a deteriorated undersized gasket installed between the RCIC trip throttle valve and the downstream governor valve. The gasket was replaced with a gasket of the proper size and the RCIC was successfully tested and returned to service.
2651999001 | Quad Cities 2 | 02/17/1999 | 03/15/1999 | 9903250171 | <strong>An unplanned Engineered Safeguards Feature (ESF) actuated on Unit 2 when the "A" channel of the Reactor Protection System (RPS) bus de-energized due to an aging related failure of a voltage regulator transformer that was not included in the Preventative</strong><br /><i>Abstract:&nbsp;</i>At approximately 0020 on 02171999, with the reactor at 100% power, the 2A Reactor Protection System (RPS) bus Electrical Protection Assembly (EPA) 2AB-1 breaker tripped open on undervoltage. The 2A RPS bus was being supplied by the reserve electrical feed. An RPS channel 2A 1/2 scram, 1/2 group 1 and 1/2 group 2 isolations and a Reactor Water Cleanup system isolation occurred. As part of the Engineering Safeguards Feature (ESF) actuation and partial group 2 isolation, the expected Primary Containment Isolation (PCI) valves closed. The RPS bus was re-energized at 0036 on 02171999. The cause of the EPA 2AB-1 breaker tripping was attributed to an undervoltage condition when the RPS bus reserve electrical feed Voltage Regulating Transformer (VRT) failed. The failure mode was aging of discreet components, i.e., a control transformer and circuit board contained within the transformer. The root cause was the fact that the VRT was not included in the preventive maintenance program. This original equipment was installed in 1982. The control transformer and circuit board on Unit 2 were replaced on 02191999 and the VRT was returned to service. The control transformer in the VRT for Unit 1 is scheduled for replacement by 06301999. Engineering will determine what type and frequency of preventive maintenance that should be performed on the VRT's. There was no safety significance to this event. The failure of the RPS EPA breaker did not increase risk to the health and welfare of the public or to onsite personnel. The partial PCI group 1, 2 and 3 initiations occurred as expected and valves isolated, as required. All required ESF and emergency systems were fully capable of performing their design functions.
2651999002 | Quad Cities 2 | 05/27/1999 | 06/25/1999 | 9907010175 | <strong>Reactor Building Secondary Containment Penetration no sealed</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1999 station personnel discovered an unsealed one inch diameter pipe penetrating secondary containment. The secondary containment was declared inoperable, and operators entered Technical Specifications (TS) 3/4.7.N action statement 1, which requires restoring secondary containment within 4 hours or placing the plant in at least hot shutdown within the next 12 hours. The immediate corrective action to restore secondary containment was to install a plug in the piping and issue a temporary modification for the plug installation. The TS action statement was then exited at 1525 hours. The condition has existed since installation of a modification in 1981. Therefore, this report is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's TS. The root cause of this event was the lack of proper work control during installation of a modification in 1981. The current work control process and the modification process have changed significantly since 1981. These new processes would preclude a similar occurrence. This event was not safety significant because the Standby Gas Treatment System had adequate capacity to maintain secondary containment at a negative pressure with an assumed one inch diameter pipe open.
2651999003 | Quad Cities 2 | 08/25/1999 | 11/24/1999 | ML99340047 | <strong>Reactor Core Isolation Cooling Overspeed Trip due to a Failed Governor Control Power Resistor</strong><br /><i>Abstract:&nbsp;</i>On August25, 1999, at 10:15 a.m., the Unit 2 Reactor Core Isolation Cooling (RCIC) system turbine tripped on overspeed immediately after the opening of the steam inlet valve. RCIC was being functionally tested for a return-to-service following maintenance and testing. The root cause of this event is failure of the 125 vdc governor power supply resistor. Corrective actions include replacement of the resistor on Unit 2, replacement of this resistor on Unit 1 and the implementation of a preventive maintenance frequency for the resistor. A search of Licensee Event Reports, Operating Experience and Deviation Reports was performed and there were no previous occurrences of RCIC overspeed events due to a resistor failure. This trip occurred while the RCIC system was in a planned Limiting Condition for Operation maintenance activity and the system was returned to an operable condition within the allowed outage time. In addition, the High Pressure Coolant Injection system was available during this event. Therefore, there was no impact with respect to safety of the plant.
2651999004 | Quad Cities 2 | 11/02/1999 | 11/29/1999 | ML99342021 | <strong>High Pressure Coolant Injection Subsystem Steam Exhaust Vacuum Breaker Failure to Close During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1999, at 1901 hours, the High Pressure Coolant Injection (FIPCI) Steam Exhaust Line Vacuum Breaker 2- 2399-65 valve failed to meet the acceptance criteria of QCOS 2300-18, "HPCI Steam Exhaust Vacuum Breaker Line Check Valves 1ST Functional Test," when it was tested in the closed direction. After disassembly and inspection, the 2-2399-65 valve was re-assembled and satisfactorily tested. The Unit 2 HPCI subsystem was declared operable at 1932 hours on November 3, 1999. Although no foreign material was discovered, alternative causes were ruled out through investigation, and foreign material underneath the valve disk during the test failure was determined to be the root cause of this event. The safety significance of this event was minimal. The redundant in-line vacuum breakers passed their testing at the time of this event; therefore, primary containment was intact. The affected Unit 2 HPCI turbine exhaust piping will be flushed during the next refueling outage.
2661999001 | Point Beach 1 | 01/05/1999 | 05/18/1999 | 9905270105 | <strong>Safety Injection Recirculation Line to Refueling Water Storage Tank Frozen</strong><br /><i>Abstract:&nbsp;</i>On 1/5/99 PBNP discovered that the Unit 1 common mini-recirculation flow line return to the refueling water storage tank (RWST) for the SI and containment spray (CS) pumps would not pass flow. The line was frozen due to a partial failure of the freeze protection heat tracing for this piping. Both SI pumps and both CS pumps were declared out of service and the provisions of TS 15.3.0.B were entered at 1240 CST. ENS notifications were made at 1412 for a condition outside the design bases and at 1515 for initiation of a shutdown required by TS. A notice of enforcement discretion (NOED) was requested and approved by the NRC to permit six additional hours to complete a realignment and 50.59 evaluation to permit use of the full flow SI test line as an alternate recirculation path for the B SI pump and to complete an operability determination for the CS pumps. The NOED was verbally approved at 1820. At 2234 efforts to thaw the mini-recirculation line were successful. At 0026 on 1/6/99, the B SI pump and both CS pumps were returned to service and the action statement of TS 15.3.0.B was exited. Unit 1 returned to full power at 0924. At 2108 the A SI pump was declared operable using the mini-recirculation line. A safety assessment concluded that the SI pumps were operable during the event and would have performed their design function under postulated accident or transient conditions.
2661999002 | Point Beach 1, Point Beach 2 | 01/22/1999 | 02/22/1999 | 9902250220 | <strong>Technical Specification Required Shutdown of Unit 1 Due To Potential Failure of 4160 Volt Electrical Breakers</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1999, WE determined that several 4160 volt breakers were susceptible to a failure that could prevent the breaker from changing position. An insulating block (a component of the breaker blowout magnets), whose adhesive had degraded with age, could become loose and fall into the breaker mechanism and prevent breaker operation. Among the affected breakers were the Unit 1 reactor coolant pump breakers. Technical specifications required the reactor coolant pump breakers to be operable and specified an eight hour action statement in the limiting condition for operation. Since the problem could not be addressed within the time allowed, Unit 1 was promptly shut down in a controlled manner to effect breaker modification. Initiation of this shutdown was reported to the NRC operations center as required. The adverse condition on affected breakers was corrected January 23 and Unit 1 was started up on January 24. Unit 2 was in a refueling outage during this period and therefore its operation was not immediately impacted by this condition.
2661999003 | Point Beach 1, Point Beach 2 | 04/06/1999 | 05/06/1999 | 9905170093 | <strong>Technical Specification Surveillance Requirement for ECCS and Containment Spray Not Fully Implemented</strong><br /><i>Abstract:&nbsp;</i>While evaluating an external industry operating event, Point Beach Nuclear Plant (PBNP) personnel determined that the requirements of Technical Specification (TS) surveillance requirement 15.4.5.II.B.2, "Emergency Core Cooling System and Containment Cooling System Tests," have not been fully implemented. The licensee identified 19 valves in Unit 1 and 21 valves in Unit 2 that were not being verified as being in their proper position every 31 days. All the valves were verified to be properly positioned. Procedures have been revised to verify the positioning of these valves each month. This event resulted from a more conservative interpretation of which valves could impact the safety function of the system. The safety impact was negligible. This event was reportable in accordance with 10 CFR 50.73 (a) (2) (i).
2661999004 | Point Beach 1, Point Beach 2 | 04/20/1999 | 09/02/1999 | 9909090041 | <strong>Fuel Oil Transfer Pump Cable in the AFW Pump Room Outside Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>While conducting a revalidation and verification project for the Point Beach Nuclear Plant 10 CFR 50 Appendix R fire protection programs, the licensee discovered that a postulated fire in the north half of AFW room fire zone could potentially result in the disruption of the electrical power supply to the Fuel Oil Transfer Pump, P-206A, which provides a continuous fuel oil supply to the G-01 Emergency Diesel Generator (EDG). Following the postulated fire, G-01 is the only available emergency backup power source to provide emergency power to the Unit 1 "A" Train 4160 Volt Safeguards Bus (1A-05). Fire rounds in the AFW pump room (FZ 304) were increased to hourly, in excess of the normal Appendix R compensatory measure. Use of transient combustibles and issue of ignition permits in the fire zone have been curtailed. This event was reported in accordance with 10 CFR 50.72 as a condition outside the Appendix R design basis for the plant. Subsequent analysis has verified that the on-site combustion turbine (G-05) can be used as an alternate source of power to the 1A05 bus following the postulated fire. Procedures are being developed to facilitate using G-05 as an Appendix R credited power source. During development of these procedures, we concluded that the current procedures do not provide adequate guidance to the operating staff to address all of the potential actions necessary in the event of a fire in the AFW pump room. Additional corrective actions, including physical modifications, are planned.
2661999005 | Point Beach 1 | 05/14/1999 | 06/11/1999 | 9906210116 | <strong>Steam Leak From Low Pressure Feedwater Heater</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1999, with the Unit 1 operating at full power, Point Beach Nuclear Plant (PBNP) experienced a steam leak from the rupture of the shell side of the #4B feedwater heater. In response to this incident, the Unit 1 reactor was manually tripped and the steam to the #4B feedwater heater was secured. In response to a decreasing pressurizer level, a manual safety injection signal was initiated. The pressurizer level was restored with no need for actual ECCS injection. Plant systems operated as anticipated in response to the incident. There were no personnel injuries or significant incidental equipment damage. An inspection of the Unit 1 #4 feedwater heaters revealed shell wall thinning in the vicinity of the inlet nozzle deflector plates. The apparent cause of the rupture and wall thinning was a combination of steam impingement and flow accelerated corrosion. Inspection of the Unit 2 heaters revealed no comparable wall thinning. Following repair of the feedwater heaters, Unit 1 was returned to operation after nine days.
2661999006 | Point Beach 1, Point Beach 2 | 07/20/1999 | 08/19/1999 | 9908250093 | <strong>Postulated Fire and Inability to Isolate PORV Outside Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>While reassessing the fire hazard evaluation for the central area of the 26 foot elevation of the Point Beach Nuclear Plant (PBNP) Primary Auxiliary Building (PAB) the licensee discovered that a fire, although unlikely, could be postulated in this fire zone which could result in spurious operation of a primary system Power Operated Relief Valve (PORV) and could also preclude the ability of the plant staff to isolate that valve. A fire could cause the PORV block valves to fail in the open position and, at the same time, create a hot short on a PORV cable which could cause a PORV to open. This event can be mitigated by securing and venting instrument air (IA) to containment which would fail the PORV closed. However, the valves to do this are located in the same fire zone and may not be accessible until the postulated fire is extinguished. A failure to promptly shut the PORV could result in the failure to meet the safe shutdown performance criteria of 10 CFR 50 Appendix R. Compensatory measures, including hourly fire rounds and procedure changes, have been initiated until permanent corrective actions can be evaluated and implemented. A safety assessment has been completed and concluded that due to the low probability of the postulated fire and the ability to address the consequence of a failure to isolate an open PORV using existing abnormal operating procedures, the impact on the health and Safety of the plant staff and public is not significant.
2661999007 | Point Beach 1 | 08/31/1999 | 09/30/1999 | 9910050288 | <strong>Cable Tray Fire Stops Do Not Meet Appendix R Exemption Requirements</strong><br /><i>Abstract:&nbsp;</i>While conducting a review of Appendix R alternate and dedicated safe shutdown exemption requirements, the Licensee for the Point Beach Nuclear Plant (PBNP) determined that cable tray fire stops intended to preclude a single fire from engaging the power cables for all three charging pumps were installed in the wrong location. The exemption was granted on July 3, 1985 to Section III.G.2.b of Appendix R due to the presence of intervening combustibles between redundant charging pump cables. The fire stops were installed in 1986; however, the post modification validation and verification during the modification close out process were not adequate to identify the installation error. A similar installation for a PBNP Unit 2 exemption was verified to be correct. A new modification has been initiated to provide a three hour rated fire barrier between the redundant charging pump power cables. Compensatory measures, including hourly fire rounds, have been initiated until the permanent corrective actions are complete. A safety assessment of this condition has determined that an alternate means of reactor coolant inventory control is available using a safety injection pump; however, this source would not satisfy the Appendix R performance goals which makes this event reportable as a condition outside the plant's Appendix R design basis.
2661999008 | Point Beach 1, Point Beach 2 | 10/04/1999 | 11/03/1999 | ML99316006 | <strong>Postulated Fire Could Lead To Loss of Redundanta Trains of Charging Capicity</strong><br /><i>Abstract:&nbsp;</i>While conducting a review of Appendix R alternate and dedicated safe shutdown analyses and exemption requirements, the licensee determined that for certain postulated Appendix R design basis fires, a hot short on a conductor of the control cable for valve CV-112C the normal suction supply from the volume control tank (VCT) to the charging pumps, could cause the valve to shut. The same fire could also damage the cables for the alternate charging water supply valve, CV-112B and prevent that valve from opening. Under these conditions, there is a potential for causing damage to any of the operating, positive displacement charging pumps if an alternate charging water supply is not established or the pump(s) are not turned off. Compensatory measures consisting of increased fire rounds and administrative controls on charging pump operations have been initiated. A plant modification is planned to eliminate the potential for this fire induced spurious valve operation. A safety assessment of this condition has determined that an alternate means of reactor coolant inventory control is available using a safety injection pump; however, this source would not satisfy the Appendix R performance goals which makes this event reportable as a condition outside the plant's Appendix R design basis.
2661999009 | Point Beach 1, Point Beach 2 | 10/11/1999 | 11/10/1999 | ML99325023 | <strong>Design Basis For Control Room/Cable Spreading Room Fire Barrier Not Fully Implemented</strong><br /><i>Abstract:&nbsp;</i>While investigating a degradation of the fire barrier between the Point Beach Nuclear Plant (PBNP) control room and the adjacent cable spreading room (CSR), PBNP fire protection engineers identified a deficiency in the application of a plant modification which was intended to upgrade that fire wall to a three hour fire barrier rating. This constituted a failure to meet a design basis commitment from Appendix A to BTP APCSB 9.5.-1 as documented in an NRC Safety evaluation report. We concluded that this event should be considered as a condition outside the design basis for fire protection and was reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B). Corrective actions consisted of preparation of a Fire Protection Engineering Evaluation in accordance with plant procedures and NRC Generic Letter 86-10, and a 10 CFR 50.59 evaluation which provides justification for the as-found condition as providing an acceptable fire separation barrier as defined by the requirements of 10 CFR 50 Appendix R. Since the separation criteria of Appendix R for the CSR has been documented as being satisfied, there was no impact on the health and safety of the public or plant staff from this event.
2661999010 | Point Beach 1, Point Beach 2 | 10/25/1999 | 11/19/1999 | ML99331004 | <strong>Inadequate Appendix R Emergency Lighting</strong><br /><i>Abstract:&nbsp;</i>While conducting a verification and validation walkdown and evaluation of equipment which may have to be operated in the event of a postulated 10 CFR 50 Appendix R safe shutdown fire, PBNP fire protection engineers identified a number of safe shutdown equipment locations, and/or access/egress pathways to these equipment locations, which appeared, based on engineering judgment, to have deficient emergency lighting provisions. Emergency lighting is required for these locations by Appendix R, Section III.J. These locations are being evaluated for possible adjustments of existing lighting fixtures or installation of additional emergency lighting provisions. This event was reported to the NRC on October 25, 1999, as a condition outside the design basis of the plant.
2661999011 | Point Beach 1 | 11/04/1999 | 12/02/1999 | ML99342017 | <strong>Main Steam Safety Valve Lift Set Point Exceeds Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>This report describes the discovery during routine Technical Specification surveillance testing that two main steam safety valves (MSSVs), MS-2012 and MS-2013, had lift set points which exceeded the licensee's acceptance criteria. The lift set point for MS-2012 also exceeded the ASME B&PV Section XI acceptance criteria. This condition was reported to the NRC by ENS telephone call on November 4, 1999, in accordance with 10 CFR 50 72(b)(2)(i). This condition probably existed since 1995 when these MSSVs were last tested and adjusted while installed using a lift assist device. The valves are now tested off site at a vendor facility using full pressure boiler testing. The PBNP Technical Specifications required additional MSSV testing as a result of this failure to meet acceptance criteria. This resulted in all eight MSSVs being sent off site for testing. The lift set points for the rest of the MSSVs were found to be acceptable. The lift set points for MS-2012 and MS-2013 were reset to the specified 1125 psig.
2661999012 | Point Beach 1 | 11/04/1999 | 12/02/1999 | ML99342016 | <strong>Through Wall Defect On Steam Generator Drain Valve Weld</strong><br /><i>Abstract:&nbsp;</i>This report discusses the discovery of an approximately 1/64 inch through-wall defect or flaw on the upstream weld for valve 1RC-526A, the isolation valve for the Unit 1 “A” steam generator channel head drain. This indication was discovered while conducting an informational liquid dye penetrant examination of that weld due to the visual identification of boric acid crystals on the weld. The unit was shutdown at the time of this discovery. A four hour non-emergency event notification was made to the NRC at 0307 CST on November 4, 1999, in accordance with 10 CFR 50.72(b)(2)(i) for an event discovered while the plant was shutdown that, had it been discovered while the reactor was operating, would have resulted in the principal safety barriers being seriously degraded. The weld has been replaced.
2661999013 | Point Beach 1 | 11/08/1999 | 12/08/1999 | ML99350013 | <strong>Inadvertent ESF Actuation During Post Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>On November 8, 19999, while completing post-maintenance testing of a safety injection (SI) pump, an inadvertent, unplanned Engineered Safety Feature (ESF) actuation occurred. The actuation of a safety injection signal occurred when a test jumper was installed to simulate an auto start signal for the SI pump motor. Point Beach Unit 1 was shutdown, cooled down and defueled at the time of this event. Systems and components required to operate as a result of the SI signal functioned as expected for the plant conditions. The cause of the event was a incorrect step in the PMT work plan. A NRC ENS notification was made at 1730 CST pursuant to 10 CFR 50.72(b)(2). The only safety significant result of this ESF was the isolation of service water to the spent fuel pool cooling heat exchangers. Service water was restored within approximately 50 minutes. The time to boil for the spent fuel pool at the time of this event was greater than 19 hours.
2661999014 | Point Beach 1 | 12/28/1999 | 01/27/2000 | ML00367945 | <strong>Containment Upper Hatch Outer Door Vent Valve Found Open</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1999, the outer door vent valve in the 56 foot containment access air lock was discovered to be in the open position. The valve was immediately shut. An investigation determined that the air lock was last used for a containment entry on December 24, 1999, and it was probable that the vent valve was open for that four day period. During that time the inner door was properly closed therefore containment integrity as defined in the Technical Specifications (TS) was satisfied at all times. However, with the vent valve open the outer door was considered to be inoperable and the provisions of TS LCD 15.3.6.A.l.d.(1) that require the operable inner door to be locked within 24 hours was not met. This event is reportable as a condition prohibited by TS. There was no safety significance to this condition since containment integrity was maintained throughout the event.
2691999002 | Oconee 1, Oconee 2, Oconee 3 | 03/17/1999 | 04/15/1999 | 9904210011 | <strong>Technical Specification Requirement Not Met Due To An Inadequate Process</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1999, Oconee Units 1, 2, and 3 were at 100% power. A review of operator actions in the Emergency Operations Procedure identified a problem associated with the ability to establish flow in both Low Pressure Injection (LPI) discharge headers within 15 minutes. This requirement was specified in Technical Specification (TS) 6.4.1.k. and is associated with establishing LPI following a core flood line break accident. Validation exercises on the simulator and discussions with Operations shift personnel concluded that the 15 minute time frame would not be met when applying certain single failures. Establishing LPI flow following a core flood line break is not time critical since one High Pressure Injection train and one Core Flood Tank provide sufficient core cooling. The root cause of this event is an inadequate validation process. The 15 minute time frame was not validated initially nor when the Emergency Operations Procedure was implemented because it was contained in a referenced procedure that was not validated. Corrective actions include completing the operator action review and revising the licensing basis to accurately reflect long term cooling requirements following a core flood line break accident. This event is considered to have no significance with respect to the health and safety of the public.
2691999003 | Oconee 1, Oconee 2, Oconee 3 | 05/12/1999 | 06/07/1999 | 9906140036 | <strong>Low Temperature Overpressure Protection Inoperable: Misapplication of Design Input</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1999, with Oconee Units 1, 2 and 3 in Mode 1 at approximately 100 percent power, it was determined that one train of Low Temperature Overpressure Protection (LTOP) Administrative Controls (ACs) required by Technical Specification 3.4.12 were deficient. These ACs are intended to assure operators have at least 10 minutes to mitigate a LTOP event. The deficient ACs would not have allowed 10 minutes for operator action if all pressurizer heaters were actuated with nitrogen (N2) in the pressurizer. This condition could have previously existed for more than the four hour Completion Time of TS 3.4.12, Required Action F.1, to implement compensatory measures. At 1329 hours, the NRC was notified via the Emergency Notification System. The presence of N2 in the pressurizer had not been adequately considered in prior LTOP analyses that established limits and setpoints for the LTOP ACs. The cause of this error was a misapplication of design input. After concluding that the effects of N2 in the pressurizer had not been analyzed, Operations was conservatively notified to implement the required compensatory measures. Following reanalyzes of the LTOP scenarios, the setpoints and limits of the ACs were revised to assure operators have at least 10 minutes to mitigate potential LTOP events. This event was of no safety significance.
2691999004 | Oconee 1 | 06/10/1999 | 07/08/1999 | ML99361030 | <strong>Pressurizer Relief Valve Setpoint Found Out-of-Tolerance</strong><br /><i>Abstract:&nbsp;</i>On June 10, 1999, with Oconee Unit 1 in mode 6 (refueling), notification was received from Wyle Laboratories that the initial as-found lift pressure (2600 psig) of one reactor Coolant System (RCS) Pressurizer Safety Valve, during testing, was greater than the Technical Specification limits of 2500, psig including tolerance of +/- 25 psi. The cause is believed to be set point drift. Corrective action taken included disassembly, inspection, and refurbishment by Dresser personnel. The pressurizer safety valve exhibited no abnormal conditions during the inspection. This valve will be tested as part of routine certification testing for pressurizer safety relief valves prior to being reinstalled. The condition posed no threat to public health and safety.
2691999005 | Oconee 1 | 07/07/1999 | 08/06/1999 | 9908100149 | <strong>Loss of Feedwater Reactor Trip due to Misrouted Instrument Lines</strong><br /><i>Abstract:&nbsp;</i>On July 7, 1999, Oconee Unit 1 was in Mode 1 at 15 percent Full Power preparing to place the Turbine-Generator on line following a refueling outage. Operations secured and isolated the 1B Main Feedwater Pump (MFP) at 0110 hours. Due to misrouted instrument lines on non-safety related pump suction pressure switches, the 1A MFP tripped which caused the Reactor Protective System to trip the reactor on loss of feedwater. Operators stabilized the reactor in Mode 3. The root cause of the trip was inadequate procedural guidance such that personnel did not maintain adequate configuration control when disconnecting and reconnecting instrument lines during a modification in 1996. A contributing cause was deficient post-modification testing (PMT). The PMT did not identify that the pump suction pressure sensing lines were connected to the wrong pumps. Corrective actions include connecting the instrument lines to the correct pumps, and revisions to processes and procedures. The health and safety of the public was not compromised by this event.
2691999006 | Oconee 1 | 08/18/1999 | 09/09/1999 | 9909150157 | <strong>Drop of Control Rod Group Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1999, Oconee Unit 1 was in Mode 1 at 100 percent Full Power, when at approximately 1956 hours Unit 1 tripped. Operators stabilized the reactor in hot standby condition (mode 3). The unit post trip response was normal. The events recorder indicated that group 5 control rods had dropped into the core. Approximately three seconds later the Reactor tripped on a Reactor Protective System variable low pressure/temperature trip. There was no testing or maintenance being performed at the time of the trip. The root cause of the trip was equipment malfunction of the rod group 5 programmer. Corrective actions include replacing the programmer and sending the suspect programmer offsite for further testing and evaluation. The health and safety of the public was not compromised by this event.
2691999008 | Oconee 1, Oconee 3 | 11/10/1999 | 12/10/1999 | ML99350001 | <strong>Improper Notification Prevents Required Technical Specification Actions</strong><br /><i>Abstract:&nbsp;</i>On November 10, 1999, at 2347 hours with Oconee Units 1 and 3 in Mode 1, at approximately 100% Power and Unit 2 in Mode 6, Refueling, it was discovered that a condition had existed where one control battery (CB) had been removed from service and a second CB was in a degraded state without the necessary actions being completed per TS for Units 1 and 3. On September 20, 1999, the weekly cell parameter surveillance for control battery (CB) 3CB found one of the sixty cells below the minimum voltage. On October 7, 1999, the quarterly cell parameter surveillance for CB 3CB found two of the sixty cells below the minimum voltage. Operations (OPS) was not notified to evaluate battery operability for either surveillance. On November 4, 1999, at 2200 hours, OPS authorized removal of CB 2CA from service to perform testing. OPS was unaware that CB 3CB was already inoperable. CB 2CA was returned to service on November 10, 1999, at 1625 hours. This problem was discovered during a review of outstanding work orders. The cause of the event was Maintenance failure to notify OPS. Corrective actions include procedure changes to add a step for OPS notification, training for Maintenance on proper notification and benchmarking of the notification process at other utilities.
2691999009 | Oconee 1, Oconee 2, Oconee 3 | 11/15/1999 | 12/15/1999 | ML99355018 | <strong>Operation with Unrepaired Steam Generator Tube Ends</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1999, Oconee Units 1 and 3 were operating at approximately 100 percent power. Unit 2 was shutdown for refueling. At 1605 management concluded that the units were operating or had operated with unrepaired Steam Generator (SG) Tube End Anomalies (TEAs) contrary to Technical Specification (TS) 5.5.10, section e.6, repair criteria. Since the existence of the SG TEAs are of no safety significance, Oconee requested and received a Notice of Enforcement Discretion on November 15, 1999. The root cause of this event was Duke's failure to recognize the need to propose a TS change request to exclude axial SG TEAs from the TS SG tube repair criteria when SG TEAs were identified and characterized in May and June of 1998. This event was of no significance to the health and safety of the public.
2701999001 | Oconee 2 | 02/28/1999 | 03/30/1999 | 9904070235 | <strong>Equipment Failure Results In A Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1999, at 1544 hours, Unit 2 was at 100% power. A small Reactor transient occurred when Electro Hydraulic Control (EHC) System normal electrical power was lost and a swap over to backup power occurred. The loss of EHC system normal electrical power was due to the failure of a fuse. Reactor power stabilized at 98% following the transfer of EHC electrical power. At approximately 2040 hours, during troubleshooting and root cause investigation, there was a spurious reapplication of power through the failed fuse. The reaction of the EHC system caused Unit 2 Turbine control valves to close and the Reactor tripped on high Reactor Coolant System pressure. All primary and secondary parameters responded as expected and operations personnel appropriately stabilized the unit at hot shutdown conditions. The root cause of the reactor trip is equipment failure. The fuse failed due to an internal open circuit fault at one end of the fuse rather than an overcurrent condition. A detailed laboratory analysis of the failed fuse is being performed. Corrective action includes replacing the failed fuse, having the failed fuse analyzed, and revising maintenance processes as required. This event is considered of no significance with respect to the health and safety of the public.
2701999002 | Oconee 2 | 06/19/1999 | 07/19/1999 | 9907260102 | <strong>Reactor Trip due to Secondary System DC Grounds</strong><br /><i>Abstract:&nbsp;</i>On June 19, 1999, Oconee Unit 2 was operating in Mode 1 at 66 percent Full Power. At 1015:14 hours, the Unit 2 Reactor tripped on an anticipatory trip following a Main Turbine trip. Operators took immediate action to stabilize the unit in Mode 3. No significant problems were encountered. The trip was due to a spurious trip signal caused by two concurrent electrical ground faults in the Moisture Separator Reheater high level switches. The root cause of one ground was a manufacturing deficiency that allowed a wire to chafe against a sharp edge. The second ground was due to missing adhesive that allowed a Mercury switch vial to move in its retaining bracket until a conductor contacted the metal bracket. The investigation determined the adhesive may have degraded over time. Corrective actions included inspecting all similar switches, moving wires away from the sharp edge, and installing new adhesive, as necessary. The switch manufacturer is being consulted for additional possible corrective actions. The health and safety of the public was not compromised by this event.
2701999003 | Oconee 2 | 12/20/1998 | 11/17/1999 | ML99331012 | <strong>Inadvertent Engineered Safeguards Actuation While at 100 Percent Power</strong><br /><i>Abstract:&nbsp;</i>On December 20, 1998, Oconee Unit 2 was in Mode 1 at 100 percent full reactor power. At approximately 0253 hours, Unit 2 received an invalid actuation of Engineered Safeguards (ES) Channel 3. Performance of procedure IP/O/A/0310/012B "Engineered Safeguards Systems Logic Subsystem 1 Low Pressure Injection (LPI) Channel 3 On Line Test" was in progress. The "2A" LPI Pump and the "C" Low Pressure Service Water (LPSW) Pump automatically started and were later secured at the direction of the Control Room Senior Reactor Operator (SRO). The root cause was equipment malfunction of a logic test module. Corrective actions included replacing and testing the logic test module. The health and safety of the public was not compromise by this event.
2701999004 | Oconee 2 | 06/18/1999 | 02/16/2000 | ML00368570 | <strong>Reactor Coolant Pump Lube Oil collection System OUtside Design Basis with respect to 10CFR 50 Appendix R (iii) (O)</strong><br /><i>Abstract:&nbsp;</i>At 2335 on 6-18-99 control room instruments indicated an oil leak from the 2A1 Reactor Coolant Pump (RCP) Motor. Power was reduced to <70% at 0217 on 6-19-99 and the 2A1 RCP was secured at 0218. An unrelated reactor trip occurred at 1015 on 6-19-99 from approximately 65% due to a Main Turbine Trip (reference LER 270/1999-02). Subsequently, it was observed that the Appendix R oil collection system, that is designed to collect and route leakage to an oil collection tank in the reactor building basement, had leaked approximately 10 gallons of oil. The source of this leakage was a seal at the gasketed drip pan joint. The drip pan was reassembled using high temperature RTV sealant on the gasket to improve the seal. Corrective actions include the repair addressed above and enhanced maintenance procedural guidance.
2711999001 | Vermont Yankee | 01/05/1999 | 02/04/1999 | 9902110154 | <strong>Inadequate Communication between Licensee and Equipment Manufacturer Results in the Incorrect Application of a Manufacturer Supplied Pump Curve and an Unanalyzed Condition.</strong><br /><i>Abstract:&nbsp;</i>On 01/05/99 VY determined that pump curves used in assessing Residual Heat Removal Service Water Pump performance had not been correctly applied to the VY configuration. The curves supplied by the manufacturer were for the VY pump design when installed in a standing pool. The pumps supplied to VY for this application were of a "canned" design. The can, which houses the pump casing, allows a piped connection to the pump suction. The canned design introduces a pressure drop that should be included during NPSH calculations. It was not understood by VY that there was an adjustment necessary when applying the curves to the pumps provided to VY. The reduction in available NPSH, caused by the canned design was not considered in subsequent calculations. The effect of that reduction is being assessed in a calculation. RHRSW safety functions relating to accident mitigation, as described in the VY FSAR, are not challenged by this condition. The issue of concern relates to the RHRSW pumps running in the Alternate Cooling System (ACS) mode. This mode would be employed in the event of a loss of access to the Connecticut River as the plant's normal heat sink. VY had previously established administrative limits upon plant operation with elevated supply temperatures (>73 F) that ensured adequate RHRSW pump NPSH while calculations were being performed. It is expected that calculations will demonstrate that the RHRSW system as-built configuration supports all system safety functions including the ACS mode. Therefore, this event did not increase the risk to public health and safety.
2711999002 | Vermont Yankee | 03/16/1999 | 04/15/1999 | 9904200315 | <strong>Lack of Understanding of the Relationship between TS Pump Flow Requirements and Flow Rates Credited in Analyses Results in Failure to Properly Test Core Spray Pump Discharge Check Valves</strong><br /><i>Abstract:&nbsp;</i>On 03/16/99, VY determined that the testing performed on the Core Spray (CS) pump discharge check valves has not been in full conformance with Vermont Yankee (VY) Technical Specifications (TS). The check valve exercising requirements had not been performed per the applicable code. VY has been exercising the cited check valves coincident with pump testing. However, the flow rate established during pump testing was less than that required by the ASME Code, Section XI, invoked by VY TS. VY immediately tested the CS check valves per the ASME Code requirements. Both valves performed satisfactorily. The cause of this event was a lack of understanding of the relationship between TS pump performance requirements and the system flow rates credited in accident analyses. This allowed the accident mitigating flow rates credited in the VY 10CFR50.46 LOCA analysis to go undetected by those persons responsible for determining check valve testing requirements. VY is evaluating the need to train the Engineering organization on this relationship. This event was identified during the implementation of a corrective action for a similar event. Although not sufficient to meet ASME Code, Section XI requirements, previous testing provided a high degree of confidence that the subject valves could perform their safety functions and the components were operable. The valves were consistently tested, and subsequently passed the more rigorous testing required by the code. Therefore, this event presented no increased risk to public health and safety.
2711999003 | Vermont Yankee | 09/02/1999 | 10/04/1999 | 9910080162 | <strong>Inadvertent Primary Containment Isolation System Actuation Due To A Spurious Signal On A Refuel Floor Radiation Monitor.</strong><br /><i>Abstract:&nbsp;</i>At 1143 on 09/02/99, with the reactor operating at 100% power, a Standby Gas Treatment System (SBGTS) initiation and Reactor Building Ventilation isolation occurred concurrent with a Primary Containment Isolation System (PCIS) Group III isolation. These isolations and the initiation of SBGTS were caused by an erroneous signal on the "A" Refuel Floor Area Radiation Monitor. The isolation occurred while new fuel inspection activities were ongoing on the refuel floor. A radiation protection technician providing support for the new fuel inspections immediately surveyed the area monitored by the alarming Radiation Monitor. Radiation levels were confirmed to be normal. The cause of the event was a radiation detector failure that delivered a spurious signal that exceeded the monitor trip setpoint. Corrective actions consisted of conducting the radiation survey and troubleshooting the radiation monitor circuitry. The faulty detector has been replaced. Because affected systems responded as designed, and there was no high radiation condition, this event presented no increased risk to public health or safety.
2711999004 | Vermont Yankee | 10/05/1999 | 10/28/1999 | ML99309018 | <strong>Inadequate Communication Results In A Work Team Rendering HPCI System Inoperable During Minor Modification Installation</strong><br /><i>Abstract:&nbsp;</i>On 10/05/99, while performing pre-outage work in the vicinity of the High Pressure Coolant Injection (HPCI) System, a technician leaned upon a HPCl control oil line, causing the line to leak. The leak was immediately reported to the station Shift Supervisor. The magnitude of the leak was sufficient to render the HPCI system inoperable. The operating crew Shift Supervisor declared the HPCI system inoperable and took actions per the Plant Technical Specifications. Vermont Yankee (VY) technicians were dispatched to repair the leaking line. The repair was made, HPCI tested, and declared operable in approximately 11 hours. VY Technical Specifications allow reactor operation for 7 days without HPCI available. This event was caused by inadequate communication regarding the sensitivity of work on or near operable plant equipment, and the need to reevaluate work plans if unforeseen difficulties are encountered. VY management expectations related to work in the vicinity of operable plant equipment have been clearly communicated to the applicable members of the VY work force. Meetings have been conducted, and procedure changes are being prepared to enhance personnel sensitivity while working in the vicinity of operable plant equipment, and to enforce the need to reevaluate work plans should unforeseen difficulties be encountered during work activities. The damage to the HPCI control oil line was recognized immediately, and actions were promptly taken to restore the system to service in accordance with VY Technical Specifications. Therefore this event presented no significant increase in risk to public health and safety.
2711999005 | Vermont Yankee | 11/04/1999 | 11/29/1999 | ML99341012 | <strong>Inadequate Procedures Result In the Failure to Establish the Neutron Monitoring System Configuration Required By Plant Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 11/04/99, while in Cold shutdown, the VY plant operated for approximately 13 minutes without the minimum number of operable Average Power Range Monitor (APRM) channels required by plant Technical Specification (TS). VY TS require that a minimum of 4 APRM reduced high flux reactor trip channels be operable whenever the Reactor Mode Selector Switch RMSS is in the “Startup and Hot Standby” (STARTUP) position. Previous to the event, the APRM trip channels had been disables with the RMSS in REFULE/SHUTDOWN. This was consistent with VY TS. Inadequate procedures allowed the operating crew to perform a test that required placing the RMSS in STARTUO, without first restoring the APRM’s or establishing appropriate alternative conditions (the removal of SRM shorting links). The procedures have been revised as necessary to prevent recurrence. The non-conforming alignment was short in duration. Five channels of Intermediate Range Monitoring (IRM) were operable, providing automatic protection against excessive core power. The rest procedure, which was implemented as written, limits rod withdrawal to a single notch on two “non-adjacent” control rods, precluding reactor criticality. Therefore this event did not significantly increase the risk to public health and safety.
2711999006 | Vermont Yankee | 12/16/1999 | 01/17/2000 | ML00367773 | <strong>Limitorque Actuator Malfunction Results in Failure of an RHR Heat Exchanger Bypass Valve Stem</strong><br /><i>Abstract:&nbsp;</i>On 12/16/99, Vermont Yankee (VY) determined that one of two Residual Heat Removal (RHR) subsystems had been operated for approximately 18 months with a degraded heat exchanger bypass valve. A review of historical data and valve manufacturer specifications revealed that the "B" RHR heat exchanger bypass valve stem had broken between 03124/98 and 05/29/98, but had gone undetected. The valve stem has been replaced. The as-found condition of the stem was a through-stem break above the valve backseat. The root cause of this event was a failure of the actuator to cease open movement at its open limit setting (backseating). The most likely cause of the backseating was a loosened motor-actuator worm gear locknut identified in 1995. Securing the MOV worm gear locknut is properly controlled/verified in the current VY MOV maintenance procedure as was recommended in industry operating experience. The failed actuator worm gear lock nut had been installed in 1989, when VY maintenance procedures lacked their current controls. The VY RHR heat exchanger bypass valve is a 20 inch globe valve. With the valve stem separated, the valve consistently performed as expected, throttling upon demand to direct flow through the RHR heat exchanger for torus/shutdown cooling, and opening sufficiently to allow the necessary flow via the LPCI injection path. The disk guides apparently provided adequate alignment of the separated disk and stem segment to allow the valve to function as a stop-check valve. The valve was repeatedly operated and tested during the period it was degraded, showing itself consistently capable of opening or throttling closed upon demand. Therefore, this event did not significantly increase the risk to public health and safety.
2721999001 | Salem 1 | 02/28/1999 | 03/29/1999 | 9904080221 | <strong>Reactor Scram As A Result Of Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>At 1:38 AM, on February 28, 1999, the Salem Unit 1 Reactor was automatically shut down due to a Low Oil Pressure Trip of the Main Turbine. The unit was operating at 60% power prior to the shutdown and was being maintained at this power level to allow maintenance troubleshooting activities. Preparations were also being made to allow maintenance to repair a leaking Main Turbine Lube Oil Cooler. While adjusting the cooler isolation valve, the operators inadvertently positioned the valve off of its closed seat, allowing oil from the in service cooler to enter the partially drained out-of-service cooler. This diverted flow caused a momentary drop in the turbine oil pressure and resulted in the automatic shutdown of the Main Turbine and Reactor. A root cause investigation determined that the cause of this event was personnel error. This event is being reported pursuant to 50.73(a)(2)(iv) Licensees shall report "any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor m RPS ."
2721999002 | Salem 1 | 04/13/1999 | 05/12/1999 | 9905210035 | <strong>Auxiliary Building Ventilation Found Outside of Design</strong><br /><i>Abstract:&nbsp;</i>On 04/13/99 at 2135, the Unit 1 auxiliary building was identified by the operators as being at a pressure of +0.03 inches of water with respect to the outdoors. The Updated Final Safety Analysis Report (UFSAR) Section 9.4.2.2.1 states that the auxiliary building is designed to be at a slight negative pressure continuously, with respect to the outdoors, to satisfy the criterion for preventing the uncontrolled release of radioactivity, therefore the plant was being operated outside of the design basis. Subsequent investigation determined that the #12 auxiliary building exhaust fan was rotating backwards. Corrective maintenance activities had been performed on the prior day that required the motor leads to be disconnected. The apparent cause is mis-wiring of the motor due to human error by the maintenance technician. The mis-wired fan had been returned to service at 1337 on 04/13/99. The mis-wiring was corrected and the fan was returned to service at 1110 on 04/14/99. Tech Spec 3.7.7.1, which provides a seven day action statement, was in effect for the duration of the event. A 4-hour report was made to the NRC as required by the plant's Emergency Classification Guide and 10CFR50.72(b)(1)(ii). This report is being made pursuant to 10CFR50.73 (a)(2)(ii)(B) "Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded; or that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant;"
2721999003 | Salem 1 | 05/13/1999 | 06/09/1999 | 9906150194 | <strong>Unplanned Entry into Technical Specification 3.0.3 for the Control Room Ventilation System.</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1999, during performance of procedure S2.OP-ST.SSP-001 (manual safety injection system testing) an unplanned entry into Technical Specification (T/S) 3.0.3 was made. Per procedure requirements, the #12 and #22 control room emergency air conditioning system (CREACS) supply fan controller selector switches were placed in the "stop" position. Following performance of this step, personnel recognized that placing both of these switches in the "stop" position removed the required standby feature and rendered more than one CREACS filter train inoperable. Technical Specification 3.7.6.1.a states, in part, that 2 fans and associated outlet dampers are required for an operable filtration train. The current TS as written does not provide actions when two filter trains are inoperable for a unit in mode 1 through 4. Selecting both #12 and #22 fans controllers to the "stop" position placed the Units in a TS 3.0.3 condition. This event was caused by human error, specifically a faulty procedure resulting from an inadequate procedure review. A contributing cause was a less than adequate questioning attitude by the operations crew. Corrective actions included restoring the fan controllers to the "stby" position, and correcting the appropriate procedures. Measures were also taken in conjunction with another similar event to improve operator awareness. This condition is reportable in accordance with 10CFR50.73 (a)(2)(i)(B), a condition prohibited by the plant Technical Specifications.
2721999004 | Salem 1 | 05/20/1999 | 06/17/1999 | 9906290019 | <strong>Unplanned Reactor Trip Due To Negative Flux Rate Trip.</strong><br /><i>Abstract:&nbsp;</i>On 5/20/99, at approximately 2137 hours, the reactor tripped from 100% power due to a negative flux trip signal from the nuclear instrumentation. The negative flux rate resulted from a dropped control rod which was caused by a loss of power to the stationery gripper coil. The loss of power was determined to be the result of a blown fuse. Investigation identified a low insulation resistance pathway on the control cable at the containment penetration seal. The junction box for this seal was found to have an accumulation of rust on the lower panel area with some warpage of the side plates, possibly resulting from a previous service water leak which may have impinged on the junction box. The cable in question was rerouted through a spare cable "feedthrough" in the penetration assembly and returned to service. The penetration seal continues to serve the mechanical sealing function without degradation. All systems functioned as designed in response to the trip. The fuse functioned properly to protect the penetration. The root cause of the cable failure has not been determined. A report was made to the NRC as required by the plant's Emergency Classification Guide and 10CFR50.72(b)(2)(ii). This report is being made in accordance with 10CFR50.73(a)(2)(iv) Licensees shall report "any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS)".
2721999005 | Salem 1 | 06/05/1999 | 07/02/1999 | 9907120210 | <strong>11 Containment Fan Coil Unit (CFCU) Out of Service More than Tech Spec Allowed Time</strong><br /><i>Abstract:&nbsp;</i>At 0124 on 5/29/99 after the performance of a valve stroke timing surveillance for the 11 Containment Fan Coil Unit (CFCU), a leak developed in Containment. The CFCU was isolated and Tech Spec(TS) 3.6.2.3 was entered. Containment entry revealed leakage at 3 of the top 4 11 CFCU cooler cover plate gaskets. The CFCU was declared inoperable and the TS action statement was entered. The action statement which expired on 6/5/99 at 0124 required that the unit be in hot standby by 0724 on 6/5/99. On June 4, 1999, following initial repairs and pressurization of the CFCU with service water, additional cooler leaks developed on the top two coolers. On 6/4/99 PSEG submitted a request for a Notice of Enforcement Discretion (NOED) to the NRC asking for an extension of the allowable outage time for the inoperable CFCU of 5 days or until the CFCU was returned to an operable status. NRC granted this NOED on 6/4/99 (documented via letter A. Randolph Blough, Director Division of Reactor Projects, NRC Region I, NOED No. 99-1-004 dated 6/9/99). This LER is being submitted since the unit operated past the allowable outage time stated in the tech spec action statement. Repairs were completed, operability testing was successfully performed and the CFCU was returned to an operable status at 1818 on 6/7/99. Sufficient safety system components to mitigate relevant events remained operable during the entire duration of 11 CFCU outage, therefore there was no impact to the health and safety of the public. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
2721999006 | Salem 1, Salem 2 | 07/29/1999 | 08/26/1999 | 9909030051 | <strong>Non-Conservative Setpoint for Steam Generator Blowdown Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>A safety evaluation in support of a calorimetric calculation change determined the SG blowdown radiation monitors' setpoint was non-conservative. The set point was based on a blowdown flow of approximately 60,000 lbm/hr. The plant has been operated at flows in excess of 60,000 lbm/hr. Upon discovery, SG blowdown flow was restricted to a maximum of 35,000 lbm/hr. Technical Specifications (TS) require, with non-conservative setpoints, discharge of liquid effluents via this pathway be suspended. The cause of occurrence is inadequate administrative controls for incorporating original plant licensing data and plant testing data into plant procedures. Offsite Dose Calculation Manual (ODCM) effluent radiation monitor assumptions will be reviewed to verify consistency with actual plant operation. Past operation with increased blowdown flow did not exceed 10CFR20 limits. Therefore, the health and safety of the public was not affected. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B), any condition prohibited by the plant's Technical Specifications.
2721999007 | Salem 1 | 09/24/1999 | 10/25/1999 | ML99308005 | <strong>Engineered Safety Feature Actuation, 1R12A Containment Noble Gas Monitor Alarm and Containment Ventilation System Isolation</strong><br /><i>Abstract:&nbsp;</i>This LER reports the automatic actuation of an Engineered Safety Feature (ESF) due to a valid signal, as required by 10CFR50.73(a)(2)(iv). On September 24, 1999 the Salem Unit 1 Containment Noble Gas monitor (1R12A) alarmed in response to a valid radiation condition that was above its alarm setpoint, generating a signal to isolate the Containment Ventilation system. At the time of the alarm, the 1R12A was in service but inoperable and the Containment Isolation Valves were closed because of modification activities that were in progress. The high radiation condition was caused by the release of activity from noble gases from the Reactor Coolant system during normal refueling outage maintenance activities. The cause of this occurrence was a trip of the 1R12A as a result of a conservative alarm/trip setpoint that does not account for expected spikes in containment noble gas activity during normal refueling outage maintenance activities. Corrective Actions for this event included containment atmosphere monitoring to verify that an abnormal radiological condition did not exist. In addition, PSE&G will evaluate alternative methods to determine Containment atmosphere background activity level to provide a method that will maintain the ability of the 1R12A to carry out its design function while eliminating unnecessary alarms and Containment Ventilation System isolations.
2721999008 | Salem 1 | 09/25/1999 | 10/25/1999 | ML99307024 | <strong>Engineered Safety Feature Actuation, 1R11A Containment Air Particulate Monitor Alarm and Containment Ventilation System Isolation</strong><br /><i>Abstract:&nbsp;</i>This LER reports the automatic actuation of an Engineered Safety Feature (ESF) due to a valid signal, as required by 10CFR50.73(a) (2) (iv). On September 25, 1999 the Salem Unit 1 Containment Air Particulate (1R11A) alarmed in response to a valid high radiation condition, causing a Containment Ventilation system isolation. The high radiation condition was caused by the release of particulate activity during the performance of local leak rate testing, due to poor radiological work practices. In preparation for the performance of local leak rate test on Chemical and Volume Control System, station personnel blew down a section of piping using compressed air directly to the containment atmosphere. Since the discharge was not filtered, particulate activity in the containment increased to above the 1R11A alarm/trip setpoint and actuated a Containment Ventilation System isolation. The corrective Actions for this event included containment atmosphere monitoring to verify that an abnormal radiological condition did not exist. All personnel who perform local leak rate tests were advised of the details of this event. Additionally, local leak rate test procedures will be modified to add precautions for performing pressurized draining of potentially contaminated systems to avoid releasing radioactive contaminants into the containment atmosphere.
2721999009 | Salem 1, Salem 2 | 10/08/1999 | 10/22/1999 | ML99306003 | <strong>Pressurizer PORV and Block Valves Do Not Meet the Requirements of 10CFR50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>During a review of the Salem Post-fire Safe Shutdown Analysis a concern was identified with the cable routing of the air operated pressurizer Power Operated Relief Valves (PORVs) and motor operated block valves. The cable for each PORV and associated block valve is routed in the same cable tray inside the containment. The pressurizer PORVs and block valves are considered a high/low pressure interface point for 10CFR50 Appendix R analysis. The PORVs and block valves provide isolation of the pressurizer [high pressure] from the pressurizer relief tank (PRT) [low pressure]. Therefore each PORV/block valve combination is considered as redundant components that require proper separation in accordance with Section III.G.2 and III.L.7 of 10 CFR Appendix R when evaluating the affects of hot shorts, open circuits, or shorts to ground from causing spurious operation of these valves. The cause of occurrence is the failure to properly evaluate the high/low pressure interface function of the PORVs and block valves during the development of the Appendix R Safe Shutdown Analysis. Immediate and long-term corrective actions are described in detailed report. This event is reportable in accordance with 10CFR50.73(a)(2)(ii)(B), '...a condition that was outside the design the plant..." This LER also satisfies the special reporting requirements of the Salem Unit 1 and 2 Technical Specifications Section 6.9.3 and Salem Unit 2 License Condition 2.I.
2721999010 | Salem 1 | 10/24/1999 | 11/22/1999 | ML99341021 | <strong>Subcritical Manual Reactor Trip Due To Rod Control System Failure.</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1999 at approximately 1219, Salem Unit 1 reactor was manually tripped during rod worth testing because Control Bank C Group 1 rods failed to respond to demand. Rod worth measurements were in progress. All testing was being performed under the provisions of Special Test Exception 3.10.1 and 3.10.3 (Shutdown Margin and Physics Tests). Control Bank C was being inserted when the Reactor Operator noted a discrepancy between the Group 1 and Group 2 Step Counters. Rod insertion was terminated, the situation was evaluated and the decision was made to manually trip the reactor and place the control rods in a full in position. After briefings concerning the expected plant response were completed the trip breakers were opened and all rods were inserted. The plant was stable at approximately 100 counts in the Source Range. The cause of the event was traced to a poor connection on one of the rod control system power regulator boards. All of the regulator boards were removed from the power cabinets, the edge connectors were cleaned and aligned and the boards were reseated. A report was made to the NRC as required by the plant's Emergency Classification Guide and 10CFR50.72. This report is being made in accordance with 10CFR50.73(a)(2)(iv) “any event or condition that resulted in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS)”.
2721999011 | Salem 1, Salem 2 | 10/28/1999 | 11/12/1999 | ML99327014 | <strong>125 VDC Control Power Circuits for 4KV Breakers Do Not Meet the Requirements of 10CFR50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>During an ongoing review of the current Salem Post-fire Safe Shutdown Analysis, a concern was identified with the 125V DC control circuits for the 4KV circuit breakers in the post fire Alternate Shutdown (ASD) Area. In the event of a postulated fire in the ASD area, cables associated with the 4KV breaker 125 VDC control circuits could experience an external hot short on the positive side of the open/close coils. Such a short occurring in combination with multiple grounds (occurring due to postulated fire) on the negative 125 VDC circuit legs could result in energization of the closing or trip coils. This fire induced circuit failure (due to a combination of one hot short and two shorts to ground) could result in the inability to locally operate one or more 4KV breakers as required for alternate shutdown unless the hot short is removed. The multiple occurrence of this scenario could potentially cause multiple spurious operation and lead to loss of the vital buses. The cause of this event is attributed to human error. Personnel involved with the development of the Safe Shutdown Analysis incorrectly interpreted the guidance of Generic Letter 86-10 for the evaluation of spurious operation of equipment. Immediate and long-term corrective actions are described in the detailed report. This event is reportable in accordance with 10CFR50.73(a)(2)(ii)(B), “...a condition that was outside the design basis of the plant…” and 10CFR50.73(a)(2)(v), "...any event or condition that alone could have prevented the fulfillment of the safety function of structures that are needed to shutdown the reactor and maintain it in a safe shutdown condition,.." This LER also satisfies the special reporting requirements of the Salem Unit 1 and 2 Technical Specifications Section 6.9.3 and Salem Unit 2 License Condition 2.I.
2751999001 | Diablo Canyon 1 | 03/03/1999 | 04/02/1999 | 9904070401 | <strong>Engineered Safety Features Actuation During Main Turbine Generator Testing Due to Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On March 3, 1999, at 1501 PST an engineered safety features actuation, automatic start and loading of an emergency diesel generator (EDG) from 4 kV vital bus undervoltage, occurred when a unit trip signal was initiated during main turbine generator (TG) maintenance testing. The unit trip signal isolates the 500 kV offsite electrical system from the plant as a TG protective feature. When initiated, the unit trip opens the main electrical breakers and deenergizes 4 kV vital Buses F, G, and H. The loss of bus voltage was sensed and initiated a vital bus transfer to the startup (offsite power) source. Due to unrelated concurrent testing on 4 kV vital Bus G, the startup source feeder breaker was not available, so the undervoltage condition initiated an EDG start and load sequencing. A 4-hour non-emergency report was made in accordance with 10 CFR 50.72(b)(2)(ii) at 1731 PST. Plant operators responded to alarms and indications in the control room, stabilized the plant, restarted Residual Heat Removal Pump 1-1 and transferred 4 kV vital Bus G to the startup offsite power source. The cause of this event was inadequate operating procedure detail regarding the main TG thrust bearing wear trip cut out switch position for outage conditions and personnel error. Plant operating procedures were revised to include specific steps to ensure proper main TG protective features were cut out during maintenance activities. An operations department incident summary has been issued regarding this event reemphasizing management expectations for maintaining a questioning attitude.
2751999002 | Diablo Canyon 1 | 03/20/1999 | 04/23/1999 | 9904290043 | <strong>Technical Specification 3.3.1 Not Met Due to Inadequate Knowledge and Communication</strong><br /><i>Abstract:&nbsp;</i>On March 20, 1999, at 1753 PST, with Unit 1 in Mode 1 (Power Operation) at 92 percent power, Technical Specification 3.3.1, "Reactor Trip System Instrumentation", Table 3.3-1, Action 6, was not met when two channels affecting over-power delta temperature and over-temperature delta temperature were placed in bypass on three occasions, instead of keeping one channel in the tripped condition. The condition lasted less than one hour; therefore, Technical Specification 3.0.3 was met. On March 25, 1999, this condition was discovered by a utility engineer reviewing the control room logs. The condition was caused by inadequate knowledge and communication. The operators did not know that the temperature instrumentation calibration process would place each channel in bypass. During preparation for the calibrations, the Maintenance personnel did not communicate to Operations personnel that the channels would be in bypass. Therefore, an additional inoperable channel was left in bypass during the calibration. Also, the intent of the Technical Specification Action was not clear to all involved personnel. Corrective actions include providing licensed operators with training on this event, and adding requirements in work orders to inform Operations personnel of the anticipated condition of the channel during the maintenance activity (trip or bypass) and the channels affected.
2751999003 | Diablo Canyon 1, Diablo Canyon 2 | 04/29/1999 | 06/01/1999 | 9906100116 | <strong>Technical Specification 4.3.1.2 Time Response Test Not Performed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1984, and August 20, 1985, Units 1 and 2, respectively, initially entered Mode 2 (Startup) without a valid reactor trip system response time test required by Technical Specification (TS) 4.3.1.2, "Reactor Trip System Instrumentation," Table 3.3-2, "Reactor Trip System Instrumentation Response Times," Functional Unit 2, Power Range (PR), Neutron Flux, Low Setpoint. On April 29, 1999, with Units 1 and 2 in Mode 1 (Power Operation), at approximately 100 percent power, PG&E identified that TS 4.3.1.2 surveillance had not been performed for Functional Unit 2 since prior to initial plant startup. A 1-hour, non-emergency report was made to the NRC at 1321 PDT in accordance with 10 CFR 50.72(b)(1)(ii)(B). The initial cause of the missed surveillance is unknown since personnel that prepared the original test program are no longer available. However, PG&E believes that the cause is a knowledge based error(s) by utility nonlicensed personnel in that they believed only the PR Neutron Flux, High Setpoint was required. In 1985 PG&E personnel believed that Functional Unit 6, "Source Range, Neutron Flux," time response testing fulfilled the low power protection functional requirements and the PR low setpoint was not required to be response time tested.
2751999004 | Diablo Canyon 1 | 07/06/1999 | 08/05/1999 | 9908100232 | <strong>Technical Specification 3.8.1.1c, Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1999, at 1105 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.8.1.1, "A.C. Sources," Action c, was exceeded when TS 4.8.1.1.1a was not performed within 1 hour of declaring the offsite 230 kV startup power source inoperable with a diesel generator inoperable. On July 6, 1999, at 1112 PDT, TS 4.8.1.1.1a was performed successfully by demonstrating the operability of the remaining A.C. sources. The condition was discovered by a licensed shift foreman (SFM) in the control room and was caused by personnel error. The SFM became distracted with other impending plant activities and failed to direct performance of the surveillance within the required time limit. An event summary was issued to all operating personnel. The summary discussed the event and defined operations expectations for performing nonroutine conditional surveillances. Surveillance Test Procedure M-75, "4kV Vital Bus Undervoltage Relay Calibration," will be enhanced to assure the operators perform conditional surveillance within required times. Similar surveillance procedures will be reviewed to incorporate lessons learned from this event.
2751999005 | Diablo Canyon 1 | 07/13/1999 | 08/12/1999 | 9908170073 | <strong>Technical Specifications 4.1.1.1.1a, Not Met Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On July 13, 1999, at 1930 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.1.1.1 "Shutdown Margin - Modes 1-2," was not met when a shutdown margin (SDM) calculation was not performed within 1 hour as required by TS 4.1.1.1.1a. At 1830 PDT, plant operators had declared the rod control system inoperable and entered the limiting condition for operation for TS 3.1.3.1.c. On July 16, 1999, at 0146 PDT, following planned corrective maintenance, plant operators satisfactorily performed surveillance testing and declared the rod control system operable, exiting TSs. Plant operators failed to identify that a SDM calculation was required with an inoperable rod control system due to ambiguity in TS 3.1.3.1c. PG&E will provide guidance to plant operators to perform a SDM calculation whenever TS 3.1.3.1c is entered. Additionally, all plant operators will be counseled regarding management's expectations to perform a thorough and complete review of TS to ensure that all applicable surveillances are properly completed.
2751999006 | Diablo Canyon 1 | 09/22/1999 | 10/15/1999 | 9910200027 | <strong>Reactor Trip Due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1999, at 0932 PDT, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the unit experienced a full load rejection after the 500 kV supply breakers opened. Approximately 9 seconds later, the reactor tripped automatically. Unit 1 was stabilized in Mode 3 (Hot Standby) in accordance with plant emergency procedures. During the transient, two power operated relief valves opened for less than 1 second each. A 4-hour non-emergency report was made to the NRC at 1150 PDT in accordance with 10 CFR 50.72 (b)(2)(ii). The full load rejection was caused by a lightning strike which actuated a 500 kV overvoltage relay and opened the 500 kV breakers for Unit 1. The reactor trip was initiated by a valid OT delta T signal. Walkdowns of the affected areas were completed with no equipment damage indicated. PG&E is evaluating the design of the lightning protection system and the relay protection scheme for enhancements.
2751999007 | Diablo Canyon 1, Diablo Canyon 2 | 11/15/1999 | 02/18/2000 | ML00368586 | <strong>Plant Outside Design Basis Due to degraded Indicating Lamp Sockets</strong><br /><i>Abstract:&nbsp;</i>On November 15, 1999, with Units 1 and 2 in Mode 1 (Power Operation), at 100 percent power, PG&E identified a condition outside the design basis of the plant. Multiple degraded indicating lamp sockets in the control room control boards were discovered which could have caused redundant safety-related equipment to become inoperable due to a postulated seismic event. The lamp sockets provide indication for various safety and nonsafety-related equipment. During a seismic event, the degraded sockets could separate and create a short circuit. This could adversely affect the operation of the associated equipment due to the control power circuit fuse opening because of electrical shorting. On November 15, 1999, at 1120 PST, PG&E made a 1-hour non-emergency notification to the NRC in accordance with 10 CFR 50.72(b)(1)(ii)(B). The cause of the condition is lamp socket design. An easily achievable torque in the socket assembly retaining nut generates a stress in the plastic socket material exceeding its yield value. Time dependent deformation occurs, eventually leading to cracking and failure. Lamp sockets in Units 1 and 2 have been inspected and either replaced or evaluated to use-as-is. PG&E is evaluating the present lamp socket design and alternatives for long term corrective actions. Applicable vendors have been notified.
2751999008 | Diablo Canyon 1 | 09/23/1999 | 10/22/1999 | ML99306002 | <strong>Engineered Safety Feature Acutation - Auxiliary Feedwater Pump 1-1 Started on 12kV Undervoltage due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 23, 1999, at 1752 PDT, with Unit 1 in Mode 3 (Hot Standby), an engineered safety features (ESF) actuation, automatic start of Turbine Driven Auxiliary Feedwater Pump (TDAFW) 1-1 from 12 kV bus undervoltage, occurred during an automatic transfer of offsite power from the 500 kV system source to the 230 kV system startup source. The automatic transfer was initiated when Diablo Canyon Switching Center personnel cut in a 500 kV overvoltage (OV) protective relay with a trip signal picked up. All equipment responded as designed. Operators secured the TDAFW pump within 5 minutes. A 4-hour non-emergency report was made in accordance with 10CFR 50.72(b)(2)(ii) at 2313 PDT; however, the report was made 1 hour and 21 minutes late. The ESF actuation was caused by an undervoltage condition on the 12 kV buses which was caused by a slow transfer to startup power. The transfer to startup power was caused by a personnel error, noncognitive. The late notification to the NRC was caused by a cognitive personnel error. Corrective actions include training the switchyard operators on the unique design of the OV relay, modifying or replacing the OV relays, and training the licensed plant operators on reportability requirements of 10CFR50.72.
2751999009 | Diablo Canyon 1, Diablo Canyon 2 | 10/28/1999 | 11/29/1999 | ML99341007 | <strong>Manual Reactor Trips Due to Heavy Debris Loading of Traveling Screens During a Pacific Ocean Storm</strong><br /><i>Abstract:&nbsp;</i>On October 28, 1999, at 1359 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 30 percent power, and at 1400 PDT, with Unit 1 in Mode 1 at 50 percent power, plant operators initiated manual reactor trips as required by Operating Procedure AP-7, "Degraded Condenser." The trips were required when differential pressure across the intake water traveling screens exceeded limits due to sudden heavy debris loading from a major Pacific Ocean storm. The units were stabilized in Mode 3 (Hot Standby) in accordance with emergency procedures. A 4-hour, non-emergency report was made to the NRC, in accordance with 10 CFR 50.72(b)(2)(ii), at 1520 PDT. PG&E previously added screen rakes and debris grinders to the seawater cooling system to improve debris removal. Operator training was enhanced regarding loss of circulating water system screen functions. PG&E cannot entirely eliminate the potential need to expedite manual reactor trips when high seas and dislodged plant life from the ocean bottom result in heavy debris loading on the traveling screens. PG&E will designate an operations management team to focus on lessons learned and streamline the coping strategy decision making process during storm warning conditions.
2771999001 | Peach Bottom 2 | 01/19/1999 | 02/16/1999 | 9902250293 | <strong>Single failure of the High Pressure Coolant Injection system</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1999, during the performance of a surveillance test on the High Pressure Coolant Injection (HPCI) system, a leak developed from the gland seal condenser which required a system shutdown. Operators secured the HPCI system, declared the system inoperable and entered the applicable Technical Specification Action. A follow-up investigation identified that the HPCI turbine stop valve lower limit switch was not adjusted properly. The switch position provides input into the HPCI control valve ramp generator circuit to open the HPCI control valves in conjunction with HPCI stop valve opening. The switch caused a delayed input to the control circuit which resulted in improper valve sequencing during turbine start-up causing a rapid start of the HPCI Turbine. The resulting pressure surge caused the failure of the gland seal condenser lower shell-to-bonnet gasket. The switch was replaced and adjusted, the gland seal condenser gasket was replaced and the system was tested satisfactorily. The Technical Specification Action was exited on January 24, 1999.
2771999002 | Peach Bottom 2 | 01/29/1999 | 02/25/1999 | 9903050112 | <strong>Inoperability of both channels of the Rob Black Monitor due to a wiring error</strong><br /><i>Abstract:&nbsp;</i>As a result of post modification testing, on January 29, 1999, a wiring error associated with two local power range monitor (LPRM) inputs to both rod block monitor (RBM) channels was discovered. Both LPRM inputs were immediately bypassed to restore Technical Specification operability to both RBM channels and a detailed investigation for both Unit #2 and Unit #3 was performed to identify any additional wiring errors. No other wiring discrepancies were identified. An evaluation to determine the extent of the wiring error and its impact on other plant systems using LPRM inputs was also performed. The results of this investigation found no other cases of LPRM wiring errors to the RBM channels nor any impact on any other related systems. The investigation to date has concluded that the wiring error has existed since original plant installation. An analysis of the event determined that although the RBM operated outside its design basis and licensing basis, at no time were any safety limits challenged. In addition, the wiring error only affected a small group of control rods, and other administrative processes would have prevented any significant errors.
2771999003 | Peach Bottom 2, Peach Bottom 3 | 03/18/1999 | 04/16/1999 | 9904280019 | <strong>This LER reports the failure to maintain the provisions of the Fire Protection Program to properly address the effects of flooding caused by fire induced mis-operation of High / Low pressure interfaces in low pressure ECCS</strong><br /><i>Abstract:&nbsp;</i>During a review of the Fire Safe Shutdown (FSSD) supporting documents, it was concluded that potential damage from a postulated fire in specific fire areas could result in spurious operation of High/Low pressure interface motor operated valves and air operated valves in the Residual Heat Removal (RHR) or Core Spray Reactor Pressure Vessel injection lines. The sustained opening of these valves could result in pressure relief valve discharge and unacceptable flooding of a sump pump room in the Unit 2 or Unit 3 Reactor Building. These sump pump rooms contain instruments associated with the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems. Water damage to these instruments may result in isolation of these systems, which are protected for FSSD in several fire areas. RHR and Core Spray piping integrity would be maintained during the postulated event. Previous analysis contained erroneous information regarding the potential effects of the sump room flooding on other systems. Hourly roving fire watch patrol inspections were immediately established for the identified fire areas. Temporary plant alterations were subsequently installed to remove power from one of the valves in each of the impacted High/Low pressure interfaces to isolate the water flow paths. This condition represents a failure to maintain the provisions of the Fire Protection Program.
2771999004 | Peach Bottom 2, Peach Bottom 3 | 05/21/1999 | 06/20/1999 | 9906240152 | <strong>This LER reports multiple unplanned Engineered Safety Feature (ESF) actuations During a planned electrical bus restoration following maintenance activities</strong><br /><i>Abstract:&nbsp;</i>On Friday, May 21, 1999 at approximately 2220 hours, during restoration of the normal power source to electrical bus 343 SU, the bus (343SU) was deenergized. This caused the 4KV emergency buses E13, E22, E33, and E42 to swap to their respective alternate power supplies (the 2SU-E transformer). During the swap to alternate power, 4 kV buses E13, E22, E33, and E42 experienced a momentary drop in voltage which resulted in multiple ESF actuations. The ESF actuations included a Unit 2 Outboard Primary Containment Isolation System (PCIS) Group II and Reactor Water Cleanup isolation and a Unit 3 Inboard PCIS Group II isolation. Additionally, a full Reactor Water Cleanup isolation (RWCU) occurred on Unit 3. The cause of the deenergization was inadequate configuration control; specifically, a line disconnect from the normal power source was left in the open condition and the operating crew transferred the 343SU-E transformer to a dead power source. The operating crew responded to the fast transfer per appropriate plant procedures and restored all PCIS systems to their normal configurations on both Unit 2 and Unit 3. This condition is reportable per 10 CFR 50.73(a)(2)(iv).
2771999005 | Peach Bottom 2 | 06/16/1999 | 07/16/1999 | 9907220218 | <strong>This LER reports a failure to maintain the provisions of the Fire Protection Program, where the Fire Safe Shutdown analysis did not recognize that a Unit 2 HPCI vacuum breaker motor operated isolation valve could fail closed During a fire, preventing the</strong><br /><i>Abstract:&nbsp;</i>During a review of the Fire Safe Shutdown (FSSD) supporting analyses, an issue associated with a failure to maintain the provisions of the Fire Protection Program was identified. This issue involves potential damage to the Unit 2, High Pressure Coolant Injection (HPCI) vacuum breaker motor operated isolation valve's motive and control power source as a result of a postulated fire. Spurious closure of the vacuum breaker motor operated isolation valve due to fire damage, would allow initial start of the HPCI system, but could prevent subsequent restarts of the HPCI system as required for the Fire Safe Shutdown scenario. Subsequent restarts of the HPCI system could be impacted as a result of potential damage from a waterhammer event in the steam exhaust line. The primary cause of issue has been attributed to less than adequate engineering rigor in both the development and review of an analysis that supports the Fire Safe Shutdown Program. An hourly roving fire watch was immediately established for the affected fire area. This condition represent a failure to maintain the provisions of the Fire Protection Program.
2771999006 | Peach Bottom 2 | 09/30/1999 | 01/13/2000 | ML00368389 | <strong>This LER is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(iv) for the Engineered Safety Feature actuations following the turbine trip and the requirements of 10CFR50.73 (a)(2)(i)(B) for exceeding the heatup rate specified by the Tech Spec.</strong><br /><i>Abstract:&nbsp;</i>On Thursday, September 30, 1999 at approximately 19:06 hours, with Unit 2 operating at 100 percent power, a generator lockout and subsequent turbine trip, occurred that resulted in a reactor SCRAM. The turbine trip caused a high reactor pressure condition resulting in three Main Steam Relief Valves (MSRV) lifting and an Alternate Rod Insertion (ARI) initiation. Additionally, Primary Containment Isolation System (PCIS) Group II and Group III isolations occurred due to low reactor water level following the SCRAM. The generator lockout occurred when the Generator Over Frequency relay actuated the Accidental Energization Protection generator lockout relay. The Generator Over Frequency relay was actuated by a transient ground on the DC Power System. On Saturday, October 2, 1999, at approximately 04:20 hours, with Unit 2 in Mode 3, the Reactor Recirculation System piping experienced a heatup rate of approximately 170° F within 45 minutes. This exceeded the 100° F/hr heatup rate as specified In Tech. Spec. Section 3.4.9. This occurred while flushing the Residual Heat Removal (RHR) system to equalize temperatures in the 2A Reactor Recirculation piping prior to restarting the 2A recirculation pump. These activities were being performed as part of the SCRAM recovery activities. There were no safety consequences from these events and all safely systems were available. The ARI initiation, the lifting of MSRVs, and the PCIS isolations are reportable per 10 CFR 50.73 (a)(2)(iv). Exceeding the heatup rate of the recirculation line specified in Tech. Spec. Section 3.4.9 Is reportable per 10CFR 50.73 (a)(2)(i)(B).
2771999007 | Peach Bottom 2 | 11/11/1999 | 12/11/1999 | ML99354045 | <strong>This LER reports an inoperability of a Core Spray pump room ooler fan due to the control switch not being in the RUN position, causing the associated Core Spray subsystem to be inoperable for a time period greatre than the Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1999, with Unit 2 operating at approximately 100 percent power, the operating crew performed a surveillance test of the 2B Core Spray pump. The applicable Core Spray pump room cooler fan failed to automatically start, as expected. The operating crew declared the room cooler inoperable and declared the Core Spray subsystem inoperable, as directed by the Technical Requirements Manual. A seven day Technical Specification Action was entered. Subsequent investigation determined that the contact for the control switch for the Core Spray pump room cooler tan was not fully made up when the switch indicated in the RUN position. All other ECCS cooler switch positions were verified. Further investigation revealed the Core Spray room cooler tan and its associated Core Spray subsystem were inoperable for approximately forty-eight days. The Technical Specification allowable outage time is seven days for a Core Spray subsystem. The unit was also started up and taken to Mode 1 with an inoperable Core Spray subsystem, which violated Technical Specification 3.0.4. The LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(i)(B) due to a condition prohibited by Technical Specifications existing for greater than the time allowed by the applicable action statement and violating Technical Specification 3.0.4.
2771999008 | Peach Bottom 2, Peach Bottom 3 | 12/02/1999 | 01/01/2000 | ML00367284 | <strong>This LER reports an inoperability of all RHR pumps simultaneously During the RHR Logic System Functional Test</strong><br /><i>Abstract:&nbsp;</i>During a review of the RHR Logic System Functional Test (LSFT) procedure, Engineering Department personnel discovered that a portion of the current revision of the procedure caused all four Residual Heat Removal (RHR) pumps to be inoperable (incapable of automatically starting) simultaneously for approximately two hours during performance of the test This discovery occurred on December 2, 1999. Further investigation revealed that the 2A RHR logic was last tested in August, 1997; the 2B RHR logic was last tested in March, 1997; the 3A RHR logic was last tested in March, 1997; and the 3B RHR logic was last tested in September, 1997. A review of previously performed RHR LSFT procedures from 1992 through 1997 indicate that this situation has occurred during previous test performances. Both units were in Mode 1 the last time the tests were previously completed. The resulting condition placed the applicable unit in LCO 3.0.3 for approximately two hours. The LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(i)(B) and 10 CFR 50.73 (a)(2)(v) due to all Residual Heat Removal (RHR) system pumps being rendered inoperable during performance of the RHR Logic System Functional Test This occurred on both Unit 2 and Unit 3.
2781999001 | Peach Bottom 3 | 03/12/1999 | 04/08/1999 | 9904150008 | <strong>An Engineered Safety Feature actuation of Reactor Core Isolation Cooling System due to a high steam flow signal During system resotration</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1999, an automatic Reactor Core Isolation Cooling (RCIC) system isolation occurred due to a high differential pressure signal while realigning the system for automatic operation. The RCIC system had previously been removed from service to place the inboard RCIC steam isolation valve into a back seated position. After the inboard isolation valve was opened to its back seated position, the outboard isolation valve was partially opened to allow the system to slowly pressurize in accordance with the restoration procedure. The valve was opened too far and the system isolated automatically on a differential pressure condition signal. The RCIC system isolation completion was confirmed utilizing operating procedures, the system integrity was verified and the system isolation signal was reset. A temporary change to the restoration procedure was initiated to open the RCIC outboard steam isolation valve in smaller increments to eliminate the potential for a high differential pressure condition signal from occurring. The RCIC inboard isolation valve was returned to the back seated position and the RCIC system was returned to service on March 12, 1999.
2781999003 | Peach Bottom 3 | 08/14/1999 | 09/13/1999 | 9909160036 | <strong>High Pressure Coolant Injection System Declared Inoperable Due to Erratic Behavior Resulting in a Loss of a Single Train Safety System.</strong><br /><i>Abstract:&nbsp;</i>On 08/14/99 at approximately 0435 hours, during performance of Surveillance Test ST-0-023-301-3, HPCI Pump, Valve, Flow, and Unit Cooler Functional and In-Service Test, the High Pressure Coolant Injection (HPCI) system exhibited oscillations in discharge pressure, speed, and flow rate. HPCI was subsequently declared inoperable and the appropriate Technical Specification Action statement was entered. The Nuclear Regulatory Commission was notified at approximately 0535 to meet the requirements of 10 CFR 50.72(b)(2)(iii), Four Hour Reports. No actual safety consequences occurred as a result of this event. The cause of this event has been determined to be a weakness in procedural guidance for adjusting the hydraulic governor (EG-R) needle valve which lead to oscillations in the HPCI control system. Following the event, the hydraulic governor needle valve was readjusted and the HPCI system was restored to an operable status.
2781999004 | Peach Bottom 3 | 09/01/1999 | 10/01/1999 | 9910050207 | <strong>This LER reports multiple unplanned Engineered Safety Feature (ESF) actuatjions During planned modification activities in the Main Control Room</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, September 1, 1999 at approximately 0850 hours, during planned modification activities on a Main Control Room panel, the 3A Reactor Protection System (RPS) bus was inadvertently deenergized. An electrician inadvertently repositioned the RPS Alternate Power Transfer switch which caused the deenergization of the 3A RPS bus. This caused the inboard PCIS Group III isolation valves to close and initiated the Unit 3 Standby Gas Treatment (SGT) system. This constituted an unplanned Engineering Safety Feature (ESF) actuation and resulted in a non-emergency four hour notification to the NRC per 10 CFR 50.72(b)(2)(ii). The operating crew responded to the loss of power to the 3A RPS bus per appropriate plant procedures and restored all PCIS Group III isolation valves systems and SGT system to their normal configurations. This condition is reportable per 10 CFR 50.73(a) (2) (iv).
2781999005 | Peach Bottom 3 | 09/20/1999 | 10/20/1999 | 9910260115 | <strong>Unplanned Engineered Safety Feature (ESF) actuations During planned modification activities in the Main Control Room.</strong><br /><i>Abstract:&nbsp;</i>On Monday, September 20, 1999 at approximately 1435 hours, during planned modification activities on a Main Control Room panel, a unit 3 'B' channel reactor manual half scram occurred. As a result of the manual half scram, the outboard scram discharge volume (SDV) vent and drain valves closed. This event occurred when a reactor protection system (RPS) wire was damaged during drilling activities for installing a mounting plate. This constituted an unplanned Engineering Safety Feature (ESF) actuation and resulted in a non-emergency four hour notification to the NRC per 10 CFR 50.72 (b) (2) (ii). The operating crew responded to the loss of power to the 3 'B' RPS manual half scram logic per appropriate plant procedures, the damaged RPS wire was repaired, the manual half scram was reset, and the SDV vent and drain valves were reopened. This condition is reportable per 10 CFR 50.73(a)(2)(iv).
2801999001 | Surry 1 | 12/22/1998 | 01/21/1999 | 9901270157 | <strong>Auxiliary Feedwater Pipe Support MIssed Surveillance Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 22, 1998, it was determined that two pipe supports on the cross-connect line of the auxiliary feedwater pumps had not been inspected during the second Inservice Inspection (ISI) interval in accordance with Technical Specification (TS) 4.0.5. The TS requires inspection and testing of ASME Class 1, 2, and 3 components. The supports in question were not shown on the current station drawings and as a result were omitted from the ISI Program. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. The two supports received Code inspection and were found fully acceptable. Therefore, no conditions adverse to safety resulted from this event.
2801999002 | Surry 1, Surry 2 | 03/01/1999 | 03/29/1999 | 9904060211 | <strong>Prematurely Released Fire Watches Resulted in Violation of TS 3.21.B.7</strong><br /><i>Abstract:&nbsp;</i>During a recent 10CFR50 Appendix B audit of the Surry Fire Protection Program conducted by the Nuclear Oversight Department, it was observed that the procedure for opening and sealing fire stops allowed the fire watch to be released after an initial inspection, but prior to final inspection and prior to the recommended 24-hour cure time of the silicone foam used. Upon further review, it was recognized that allowing the fire watch to be released prior to completion of the final inspection also constituted a past violation of Technical Specifications. The cause of this situation was an inadequate procedure. The procedure for opening and sealing fire stops has been revised to change the sequence of activities to require the final inspection after the 24-hour cure time and to release the fire watch following satisfactory completion of the final inspection. This situation resulted in no safety consequences or implications and is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a past occurrence of a condition prohibited by Technical Specifications.
2801999003 | Surry 1, Surry 2 | 03/31/1999 | 04/28/1999 | 9905050111 | <strong>Potential Loss of Charging Pumps Due to Main Control Room Fire</strong><br /><i>Abstract:&nbsp;</i>As part of the ongoing Configuration Management Project's integrated review of fire protection and in conjunction with review of recent industry operating experience events, it was determined that the potential to lose the charging/high head safety injection pumps in the event of an Appendix R main control room fire existed at Surry Power Station. The Surry procedure for the main control room fire, as written at the time of the reviews, was inadequate. The procedure did not include specific direction to ensure that charging/high head safety injection suction alignment and control was established and maintained in a time frame to minimize the possibility of volume control tank depletion and potential loss of the charging pumps. These circumstances placed the station outside its Appendix R design basis for both units in that the potential loss of charging/high head safety injection pumps could result in the inability to achieve and maintain a safe shutdown condition in the event of an Appendix R MCR fire. This situation resulted in no safety consequences or implications and is being reported pursuant to 10CFR50.73(a)(2)(ii)(B) and 10CFR50.73(a)(2)(ii)(C).
2801999004 | Surry 1, Surry 2 | 07/14/1999 | 11/24/1999 | ML99335002 | <strong>TS Violation Due to Non-Safety Related Fans' Effect on Control Room Boundary</strong><br /><i>Abstract:&nbsp;</i>The non-safety related Cable Vault fans were tagged out in October 1998 when it was determined that the Main Control Room (MCR) bottled air system was not capable of meeting Technical Specification (TS) requirements with the fans running. The fans were returned to service June 11, 1999, following maintenance and an Engineering evaluation. The fans were tagged out on June 23, 1999 following additional testing. On July 22, 1999, based on further evaluation it was determined that under certain conditions the bottled air system would not have met the TS differential pressure (DP) requirement during the period of time the fans had been returned to service. The Cable Vault fans have remained out of service except for testing (during which time they are administratively controlled) since this time. While investigating the Cable Vault fan issue, a concern was identified with the DP between the MCR and the Cable Spreading Room. It was determined on July 14, 1999 that the TS required DP between the MCR and the Cable Spreading Rooms was not met with the Cable Spreading Room fans running. The doors between the Cable Spreading Rooms and the Mechanical Equipment Rooms were opened and have remained open except for testing (during which time they are administratively controlled) in order to meet the TS required DP. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications.
2801999005 | Surry 1, Surry 2 | 07/31/1999 | 08/27/1999 | 9909020020 | <strong>Radiation Monitors Inoperable Due to Heat Trace Failure</strong><br /><i>Abstract:&nbsp;</i>Units 1 and 2 were operating at 100% and 82% power, respectively, on July 31, 1999, when a control room annunciator alarmed, indicating a problem with the effluent radiation monitors. The appropriate annunciator response and abnormal procedures were promptly performed and a low sample flow condition was identified for the gaseous vents system radiation monitors, 1-VG-RM-131-1 and 1-VG-RM-131-2. The monitors were declared inoperable at 08:28 and the preplanned alternate method of monitoring was initiated in accordance with Technical Specifications (TS) Table 3.7-6. An action statement was entered in accordance with TS Table 3.7-6, requiring restoration of the monitors within seven days or the submittal of a Special Report within 30 days. Investigation of the problem revealed that one of the heat trace circuits for the monitors' sample suction line was degraded, which allowed the formation of condensation within the system. As a result, condensation accumulated and blocked the sample flow through the system. The degraded heat trace circuit was replaced, additional heat trace is being installed, and the monitors are scheduled to be returned to service by August 30, 1999. To prevent recurrence, a preventive maintenance task was initiated to periodically check the condition of the heat trace circuits. This Special Report is being submitted pursuant to TS Table 3.7-6.
2801999006 | Surry 1, Surry 2 | 08/02/1999 | 08/27/1999 | 9909030032 | <strong>Outside Appendix R Design Basis Due to Fire Barrier Deficiencies</strong><br /><i>Abstract:&nbsp;</i>During performance of the 18-month periodic test for fire barrier inspections, two separate, not easily accessible design deficiencies were identified. The first was a gap at the top of a wall between the Turbine Building fire area and the Auxiliary Building fire area; the second was a through-wall mechanical blockout between the Emergency Switchgear Room fire area and the Main Control Room fire area. The configuration of these fire barriers did not provide the required fire rating and may not have fulfilled the Appendix R design basis requirements in the event of a fire. These deficiencies are part of the original plant design and construction, and neither resulted in any significant safety consequences or implications. Design modifications have been completed to repair both deficiencies. This report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(B) for two design deficiencies that each constitute a condition outside the Appendix R design basis of the plant.
2801999007 | Surry 1, Surry 2 | 10/09/1999 | 11/05/1999 | ML99319047 | <strong>Undervoltage Actuation Due to a Loss of Reverse Station Service Transformer</strong><br /><i>Abstract:&nbsp;</i>On October 9, 1999, at 1234 hours, with Units 1 and 2 at 100% power, control room annunciators alarmed, indicating an overvoltage condition on the Unit 1 "H" (1H) and Unit 2 "J" (2J) emergency buses. Operators dispatched to the "C" Reserve Station Service Transformer (RSST) saw small flames at the bus bar-to-cable connections for the "A" phase of the 4160 V feeder from the "C" RSST to the station. At 1241 hours, an electrical arc from a cable connection to the metal siding of the adjacent Turbine Building resulted in an "A" phase-to-ground fault and "C" RSST lockout. The loss of the "C" RSST caused an undervoltage condition on the "F" transfer bus and a loss of the 1H and 2J emergency buses. Emergency Diesel Generators Nos. 1 and 3 automatically started, as designed, and re-energized the buses. The station's fire brigade quickly responded to the fire and control room operators executed the appropriate abnormal and operating procedures. A root cause evaluation (RCE) has preliminarily concluded that moisture intrusion into the protective sleeve of one of the cable connections provided a conductive path, producing electrical arcing. The damaged "C" RSST "A" phase cable connection was replaced. Approved RCE recommendations, designed to prevent the recurrence of a similar event, will be implemented. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv).
2811999001 | Surry 2 | 03/01/1999 | 03/31/1999 | 9904060129 | <strong>RPS Relay Not placed in Trip Results in Violation of TS 3.7</strong><br /><i>Abstract:&nbsp;</i>At 0115 hours on March 1, 1999, with Unit 2 operating at 91 % power, an Operator found the limit switch lever arm for the Unit 2, train A, No. 4 Turbine Stop Valve lying on the floor. Operations declared the valve inoperable and entered TS Table 3.7-1, Operator Action Statement 12, which requires the affected channel of the Reactor Protection System (RPS) to be placed in the tripped condition within 6 hours. At 0528 hours, a procedure was initiated to place the subject RPS channel in the tripped condition. While performing the procedure, relays corresponding to No. 2 Turbine Stop Valve were placed in trip instead of those corresponding to No. 4 Turbine Stop Valve. The limit switch lever arm was repaired and operability testing was performed. While testing, Control Room personnel noted a discrepancy in the RPS channel that had been placed in trip. This event was caused by the lack of specific procedural guidance and the failure of I&C personnel to obtain sufficiently detailed information. To prevent recurrence, a new procedure will be developed to provide more explicit instructions for placing a stop valve relay in trip. This event resulted in no safety consequences or implications because RPS train B remained operable. Since the inoperable RPS channel was not placed in the tripped condition as required by TS, this event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
2811999002 | Surry 2 | 04/25/1999 | 05/18/1999 | 9905240126 | <strong>Main Steam Safety Valves Tested Out of Tolerance for As Found Setpoint</strong><br /><i>Abstract:&nbsp;</i>On April 25, 1999, April 27, 1999, and April 28, 1999, with unit 2 in Refueling Shutdown, setpoint testing of Unit 2 Main Steam Safety Valves (MSSVs) revealed that the lift settings for three valves were outside of the as found setpoint tolerance (+/- 3%) that is allowed by Technical Specification (TS) 3.6.A. The event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for conditions prohibited by TS 3.6.A. The safety valves were overhauled, adjusted, and tested to verity that they were within the correct as left setpoint tolerance (+/- 1 %) allowed by TS. The event posed no significant safety implications because the safety valves would have still performed their safety function in the event of an overpressure condition. The health and safety of the public were not affected at any time.
2811999003 | Surry 2 | 07/05/1999 | 07/30/1999 | 9908120152 | <strong>Auto Reactor Trip on Low Coolant Flow Due to Loop Stop Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1999, at 11:22, the Unit 2 reactor automatically tripped from 100% power as a result of low flow in the "A" loop of the reactor coolant system (RCS). The plant responded to the reactor trip, as designed. The auxiliary feedwater pumps were secured and withdrawal from the condensate storage tank (CST) was terminated at 12:07. The Technical Specification (TS) two hour action statement for refilling the tank was inadvertently not entered, and refilling of the CST began at 19:05. At 18:10, the "A" cold leg loop stop valve, 2-RC-MOV-2591, was removed from its backseat as a part of the normal unit cooldown sequence. When an attempt was made to reopen the valve fully, a full open position was not indicated. Since compliance with TS 3.17.1 was not maintained, a 30 hour action statement to place the unit in a cold shutdown condition was entered in accordance with TS 3.0.1. A root cause evaluation (RCE) investigation determined that the low flow condition in the "A" RCS loop resulted from the separation of the 2-RC-MOV-2591 valve's disc assembly from the stem, which allowed the disc assembly to drop into the flow stream. Approved RCE recommendations, designed to prevent the recurrence of a similar event, will be implemented through the corrective action program. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(iv) and 10 CFR 50.73 (a)(2)(i)(B).
2811999004 | Surry 2 | 11/09/1998 | 10/01/1999 | 9910080212 | <strong>EDG Inoperable Longer than Allowed by TS Due to Governor Compensation Valve</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1998, emergency diesel generator (EDG) No. 3 was rendered inoperable by an electrical fault. Repairs were effected and testing was performed to return the EDG to service. During the testing, the EDG governor load response characteristics were not as expected. Engineering and vendor personnel investigated the condition and concluded that the observed anomaly would occur only under test conditions and would not affect EDG emergency operation. EDG No. 3 was returned to an operable status on November 7, 1998. During the following two days, the potential causes of the governor load response anomaly were further evaluated. As a conservative measure, the suspect governor was replaced on November 10, 1998, and was subsequently sent to the vendor for testing. On September 9, 1999, engineering personnel concluded, based on the results of the vendor testing, that the governor would not have maintained the correct speed during emergency operation. Based on this conclusion, EDG No. 3 remained inoperable from November 2 to 10, 1998. This event was caused by the governor compensation valve being closed. A root cause evaluation is being performed to determine how the compensation valve became closed. This report is being submitted pursuant to 10 CFR 50.73 (a)(2)(i)(B) since EDG No. 3 was inoperable longer than allowed by Technical Specifications.
2821999001 | Prairie Island 1, Prairie Island 2 | 01/05/1999 | 02/04/1999 | 9902120157 | <strong>Reactor Trip Following Failure of the Station Auxiliary Transformer</strong><br /><i>Abstract:&nbsp;</i>At approximately 1311 on January 5, 1999, with Unit 1 operating at 100% power and no electrical switching in progress an internal fault occurred in the Unit 1 Main (1M) transformer. The fault caused an explosion in the transformer and Unit 1 Turbine Trip / Reactor Trip. As a result of the explosion, the 1M transformer was breached and a large was expelled and ignited in an area approximately 40 feet north of the transformer. The Fire Brigade was spa the site and extinguished the burning oil fire at approximately 1325. As a result of the fault, explosion, and fire, both 1M and 1R (Unit 1 reserve transformer) were locked out. This caused the loss of non-safeguards buses 11, 12, 13, & 14 and major equipment on Unit 1 powered from these buses including both reactor coolant pumps (RCPs), both feedwater pumps, both circulating water pumps, all condensate pumps, all heater drain pumps, 11 cooling water pump, all Turbine Building and Auxiliary Building lighting (except for battery backed emergency lighting), motor driven fire pump, spent fuel pool cooling, and a loss of all non-safeguards 480V buses fed from these buses. With the loss of both RCPs, Unit 1 was on natural circulation. No diesel generators started. One safeguards bus was never lost, the other successfully transferred sources automatically. After the initial response to the event was completed and the unit stabilized, power was restored to non-safeguards 4KV buses and the RCPs were restarted between 7 and 8 hours following the transformer fault. The unit was restored to normal power operation over the following week.
2821999002 | Prairie Island 1 | 01/08/1999 | 02/04/1999 | 9902120133 | <strong>While at Hot Shutdown a RCP was Tripped During Surveillance Testing of RCP Breakers, Resulting in no RCPs Running and an Auto-Start of an Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1999, while Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was at hot shutdown (due to the 1M transformer fault) surveillance procedure SP 1016, "RCP Breakers Test," was being performed. Per the SP, the 11 Reactor Coolant Pump (RCP) was stopped and Bus 11 was de- energized. At 0852, during the execution of SP 1016, 12 RCP tripped and the 11 Turbine Driven Auxiliary Feedwater Pump (TDAFWP) auto-started. This event was reported via the Emergency Notification System on the basis of entry in PINGP Technical Specification 3.0.C (due to loss of both RCPs) and on the basis of ESF actuation of the 11 TDAFWP. SP 1016 (and corresponding Unit 2 SP 2016) will remain quarantined until the procedures are appropriately revised.
2821999003 | Prairie Island 1, Prairie Island 2 | 01/21/1999 | 02/22/1999 | 9903020203 | <strong>Design Basis Issues Identified While Updating with High Energy Line Break Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1999, Prairie Island Nuclear Generating Plant Units 1 and 2 were operating at 100% power. Engineering staff, revising the high-energy line break (HELB) analysis, found the configuration of four Auxiliary Building doors violated the assumptions of the analysis. Certain areas of the Auxiliary Building were determined to be susceptible to room over-pressurization during a postulated HELB. Four of six doors that were assumed to open during the HELB to minimize the pressure transient in the affected room were latched, thus, preventing them from opening at the pressure assumed in the analysis. Two of the six doors had been blocked open to alleviate flooding concerns. A work order (and supporting 10 CFR 50.59 safety evaluation and temporary modification package) was written to release door latch pins on the six doors and secure the pins to prevent re-latching.
2821999004 | Prairie Island 1, Prairie Island 2 | 04/02/1999 | 05/03/1999 | 9905070038 | <strong>Surveillance Procedure Inadequate to Demonstrate Operability of Spent Fuel Pool Special Ventilation System</strong><br /><i>Abstract:&nbsp;</i>With Prairie Island Units 1 and 2 operating at 100% power, the plant engineering staff concluded on April 2, 1999 that surveillance testing of the Spent Fuel Pool Special Ventilation System (SFPSVS) did not satisfy Technical Specifications Section 4.15.A.2, which requires that "automatic initiation of each train shall be demonstrated with a simulated high radiation signal." SP 1115, "Spent Fuel Pool Special Ventilation System Test," does verify that a high level alarm from either radiation detectors R-25 or R-31 will isolate the Spent Fuel Normal Ventilation Supply and Exhaust Dampers and actuate the Spent Fuel Special Ventilation System, but it does not verify that the In-Service Purge System exhaust lines isolate. Testing on Unit 1 has indicated that the In-Service Purge System exhaust lines would have isolated when required. This deficiency in SP 1115 has existed since its first initial issuance and was not identified by our initial Generic Letter 96-01 review.
2821999005 | Prairie Island 1 | 05/08/1999 | 06/07/1999 | 9906150092 | <strong>Containment Inservice Purge System Not Isolated During Heavy Load Movement Over Fuel</strong><br /><i>Abstract:&nbsp;</i>On May 8, 1999, with Prairie Island Unit 1 in a refueling shutdown (Mode 6) and Unit 2 operating at 100% power, the plant staff identified that during the just completed performance of D58.1.6, "Reactor Upper Internals Replacement," the reactor upper internals, a heavy load, was transported over the open fueled reactor vessel with the Containment Inservice Purge system operating. A procedure step in D58.1.6 for closing the containment inservice purge system containment isolation valves was inadvertently missed and was not discovered until after the upper internals had been set in the reactor vessel. Analysis of the event concluded that this event has had no adverse impact on the health and safety of the public and was of negligible safety significance.
2821999006 | Prairie Island 1 | 05/19/1999 | 06/18/1999 | 9906220035 | <strong>Manual SI Actuatjion Switch Not Tested On Staggered Basis During Intergrated SI Test</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1999, with Prairie Island Unit 1 in a refueling shutdown (Mode 6) and Unit 2 operating at 100% power, the plant Superintendent I&C System Engineering identified that during the just completed performance of SP 1083, "Unit 1 Integrated SI Test With a Simulated Loss Of Offsite Power," the incorrect manual initiation switch had been used to actuate the manual SI initiation. Further investigation revealed that this error had also occurred during the previous performance of SP 1083 for the Unit 1 refueling outage in 1997, but had not occurred during any of the last three performances of SP 2083 (Unit 2). Technical Specification Table 4.1-1B requires that a functional test (table notation 20) of the Safety Injection manual injection functional unit (item 1.a) be performed each refueling shutdown, where "one manual switch shall be tested at each refueling on a STAGGERED TEST BASIS." During the Unit 1 1997 refueling outage this requirement was not satisfied. The surveillance procedures for the "Integrated SI Test With a Simulated Loss of Offsite Power," SP 1083 and SP 2083 have been determined to be inadequate and have been quarantined until a procedure revision is completed to clarify the required testing sequence of the manual SI actuation switches.
2821999007 | Prairie Island 1, Prairie Island 2 | 06/25/1999 | 08/26/1999 | 9908310307 | <strong>Loss of Control Room Special Ventilation Function Due to Broken/Inadequate Door Latch Pins On Control Room Chiller Doors</strong><br /><i>Abstract:&nbsp;</i>On several recent occasions this year with Prairie Island Units 1 and 2 operating at 100% power, the integrity of the barrier provided by the door for doorway 158 in the train B Control Room Chiller room was either found to be inoperable or was believed at the time to be inoperable. The doorway 158 consists of a double door with one side configured and utilized as an active door while the other side is utilized infrequently and configured as a passive door with an upper and a lower latch pin maintaining it in a closed position. On June 25 and July 27 plant staff found that the double doors could be pushed open into the chiller room and that the passive door latch pins were not intact. On August 5 the lower latch guide plate was found detached from the door. On August 12 testing of the material composition in the original (brass) and replacement (steel) latch pins indicated that it was very likely that neither of these materials had the yield strength required to perform their safety function. Plant staff has concluded that the failure evident in the first three incidents was due to a lack of timely and proper maintenance on the door, which was due to the absence in Technical Specification 3.13 of a sufficient provision for an allowed out of service time (AOT) for the Control Room Special Ventilation System. An amendment request to establish an AOT is under preparation and will be submitted to NRC staff. The latch pins for doorways 158 and 159 (Train A and B Control Room Chiller rooms) have been replaced with pins machined onsite from traceable material having significant margin to the required yield strength.
2821999008 | Prairie Island 1, Prairie Island 2 | 11/04/1999 | 12/06/1999 | ML99347014 | <strong>Engineered Safety Features Actuation Following Bus Lockout Caused by an Accidental Actuation of a Lock Out Relay</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1999, with both units at 100% power, Breaker CT11-1 was being aligned to be placed into its cubicle following maintenance when the breaker primary stabs came in contact with terminals 1 and 2 of the A-phase Overcurrent Relay, 51A. This caused actuation of the Bus CT11 Lock Out Relay (LOR), 86B/CT11. The LOR, 86B/CT11, tripped Breaker CT11-6 and Breaker CT-BT112. Trip of Breaker CT-BT112 caused Bus CT11 to go dead. Trip of Breaker CT11-6 caused Bus 16 (Unit 1 Train B Safeguards 4160V Bus) to go dead. Upon undervoltage on Bus 16, 12 Component Cooling Water Pump tripped and the load sequencer re-aligned Bus 16 to the 1R Source. Technical Specification 3.7.B, loss of one of the two required paths from the grid to the unit 4 kV safeguards distribution system, was entered. The 11 Component Cooling Water Pump also auto- started on low pressure in the Component Cooling Water system resulting from the trip of the 12 Component Cooling Water Pump. Inspection of Breaker CT11-1 and the associated 51A relay showed no obvious signs of damage due to the contact. Therefore, the breaker was placed into cubicle CT11-1 in preparation for post maintenance testing. After evaluation by the System Engineer of the apparent cause and effects, the Bus CT11 LOR, 86B/CT11, was reset and Breaker CT-BT112 and Breaker CT11-6 were closed. Bus 16 was realigned to the CT source.
2851999001 | Fort Calhoun | 02/03/1999 | 03/05/1999 | 9903100133 | <strong>Shutdown Technical Specification Entry Due to Auxiliary Feedwater Inoperability</strong><br /><i>Abstract:&nbsp;</i>On February 2, 1999, at 1235, the steam driven auxiliary feedwater pump (FW-10) was logged as inoperable per Technical Specification (TS) 2.5 in preparation for the planned performance of quarterly surveillance test IC-ST-IA-3009, "Operability Test of IA-YCV-1045-C and Close Stroke Test of YCV-1045." This test manually isolates steam to the FW-10 turbine to allow functional testing of IA-YCV-1045-C, the FW-10 Steam Inlet Instrument Air Accumulator Check Valve. During the performance of IC-ST-IA-3009, IA-YCV-1045-C failed to meet the acceptance criteria specified in the surveillance test. On February 3, 1999, at 1202, Fort Calhoun Station commenced a TS 2.0.1 required shutdown. Testing of IA-YCV-1045-C was conducted in parallel with the plant shutdown. The revised surveillance test and FW-10 operability test were successfully completed and FW-10 was restored to an operable condition at 1424. The plant shutdown was subsequently terminated, with plant power at 59 percent. The root cause of this event is that the initial markup of procedure IC-ST-IA-3009 did not place valve YCV-1045-20-1, Solenoid Isolation to Steam Supply to FW-10, in the vented position during the performance of the IA-YCV-1045-C check valve leakage test as it would be for an actual overpressure condition at FW-10. Procedure IC-ST-IA-3009 was corrected to properly perform the surveillance test.
2851999002 | Fort Calhoun | 09/10/1998 | 07/08/1999 | 9907130122 | <strong>Inadvertent Initiation Of An Engineered Safeguards Feature Circuit Due To Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1998, with the plant operating at 100 percent power, an inadvertent Ventilation Isolation Actuation Signal (VIAS) occurred while maintenance was being performed on process radiation monitor RM-062 due to a defective key switch on the radiation monitor. While the RM-062 high alarm output signal to the Containment Radiation High Signal (CRHS) logic circuitry was being disabled by repositioning its key switch from "ON" to "KEYPAD," a problem associated with the key switch allowed the interruption of power to the Integrated Circuit (IC) used to determine trip actuation. The loss of power to the IC resulted in the triggering of an internal relay that provides an input to CRHS logic. This in turn caused CRHS to actuate, which in turn caused VIAS to actuate. Following a review on June 8, 1999, of the control room log for September 10, 1998, to determine the events surrounding the inadvertent VIAS actuation, station personnel determined that the inadvertent VIAS actuation should have been reported on September 10, 1998. The key switch for RM-062 has been replaced. The four hour report required by 10 CFR 50.72(b)(2)(ii)(B)(3) was made on June 8, 1999. A cause analysis for the inadvertent VIAS actuation and the failure to report the inadvertent VIAS actuation has been completed and resulting corrective actions developed. These include evaluating other similar switches for replacement and revising appropriate plant procedures to provide clearer guidance for reporting VIAS actuations.
2851999003 | Fort Calhoun | 10/11/1999 | 11/09/1999 | ML99323005 | <strong>Pressurizer Safety Valve Outside Lift Setting Acceptance Range</strong><br /><i>Abstract:&nbsp;</i>At 1331 hours on October 11, 1999, during a scheduled refueling outage, it was discovered that the "as-found" lift pressure of Pressurizer Safety Valve (PSV) RC-142 was outside its specified lift setting acceptance range. Fort Calhoun Station (FCS) Technical Specification (TS) 2.1.6(1) indicates that this valve is to have its lift setting adjusted to ensure valve opening at 2485 psig +/-1% (i.e., a range of 2460.2 to 2509.8 psig). The "as-found" lift pressure was 2516 psig, which is 1.25% above the nameplate set pressure. The other PSV, RC-141, was found to be within its acceptance range. It was concluded that the root cause of this event was normal setpoint drift/scatter. Corrective actions included disassembling, cleaning, inspecting, and refurbishing RC-142, followed by testing and adjustment to achieve an "as-left" lift setting within the +/-1% tolerance range.
2851999004 | Fort Calhoun | 10/26/1999 | 11/24/1999 | ML99335003 | <strong>Loss of Both Station Vital Buses While Transferring Station Lighting</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1999, with the plant operating in Mode 5 for refueling operations, procedural steps were being performed to prepare for load shedding of one of the two station 4160 V vital buses and an automatic start of its associated diesel generator (DG. As part of the setup, normal station lighting is transferred from one vital bus to the other. When the control room (CR) operator performed the step to transfer lighting, a loss of normal lighting and power to both vital buses occurred. Emergency lighting actuated and functioned as designed until normal lighting was restored. The loss of power caused a loss of shutdown cooling (SDC). The CR operators restored power to the vital buses using the DGs. SDC was lost for about 2 minutes with no temperature rise. An extensive investigation was conducted to determine the cause of the event. The root cause is the introduction of an electrical noise spike into the 125 VDC system from the electromagnetic coupling of the 125 VDC system with the 4160 V system during operation of the lighting transfer switch due to wiring practices employed when the switch was installed. It was also determined that a recent modification had removed a significant amount of capacitance from the 125 VDC control circuit associated with a relay that initiated the event. The lighting transfer switch has been danger tagged in the "NORMAL" position to prevent its operation until suitable corrective action can be designed to reduce the induced noise in the 125 VDC circuitry from the operation of the switch. Two filter networks have been added to the lockout relay circuit to restore the noise immunity of this circuitry.
2851999005 | Fort Calhoun | 10/29/1999 | 11/24/1999 | ML99335002 | <strong>Failure to Satisfy Surveillance Requirements for a Containment Penetration</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1999, with the plant in Mode 5 for refueling, it was discovered that a pipe nipple, used to pressurize the Waste Disposal Gas (WDG) header piping associated with containment penetration M-14 for containment isolation valves leak rate testing, did not penetrate the system piping. A review of past records indicates that containment isolation valves leak rate (Type C) tests performed during the 1993, 1995, and 1996 refueling outages using this pipe nipple were invalid as a result of this problem. The containment isolation valves associated with penetration M-14 were not checked for leakage as required by technical specifications since no pressure was applied to them. The cause of this event was determined to be inadequate corrective actions, in that the evaluation in 1993 was not adequate to determine the condition of the pipe nipples associated with penetrations M-14 or M-80. The evaluation in 1996 resulted in the leakage data for penetration M-14 being incorrectly interpreted. Physical checks of all other penetrations addressed by corrective actions in response to NRC Information Notice (IN) 92-20, inadequate Local Leak Rate Testing," have been conducted to determine that all in-use fill connections are drilled through the pipe and physically connect with the components being tested.
2851999006 | Fort Calhoun | 10/29/1999 | 12/30/1999 | ML00367707 | <strong>Missed Technical Specification Requirement for Low Power Core Physics Test</strong><br /><i>Abstract:&nbsp;</i>While reviewing results of the low power core physics testing conducted during the start of operating cycle 18 (June, 1998) in preparation for low power core physics testing following the present refueling outage (cycle 19, November 1999), it was determined that control rod drop testing was completed 8 days prior to the control element assembly (CEA) group worth test instead of within 7 days as required by the station's technical specifications. The rod drop test exercises each control rod and verifies that if will fall to the bottom of its range when the rod drive mechanism is deenergized. The cause of this event was inadequate review of a procedure change by the preparer of the change document. A contributing cause of this event was the unclear guidance on the form used to correct documentable errors regarding what constitutes adequate verification and validation of a documentable error. The low power core physics test procedure was revised to reinsert the prerequisite to perform control rod drop testing within 7 days prior to the performance of the CEA group worth test.
2861999001 | Indian Point 3 | 01/08/1999 | 02/05/1999 | ML10049132 | <strong>A Condition Prohibited by Technical Specifications Because a Containment Isolation Valve Was Not Tested Adequately Due to an Inadequate Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On January 8, 1999, a system engineer discovered a test inadequacy during a review of completed re-tests for a previous event (see LER 1998-009-00). During a November 1998 forced outage, in order to address inadequate containment isolation valve (CIV) testing, special tests were prepared and performed to re-test specific CIVs, including "Recirculation Pump Discharge Sample Line Isolation" valve, SP-MOV-990A. The test required venting and draining of piping upstream of the valve, but a spring loaded check valve in the upstream piping prevented proper venting. Without proper venting, the differential pressure applied across the valve was not demonstrated for determining acceptable valve leakage in accordance with Technical Specification (TS) 4.4.E, "Containment Isolation Valves." The cause of the inadequate test procedure was that a system flow diagram failed to show a check valve that was spring loaded to 75 psi. As a result, in November 1998, personnel preparing and reviewing the test instructions failed to require proper venting of piping upstream of valve SP-MOV-990A. Corrective actions included satisfactory retesting to demonstrate operability, and an extent of condition review of other surveillance leak test procedures for the presence of other similar type check valves. The review concluded there were no other instances of inadequate testing. A request for drawing change will be issued to revise the applicable system flow diagram to note that valve SI-1820 is spring loaded to a high opening pressure, and a review will be performed to determine if other critical plant drawings need to be revised to indicate check valve characteristics associated with high opening pressures. The event had no effect on public health and safety because the valve was demonstrated to be operable.
2861999002 | Indian Point 3 | 01/22/1999 | 02/19/1999 | ML10049132 | <strong>Plant Outside Design Basis Due to Error in Original Design Allowing Single Failure to Cause Loss of Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 22, 1999, with reactor power at approximately 100 percent, NYPA notified the NRC that a design condition that had the potential to place the plant outside its design basis was confirmed to exist. operations declared the Vapor Containment Pressure Relief System inoperable. It was determined that considering a single failure of containment isolation valve VS-PCV-1190 to close upon demand, a potential containment release path (PS-SOV-1280) would exist. Use of the system was prohibited unless a one-hour Containment Integrity Limiting Condition of operation action statement was entered, with subsequent action to close a manual isolation valve in the Weld Channel and Containment Penetration System supply/containment atmosphere exhaust line. The most likely cause of the event is an oversight during the initial design phase of the plant when considering single failure. Corrective actions included applying administrative controls to manually isolate the exhaust port of Weld Channel and Containment Penetration Pressurization System (WCCPPS) valve PS-SOV-1280 during pressure reliefs and installation of a manual valve. This event had no actual effect on the health and safety of the public.
2861999003 | Indian Point 3 | 03/09/1999 | 07/02/1999 | ML10049133 | <strong>Automatic Reactor Trip Due to Flow Transmitter Low Flow Bistable Actuation on Reactor Coolant Loop 3 While Unisolating Another Transmitter as a Result of an Inadequate Work Package</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1999, an automatic reactor trip (RT) occurred after Instrumentation and Control personnel completed installation of a temporary modification (TM). The TM was installed downstream of the normally closed low pressure side blowdown line isolation valve for Reactor Coolant System (RCS) flow transmitter FT-436. FT-436 is one of three differential pressure transmitters on RCS loop 3. To implement the TM the transmitter's low pressure supply side isolation valve (ISV) was closed (and the bistable placed in trip) then opened to return the transmitter to service. Upon opening, a RT occurred and auxiliary feedwater actuated. The plant was stabilized in the hot shutdown condition. The direct cause of the RT was due to satisfying the reactor protection system (RPS) logic of two out of three RCS low flow in a single loop. The RPS logic was satisfied because the bistable for FT-436 was in the tripped condition and the bistable for FT-435 actuated due to a pressure oscillation in the common high pressure side transmitter sensing line. The oscillation, caused by unisolating FT-436, was sufficient to actuate (trip) the low flow bistable for FT-435. The root cause was inadequate planning and change management for the TM, due to a failure to assess the risks, consequences and system interactions associated with the TM. A contributing cause was the sensitivity of FT-435. Corrective actions included an inspection of like valves to confirm leak tightness, installation of a TM on FT-435, evaluation of the TM procedure for adequacy in addressing plant mode and system interactions, and a procedure revision to prevent work on RCS FTs above P-8. FT-435 and FT blowdown valves not previously replaced will be replaced, and an Operating Experience report was issued. The event had no effect on public health and safety.
2861999004 | Indian Point 3 | 04/21/1999 | 05/18/1999 | ML10049132 | <strong>Operation in a Condition Prohibited by Technical Specifications, Both Boric Acid Transfer Pumps Inoperable Due to No Allowed Outage Time Being Provided and Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 21, 1999, investigation of off-normal control room indicators revealed that the 32 Boric Acid Transfer Pump (BATP) was not running, and it was declared inoperable. During this time the 33 Emergency Diesel Generator (EDG) was inoperable as a result of corrective maintenance. Because the 33 EDG is the emergency power supply for the 31 BATP, it was also declared inoperable, resulting in two inoperable BATPs. Technical Specification (TS) 3.2.B.2 requires two BATPs to be operable, and has no allowed outage time for two inoperable BATPs. For Limiting Conditions for operation (LCO) where no exception time is specified, the plant is in a condition prohibited under TS 3. At 1422 hours, Operations entered TS 3, and began making preparations for plant shutdown and for returning the 32 BATP and EDG-33 to operable. The 33 EDG was made operable and returned to service and the 31 BATP made operable at 1610 hours. No load reductions were initiated. The 32 BATP was determined to have tripped as a result of undersized thermal overload heaters (O/L HTRs) for the pump motor; the O/L HTRs were installed during preventive maintenance of its motor control center feeder cubicle. The cause of the undersized O/L HTRs was personnel error due to poor work practices and inadequate written communication. The event was a result of TS 3.2 not specifying an allowed outage time. Corrective actions included replacing the 32 BATP O/L HTRs, reinforcing management’s expectations to engineering, and submittal of a TS change to the NRC that will allow correcting the lack of an allowed outage time. A review will be performed of the O/L HTR configuration control, sizing, re-testing, and extent of condition findings and corrective actions implemented as required. The event had no effect on public health and safety.
2861999005 | Indian Point 3 | 05/18/1999 | 06/03/1999 | ML10049132 | <strong>A Condition Prohibited by Technical Specifications, Incomplete Testing of Emergency Power Supply Tie-Breaker Interlocks due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1999, it was determined that in the past, both above cold shutdown and in cold shutdown, a Technical Specification (TS) surveillance requirement for emergency power system testing was not met. There was incomplete testing of the emergency power supply breaker closure permissive when the tie-breakers were placed in positions different than the tested configuration. When the tie-breaker is not in the connect/closed position a permissive is provided for the emergency power supply breakers to close upon a loss of offsite power. The permissive consists of a parallel set of contacts, one from the switchgear cell switch and one from the tie-breaker auxiliary switch. The permissive circuit contacts were tested in parallel, but were not tested individually. Currently, these tie-breakers are controlled in the test/open position, the same position as tested. Prior to 1992 or when the plant was the cold shutdown condition, the tie-breakers were placed in positions other than the tested position, in which only one of the two contacts provides the permissive. Since the contacts were not tested individually, a postulated high resistance contact failure could cause an undetected failure of the permissive. The cause of the event is cognitive personnel error in writing and revising the surveillance test. Prior to Generic Letter 96-01, the importance of testing both circuit paths of a parallel circuit was generically not understood. More recently, the error was a misunderstanding that the TS surveillance requirement did not need to be met for the cold shutdown condition. Corrective actions include controlling the configuration as tested until individual contact testing can be performed, disseminating information on the applicability of the surveillance in cold shutdown and reviewing for extent of condition. This event did not have a significant effect on the health and safety of the public because the risk was found to be acceptable upon review and actual plant experience has demonstrated the emergency power permissive circuit capability upon loss of offsite power.
2861999007 | Indian Point 3 | 06/16/1999 | 07/13/1999 | ML10049133 | <strong>Plant Outside Design Basis - The Control Room Ventilation System and Component Leakage Design Bases Are Not Met Due To Safety Injection System Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>At approximately 1857 hours on June 16, 1999, with the plant at about 99.5 percent power, NYPA notified the NRC that High Pressure Safety Injection System (HHSI) drain valve packing leakage placed the Control Room Ventilation System (CRVS) outside its system design basis (dose calculations assumed 0.7054 gallons per hour (gph) external recirculation system leakage . NYPA administrative controls for this assumption, 0.68 gph, account for measurement uncertainty. The valve leakage was approximately 0.083 gph which, when scaled to reflect operating pressure, raised total measured leakage to 0.751 gph. Corrective action reduced the leakage on the drain valve to 0.015.gph, when scaled for operating pressures, on June 17, 1999. This remained above the administrative limit. On June 18, 1999, the ENS was supplemented to report packing leakage from a HHSI System motor operated valve that raised total measured leakage to 0.689 gph. This is higher than the administrative limit. No equipment was declared inoperable because an existing operability determination demonstrates that the CRVS can perform its design function with leakage up to 2.0 gph. Corrective action is to repack the drain valve and either adjust or repack the motor operated valve. Leakage remains at about 0.689 gph. The cause was the normal wear of packing. There was no safety significance to the public health and safety.
2861999008 | Indian Point 3 | 07/22/1999 | 08/23/1999 | ML10049134 | <strong>Plant Outside Design Basis Due to an Error in an Assumption in the Main Steam Line Break Analysis</strong><br /><i>Abstract:&nbsp;</i>At approximately 1430 hours on July 22, 1999, with the plant at about 100 percent power, New York Power Authority (NYPA) made an Emergency Notification System notification to advise the Nuclear Regulatory Commission that the plant was outside design basis due to a non-conservative assumption for the main steam line break (MSLB) analysis. NYPA made the notification when informed by the Nuclear Steam Supply System (NSSS) vendor that a preliminary calculation showed that the containment design pressure would be exceeded for the MSLB unless there were changes to the design input assumptions that are part of the Indian Point 3 (IP3) licensing basis. The event was caused by failure to consider the unisolatable feedwater following the MSLB when the plant considered single failure of the main feedwater regulating valve in a 1983 analysis and considering too low a value for unisolatable feedwater in subsequent analyses. At IP3 there are 3,783 cubic feet of unisolatable feedwater piping for this case and subsequent analyses considered 800 cubic feet. The plant remained in operation because an operability determination demonstrated that, with changes to the design input assumptions, the peak calculated pressure would remain within the peak pressure currently identified on the docket. Corrective action includes performance of sampling to substantiate an assumption and performance of a safety evaluation to establish the design basis for upcoming fuel cycle based on more finalized analyses. An extent of condition review will be performed. There was no effect on the public health and safety.
2861999009 | Indian Point 3 | 07/27/1999 | 08/25/1999 | ML10049134 | <strong>A Condition Prohibited by Technical Specifications Because the Allowed Outage time was Exceeded for a Loss of Containment Integrity Caused by Personnel Error and Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1999, operations discovered that a modification, which installed a new Isolation Valve Seal Water System (IVSWS) test connection between two containment isolation valves (CIVs) (WD-AOV-1728 and WD-AOV-1723), was improperly installed and improperly returned to service. The installed configuration allowed a pathway from containment. This condition could have resulted in exceeding 10 CFR 100 and 10 CFR 50, Appendix A, GDC-19 dose limits under a Design Basis Accident and a single failure of CIV WD-AOV-1728 to close on demand. This condition existed for greater than the Technical Specification allowed outage time. The cause of the event was personnel error due to inattention to detail and an inadequate work control process regarding system restoration after performing work. Corrective actions included counseling appropriate personnel on management's expectations for attention to detail and the need to perform adequate error detection, revision of the work control (WC) process on requirements for a recovery plan, and an extent of condition review of work packages (WP). WPs for modifications and maintenance will be reviewed against the revised WC process prior to system restoration. A task analysis will be performed on the operations impact process and lesson learned implemented as required. The event had no actual significant effect on public health and safety. This event did not qualify as a safety system functional failure.
2861999010 | Indian Point 3 | 08/12/1999 | 09/09/1999 | ML10049134 | <strong>Automatic Reactor Trip Due to Low Low Level in Steam Generator 33 Caused by Equipment Failure Resulting in Loss of the 34 Instrument Bus</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1999, with the reactor at 100% power, an automatic reactor trip (RT) occurred. The RT occurred after a component failure of the 34 Static Inverter caused a loss of the 34 Instrument Bus (IB). With the loss of the 34 IB, a low low level occurred on the 33 Steam Generator (S/G). This low low level on 33 S/G was due to the plant's response to an IB failure. This satisfied the Reactor Protection System (RPS) logic of two out of three low low level signals on any one S/G causing the RT. The plant was stabilized in hot shutdown condition and the transient was terminated. Safe Shutdown systems responded as required. The cause of the 34 Instrument Bus (IB) failure was a failed power resistor in the 34 Static Inverter which prevented the Static Inverter from providing proper output to the IB. Significant corrective actions include performing a Failure Analysis on the failed power resistor, replacement of the failed power resistor and other Static Inverter components which failed as a result of the resistor, and evaluating the need for adding an Automatic Bus Transfer system to the 34 Static Inverter. This event qualifies as an unplanned reactor scram with the loss of normal heat removal, but was not a safety system functional failure in accordance with the guidelines of NEI 99-02. This event had no effect on the public health and safety.
2861999011 | Indian Point 3 | 09/16/1999 | 10/15/1999 | ML99306003 | <strong>Pressurizer Safety Valves Inoperable with the Reaactor Vessel Head On Without an equivalent Opening of One Valve Flange Established Due to Inadequate Communications; A Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1999, while in Cold shutdown (CSD) during preparations for refueling, the assistant operations manager discovered that the pressurizer safety valves (SV) had all but two of their bolts removed from their associated flanges prior to the reactor vessel head being removed. Technical Specification (TS) 3.l.A.2.a requires that at least one pressurizer code SV be operable or that there be an opening greater than or equal to the size of one code SV flange to allow for pressure relief, whenever the reactor head is on the vessel. The reactor vessel head was fully detensioned, but with some bolts of the pressurizer SVs removed the SVs were considered inoperable and an equivalent Opening was not available. The cause of the inoperable SVs was inadequate verbal communication due to misunderstanding. Maintenance requested from work control (WC) and believed they received permission to de-tension the SVs, but WC believed they only authorized removal of their whip restraints. Corrective actions include removal of one SV to establish the required reactor coolant system opening, and counseling appropriate personnel on management's expectations for attention to detail and the need to perform adequate communications. The procedure on Outage Management will be revised to ensure changes in work sequences require assessment for impact of TS requirements. The requirements of TS 3.l.A.2.a are to be relocated to the FSAR when the current TS are revised to the improved TS (ITS) which does not have this requirement in CSD. The event had no effect on public health and safety. This event was not considered a safety system functional failure in accordance with Nuclear Energy Institute guide line NEI 99-02.
2861999012 | Indian Point 3 | 09/30/1999 | 10/26/1999 | ML99308009 | <strong>A Common Condition Causing Multiple Core Exit Thermocouples to be Inoperable During Postulated Accident Conditions Due to Moisture Intrusion</strong><br /><i>Abstract:&nbsp;</i>On September 30, 1999 the unit was in cold shutdown due to a refueling outage and the core was off loaded to the spent fuel pool. It was determined that ten (10) CKB Industries safety-related core exit thermocouples would be inoperable during post accident conditions due to moisture intrusion. The exact time of the moisture intrusion condition for the thermocouples is unknown and may have occurred between the previous refueling outage and September 30, 1999. A meggar insulation resistance (IR) measurement on all Regulatory Guide 1.97 qualified thermocouples indicated that these ten thermocouples failed to meet the IR requirements. These ten (10) Regulatory Guide 1.97 thermocouples were replaced. The replacement core exit thermocouples are not manufactured by CKB Industries. This event had no effect on the health and safety of the public.
2861999013 | Indian Point 3 | 10/12/1999 | 11/09/1999 | ML99330003 | <strong>Automatic Actuation of an Emergency Diesel Generator as a Result of an Inadvertent Actuation of Safety Injection Relays Due to Personnel Error Caused by Poor Man-Machine Interface Design</strong><br /><i>Abstract:&nbsp;</i>On October 12, 1999, during a refueling outage, the 32 Emergency Diesel Generator (EDG) associated with bus 6A automatically started. EDG 32 started due to inadvertent actuation of Safety Injection (SI) relays, in the switchgear for bus 6A, during performance of blackout test 3PT-R003B. A technician performing the test was installing an electrical jumper in accordance with the test procedure when he inadvertently made up a nearby contact that actuated SI relays. The Engineered Safety Feature (ESF) equipment associated with bus 6A, including the 33 SI pump, had their electrical breakers racked into the test position for the test. Therefore, ESF equipment, including the 33 SI pump, did not start and no safety injection occurred. The EDG output breaker did not close onto bus 6A, per design, because normal (offsite) power was available. The event was due to personnel error caused by poor design (man-machine interface) in that the application of jumpers on field relays was required to fulfill the requirements of testing with relay terminal screws that are not specifically designed for the application of jumpers. Corrective action to be taken is to install relay test connectors on applicable relay terminals to facilitate surveillance testing. There was no effect on public health and safety.
2871999001 | Oconee 3 | 04/29/1999 | 06/01/1999 | 9906090037 | <strong>Control Room Cooling Inoperable Due to Valve Misalignment</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1999, all three Oconee Units were operating in Mode 1 at 100% power. At 1200 hours, Operators noticed that the Unit 3 Control Room (CR) area temperature was warmer than desired. The Chilled Water (WC) Makeup Tank was found empty and the make-up line isolation valves were closed, contrary to procedure. The valves were reopened and the WC system was refilled by 1500 hours. The Technical Specification (TS) limit of 80F was not exceeded. The WC system is shared with the Unit 1&2 CR, but the Unit 1&2 CR was not affected. On April 29, 1999, Engineering concluded that WC cooling coils of both trains of the Unit 3 CR air conditioning system were airbound and inoperable during the event. This would have placed the Unit in TS 3.0.3. An investigation concluded that the most probable root cause was inadequate self-verification by an operator who performed a valve checklist on January 17, 1999. Prior trending had identified a small leak, which allowed this system to partially drain while the makeup valves were closed. Corrective actions include revising the procedure to require a second check list to be run as a verification.
2871999002 | Oconee 3 | 12/15/1999 | 01/13/2000 | ML00367707 | <strong>Violation of Technical Specification 3.6.5 Due to Failure of Reactor Building Cooling Unit - With NOED</strong><br /><i>Abstract:&nbsp;</i>At approximately 18:30 on December 8, 1999, with Unit 3 in Mode 1 at approximately 100 percent power, Reactor Building Cooling Unit (RBCU) "B" was determined to be inoperable. At this time, Technical Specification (TS) 3.6.5, Required Action B.l was entered that requires, in part, the RBCU be restored to Operability within 7 days. The cause of the failure could not be determined in sufficient time to complete the repairs within the allowed out-of-service time. Since it was safer to complete the repairs without unit shutdown, a Notice of Enforcement Discretion (NOED) was requested and received from the NRC on December 15, 1999. Following RBCU repairs and testing, the RBCU was restored to Operability at approximately 17:27 on December 19, 1999, thereby exiting TS 3.6.5, Required Action B.l and the NOED. The root cause of the failure was determined to be procedural technical deficiencies that resulted in inadequate assembly of the RBCU propeller to the motor shaft when the motor was replaced in September 1997. The procedural deficiencies have been corrected. Additionally, preventive and/or predictive monitoring of the RBCUs will be enhanced. This event was of no significance to the health and safety of the public.
2891999001 | Three Mile Island 1 | 01/22/1999 | 02/19/1999 | 9903050397 | <strong>Boric Acid Mix Tank Piping Heat Trace Problems Caused by Misplacement of Sensing Elements and Insulation that Caused Short Sections of Piping to be Below the Temperatures Specified in FSAR Section 9.2.1.2</strong><br /><i>Abstract:&nbsp;</i>On 12/31/98 the NRC resident inspector reported to the control room that Boric Acid Injection Pumps CA-P-1A and CA-P-1B discharge piping temperature appeared to be low. On 1/2/99 Work Requests JO 161895 and 161896 were issued to verify heat trace set points. Subsequent to the completion of the measurement of the piping temperature, it was determined that a short section of the piping was below the required temperature as specified in FSAR 9.2.1.2. This condition was entered into the GPU Nuclear corrective action program on CAP T1999-0052 on 1/20/99. The root cause of this event was a failure to adhere to vendor instructions when the heat trace system was re-installed after a modification or corrective maintenance activity. The exact date of re- installation could not be determined. Three of the four temperature sensing elements were placed in contact with or near the heat trace wire. Additionally sections of the piping were missing pipe insulation. Routine testing and inspections are designed to ensure system function not design parameters. Post maintenance testing also failed to recognize the deficient condition. Periodic surveillance testing has demonstrated that this system remained fully capable of performing its design function at all times. Immediate corrective actions included the installation of additional insulation and relocation of the temperature sensing bulbs. Once the temperature sensing bulbs were relocated and additional insulation installed, the temperatures came back into specification. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2891999002 | Three Mile Island 1 | 02/12/1999 | 03/14/1999 | 9903260120 | <strong>Potential Failure of Multiple Containment Monitoring System (CM) Containment Isolation Valves (CM-V-, 1, 2, 3, and 4) due to Inappropriate Use of Vendor Information</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1999, after it was discovered that Containment Post Accident Sampling System (CATPASS) Containment Isolation Valves (CIVs) CM-V-1 and 3 exceeded Local Leak Rate Testing (LLRT) limits, it was determined that a condition existed that could have prevented the fulfillment of the safety function needed to control the release of radioactive material. The NRC was notified in accordance with 10CFR50.72(b)(2)(iii)(c). The root cause of this event was inappropriate use of vendor information in that a packing torque was taken from a vendor manual without the evaluation required by administrative procedures. Contributing to this event was lack of periodic maintenance (PM) for this component and inadequate post maintenance testing (PMT). CM-V1, 2, 3, and 4 were declared operable after repairs and leakage tests were completed. Additional repair work is planned for the next refueling outage. Personnel will be trained on management expectations regarding the vendor manual program; periodic maintenance for these valves will be developed; and PMT procedures will be revised. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2891999003 | Three Mile Island 1 | 03/10/1999 | 10/29/1999 | ML99314021 | <strong>Discovery of a Condition Outside the UFSAR Design Basis for Control Room Habitability</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1999, the failure of a manual balancing damper in the supply duct of the Control Building Emergency Ventilation System (CBEVS) led GPU Nuclear (GPUN) Inc. to discover a condition which was outside UFSAR design basis. When the manual damper failed (in the closed position), a negative pressure was experienced in the Control Room (CR). The inability to meet the positive pressure requirement of the UFSAR design basis description is reportable in accordance with 10 CFR 50.73(a)(ii)(B). The TMI-l UFSAR Section 7.4.5.2.1 states: "The main Control Room (CBE [Control Building Envelope] Elevation 355'-0") is a leak tight room maintained at a positive pressure of 0.10 inches w.g. by the CBEVS in the Emergency Recirculation mode of operation with or without single failure of Outside Air Intake Damper (OAI) AH-D-39, Exhaust Damper AH-D-37 and Damper AII-D-28." This failure of the manual damper simulated the potential single failure of AII-D-39 (an active damper 2 ft, downstream of the manual damper). The Technical Specification 3.15.1 required CR Emergency Air Treatment System remained operable on the basis that recirculation filters and fans were not affected by this equipment failure. The CBEVS Normal and Abnormal Operating Procedures for initiation of emergency recirculation were changed in late 1985 to address a postulated failure of the isolation damper AH-D-28 and resultant negative pressures in the CBE. The procedure change established a new configuration which was not fully analyzed, tested, or reviewed for the potential creation of new single active failures; as a result, the single active failure of AH-D-39 was not recognized at that time. The root cause of the nonconformance with the UFSAR design basis was that the "Risk and Consequences of a Change were not Adequately Reviewed or Assessed" when the configuration change was implemented by procedure revision. The cause and corrective actions of the failed manual air-balancing damper, which led to the discovery of the nonconforming condition, are included in this report. The failed damper was clamped open and normal outside airflow was restored to the Control Building shortly after discovery. This event did not involve any additional equipment failures or damage, nor were there any personal injuries as a result of this event. There were no adverse safety consequences resulting front this event, and the event did not affect the health and safety of the public.
2891999004 | Three Mile Island 1 | 05/10/1999 | 06/09/1999 | 9906160042 | <strong>Emergency Feedwater Pump Inoperable Longer Than Allowed by Technical Specifications Due to Lack of Lubrication Caused by a Loose Set Screw Resulting in Bearing Failure</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1999, GPU Nuclear (GPUN) Inc. discovered a failed pump bearing during the performance of an oil change on the motor-driven Emergency Feedwater (EFW) Pump (EF-P-2B). Following this discovery, other pump bearings were checked on this component as well as the remaining motor-driven and steam-driven EFW pumps, with no significant deficiencies identified. There have been no previous events of a similar nature. There were no personnel injuries or additional equipment damage as a result of the event. The root cause of the bearing failure was determined to be an uncorrected equipment problem. A set screw, securing the oil thrower to the pump shaft is believed to have been inadequately tightened and became loose, reducing the bearing oil circulation rate and resulting in ineffective heat removal from the bearing and bearing failure. The pump was repaired and returned to service on May 12, 1999. Since it was likely that the pump had been inoperable longer than allowed by the technical specifications, the event was determined to be reportable as a condition prohibited by the Technical Specifications pursuant to 10 CFR 50.73(a)(2)(i)(B). GPU Nuclear concluded that this was an isolated event and the remaining EFW pumps were not degraded.
2891999005 | Three Mile Island 1 | 05/14/1999 | 06/14/1999 | 9906180109 | <strong>Open Flood Path Between Turbine Building and Control Building</strong><br /><i>Abstract:&nbsp;</i>On 5/13/99 engineering was evaluating whether or not adequate periodic surveillance was being performed on all flood protection provisions. Specifically, the accessibility of the backwater check valve in the Turbine Building Corrosive Waste Sump was being investigated. The investigation found that two modifications made in 1983 and 1990 to the Secondary Sample Lab Drain System added drains without adequately considering flood protection concerns. In the event of Probable Maximum Flood the installation of these drains could introduce water into the Control/Fuel Handling and Auxiliary buildings. As a result of the inadequate review of the modifications, the Flood Procedure (1202-32) did not address related operator actions, such as plugging the lines in the event of a flood. The root cause of the failure to recognize that the modifications affected the flood protection required by the FSAR was a misapplication or interpretation of design inputs (Risk and consequences with changes not adequately reviewed or assessed) [Code C10Cd]. Immediate corrective actions were to revise the flood procedures to require operators to plug the related Turbine Building floor drains and sump nozzle in the event of a flood. Also an engineering evaluation was initiated to provide guidance for repairing the inoperative corrosive waste sump backwater check valve and for plugging of the floor drains that have no function during normal operation. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2891999007 | Three Mile Island 1 | 05/28/1999 | 08/20/1999 | 9909020104 | <strong>Voluntary LER Regarding Increasing Failure Rate of ESAS Relays</strong><br /><i>Abstract:&nbsp;</i>TMI-1 has seen a decrease in the reliability of Clark type PM relays used in the Engineered Safeguards Actuation System (ESAS). Clark type PM relays are commercial grade industrial relays that are dedicated for use in safety related systems by GPU Nuclear. Recent failures have highlighted the recurring problem characterized by coil overheating and failure to fully re-close after being de-energized. It has been decided to voluntarily notify the NRC of previously unrecognized age and wear related problems with these components. The root cause of these failures has been determined to be inadequate preventative maintenance in that the frictional buildup from the gradual wear of moving parts and loosening of screws went uncorrected. This condition caused the moving components of the contact and actuator sections of the relay to occasionally bind while re-positioning to an energized state. A long-term plan that addresses both the need to replace degraded relays as well as enhanced maintenance activities to improve relay performance has been established. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2891999008 | Three Mile Island 1 | 06/04/1999 | 11/22/1999 | ML99335011 | <strong>Reactor Building Emergency Cooling System (RBECS) Outside the Design Basis with Reduced Air Flow Due to Inadequate Consideration of the Potential for Reactor Coolant Leakage to Impact RBECS Performance</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1999 during full power operation of TMI-1, GPU Nuclear discovered that the air flow through each of the Reactor Building (RB) fan cooler units was below design basis requirements. TMI-I has three fan cooler units to cool the RB during normal and emergency conditions. The fan coolers were determined to be operable but degraded due to accumulation of boric acid crystals on the external surfaces of the normal cooling coils of all three (3) units and on the fan blades of the "A" fan cooler unit. This condition was determined to be reportable in accordance with 10CFR50(a)(2)(ii) as a condition outside the design basis of the plant. The Root Cause of the failure of the RBECS to meet UFSAR design flows was the inadequate consideration of the potential for reactor coolant leakage to adversely impact the RBECS coupled with the lack of permanently installed instrumentation. Public health and safety were unaffected. Calculations completed in September 1999 demonstrate that the air flow which could have been provided at the cooling coils inlet of the most degraded fan unit during a design basis event, prior to cleaning, would have exceeded the minimum requirement. The fan cooler units have been restored by cleaning. Other actions including installation of additional instrumentation and initiation of a long term monitoring program have been completed.
2891999009 | Three Mile Island 1 | 06/26/1999 | 07/22/1999 | 9907300023 | <strong>Automatic Start of Emergency Diesel Generator 1A Due to Failure of a Fault Pressure Relay on Auxiilary Transformer 1B</strong><br /><i>Abstract:&nbsp;</i>On June 26, 1999 at approximately 10:09, the 1B auxiliary transformer (230 kV to 6900 V & 4160 V) tripped while supplying in-plant loads. The plant was operating at 100% power at the time of this spurious trip and remained at full power during and following the event transient. Following the loss of the 1B auxiliary transformer, non-Class 1E loads transferred to the 1A auxiliary transformer and Class 1E loads transferred to the 1A emergency diesel generator which had automatically started in response to the event. The cause of the spurious 1B auxiliary transformer trip was the failure of a fault pressure relay which senses transformer casing pressure changes. Based on initial examination of the failed component and vendor comments, the pressure relay is thought to have reached the end of its reliable service life. The root cause of the failure of the pressure relay is expected to be determined during inspection at the vendor's laboratory. The failed pressure relay has been replaced and long term corrective actions will include replacement of the pressure relays on both auxiliary transformers. These actions will be completed during the next plant refueling outage. The event was reported pursuant to 10 CFR 50.72(b)(2)(ii) at 1344 on June 26, 1999.
2891999010 | Three Mile Island 1 | 08/30/1999 | 09/21/1999 | 9909280124 | <strong>Discovery of a Condition outside the UFSAR Design Basis for Flood Protection</strong><br /><i>Abstract:&nbsp;</i>On 09/30/99, a potential non-conforming condition was identified. Drain lines were identified as possibly connecting a non-flood protected area of the Intermediate Building (IB) to a flood protected area, the Fuel Handling Building (FHB). On 08/31/99, this condition was confirmed and determined to be a reportable event. This problem was identified during the performance of a comprehensive review of the site flood protected structures as part of the corrective actions developed in response to a previous similar event. This problem of non-flood protected area drains connecting a flood-protected area was the result of inadequate design changes dating back to original construction prior to 1974 commercial operation. During plant construction, designers failed to adequately implement design changes to address changes to the UFSAR design basis flood protection requirements. Cause: "Original problem not corrected by the design change". Since initial operation, there has not been any flood that approached the elevation of this equipment. Therefore, no equipment damage or personnel injuries resulted from this event. Corrective actions will include actions to address the individual drains as well as to complete the verification activities developed to assure that all site structures, systems, and components relied upon to provide FSAR flood protection are in a fully functional condition.
2891999011 | Three Mile Island 1 | 09/11/1999 | 04/18/2001 | ML01114018 | <strong>Voluntary LER: "Incomplete Control Rod Insertion During Trip Insertion Time Testing"</strong><br /><i>Abstract:&nbsp;</i>On September 11, 1999 TM1 Unit 1, then owned by GPU Inc. now owned and operated by AmerGen Energy Co. L.L.C. (AmerGen), conducted an elective post-shutdown Control Rod Trip Insertion test on the Control Rod Drive System in support of Maintenance Rule (a)(1) monitoring. Sixty of 61 control rods inserted to the Technical Specification 4.7.1.1 required 3/4 insertion position within the 1.66 second time requirement, while one rod did not. One control rod stopped at 26% withdrawn and it was declared inoperable. Technical Specification 3.5.2.2 allows for one inoperable control rod to remain completely out of the core. One additional control rod stopped at approximately 7% withdrawn; however, this control rod did meet the Technical Specification insertion position and time requirements. Additionally all remaining control rods inserted fully into the reactor core. There were no violations of Technical Specification requirements or Safety Analyses during this event and the original LER was submitted voluntarily to the NRC on October 21, 1999. The direct cause of the incomplete control rod insertion was determined to be fuel assembly guide tube distortion, which resulted in excessive mechanical drag. Contributing factors were core location and shuffle history of the affected assemblies and hold down spring force. The Technical Specification required trip insertion time testing was performed prior to Cycle 13 startup, during which velocity profiles on selected rods were obtained, and no abnormal drag was found to be present. The two fuel assemblies where incomplete rod insertion occurred were discharged from the core. Additionally, TMI-1 redesigned the Cycle 13 core loading pattern and relaxed the pre-load forces in the hold down springs on specific fuel assemblies. Long term corrective actions were developed through the fuel vendor. It should be noted that there had been no prior instances at TMI of a control rod failing to fully insert when the Control Rod Drive Mechanism (CRDM) was de-energized. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public .
2891999012 | Three Mile Island 1 | 10/19/1999 | 11/17/1999 | ML99331010 | <strong>Main Steam Isolation Valve, MS-V-1B, Valve Operator Motor Failure due to the Manufacturing Process</strong><br /><i>Abstract:&nbsp;</i>During a plant startup on October 19, 1999 Main Steam Isolation Valve (MSIV) MS-V-1B failed to open completely and the valve operator motor was found to be inoperable. With no Technical Specification (T.S.) operability requirements or allowable outage time (AOT) guidance specified, MS-V-1B was opened manually and plant startup was resumed. The following day on October 20, 1999, the Plant Review Group (PRG) concluded that operation without remote closure capability for MS-V-1B was reportable in accordance with 10 CFR 50.72(b)(1)(ii)(B), as a condition outside of the design basis. The motor was replaced on October 25, 1999. The root cause of the motor failure was insulation breakdown in the stator windings due to a lack of end turn bracing during the manufacturing process. The root cause of the incorrect reportability determination was over-reliance on individual knowledge. Planned actions include a review to determine if other safety significant motor operated valves (MOVs) are affected, communication of the lessons learned from this event, and providing additional guidance. Public health and safety were unaffected. MSIV closure is not credited in the accident analyses, except for the stop-check function, which was unaffected throughout this event. Based on a Probabilistic Risk Assessment (PRA) evaluation, the safety significance of this event was low.
2891999013 | Three Mile Island 1 | 12/01/1999 | 12/28/1999 | ML00367112 | <strong>Improperly Made-up Electrical Connection on a Control Rod Drive Breaker Test Switch</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1999 a deficient condition regarding an improperly made-up electrical connection was identified. A technician troubleshooting anomalies experienced during the performance of Surveillance Procedure 1303-4.2B "RPS Chan B CRD Breaker Logic Test" found an incorrectly attached lug on control rod drive breaker, CB-11 test switch C2 . A panel indication light for "SHUNT TRIP PWR" did not return to the "ON" state and an annunciator light for "CRDM Breaker Test Trouble" that was expected to clear did not. Upon identification, the improperly made-up jumper connection was remade and the surveillance was satisfactorily completed. The deficient condition was documented by an entry into the Corrective Action Process: form number T1999-1202. An evaluation by GPU Nuclear identified that the specific cause of this event was the failure of the I&C technician assigned the task to correctly make-up the connection as part of a plant modification. Individuals assigned independent verification tasks also failed to identify the incorrectly connected lug. The long term corrective actions to reduce the probability of similar occurrences in the future involve a review of the lessons learned from this and similar events with Electrical and I&C maintenance and Quality Verification personnel during cyclic and position specific training. The deficient condition is being reported per 10 CFR 50.73(a)(2)(i)(B).
2931999001 | Pilgrim | 04/12/1999 | 05/06/1999 | 9905170170 | <strong>Environmental Enclosures of MCCs Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1999, the pressure relieving devices that are part of the environmental enclosures for three safety related motor control centers were found to be obstructed or retarded from opening. The devices function to automatically open if an internal pressure of 0.5 psi occurs as a result of a design basis tornado. The environmental enclosures were installed (c. 1984) as part of actions required for environmental qualification of electric equipment important to safety (10 CFR 50.49). The most probable cause was a failure to translate the design function of the pressure relieving devices into a procedure to test, inspect, or check the opening function of the devices. Corrective action taken consisted of removing the obstructions on the affected environmental enclosures. The action was completed on April 12, 1999. The environmental enclosures of other motor control centers were inspected with satisfactory results. Corrective action planned includes revision of the procedure used for maintenance of motor control center enclosures to include a test, inspection, or check of the opening function of the pressure relieving devices of the environmental enclosures. The condition was discovered during power operation while at 80 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1030 psig with the reactor vessel water temperature at the saturation temperature for that pressure. The condition posed no threat to public health and safety.
2931999002 | Pilgrim | 05/04/1999 | 06/03/1999 | 9910150171 | <strong>HPCI and RCIC Systems Surveillance Testing Outside Design Bases due to Incorrect Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 4, 1999, it was identified that the Technical Specifications upper pressure (1000 psig) for the high pressure coolant injection (HPCI) and reactor core isolation cooling (RCIC) systems is less than the setpoint (1126 psig) of the main steam relief valves including tolerance, and as such, a condition representing operation outside the design basis. The upper pressure of 1000 psig was specified in the original Technical Specifications for the HPCI and RCIC systems and has remained unchanged since the Technical Specifications were originally issued (in 1972). The cause of the original HPCI and RCIC Technical Specifications not identifying the correct pressure could not be determined. Corrective action taken included the submittal of proposed changes to the HPCI and RCIC Technical Specifications that change the pressure from 1000 psig to 1126 psig. Corrective action planned includes the performance of a design basis calculation(s) for the HPCI and RCIC pumps' pressure (and flows) necessary to meet the proposed Technical Specifications. The condition was identified during power operation while at 80 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1032 psig with the reactor water temperature at the saturation temperature for that pressure. The condition posed no threat to public health and safety.
2931999003 | Pilgrim | 05/16/1999 | 02/27/2002 | ML02077006 | <strong>Local Leak Rate Test Results Exceeding Allowable Technical Specification Leakage Rates</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1999, the Control Room was informed that the containment isolation valves for the 'C' main steam line exceeded the Technical Specifications (T.5.) allowable leakage rates during Appendix Local Leak Rate Testing that was being performed during the 1999 Refueling Outage (RFO 12). The in-series main steam line 'C' isolation valves were found to have leakage of 280 standard liters per minute (SLM) and 255 SLM. The test failure of the inboard valve (AO 203-1C) was caused by minor imperfections in the seating surface due to normal age related wear. The test failure of the outboard valve (AO 203-2C) was caused by flow induced vibration that caused wear on the main disk and pilot poppet seating surfaces. Bath valves were refurbished and successfully leak rate tested before being returned to service in RFO 12. On May 24, 1999, a globe stop-check valve in the Reactor Core Isolation Cooling System turbine exhaust piping did not meet the leakage acceptance criteria during the performance of Appendix J testing. Valve disassembly revealed that a portion of the resilient seat ring was missing. The seat ring was replaced and the valve was successfully leak rate tested before being returned to service in RFO 12. The conditions were discovered during reactor refueling operations with the reactor mode selector switch in the REFUEL position. The reactor vessel pressure was zero prig and reactor coolant temperature was 84° Fahrenheit. The condition posed no threat to public health and safety.
2931999004 | Pilgrim | 05/29/1999 | 10/19/2001 | ML01302042 | <strong>Setpoint of Target Rock Relief Valves Found Out of Tolerance Due to Stellite Oxidation and Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On May 29, 1999, it was identified that the initial as-found popping pressure of the pilot assemblies that were previously installed in three of the four Target Rock two-stage main steam relief valves exceeded Technical Specification 3.6.D.1. The pressures occurred during routine testing at a test facility. The cause of the out of tolerance popping pressure of one of the pilot assemblies was attributed to setpoint drift. The cause of the out of tolerance popping pressures of the other two pilot assemblies was not identified when LER 99-004-00 was prepared, but is now believed to be Stellite oxidation . This supplement to LER 99-004-00 reflects findings made after the pilot assemblies had been disassembled for inspection, reworked, and reassembled. Following the rework, the assemblies were tested for certification by test facility personnel. The pilot assemblies removed for testing were replaced with certified spare pilot assemblies during the refueling outage. The as-found popping pressures occurred during testing of the pilot assemblies while shut down for the 1999 refueling outage. The as-found popping pressures posed no threat to public health and safety.
2931999005 | Pilgrim | 06/08/1999 | 07/08/1999 | 9907140164 | <strong>Partial Actuation of RHR/LPCI Circuitry During Surveillance Test Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1999, at 1740 hours, a partial actuation of the Residual Heat Removal (RHR) System Low Pressure Coolant Injection circuitry occurred while the RHR channel 'A' circuitry was being surveillance tested for the trip function of the Recirculation System MG set 'B' drive motor breaker. The cause of the event was utility non-licensed personnel error in that the circuitry was not reset before backing out of the surveillance procedure because of an error in the procedure. The procedure identified the wrong contacts of an RHR channel 'A' relay that were to be booted for the test. Corrective action taken included revision of the procedure to correct the procedure error. The event occurred while shut down during the 1999 refueling outage. The reactor mode selector switch was in the REFUEL position. The reactor vessel head was installed and the reactor water level was approximately +40 inches (narrow range level). The reactor water temperature was approximately 105 degrees Fahrenheit. The event posed no threat to public health and safety.
2931999006 | Pilgrim | 07/05/1999 | 08/04/1999 | 9908100256 | <strong>Both Emergency Diesel Generators Inoperable Due to Ambient Air Temperature Exceeding 88 Degrees Fahrenheit</strong><br /><i>Abstract:&nbsp;</i>On July 5, 1999, both emergency diesel generators (EDG) were declared inoperable because the site ambient outside air temperature was greater than the EDG design and operability limit of 88 degrees Fahrenheit. An engineering evaluation concluded the EDGs would be operable up to a maximum temperature of 95 degrees if temporary modifications to the EDG control cabinets and radiators were implemented. The temporary modifications were implemented for EDG 'A' on July 5, 1999. On July 6, 1999, EDG 'B' was inoperable because the air temperature was greater than 88 degrees and the temporary modifications for EDG 'B' had not yet been implemented at that time. The cause was inadequate EDG cooling and building ventilation design to support EDG operability when site ambient air temperature exceeded 88 degrees. Corrective actions planned include the implementation of permanent modification options to extend the operability of the EDGs to greater than 88 degrees Fahrenheit. The events occurred during a plant startup while at about 22 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was 950 psig with the reactor water temperature at the saturation temperature for that pressure. The event posed no threat to public health and safety.
2931999007 | Pilgrim | 07/16/1999 | 08/13/1999 | 9908200194 | <strong>Bus B6 Voltage Restoration Not Consistent with Safety Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1999, engineering personnel were reviewing the operating characteristics of a design change and discovered a potential failure mode that could result in 480V swing bus B6 remaining deenergized following a loss of coolant accident coincident with degraded grid voltage. Due to the circuit design change, the B6 supply breaker charging springs may not be fully precharged when signaled to close, thereby leaving bus B6 deenergized. An engineering evaluation determined that the guidance contained in procedures is sufficient to ensure that safety-related components will operate within their design limits during a degraded voltage condition. The cause was personnel error during the development of the design change. During the design process all possible scenarios were not considered for impact. Corrective action taken consisted of an extent review which determined that this potential failure mode is limited to only the bus B6 transfer scheme. No other breakers at Pilgrim Station are subject to this potential failure mode. Corrective action planned is to evaluate the need for any modifications to correct the problem. The condition was discovered on July 16,1999. The reactor mode selector switch was in the RUN position. The reactor vessel pressure was approximately 1034 psig with the reactor water temperature at the saturation temperature for that pressure. The event posed no threat to public health and safety.
2931999008 | Pilgrim | 08/05/1999 | 06/08/2004 | ML04167061 | <strong>Automatic Scram at 100 Percent Power Due to Automatic Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On August 5, 1999, an automatic scram occurred while at 100 percent power. The scram resulted from a turbine trip initiated by a high water level in turbine steam moisture separator tank 'A'. Automatic responses included the brief opening of the main steam relief valves for pressure relief. The cause of the trip was a malfunction of moisture separator drain tank 'A' drain valve controller and incorrect setting of the drain tank's dump valve controller. The root cause determined that a lack of knowledge in understanding how this type of moisture separator level controller operated existed in the Engineering and Maintenance disciplines. This lack of knowledge led to inappropriate changes to the associated calibration procedure and improper field adjustments to the controllers themselves resulting in the high water level condition. Corrective actions taken prior to plant restart included replacement and calibration of the level controllers. Corrective actions taken after plant restart included additional training for the Instrumentation & Calibration Technicians and Engineering Support Personnel and revision to plant procedures dealing with the calibration of controllers. The event posed no threat to public health and safety.
2931999009 | Pilgrim | 09/13/1999 | 10/13/1999 | 9910180149 | <strong>Manual Scram at 27 Percent Power Due to Degrading Main Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On September 13, 1999, at 1825 hours, an unplanned scram was manually initiated while at 27 percent reactor power. This action was taken because of degrading vacuum in the main condenser. The root cause of the event was the failure of the augmented offgas (AOG) system train 'B' condenser level control system in conjunction with AOG air purge flow, that overcame the capacity of the main condenser air ejector system. The AOG system bypass procedure requires the air purge. Corrective actions taken included the cleaning of a plugged level control sensing line, replacement of a level control instrument root valve and level transmitter, and loop calibrations of the AOG train 'B' condenser level control system. Other corrective actions are planned. The event occurred during power operation while at about 27 percent reactor power. The reactor vessel pressure was about 952 psig with the reactor vessel water temperature at the saturation temperature for that pressure. The event posed no threat to public health and safety.
2931999010 | Pilgrim | 09/18/1999 | 10/18/1999 | 9910210269 | <strong>HPCI and RCIC Systems Isolation Not Reset During Startup and Subsequent RCIC Isolation Due to High Steam Flow Signal</strong><br /><i>Abstract:&nbsp;</i>On September 18, 1999, a reactor startup was in progress. The High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems are required to be operable when reactor pressure exceeds 150 psig. Contrary to this requirement, the low reactor pressure isolation signals to both systems were reset after reactor pressure exceeded 150 psig. Failure to reset these signals caused both systems to be inoperable. The HPCI and RCIC isolations were reset and while the RCIC system was being placed in normal standby service, a high steam flow isolation signal occurred. The failure to reset HPCI and RCIC was caused by a communications breakdown that resulted in operations personnel failing to complete actions in accordance with station procedures. The high steam flow isolation signal was caused by an operator opening a RCIC turbine steam supply isolation valve too quickly. Corrective action includes licensed operator training. The events occurred during plant startup with the reactor mode selector switch in the STARTUP position. The reactor power level was about 1 percent. The reactor vessel pressure was less than 167 psig with reactor water at the saturation temperature for that pressure. The events posed no threat to public health and safety.
2931999011 | Pilgrim | 09/22/1999 | 10/25/1999 | ML99309010 | <strong>Postulated Fire in Cable Spreading Room Potentially Affecting Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1999, a Condition outside the design basis was identified. Specifically, a postulated fire in the cable spreading room (CSR) could potentially affect the alternate shutdown panel of an emergency diesel generator (EDG) and hence, the ability of one (or both) EDQ(s) to sufficiently power AC powered electrical loads necessary to achieve or maintain safe shutdown. The postulated fire could limit EDG electrical output because EDG watt-meter cabling in the CSR was not protected as part of 10 CFR 50 Appendix R modifications. The preliminary root cause analysis could not determine the exact cause. The original design of the alternate shutdown panels was developed in the 1978-1979 time frame and additional modifications were added in the 1986-1987 time frame. Fire watches for the potentially affected alternate shutdown panels were established in accordance with Technical Specification 3.12. The operability of the EDGs is not affected. This report will be supplemented after the root cause analysis is completed. Corrective action being evaluated includes revision of a procedure for a shutdown outside of the control room. The condition was identified during power operation while at 100 percent reactor power. The reactor vessel pressure was about 1034 psig with the reactor vessel water temperature at the saturation temperature for that pressure. The condition posed and poses no threat to public health and safety.
2961999001 | Browns Ferry 3 | 01/14/1999 | 02/12/1999 | 9902250072 | <strong>Unit 3 HIgh Pressure Coolant Injection Inoperable As A Result of An Oil Leak on the Stop Valve</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1999, at 1640 hours CST, during routine surveillance testing, the Unit 3 High Pressure Coolant Injection (HPCI) [BJ] system was declared inoperable as a result of an oil leak on the HPCI turbine inlet stop valve. As required by Technical Specifications, Browns Ferry entered a fourteen day Limiting Condition for Operation for an inoperable HPCI system. Following corrective maintenance and subsequent surveillance testing, the HPCI system was returned to an operable status at 1907 hours on January 15, 1999. The oil leak was attributed to an overload failure of one of the four stud bolts which attach the pilot relay valve to the stop valve (Model J53) cylinder supplied by Schutte and Koerting. The failed stud bolt was subsequently determined to be fabricated from improper material in the original installation. Corrective actions included replacing the stud bolts on the Unit 3 HPCI system stop valve with ASTM A193 Grade B7 which has a higher strength and ductility than the original bolts. TVA plans to replace the stud bolts on the Unit 2 HPCI system stop valve as soon as practicable. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that alone could have prevented the fulfillment of the safety function of a structure or system needed to mitigate the consequences of an accident.
2961999002 | Browns Ferry 3 | 01/22/1999 | 02/19/1999 | 9903020320 | <strong>LCO Not Entered During Calibration Testing Of 3D 480 Volt RMOV Board</strong><br /><i>Abstract:&nbsp;</i>On January 4, 1999, a relay calibration on 3D 480 volt Reactor Motor Operated Valve (RMOV) Board was performed which disabled the auto-transfer logic of the board. The plant's Technical Specifications (TS) Bases state that the 3D and 3E 480 volt RMOV Boards are to be considered inoperable if the auto-transfer capability between the normal and alternate power supply for these boards is inoperable for any reason. TS 3.8.7 Required Action C.1 requires that the respective Residual Heat Removal (RHR) subsystem supported by the board must be declared inoperable for Low Pressure Coolant Injection (LPCI) immediately. However, the appropriate LCO had not been entered and TS 3.8.7 Required Action C.1 had not been satisfied by declaring the affected RHR subsystem immediately inoperable. This condition was discovered on January 22, 1999, when Operations personnel conducted a review of past performances of this calibration procedure and determined that on January 4, 1999, the proper LCO had not been entered. The root cause of this event was personnel (utility-licensed operator) error resulting from failure to recognize the LCO condition. TVA has briefed Operations personnel to preclude recurrence of this event. This report is submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant's TS.
2961999003 | Browns Ferry 3 | 04/08/1999 | 05/06/1999 | 9905140178 | <strong>Unit 3 High Pressure Coolant Injection (HPCI) system Inoperable Due to Loose Wire</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1999, at approximately 2045 hours Central Daylight Time (CDT) during the performance of a regularly scheduled Instrumentation surveillance on the Unit 3 HPCI Steam Line Space High Temperature switches, a loose wire was found in the power supply pathway for the HPCI logic circuit. This loose wire had the potential to prevent adequate voltage from being supplied to the initiation and isolation logic for the Unit 3 HPCI system. The loose wire was tightened. The potential for inadequate voltage being available for the HPCI logic circuit resulted in the decision to declare the HPCI system inoperable. The most likely cause of this event was determined to be a failure to properly tighten the screw at some time in the past. This report is submitted pursuant to 10 CFR 50.73 (a)(2)(v) as a condition that alone could have prevented the fulfillment of the safety function of a structure or system needed to mitigate the consequences of an accident.
2961999004 | Browns Ferry 3 | 06/25/1999 | 07/26/1999 | 9908030241 | <strong>Inoperability of Two Divisions of the Unit 3 Core Spray System Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1999, at 1352 hours Central Daylight Time (CDT), Unit 3 Core Spray (CS) Divisions I and II were technically inoperable at the same time. This condition was the result of personnel error during performance of the surveillance test, Backup Control Panel Testing [3-SR-3.3.3.2.1(75 I)] for CS Division I. During performance of the surveillance test, the electrical supply breaker for CS Division II pump 3B was racked out instead of the breaker for CS Division I pump 3C as required by the surveillance test. Prior to the event, CS Division I pump 3A had been made inoperable per the surveillance test. This action had made CS Division I inoperable. At the time of the event, pump 3A had been returned to a condition where it was available (and hence CS Division I was available), and would have functioned if required. However, CS Division I was still inoperable per plant Technical Specifications. The operations' staff recognized that two divisions of CS were inoperable and appropriately entered LCO 3.0.3. At 1418 hours CDT, CS Division II was returned to operable status and LCO 3.0.3 exited. The root cause of this event was personnel error. Prior to, and during the event, all other Emergency Core Cooling Systems (ECCS) were operable. Accordingly, there was no significant reduction in the degree of protection provided to the public health and safety. Furthermore, the safety of the plant, its personnel, and the public was not compromised. This report is submitted pursuant to 10 CFR 50.73 (a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications.
2961999005 | Browns Ferry 3 | 09/01/1999 | 09/30/1999 | 9910080129 | <strong>Surveillance Requirement For Standby Liquid Control Sampling Was Not Met</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1999, plant personnel discovered that Surveillance Requirement (SR) 3-SR-3.1.7.9 had not been performed within the required 24-hour period following a chemical addition made to the Standby Liquid Control (SLC) tank on August 9, 1999. The SR requires that the sodium pentaborate enrichment is within the established limits after addition of boron to the SLC tank in order to ensure the proper boron atom percentage is being used. The sodium pentaborate enrichment must be calculated within 24 hours and verified by analysis within 30 days. Upon discovery of the missed surveillance, the required surveillance was initiated and the sample was shipped to the contract lab to verify the analysis. The analysis verified that the established limits were being met. The root cause of the event was a deficient procedure for chemical addition to the SLC tank. The procedure will be revised to require the conditional surveillance. There were no actual or potential safety consequences as a result of this event nor did this event adversely affect the safety of plant personnel or the public. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2981999001 | Cooper Station | 02/22/1999 | 03/22/1999 | 9903310047 | <strong>Failure to Recognize Set Point Shift Causes Common Mode Failure of High Pressure Coolant Injection Pressure Switches</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1999, during the performance of the Division II functional surveillance test for High Pressure Coolant Injection (HPCI) (EIIS:BJ) Steam Line Low Pressure switches (EIIS:PS), HPCI-PS-68B and -68D were found out of allowable calibration range and below the Technical Specification (TS) allowable value. The instruments were recalibrated and returned to service. During the subsequent performance of the Division I functional/calibration test, HPCI-PS-68C was also found to be out of allowable calibration range and below the TS allowable value. Action was taken to increase the frequency of the functional/calibration testing to ensure set point accuracy is maintained. On February 22, 1999, during an evaluation of the performance of the pressure switches with the increased surveillance frequency, it was recognized that these failures were due to a single condition. This common mode failure is reportable under the requirements of 10CFR50.73(a)(2)(vii) as an event where a single cause or condition caused two independent trains or channels in a single system designed to control the release of radioactive material to become inoperable.
2981999002 | Cooper Station | 04/06/1999 | 05/05/1999 | 9905120197 | <strong>Failure to Response Time Test all Reactor Protection System Relays Results in Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1999 it was determined that four of eight Reactor Protection System (RPS)(EIIS: IBA) SCRAM relays (5A-14E, 5A-14G, 5A-14H, and 5A-14F)(EIIS: RLY) were not being response time tested as required by Technical Specification (TS) Surveillance Requirement 3.3.1.1.1 5. Immediate actions were taken to enter TS Surveillance Requirement (SR) 3.0.3, revise the affected Surveillance Procedures, and successfully test the additional relays within 24 hours. Successful test results were expected as all eight relays are procured and maintained to the same safety related standards and are routinely functionally tested and verified to be operating properly.
2981999003 | Cooper Station | 04/23/1999 | 05/24/1999 | 9905280202 | <strong>Missed Port Maintenance Testing of Service Water Air Operated Valve</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1999, at 0500 hours Central Standard Time, it was discovered that the post maintenance testing of the Service Water system [EIIJ Code:BI] air operated temperature control valve [EIIJ Code:V], SW-AOV-TCV451A did not include a stroke time test. Minor maintenance on the valve was performed during Refueling Outage 18, and included adjusting the valve packing. A stroke time test is required by ASME Code, Section XI, Subsection IWV, OM Part 10, Paragraph 3.4. The ASME Code Inservice Testing Program for the Cooper Nuclear Station (CNS) is described in Technical Specification 5.5.6. The cause of this event is attributed to the lack of structure within the CNS Post Maintenance Testing Program. The SW-AOV-TCV451A valve was tested satisfactorily within the retest time limits.
2981999004 | Cooper Station | 04/26/1999 | 06/28/1999 | 9907070375 | <strong>Safety Relief Valve Found Outside Technical Specification Safety Function Lift Setpoint</strong><br /><i>Abstract:&nbsp;</i>On April 26,1999, a review of Target Rock safety relief valve (SRV) test data, provided by Wyle Laboratories, determined that one of eight SRV pilot valve assemblies failed to lift within its current Technical Specification safety function lift setpoint of 1080 +/- 32.4 psig. Specifically, the SRV pilot valve assembly lifted at 1140 psig which is 60 psig above the Technical Specification setpoint value of 1080 psig. The "as found" lift setpoint of 1140 psig is bounded by existing station safety analysis. The discovery was made as a result of a routine Technical Specification surveillance test of the pilot valve assembly. CNS was at 1 00 percent reactor power at the time of the determination. Sufficient corrosion bonding existed between the SRV pilot valve assembly Stellite 21 disc and the pilot valve Stellite 6 in-body seat to cause the SRV pilot valve to lift outside of its Technical Specification safety function lift setpoint tolerance. As documented in CNS LER 1998-006, this is a recurring problem at CNS and within the industry. The affected SRV pilot valve assembly had been replaced with a certified spare during Refueling Outage 18 which ended December, 1998. Corrective action taken included disassembly, inspection and evaluation of the pilot valve, and its components, by Target Rock Corporation and Southwest Research Institute. CNS will continue to monitor industry efforts for a proven solution to the corrosion bonding phenomenon. Additionally, CNS will investigate the possibility of incorporating an SRV upper bound setpoint value in the SRV Technical Specification lift setpoint tolerance criteria.
2981999005 | Cooper Station | 06/01/1999 | 07/01/1999 | 9907080264 | <strong>Failure to Adequately Perform Logic System Functional Testing Places Plant in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 1, 1999, it was determined that two Residual Heat Removal System (RHR) (EIIS:BO) logic relays (10A-K14A and B) (EIIS:RLY) were not adequately tested to satisfy Logic System Functional Test (LSFT) requirements for the reactor vessel shroud level function. This function is required by Technical Specification (TS) Surveillance Requirement (SR) 3.3.5.1.5, function 2.e. Immediate actions were taken to enter TS SR 3.0.3, revise the affected procedure, and successfully test the "to open" function of contact set 5/6 for both relay. Successful results were expected as the "to open" function for contact set 7/8 of the same relays is routinely tested and verified as operating properly, and successful results were achieved. On June 3, 1999 as part of the required follow-up investigation for the June 1 condition, it was confirmed that parallel logic path contacts for the override keylocked switches (10A-S18A and B) (EIIS:HS) must be verified open during the test to fully demonstrate relay contact operation. Immediate actions were taken to enter TS SR 3.0.3, temporarily revise the affected surveillance procedure, and confirm the keylocked switch override contacts were in fact open. Successful test results were expected as the keylocked switches are routinely tested by exercising the keylocked switches and receiving and then clearing an alarm driven from a separate set of contacts on the same keylocked switch. Successful test results were achieved.
2981999006 | Cooper Station | 07/27/1999 | 08/26/1999 | 9908310262 | <strong>Inadvertent Half-Group VII Isolation due to Deenergization of a Relay</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1999, at 0850 hours, while replacing the Primary Containment Isolation System [EIIS Code: JM] relay, PCIS-REL-K75, it was discovered that an inadvertent half-group VII isolation occurred on Logic A. This isolation was caused by deenergization of PCIS-REL-K65 relay. Both the PCIS-REL-K75 and PCIS-REL-K65 relays are mounted on the same snap rail channel. The deenergization of PCIS-REL-K65 relay resulted in the closure of Reactor Recirculation Air Operated Valve, RR-AOV-741AV, and thus prevented the capability to sample the reactor coolant. A Group VII isolation is caused by either a Low-Low reactor water level signal or a High-High radiation in the main steam line signal. Neither of these signals were present at the time of the occurrence of the half-group VII isolation. On July 27, 1999, at 0937 hours, Cooper Nuclear Station (CNS) Technical Requirements Manual Limiting Condition for Operation (LCO) 3.4.1, Condition B, was entered due to CNS's inability to sample the reactor coolant. The PCIS-REL-K65 relay and the half-group VII isolation were reset. The RR-AOV-741AV valve was reopened. On July 27, 1999, at 1112 hours, the LCO 3.4.1 was exited. On July 27, 1999, at 1150 hours, a Four-hour report of the event was submitted to the NRC per the 10CFR50.72(b)(2)(ii) requirements.
2981999007 | Cooper Station | 09/17/1999 | 11/29/1999 | ML99341015 | <strong>Sump Z Inoperability Results in Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1999, at 1350 hours, a plant shutdown was initiated in accordance with Technical Specification 3.0.3, due to both trains of Standby Gas Treatment (SGT) being declared inoperable when both Sump Z pumps, which support the SGT system, failed a surveillance. A one-hour non-emergency report was made pursuant to 10CFR50.72(b)(1)(i). It was later discovered that a hydrogen ignition had occurred in Sump Z during start-up of the Augmented Off Gas (AOG) system, and a Notification of Unusual Event (NOUE) was declared on September 17, 1999, at 2056. The cause of this event was an inadequate conduit seal and a deficient operating procedure which allowed throttling the AOG supply valve for an extended period. This developed a backpressure which resulted in the loss of a drain line water seal, creating a direct path for Off Gas (OG) hydrogen to reach Sump Z and to the Z1 sump pump starter contacts through the inadequate conduit seal. A spark was generated when the contacts changed state which ignited the hydrogen. Necessary repairs were made to damaged sump equipment and to the conduit seals, the deficient procedure was revised, and operating crews were briefed on the event. The NOUE was exited at 0107 on September 18, 1999, and plant operation restored to 100% power on September 27, 1999.
2981999008 | Cooper Station | 10/18/1999 | 11/17/1999 | ML99330017 | <strong>Troubleshooting Activities Causes Critical Bus Undervoltage and ESF Actuations</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1999, at approximately 1512, troubleshooting activities for Circulating Water system [EIIS:NN] Pump [EIIS :P] D resulted in an erroneous undervoltage signal being sensed on non-critical 4160V bus [EIIS:BU] 1B and caused unexpected plant equipment responses including tripping critical 4160V bus 1G. An automatic start of Diesel Generator [EIIS:DG] (DG) 2 and activation of several Primary Containment Isolation System [EIIS:JM] components and Secondary Containment isolation system components, including a start of the Standby Gas Treatment [EIIS:BH] system resulted from the undervoltage on Critical 4160V bus 1G. The start of DG 2 was an automatic engineered safety feature actuation, however, the DG did not load because the Emergency Station Service Transformer [EIIS:XFMR1 automatically re-energized the bus after approximately two seconds in accordance with the undervoltage protection circuitry design. The DG was returned to a normal standby lineup at 16:34. The erroneous undervoltage condition occurred when a portable analog recorder (EIIS:IR] was attached at the 4160V bus 1B panel meter which is on the bus metering potential transformer [EIIS:XPT] (PT) secondary circuit. The recorder's signal input terminals include a removable ground strap that introduced a short circuit to ground, blew the PT secondary fuse, and led to the erroneous undervoltage signal. The plant power generation systems were restored to normal alignments on October 18, 1999, at 17:30. The normal alignment for auxiliary AC power was restored on October 19, 1999, at 16:07.
2981999009 | Cooper Station | 12/30/1999 | 01/31/2000 | ML00368042 | <strong>Failure to Meet Acceptance Criteria Associated with Reactor Equipment Cooling System Operability Requirements Results in Non-Compliance with Technical Specification Limiting Condition for Operation 3.7.3</strong><br /><i>Abstract:&nbsp;</i>On December 30, 1999 at 0850, a leak with the potential to impact the operability of the Reactor Equipment Cooling (REC) [EIIS:CC] system was identified . System walkdowns and a corresponding increase in drywell unidentified leakage rate indicated that the REC leak was located in the drywell . Increased system inventory monitoring identified a slow increase in the leak rate, and the REC system was declared inoperable in accordance with acceptance criteria associated with Technical Specification Limiting Condition for Operation 3.7.3 at 1600 hours. At 2130 on December 30, 1999, the Nuclear Regulatory Commission verbally granted a Notice of Enforcement Discretion (NOED) which allowed continued operation of Cooper Nuclear Station (CNS). The safety basis of the NOED was contained in a previously submitted License Amendment request which would permit an increase in REC system leakage and the use of the Service Water [EIIS:KW] system to provide required cooling in a post Loss of Coolant Accident condition . The REC system leakage rate continued to increase and CNS initiated a controlled shutdown to identify and isolate the leak at 1152 on January 8, 2000. The NOED was no longer required upon entry into Mode 3. Subsequent activities identified leakage in one of the drywell fan coil units (FCU) [EIIS:FCU] which corresponds to the previously identified leakage rate . The apparent cause of the leakage is a form of pitting corrosion. The FCU has been isolated from the system until it can be replaced during the refueling outage scheduled for March 2000.
3011999001 | Point Beach 2 | 02/11/1999 | 03/10/1999 | 9903180084 | <strong>Emergency Diesel Generator Output Breaker Failed to Remain Closed During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On February 1-1, 1999, during performance of a post refueling surveillance test (ORT 3A) the output breaker for the G-01 emergency diesel generator to the Unit 2 Train "A" safeguards Bus failed to remain closed as expected during testing of the load shedding and restoration portion of the test. GO-1 is the alternate standby emergency power supply to the Unit 2 4160 V safeguards Bus (2A05.) The test procedure directed the breaker control switch to be placed in "Pull Out" for four seconds and then returned to the "Auto" position. The breaker did not remain closed and failed to re-power the Bus. Subsequent Investigation determined that the anti-pumping circuit was activated while the breaker control switch was moved from "Pull Out" through "Trip" to "Auto." The anti-pumping circuit was reset and the breaker subsequently closed to re-power the bus. Unit 2 was in cold shutdown and less than 140 degrees F during this event. While the "A" Train safeguards buses were deenergized, one of the two RHR decay heat removal loops required to be operable by TS 15.3.1-A.3.b was not available. This condition was reportable in accordance with 10 CFR 50.73(a)(2)(i)(D) as a condition prohibited by the TS.
3011999002 | Point Beach 2 | 03/23/1999 | 04/16/1999 | 9904270213 | <strong>Red Channel of Steam Generator Pressure Indication Passes Through Fire Zone</strong><br /><i>Abstract:&nbsp;</i>While conducting a revalidation and reverification project for the Point Beach Nuclear Plant 10 CFR 50 Appendix R fire protection programs, the licensee discovered that a cable necessary to provide a plant parameter required to be monitored for an Appendix R safe shutdown location was not routed independent of the appropriate fire zone. In accordance with plant procedures a twice per shift fire round has been established for that fire zone pending correction of the cable routing. This event was reported in accordance with 10 CFR 50.72 as a condition out-side the Appendix R design basis for the plant.
3011999003 | Point Beach 2 | 05/05/1999 | 05/28/1999 | 9906080190 | <strong>Missed Technical Specification Surveillance Test of Emergency DC Lighting</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1999, while operating at full power, licensee personnel discovered that the refueling interval surveillance of the DC Emergency Lighting required by Technical Specification (TS) 15.4.6.A.3 was not conducted during the last Point Beach Nuclear Plant Unit 2 refueling outage. The DC Emergency Lighting system was declared out of service. There is no limiting condition for operation (LCO) associated with this surveillance item. Because of the potential for secondary system transients resulting from deenergizing equipment during this test with the unit in operating, a decision was made to leave the system out of service until the normal conditions for completing this test, cold shutdown, can be met. An evaluation concluded that adequate alternatives are available to provide backup emergency lighting in all areas serviced by the Emergency DC Lighting and there is a high likelihood that the system would function as designed in the event of an actual loss of AC lighting.
3011999004 | Point Beach 2 | 07/21/1999 | 12/20/1999 | ML99363032 | <strong>Failure to Enter Containment Penetration LCO Constitutes a Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>This event discusses the discovery that valve 2CV-133, the RHR to Letdown Isolation Valve, was leaking by while in the shut position and causing the containment penetration P-8 flow path to be pressurized. The licensee initially evaluated this event as not reportable on the basis that, although the valve is designated in an FSAR figure as a containment isolation valve (CIV), the FSAR was in error since this valve did not satisfy the definition of a CIV as found in the TS bases. We therefore concluded that the LCOs for containment penetrations in TE 15.3.6 were not applicable. The NRC subsequently reviewed this evaluation and concluded that a TE violation did occur because the licensee failed to recognize the containment integrity function of the valve as described in the FEAR. Accordingly, we are now reporting that this failure to enter into the action statements of TE LCO 15.3.6.A.l.b.(2) when valve 2CV-133 was identified as the source of leakage between the RHR and CVCS constituted operation or a condition prohibited by the plant's Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B).
3021999001 | Crystal River 3 | 01/18/1999 | 02/17/1999 | 9902250319 | <strong>Personnel Failed to Perform A Surveillance Requirement Withing The Time Specified In The Improved Technical Specifications With A Computer Alarm Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1999, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 99.9 percent RATED THERMAL POWER (RTP). FPC personnel discovered that a Surveillance Requirement (SR) had not been performed within the time specified in Improved Technical Specifications (ITS) when a regulating control rod computer alarm became inoperable without operator knowledge. ITS SR 3.2.1.2 requires verification that the regulating rod group position meet the insertion limits specified in the Core Operating Limit Report (COLR) once every 12 hours when the regulating rod insertion limit alarm is OPERABLE, and once every 4 hours when the regulating rod insertion limit alarm is inoperable. FPC determined that the rod insertion limit alarm on the plant computer was bypassed for power below 15% RTP. Plant procedures did not reflect that the rod insertion limit alarm is inoperable below 15% RTP, and did not require the increased surveillance frequency of once per 4 hours. During past occurrences of plant operation between entry/exit of MODE 2 and 15% RTP that lasted greater than 4 hours, required surveillances were not met. This condition has existed since the computer became operational in 1981. The cause was personnel error. Corrective actions include verification of other alarms and procedure revisions. One previous similar event has been reported.
3021999002 | Crystal River 3 | 02/12/1999 | 03/09/1999 | 9903190045 | <strong>Contaminated Clothing Leads to Exceedance of a Radiological Dose Rate Limit of 10 CFR 20.1301(a)(2)</strong><br /><i>Abstract:&nbsp;</i>On February 12, 1999, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 98.5 percent RATED THERMAL POWER (RTP). While attempting to exit the Protected Area, a French contractor alarmed a gamma sensitive exit portal monitor. Surveys detected a discrete radioactive particle (DRP) inside the contractor's coat. The DRP had a measured activity of 0.12 microcuries of Cobalt-60. The newly arrived contractor had not yet entered the Radiation Control Area at CR-3. The contractor stated the coat had been previously contaminated and released from a French nuclear plant. The extent of the contamination was localized to one piece of clothing. The calculated dose rate of the DRP was 0.0301 rem per hour which exceeds the dose rate limit of 10 CFR 20.1301 (a)(2). The total effective dose equivalent (TEDE) received by the contractor in 1999 did not exceed the TEDE limit for members of the public. The apparent cause was release of the DRP from a French facility as insignificant contamination. Corrective actions include surveys of other plant areas visited by the contractor and surveys of the personal belongings of other French contractors. No previous similar events have occurred at CR-3. This event is being reported in accordance with 10 CFR 20.2203(a)(3)(ii).
3021999003 | Crystal River 3 | 09/02/1995 | 07/01/1999 | 9907080071 | <strong>Inadequate Development Of Instrumentation Specification Leads To Operation Prohibited By Improved Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1999, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 85 percent RATED THERMAL POWER. FPC determined that CR-3 had operated in a condition prohibited by Improved Technical Specifications (ITS). From September 2, 1995 until October 14, 1995, CR-3 operated with a Reactor Coolant Pump Power Monitor (RCPPM) in bypass. Although this condition is allowed by ITS 3.3.1, Reactor Protection System (RPS) Instrumentation, this condition also applied to ITS 3.3.11, Emergency Feedwater Initiation and Control (EFIC) System. FPC did not recognize the applicability of ITS 3.3.11 and the Limiting Condition for Operation (LCO) for the EFIC System instrumentation was not met. This event had no impact on the health and safety of the public. The cause of the event was the EFIC Instrumentation specification was inadequately developed when EFIC was installed in that it inappropriately credited the signal from RCPPMs in the RPS Instrumentation specification. Corrective actions include issuance of a Short Term Instruction and a clarification to the ITS BASES. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B).
3021999004 | Crystal River 3 | 10/01/1999 | 10/29/1999 | ML99308014 | <strong>Main Feedwater Pump Trip During Refueling Shutdown Results in Emergency Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 1,1999, Florida Power Corporation's Crystal River Unit 3 (CR-3) was reducing power in preparation for a refueling outage. At less than five percent RATED THERMAL POWER, a trip occurred of the operating main feedwater (FW) pump. The loss of main FW resulted in actuation of Emergency Feedwater (EFW). The FW pump trip was caused by an overspeed Condition of the pump turbine. A conclusive cause for the pump trip has not been established. Steam cuts were found on the seat of the high pressure control valve that may have been sufficient to overspeed the pump turbine when a steam pressure transient occurred while transferring the steam supply. EFW actuated appropriately and operated as designed. This event had no impact on the public health and safety. Immediate corrective actions included repair of the damaged components and have been completed.
3021999005 | Crystal River 3 | 10/28/1999 | 11/24/1999 | ML99340040 | <strong>ASME Code Section XI System Pressure Test Was Not Performed Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>This Licensee Event Report discusses two separate events where an American Society of Mechanical Engineers (ASME) Code Class 3 component had been returned to service without an ASME Code Section XI system pressure test. At 2130, on October 28, 1999, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 6 (REFUELING) at 0 percent RATED THERMAL POWER. FPC personnel identified an ASME Code Class 3 component that had been returned to service on August 31, 1999, without an ASME Code Section XI system pressure test. At 1730, on November 11, 1999, FPC's CR-3 was in MODE 1 at approximately 8 percent RATED THERMAL POWER. FPC personnel identified another ASME Code Class 3 component that had been returned to service on October 10, 1999, without an ASME Code Section Xl system pressure test. Both components were subsequently pressure tested satisfactorily. There was no increased risk to the public health and safety. FPC determined this was a result of personnel error during the planning and implementation of maintenance work packages. Maintenance Study Book Entries have been issued. An internal assessment of the ASME Code Section XI Repair/Replacement and Pressure Testing Programs will be completed by December 31 1999. Three similar events were previously reported by FPC.
3021999006 | Crystal River 3 | 11/04/1999 | 12/01/1999 | ML99341015 | <strong>Procedure Revision Causes Improved Technical Specification Surveillance Requirements To Be Implemented Improperly</strong><br /><i>Abstract:&nbsp;</i>On November 4, 1999, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) at 0 percent Rated Thermal Power prior to restart from a refueling outage. While performing a Surveillance Procedure, FPC determined Improved Technical Specification (ITS) Surveillance Requirements (SR) were not being implemented properly. When applicable, ITS 3.4.11, Reactor Coolant System Low Temperature Overpressure Protection System, SR 3.4.11.1 and SR 3.4.11.2, require verification every twelve hours that the High Pressure Injection (HPI) non- operating pumps and injection valves are deactivated. During a procedure revision in May, 1999 the frequency for verifying HPI deactivation was changed from once per shift to once per day for portions of HPI. The cause was personnel error. The procedure was corrected on November 5, 1999. There have been two similar occurrences identified. The components remained under administrative control. FPC concluded this event did not impact the public health and safety.
3051999001 | Kewaunee | 02/28/1999 | 03/30/1999 | ML11188063 | <strong>Inadequate Configuration Controls Cause Personnel to Unknowingly Place Plant In Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1999, with the plant operating at full power, the operating shift crew closed a valve being relied on to provide overpressure protection of a containment penetration. This was contrary to the commitments made regarding Generic Letter (GL) 96-06 concerns with overpressurization of containment penetrations. Following a timing test failure of redundant containment isolation valves, the crew closed another manual isolation valve in the containment penetration system piping. The crew's action was consistent with guidance provided by the Kewaunee Technical Specifications, when a containment isolation valve is found inoperable. There was a control card hung on the valve which was expected to have precluded this type of event. However, the investigation into the event found that the configuration controls established in response to the GL were ineffective. Accordingly, the Operations staff was not provided with sufficient guidance to ensure continued compliance with the GL concerns. The plant was in this condition for approximately four hours, from about 0400 to 0800. When the containment isolation valves were retested and declared operable, the valve relied upon to address the GL overpressure concern was reopened. The safety consequences of this event were minimal. The concerns of GL 96-06 are noted to be concerns with overstressing containment penetrations in the event of a high energy line break in containment. At no time was the penetration actually challenged.
3051999002 | Kewaunee | 05/14/1999 | 06/14/1999 | ML11188063 | <strong>Inadequate Surveillance Test Procedure Results in Redundant Containment Level Instrument Channels Degraded and in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1999 with the plant at 97% power, during a review of plant logs, an Operator noted the plant process computer for 'B' wide range containment sump level was indicating "*N". The indication was noted and reported to the Control Room Supervisor (CRS). The control board indicator was indicating zero, as expected. The "*N" indication was a result of the output loop's voltage being outside the limits for the plant process computer to accurately read. We believe the cause of the voltage output anomaly was due to the calibration process used in the Surveillance Procedure (SP) for this system. The process used in this SP involves open circuiting the output current loop during calibration, while the input power is still applied. According to the equipment vendor, open circuiting the output loop, with power applied, may cause the isolation amplifier (part of the signal converter) to shift the output voltage off-scale, causing an abnormal reading. Since we were not able to recreate the condition, we were unable to conclusively determine the resultant shift in the wide range containment sump level indication. Therefore we were unable to definitively determine the channel's operability. As a result, we are conservatively reporting this event as a violation of Technical Specification, Table 3.5-6. After restoring the voltage on the output loop to within the acceptable limits, both trains of Wide Range Containment Sump Level were returned to operable status on May 14, 1999.
3051999003 | Kewaunee | 09/21/1999 | 10/21/1999 | ML11188064 | <strong>Seismic Monitor Calibration Procedures Do not Ensure Technical Specifications Requirements are Fulfilled Since System Installation in 1986-Cause Indeterminate</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1999, while the plant was operating at full power, the refueling interval calibration of the Seismic Monitoring System was in progress. The I&C technician performing the surveillance questioned operability of the system because he believed several internal jumper wires were missing from the analog trigger switch printed circuit board (PCB) in the accelerograph recorder portion of the system. Investigation showed that the proper jumpers were installed. However, procedure improvements were needed to fully test the analog trigger switch PCB so procedure changes were implemented on September 20, 1999. On September 21, 1999, I&C Engineering determined that the added calibration procedure steps were necessary to fully test the analog trigger switch PCB, and that the seismic monitoring system had not been properly calibrated since its installation in March 1986. This constituted an improper implementation of the calibration surveillance requirement Technical Specifications (TS), Table TS 4.1-1, item 29, Seismic Monitoring System. The improved calibration surveillance, which fully tested the seismic monitoring system and the analog trigger switch PCB, was completed on September 23, 1999.
3051999004 | Kewaunee | 10/06/1999 | 11/05/1999 | ML99316014 | <strong>Contrary to TS Requirements Non-Automatic Containment Isolation Valves Have Been Opened for Testing</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1 999, while the plant was operating at full power, it was identified that contrary to Technical Specifications (TS) requirements, non-automatic containment isolation valves were being testing following maintenance. Kewaunee TS defines containment in part, when, "the non-automatic Containment System isolation valves and blind flanges are closed as required." This statement is interpreted to mean that non-automatic isolation valves cannot be opened unless there is a specific license requirement to do so. Twelve such valves are listed in Kewaunee's in-service test (IST) program plan as valves important enough to be tested in accordance with IST requirements. These valves are noted as being outside the scope of ASME Section XI IST testing requirements. Consequently, IST testing requirements do not apply to these valves. When IST testing of the subject valves began in 1977, they were considered to be within the scope of Section XI testing requirements. Subsequent revisions to the Code and understanding of the valves' status resulted in reclassifying the valves as outside the scope of IST testing. The plan was revised in 1993 to note the change in status. However, the valves were felt to be important enough to remain in the IST plan and testing continued. The cause is attributed to a more conservative understanding of the TS today than there would have been when the status of the valves changed. There were no safety Consequences to operating the valves. The valves were only operated individually with their redundant in-series isolation valve closed.
3051999005 | Kewaunee | 11/05/1999 | 12/06/1999 | ML99347022 | <strong>Internal Power Supply Failure for Radiation Monitor R-19 Results in Steam Generator Blowdown Isolation</strong><br /><i>Abstract:&nbsp;</i>The following event is reportable as an unplanned actuation of steam generator blowdown isolation valves which are engineered safety features (ESF). On November 5, 1999 while the plant was operating at full power, radiation monitor system channel R-19, "Steam Generator Blowdown Sample Radiation Monitor" failed. As a result, inadvertent blowdown isolation occurred. R-19 failed due to an internal power supply failing. The radiation monitor was repaired, tested and returned to service on November 8, 1999
3051999006 | Kewaunee | 12/20/1999 | 01/19/2000 | ML00367758 | <strong>Both Trains of Control Room Post-Accident Recirculation Inadvertently Removed from Service</strong><br /><i>Abstract:&nbsp;</i>At 0710 CST on December 20, 1999, with the plant at 96.5% power both trains of Control Room Post Accident Recirculation (CRPAR) were rendered inoperable. This event occurred while attempting to rotate running equipment. The Control Room Air Conditioning (CRAC) train B control switch was placed in ON. The CRAC train A was placed in OFF. Train A was placed in OFF in order to allow CRAC train B to start. Train B failed to start because the train A control switch was not placed in OFF within 20 seconds. The CRAC system start logic requires the unit selected to ON to start within 20 seconds after the control switch is placed in the ON position. With train A in OFF and the failure of train B to start, both trains of CRAC were incapable of automatically starting. Since one train of CRAC ventilation must be operating to support CRPAR, both trains of CRPAR were rendered inoperable. Once the operator recognized that train B did not start, the train A control switch was returned to the auto position and the unit returned to service. At 1025 during a review of this event it was determined that both CRAC trains were inoperable for a total of 12 seconds and therefore, both trains of CRPAR were also inoperable for 12 seconds. Having both trains of CRPAR inoperable is a violation of KNPP Technical Specifications that require at least one train of CRPAR to be operable with the reactor critical.
3061999001 | Prairie Island 2 | 02/06/1999 | 03/08/1999 | 9903180126 | <strong>Technical Specification-required Reactor Protection Logic Test Missed due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1999, Unit 2 was taken to Hot Shutdown to repair a Nuclear Instrumentation System cable. The unit reached Hot Shutdown at 0358. A Temporary Change Notice (TCN) had been issued affecting the shutdown procedure 2C1.3. The TCN required performance of a reactor protection logic test prior to rod withdrawal. Due to personnel error, the test was not performed at the proper time, and shutdown rods were withdrawn at 0516. Later, the error was discovered and the shutdown banks were inserted at 0544, the reactor trip breakers were opened, and the test was performed with satisfactory results.
3111999001 | Salem 2 | 03/30/1999 | 04/23/1999 | 9905030062 | <strong>Main Steam Safety Valves Failed Lift Set Test</strong><br /><i>Abstract:&nbsp;</i>During the period from March 30 through March 31, 1999 with the Salem Unit 2 in Mode 1 at 75% reactor power and steam pressure at >804 psig, in place lift assist testing of the main steam safety valves (MSSV) was performed. Because the testing of the MSSV was performed at end of life conditions, when power related xenon transients have greater effects, Public Service Electric and Gas reduced power to 75% and the high flux trip setpoint to 87%, thus meeting the Technical Specifications requirements for one inoperable MSSV. When a MSSV valve was determined to be inoperable, the MSSV valve was adjusted and subsequently retested to meet the table 4.7-1 tolerance prior to continuing with the test. The cause of this event was consistent with AEOD/S92-20 study, which classified these failures as "setpoint variance." Setpoint variance, as discussed in this report, is a result of aging. Aging is the effects seen by a component that remained unexercised for an extended period of time at extreme temperatures. Lubrication dries out due to high temperature, and due to component design, there is no lubricity provided by system fluid. The valves were adjusted land retested to ensure compliance with the +/- 1% Technical Specification tolerance prior to continuing with the test.
3111999002 | Salem 2 | 04/05/1999 | 07/01/1999 | 9907140040 | <strong>Containment Isolation Valve Fails LLRT - Degraded Containment Integrity</strong><br /><i>Abstract:&nbsp;</i>During performance of Type C local leak rate testing on April 5, 1999 it was determined that 2SA118 (containment service air outboard manual isolation valve) failed the as found leakrate test. Because this failure was the second valve for this penetration to fail (2SA-119 inboard check had also failed) containment integrity was considered to be degraded. At the time of discovery the Unit was shut down for refueling and containment integrity was not required. A 4-hour report was made to the NRC as required by the plant's Emergency Classification Guide and 10CFR50.72(b)(2)(i). These valves are on the service air supply to the containment and are normally not open except during periods when maintenance activities are being performed within containment. The manual valve was cycled several times and the leakage returned to measurable levels. The check valve was mechanically agitated and returned to the normal closed position. Both valves were opened and inspected prior to entry into mode 4 during restart from the current refueling outage. Foreign material was found in the 2SA118 valve. In addition, the valve was unable to pass the LLRT so the valve wedges were replaced and machined and the valve was successfully tested. This report is being made pursuant to 10CFR50.73 (a)(2)(ii) Licensees shall report: "Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded;.."
3111999003 | Salem 2 | 04/06/1999 | 05/04/1999 | 9905120265 | <strong>Unplanned Loss of all Unit 2 Chillers</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1999, all Salem Unit 2 chillers were rendered inoperable. At the time of the event one of the three Unit 2 chillers was removed from service to support outage maintenance, and the other two were being supplied service water (SW) from #22 nuclear SW header. Operations personnel, in the process of removing 22 nuclear SW header from service, isolated #22 nuclear SW header prior to realigning the remaining two chillers to #21 nuclear SW header (the other SW header). 21 and 22 chillers were realigned to the 21 nuclear SW header and returned to operation within 35 minutes of being isolated. This event was caused by human error, specifically a less than adequate procedure review implementation. A recent procedure revision changed the sequence of steps in the procedure used to remove #22 nuclear SW header from service. The revised sequence isolated #22 nuclear SW header prior to cross-connecting the remaining chillers to #21 nuclear SW header. There was minimal safety significance associated with this event because the outside temperatures were cool (42 degrees F, well below the design maximum outside temperature of 95 degrees F), reactor and secondary side heat loads were minimal since the unit was in mode 5, and 2 chillers were restored within 35 minutes. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications.
3111999004 | Salem 2 | 04/11/1999 | 05/10/1999 | 9905120025 | <strong>Engineered Safety Feature Actuation, Containment Ventilation System Isolation During Reactor Vessel Head Removal</strong><br /><i>Abstract:&nbsp;</i>This LER reports the automatic actuation of an Engineered Safety Feature (ESF) due to a valid signal, as required by 10CFR50.73(a)(2)(iv). On April 11, 1999 during Reactor Vessel Head removal in support of refueling operations, the Salem Unit 2 Containment Noble Gas monitor (2R12A) alarmed in response to a valid high radiation condition, causing a Containment Ventilation system isolation. The high radiation condition was caused by the release of gaseous activity in the upper Reactor Vessel following plant depressurization. Although the alarm of the 2R12A and the subsequent isolation of the Containment Ventilation system should be anticipated as a part of the pre-planned sequence of Reactor Vessel disassembly, procedural requirements were not in place to secure Containment purge in anticipation of a possible ESF isolation of the Containment Ventilation system. Corrective Actions for this event included containment atmosphere monitoring and a follow on Containment Purge to Plant Vent evolution. In addition, the Cold Shutdown to Refueling procedure, S1/S2.OP-IO.ZZ-0007, will be revised to require that Containment purge be secured prior to lifting the Reactor Vessel Head in anticipation of a possible isolation of the Containment Ventilation system as a result of an alarm of the Containment Noble Gas monitor.
3111999005 | Salem 2 | 05/04/1999 | 06/02/1999 | 9906080296 | <strong>Failure To Meet Technical Specification Action Statement Requirements For High Oxygen Concentration In The Waste Gas Holdup System</strong><br /><i>Abstract:&nbsp;</i>This LER reports the operation of Salem Unit 2 in a condition prohibited by Technical Specification (TS) 3/4.11.2.5, Radioactive Effluents, Explosive Gas Mixture. Specifically, TS 3/4.11.2.5 requires that the concentration of oxygen in the waste gas holdup system shall be limited to less than or equal to 2 percent by volume at all times. In the event that oxygen concentration is greater than 2 percent by volume, but less than 4 percent by volume, oxygen concentration must be reduced to 2 percent or less within 48 hours. Contrary to these requirements, on May 2, 1999, during draining of the Refueling Water Storage tank, the oxygen concentration in the 24 Waste Gas Decay Tank exceeded 2.8 percent. Corrective measures were commenced in accordance with station procedures to reduce the oxygen concentration when the out of specification condition was identified. However, the oxygen concentration was not reduced to a level of 2 percent or less within the required 48 hours. The failure to reduce the oxygen concentration to within TS limits within the required time was caused by the operators' inability to perform the necessary number of tank purges in the time available. To prevent recurrence, existing procedures and practices that involve the processing and purging of the Waste Gas Decay tanks will be evaluated to identify improvements that would allow for a shorter purge time. Operations Department Management will provide a read and sign notice to all Supervisors in the Control Room emphasizing the importance of taking immediate actions to remedy entering TS Action Statements. The notice will stress the importance of the timely planning and execution of actions to correct out of specification conditions. In addition, an investigation will be conducted to identify and correct any process failure or equipment deficiency that may have contributed to the intrusion of oxygen into the Waste Gas System.
3111999006 | Salem 2 | 05/01/1999 | 07/01/1999 | 9907140035 | <strong>High Head Safety Injection Flow Balance Discrepancy Noted During Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 30, May 1, 1999, during performance of a surveillance on the safety injection system throttling valves to balance injection flow, it was determined that there was no flow in one of the four injection legs (21 leg). Upon throttling the valves in the remaining legs the flow was re-established to the 21 leg. It is believed that the 21SJ17 (safety injection line to cold leg) check valve had been stuck closed. The four legs were subsequently flow balanced successfully. The 21SJ17 was cut out of the system and replaced in kind. Subsequent inspection of the valve found no evidence of malfunction which would have rendered the valve inoperable. The valve seats were in specification and the internal clearances were at the low end of the manufacturer's (Edwards) recommendation. It is suspected that there may have been foreign material which jammed the valve in the closed position. This voluntary report is being submitted in order to provide a record of the failure which was initially communicated in a 4-hour report to the NRC under 10CFR50.72. In accordance with NUREG 1022, Revision 1 guidance, which states that the out of service time is calculated using the "time of discovery unless there is firm evidence based on a review of relevant information (e.g. the equipment history and cause of failure) to believe the discrepancy existed previously," this event is not reportable. Technical specification requirements for this system were satisfied for the mode of operation at the time of discovery and the event is bounded by current analyses.
3111999007 | Salem 2 | 06/05/1999 | 07/06/1999 | 9907200070 | <strong>Missed Surveillance for Quadrant Power Tilt Ratio (QPTR)</strong><br /><i>Abstract:&nbsp;</i>On June 5, 1999, the operations shift determined that the 12-hour surveillance to perform a Quadrant Power Tilt Ratio (QPTR) calculation in accordance with Technical Specification Surveillance Requirement 4.2.4.1.d had not been performed during their shift. The cause of this event is attributed to human error. The calculation of QPTR was not adequately tracked to ensure compliance with the 12-hour surveillance requirement. Upon discovery the required QPTR calculation was performed. Personnel involved with this event have been held accountable in accordance with PSE&G polices. This item is reportable under 10CFR50.73(a)(2)(i)(B), "any operation or condition prohibited by the plant's Technical Specifications."
3111999008 | Salem 2, Salem 1 | 07/14/1999 | 07/28/1999 | 9908030284 | <strong>Fire Program Deficiency - Limit Switch Cables Subject to Multiple Hot Shorts in Same Fire Area</strong><br /><i>Abstract:&nbsp;</i>This Special Report is being made pursuant to the requirements of License condition 2.I which requires that a 14 day report be submitted for cases where the provisions of the approved fire protection program are not maintained. Further, Technical Specification 6.9.3 states that "violations of the fire protection program ... shall be submitted ... via the Licensee Event Report System within 30 days." This report satisfies both of these requirements. During the on-going review of the Fire Protection Program and the post fire safe shutdown analysis as part of the fire wrap project it was determined that cables associated with the limit switches for both of the service water header valves (SW22) are routed through the same fire protection area (mechanical penetration area). This is not in conformance with the approved fire protection program. In the event of fire in this area, hot shorts are required to be postulated, per NRC guidance, in both of these cables. These shorts could result in the closure of both of the header valves with the attendant loss of service water to safety related equipment. Long term loss of service water would result in loss of some equipment necessary to maintain safe shutdown, if left uncorrected. The area in question has been subject to compensatory actions due to fire wrap issues which had been previously identified. The likelihood of this hot short event is extremely low. No further immediate actions are necessary. Current plans are to perform a design change which will eliminate the concern. There is no significant impact on the public health and safety.
3131999001 | Arkansas 1 | 05/21/1999 | 06/21/1999 | 9906290009 | <strong>Automatic Actuation of the Control Room Emergency Ventilation System Due to Higher Than Normal Radiation At The Detector When a Radioactive Filter Was Moved In An Adjacent Area</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1999, when a radioactive spent fuel pool purification filter was moved, a radiation field was created at a detector for the Control Room Emergency Ventilation System (CREVS) of sufficient strength to cause a CREVS actuation. Ventilation was restored to the normal configuration approximately fifty-six minutes after the actuation. This event did not create a threat to the safe environment for Control Room Operations personnel or to safe plant operation. The root cause of this event is attributed to the design of the CREVS being sensitive and therefore susceptible to spurious actuations. A similar event reported in Licensee Event Report (LER) 50-313/98-002-00 involved a different CREVS detector in a different area. The corrective action plan from the previous event was intended to minimize, but not necessarily prevent, recurrence based upon various considerations. Additional training has been provided to Radiation Protection (RP) personnel regarding this event. Other corrective actions being taken are considered enhancements that also may minimize, but not necessarily prevent, recurrence.
3131999002 | Arkansas 1 | 07/06/1999 | 08/05/1999 | 9908100260 | <strong>Technical Specification Allowable Outage Time For One Emergency Diesel Generator Was Exceeded Due To Idler Gear Stub Shaft Bracket Bolting Failure Caused By Loss Of Bolt Pre-Load</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1999, the Technical Specifications Allowable Outage Time (AOT) and the shutdown action time for Emergency Diesel Generator #2 were exceeded. The engine had been removed from service on June 28, 1999, for scheduled maintenance. During post-maintenance testing, low lubricating oil pressure was experienced. The cause was fatigue failure of bolts for the idler gear stub shaft bracket. A new modified idler stub shaft bracket assembly was installed and the gear train was replaced. A Notice Of Enforcement Discretion was received from the NRC on July 5, 1999. The engine was tested and restored to an operable status on July 8, 1999. The root cause for the failure is a loss of bolt pre-load. Pre-load was lost by either improper initial bolt torque or original joint design issues that resulted in loss of pre-load due to stresses from vibration, thermal cycles, or loads transmitted to the bolting from the gear train via the bracket. The configuration of the stub shaft bracket assembly on EDG #1 differed from EDG #2 because of a vendor modernization recommendation implemented in 1984.
3131999004 | Arkansas 1 | 09/28/1999 | 10/27/1999 | ML99309016 | <strong>Fuel Handling Area Ventilation System Flow Rate Below Technical Specifications Requirement While Irradiated Fuel Movement Was In Progress To Inapppropriate Installation Of A Temporary Device to Restrain The Exhause Damper Open And A Work Plan Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1999, the flow rate of the Fuel Handling Area Ventilation System was below the Technical Specifications requirement while irradiated fuel was being moved in the Spent Fuel Pool. Ventilation flow rate was reduced below requirements at approximately 1810, and fuel handling was stopped at 1938 when the condition was discovered. A rope had been installed to restrain the ventilation exhaust damper in the open position during an outage of an electrical bus. The rope allowed the damper to close enough to reduce flow rate by automatic adjustment of fan blade pitch due to system backpressure. Installation of the rope was not addressed by the work plan (procedure) for the bus outage or authorized under the administrative controls for temporary alterations. The root causes of this condition are inappropriate work practices by the individual installing the restraining device and the deficient work plan. Lessons learned from this event are being reviewed with Operations personnel of both ANO units. The deficient work plan will be corrected and other work plans for bus outages will be reviewed prior to their next use to verify adequate controls for temporary alterations.
3131999005 | Arkansas 1 | 12/15/1999 | 01/13/2000 | ML00367705 | <strong>Once Through Steam Generator Tube Left In Service With A Flaw Exceeding The Technical Specifications Limit As A Result Of A Process Deficiency</strong><br /><i>Abstract:&nbsp;</i>On December 15, 1999, during a review of eddy current test data from the previous refueling outage (1R15), it was discovered that an indication in the upper roll transition area of tube 110/60 in the "A" Once Through Steam Generator (OTSG) had been inadvertently reclassified from repairable to non-repairable by an independent oversight review analyst. This error resulted in leaving in service a tube with a flaw exceeding the Technical Specification (TS) limit. Since the defective tube in the "A" OTSG was not repaired as required, the "A" OTSG was declared inoperable and TS 3.0.3 was entered at 1446 CST on December 15, 1999. Enforcement discretion was requested from the NRC to allow sufficient time for submittal and NRC review and approval of an exigent TS change request. The enforcement discretion request was verbally approved by the NRC at 1836 CST on December 15. The root cause of this event was a process deficiency. The process will be revised to ensure that both the technical and administrative facets of resolving an issue are independently reviewed. Because extensive measures were already in place to enhance the operators' ability to detect and respond to OTSG tube leakage, no specific immediate corrective actions were taken regarding this event. The defective tube will be repaired during the next refueling outage.
3151999001 | Cook 1, Cook 2 | 01/06/1999 | 12/08/2000 | ML00377696 | <strong>General Electric HFA Relays Installed in Emergency Diesel Generators May Not Meet Seismic Qualification</strong><br /><i>Abstract:&nbsp;</i>This revision replaces the initial LER in its entirety. The LER has been rewritten to provide new information concerning the analysis of the event and corrective actions. On January 6, 1999, while in mode 5, it was determined that the General Electric (GE) HFA safety related relays installed in plant system circuits may not be properly configured in accordance with vendor instructions for relay contact adjustment and servicing, and therefore, may not meet seismic qualification. The relays were procured with all contacts in the "normally open" position, which were converted to "normally closed" as required for installation. When converting, past plant practices did not verify that all critical relay adjustments were within the vendor specified tolerances. It was determined that, for mode 5, only the Emergency Diesel Generators (EDGs) were adversely impacted such that these relays could prevent the EDGs from performing their safety related function. The EDGs were declared inoperable on January 11, 1999. Follow-up investigations for modes 1 through 4 identified additional HFA relays that were not properly configured. Affected systems included degraded grid detection, Essential Service Water, Safety Injection, Containment Spray, Auxiliary Feedwater and Main Steam. This event was reported on January 11, 1999 under: 10CFR50.72(b)(2)(i) , as a condition which, if it had been found while the plant was operating, would have resulted in the plant being seriously degraded, and; 10CFR50.72(b)(2)(iii)(A), a potential to alone prevent fulfillment of the safety function of systems that are needed to maintain the reactor in a safe shutdown condition. Deficiencies in the management of industry operating experience resulted in the failure to address the seismic qualification issues concerning the HFA relays. Corrective Actions were implemented to restore the operability of all affected Unit 1 and Unit 2 systems, and to address the concerns regarding the Operating Experience program. A qualitative assessment of the as found condition against the licensing bases concluded that the improper configuration of the HFA relays resulted in consequences of the condition that were of low safety significance.
3151999002 | Cook 1 | 01/12/1999 | 02/11/1999 | 9902220034 | <strong>Failure to Perform Technical Specification Surveillance Test for Pressurizer Power Operated Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1999, with Unit 1 depressurized in Mode 5, surveillance test section personnel determined that the reactor coolant system pressurizer power operated relief valves (PORVs) had not been tested as required by Technical Specification (TS) Surveillance Requirements 4.4.9.3.1a. and 4.4.9.3.1e.2.(a) for low temperature overpressure (LTOP) mitigation. The related surveillance procedure was required to be performed by January 10, 1999, but was not completed until January 13, 1999. Because of the missed surveillance the LTOP PORVs had become inoperable on January 10, 1999. Since the operators were not initially aware of the missed PORV surveillance, all actions required by TS 3.4.9.3 for inoperable PORVs had not been taken within the allowed Action times for the Limiting Condition for Operation. As the surveillance requirements had not been met, this event is reportable as operation prohibited by the plant's TS. Inadequate scheduling controls allowed two personnel errors to cause the event. After determining the surveillance procedure due date by using the Nuclear Plant Maintenance (NPM) computer system, a surveillance scheduler failed to verify the NPM due date against the Nuclear Test Scheduler (NTS) computer scheduled due date. The NPM due date was wrong because data had not been entered correctly for the previous (December 1998) surveillance. This caused NPM to generate an erroneous surveillance due date of January 15, 1999. As corrective action, additional direct management oversight was instituted to verify that all TS surveillances are current and to improve the accuracy of future surveillance scheduling. This included emphasis on personal accountability standards and proper use of NTS. The root cause investigation for this event has not been completed. It is anticipated that, if significant changes to the LER are identified as a result of completion of the root cause investigation, an update to this LER will be submitted by March 25, 1999. At the time of the event the unit was depressurized, both LTOP PORVs remained capable of performing their safety functions, and one PORV was open (although not blocked open) for pressure control, therefore this event had no safety significance.
3151999004 | Cook 1, Cook 2 | 10/30/1997 | 07/01/1999 | 9907090123 | <strong>Failure to Perform Technical Specification Surveillance Analyses of Reactor Coolant Chemistry with Fuel Removed</strong><br /><i>Abstract:&nbsp;</i>On February 16, 1999, Chemistry personnel determined that Unit 2 reactor coolant system (RCS) chemistry had not been analyzed for fluorides and chlorides, as required by Technical Specification (TS) Surveillance Requirement 4.4.7, while the unit was defueled. The analyses, required "at all times," were not performed from October 30 to November 23, 1997. Unit 2 has remained in Mode 5 or 6 since that time. Additional investigation identified a total of ten periods (6 for Unit 1 and 4 for Unit 2) since 1989, when the chemistry analyses had not been performed. TS Clarification (TSC) #54, which had been in effect since 1992, provided an inappropriate exemption from sampling while the core was off-loaded and RCS circulation was suspended. Since the surveillance requirements were not met, this event is reportable pursuant to the requirements of 10CFR 50.73(a)(2)(i)(B), as an operation prohibited by the plants' Technical Specifications. The root causes for this event include: 1) ineffective management of Technical Specifications, and 2) ineffective ownership of Chemistry department performance. Chemistry personnel have been instructed on the requirement to follow the TS as written without reliance on the use of TS clarifications or interpretations. The written job order activities used to control shutdown chemistry sampling were corrected to remove references to the Spent Fuel Pool as an alternate RCS sample point. In each identified case when analyses were not done, the affected unit was at low pressure and temperature, and analyses completed prior to and after the missed analyses provided no indication of an out-of-limit condition. Based upon this information, this event had minimal impact on the health and safety of the public
3151999005 | Cook 1 | 05/12/1994 | 03/10/2000 | ML00369375 | <strong>Reactor Protection System Actuations During Testing Not Previously Reported</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1999, during a review of industry Licensee Event Reports submitted by other utilities for actuations of the Reactor Protection System (RPS) during rod drop surveillance testing, Engineering personnel questioned the reportability of past Donald C. Cook Nuclear Plant RPS actuations during rod drop surveillance testing. In the course of performing rod drop testing, the RPS was manually actuated to open the reactor trip breakers when unanticipated test equipment problems occurred during the surveillance. These RPS actuations should have been reported in accordance with 10 CFR 50.72(b)(2)(ii) and 10 CFR 50.73(a)(2)(iv) as conditions that result in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System, but they were not reported. An ENS notification was made on February 16, 1999, at 1808 hours in accordance with 10 CFR 50.72(b)(2)(ii), and this LER is submitted in accordance with 10 CFR 50.73(a)(2)(iv). The causes of this event were a lack of knowledge of NRC reportability requirements related to unplanned ESF and RPS actuations during surveillance testing, and surveillance procedure inadequacies. Training on 10 CFR 50.72 and 10 CFR 50.73 reportability requirements has been provided to Operations and is being considered for additional plant personnel. Administrative procedures were revised to provide a requirement to evaluate procedure changes for the possibility of a manual actuation of an ESF, including the RPS. Rod drop surveillance procedures will be revised to allow a manual actuation of RPS when specific types of problems occur during testing. It has been determined that there is no safety significance due to these manual actuations of the RPS or the delay in reporting the events. When unanticipated problems were encountered during the rod drop surveillance, manual actuation of the RPS was a conservative action and was not in response to adverse plant conditions.
3151999006 | Cook 1, Cook 2 | 01/15/1999 | 05/24/2000 | ML00371952 | <strong>Fuel Crane Loads Lifted Over Spent Fuel Pool Could Impact Energies Greater Than Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1999, a discrepancy was identified between the Unit 1 and 2 Technical Specification (TS) 3.9.7 impact energy limit of 24,240 inch-pounds (in-lbs) and TS 4.9.2 surveillance procedure, which permits fuel assemblies to be lifted 15 inches above the spent fuel pool racks. On February 23, 1999, a review of fuel assembly and Rod Cluster Control Assembly (RCCA) weights identified that a combined dry fuel assembly and RCCA weight of 1619 lbs had been lifted over the spent fuel racks. Based on this weight and a lift height of 15 inches, a calculated impact energy of 24,285 in-lbs could be imparted on the fuel racks in the event the fuel crane dropped its load. This resultant impact energy is greater than the TS limit of 24,240 in-lbs. On February 23, 1999, per 10CFR 50.73(a)(2)(i)(B), this condition was determined to be reportable for a condition prohibited by plant TS and an interim LER was submitted on April 16, 1999. The root cause is an inadequate TS surveillance program. A contributing cause is inadequate design change process. On March 17, 1999, a maximum fuel weight limit was imposed on all future fuel shipments to ensure combined fuel assembly plus RCCA weights would not exceed the design limit of 1616 lbs. In addition, a calculation was performed which determined the maximum height which Unit 1 and 2 fuel assemblies currently resident in the cores and spent fuel pool, could be lifted without exceeding the TS impact energy limit of 24,240 in-lbs. This limit has been incorporated into the appropriate TS surveillance procedures. A procedure is being developed to ensure that the design change process will be implemented when mechanical changes are made to the fuel assemblies, including fuel assembly weights, during core reload design activities A calculation will be performed to determine the design basis impact energy limit for the Holtec racks. Upon completion of the calculation, a TS Amendment request will be submitted to the NRC. Based on recent impact energy calculations which take into consideration the effects of buoyancy of the fuel and the resultant Holtec analysis impact energy value of 55,800 in-lbs, this condition has no safety significance.
3151999007 | Cook 1, Cook 2 | 10/20/1998 | 04/04/2002 | ML02107051 | <strong>Retraction - The Divider Barrier between Upper and Lower Containment Volumes May Be Overstressed</strong><br /><i>Abstract:&nbsp;</i>This LER is being retracted. <br /><br /> On October 20, 1998, based on preliminary stress analyses, engineering personnel determined that a postulated steam line break could result in calculated stresses exceeding the code allowable stresses for the Unit 1 Steam Generator (SG) enclosures. These reinforced concrete enclosures are part of the divider barrier between the upper and lower containment volumes. Overstressed conditions in these enclosures could allow increased steam bypass flow around the ice condensers, which could result in higher than expected containment pressure. Due to a lack of reasonable assurance that the structures would not be overstressed, on March 2, 1999, at 1314 hours, an Emergency Notification System (ENS) notification was made in accordance with 10CFR50.72(b)(2)(i), for a condition outside the design bases of the plant. An LER was submitted on April 1, 1999, in accordance with the related 10CFR50.73(a)(2)(ii) requirement.<br /><br /> When the ENS notification was made, Donald C. Cook Nuclear Plant (CNP) was applying the conservatisms of two different stress analysis methods into a combined stress limit, creating a third method of analysis. This third method conservatively bounded the licensing requirements, but resulted in preliminary calculated overstresses of the SG sub-compartment structures. CNP performed an in-depth review of the licensing basis and determined that the two different stress analysis methods are individually adequate, and need not be combined. The potential overstresses were calculated using methods beyond the CNP licensing bases. An overstress condition for the load combinations applicable to the steam generator enclosure analyses did not exist for the pressure values calculated at the time of licensing, and LER 50-315/1999-007-00 is hereby retracted.
3151999008 | Cook 1, Cook 2 | 01/15/1999 | 07/13/2001 | ML01205045 | <strong>Residual Hear Removal (RHR) Piping Vibrations Could Potentially Cause RHR Piping Failures</strong><br /><i>Abstract:&nbsp;</i>This LER is being issued to provide the results of the root cause analysis and replaces the original LER in its entirety. On January 15, 1999, with both units in Mode 5, plant operators reported excessive piping vibration in the residual heat removal (RHR) rooms. Since initial plant operation, noise and vibration has been known to occur in both the Unit 1 and Unit 2 RHR systems while the systems operated in shutdown cooling with low decay heat, a depressurized reactor coolant system (RCS), and low RCS temperature. On March 10, 1999, an ENS notification was made to the NRC in accordance with 10 CFR 50.72(b)(2)(i), for any condition, found while the reactor was shutdown, that had it been found while the plant was operating, would have resulted in the plant being in an unanalyzed condition. As such, LER 50-315/99-008 was submitted in accordance with 50.73(a)(2)(ii)(A), for the plant being in an unanalyzed condition. The source of excessive vibration in the RHR system was caused by cavitation across the RHR flow control valves. This cavitation was due to excessive pressure drops across the control valves under certain relatively low flow conditions when the RHR system flow was throttled and pumping into a depressurized reactor vessel. The primary cause of failures in the tieback structures (originally installed to control vibration of the branch lines) was inadequate design. The design process failed to account for the thermal stress and loading conditions on the tieback structures. Excessive RHR system vibration occurs under specific flow conditions where the RHR system is being throttled and when the normal cooldown path is used. However, under an accident scenario, flow is not throttled and the injection path is utilized. Therefore, the conditions for vibration would not occur during accident operation. Corrective actions have been taken to reduce the susceptibility of the RHR system to excessive vibration. The RHR system was monitored during system testing and operation to verify the effectiveness of these corrective actions. A final design change to resolve the system vibration will be implemented by the end of the next refueling outage for Unit 1 and by the end of cycle 14 for Unit 2.
3151999010 | Cook 1, Cook 2 | 04/01/1999 | 03/06/2000 | ML00370164 | <strong>Retraction - Reactor Coolant System Leak Detection System Sensitivity Not in Accordance with Design Requirements</strong><br /><i>Abstract:&nbsp;</i>This revision replaces LER 315199-010-00 in its entirety. On April 1, 1999, with both Units in Mode 5, it was concluded that the containment sump level and flow monitoring subsystem of the Reactor Coolant System (RCS) Leakage Detection System was not consistent with the design recommendations of Regulatory Guide (RG) 1.45 as stated in Technical Specification (T/S) Bases 3/4.4.6.1. As the containment sump level and flow monitoring subsystem was not capable of detecting a change in leakage rate of one gpm in one hour or less, it was considered historically inoperable. This condition was originally reported under 10CFR50.73(a)(2)(I)(B) as a condition prohibited by the plant's T/S. Subsequent investigation has determined that wording in the T/S Bases 3/4.4.6.1 was not clear and was misinterpreted when this issue was initially reported. The Bases stated that the Reactor Coolant Pressure Boundary leakage detection systems are consistent with the recommendations of RG 1.45. However, the Bases statement did not describe the extent to which the leakage detection systems are consistent with the RG. The design for the D.C. Cook Nuclear Plant (GNP) units was not required to meet the recommendations of RG 1.45. Since CNP is not required to meet the recommendations of RG 1.45 and is not committed to RG 1.45, the LER is being retracted.
3151999011 | Cook 1 | 04/07/1999 | 03/14/2000 | ML00369371 | <strong>Air System for Emergency Diesel Generators (EDG) May Not Support Long Term Operability Due to Original Design Error</strong><br /><i>Abstract:&nbsp;</i>In February 1999, during the Expanded System Readiness Review of the Emergency Diesel Generator (EDG) system, the ability of the starting air/control air system to support long term operability of the EDGs was questioned due to the non-safety related design of the compressors. An operability determination was performed which concluded that the EDGs could not maintain long term operability without reliance on the non-safety related, non-seismic starting air compressors, and were therefore inoperable. On April 7, 1999, an ENS notification was made in accordance with 10CFR50.72(b)(2)(i), for an unanalyzed condition with potential safety significance. The apparent cause of the inadequacy of the EDG starting/control air system is original design error. The designers apparently failed to consider that the starting air system provides the control air to the EDG and loss of air could result in shutdown of the engine. After completion of system maintenance and additional review of the Seismic Qualification Utility Group evaluation guidance for seismic adequacy, it was determined that the compressors could be relied upon to perform the function of providing make-up air to the EDGs. Permanent design changes have been developed that will upgrade the starting air system for each EDG, replacing the existing starting air compressors with qualified components. Air consumption and leakage data were evaluated to determine the safety significance of the condition. This condition was determined to have had minimal safety significance with respect to past operation of the plant.
3151999012 | Cook 1, Cook 2 | 04/20/1999 | 03/15/2002 | ML02092053 | <strong>Auxiliary Building ESF Ventilation System May Not be Capable of Maintaining ESF Room Temperature Post-Accident</strong><br /><i>Abstract:&nbsp;</i>This LER supplement is being submitted to include revised information related to the completed root cause evaluation and replaces the previous LER in its entirety. On April 20, 1999, during performance of the Expanded System Readiness Review for the Auxiliary Building Ventilation Systems, it was concluded that there was insufficient assurance that the Engineered Safety Features Ventilation (AES) system is capable of performing its safety and accident mitigation function. This conclusion was based on a preliminary evaluation of numerous identified system deficiencies taken in the aggregate. Specifically, the identified concerns were significant errors in calculations for auxiliary building Engineered Safety Features cubicle temperatures expected during postulated accident scenarios, vulnerability of AES damper control air system modification to single failure; and lack of missile protection for the Component Cooling Water pump area supply fans. Based on the combined effects of these deficiencies, the ability of the AES system to maintain auxiliary building temperatures to within safety-related equipment design temperatures under accident conditions could not be assured. The cause for this condition was the failure to adequately control design basis calculations and supporting documentation. Specifically, documentation and calculations supporting the plant configuration related to Auxiliary Building ESF Ventilation System contained errors, or did not meet current standards for technical attributes. Corrective actions included implementation of analysis and implementation of plant modifications to demonstrate and ensure compliance with design requirements.
3151999013 | Cook 1, Cook 2 | 03/27/1999 | 02/08/2001 | ML01045013 | <strong>Safety Injection and Centrifugal Charging Throttle Valve Cavitation During LOCA Could Lead to ECCS Pump Failure</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1999, during development of an Emergency Core Cooling System (ECCS) thermal hydraulic flow analysis model, Engineering concluded that preliminary hydraulic flow analysis results indicated that the Unit 1 Safety Injection (SI) and Centrifugal Charging (CC) throttle valves could potentially experience cavitation during a Loss of Coolant Accident (LOCA). Cavitation-induced erosion could lead to a pump runout condition and subsequent failure of the ECCS pumps. The analysis also identified that the throttle valves were less open than previously determined. LOCA generated debris could potentially clog the throttle valve, resulting in reduced cooling flow to the reactor core. On May 4, 1999, a 4-hour notification was made to the NRC in accordance with 16CFR50.72(b)(2)(i) for the plant being in an unanalyzed condition, and 10 CFR 50.72(b)(2)(iii)(D) for any event or condition that alone could have prevented the fulfillment a safety function. Similar conditions also exist for the Unit 2 S1 and CC throttle valves. Information regarding safety significance and corrective/preventive actions is being provided in this LER supplement based on completion of the root cause evaluation. The cause for this condition is inadequate original design application of the SI and CC throttle valves. Opportunities to identify this condition were missed during previous evaluations of industry events and regulatory and vendor information. This condition has minimal safety significance because the likelihood of design basis debris being transported to the CC throttle valves is low based on the potential for detrimental debris to flow such a distance at the available flow rates. In the event the CC throttle valves become clogged, the SI and RHR pumps are still available for long-term core cooling following a LOCA. The Unit 1 and Unit 2 SI and CC system throttle valves were replaced with a different valve design. An extent of condition evaluation was performed to identify other systems that utilize manual throttle valves that are subjected to large pressure drops over a long period of operation. No other valves operating under similar conditions were identified as susceptible to cavitation-induced erosion or potential clogging under LOCA conditions.
3151999014 | Cook 1, Cook 2 | 05/21/1999 | 06/18/1999 | 9906220207 | <strong>Requirements of Technical Specification 4.0.5 Not Met for Boron Injection Tank Bolting</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1999, the Engineering Programs group determined that the Boron Injection Tank (BIT) manway bolts were not included in the ISI Program, creating a missed examination for the previous ISI interval. The bolts were being reviewed for surveillance requirements for replacement of two bolts that were identified with no markings by the System Engineer while performing an Expanded System Readiness Review walkdown. Pressure retaining bolting greater than 2 inches in diameter are required to be volumetrically examined once each ISI interval per the 1989 ASME XI Code. The bolting on the Boron Injection Tank manway is 2-1/2 inches in diameter and as such is required to be in the ISI Program. This is reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications (T/S), for the failure to comply with T/S 4.0.5 on the ISI program. This condition was found to exist on both Units. The apparent cause for this event is programmatic weakness. The BIT manway bolts were removed from the ISI Program without proper review, approval and documentation. This occurred in the early 1980's when ISI Program correspondence and documentation was less formal. No immediate corrective actions were required as the Units are currently in Mode 5 making the BIT and associated piping in the current Mode exempt from examination in accordance with the 1989 ASME Section XI Code. The BIT manway bolting has been administratively placed in the ISI Program for the third ISI interval, and will be examined prior to Mode 4. Review of the ISI database did not identify any other Code category C-D bolts that had not been examined during the previous ISI intervals. Engineering has developed an action plan to review the ISI Program for compliance with applicable regulatory requirements prior to restart. Based on the System Engineer walkdown identifying no degraded BIT manway bolts and a work history of no bolt failures, it has been determined that the failure to perform BIT manway bolting examinations for the previous ISI intervals had minimal impact on the safe operation of either Unit.
3151999015 | Cook 1, Cook 2 | 04/08/1999 | 07/01/1999 | 9907090127 | <strong>Radiation Monitoring System Not Tested in Accordance with Technical Specification Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1999, during performance of the Expanded System Readiness Review for the Radiation Monitoring System (RMS), it was identified that the Eberline RMS radiation monitor channel functional test methodology does not meet the intent of Technical Specification (TS) 4.3.3.1, 4.3.2.1.1 and 4.4.6.1.a and Offsite Dose Calculation Manual (ODCM) surveillance requirements. Channel functional testing was determined to be in non-compliance with the TS and ODCM. Subsequent evaluation also identified the RMS calibration procedures to be inadequate. As a result, concerns arose regarding the RMS radiation monitors ability to perform their design function. These conditions have existed since the Eberline radiation monitors were installed in 1982 and are applicable to both units. On April 9, 1999, at 1715 hours, the radiation monitors were declared inoperable. It is recognized that this condition should have been identified as reportable on April 9, 1999, in accordance with 10 CFR 50.73(a)(2)(i)(B) and that this is a late LER submittal. A condition report has been written to address this deficiency. The cause was inadequate implementation of Technical Specification surveillance requirements into plant surveillance procedures. Confidence exists that the monitors would function as designed, since sufficient overlap is provided in existing test procedures which ensures that the entire monitor circuit is tested. In addition, a source check of each monitor channel is routinely performed. Also, offsite dose calculations for routine releases are made using "grab" samples of the process effluents. Based upon this information, this condition has minimal safety implication to the health and safety of the public. On May 9, 1999, channel functional testing of the RMS unit vent effluent radiation monitors (1-VRS-1500 and 2-VRS-2500) was successfully completed and the monitors were declared operable. An extent of condition review is being performed to evaluate the adequacy of channel functional testing for other plant TS instrumentation. Based on the completed evaluation, additional corrective and preventive actions may be developed and included in a supplement to this LER, if required.
3151999016 | Cook 1, Cook 2 | 06/15/1999 | 07/13/1999 | 9907200116 | <strong>Technical Specification Requirements for Source Range Neutron Flux Monitors Not Met</strong><br /><i>Abstract:&nbsp;</i>On June 15, 1999 at 1700 hours EST with both units in Mode 5, the Source Range Nuclear Instrumentation channels on both Units were determined to be inoperable. The Expanded System Readiness Review identified that the Technical Specification (T/S) 3.3.1.1 and T/S 3.9.2 surveillance tests did not verify the Source Range "High Flux at Shutdown" alarm operable. This alarm function is required to be operable during modes 3, 4, 5 and 6. On June 15, 1999 at 2013 hours EST an ENS report was made in accordance with 10 CFR 50.72(b)(2)(iii)(D) for an event that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. This LER is therefore submitted in accordance with 10 CFR 50.73(a)(2)(v)(D), and is also reportable per the requirements of 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by the plant's T/S. The apparent cause of this event is failure to understand the design basis of the plant. Upon declaring the Source Range Nuclear Instrumentation channels inoperable, Operations entered the action statements for T/S 3.3.1.1. Additional compensatory measures implemented by Operations included hourly checks of Source Range instrumentation response and the "High Flux at Shutdown" alarm clear. The surveillance procedures were revised and the "High Flux at Shutdown" alarm was verified operable June 17, 1999 on each Unit. The Source Range "High Flux at Shutdown" alarm and the containment evacuation horns share common circuitry. When the containment evacuation horns are verified operable by surveillance test, the "High Flux at Shutdown" alarm is received but not documented. Although not verified in the past by surveillance test, it is our belief the alarm has been functional. Therefore, there were minimal implications to the health and safety of the public as a result of this event.
3151999017 | Cook 1 | 06/25/1999 | 07/26/1999 | 9907280081 | <strong>Improperly Installed Fuel Oil Return Relief Valve Renders Emergency Diesel Generator Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1999 at 2030 hours EST with both units in Mode 5, the Unit 1 CD Diesel Generator (D/G) was determined to be inoperable after the fuel oil return relief valve was identified as being installed backwards. The correct orientation of this valve is important to ensure that fuel oil is continuously circulated around the D/G fuel oil injector pump barrel for cooling. On June 25, 1999 at 2308 hours EST an ENS report was made in accordance with 10CFR 50.72(b)(2)(iii)(D), a condition that alone could have prevented the fulfillment of the safety function of systems that are needed to mitigate the consequences of an accident and 10CFR 50.72(b)(2)(i), a condition found while the reactor is shutdown that had it been found while in operation, would have resulted in the plant being seriously degraded or in an unanalyzed condition. This LER is therefore submitted in accordance with 10CFR 50.73(a)(2)(v)(D) and 10CFR 50.73(a)(2)(ii)(A). The apparent cause of this condition is personnel error. The valve has been installed backwards since prior to 1986. Inspection of the corresponding valves on the 1AB, 2AB and 2CD D/Gs determined the valves were installed in the correct orientation. Operations entered the action statements for the applicable Technical Specifications upon declaring the Unit 1 CD D/G inoperable. Following replacement of the valve and D/G surveillance testing the 1CD D/G was declared operable on July 7, 1999 at 2243 hours EST. The successful completion of past Technical Specification (T/S) surveillance tests for the Unit 1 CD D/G has verified acceptable engine performance, regardless of the incorrect orientation of this valve. A review of maintenance history did not reveal any abnormal D/G operation that could be attributed to the incorrect valve orientation. Therefore, there were minimal implications to the health and safety of the public as a result of this event. If significant changes are identified as a result of completion of the root cause investigation, an update to this LER will be submitted.
3151999018 | Cook 1 | 06/29/1999 | 07/29/1999 | 9908060217 | <strong>Refueling Water Storage Tank Suction Motor Operated Valves Inoperable Due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On June 29, 1999, during a review of a stress calculation for the Refueling Water Storage Tank (RWST) motor-operated (MOV) suction valves to the centrifugal charging pumps (CCPs), it was determined that the valve yokes may yield under the combined stress of a seismic event and the static, valve closed, stem thrust. Based upon discussions with Engineering personnel, Operations declared the MOVs inoperable at 1540 hours, June 29,1999. Since these MOVs were considered to be incapable of opening during a postulated seismic event, this condition is reportable pursuant to the requirements of 10CFR50.73(a)(2)(ii) as an event that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. Technical Specifications (TS) require one boron injection path from the RWST to the Reactor Coolant System (RCS) to be operable in Modes 5-6 and two boron injection flow paths in Modes 1-4. Since these valves were determined to be inoperable in those modes, this condition is also reportable pursuant to the requirements of 10CFR50.73(a)(2)(i) as an operation or condition prohibited by TS. The apparent cause for this event was inadequate design of the MOVs. This event is applicable to both Units. Compensatory action for the RWST to CCP MOVs for both Units has been taken via a temporary modification to restore operability in anticipation of changing from Mode 5 to Mode 6 to allow removal of fuel from the vessel. Evaluation of the extent of this condition has identified that a change in the method of calculating torque/thrust available from the actuator, initiated by Limitorque Technical Update 98-01, may also impact the operability of the RWST to CCP suction MOVs and other Limitorque MOVs. Operability determinations were performed for those valves required for core offload and reload to establish operability in Modes 5 and 6. Necessary corrective actions or analyses to establish operability for safety-related Limitorque MOVs in Modes 1-4 will be performed prior to entering Mode 4. Based upon the proceduralized capability to establish an ECCS boration flowpath, should the RWST to CCP suction MOVS fail to open on demand, this event had minimal impact on the health and safety of the public.
3151999019 | Cook 1, Cook 2 | 07/16/1999 | 08/16/1999 | 9908240285 | <strong>Victoreen Containment High Range Radiation Monitors Not Environmentally Qualified to Withstand Post-LOCA Conditions</strong><br /><i>Abstract:&nbsp;</i>On May 21, 1999, during an Environmental Qualification (EQ) program self-assessment, preliminary review identified that the containment high range radiation monitors (HRRM) may not be environmentally qualified to withstand the effects of a Loss of Coolant Accident (LOCA). The self-assessment found that D.C. Cook's evaluation of NRC Information Notice (IN) 97-45, "Environmental Qualification Deficiency for Cables and Containment Penetration Pigtails," failed to adequately address the susceptibility of the containment HRRMs to moisture intrusion. IN 97-45 identified that electrical signal cables and connectors found in HRRMs are sensitive to moisture exposure effects, such as from a LOCA or pipe break event. Industry events have identified that moisture intrusion into the cable jacket and connectors has resulted in erratic indication of radiation levels and loss of HRRM function. Based on continued evaluation of the EQ deficiencies, the Unit 1 and 2 HRRMs were declared inoperable on July 16, 1999. The apparent cause was inadequate design control. In response to NRC IN 89-63, a design change to the HRRM system added drainage features to several components. However, the EQ requirement that the HRRM system be leaktight against possible moisture intrusion was not considered. A permanent solution for the susceptibility of the HRRMs to moisture intrusion will be developed to support HRRM operability in Modes 1-4. Options for the permanent solution are currently under review and the method selected will be implemented prior to Mode 4 for each unit. An evaluation of the as-built configuration for other low signal current application EQ equipment is also being performed to identify other electrical equipment that may be susceptible to moisture intrusion due to a LOCA and/or pipe break condition. This evaluation will be completed by September 30, 1999. This condition has minimal safety significance due to the availability of alternate post-accident radiation monitoring instrumentation.
3151999020 | Cook 1, Cook 2 | 07/27/1999 | 08/26/1999 | 9908310153 | <strong>Emergency Diesel Generators Declared Inoperable Due to Inadequate Protection of Air Intake, Exhaust and Room Ventilation Structures from Tornado Missile Hazards</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1999, D.C. Cook Unit 1 was in Mode 5 (Cold Shutdown) and Unit 2 was defueled. During the Expanded System Readiness Review (ESRR) for the Emergency Diesel Generators (EDGs), it was identified that the combustion air intake and exhaust piping, and the room ventilation supply duct for the EDGs do not meet the design criteria specified in the Updated Final Safety Analysis Report (UFSAR). These structures are not protected from tornado-generated missiles. Based upon the determination that the EDGs may not have performed their safety function during a tornado event, they were declared inoperable at 1845 hours EDT. A four hour non-emergency ENS Report was made to the NRC at 2110 hours EDT pursuant to the requirements of 10CFR50.72(B)(2)(i). Subsequent evaluation determined that there was minimal safety significance associated with the identified condition, therefore, the notification under 10CFR50.72(B)(2)(i) is hereby retracted. This event is still reportable, however, in accordance with the requirements of 10CFR50.73(a)(2)(ii)(B), as an event or condition that resulted in the nuclear power plant being outside of its design basis. The apparent cause for this event was the failure to adequately address tornado missile hazards in the original plant design. Compensatory measures in the form of administrative controls and restrictions on plant operations have been implemented until the non-conformance with UFSAR design criteria is resolved. A long term solution for this condition will be completed by Mode 4 for each unit. The operability evaluation performed to evaluate this condition concluded that the EDGs were operable, but degraded, and that the identified condition had minimal safety implications to the health and safety of the public.
3151999021 | Cook 1, Cook 2 | 07/28/1999 | 08/27/1999 | 9909020033 | <strong>Generic Letter 96-01 Test Requirement Not Met In Surveillance Tests</strong><br /><i>Abstract:&nbsp;</i>On July 28, 1999, Unit 1 was in cold shutdown and Unit 2 was shut down in a defueled condition. A review performed of Technical Specification (T/S) surveillance tests for the systems requiring conformance to Generic Letter (GL) 96-01 identified that not all requirements were being met. The surveillance tests for the Solid State Protection System, Engineered Safeguards System and the Emergency Diesel Generator load shed and sequencing circuits did not meet the GL 96-01 test requirements. Failure to test these systems per the requirements of GL 96-01 was determined to be a violation of T/S and reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by T/S. The Control Room Ventilation System is required to meet the requirements of GL 96-01 but there is no T/S requirement to test system response to a high radiation signal. The apparent cause of this event was a failure to understand the full extent of the GL 96-01 requirements when the surveillance tests were initially evaluated, as the initial review was restricted to T/S required surveillances only. A third party review, performed as part of the restart effort, identified these discrepancies and led to an in depth independent review of the GL 96-01 implementation. The independent review has not identified to date any additional discrepancies other than those found during the third party review. Surveillance procedures are being revised or developed to test the nonconforming systems per GL 96-01 test requirements prior to Mode 4 entry for each unit. Surveillance testing is performed on the nonconforming systems. Even though these tests do not meet the complete requirements of GL 96-01, the successful completion of these tests provides confidence that the systems would perform their safety function if called upon to do so. Therefore, the identified conditions had minimal safety implications to the health and safety of the public.
3151999022 | Cook 1, Cook 2 | 06/09/1999 | 03/23/2000 | ML00369603 | <strong>Electrical Bus Degraded Voltage Could Be Too Low For Safety Related Loads</strong><br /><i>Abstract:&nbsp;</i>This LER was revised in its entirety to provide the results of electrical load flow calculations and engineering evaluations performed as corrective actions for LER 315/99-022-00. These evaluations resulted in a better understanding of the degraded grid voltage setpoint basis and the safety related electrical system analytical limit, and new corrective actions. On June 9, 1999, during performance of preliminary electrical load flow analyses, it was thought that the Technical Specifications (TS) 4160 VAC electrical bus degraded voltage lower allowable limit may be too low to ensure adequate voltage for some of the 600 VAC and 120 VAC safety related loads during a design basis accident (OBA). On August 21, 1999, a four-hour prompt notification to the NRC was made, and LER 315199-022-00 was subsequently submitted for a condition that alone could have prevented the fulfillment of the safety function of safety related systems. Additional reviews determined that the degraded voltage relay setpoint is not related to ensuring adequate voltage to safety related equipment during a DBA. However, a postulated sustained worst case offsite degraded grid voltage condition, above the relay setpoint, could have resulted in some electrical equipment terminal voltages below that required for starting or continuous operation during a DBA. The cause of the condition was a lack of understanding of the design and licensing basis, and a lack of control of design basis supporting documentation. These issues are symptoms of a programmatic issue related to inadequate design and licensing basis control. Corrective actions include establishment of an analytical limit for low 4160 VAC bus voltage, plant modifications to improve equipment terminal voltage, a working agreement with system operations to improve grid low voltage conditions when they occur, evaluation of long-term solutions, and a review of the basis for the degraded voltage relay setpoint and time delay. Programmatic design control issues are being addressed through the Donald C. Cook Nuclear Plant Restart Plan and Corrective Action Program. The safety significance of the condition described in this LER is low, due to the small likelihood of this scenario to occur.
3151999023 | Cook 1, Cook 2 | 09/07/1999 | 11/01/2000 | ML00376715 | <strong>Retraction of LER 315/1999-023-00</strong><br /><i>Abstract:&nbsp;</i>This supplement replaces the prior revision in its entirety. On September 7, 1999, with both units defueled, it was concluded that surveillance testing for the Essential Service Water (ESW) system pump response time did not satisfy the Technical Specification (TS) definition for Engineered Safety Feature (ESF) response time. This conclusion was reached based on a footnote to UFSAR Table 7.2-7, "ESF Response Times", which appeared to require system response testing from signal initiation until a specific ESW pump discharge valve position or header pressure was reached. As no surveillance meeting this requirement existed, this condition was considered a missed surveillance and was reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS. Subsequent investigation has determined that the requirements for ESF response time testing of the ESW system are being adequately met by timing system response from actuation of the channel sensor until the pump breaker closes. In addition to the ESF response time testing performed every refueling outage, it was also verified that the stroke time testing of the ESW pump discharge valves is performed on a quarterly basis. As it has been determined that all ESF response time testing requirements of TS for the ESW system are being met, LER 315-99-023-00 is hereby retracted.
3151999024 | Cook 1, Cook 2 | 07/08/1999 | 10/18/1999 | 9910260103 | <strong>Literal Technical Specifications Requirement Not Met By Accumulator Valve Surveillance</strong><br /><i>Abstract:&nbsp;</i>On July 8, 1999, during a review of Technical Specifications (TS) surveillance procedures, it was discovered that TS Surveillance Requirement (SR) 4.5.1.c was not being met by the associated surveillance procedure. SR4.5.1.c requires that power to the RCS accumulator isolation valve motor operator be disconnected by, "... removal of the breaker from the circuit." The surveillance procedure does not meet the literal wording of TS SR 4.5.1.c in that the breaker is opened and maintained in that position rather than being physically removed. This LER is therefore submitted in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. This condition resulted from a misjudgment made in the conversion from the initial D.C. Cook Nuclear Plant (CNP) TS to the Westinghouse Standard Technical Specifications (STS), as described in NUREG-0452. The wording appears to have been adopted from the STS without considering the type of breaker installed for the accumulator isolation valves. A license amendment request will be submitted to change TS SR 4.5.1.c. A comprehensive review of the adequacy of TS surveillance test procedures is being performed as part of Restart Action Plan #0001, "Programmatic Breakdown in Surveillance Testing." The identified condition has no safety significance because power was removed from the accumulator isolation valve control circuit, thereby preventing inadvertent valve operation due to a single failure in the valve control circuitry.
3151999025 | Cook 1, Cook 2 | 09/29/1999 | 10/29/1999 | ML99308028 | <strong>Technical Specification Surveillance Requirements for Auxiliary Building Crane Not Met</strong><br /><i>Abstract:&nbsp;</i>On September 29, 1999, with both units defueled, it was determined that the failure to test an interlock for the East Auxiliary Building Crane was reportable per 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications (TS). A review of the surveillance test for Technical Specification (T/S) 4.9.7.1 had raised the concern that an interlock that prevents a weight of more than 2500 pounds from being lifted to the hook full up position and moved over the spent fuel pool was not being tested in according with T/S. The crane was not in use at the time the concern was raised. The apparent cause of this condition is that a decision was made to not take credit for the interlock on the East crane and to rely on the crane operator to insure that a load greater than 2500 pounds is not carried over the spent fuel pool. Following repairs to the interlock, the T/S surveillance procedure was revised to include verification of the interlock and the surveillance test was successfully performed. The primary purpose of the crane interlocks are to protect against inadvertent action on the part of the crane operator. Crane operator training, plant procedures and travel interlocks provide barriers to inadvertent action. All other interlocks have been functional, and no incidents have occurred where a load greater than 2500 pounds was taken over the spent fuel pool. Therefore, the identified condition had minimal safety implications to the health and safety of the public.
3151999026 | Cook 1, Cook 2 | 10/22/1999 | 08/24/2001 | ML01241001 | <strong>High Energy Line Break Programmatic Inadequacies Result in Unanalyzed Conditions</strong><br /><i>Abstract:&nbsp;</i>This LER is revised in its entirety to include information from the completed root cause evaluation. On October 22, 1999, it was determined that a number of locations in the plant should be considered unprotected from the dynamic and environmental effects of a postulated nearby high-energy line break (HELB) event. An evaluation of the HELB program identified important equipment that was either not qualified for the harsh environment that would result from a HELB in its area, or would have been damaged by jet impingement from a break or crack in high-energy piping near the equipment. Equipment potentially affected includes the auxiliary feedwater (AFVV) pumps, safety and non-safety-related 600 VAC and lower voltage switchgear, emergency diesel generators (EDGs) and associated ventilation systems, component cooling water (COW) pumps, battery trains for the turbine-driven auxiliary feedwater pumps (TDAFP), equipment located near the pressurizer surge line, auxiliary building ventilation equipment located near the chemical volume control system (CVCS) letdown and steam generator (SG) blowdown piping, equipment located near HELB doors, and cables and conduits inside containment. Six of the above conditions were reported in an Emergency Notification System (ENS) phone call made on October 22, 1999, at 1500 hours in accordance with 10CFR50.72(b)(2)(i), of a condition which could have resulted in the nuclear plant being in an unanalyzed condition that significantly compromises plant safety. This LER is submitted in accordance with the corresponding 10CFR50.73(a)(2)(ii)(A) reporting requirement. The root cause of the condition was linked to a programmatic failure, one of inadequate design and licensing basis control. The entire HELB program was evaluated and re-constituted, HELB procedures were revised, and plant modifications were performed. The condition is safety significant because the affected systems are vital for controlling core reactivity, removing core decay heat, controlling reactor coolant inventory, or providing indication of plant parameters. Loss of all auxiliary feedwater pumps or loss of power to vital equipment would significantly challenge the plant.
3151999027 | Cook 1, Cook 2 | 10/27/1999 | 11/29/1999 | ML99340024 | <strong>Underrated Fuses Used in 250VDC System Could Result in Lack of Protective Coordination</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1999, with both units defueled, it was determined that fuses rated only for 250 VAC service were installed in various DC circuit applications without adequate supporting analysis, which could challenge the ability of the DC system in various DC circuit applications without adequate supporting analysis, which could challenge the ability of the DC system to respond to overload conditions and to effectively accommodate the initiating event and a single electrical failure. This condition was initially determined to represent an unanalyzed condition due to a potential for redundant safety equipment to be rendered inoperable by a single active failure, and a 4-hour non-emergency ENS notification was made pursuant to 10CFR50.72(b)(2)(i). Upon further review, it was determined that faults would be cleared without collateral damage to surrounding safety related components, and this issue was more appropriately characterized as a condition which could compromise the protective coordination scheme of the 250 VDC system. As such, this LER is submitted in accordance with 10CFR50.73(a)(2)(ii) for a condition outside the design basis. The cause of this condition is the failure to perform an adequate review of applicable industry experience and vendor supplied information, and to fully understand the design basis of the system. Corrective actions will include replacement of the affected fuses as appropriate. Actions to prevent recurrence relative to the operating experience and design basis have been previously addressed in AEP:NRC:1260GH. Based on our review, it was concluded that faults due to an accident initiating event would be cleared without collateral damage to surrounding safety related components. Postulated impact is restricted to partial loss of the DC safety trains. Based on the results of previous testing conducted by both the fuse manufacturer and DC Cook, and the lack of recorded instances at the plant where the protective coordination failed to function as designed, it is concluded that this condition had minimal safety significance and did not jeopardize the health of safety of the public.
3151999028 | Cook 1 | 12/16/1999 | 01/17/2000 | ML00368100 | <strong>ESF Actuation and Start of Emergency Diesel Generator 1CD During Transformer Maintenance</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1999, at 2052 hours EST with Units 1 and 2 in a defueled condition, reserve power was lost to the Unit 1 "CD" 4kV safeguards busses due to the inadvertent actuation of a protective relay on the Unit 2 Reserve Auxiliary Transformer during a maintenance activity. This caused the start and loading of the Unit 1 CD Emergency Diesel Generator (EDG). At 0030 hours EDT on December 17, 1999, this event was reported in accordance with 10CFR50.72(b)(2)(ii), as a valid actuation of an Engineered Safety Feature. This LER is submitted in accordance with 10CFR50.73(a)(2)(iv), for "any event that resulted in an automatic actuation of any Engineered Safety Feature." The cause of this event was inadequate ownership of the interface between Donald C. Cook Nuclear Plant (CNP) Maintenance Department and the American Electric Power (AEP) Division (transmission and distribution) personnel. Within an hour of the event Spent Fuel Pool Cooling was re-established. Offsite power was restored to the affected busses through the Unit 1 RAT, the Unit 1 CD EDG was secured by 0044 hours on December 17. A Stop Work order was issued for all AEP Division activities performed at CNP, and the transformer maintenance activity was completed under CNP Maintenance supervision. Corrective actions will involve improvements in the CNP/AEP Division interface to clarify that CNP personnel will have primary responsibility for all work performed at CNP by AEP Division personnel. The safety significance of this event was minimal. All equipment required to function during a loss of power to a bus operated as expected, with the minor exception of a lighting transformer which failed to properly strip during the initial load shed. This did not challenge the Emergency Power System capability. Spent Fuel Pool temperature remained stable throughout this event, and the health and safety of the public was not jeopardized.
3151999029 | Cook 1 | 11/18/1998 | 02/25/2000 | ML00368913 | <strong>Lack of Verbatim Compliance Results in Violations of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>This revised LER is submitted to describe an additional reportable condition with the same root cause discovered during the investigation supporting LER 315/99-029-00. On December 17, 1999, it was determined that Donald C. Cook Nuclear Plant (CNP) was not in verbatim compliance with the wording of Technical Specifications (TS) Surveillance Requirement (SR) 4.8.2.3.2.c.2 due to minor surface corrosion identified November 18, 1998, on a terminal connection of the 1-BATT-AB battery. No action was taken to declare the battery inoperable in accordance with TS or to correct the condition. During the investigation, CNP discovered that minor surface corrosion had also been identified on a terminal of the redundant 250 VDC safety related 1-BAIT-CD battery, and that battery acid had corroded through the side of a horizontal battery rack support member for the 1-BATT-AB battery, but the batteries were not declared inoperable in accordance with TS. The above-described conditions were determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), as conditions prohibited by the plant's Technical Specifications. The cause was that CNP believed that compliance with the intent of the TS wording was deemed to be acceptable. Contributing causes were that the weekly battery maintenance procedure did not identify battery corrosion as a TS operability concern, and that TS SR 4.8.2.3.2.c.2 was not current with changes in industry standards. Corrective actions were to declare the 1-BATT-AB battery inoperable, verify that the remaining battery cell terminal connections for Units 1 and 2 were free of corrosion, and increase awareness of the need for verbatim compliance with the TS wording. Future actions are to provide training on Operability Evaluations and TS compliance, revise the battery maintenance procedures, and submit an amendment request for the battery TS SR. There is no safety significance for this event because the 1-BATT-AB and 1-BATT-CD batteries would have been capable of performing their safety related functions even with the surface corrosion on the terminal lugs and the hole in the rack.
3151999030 | Cook 1 | 10/13/1999 | 01/12/2000 | ML00367686 | <strong>Improper Use of Clarifications Results in Violation of Two Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>As a corrective action to LER 315/99-004-01, a review of all Technical Specifications (TS) clarifications was performed to determine if any contained guidance deviating from the letter of the TS. As a result of that review, 2 clarifications were identified. These clarifications dealt with Low Temperature Overpressure (LTOP) requirements when the reactor vessel head is on but not fastened, and operability of the 4KV bus undervoltage relays when the associated Emergency Diesel Generator is inoperable. There is evidence that these clarifications were used in the past, it was determined that their use constituted a condition reportable under 10 CFR 50.73 (a) (2) (i) (B), for any operation or condition prohibited by the plant's Technical Specifications. The root cause of this condition was determined to be the continued use of the past industry practice of TS interpretation and compliance with the intent of the TS. The remaining TS clarifications will be cancelled and dispositioned by TS amendment, TS Bases change or other means, as appropriate. To prevent recurrence, the TS clarification program will be eliminated. A policy memo has been issued by Regulatory Affairs to all department managers and Regulatory Affairs personnel describing the need to comply with both the letter and the intent of TS. The safety significance of the instances where the TS clarifications were used was evaluated. The TS clarification involving LTOP was found to meet the intent of the TS requirement although not the word. Both events involving the undervoltage relay clarification were of extremely short duration and redundant equipment was available. Therefore, it has been concluded that the use of these clarifications had minimal safety significance.
3151999032 | Cook 1, Cook 2 | 12/17/1999 | 01/18/2000 | ML00367769 | <strong>Failures to Comply with Technical Specification 4.0.5 Identified by Inservice Testing Program Assessment</strong><br /><i>Abstract:&nbsp;</i>On December 17, 1999, further examples of failure to comply with Technical Specification (TS) 4.0.5 that were identified during the extent of condition investigation being conducted for LER 315/98-057-00 were determined to be reportable as individual failures to comply with TS 4.0.5. The examples include failure to verify stroke timing of valves, failure to include active check valves in the IST program, and failure to verify valve local/remote position indications. The systems in which these examples were found include the Spent Fuel Pit Cooling/Cleanup, Auxiliary Feedwater, Component Cooling Water, Residual Heat Removal, Reactor Coolant Pump Seal Water Injection, and Containment Purge System. The extent of condition was being conducted as part of the Inservice Testing (IST) Program Assessment, as discussed in the previously cited LER. The further examples of failure to comply with TS 4.0.5 are reportable as conditions prohibited by TS pursuant to the requirements of 10CFR50.73(a)(2)(i)(S).<br /><br /> The causes of these conditions have been determined to be a lack of knowledge of the American Society of Mechanical Engineers (ASME) Codes, licensing and design basis of the plant, and ineffective scoping and implementation of the IST program. Each of the specific examples will be resolved prior to the respective system being returned to operable status. Past testing and/or operation of the valves have not indicated any failure or malfunction which would have caused the valves not to have performed their intended function.
3161999001 | Cook 2, Cook 1 | 06/10/1996 | 03/22/2005 | ML05089034 | <strong>Supplemental LER for Degraded Component Cooling Water Flow to Containment Main Steam Line Penetrations</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1999, during an engineering review of the Unit 2 Containment System, it was identified that power operation was permitted in June 1996 with degraded Component Cooling Water System (CCW) flow to the coolers for containment penetrations 2-CPN-3 and 2-CPN-4. The main steam lines for steam generators 22 and 23 pass through these penetrations. Operating with the degraded CCW to these coolers may have resulted in excessive thermal stress on the penetration sleeves/liners. This event was reported via a 4-hour Emergency Notification System (ENS) report on February 27, 1999, in accordance with the reporting requirements of 10 CFR 50.72(b)(2)(i), that were in effect at the time the event was discovered, as an event of being in an unanalyzed condition that significantly compromises plant safety. The initial LER was submitted as an event or condition that resulted in the nuclear power plant being in a condition that was outside the design basis of the plant. This LER supplement reports the final results of the investigation of this event, including root causes, additional analysis, and corrective actions. The causes of this event were deficiencies in the processes for understanding and controlling the design and licensing documents of the penetration coolers and a less than adequate process for initiation, review, and approval of Operability Determinations. Additional analyses have been performed which determined that the penetrations, including the concrete, sleeves, and liner, were not degraded due to increased local temperatures which resulted from the coolers being out of service. Corrective actions taken include clarification of the UFSAR text that describes the coolers, improvements to the Operability Determination process, a change to the design and licensing basis for the containment concrete to permit local temperatures up to 200 degrees F, and returning all of the main steam penetration coolers to service.
3161999002 | Cook 2 | 04/15/1996 | 05/10/1999 | 9905170112 | <strong>Requirements of Technical Specification 4.0.5 Not Met Due to Improperly Performed Test</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1996, with Unit 2 in Mode 6, the containment sump pump discharge piping at containment penetration 2-CPN-41 was pressurized for approximately one minute to perform an Inservice Inspection (ISI) system functional pressure test. ASME Code, Section XI required the line to be pressurized for at least ten minutes for the test. At the time, the one-minute test was considered an acceptable alternative to the ten-minute test. On April 9, 1999, this was identified as an incorrect test method, which did not meet the requirements of the surveillance. Since the requirements of Technical Specification 4.0.5 were not met, this event is reportable under 10 CFR 50.73(a)(2)(i)(B), as an operation prohibited by the plant's Technical Specifications. The apparent cause of the event was an incorrect interpretation of the ASME Code. No immediate corrective actions were required as the unit is currently in Mode 5 and containment integrity is not required. The Appendix J testing for the penetration piping will be completed prior to restart of the unit. Procedures are being revised to strengthen the ISI program and the interface with the program coordinator. Based on the satisfactory results of Appendix J testing performed on the same penetration and a work history of no leakage, it has been determined that there is no safety significance associated with the incorrectly performed test. The root cause investigation for this event has not been completed. If significant changes to the LER are needed as a result of the completion of the investigation, a supplemental report to this LER will be submitted.
3161999003 | Cook 2 | 09/26/1999 | 09/29/2000 | ML00375759 | <strong>Fuses Not Installed for Cable Passing through Containment Penetration</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1999, during an inspection of a Unit 2 electrical cabinet, maintenance personnel were unable to find fuses for the lighting transformer power cable that passes through containment penetration 2-CEP-3P3. The fuses and the associated fuse holder were within the scope of a plant modification that was installed in 1979. The modification provided redundant fault protection for containment electrical penetrations. Without the fuses, penetration 2-CEP-3P3 was vulnerable to damage by fault currents if a single circuit breaker failed during certain electrical faults. This LER is therefore submitted in accordance with 10 CFR 50.73(a)(2)(ii)(B), to report a condition found while the reactor is shut down, that, had it been found while the reactor was in operation, would have resulted in the nuclear power plant being outside its design basis. This LER supplement is being submitted to include the results of the evaluation of the safety significance. The cause of the failure to install the fuses could not be determined. The modification package, which should have installed the fuses to provide redundant fault protection for containment electrical penetrations, was reviewed, and there was no apparent requirement to verify installation of the fuses. This may have contributed to the failure to install the fuses. Fuses for the protection of penetration 2-CEP-3P3 were installed prior to the unit's return to service in June, 2000. Assuming the worst case location of a fault and failure of the upstream breaker to trip, some damage to the penetration could be postulated. The likely failure mode would be for the seals on the penetration feed-through assembly to fail. This potential loss of containment integrity would likely be limited to the feed-through assembly itself. The combination of events required to present a challenge to containment integrity through this penetration have a low probability of occurrence. It was estimated that, in the unlikely event that a release did occur, the dose consequences would remain within regulatory limits. Therefore, the safety significance of this condition is considered low.
3171999001 | Calvert Cliffs 1, Calvert Cliffs 2 | 01/18/1999 | 02/17/1999 | 9902230314 | <strong>Containment Penetration Room Violation System Inadequate Isolation Boundaries</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1999, during review of scheduled maintenance on the Penetration Room Exhaust Ventilation System, Operations personnel identified that the condition of the train under maintenance could potentially degrade the safety function of the other train. Specifically, dampers used to isolate the out-of-service exhaust filter unit for maintenance or testing, would open upon receipt of a containment isolation signal, cross-connecting the out-of-service train to the in-service train. This potentially challenges the design function of the Penetration Room Exhaust Ventilation System, as unfiltered-bypassed air is circulated through the plant vent. This condition has existed since the initial licensing of Unit 1 and Unit 2. This event resulted from the selection of inadequate maintenance isolation boundaries. The maintenance activity was cancelled and a station Issue Report was initiated. A formal Root Cause Analysis is in progress.
3171999002 | Calvert Cliffs 1 | 04/01/1999 | 05/25/1999 | 9905280232 | <strong>Lost Radioactive Sources Due to Inadequate Control</strong><br /><i>Abstract:&nbsp;</i>On April 1, 1999, during a quarterly inventory of radioactive sources, four 100 microcurie Cesium-137 sources could not be located. Unit 1 was in Mode 1, operating at 100 percent power, and Unit 2 was shut down in Mode 5 for refueling at the time the sources were discovered missing. The four sources were purchased from Victoreen, Incorporated, and have decayed to approximately 72 microcuries each, for an aggregate quantity of 288 microcuries Cesium-137. Radiation levels are calculated to be 0.3 millirem per hour at one foot for each source; or, 1.2 millirem per hour at one foot for all four sources together. A search was immediately started for the missing sources. All probable locations and exit points were searched and investigated. The sources have not been found.
3171999003 | Calvert Cliffs 1, Calvert Cliffs 2 | 07/01/1999 | 07/30/1999 | 9908030092 | <strong>Use of an Unapproved Methodology Puts Plant Outside of its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1999, during a discussion with Nuclear Regulatory Commission inspectors, plant staff recognized that an "unapproved" methodology was used to allow the Control Room Emergency Ventilation System to remain operable in an "accept-as-is" condition, without processing an appropriate licensing action. Use of a methodology different than that explicitly approved in the Updated Final Safety Analysis Report, placed the plant in a condition outside of the design basis of the plant. Prior to testing control room inleakage on November 21, 1997, an existing calculation was used to show the system was operable. This calculation allowed an increase of current design basis inleakage from 910 scfm to 8300 scfm. However, improved, but less conservative, atmospheric dispersion coefficients were used. Corrective actions include providing written guidance and training that, when using methodologies different than those approved in the Updated Final Safety Analysis Report, formal changes to the licensing basis must be processed when the condition will be "accepted as-is" and required notifications must be made.
3171999004 | Calvert Cliffs 1 | 07/24/1999 | 08/23/1999 | 9908260087 | <strong>Reactor Trip due to Main Transformer Bushing Flashover</strong><br /><i>Abstract:&nbsp;</i>At 1438 on July 24, 1999, Unit 1 tripped from 100 percent power due to electrical arcing (flashover) across the No. 12 Main Transformer (U-25000-12) A-phase 500 kV bushing. The main generator output breaker opened, and the Unit 1 Reactor tripped on loss of turbine load. A thunderstorm was in progress at the time of the Unit trip with high winds and heavy rain. Witnesses observed a lightning strike near the affected transformer. Lightning apparently struck the A-phase 500 kV transmission line near the transformer, increasing the electrical potential beyond the insulating capabilities of the bushing, creating an electrical arc around the bushing. The arcing across the A-phase bushing affected the A-phase current flow. Protective relays sensed the abnormal condition, and opened two Switchyard Breakers (552-22 and 552-23), the Generator Field Breaker, and the Exciter breaker. Operators responded appropriately and plant systems functioned as designed. The plant was brought to a safe shutdown condition.
3171999005 | Calvert Cliffs 1, Calvert Cliffs 2 | 07/20/1999 | 08/23/1999 | 9908260099 | <strong>Corrosion Behavior and Onset of Oxide Spalling of High Duty Fuel</strong><br /><i>Abstract:&nbsp;</i>On July 20, 1999, inspections performed on fuel assemblies discharged at the end of Unit 2 Cycle 12 (after two cycles of irradiation) indicated that some fuel rods had an oxide layer that was thicker than predicted. In some cases, early stages of oxide spallation were observed where none was anticipated. These phenomena could affect the performance of the cladding during certain accident conditions. Improved plant performance has resulted in longer cycles (more Effective Full Power Days), and, subsequently, the fuel has been pushed to higher duties than in the past. Corrosion has typically been correlated to burnup. It has become evident that corrosion is better correlated to fuel duty. The effect of the onset of spallation has not been analyzed and needs to be addressed. Neither Unit is currently operating with fuel that is likely to be in this condition, but this condition is expected to exist later in Unit 1 Cycle 14 and Unit 2 Cycle 13.
3171999006 | Calvert Cliffs 1 | 09/22/1999 | 10/22/1999 | 9910270216 | <strong>Inadequate Electrical Current Determination Leads to Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On September 22 1999, at 9:08 a.m., Calvert Cliffs Unit 1 was manually tripped from 100 percent power in response to loss of main feedwater, which occurred when a circuit breaker supplying two cross-tied non-vital 480 volt motor control centers (MCCs) tripped on overload and de-energized the lube oil pumps for both main feedwater pumps. Water level was maintained in both steam generators by the auxiliary feedwater system. The MCCs had been cross-tied to perform maintenance on one of the MCCs feeder breakers. The electrical loading from both MCCs exceeded the trip rating of one feeder breaker because the evolution was performed at power without first having shed the excess loads. Operators responded appropriately to the loss of feedwater and plant systems functioned as designed after the trip. The root causes of this event include less than adequate trip risk assessment and weaknesses in the electrical maintenance training program. Corrective actions include evaluating the trip risk assessment process for enhancements and assessing the training needs of electricians to improve knowledge levels in the area of electrical theory application.
3201999001 | Three Mile Island 2 | 01/12/1998 | 02/05/1999 | 9902190161 | <strong>Flood Barriers Breached Between Turbine Building and Control Building Area Due To an Inadequate Prior Inspection</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1999 at about 3:00 PM, a member of the Independent Onsite Safety Review Group was inspecting repairs made to flood barriers in the wall between the Unit-2 Turbine Building and Control Building Area. These repairs had been made as corrective actions to the event reported in Licensee Event Report 05000320/98-001. Three wire chases through the wall were found that were not completely sealed. This condition is contrary to the Post Defueling Monitored Storage (PDMS) Safety Analysis Report (SAR) section 7.1.4.2.f, which states that all openings that are potential leak paths into the Control Building Area are sealed. Between January 13, 1999, and January 27, 1999, work crews re-inspected all penetrations in the affected wall and repaired the three identified openings with seals capable of withstanding the head of water of the maximum probable flood elevation of 311 feet. The root cause of this event was human error caused by inadequate communication during the performance of the prior inspections of June 16 through June 19, 1998. The corrective actions were to seal the three penetrations found to be not in accordance with design specifications and to inspect all penetrations in the wall to determine whether any others were overlooked in the prior inspections. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
3211999001 | Hatch 1 | 04/12/1999 | 05/10/1999 | 9905170097 | <strong>Drawing Errors Result in Loss of Scram Valve Air Header Air Pressure RPS Actuation</strong><br /><i>Abstract:&nbsp;</i>On 04/12/1999 at 1015 EDT, Unit 1 was in the Cold Shutdown mode with refueling outage activities in progress. At that time, a full reactor protection system actuation occurred on high water level in the scram discharge volume. At 1030 EDT, Operations personnel discovered that valve 1P52-F501 had been closed under Clearance 1-99-462. Closing this valve isolated the air supply to the scram valve air header. This allowed the header to depressurize resulting in the scram discharge volume vent and drain valves closing and the control rods traveling from the full-in to the overtravel position. The control rod movement placed water in the scram discharge volume causing it to fill and producing a reactor protection system actuation on high water level. Because the control rods had already moved to the overtravel position, the reactor protection system actuation did not result in further rod movement. This event was the result of inadequate plant drawings. The drawings personnel used to generate Clearance 1-99-462 did not indicate that closing valve 1P52-F501 would isolate the air supply to the scram valve air header. Consequently, personnel generating, reviewing, and approving the clearance had no way of knowing that closing valve 1P52-F501 would isolate and depressurize the scram valve air header. Operations personnel re-opened valve 1P52-F501 and restored air to the scram valve air header on 04/12/1999. Plant drawings have been revised to show that valve 1P52-F501 provides air to the scram valve air header.
3211999002 | Hatch 1 | 04/29/1999 | 05/24/1999 | 9905280245 | <strong>High Pressure Coolant Injection System Inoperable Due to Problems With Barometric Condenser</strong><br /><i>Abstract:&nbsp;</i>On 04/29/1999 at 0510 EDT, Unit 1 was in the Run mode at a power level of approximately 446 CMWT (16 percent rated thermal power). At that time, the High Pressure Coolant Injection (HPCI) system was rendered inoperable when the time allotted to perform Unit 1 Technical Specifications Surveillance Requirement 3.5.1.8 expired. Surveillance Requirement 3.5.1.8 requires the HPCI system to be tested within 12 hours of reaching adequate reactor steam pressure and flow. Adequate reactor steam pressure and flow were reached on 04/28/1999 at 1710 EDT. However, the required test was not completed because of high water level in the vacuum tank of the HPCI system barometric condenser. Although high water level in the tank does not make the HPCI system inoperable, this condition prevented the successful completion of the test required by Surveillance Requirement 3.5.1.8 within the allotted 12-hour period. Per the requirements of Unit 1 Technical Specifications Surveillance Requirement 3.0.1, failure to perform the surveillance within the specified frequency made the HPCI system inoperable. This event was the result of high vacuum in the HPCI system vacuum tank. The high vacuum reduced the vacuum tank condensate pump suction pressure thereby reducing its flow rate. The level in the tank increased as the tank input rate exceeded the reduced pump flow rate. Personnel lowered tank vacuum and successfully completed HPCI system testing on 05/02/1999 at 2019 EDT. The HPCI system was returned to an operable status on 05/02/1999 at 2100 EDT.
3211999003 | Hatch 1 | 05/07/1999 | 06/01/1999 | 9906080290 | <strong>Incorrect Performance of Equipment Clearance Leads to Scram on High Reactor Pressure</strong><br /><i>Abstract:&nbsp;</i>On 05/07/1999 at 0822 EDT, Unit 1 was in the Run mode at a power level of 1465 CMWT (53 percent rated thermal power). At that time, the Unit 1 reactor automatically shut down when the Main Turbine control valves closed, resulting in a high reactor pressure condition. Reactor water level decreased due to void collapse from the rapid power reduction, resulting in receipt of a Group 2 Primary Containment Isolation System signal and closure of Group 2 valves as designed. Level reached a minimum of approximately 32 inches below instrument zero (126 inches above top of active fuel) before being restored automatically by the Feedwater Level Control system. No emergency cooling systems actuated nor were any required to actuate to restore or maintain reactor water level. Pressure reached its maximum value of approximately 1083 psig at the time of the shutdown, decreasing thereafter until the main turbine bypass valves automatically controlled pressure. The peak pressure was below the Main Steam Safety/Relief Valve actuation setpoints; thus, no Safety/Relief Valve operation was required or occurred. This event was caused by the manual closure of a valve common to the pump discharge of both loops of the Main Turbine ElectroHydraulic control system, which in turn caused a loss of system pressure to the Main Turbine Control Valves, resulting in their automatic closure. A plant equipment operator performed the manual valve closure in error as part of an equipment clearance evolution preceding routine changeout of an EHC discharge filter. Corrective actions included personnel discipline and procedure improvement.
3231999001 | Diablo Canyon 2 | 03/31/1999 | 04/30/1999 | 9905060087 | <strong>Voluntary Entry Into Technical Specification 3.0.3 to Open the Containment Recirculation Sump Sensor Hatch to Verify Level Transmitter Operability</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1999, at 1412 PST, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, Technical Specification (TS) 3.0.3, "Limiting Condition For Operation Applicability," was voluntarily entered to open the containment recirculation sump sensor hatch to remove the sensor assembly for narrow range level transmitter (LT) 940. On March 31, 1999, at 1414 PST, TS 3.0.3 was exited after the assembly was removed and the hatch closed. On April 7, 1999, at 1508 PDT, with Unit 2 in Mode 1 at 100 percent power, TS 3.0.3. was entered again to reinstall the sensor assembly. On April 7, 1999, at 1518 PDT, TS 3.0.3 was exited after the assembly was reinstalled and the hatch closed. During the Unit 1 ninth refueling outage, PG&E determined both narrow range sump level channels were out of tolerance because of degraded power supply electrolytic capacitors. Based on the Unit 1 condition, the Unit 2 containment recirculation sump sensor hatch was opened to remove the 2-LT-940 sensor assembly for calibration. The electrolytic capacitors for 2-LT-940 were replaced. The electrolytic capacitors for all narrow range sump LTs will be replaced on a recurring frequency.
3231999002 | Diablo Canyon 2 | 10/04/1999 | 11/24/1999 | ML99340027 | <strong>Reactor Fuel Assembly Damage Due to Baffle Jetting</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1999, with Unit 2 in Mode 6 (Refueling), during the ninth refueling outage1 PG&E identified two damaged reactor fuel assemblies. Initial inspection revealed that assembly V03 (location L-15) contained two damaged rods and assembly V02 (location E-1) contained three damaged rods. On October 7, 1999, PG&E reviewed video tapes of fuel inspections taken during the Unit 2 eighth refueling outage. The tapes indicated that assembly UI 3 (location L-15 during the previous fuel cycle) contained one damaged fuel rod. PG&E discovered the damage to assemblies V02 and V03 during an off load foreign materials check. Damage to assembly U13 was discovered as a result of further investigation. PG&E and Westinghouse attributed the cause of fuel damage to fretting due to baffle jetting. Unit 1 is not expected to experience baffle jetting due to a different baffle configuration. Fuel rod clips were installed on eight fuel assemblies at locations with the same baffle configuration as locations E-1 and L-15. Loose parts and reactor core integrity evaluations were completed and indicated no adverse effects to the reactor coolant system components or fuel. As a precautionary measure, fuel assemblies in locations susceptible to baffle jetting will be inspected for wear and degradation during the next Unit 2 refueling outage. The continued use of fuel clips will be evaluated based on the results the inspection.
3231999003 | Diablo Canyon 2 | 10/26/1999 | 11/26/1999 | ML99340027 | <strong>Entry Into Technical Specification 3.0.3 Due to Voiding in the Emergency Core Cooling System Caused by Inadequatye Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On October 26, 1999, at 0015 PDT, with Unit 2 in Mode 3 (Hot Standby), at 0 percent power, Technical Specification (TS) 3.0.3 was entered due to voiding in the emergency core cooling system piping. Approximately 0.9 ft3 of air was identified by the ultrasonic test (UT) monitor near Valves 8807 NB. The void was vented and TS 3.0.3 was exited on October 26, 1999, at 0040 PDT. A review of the temporarily installed UT monitor tape indicated that the void formed on October 25, 1999, at 2127 PDT. Therefore, the plant was in a TS 3.0.3 condition for approximately 3 hours 13 minutes. On November 16, 1999, at 1321 PST, PG&E made a 4-hour nonemergency notification to the NRC in accordance with 10 CFR 50.72(b)(2)(iii)(D). The void was caused by the introduction and transport of air during outage activities. Fill and vent procedures did not specifically address filling and venting sections of excess letdown piping. The temporary UT monitoring equipment will remain functional during applicable parts of outages and for an appropriate time after outages to monitor the ECCS for voiding. The monitoring equipment will remain in use until PG&E is confident that it is no longer needed. Additional steps have been taken to observe the installed monitor on a more frequent basis during the transition from refueling outages to operation.
3231999004 | Diablo Canyon 2 | 12/23/1999 | 01/24/2000 | ML00367955 | <strong>Technical Specification 3.4.2.2 Not Met Due to Pressurizer Pressure Safety Valves As Found Pressure Setting Low</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1999, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, PG&E determined that a violation of Technical Specification (TS) 3.4.2.2, "Safety Valves," occurred for the pressurizer safety valves (PSVs) removed for offsite testing during the Unit 2 ninth refueling outage (2R9). The three PSVs were replaced with pretested spares during 2R9 and sent offsite for lift setting verification in accordance with plant procedures. The three PSVs were identified with as-found lift settings lower than that specified in the TS but enveloped by the Final Safety Analysis Report Update analyzed conditions. PG&E believes the cause of the PSV as-found lift settings being outside the TS tolerance is random setpoint spread, an inherent characteristic of this type of valve. The PSVs were reset to the required tolerance using Surveillance Test Procedure M-77, "Safety and Relief Valve Testing." PG&E has previously enhanced the PSV maintenance activities and offsite testing procedures resulting in improved performance of the PSVs. PG&E believes that the PSVs continue to perform within their design and analysis requirements for Diablo Canyon Power Plant and no additional corrective actions are required.
3241999001 | Brunswick 2 | 03/17/1999 | 04/16/1999 | 9904210051 | <strong>Reactor Core Isolation Cooling System Inoperable Due to Valve Packing Leak</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1999, at approximately 0336 hours, during valve operability testing of the Reactor Core Isolation Cooling (RCIC) system Steam Supply Outboard Isolation Valve (2-E51-F008), the leakage from the stem packing increased significantly. The steam leak was isolated by closing the Steam Supply Inboard Isolation Valve (2-E51-F007) and the RCIC system was declared inoperable. At the time of the event, Unit No. 2 was operating at rated power. Inspection of valve 2-E51-F008 identified degraded valve stem packing, but no evidence of mechanical problems with the valve. The packing material was replaced and the valve reassembled. The valve was tested and the system returned to service on March 18, 1999, at approximately 0542 hours. The cause of the event is attributed to inadequate packing compression on the live-load packing, which resulted in the valve 2-E51-F008 steam leak/packing failure. During the inspection, checks of the gland nut torque indicated that the torque was close to the "as left" value to which the torque was adjusted previously in February 1996. Packing enforcer testing indicated that the previous value did not provide the desired packing compression. Other valves susceptible to this condition have been identified and are scheduled to be checked/adjusted. The applicable maintenance procedure will be revised to provide a minimum packing load to ensure adequate packing compression. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(B), as a condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat.
3241999002 | Brunswick 2 | 03/29/1999 | 04/28/1999 | 9904300161 | <strong>Reactor Trip Due to Turbine Vibration Instrumentation Failure</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1999, at 0837 hours, an invalid high vibration signal from a failed main turbine bearing vibration detector caused a main turbine trip which resulted in a Unit No. 2 reactor trip and subsequent Primary Containment Isolation system Group 2, 6, and 8 valve isolations/signals being initiated. Safety Relief Valves (SRVs) "F" and "G" lifted and immediately closed. At the time of the event, Unit No. 2 was operating at 97 percent of rated power. The SRV lifts were evaluated and it was determined that the momentary lifts were to be expected based on the impact of the transient on the reactor/steam lines. The cause of the event is attributed to failed electrical connections on the vibration detector for the No. 9 main turbine bearing. The detector failure caused the invalid high vibration signal which initiated the event. Checks of bearing temperatures, the vibration behavior of adjacent bearings, and bearing oil samples were made to ensure that an actual vibration problem did not exist. The vibration detector was replaced and the other detectors for the turbine bearings were checked and replaced as applicable. Monitoring necessary to detect vibration instrumentation failure precursors is being established. A multi-disciplined team is being formed to develop and implement options to eliminate the single point turbine high vibration trip. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv), as a condition that resulted in the actuations of engineered safety features including the Reactor Protection system.
3241999003 | Brunswick 2 | 04/18/1999 | 05/18/1999 | 9905280169 | <strong>Inadequate Augmented Inservice Weld Inspection</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1999, with Unit 2 in Mode 4 at 0 percent of rated thermal power, Carolina Power & Light (CP&L) Company determined that six welds, associated with 4 inch branch connections to 28 inch American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code Class I piping, and one weld, associated with a 6 inch branch connection to 20 inch ASME Code Class I piping had not been properly inspected. These welds are inspected in accordance with the ASME Boiler and Pressure Vessel Code, Section XI and per the guidance of Generic Letter 88-01, "NRC Position On IGSCC In BWR Austenitic Stainless Steel Piping," dated January 25, 1988. These inspections are augmented inspection requirements of the Brunswick Steam Electric Plant's Inservice Inspection (ISI) program and, at the time the inadequate inspections were performed, were a requirement of Technical Specification 4.0.5.f for Unit 2. As such, this condition is being reported, in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. The root cause of this condition is attributed to incorrect assumptions, on the part of non-destructive examination (NDE) personnel, regarding the configuration of the branch connection welds. Corrective actions include inspection of the affected welds during the current Unit 2 refueling outage and ISI program enhancements.
3241999004 | Brunswick 2 | 05/02/1999 | 06/01/1999 | 9906030036 | <strong>Reactor Recirculation System Bypass Valve Inoperability Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 2, 1999, based on the results of inspection of the internals of the "B" loop Reactor Recirculation system pump discharge bypass valve 2-B32-F032B, it was determined that the valve had previously been inoperable for an extended period. The Low Pressure Coolant Injection (LPCI) "B" subsystem is considered to be inoperable in accordance with Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.5.1 when valve 2-B32-F032B is inoperable and open. Due to previous extended periods of LPCI "B" inoperability, LCO 3.5.1 Required Action Completion Times were exceeded. The cause of the event is attributed to a combination of valve internal component tolerances and a missing wedge spring. This established a condition in which pre-wedging could occur, causing the valve electrical circuit to trip on thermal overloads before the valve could complete its full stroke in the closed direction. Valve 2-B32-F032B and its motor-operated actuator were inspected, rebuilt, and tested in accordance with plant procedures, prior to returning the valve to service. Maintenance histories of valve 2-B32-F032A and the two corresponding valves on Unit No. 1 were reviewed to verify that there were no similar failures. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition that resulted in operation prohibited by the plant's TS.
3241999005 | Brunswick 2 | 05/11/1999 | 12/08/1999 | ML99350002 | <strong>Safety Relief Valves Exceeded Technical Specification Setpoint Limits</strong><br /><i>Abstract:&nbsp;</i>During the Brunswick Steam Electric Plant (BSEP) Unit No. 2 Refueling Outage (i.e. B214R1), eleven safety relief valves (SRV's) were removed for set pressure testing and recertification. Technical Specification (TS) 3.4.3 requires 10 SRVs to be operabel with lift settings within +/- 3% of their lift setpoints. On May 11, 1999, the results of the ststing performed by Wyle Laboratories identified that two of the eleven valves were found to lift at pressures outside the limits. Specifically, the as-found lift settings for safety relief valves 2-B21-F013D and 2-B21-F013E were determined to be in excess of the setpoint values allowed by the TSs by +3.7% and +3.2% respectively. The SRV pilot valve assemblies were replaced with certified spares prior to startup of Unit 2. The cause of the setpoint drift for 2.B21-F012E is attributed to valve disassembly and reassembly practices. this failure mechanism was previously identified in LER 1-98-003. The safety significance of this condition is considered minimal. Although the SRV setpoint limits required by the TS were exceeded, the condition is bounded by General Electric (GE) analysis, "Evaluation of SRV Setpoint Drift at Brunswick Steam Electric Plant Units 1 & 2," dated March 1986. This condition is being reported in accordance with the requiremrnts of 10 CFR 50.73 (a)(2)(vii)(D) as a common cause failure in a system designed to mitigate the coinsequences of an accident.
3241999006 | Brunswick 2 | 06/28/1999 | 07/28/1999 | 9907300191 | <strong>Automatic Reactor Shutdown Due to Condenser Low Vacuum Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1999, with Unit 2 operating at rated power, an automatic main turbine trip occurred due to low condenser vacuum. Consequently, as designed, the turbine trip resulted in actuation of the Reactor Protection system (RPS) trip logic and subsequent reactor shutdown. Reactor vessel water level decreased below the low level 1 setpoint (i.e., 166 inches of water) resulting in Primary Containment Isolation system Group 2 (i.e., drywell floor and equipment drains), Group 6 (i.e., containment atmospheric control valves), and Group 8 (i.e., Residual Heat Removal system shutdown cooling valve) isolation signal actuations. The affected systems functioned as expected. The low condenser vacuum condition occurred due to successive trips of the circulating water intake pumps (CWIP's). Silt accumulation clogged the circulation water intake pump traveling screens, causing a high differential pressure condition across the screens, and subsequent pump trips. Corrective actions include review of operational guidance and development of an operational strategy to mitigate CWIP trips, evaluation of intake canal dredging and depth profile to determine adequacy, and review of the period of vulnerability for CWIP trips. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(iv) in that the condition resulted in the automatic actuation of Engineered Safety Feature systems including the RPS.
3241999007 | Brunswick 2 | 07/14/1999 | 08/13/1999 | 9908170086 | <strong>Overlapping Safety System Outages Results in Operation Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>At 1030 on July 14, 1999, with Unit 2 operating at rated power, the 2A Core Spray (CS) system was removed from service for scheduled maintenance. This was concurrent with the outage for the Emergency Diesel Generator (EDG) #1 which had continued beyond it's scheduled completion time. In this case, the redundancy of CS and Residual Heat Removal (RHR) systems and this relationship to the Technical Specifications (TS) involved were not recognized by the licensed operators involved in authorizing the start of the 2A CS system outage. TS LCO 3.8.1 Action D.2 requires declaring the "required features," supported by the inoperable EDG inoperable within 4 hours, when the redundant features are inoperable. Based on the redundancy of CS and RHR systems, the RHR 2A Low Pressure Coolant Injection (LPCI) loop was required to be declared inoperable by 1430 on July 14, 1999. This condition required entry into TS LCO 3.0.3, but as the condition was not identified, no action was taken within one hour as required by the specification. At 1850, on July 14, 1999, the 2A Core Spray was declared operable. This made the 2A LPCI loop operable and TS LCO 3.0.3 was exited. This event is attributed to inadequate training/communications related to the implementation of the Improved TSs. Training is being provided to Licensed Operators. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(i) in that the condition resulted in operation prohibited by TSs.
3241999008 | Brunswick 2 | 09/20/1999 | 10/20/1999 | 9910250002 | <strong>Condenser Pressure Sensing Line Drain Activities Result In Engineered Safety Feature and Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 20, 1999, at approximately 0009 hours, operational activities to drain the condenser pressure transmitter sensing lines resulted in a Group 1 Primary Containment Isolation system actuation. The subsequent activities to recover from the isolation and continue startup resulted in an unexpected reactor power increase and the insertion of a manual Reactor Protection system (RPS) actuation at 0105 hours. At the time of the event, Unit No. 2 was in Mode 2, operating at approximately four percent of rated power. The cause of the event is attributed to the inadequate implementation of corrective action to a previously identified condition (i.e., condensate buildup in the transmitter sensing lines). The inadequate implementation involved proceduralizing a work-around for the condition. Contributing factors to the event were inadequate procedural adherence and ineffective communication regarding crew interactions on the part of the Senior Reactor Operator (SRO) in charge of the startup. Corrective actions include a procedure revision to ensure adequate steps were included. An engineering review will be performed to better understand the work-around. An evaluation will also be performed to identify other "institutionalized" work-arounds, applying the lessons learned from this event. The SRO involved with this event has been coached regarding procedural adherence and the need for ensuring adequate communication skills regarding crew interactions.
3251999001 | Brunswick 1, Brunswick 2 | 01/20/1999 | 02/19/1999 | 9902250284 | <strong>Missed Augmented Inservice Weld Inspections</strong><br /><i>Abstract:&nbsp;</i>On January 20, 1999, with Units 1 and 2 both at 100 percent of rated thermal power, Carolina Power & Light (CP&L) Company determined that certain Category E welds on Units 1 and 2 had not been inspected per the schedule provided in Generic Letter 88-01, "NRC Position On IGSCC In BWR Austenitic Stainless Steel Piping," dated January 25, 1988. Subsequently, on January 21, 1999, and January 27, 1999, CP&L determined that the required inspection frequency for certain Category D and C welds had also not been properly implemented. These inspections are augmented inspection requirements of the Brunswick Steam Electric Plant's Inservice Inspection (ISI) Program and, at the time the inspections were missed, a requirement of Technical Specification 4.0.5.f for both Units I and 2. As such, this condition is being reported, in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications. The root cause of this condition is personnel error; the ISI Program Manager inappropriately revised the inspection schedule for the affected welds. Corrective actions include performance of Engineering evaluations which demonstrated that the structural integrity of the affected systems was not adversely impacted by the missed weld inspections, ISI Program enhancements, and the scheduling of inspections of the missed welds during upcoming refueling outages on each unit.
3251999002 | Brunswick 1 | 01/23/1999 | 02/22/1999 | 9902260093 | <strong>Insertion Of Manual Reactor Trip Due To Reactor Vessel Bottom Head Stratification</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1999, at 0638 hours, with Unit 1 reactor power at approximately 25 percent, a manual reactor trip was inserted. Prior to the insertion of the manual reactor trip, operation with a single loop of the reactor recirculation system resulted in reactor vessel bottom head stratification and operation near the vessel pressure and temperature limits. Based on these conditions, the decision was made to insert the manual reactor trip signal. Reactor water level decreased below the reactor water low level 1 trip setpoint (i.e., 166 inches), resulting in the actuation of Primary Containment Isolation System (PCIS) Groups 2, 6, and 8 (i.e., isolation of the Drywell Floor and Equipment Drains, Containment Atmospheric Control system valves and the Shutdown Cooling system). Plant systems responded as designed. The causes of the event are attributed to (1) the failure to adequately evaluate the impact of a recently installed thermal hydraulic instability modification on plant operations and (2) the lack of awareness by control room personnel of the effects of longer than anticipated single loop operations at minimum flow conditions and the impact of such conditions on reactor vessel bottom head stratification. Corrective actions include establishing the necessary procedural controls and training to preclude recurrence. This event is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(iv) in that the condition resulted in the manual and automatic actuation of an Engineered Safety Feature systems.
3251999003 | Brunswick 1, Brunswick 2 | 07/24/1997 | 03/10/1999 | 9903170335 | <strong>Chlorinator Flange Leak Results in Control Building Emergency Air Filtration System Actuation</strong><br /><i>Abstract:&nbsp;</i>On July 24, 1997, at 1523 hours, with both units operating at rated power and while returning the service water chlorination system to service following scheduled maintenance on the #2 chlorinator, the Control Building Emergency Air Filtration (CBEAF) system actuated and aligned to the chlorination protection mode. The on-site chlorine tank car (i.e., chlorine source) was isolated and the chlorine system was aligned to allow system depressurization to eliminate residual chlorine from the system lines. By 1534 hours, area surveys inside and outside the service water and chlorine buildings indicted no detectable chlorine concentrations. The CBEAF system isolation signal cleared shortly thereafter and the CBEAF system was restored to its normal configuration. The cause of this occurrence is attributed to an inadequately manufactured gas inlet line spool piece. A contributing factor was determined to be the lack of a defined process for nitrogen pressure testing of the gaseous portion of the chlorination system. Corrective actions included replacement of the defective chlorine gas inlet spool piece, pressure testing of the replacement spool piece prior to system restoration, inspection of spare spool pieces for imperfections, development of nitrogen pressure testing post maintenance test procedures for the liquid and gaseous portions of the chlorination system, and review of the occurrence with maintenance personnel. This event is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(iv) in that the condition resulted in the automatic actuation of an engineered safety feature.
3251999004 | Brunswick 1 | 03/25/1999 | 04/26/1999 | 9904280240 | <strong>Drywell Pressure Instrumentation Sensing Line Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1999, it was determined that a condition existed such that two high drywell pressure transmitters and two Containment Atmospheric Control reactor building to suppression pool pressure differential switches would not have met the requirements of the Technical Specifications. The cause of the condition is incorrect design and installation of the sensing lines associated with the affected instrumentation; resulting in improper sensing line slope. The improperly sloped sensing lines allowed water collection in the sensing lines, which caused non-conservatively biased instrumentation output signals. The water was removed from the sensing lines and an engineering evaluation completed to assess continued operation. The engineering evaluation provides a periodic frequency and method for monitoring the output signals of the affected instrumentation to ensure that the accumulation of water in the instrument sensing lines is detected and, if needed, the actions for ensuring the continued operability of the instruments. Additional collective actions include further inspection and evaluation of similar sensing lines and correction of identified sensing line deficiencies. This event is reportable in accordance with 10CFR 50.73(a)(2)(i), as operation prohibited by the plant's Technical Specifications.
3251999005 | Brunswick 1, Brunswick 2 | 04/08/1999 | 05/10/1999 | 9905190136 | <strong>Control Room Emergency Ventilation System Surveillance Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1999, it was determined that the surveillance procedure used to satisfy Technical Specifications 3.3.7.1, "Control Room Emergency Ventilation System Instrumentation," was inadequate. Specifically the procedure failed to demonstrate that, for the failure of the preferred emergency air-filtration (EAF) train, the logic circuitry would properly function to start the standby EAF train after a 10 second time delay. The cause of the procedure inadequacy is a human performance error which occurred during revision of the associated test procedure (i.e., OPT-46.4, "Control Building HVAC Auto Initiation") in March of 1993. As a result of the error, scheduled surveillance testing of the standby EAF train time delay logic was not performed as required on four occasions. Corrective actions include revision of the surveillance procedure and testing of the standby train time delay start function. The testing verified that the time delay function was operating as designed. This event is reportable in accordance with 10CFR 50.73(a)(2)(i), as operation prohibited by the plant's Technical Specifications.
3251999006 | Brunswick 1, Brunswick 2 | 04/23/1999 | 05/24/1999 | 9905260351 | <strong>Missed Surveillance Requirements Result in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 23, 1999, at approximately 1300 hours, it was determined that the channel check Surveillance Requirement (SR) 3.3.3.1.1 was not being met for Suppression Chamber pressure and Drywell Area radiation post accident monitoring instrumentation. The appropriate procedure was revised to include the channel checks and the instrumentation was declared operable upon completion of the channel checks. The cause of the event is attributed to ineffective change management during the procedure development/upgrading for the more restrictive changes associated with Improved Technical Specifications, which were implemented on July 25, 1998. A combination of ineffective resource utilization and lack of detailed tracking resulted in procedure preparation and review errors going undetected. A review of the Post Accident Monitoring Instrumentation Table 3.3.3.1-1 was performed to ensure applicable Technical Specification requirements under SR 3.3.3.1.1 were being met. To ensure proper project management and oversight techniques are utilized appropriately, Operations section management has established a change management policy and incorporated this policy into the Operations Supervisor Handbook. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition that resulted in operation prohibited by the plant's Technical Specifications.
3251999007 | Brunswick 1, Brunswick 2 | 07/31/1999 | 08/30/1999 | 9909080037 | <strong>Control Building Emergency Air Filtration System Actuation During Chlorine Car Replacement</strong><br /><i>Abstract:&nbsp;</i>On July 31, 1999, at 1141 hours, with both units operating at rated power and while replacing the on-site chlorine tank car, the two chlorine detectors located outside of the service water building actuated. By design the Control Building Emergency Air Filtration (CBEAF) system actuated and aligned to the chlorination protection mode. During tank car replacement, personnel using portable monitoring instruments did not detect the presence of chlorine gas. Immediately following the event, the area in the vicinity of the tank car was again checked for the presence of residual chlorine. Upon verifying that there was no indication of chlorine gas in the area, the affected chlorine detectors were reset and the CBEAF system restored to its normal configuration by 1209 hours. At 1522 hours, a four-hour non-emergency event report (Event Number 35976) was made in accordance with 10 CFR 50.72(b)(2)(ii). The cause of this occurrence is attributed to a small amount of residual chlorine gas, which escaped from the chlorinating system piping during the tank car uncoupling process. There were no inappropriate actions identified. As a conservative measure, chlorination system configuration and the cur-rent practices used during chlorine tank car uncoupling will be evaluated to determine whether possible process enhancements could be implemented to minimize reportable occurrences. This event is being reported in accordance with the requirements of 10 CFR 50.73 (a)(2)(iv) in that, the condition resulted in the automatic actuation of an engineered safety feature.
3251999008 | Brunswick 1, Brunswick 2 | 08/09/1999 | 10/01/1999 | 9910060234 | <strong>Electric Motor Driven and Diesel Driven Fire Pump Concurrent Inoperability</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1999, it was determined that the diesel and electric motor driven fire pumps were concurrently rendered inoperable on two occasions between August 9 and August 11, 1999, for a total of 37 hours and 20 minutes. During this time, the fire suppression system was not capable of automatically providing the required flow and pressure to protect safe shutdown equipment in the event of a fire. As such, this occurrence is reportable in accordance with the requirements of 10 CFR 50.73(a)(2)(ii), as a condition outside the design basis of the plant. The cause of this occurrence is attributed to human performance errors. At approximately 0230 hours, on August 9, 1999, with the electric motor driven fire pump removed from service to support planned maintenance, a temperature switch on the diesel driven fire pump engine was damaged, rendering the pump inoperable. The electric motor driven fire pump was restored to operable status at 0450 hours. The diesel driven fire pump was restored to service at 1400 hours based on an engineering determination that the condition did not affect pump operability. The electric motor driven fire pump was then removed from service for additional maintenance activities. On August 22, 1999, during the first operation of the diesel driven fire pump after it was restored to service, a breach of the pump engine cooling water casing was identified. The breach was determined to be directly related to the degraded condition that had occurred on August 9, 1999. Investigation into this occurrence determined that the individual responsible for determining the impact of the damaged temperature switch failed to recognize that the damage to the temperature switch jeopardized the integrity of the pump engine cooling water pressure boundary. The corrective actions for this occurrence include counseling of the individual responsible for evaluating the operability of the diesel driven fire pump and a review of the lessons learned from this occurrence with engineering personnel.
3251999009 | Brunswick 1 | 11/05/1999 | 12/06/1999 | ML99347010 | <strong>Unplanned Reactor Feed Pump Trip Results in Insertion of Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1999, at approximately 1050 hours, with Unit 1 operating at rated power, the Unit 1 reactor feed pump (RFP) 1B tripped during the performance of feed pump testing activities. As a result of the RFP trip, reactor water level decreased. Prior to reaching the automatic reactor water level trip low level 1 setpoint, a manual reactor trip was inserted. The required system actuations occurred as a result of reaching the low level 1 setpoint. By 1105 hours, the 1B RFP trip logic was reset and the pump operated in conjunction with the Startup Level Control valve to control reactor water level. The most likely cause of the occurrence is attributed to a man-machine interface issue or a possible intermittent electrical malfunction of the overspeed control circuit. Corrective actions include incorporation of the lessons learned into the pre-job brief database, additional testing of the Unit 1 and 2 RFP trip lockout control switches and associated overspeed test circuit, and implementation of equipment enhancements as needed. This event is being reported in accordance with the requirements of 10 CFR 50.73(a)(2)(iv) in that the RFP tri p resulted in the actuation of Engineered Safety Feature systems.
3271999001 | Sequoyah 1 | 04/15/1999 | 05/11/1999 | 9905190112 | <strong>Failure of a Centrifugal Charging Pump Results in Exceeding the Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1999, a control room operator noticed that a pressurizer spray valve had gone closed. The crew observed that charging flow had dropped, the charging flow control valve was indicating full open, the reactor coolant pump (RCP) seal flows had dropped; the volume control tank level was increasing, and that the 1B-B CCP motor current had increased. An assistant unit operator (AUO) was dispatched to the pump and reported that the pump had excessive seal leakage. The 1A-A centrifugal charging pump (CCP) was manually started prior to receipt of any main control room alarms. This resulted in a charging and RCP seal flow increase. The operators secured the 1B-B CCP, declared it inoperable, and entered the Technical Specifications Limiting Conditions for Operation 3.1.2.2, 3.1.2.4, and 3.5.2. The cause of the event was the failure of the 1B-B CCP. Enforcement discretion was requested and subsequently approved because the estimated time required to troubleshoot, repair, and test the pump would exceed the allowed outage time. The rotating element was replaced, testing was completed, and the pump was returned to service.
3271999002 | Sequoyah 1 | 09/16/1999 | 10/15/1999 | 9910290188 | <strong>Diesel generator start as a result of a cable being damaged During installation of Thermo-Lag for implementation of the Kaowool upgrade project</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1999, at approximately 1041 hours, Eastern daylight time, with Units 1 and 2 in power operation at approximately 100 percent, an Engineered Safety Feature (ESF) actuation occurred. A loss of power to the Unit 2, 2A-A shutdown board (SDB) initiated a blackout signal. The blackout signal started the Units 1 and 2 emergency diesel generators (EDGs), the 2A-A SDB loads were shed, the 2A-A EDG loaded onto the 2A-A SDB, and electrical loads sequenced onto the 2AA SDB. During installation of Thermo-Lag for implementation of the Kaowool upgrade project, a craftsman was using a knife to penetrate Thermo-Lag material that was installed on the sides of a cable tray such that tie wires could be laced around the Thermo-Lag material. The knife inadvertently penetrated the cable jacket, shield, and conductor insulation causing a short circuit (ground fault) through the grounded shield on a 6.9-kV cable feeding the SDB. The individual performing the work was not injured by the incident. The ground fault tripped the unit board normal feeder breaker resulting in a blackout condition on the 2A-A SDB. The root cause of the event was an inadequate pre-job briefing. Review of the event determined that plant equipment functioned as designed and unit operation was not affected. The SDB was subsequently transferred to its alternate supply, EDGs were secured, and equipment affected by the blackout condition was returned to normal service. The involved individual and the crews responsible for Thermo-Lag installation were counseled on the event, safety requirements were reinforced, and lessons learned were discussed.
3271999003 | Sequoyah 1, Sequoyah 2 | 11/18/1999 | 12/14/1999 | ML99361008 | <strong>Control Room Emergency Ventilation System Start as a Result of the Smell of Smoke in the Control Room</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1999, at approximately 1220, Eastern standard time (EST), with both units in power operation at approximately 100 percent, Operations personnel smelled smoke in the main control room. At 1225 EST, Operations personnel manually started the control room emergency ventilation system (CREVS) in accordance with plant procedures. Operations personnel determined that a 5-kilovolt ampere (kVA) annunciator inverter appeared to have a failed capacitor that was overheating. Operations personnel deenergized the 5-kVA annunciator inverter. After electrically isolating the failed capacitor, Operations personnel returned the CREVS to its normal configuration. The root cause of the event was the random failure of a capacitor in the 5-kVA annunciator inverter. The capacitor was replaced and the annunciator inverter returned to service.
3311999001 | Duane Arnold | 01/12/1999 | 02/11/1999 | 9902220009 | <strong>One Train of the Standby Gas Treatment System Outside of Design Basis Due to the Loss of Seismic Qualification of a Safety Related Temperature Transmitter Caused by Inadequate Mounting Bracket Fasteners</strong><br /><i>Abstract:&nbsp;</i>During routine maintenance activities performed on January 12, 1999, a maintenance technician questioned the condition of fasteners used to support seismically qualified temperature transmitters on the "A" train of the Standby Gas Treatment System (SBGT). Engineering personnel inspected the fasteners and could not provide reasonable assurance of operability of the safety related (seismic category 1) transmitters. The components were declared inoperable which resulted in the continued unavailability of the "A" train of SBGT. A 7 day Limiting Condition for Operation (LCO) was already in progress (day 2 of 7) for the "A" train of SBGT at the time of discovery. As a result, operators remained in the original LCO until repairs were completed on January 14, 1999. The root cause of the event was the less than adequate fasteners initially used to secure the instrument support brackets to the back of the instrument panel. Corrective actions include replacement of the fasteners in the SBGT and Standby Filter Unit panels and inspections of other similar instrument panels to identify potential generic issues. There were no other instruments found inoperable as a result of these inspections. There were no actual safety consequences from this event and the potential consequences were minimal.
3311999002 | Duane Arnold | 01/19/1999 | 02/15/1999 | 9902220365 | <strong>Surveillance Declared Not Met due to a More Restricitive Interpretation of an Unclear Technical Specification Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On January 19, 1999, with the plant operating at 100% power, it was determined that the Diesel Generator (DG) Technical Specification (TS) Surveillance Requirement (SR) that tests the DG start times, could be interpreted more restrictively such that the associated Surveillance Test Procedure (STP) did not satisfy the SR. The STP did test the time to reach minimum voltage and frequency but did not account for momentary initial "overshoot" above the upper limits due to the DG being tested in an unloaded condition. The SR was declared not met and the STP was revised and re-performed but both DGs failed the more restrictive test. Both DGs were declared inoperable and a TS required plant shutdown was begun. It was determined that the DG performance did conform to the UFSAR requirements and that the TS SR could not be satisfied. Enforcement discretion was requested from and granted by the NRC until a permanent TS amendment can be implemented. On January 20, 1999 the DGs were declared operable and the shutdown stopped at 41% power. An exigent TS Change Request was submitted on January 22, 1999. Changes were made to the SR wording during the 1996 to 1998 conversion to Improved TS (based on NUREG 1433) even though no changes to the actual testing were intended. The Improved TS SR was sufficiently unclear to allow a more restrictive interpretation to be made (root cause). There was no effect on plant safety because the DGs did meet the minimum voltage and frequency in the time assumed in the accident analysis. Also, the NRC has recognized via a generic traveler that the imposition of upper limits for the starting sequence is unnecessarily restrictive. The TS Change Request is consistent with the NRC approved generic traveler. The STP will be revised as part of license amendment implementation.
3311999003 | Duane Arnold | 02/09/1999 | 03/04/1999 | 9903100176 | <strong>Entry into Technical Specification 3.0.3 due to Inoperability of Both Trains of Control Room Standby Filter Units Caused by Failure of a Low Flow Differential Pressure Switch</strong><br /><i>Abstract:&nbsp;</i>On February 9, 1999, during planned maintenance on the "A" train of the Control Room Standby Filter Units (SFU), a small light bulb in the low flow pressure differential switch (PDS) went out. At that time, it was believed this condition would render the train inoperable. During efforts to replace the bulb, it was discovered that the same bulb on the "B" SFU was also not lit. The "B" SFU was declared inoperable and with the "A" SFU already inoperable for the planned maintenance, Technical Specification (TS) 3.0.3 was entered. Plant shutdown was commenced, but was hatted at approximately 80% power after the "B" SFU was repaired and TS 3.0.3 exited. The cause of the event was the age related failure of the bulb in the "B" SFU. Corrective actions included replacement of the PDS in the "B" SFU, testing and restoration of the "A" SFU, review and inspection of other similar instruments in the plant, review of maintenance history and preventive maintenance frequencies, and planned installation of instruments with a longer service life as future replacements are needed. Reviews of the logic after the TS 3.0.3 entry indicate that the burned out bulb does not render the SFU inoperable and the safety function could have been achieved in the as-found condition. Therefore, the actual and potential consequences of this event were minimal.
3311999004 | Duane Arnold | 02/22/1999 | 03/24/1999 | 9904010163 | <strong>Entry into Technical Specification 3.0.3 due to both train of Standby Gas Treatment inoperable caused by a surveillance test coincident with a component failure</strong><br /><i>Abstract:&nbsp;</i>On February 22, 1999, with the plant operating at 100% power, and during monthly surveillance testing of the "B" train of Standby Gas Treatment (SBGT), it was discovered that the flow indicating controller (FIC5828A) for the "A" train of SBGT was not properly displaying flow. The "A" SBGT subsystem was declared inoperable and repairs were made coincident with the ongoing surveillance testing on the "B" SBGT subsystem. Securing the "B" train of SBGT from its surveillance run required its mode selector switch to be momentarily placed in "manual" position for approximately 15 seconds which, in effect, disabled "B" SBGT from automatically starting, and it was therefore declared inoperable. For those 15 seconds, both trains of SBGT were inoperable which required entry into Technical Specification 3.0.3, and is a condition that could have prevented the fulfillment of the safety function of SBGT to control the release of radioactive material.
3311999005 | Duane Arnold | 10/29/1999 | 11/24/1999 | ML99334044 | <strong>Actuation of Engineered Safety Feature, Standby Diesel Generator, due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1999, with the plant in Refueling mode, the “A" Standby Diesel Generator (SBDG) automatically started but was not required to load. The cause of the automatic start was a momentary under-voltage condition sensed by the 1A3 Essential Bus under-voltage relay that initiated the “A" SBDG start logic. The momentary under-voltage condition was caused by a lightning strike that induced a voltage transient on the 161KV switchyard bus. Following verification that the essential buses were being powered from their normal source, the “A” SBDG was secured and returned to the standby readiness mode. This event had no effect on the safe operation of the plant.
3311999006 | Duane Arnold | 11/05/1999 | 12/06/1999 | ML99350015 | <strong>Indications in Recirculation Riser Nozzle-to-Safe End Welds</strong><br /><i>Abstract:&nbsp;</i>In November 1999, during refueling outage (RFO) 16 at the Duane Arnold Energy Center (DAEC), ultrasonic (UT) examinations identified indications in three recirculation riser nozzle-to-safe end welds (RRB-F002, RRD-F002, and RRF-F002). The indications in RRB-F002 and RRD-F002 were found to be indicative of intergranular stress corrosion cracking (IGSCC), while the indication reported in RRF-F002 was determined to be a flaw remaining from the 1978/1979 safe end replacement, not IGSCC. Weld overlays were completed on RRB-F002 and RRD-F002. NRC authorization to use ASME Code Cases N-504-1 and N-606, as modified for an inconel overlay, was obtained for the repairs. The indication in RRF-F02 was evaluated under the ASME Code to be acceptable to leave as-is. This event had no effect on the safe operation of the plant.
3311999007 | Duane Arnold | 11/27/1999 | 12/22/1999 | ML99363036 | <strong>Safety Relief Valve Opened During 125VDC Ground Troubleshooting Due to Two Faults in the Solenoid Valve DC Circuit</strong><br /><i>Abstract:&nbsp;</i>On November 27, 1999, during a plant startup following Refuel Outage 16 with reactor pressure at 100 psig, a Safety Relief Valve (SRV) opened resulting in reactor pressure dropping and a reactor water level fluctuation. Troubleshooting to locate a ground on a 125 VDC bus was in progress at the time of the event. Once the troubleshooting efforts were ceased, the SRV closed. Plant equipment and parameters responded as expected for the opening of an SRV. Subsequent testing and repair efforts revealed an open circuit in the SRV's solenoid valve Grayboot connector and a positive ground in the same circuit. Given those conditions, when the troubleshooting efforts introduced a high enough current into the circuit, the solenoid valve energized, resulting in the SRV opening. The root cause of the event was personnel traffic in the area of the solenoid valve's flexible conduit located inside the plant's drywell. Corrective actions included repair of the damaged connection, testing of the SRV, briefing personnel about the event, and issuance of an industry Operating Experience report. Follow-up actions include installation of protective material over the conduit and reviewing industry information pertaining to DC ground troubleshooting. There was no impact on safe operation of the plant as a result of this event.
3331999001 | FitzPatrick | 01/14/1999 | 03/31/1999 | 9904070181 | <strong>Incorrect Emergency Diesel Generator Line-Up During Fire Placed Plant in Condition Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On January 14, 1999, at 12:56 hours, with the plant operating at 100 percent power, a fire was reported in the Hydrogen (H sub 2) Storage Facility. An Unusual Event Emergency Classification was declared. On-site and off-site fire fighting resources were dispatched. The fire was declared extinguished at 19:45 hours. The plant remained at 100 percent power for the duration of the event. During the event, the plant's offsite 115 KV reserve power was de- energized to protect firefighters working in proximity to the 115 KV switchyard. The Emergency Diesel Generator (RDG) Systems were started and run to demonstrate operability required by the plant's Technical Specifications. During the Surveillance Test to assure operability, it was decided to leave the EDGs running unloaded. However, the tie-breakers that force parallel the two EDGs on each Class IE emergency bus were open. In this configuration the plant was in a condition that was outside the design basis of the plant and was required to be in cold shutdown within 24 hours. The causes for running the EDG Systems with the tie-breakers open were inadequate procedures and insufficient operator training on the impact of EDG tie-breaker position on EDG system operability. Corrective actions include a revision to the EDG Operating and Surveillance Test Procedures and operator training program. The most probable causes for the H sub 2 fire were a lack of oversight of the H sub 2 vendors preventive maintenance program and inadequate H sub 2 system monitoring.
3331999002 | FitzPatrick | 01/13/1999 | 05/13/1999 | 9905190164 | <strong>Suppression Chamber to Reactor Building Vacuum Breaker Isolation Valve Differential Pressure Switches Out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1999 the plant was at 100% power. At 13:19, the as-found trip points for the Suppression Chamber to Reactor Building vacuum Breaker [BF] Isolation Valve Differential Pressure Switches, 27PS-110A and 27PS-110B were found out-of-tolerance (high) and exceeding the values required by technical specifications by approximately 2.5%. This event was reported in a 4-hour non-emergency report under 10 CFR 50.72(b)(2)(iii)(D) because both switches exceeded the values required by technical specifications. This condition was identified during Instrument Surveillance Test ISP-89. The condition was immediately corrected by calibrating the pressure switches as directed by the Instrument Surveillance Test Procedure.
3331999003 | FitzPatrick | 02/15/1999 | 06/28/1999 | 9907060254 | <strong>Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Review of the as-found setpoints for 15 Safety Relief Valves (SRVs) [SB] pilot assemblies, removed during Cycle 13, determined that 6 of the 15 SRVs were outside the tolerance of 1145 pig +/- 3 percent allowed by Technical Specification (TS) surveillance requirement 4.6.E. Two of the six SRVs out of tolerance conditions were found following a December, 1997 Forced Outage (FO134) and were previously reported to the NRC in LER-98-002. The effect of the six SRVs being out of tolerance, during Cycle 13, is analyzed in this report. The results of this analysis shows that Reactor Pressure Vessel (RPV) overpressure protection and nuclear plant safety were not adversely affected. The cause of the out of tolerance SRV setpoints was determined to be corrosion bonding between the SRV pilot disc and seat. Corrective actions include continued participation in the BWR Owner's Group SRV Committee, a proposed modification to provide pressure switch actuation of the SRVs, and a formal analysis to confirm that RPV pressure limits would not have been exceeded for the applicable overpressurization transient (i.e., MSIV Closure ATWS), given the as-found test data for the SRV pilots.
3331999004 | FitzPatrick | 04/03/1999 | 06/17/1999 | 9906220135 | <strong>RCIC Instrumentation Inoperable Due to Incomplete Protective Tag Restoration</strong><br /><i>Abstract:&nbsp;</i>On April 3, 1999, with the reactor at approximately 100 percent power, two electrical leads in the 09-30 panel in Ne relay room were found unlanded. This condition would have prevented the Reactor Core Isolation Cooling System (RCIC) suction valve from the Condensate Storage Tanks (CST), 13MOV-18, from closing automatically on a low level condition in the CSTs. The RCIC, pump suction swaps over to the suppression pool on CST low level by opening the suppression pool suction valves and then closing the CST suction valve. This CST low-level transfer of the RCIC suction source is required per Technical Specification section 3.2 "Instrumentation". The RCIC system would have initiated and injected into the core and performed its intended safety function. The suction source would have swamped to the suppression pool on CST low level; however, the RCIC suction valve from the CST would not have shut per design. This condition existed from October 25, 1998, due to improper restoration from a protective tag (PTR) that was hun[ during the Fall 1998 refueling outage and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition prohibited by the plant's Technical Specifications". The cause was determined to be inattention to detail and an inadequate process to ensure complete PTR closeout prior to clearing tags. Corrective actions included a complete walkdown of control room and relay room panels, a review of all PTRs hung during the refueling outage, a review of the lessons learned with operations personnel, and revisions to the PTR closeout review process.
3331999005 | FitzPatrick | 05/06/1999 | 07/07/1999 | 9907140179 | <strong>Missed Surveillance Test Due to Inoperable Containment Hydrogen/Oxygen Analyzer</strong><br /><i>Abstract:&nbsp;</i>On May 6, 1999, the reactor was at 100% power. At 0740 operators found that the switch for the pump on the 3 Containment Hydrogen/Oxygen Analyzer was found in the "Stop" position. This condition remained undetected from April 18, 1999 until May 6, 1999 due to a flow switch out of adjustment. Technical Specifications require that the primary containment oxygen concentration be verified to be within limits once each week. Contrary to this requirement the oxygen concentration of the drywell was not verified to be within limits for the period from April 18, 1999 to May 6, 1999 when the A Containment Hydrogen/Oxygen Analyzer was realigned from the suppression pool to the drywell. This missed surveillance requirement was identified on June 8, 1999 during a review of the post-event analysis. Corrective actions include counseling of personnel involved and procedural revisions.
3331999006 | FitzPatrick | 06/09/1999 | 07/08/1999 | 9907150240 | <strong>Low Pressure Coolant Injection (LPCI) Mode of Residual Heat Removal (RHR) System Inoperable Due To Loss of Automatic Startup Capability of RHR Pumps</strong><br /><i>Abstract:&nbsp;</i>On 06/09/99 at 1640 hours, with Emergency Diesel Generators (EDG) A and C inoperable due to troubleshooting activities being conducted on associated electrical circuitry, the Control Room received an alarm on annunciator 098-2-32 indicating an Emergency Core Cooling System (ECCS) restart program 125 VDC control power loss. This loss prevented automatic start of an associated Core Spray (CS) System pump (14P-1A) and two of four Residual Heat Removal (RHR) System Pumps (10P-3A and 10P-3B). At the time of the alarm, the reactor mode switch was in the RUN position with the plant operating at approximately 100 percent rated power. The cause for the loss of the 125 VDC control power was determined to be a loose fuse contact located in the 125 VDC control circuitry. Corrective actions include troubleshooting and repairing the defective fuse contact, conducting an equipment failure evaluation, inspecting other similar fuse block assemblies for loose contact, performing a maintenance history review for previous similar contact problems, and conducting training on the removal and insertion of fuse block assemblies.
3331999007 | FitzPatrick | 08/09/1999 | 10/26/1999 | ML99314035 | <strong>Both Trains of Core Spray Inoperable Due To Out of Tolerance Time Delay In Pump Start Interlock Relays</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1999, with the reactor at 100 percent power1 during the performance of Surveillance Test 3J (ST-3J), it was determined that the time delay for both A and B division Core Spray pump start interlock relays exceeded the values required by Technical Specifications by 0.25 and 0.93 seconds respectively. This condition rendered both divisions of Core Spray inoperable and is therefore reportable under 10 CFR 50.73 (a)(2)(vii). The time delay settings for both A and B Core Spray pump start interlock relays were immediately recalibrated during the performance of ST-3J at which restored the operability of both A and B divisions of Core Spray. Subsequent analysis identified that the calibration tolerance, which existed in ST-3J at the time of this event, was too wide and had previously resulted in surveillance test failures due to instrument uncertainty. This analysis concluded the Residual Heat Removal pump start interlock relays are subject to this condition as well, but to a lesser degree. Additional corrective actions include developing a tighter as-left calibration tolerance for Residual Heat Removal and Core spray pump start interlock relays and re-calibrating these relays in accordance with this new tolerance as well as conducting a root cause analysis to determine why this condition was not effectively corrected at an earlier opportunity and preparing a request for an amendment to the Technical Specifications.
3331999009 | FitzPatrick | 10/14/1999 | 11/10/1999 | ML99325012 | <strong>Standby Gas Treatment System Train "B" Charcoal Efficiency Less than Required</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1999 at 1130 hours during a review of Standby Gas Treatment System (SBGTS) Surveillance Test (ST) results, Engineering discovered that the charcoal cartridge adsorption capability of SBGTS Train "B" had been less than the ST acceptance criteria for approximately six months. The reported efficiency was 99.37percent. The ST acceptance criteria stated that the charcoal efficiency shall be greater than or equal to 99.825 percent. The personnel assigned to review the ST results failed to recognize that the charcoal efficiency did not meet the ST acceptance criteria. Upon discovery, SBGTS Train "B" was declared inoperable and a seven day Limiting Condition for Operation (LCO) was entered in accordance with Technical Specification Section 3.7.B.2.a. The charcoal in SBGTS Train "B" was replaced during the LCO time frame, personnel were counseled, lessons learned were discussed with the personnel involved in the event, and a procedure will be revised. The extent of condition is limited to this event. This event did not result in a safety system functional failure in accordance with draft NEI 99-02, Revision C.
3331999010 | FitzPatrick | 10/14/1999 | 11/15/1999 | ML99327019 | <strong>Main Turbine Trip and Reactor Scram Due to Degraded Cable in Main Generator Anti-Motoring Circuit</strong><br /><i>Abstract:&nbsp;</i>On October 14, 1999 at 17:44, an automatic Main Turbine trip followed by a Reactor Scram occurred due to a short circuit between conductors in a control cable in the Main Generator anti-motoring protective relay circuit. (Figure 1). The plant was at 100% power at the time of the Main Turbine Trip. During the event the HPCI system tripped on overspeed. Corrective actions include repairs of the Main Generator anti-motoring circuit and repairs to the HPCI system.
3331999012 | FitzPatrick | 11/05/1999 | 12/06/1999 | ML99347014 | <strong>Main Turbine Trip and Reactor Scram Due to Moisture Separator Reheater and Moisture Separator Reheater Drain Tank High Level Trip Signals</strong><br /><i>Abstract:&nbsp;</i>On 11/5/99, at 1051 hours with the mode switch in the “RUN” position and the plant operating at approximately 83 percent power during power ascension, an automatic Reactor scram occurred as a result of a Main Turbine trip. The Turbine trip initiation was a result of high water level trip signals from both Extraction Steam System Moisture Separator Reheater 31MS-1B and Extraction Steam System Moisture Separator Reheater Drain Tank 31TK-2B. The cause for the excessive water inventory in 31MS-1B and 31TK-2B was the combination of (1) a Feedwater Heater level transient during power ascension resulting in a closure signal to a Feedwater Heater control valve and (2) a failed pneumatic signal line on a 31TK-2B drain line control valve. The degraded line resulted in the drain line control valve failing in the closed position. Corrective actions include a Post Transient Evaluation that was completed prior to plant start up, an Equipment Failure Evaluation to determine the cause for the failed pneumatic line, and an extent of condition review to evaluate other equipment with potential similar failure characteristics.
3341999001 | Beaver Valley 1 | 01/23/1999 | 02/19/1999 | 9903050070 | <strong>Manual Reactor Trip Due To Continuing Degradation of Main Condenser Parameters</strong><br /><i>Abstract:&nbsp;</i>At approximately 1024 hours on 1/23/99, the Unit 1 Reactor was manually tripped from approximately 73% power, as a conservative and proactive step in response to continuing degradation of Main Condenser parameters. The Reactor control rods fully inserted and plant systems operated as expected. Emergency Operating Procedures were entered, the Unit was stabilized, and station recovery from the Reactor trip was satisfactorily completed. NRC 4-hour notification of this event was made, per 10 CFR 50.72(b)(2)(ii), at approximately 1251 hours (same day). The degraded Main Condenser parameters resulted from elevated air in-leakage through the valve seat of the closed outlet isolation valve of V Main Condenser waterbox and into the Cooling Tower pumps' suction piping. This resulted from eliminating the water seal over the waterbox outlet valve seat during routine waterbox maintenance due to failure of the on-shift operating crew to maintain adequate awareness of changes which altered level in the waterbox, with a direct contributor of procedure inadequacy. As part of corrective actions to this event, Operations Shift briefings were conducted, an Operations communication and written instructions to Maintenance were provided, and the procedure for isolating waterboxes was revised.
3341999002 | Beaver Valley 1 | 01/21/1999 | 03/03/1999 | 9903110156 | <strong>Non-Conservative Concurrent Iodine Spike Radiological Dose Calculation Methodology</strong><br /><i>Abstract:&nbsp;</i>A review of Beaver Valley Power Station (BVPS) design basis accident (DBA) dose calculations is being conducted as an extent of condition evaluation pursuant to BVPS Unit 2 LER 97-008 to verify that parameters and assumptions are appropriate and are applied in a conservative manner. Four input parameters associated with the methodology for calculating dose during DBAs with concurrent iodine spikes were identified as producing non-conservative calculated values. It was concluded on February 9, 1999 that the four identified non-conservative input parameters could have resulted in tile calculated control room dose for the Main Steam Line Break DBA and Small Line Break DBA at BVPS Unit 1 exceeding the 10CFR Part 50 Appendix A, Criterion 19 limit interpreted as 3 )O REM thyroid in the Standard Review Plan. Since BVPS no longer has reasonable assurance that acceptance criteria for control room personnel dose limits per Criterion 19 would have been met during past operation at BVPS Unit 1, use of the identified dose calculation non-conservative input parameters are reportable pursuant to 10CFR 50.73(a)(2)(ii)(B) as a condition Outside the design basis of the plant. Similarly the identified dose calculation non-conservative input are reportable pursuant to 10CFR21(c)(3)(ii) as a failure to comply that could create a substantial safety parameters hazard were it to remain uncorrected in accordance with 10CFR21(a)(1). Administrative controls have been implemented at both BVPS Units to control plant operation, thereby ensuring that station operation remains within licensed limits until dose calculations can be formally revised.
3341999003 | Beaver Valley 1 | 03/08/1999 | 04/05/1999 | 9904080127 | <strong>Inadequate Basis for Instrument Inaccuracies in Degraded Voltage Setpoints Led to Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>The ">/=" symbol used beside the Engineered Safety Feature (ESF) Degraded Voltage setpoint in the Beaver Valley Power Station (BVPS) No. 1 Technical Specifications is a mathematical symbol for values relating to the Technical Specification defined setpoint, not a directional indicator of conservative direction for "nominal" setpoints as defined in the Westinghouse-developed ESF setpoint methodology approved for use at BVPS Unit No. 1. Given this understanding for the Technical Specification symbol ">/=" with the ESF Degraded Voltage setpoint, BVPS Unit 1 violated this Technical Specification setpoint on six occasions in 1998 by setting the ESF Degraded Voltage setpoint to a value less than the setpoint described in the Technical Specifications. Failure to set the ESF Degraded Voltage setpoint in accordance with the required setpoint is a condition prohibited by plant Technical Specifications and is reportable pursuant to 10CFR50.73(a)(2)(i)(B). The action from Table 3.3-3 for Degraded Voltage requires the associated channel be placed in trip or enter the applicable Action Statement for the associated Emergency Diesel Generator made inoperable by the degraded voltage instrumentation. The six occasions that the BVPS Unit 1 ESF Degraded Voltage setpoint was not set in accordance with the Technical Specification setpoint, the setpoint was set just below the Technical Specification setpoint value, but within the analyzed tolerance band allowed by the Westinghouse WCAP setpoint methodology for a "nominal" setpoint value. The ESF Degraded Voltage setpoints implemented on these six occasions continued to preserve the design bases for BVPS Unit 1 such that the consequences from any postulated design basis accident would continued to have met UFSAR acceptance criteria. A License Amendment Request has been issued to the NRC requesting that this setpoint be defined as a "Nominal Trip Setpoint" in accordance with the Westinghouse setpoint methodology.
3341999004 | Beaver Valley 1 | 03/17/1999 | 04/14/1999 | 9904220282 | <strong>Inadequate Pre-Fire Plan Procedure Guidance Resulting in Potential Damage to the Charging / High Head Safety Injection (HHSI) Pumps</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1999 it was determined that Unit 1 was outside the design basis requirements of the Fire Protection Program required by 10 CFR 50 Appendix R, Section III.G, as a result of identified inadequacies in the Unit pre-fire plan procedures. In the event of a fire in select fire areas, this condition could have led to damage to the Charging/High Head Safety Injection (HHSI) pumps. This condition was discovered during an extent of condition review following a similar Unit 2 discovery on March 5, 1999 (reported in LER 2-99-002-00). At approximately 1528 hours on March 17, 1999, notification of this discovery was made pursuant to 10 CFR 50.72(b)(1). The apparent cause is that architect engineer and Duquesne Light Company personnel, who jointly developed the list of safe shutdown equipment for the Appendix R Report in 1982, failed to account for periods of plant operation where the Volume Control Tank operating pressure could initially exceed the static head pressure of the Refueling Water Storage Tank. This error apparently led to the procedure inadequacies, due to resulting inadequate consideration of required operator actions. Unit 1 compensatory actions, including issuance of a basis for continued operation on March 26, 1999, were implemented to preclude potential damage to the Charging/HHSI pumps. Procedure changes will be made to address the issues identified in this LER. The issues identified in this LER will be reviewed against the reporting criteria of 10 CFR 21.
3341999005 | Beaver Valley 1, Beaver Valley 2 | 03/19/1999 | 04/19/1999 | 9904260219 | <strong>Inadequate Meteorological Wind Speed Instrumentation Calibration Range led to Failure to Comply with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During a routine review of past vendor calibration data on the meteorological instruments on March 19, 1999, an I&C supervisor noted that the vendor was calibrating the wind speed sensors in a wind tunnel for a range of 0-25 mph rather than the full range specified in the UFSAR of 0-50 mph. It was recognized by the I&C supervisor that this was a potential violation of UFSAR criteria. It was subsequently determined to not meet the definition for calibration as described in the Technical Specifications. The vendor believed the results from the range of 0-25 mph could be accurately extrapolated to cover the required 0-50 mph. Given the past inadequate calibration procedures, these wind speed sensors should not have been operable. With the number of wind speed sensors less than required by Technical Specification 3.3.3.4 Limiting Condition of Operation (LCO), Action Statement a. requires that all release of gaseous radioactive material from the radwaste gas decay tanks be suspended until the inoperable channel(s) is restored to operable status. Gaseous releases were routinely performed with meteorological instrumentation which have now been determined to have not been adequately calibrated. In addition, Action Statement b. requires a Special Report be issued to the Commission within the next 10 days with one or more required meteorological monitoring channels inoperable. BVPS Unit 1 and 2 operated with these meteorological instrument monitoring instruments not meeting the LCO for more than 10 days without issuing a Special Report. These conditions are not compliant with Technical Specification 3.3.3.3 Action Statements a and b and is reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The BVPS wind speed sensors were declared inoperable, removed and were re-calibrated over the complete range of 0-50 mph. It is engineering judgment that the portion of the meteorological instrumentation not fully tested during calibration would have continued to adequately function for wind conditions in the 26-50 mph range at BVPS.
3341999006 | Beaver Valley 1 | 04/09/1999 | 05/10/1999 | 9905180230 | <strong>Inadequate Pre-Firm Plan Procedure Guidance Resulting in Potential Damage to Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On April 9, 1999, with Unit 1 in Mode 1 at approximately 98% power, an ongoing Engineering Fire Protection Safe Shutdown self-assessment identified that operator actions in certain Unit 1 pre-fire plan and alternate safe shutdown procedures were inappropriate as they would place the Unit outside the design basis of the Fire Protection Program for Appendix R Safe Shutdown capability. These actions would de-energize power to the Emergency Diesel Generator (EDG) Building Area Ventilation System Discharge Dampers 1VS-D-22-1A and 1B, and could have prevented proper ventilation for the EDGs and the fulfillment of their safety function to satisfy the Appendix R Safe Shutdown requirements. Non-emergency one-hour notification of this discovery was made to the NRC, at approximately 1846 hours on April 9, 1999, pursuant to 10 CFR 50.72(b)(1). These procedural inadequacies are not applicable to the corresponding Unit 2 procedures. The apparent cause of this event is personnel error attributed to failure to identify that the manual actions specified in the procedures would result in closure of the EDG ventilation exhaust dampers. A contributor to this personnel error was inadequate knowledge of the design of the subject ventilation dampers, which are spring return to close on loss of power. Following event determination, operating shift briefings were conducted to ensure awareness of the subject procedural inadequacies pending revision of the procedures. Unit 1 subsequently entered Mode 5, at approximately 2235 hours on April 13, 1999. Appropriate revisions to the affected procedures have been implemented to ensure that power to 1VS-D-22-1A and 1B is not de-energized by the procedures.
3341999007 | Beaver Valley 1 | 04/13/1999 | 05/11/1999 | 9905190027 | <strong>Manually Initiated Reactor Trip Signal During a Pre-Planned Shutdown of the Unit While In Mode 3</strong><br /><i>Abstract:&nbsp;</i>During shutdown to MODE 5 for a planned surveillance outage, while in Mode 2 and inserting control rods to enter Mode 3, rod Control Bank (CB)-A, group 2 insert motion did not occur when directed, and the "Rod Control Urgent Failure" alarm annunciated, at approximately 0338 hours on April 13, 1999. Attempted rod motion was stopped and at approximately 0347 hours, it was confirmed that the reactor was in MODE 3. From initial investigation, failure of a rod control printed circuit (PC) card (B) was suspected and it was decided to fully insert all withdrawn control rods by manually tripping the reactor. At approximately 0427 hours, the reactor was manually tripped and all control rods were fully inserted. Emergency operating procedures (EOPs) were entered to confirm existing stable conditions, the EOPs were subsequently exited, and normal shutdown procedures were entered/executed. A non-emergency four-hour notification was made to the NRC. Preliminary results of testing have identified the apparent cause as an intermittent transformer failure of one of the three phase-thyristor trigger gate outputs on the PC firing card of rod control power cabinet (RCPC) 2AC. Failure of the cabinet air conditioner may have contributed to this event. The RCPC firing, phase control, regulation gripper, and fail detector PC cards were replaced with equivalent cards and the removed cards were sent to the vendor for Off-Bite troubleshooting and repair. Further on-site troubleshooting did not reveal anomalies. Root cause analysis of this event will be performed. The failed cabinet air conditioner has been replaced.
3341999008 | Beaver Valley 1 | 04/23/1999 | 05/21/1999 | 9905270228 | <strong>Missed INservice Testing Program Surveillance Attribute</strong><br /><i>Abstract:&nbsp;</i>During resolution of an unrelated procedure concern involving the Beaver Valley Power Station (BVPS) Unit 1 Inservice Testing (IST) Program Basis Document, a potential problem was identified by the Unit 1 IST Program engineer on April 23, 1999 with BVPS Unit No. 1 in Mode 5. The two suction valves (MOV-1CH-115B and D) on the High Head Safety Injection (HHSI) pumps from the Refueling Water Storage Tank (RWST) were only being stroked and timed in the open direction quarterly per an Operations Surveillance Test (OST) as required by the Unit 1 IST Program. The Unit 1 IST Program should have been testing these valves for stroke and time in both the closed and open direction. The root cause was an inappropriate exclusion of testing these two valves in the closed direction within the original Unit 1 IST Program developed in 1976. The cause of this initial inappropriate exclusion is not known. An opportunity was missed to identify this Unit 1 IST Program discrepancy when the Basis Document was developed during 1995-1997. The cause of not identifying this IST Program discrepancy was that a conscious self-checking technique was not adequately applied when the Unit 1 IST Program was developed for the third IST Program 10-year interval. The Unit 1 IST Program and the OST which conducts the IST Program test for valves MOV-1CH-115B and D were revised to include the stroke and time requirements in the closed direction. This OST was performed on April 24, 1999 and satisfactory results were obtained. The safety significance of not previously performing the IST testing of the MOV-1CH-115B and valves was minimal since a weekly and quarterly surveillance test stroked these valves (without timing their stroke) and would have identified significant valve closing.
3341999009 | Beaver Valley 1 | 04/29/1999 | 08/23/1999 | 9908260149 | <strong>Missed Surveillance of Component Cooling Water System 10" to 8" Header Cross-Connect Inlet Isolation Valve 1CCR-42</strong><br /><i>Abstract:&nbsp;</i>At approximately 0030 hours on 7/23/99, review of Control Room copies of completed operating surveillance test 1(OST)-15.4 for the monthly valve position verification of the component cooling water system (CCR) determined that the 4/29/99 performance of this OST had not verified the correct position of 1CCR-42. 1CCR-42 is the 10" to 8" CCR header cross connect inlet isolation valve to the Spent Fuel Pool heat exchangers. This review confirmed the OST performances prior to and following 4/29/99 properly verified the valve position. This event is reportable due to non-compliance with Technical Specifications Surveillance Requirement 4.7.3.1b. The concluded cause of this event is insufficient degree of attention applied by the involved utility licensed operators. A contributor was the method used to implement a procedure change to the OST, which became effective on 4/22/99. This change deleted other valves from the OST by lining out, and made 1CCR-42 difficult to distinguish from the deleted valves. Involved personnel have been counseled on closer scrutiny of surveillances. A permanent change has been made to the OST to distinguish 1CCR-42 from deleted valves in the procedure. By 12/31/99, this LER will be discussed in the Plant Status Update for licensed and non-licensed operators and appropriately reviewed as part of plant Engineering Support Personnel Continuing Training.
3341999010 | Beaver Valley 1 | 09/06/1999 | 10/01/1999 | 9910080124 | <strong>Beaver Valley Power Station Unit No. 1 Manual Reactor Trip Due to Main Unit Generator Voltage Regulator Malfunction</strong><br /><i>Abstract:&nbsp;</i>On September 6, 1999 with the Beaver Valley Power Station (BVPS) Unit No. 1 running at 100% power, the following four alarms were received at 1722: Generator Field Forcing, Generator Field Overcurrent, Voltage Regulator Firing Circuit #1 Blown Fuse/Power Loss, and Voltage Regulator Firing Circuit #2 Blown Fuse/Power Loss. Control room operators observed the main generator power factor, VAR and current meters to be fluctuating rapidly above and below normal values. The above four alarms then cleared and reoccurred within approximately two seconds. These alarms continued to clear and reoccur on an approximate two second frequency. The reactor was manually tripped 18 seconds after the receipt of the initial alarm. The control room operators followed station procedures to recover from a (manual) reactor trip. Safety related systems functioned properly following the reactor/turbine trip and the Unit was stabilized in hot standby conditions. This is an event that resulted in a manual actuation of the Reactor Protection System (RPS) and an automatic actuation of the Auxiliary Feedwater System which is an Engineered Safety Features System. These two actuations are reportable pursuant to 10CFR50.73(a)(2)(iv). A definitive root cause for this event could not be identified. However, the apparent cause of the event is an electronic circuit open/fault in the Voltage Regulator Logic Drawer of the Main Unit Generator. There were minimal safety implications to the health and safety of the public.
3341999011 | Beaver Valley 1 | 09/09/1999 | 10/09/1999 | 9910200112 | <strong>Inadequate Axial Flux Difference (AFD) Monitor Alarm Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1999, it was identified that the Operations Surveillance Test 1OST-5A.1, "Delta Flux Alarm Program Operability Check" was inadequate to support the Beaver Valley Power Station (BVPS) Unit 1 Technical Specification (TS) 3/4.2.1. The Axial Flux Difference (AFD) monitor alarm has not previously been sufficiently proven to be operable by a suitable periodic surveillance test and thus, the AFD monitor alarm had been inoperable. The periodic AFD monitor alarm test procedure did not fully test all possible combinations of potential operating conditions. The failure to perform the required more frequent AFD monitoring when the AFD monitor alarm was inoperable constitutes noncompliance with TS Action Statement 3.2.1, in accordance with TS 4.0.3. This is a condition prohibited by the plant's TS and is reportable pursuant to 10CFR50.73(a)(2)(i)(B). Subsequent evaluation determined that this deficiency also applied to Unit 2 operation prior to 1998. There were no indications that either BVPS Unit's axial flux monitor alarm had not been functioning correctly when it was in operation during power operation. There was no indication that the axial flux difference limits were ever exceeded at either BVPS Unit and that the reactor cores have been operated as described within the UFSAR. There were minimal safety implications to the health and safety of the public. A review of TS on each Unit will be conducted to identify any similar instances, where the operability of equipment addressed in TS Surveillance Requirements (TSSRs) is dependent upon support equipment not addressed by TSSRs.
3351999001 | St. Lucie 1 | 03/09/1999 | 04/07/1999 | 9904090141 | <strong>Inadequate Design and IST Surveillance Requirements for Iodine Removel System</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1999, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. While investigating a failed full flow in-service test surveillance of a vacuum breaker check valve serving the sodium hydroxide (NaOH) tank in the Unit 1 iodine removal system (IRS), FPL determined that in certain scenarios the design of the NaOH tank venting arrangement was inadequate to ensure proper post accident containment spray Ph. Additionally, although a previous review of the St. Lucie IST program identified an issue with the NaOH vacuum breaker check valve full flow test considering a failure of the redundant vacuum breaker check valve, the significance of this finding was not immediately recognized. This condition was caused by original IRS design inadequacies and personnel error. Immediate corrective actions were taken to place the IRS NaOH tank in a condition bounded by the design calculations to assure operability of the IRS. Long term corrective actions for the IRS design inadequacies are being investigated by FPL. Additionally, FPL completed a review of check valve full flow IST surveillance criteria and no other operability or reportability issues were found.
3351999002 | St. Lucie 1, St. Lucie 2 | 05/05/1999 | 06/04/1999 | 9906090067 | <strong>Both Trains of Safety Injection Actuation Blocked During Surveillance Due to Procedure Error</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1999, St. Lucie Units 1 and 2 were operating in Mode 1 at 100 percent power. At approximately 1742 hours, FPL determined that both units' emergency safeguards features actuation signal monthly channel functional surveillance procedures, "ESFAS Monthly Functional Test," simultaneously blocked both channels of safety injection actuation signal. The NRC was notified of this event via a four-hour non-emergency notification made pursuant to 10 CFR 72(b)(2)(iii) at 2016 hours on May 5, 1999. Cognitive personnel error during development of the original surveillance procedures caused the inadequate procedural steps that allowed the simultaneous blocking of both channels of automatic safety injection actuation. Contributing factors include weaknesses in the procedure change and review process, and weak administrative controls for controlled keys. Corrective actions include changes to the surveillance procedures, enhancements to the procedure change process and administrative controls for controlled keys, and stand down meetings with appropriate plant personnel. Additionally, FPL performed a review of applicable surveillance procedures to determine if similar issues exist in other procedures. No other instances were found.
3351999004 | St. Lucie 1 | 09/12/1999 | 10/07/1999 | 9910140083 | <strong>Main Steam Safety Valves Surveillance Outside Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1999, St. Lucie Unit 1 was in Mode 1 and holding at approximately 70 percent reactor power for testing of the main steam safety valves (MSSVs) in accordance with procedure 1-MSP-08.07, "Main Steam Safety Setpoint Surveillance." Three train A and one train B MSSVs lifted low, outside of the required Technical specification pressure setpoint range of +/-1 percent. Prior to testing, the reactor trip setpoints were reduced to allow continued operation with two MSSVs per train out of service. The set pressure of one of the train A MSSVs was reset to allow continued operation. The apparent cause of the MSSV surveillance failures was setpoint drift. Per ASME code considerations, a formal root cause is not required. The safety significance of the low as-found MSSV setpoints was evaluated and found to be insignificant. The subject MSSVs are being refurbished and retested prior to unit startup from the SL1-16 refueling outage. FPL is considering whether a change to the St. Lucie Technical Specifications or TS bases is appropriate to address the differences between NUREG-1432 and the St. Lucie Technical Specifications concerning as-found and as-left safety relief setpoints.
3351999005 | St. Lucie 1 | 10/05/1999 | 11/01/1999 | ML99314023 | <strong>Pressurizer Pressure Instrumentation Cable Separation Outside Appendix R Design Bases</strong><br /><i>Abstract:&nbsp;</i>On October 5 1999, St. Lucie Unit 1 was in Mode 6 during a refueling outage. FPL engineers finished their initial assessment of the inside containment Appendix R cable separation walkdowns. This walkdown was planned as part of the continuing safe shutdown analysis validation effort. The assessment results showed that pressurizer pressure instrumentation did not meet the required 10 CFR 50 Appendix P cable separation criteria inside containment at the penetration area where the cables for pressurizer pressure transmitters PT-1102B and D pass over the penetrations for PT-1102A and C. FPL determined that this 10 CFR 50 Appendix P noncompliance does not adversely affect the fire protection program, and that the pressurizer pressure instrumentation remains operable with respect to the required safe shutdown functions. Modifications required to place the field condition within design basis conditions will require extensive engineering, procurement and construction time, and are planned to be performed during the next St. Lucie Unit 1 refueling outage.
3351999006 | St. Lucie 1 | 10/29/1999 | 11/24/1999 | ML99340040 | <strong>Turbine/Reactor Trip Due to Ruptured Turbine Low Bearing Oil Trip Diaphragm</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1999, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. At 0105 hours the St. Lucie Unit 1 control room received annunciation of D-12 "Turbine Bearing Oil Pressure Low." Operations personnel discovered that a small amount (approximately two drops per minute) of oil was leaking from the cover of the turbine protective device trip block. The turbine/generator and reactor automatically tripped at 0129 hours. Standard post trip actions were carried out and the reactor was stabilized in Mode 3. The cause of this event was the installation of a Westinghouse supplied defective diaphragm for the turbine low bearing oil trip protective device. The failure of this diaphragm dumped the autostop oil pressure and tripped the turbine/generator. The loss of autostop oil pressure resulted in the opening of the DEH interface valve, dumping all DEH oil pressure. The loss of DEH oil pressure resulted in the automatic trip of the reactor. The faulty diaphragm was replaced and miscellaneous minor equipment issues were dispositioned.
3351999007 | St. Lucie 1 | 10/30/1999 | 11/29/1999 | ML99340018 | <strong>Manual Reactor Trip Due to Low Steam Generator Levels During Startup</strong><br /><i>Abstract:&nbsp;</i>On October 30, 1999, St. Lucie Unit 1 was in the process of a reactor startup. While Operations personnel were performing turnover activities, the level of the 1A steam generator began dropping and attempts to recover the 1A steam generator level were unsuccessful. Upon receiving annunciation of steam generator low level pre-trip alarms the reactor was manually tripped at 0641 hours. The plant was stabilized in Mode 3. There were no significant equipment issues during or after the manual reactor trip. The cause for the manual reactor trip was personnel error. Operators paid insufficient attention to detail regarding the 1A steam generator steam flow/feed flow mismatch that resulted from unbalanced operation of the atmospheric dump valves. Operations Management reinforced expectations regarding the role of control room supervisors and the conduct of crew turnovers. The plant was restarted later the same day. Procedural enhancements will be made with regard to the role of control room supervisors and atmospheric dump valve operation.
3351999008 | St. Lucie 1 | 11/17/1999 | 12/16/1999 | ML99361002 | <strong>As Found Cycle 15 Pressurizer Safety Valve Setpoint Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On November 17, 1999, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. Wyle Labs informed FPL of unsatisfactory test results for code pressurizer safety valves (PSVs) removed during the cycle 16 refueling outage. Wyle Labs was contracted to perform the offsite pressurizer safety valve testing and the testing was conducted within the required time restraints. Technical Specification 3.4.2.1 requires the PSVs to lift at 2500 psia (+/-1 percent). The as found settings for two of the removed St. Lucie Unit 1 pressurizer safety valves were 3.0 percent high and 4.0 percent low, outside the Technical Specification tolerance limit of +/-1 percent. The cause of the failed pressurizer safety valve tests were setpoint drift and mishandling of the valves during removal or transportation. The subject pressurizer safety valves were removed and replaced with pre-tested valves during the St. Lucie Unit 1 cycle 16 refueling outage. There was no affect on the health and safety of the public during past St. Lucie Unit 1 cycle 15 power operations because the limiting overpressure analyses remain bounded when actual St. Lucie Unit 1 cycle 15 operational parameters were considered.
3351999009 | St. Lucie 1 | 12/16/1999 | 01/18/2000 | ML00368161 | <strong>Appendix R Exemption Request K1 Not Met Resulting in Plant Outside Design Bases</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1999, St. Lucie Unit 1 was in Mode 1 operation at 100 percent reactor power. FPL discovered inconsistencies between FPL's exemption request K1 (separation criteria for redundant safe shutdown trains inside the Unit 1 reactor containment building) and the NRC Safety Evaluation Reports for Appendix R. St. Lucie Unit 1 meets the separation criteria specified in its Appendix R submittals, but does not meet the 25 feet vertical separation criteria specified in the NRC SERs. The cause of this event was personnel error during the original St. Lucie Unit 1 10 CFR 50 Appendix R licensing activities. FPL determined that the fire protection program remains operable in this condition. FPL will resubmit exemption request K1 to clarify vertical separation criteria.
3361999001 | Millstone 2 | 01/06/1999 | 02/01/1999 | 9902100227 | <strong>Failure to Perform Required Surveillance on Fire Door</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1999, it was discovered that one of the rated fire doors in the barrier between Unit 2 Turbine Building and Unit 1 Access Control Area consisted of a 3-hour rated roll-up fire door that has not been properly surveilled as required in the Unit 2 Technical Specifications. The door is located in the southeast corner of the 14'-6" elevation and is a 3-hour rated roll-up fire door. The station fire protection program identifies this door as satisfying the Technical Requirements Manual requirement for a fire door in this barrier. There is a double door on the Unit 1 side of the opening that is improperly labeled. The double door is only rated for 1 1/2 hours. As a result of mislabeling the Unit 1 door, surveillances were performed on the 1 1/2 hour fire door, and not performed on the 3-hour rated Unit 2 roll-up door. The 3-hour rated roll-up door has been abandoned in place and has not been maintained operable. The cause of the condition was that the double door on the Unit 1 side of the opening was improperly labeled due to a historical lack of configuration control. As a result of mislabeling the Unit 1 door, surveillances under the plant procedure were performed on the Unit 1 door instead of the Unit 2 roll-up door. Compensatory measures were implemented by establishing fire watches as required by the Unit 2 Technical Requirements Manual and a design change will replace the door with a 3-hour rated fire door. Past configuration management problems will continue to be addressed as found.
3361999002 | Millstone 2 | 01/18/1999 | 02/17/1999 | 9902250218 | <strong>Violation of Technical Specificatijon 4.3.3.9, Verification of Steam Generator Blowdown Throttle Valve Position</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1999, the method by which the Steam Generator blowdown flow rate surveillance is satisfied was questioned. Technical Specification Surveillance Requirement (TSSR) 4.3.3.9, Table 4.3-12, Item 3.e. requires blowdown flow to be verified operable by checking throttle valve or pump status on a daily basis. Compliance with TSSR 4.3.3.9 requires a field verification of actual valve position or pump flow in all modes of operation, which was not performed. The cause of this condition was failure to properly incorporate Technical Specification surveillance requirements into plant surveillance procedures. To correct this deficiency, the throttle valves will be maintained in a locked position as necessary to ensure compliance with Technical Specification functional requirements.
3361999003 | Millstone 2 | 01/23/1999 | 02/22/1999 | 9903030243 | <strong>Inadequate Net Positive Suction Head for Containment Spray Pumps</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1999, based on a review of the Containment Spray System (CSS) flow analysis, it was identified that the analysis showed negative Net Positive Suction Head (NPSH) margin for the CSS pumps in the recirculation phase of a design basis accident. Negative NPSH margin can cause fluid voiding and pump cavitation which could adversely affect the ability of the CSS to perform its accident function. The cause of this condition was the installation of additional spray nozzles subsequent to the original system design and the use of non-conservative assumptions in the original analysis with respect to containment sump fluid temperature. As corrective action, some spray nozzles will be replaced and the CSS flow analysis will be revised to reflect the increased system pressure and reduced total flow associated with the nozzle replacement.
3361999004 | Millstone 2 | 02/11/1999 | 03/14/1999 | 9903240218 | <strong>Violation of Technical Specification 3.7.6.1, Positive Reactivity Addition to Reactor Coolant Systems from the Refueling Water Storage Tank</strong><br /><i>Abstract:&nbsp;</i>On February 11, 1999, at approximately 0620 hours, the requirements of Technical Specification (TS) 3.7.6.1 and its associated action statement were violated when water was transferred to the Reactor Coolant System (RCS) from the Refueling Water Storage Tank (RWST). The action statement for TS 3.7.6.1 requires that all operations involving core alterations or positive reactivity changes be suspended when both control room emergency air cleanup systems are inoperable. The cause of this event was a failure to verify the boron concentration of a makeup source prior to RCS addition. As a result of this event a briefing will be provided to the appropriate personnel.
3361999005 | Millstone 2 | 02/23/1999 | 03/24/1999 | 9904010289 | <strong>Insufficient verification of Technical Specification Surveillance 4.8.2.3.2, 125 Volt Class 1E Battery Bank Load Test</strong><br /><i>Abstract:&nbsp;</i>On February 23, 1999, during a review of a proposed change to the facility Final Safety Analysis Report, it was identified that the eighteen month surveillance performed to verify battery loadings for the Class 1E 125 Volt Direct Current battery banks was inadequate to satisfy Technical Specification (TS) Surveillance 4.8.2.3.2.d. This surveillance requires that battery capacity be verified adequate to supply and maintain actual emergency loads. The cause of this condition was an inadequate estimation of existing loads in the original battery loading calculation and an inadequate control over the addition of new battery loads. To correct this deficiency, design controls and administrative controls have been implemented to ensure that the most recent battery load profile tests are adequate to meet the applicable TS surveillance requirements. These controls will include physical disconnection of some loads and manual (in lieu of automatic) loading of other non-essential load(s). Additionally, the applicable surveillance procedure shall be revised to ensure that battery capacity is verified for actual emergency loads.
3361999006 | Millstone 2 | 03/01/1999 | 03/30/1999 | 9904060440 | <strong>Failure to Satisfy Reactor Coolant Pump Underspeed Sensing Circuit Response Time Technical Specifications Surveillance Requirement 4.3.1.1.3</strong><br /><i>Abstract:&nbsp;</i>On March 1, 1999, with the unit in Mode 5, following troubleshooting and analysis of the "A" channel Reactor Coolant System Pump (RCP) speed sensing circuit, it was self-identified that the response time of the RCP speed sensing circuit did not satisfy acceptance criteria stated in Table 3.3-2 of the Technical Requirements Manual and as such, the historical demonstration of the trip response times, as required by Technical Specifications 3/4.3.1, "Reactor Protective Instrumentation," Surveillance Requirement 4.3.1.1.3, could not be assured. The cause of this condition was the historical use of an unconservative testing methodology that was not appropriately based on current industry response time testing standards. As a completed corrective action, a Technical Requirements Manual change has been implemented to increase the response time acceptance value.
3361999007 | Millstone 2 | 03/19/1999 | 04/15/1999 | 9904260251 | <strong>Failure to Monitor Steam Generator Primary and Secondary Coolant Temperatures in Accordance with Technical Specifications Surveillance Requirement 4.7.2.1</strong><br /><i>Abstract:&nbsp;</i>On March 19, 1999 at approximately 1900 hours, to set conditions in support of a Low Pressure Safety Injection System and Shutdown Cooling Heat Exchangers leakage surveillance test, the Reactor Coolant System pressure was increased to greater than 200 psig with Tavg less than 200 degrees Fahrenheit (F). At these system conditions, Technical Specifications Surveillance Requirement (TSSR) 4.7.2.1 requires that, at least once an hour, verification of the steam generators primary and secondary coolant temperatures be conducted in order to ensure that steam generator pressure induced stresses remain below a maximum allowable fracture toughness stress limit (RT sub NDT) of 50 degrees F. On March 20th, it was discovered that the initial verification had not been conducted within 1-hour, as required, which constitutes a missed surveillance. The cause of this event was attributed to procedural inadequacies and operator inattention to detail. As corrective actions, appropriate Operations personnel were provided with briefings on applicable Mode 4 and 3 Condition Based Surveillances and as necessary, procedures will be revised to assure compliance with TSSR 4.7.2.1 criteria.
3361999008 | Millstone 2 | 05/11/1999 | 06/09/1999 | 9906180029 | <strong>Auxiliary Feedwater Regulating Valve Failed Surveillance Test, Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1999, at 1919 hours, an Auxiliary Feedwater Regulating Valve (AFRV) failed its monthly inservice operability test, which strokes the valve through its full range of motion. With this valve inoperable the auxiliary feedwater flowpath to one steam generator was no longer available. Since the facility TS do not address the loss of an auxiliary feedwater flowpath, Technical Specification Action Statement (TSAS) 3.0.3 was conservatively entered at 1919 hours while investigating operability of the valve. Upon determining that the valve was operable at all times, it was concluded that entry into TSAS 3.0.3 was not required. At the time of this event, the facility was in Mode 1 at approximately six percent power. The cause of this event was a mechanical failure of the AFRV's non-safety grade positioner. A contributing factor in the event was a lack of guidance in the applicable inservice test procedure with respect to required steps to determine valve operability upon failure of the identified operability test. Corrective actions for this event include repair of the AFRV positioner and revision to applicable procedures to provide additional guidance on determining action required upon failure of the monthly inservice operability test.
3361999009 | Millstone 2 | 05/25/1999 | 06/23/1999 | 9907010234 | <strong>Manual Reactor Trip Due to Steam Leak in Turbine Building</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1999, (Mode 1, 100% power) at 1512, a manual reactor trip was initiated due to a report of a steam leak in the turbine building. The steam leak occurred following erratic feedwater heater level response. The steam leak was located at the inlet flange to the shell side relief valve for the 1A feedwater heater. All safety related equipment performed as expected and the plant was stabilized at normal post trip parameters. Additionally, the Main Steam Isolation Valves were shut to isolate steam to the turbine building. The event was caused by inadequate controls associated with the adjustment and grooming of the feedwater heater level control valves which resulted in an overpressure condition when the shell side relief valve lifted. The resultant force caused a steam leak at the relief valve flange. Inadequate gasket compression was caused by improper torquing of the feedwater heater 1A shell side relief valve flange studs which resulted from unclear guidance in the procedure used for determining the torque values. Corrective actions pertaining to this event include refining of controls for adjusting feedwater heater string controls and clarifying guidance concerning torqued connections when significant dynamic piping loads are expected from events such as water hammer's or the opening of pressure relief devices.
3361999010 | Millstone 2 | 08/04/1999 | 09/02/1999 | 9909080038 | <strong>Failure to Perform ASME Section XI Inservice Testing on Pressurizer Relief Line Flow Control Sample Valve Following Maintenance Activities</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1999, during a routine review of Inservice Test (IST) quarterly surveillance results, it was determined that inadequate post maintenance testing was performed on a Pressurizer Relief Line Flow Control Sample Air Operated Valve (AOV). By replacing the valve operator air supply solenoid, which is an auxiliary to the parent AOV (2-RC-003), the valve closing stroke time performance characteristics were affected, necessitating a retest of the valve stroke time in accordance with the facility Technical Specification Surveillance Requirements (TSSR). A retest of the valve stroke time was not performed in a timely manner. The cause of this event was an inadequate man-machine interface and a lack of training on post maintenance test requirements which led to the development of a deficient work package. To correct this deficiency training shall be performed on both identification of post-maintenance test requirements and on expectations for review and approval of work package post maintenance test requirements. Additionally, the facility electronic database system shall be upgraded to ensure the work order development process reflects quality controlled program indicators.
3361999011 | Millstone 2 | 08/23/1999 | 09/20/1999 | 9909270153 | <strong>Exceedness of Thermal Reactor Power Limit</strong><br /><i>Abstract:&nbsp;</i>On August 23, 1999, during the performance of independent control board checks, it was determined that the eight hour running calorimetric power calculation exceeded the licensed limit of 2700 MWT. In the four hours before and during the increase there were no adjustments to Reactor Coolant System boron concentration, turbine power, or control rod position. Additionally, during the investigation of this event, four other events of exceeding the eight-hour running calorimetric power calculation limit were discovered. In all cases the largest power exceedness was less than 0.2 MWT above the licensed limit. The cause of this event was a lack of conservatism in the procedures and alarm setpoints used to limit reactor power. To correct these deficiencies operating procedures will be changed. In addition, guidance, in the form of a stated goal for the eight-hour averaged reactor thermal power, will be provided to licensed operators. Revised alarm setpoints for the plant process computer will be investigated to provide an alarm prior to exceeding 2700 MWT as expressed by the eight-hour calorimetric average. The cause of the failure to report the additional four events is still under investigation. Other corrective actions, if necessary, will be included to address these deficiencies.
3361999012 | Millstone 2 | 09/17/1999 | 10/15/1999 | 9910260229 | <strong>Unrecoverable CEA Misalignment, Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On September 17, 1999, at 1346, Technical Specification Action Statement (TSAS) 3.0.3 was invoked (the first time) when a Control Element Assembly (CEA 7-65) could not be aligned with its group within one hour as required by technical specifications (TSAS 3.1.3.1.e, Movable Control Element Assembly, Full Length CEA Position). During the shutdown process the TOTAL UNRODDED INTEGRATED RADIAL PEAKING FACTOR (F sub r**T) exceeded its 100% power limit while the TSAS for Power Distribution Limits, AZIMUTHAL POWER TILT (T sub q) (TSAS 3.2.4.a) was in effect. This condition also required invoking TSAS 3.0.3 (the second time). The cause of this event was a grounded coil wire for the lower gripper assembly. The reason for the ground cannot be determined until the coil stack is disassembled during refueling outage 13. F sub r **T and T sub q exceeded TS limits due to local power peaking effects caused by the misaligned CEA and subsequent reactor power reduction. As a result of this event, the leads leading to lower gripper coil for the CEA were insulated. The coil stack for the CEA shall be replaced during refueling outage 13 and shall be examined for cause of failure of the insulator. Other corrective actions, if necessary, will be tracked in the corrective action program.
3361999013 | Millstone 2 | 10/18/1999 | 11/17/1999 | ML99330003 | <strong>Auxiliary Feedwater Pump room High Energy Line Break Door Left Unsecured</strong><br /><i>Abstract:&nbsp;</i>On October 18,1999 at approximately 1532 hours it was discovered that the High Energy Line Break (HELB) door between the two Auxiliary Feedwater (AFW) Pump Rooms was closed, but it's locking mechanism was not secured. This event resulted in the HELB door being inoperable for less than 10 minutes. The cause of this event was a skill based human performance error, a lack of adequate Verification that the HELB door was properly secured. For this event, a briefing was performed for appropriate fire watch and security personnel to emphasize the importance of securing HELB doors and the process used to control compensatory fire watches shall be reviewed and enhanced as necessary to ensure fire watches are terminated when no longer required.
3361999014 | Millstone 2 | 10/21/1999 | 11/22/1999 | ML99335001 | <strong>Failure to Enter the Limiting Condition for Operation of Containment Isolation Valves Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On October 21, 1999 at 1845, it was discovered that plant operators failed to enter the Limiting Condition for Operation (LCO) of Containment Isolation Valves (CIV) Technical Specification (TS) while performing monthly surveillance testing on a CIV (valve 2-SI-628). This valve supports the Low Pressure Safety Injection and High Pressure Safety Injection and the Safety Injection test lines. The forty-eight hour Technical Specification Action Statement for ECCS SUBSYSTEMS - Tavg > 3000°F was previously invoked, at 0052, when the valve failed the TS Surveillance stroke test. The cause of this event was human error. Plant operators failed to recognize 2-SI-628 as a CIV hence failed to enter the LCO of CIV Technical Specification while performing the monthly surveillance testing on CIV 2-SI-628. As a result of this event, applicable Operations department personnel are being briefed on this event.
3361999015 | Millstone 2 | 09/19/1999 | 02/17/2000 | ML00368693 | <strong>Unanticipated Reactor Protection System Trip Signal Generation On Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1999, with the plant in Mode 3 following a normal reactor shutdown, an unanticipated Low Steam Generator(S/G) Water Level actuation S/G signal was received on 4 out of 4 Reactor Protection System (RPS) Channels. The Low S/G Level RPS trip was set consistent with Technical Specifications at 49.5%. S/G Level was being manually controlled between 45 percent (%) and 75% and "maintained in the lower end of the band until cooldown rate reduces" in accordance with plant procedures. Actual S/G water level was decreased to less than 49.5%, constituting an actual plant parameter satisfying the requirement for RPS actuation. The plant was in a mode for which actuation of the S/G Low Water Level RPS trip was not required to mitigate the consequence of an accident Additionally, no component changed state as a result of the trip since the control rods had been previously fully inserted and the TCB's had been opened. Subsequent investigation determined that several other RPS bistables tripped as a result of the input process variables having exceeded the trip setpoints for the parameters during this and previous plant cooldowns. The cause of this event was determined to be organizational and programmatic deficiencies in that operating procedures did not contain warnings for pre-planned ESF or RPS trips. As a result of this event, applicable procedures will be revised to identify pre-planned Engineered Safety Feature (ESF) and Reactor Protection System (RPS) trips. This event is being reported pursuant to 10CFR50.73(a)(2)(iv), as an event or condition that resulted in an automatic actuation of any Engineered Safety Feature (ESF), including the RPS.
3361999016 | Millstone 2 | 12/01/1999 | 12/30/1999 | ML00367381 | <strong>Technical Specification Surveillance Requirements of Seismic Instrumentation Were Not Historically Met</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1999 at 1230, it was discovered that the Technical Specification Surveillance Requirements (TSSR) for the seismic instrumentation were not historically met. The seismic instrumentation TS was subsequently relocated to the TRM upon receiving the Nuclear Regulatory Commission's (NRC) approval on July 13, 1999. The surveillance procedure called out calibration of four reeds (out of 12) at each eighteen (18) month interval while the TSSR called out for complete calibration of the recorder every eighteen months. The cause of this event was lack of understanding of the TSSR. Historically, the TSSR requirement for calibration every eighteen months was being used, but the original manufacturer's recommendations for the definition of a calibration were used, in lieu of the TSSR's definition of a CHANNEL CALIBRATION. As a result of this event, a briefing is being conducted to the appropriate I&C Department personnel to discuss the correct interpretation of the TRM Section 4.4, "Seismic Instrumentation," item no. 4, "Response Spectrum Recorder." Additionally, surveillance procedure SP 2405E will be revised to correct the number of reeds to be calibrated per procedure performance.
3381999001 | North Anna 1 | 01/06/1999 | 01/10/1999 | 9901290129 | <strong>RCS Leak Rate Missed Surveillance Due To Computer Malfunction</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1999, with Unit 1 in Mode 1, 100 percent power it was determined a missed surveillance had occurred on January 3, 1999, as a result of an inaccurate Reactor Coolant System (RCS) leak rate calculation. Technical Specification 4.4.6.2.1.d, requires performance of a RCS inventory balance every 72 hours. During the performance of the inventory balance the level inputs from the Volume Control Tank (VCT) and Pressurizer (PZR) were indicating zero rather than actual levels. As such, the computer calculation provided an inaccurate RCS unidentified leak rate. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by the TS. The cause of the inaccurate leak rate calculation was due to a computer malfunction where the VCT and PZR levels were not processed properly by the computer program. This event posed no significant safety implications since RCS leakage never exceeded TS limits and there were other methods available to detect RCS boundary leakage. Therefore, the health and safety of the public were not affected at any time during this event.
3381999002 | North Anna 1, North Anna 2 | 02/13/1999 | 09/17/1999 | 9909220257 | <strong>ISOLATION VALVE UNSECURED DUE TO VALVE CONFIGURATION</strong><br /><i>Abstract:&nbsp;</i>On February 13, 1999, with Units 1 and 2 in Mode 1, 100 percent power the boron injection tank (BIT) manual bypass isolation valve, 1-SI-77, was discovered unsecured. Technical Specification 3.6.1.1 requires manual valves, that are required to be closed during accident conditions, be closed and secured in position. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by the TS. 1-SI-77 was subsequently verified to be in the required closed position and the lock and chain was re-installed and placed in a manner that would properly secure the valve operator. The cause of the valve being unsecured was a result of not having a positive means to lock the valve. The chain and lock had fallen from the valve and would allow manipulation of the valve tee handle. This event posed no significant safety implications since the isolation valve was in its closed position. Therefore, the health and safety of the public were not affected at any time during this event.
3381999003 | North Anna 1, North Anna 2 | 03/31/1999 | 04/27/1999 | 9905040138 | <strong>Potential Loss of HHSI Pumps Due To Postulated Main Control Room Fire</strong><br /><i>Abstract:&nbsp;</i>As part of the ongoing Configuration Management Project's integrated review of fire protection and in conjunction with review of recent industry operating experience events, a deviating condition was identified that is applicable to the North Anna Power Station. In the event of an Appendix R main control room (MCR) fire a potential exists for rapid depletion of the volume control tank level resulting in the loss of the charging/high head safety injection (HHSI) pumps based on applicable Appendix R assumptions. The procedure for the MCR fire was inadequate because it did not include specific direction to ensure that adequate HHSI suction alignment and control was established in a time frame to minimize the possibility of volume control tank depletion and potential loss of the HHSI pumps. These circumstances placed the station outside its Appendix R design basis for both units in that the potential loss of HHSI pumps could result in the inability to achieve and maintain a safe shutdown condition in the event of an Appendix R MCR fire. This situation resulted in no safety consequences or implications and is being reported pursuant to 10CFR50.73(a)(2)(ii)(B).
3381999004 | North Anna 1 | 04/13/1999 | 05/11/1999 | 9905190036 | <strong>SWITCH MISPOSITION FOR SUPPLY DAMPERS TO CONTROL ROOM EMERGENCY FAN</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1999, at 1025 hours, with Units 1 and 2 at 100 percent power, the position switch for the suction supply dampers to a Control Room (CR) emergency fan was discovered out of position. The switch has two positions "Normal" and "Lockout." The switch is required to be in the "Lockout" position to maintain the CR emergency fan in the recirculation mode during the initial stages of a fuel handling accident or safety injection. The station entered a seven-day action statement under Technical Specification 3.7.7.1 to perform corrective action. At 1032 hours on April 13, 1999, the switch was returned to its correct position and the action statement was exited. The cause of this event could not be determined, but is believed to be a result of accidental contact. This event posed no significant safety implications since the control room habitability system was capable of significantly reducing the dose with the identified configuration had an accident occurred. Therefore, the health and safety of the public were not affected at any time during this event.
3381999005 | North Anna 1, North Anna 2 | 06/16/1999 | 07/08/1999 | 9907150089 | <strong>Potential for Continued Feed Flow to Faulted Steam Generator During MSLB</strong><br /><i>Abstract:&nbsp;</i>The Configuration Management Project integrated review of the Feedwater (FW) System identified a condition that may have previously placed Units 1 and 2 outside the plant design basis. During a main steam line break (MSLB) with offsite power available, there is the potential for FW flow from the condensate pumps to feed the faulted steam generator (SG) through the standby FW pump's open discharge isolation valve and a main FW regulating bypass valve that fails to close. Manual operator action to isolate flow to the faulted SG may be required shortly after the initiation of the accident to prevent a containment over-pressurization condition. Emergency procedures do not support flow isolation in this timeframe. This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B). The condition was caused by an incorrect assumption that the discharge isolation valve on the standby FW pump would automatically close following a safety injection. The condition posed no significant safety implications since it pertains to previous plant operation, a MSLB has not occurred, and controls have been taken to prevent susceptibility to the condition.
3381999006 | North Anna 1, North Anna 2 | 09/04/1999 | 09/28/1999 | 9910050266 | <strong>Potential for Safeguards Exhaust Flow to Bypass Charcoal Filter Due to Degraded Damper</strong><br /><i>Abstract:&nbsp;</i>On September 4, 1999, at 1600 hours, with Unit 1 in Mode 1 at 100% power and Unit 2 in Mode 1 at 88% power, it was discovered that a damper associated with the Auxiliary Building General Exhaust Ventilation System was degraded due to missing damper seals. The degraded damper had the potential to cause a portion of the Safeguards Area exhaust flow to bypass the charcoal filter prior to release to the environment following an accident. The bypass flow could degrade the ventilation system to the extent that the fulfillment of the safety function of the Safeguards Area Exhaust System may have been adversely affected. This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B), 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). The condition was caused by degradation of the ventilation system damper. The condition posed no significant safety implications since the potential bypass flow would still be monitored by the radiation monitoring system, a design basis accident has not occurred, and administrative controls have been taken to prevent susceptibility to the condition.
3381999007 | North Anna 1, North Anna 2 | 10/27/1999 | 11/19/1999 | ML99334041 | <strong>Battery Chargers Not Sized for Design Capability Due to Incorrect Calculations</strong><br /><i>Abstract:&nbsp;</i>During a review of the Emergency Power System, a condition was identified that may have placed both units outside the plant design basis. Design calculations indicate that battery chargers 1-III and 2-III and swing chargers 1C-II and 2C-II may not meet the design basis requirement for a 24-hour recharge following a two-hour duty cycle discharge of its associated battery during emergency loading conditions. Also, battery charger currents may exceed TS surveillance requirements. This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B). The condition was caused by charger sizing calculations incorrectly calculating the maximum potential charger loads. The condition posed no significant safety implications since no accidents occurred that would have challenged battery charger design capability. Administrative controls were previously implemented for battery chargers 1-III and 2-III and swing chargers 1C-II and 2C-II to ensure they are capable of meeting design requirements. Since implementation of administrative controls, the chargers are fully capable of supplying loads and recharging the batteries in accordance with design basis requirements.
3391999001 | North Anna 2 | 09/15/1999 | 10/12/1999 | 9910200207 | <strong>Failure To Lock Open Loop Stop Valve Breakers As Intended By Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On September 15, 1999, with Unit 2 in Mode 5, Cold Shutdown, it was identified that the loop stop valve breakers were not locked open as intended by Technical Specification (TS). TS 3.4.1.6 states that whenever a reactor coolant loop is isolated and drained, AC power shall be removed from the loop stop valves and the associated breakers locked open. This event is reportable pursuant to 10CFR50.73 (a)(2)(i)(B) for a condition prohibited by the TS. The affected procedures were revised and the breakers were locked in the open position. The cause of the breakers not being locked open was a result of the failure to update the operating procedures when the Technical Specifications were amended to allow returning an isolated Reactor Coolant System (RCS) loop by backfilling from the active portion of the RCS. This event posed no significant safety implications since the loop stop valve breakers were secured by the use of tie-wraps and danger tagged in the open position. Therefore, the health and safety of the public were not affected at any time during this event.
3391999002 | North Anna 2 | 09/22/1999 | 10/21/1999 | 9910270240 | <strong>Containment Liner Through Wall Defect Due To Corrosion</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1999, while Unit 2 was shutdown for a scheduled refueling outage (RFO), a coatings assessment of the containment liner identified areas in the protective coating that had blistered. During coatings repair of an area located at elevation 246.5 mean sea level (msl), a small area of rust was discovered upon removal of the blistered coating. Evaluation by the Inservice Inspection Engineer, identified a small hole in the containment liner. Preliminary measurements showed the depth of the hole to be approximately three eighths of an inch which would indicate a through wall defect. Subsequent local pressure testing confirmed the hole to be through wall. The condition was caused by active corrosion at the point of contact between the steel liner and a piece of wood discovered embedded in the concrete wall. The pressure test performed upon identification of the potential through wall defect identified a leak rate well within acceptable limits as required by the TS for containment leakage rates. As such, there are no significant safety consequences or implications. A VOLUNTARY LER is being submitted to document this defect.
3391999003 | North Anna 2 | 11/02/1999 | 11/30/1999 | ML99341013 | <strong>Failure To Lock Containment Isolation Valve Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1999, at 0346 hours, with Unit 2 in Mode 1 operating at 100 percent power operations personnel identified that Unit 2 Safety Injection (SI) Accumulator makeup manual isolation valve, 2-SI-47 was not properly locked closed. The valve was found closed with a chain through the handwheel, the hasp of the lock through the chain, but the hasp was not fully engaged in the locking mechanism. Technical Specification (TS) 3.6.3.1 requires that each containment isolation valve shall be operable. With 2-SI-47 not properly locked, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by the TS. The valve was immediately locked and independently verified as being properly locked. The cause of the condition is attributed to personnel error. Operations personnel did not properly lock 2-SI-47 following refilling of the Unit 2 SI Accumulators at the end of the 1999 Unit 2 refueling outage. This event posed no significant safety implications since containment integrity was maintained. Isolation valve 2-SI-47 was found in the closed position. Therefore, the health and safety of the public were not affected at any time during this event.
3391999004 | North Anna 2 | 12/02/1999 | 12/23/1999 | ML00367066 | <strong>Manual Reactor Trip Due To Loss Of Feedwater Pump Suction Pressure And Auxiliary Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1999, at 1647 hours, with Unit 2 in Mode 1 operating at approximately 98% power, the reactor was manually tripped due to the loss of two of three main feedwater pumps The main feedwater pumps tripped on low suction pressure due to the loss of discharge flow from the "A" high pressure heater drain pump following a secondary plant transient. The auxiliary feedwater pumps automatically actuated following the reactor trip to restore inventory in the steam generators. This event is reportable pursuant to 10CFR50.73 (a)(2)(iv) for any event or condition that resulted in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS). The cause of the event is attributable to the failure of a feedwater heater level control switch to properly actuate. A root cause evaluation of the event is being performed. This event posed no significant safety implications. The reactor was safely shut down and ESF equipment operated properly. The health and safety of the public were not affected.
3411999001 | Fermi 2 | 01/04/1995 | 01/12/1999 | 9902220370 | <strong>Previous Essential Room Cooler Maintenance Violated Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 13, 1999, a review of past preventive maintenance activities determined that the Division I Emergency Equipment Cooling Water System (EECWS) room cooler had been removed from service on January 4, 1995, for approximately 31.5 hours. This exceeded the limiting applicable Technical Specifications (TS) allowed outage time of 18 hours for TS 3.8.2.1, DC Sources. Specifically, at 0121 hours on January 4, 1995, the Division IEECWS room cooler was removed from service for preventive maintenance by removing fuses at the associated motor control center. It was subsequently returned to service at 0855 hours on January 5, 1995, when the fuses were reinstalled. This event constitutes a condition prohibited by Technical Specifications and is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). No TS Limiting Condition for Operation (LCO) was invoked because a design calculation had justified operability of an EECWS division with its associated room cooler removed from service. The design calculation did not consider a single failure affecting the opposite EECWS division and assumed that its room cooler would be available during postulated design basis events. Inadequate oversight and verification of activities associated with the design calculation did not identify this erroneous assumption. Corrective actions include: restricting preventive maintenance for EECWS room coolers without invoking the appropriate LCOs; conversion to the Improved Standard Technical Specifications which provide more flexibility when support systems are removed from service; and, licensing basis training which has increased assurance that important considerations are not misapplied or overlooked.
3411999002 | Fermi 2 | 05/18/1999 | 06/17/1999 | 9906220016 | <strong>Reactor Recirculation Pump Trip Results in Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1999, plant personnel were performing routine field brush maintenance for the Reactor Recirculation Pump (RRP) "A" Motor Generator (MG) Set. The RRP tripped when personnel were changing the MG set exciter brush. The brush had shorted on the opposite polarity bus bar. Core flow decreased which placed the plant in the "Scram Region" of the Power to Flow Map. Operators inserted a manual Scram at 1709 hours. Plant systems responded as designed. All Control Rods fully inserted. Reactor Water Level 3 Primary Containment Isolation Valves [ISV] for Groups 4 (Shutdown Cooling/Head Spray), 13 (Drywell Sumps), and 15 (Traversing In-Core Probe) isolated as designed. Reactor water level was restored to its normal band, and Emergency Core Cooling Systems did not actuate. The brush change out was completed while the plant was shutdown. Previous actions taken to minimize risk for a RRP trip during MG set brush replacement were not effective. An action was included in the corrective action program to evaluate options for improving the ability for successful changing of MG set brushes online.
3411999003 | Fermi 2 | 06/25/1999 | 07/26/1999 | 9907300120 | <strong>High Pressure Coolant Injection System Flow Controller Failure</strong><br /><i>Abstract:&nbsp;</i>At 1928 hours on June 25, 1999 the high pressure coolant injection system (HPCI) [BJ] was declared inoperable after a routine check of control room indications conducted each shift identified that the HPCI flow controller [BJ] [FC] had failed downscale. In this condition, the HPCI system would have produced less than the minimum required flow for HPCI to be considered operable. The required Technical Specifications actions were taken. A four hour notification required by 10 CFR 50.72(b)(2)(iii)(D) was made at 2230 hours on June 25, 1999, Event Number 35865. Repairs were made to the HPCI flow controller and HPCI was restored to operable status at 2248 hours on June 27, 1999, terminating the event. The event was caused by failure of the control amplifier [AMP] for the automatic HPCI flow control loop. Subsequent examination of the affected circuit board determined that a degraded electrolytic capacitor [CAP] caused the failure of the control amplifier. The control amplifier circuit card in the HPCI flow controller automatic flow control loop was replaced with a refurbished card.
3411999004 | Fermi 2 | 09/13/1999 | 10/13/1999 | 9910200157 | <strong>High Pressure Coolant Injection System Inoperability due to Failed HPCI Room Temperature Switches</strong><br /><i>Abstract:&nbsp;</i>On two occasions on September 13 and 20, 1999, the High Pressure Coolant Injection (HPCI) system was removed from service after HPCI room temperature switches failed to reset when the trip setpoint was exceeded during routine calibration/functional testing. Technical Specifications for the HPCI room temperature switch required isolation of the HPCI turbine steam supply valves, rendering HPCI inoperable. The temperature switches were replaced and HPCI was restored to operable status. HPCI was inoperable for approximately eleven hours on September 13, 1999, and approximately nine hours on September 20, 1999. The HPCI room temperature switches provide protection from high energy line breaks outside containment by initiating isolation of the HPCI steam supply. The failure of the temperature switches to reset was determined in each case to result from failure of the same capacitor (C2) in each temperature switch circuit. Further evaluation determined that the HPCI room temperature switches would have performed their specified function in the as found condition; however, HPCI was made inoperable on both occasions when the HPCI steam supply was isolated.
3411999006 | Fermi 2 | 10/27/1999 | 11/24/1999 | ML99340024 | <strong>Plant Fire Protection Program Dedicated Shutdown Procedure Omitted a Required Action for Certain Fire Zones</strong><br /><i>Abstract:&nbsp;</i>At approximately 1700 hours, on October 27, 1999, it was determined that a deficiency existed in the dedicated shutdown procedure used for plant shutdown in the event of fires in certain areas of the plant. The dedicated shutdown procedure did not include a required action for fires in all fire zones for which the action would be required. The dedicated shutdown procedure directs isolation of the control air supply [LF] for the High Pressure Coolant Injection System (HPCI) [BJ] test return line control valve [BJ][FCV], E41F011, only for some fires in some of the fire zones where the action is required. Isolation of the control air supply is required to prevent fire induced spurious opening of the HPCI test return line control valve which, in combination with fire induced spurious opening of two other valves, could result in Standby Feedwater (SBFW) [SJ] flow being bypassed to the condensate storage tank (CST) [SD][TK], reducing flow to the reactor vessel. The SBFW system was declared inoperable invoking Technical Specification (TS) 3/4.7.11, Appendix R Alternative Shutdown Auxiliary Systems. The dedicated shutdown procedure was revised to correct the omission. The TS action was exited at approximately 1500 hours on October 28, 1999, terminating the event. This event is reportable in accordance with Operating License Section 2.F as a condition not fully satisfying License Condition 2.C (9). A 24 hour initial telephone notification was made to the NRC Operations Center at 1157 hours on October 28, 1999, Event Number 3632. This Licensee Event Report constitutes the 30 day written follow-up report required by Operating License Section 2.F.
3411999007 | Fermi 2 | 11/11/1999 | 12/13/1999 | ML99350002 | <strong>Reactor Water Cleanup (RWCU) System Isolation Due to a High Ventilation Differential Temperature Condidtion</strong><br /><i>Abstract:&nbsp;</i>At 0715 hours on November 11, 1999, an automatic actuation occurred in the Reactor Water Cleanup (RWCU) System portion of the Primary Containment Isolation System (PCIS) due to a high area ventilation differential temperature condition that existed in the South RWCU Pump Room. This actuation automatically closed RWCU Primary Containment Outboard Isolation Valves, G3352-F220, isolating reactor coolant flow to the RWCU System. Immediate corrective actions were taken to verify that no actual system leakage had occurred. The cause of the RWCU isolation was determined to be an undetected trip of the RWCU "B" Pump Room Cooler which occurred on November 9, 1999. This led to the RWCU isolation when the Reactor Building Heating, Ventilation, and Air Conditioning (RBHVAC) System tripped at 0648 hours on November 11, 1999 due to freezestat actuation (low outside temperature). Investigation revealed that the thermal overloads on the RWCU "B" Pump Room Cooler had tripped and gone unnoticed by operations personnel because of the RWCU "B" Pump Room Cooler location, inadequate equipment indications available to the operators, and inadequate work practices. A four hour notification required by 10CFR50.72(b)(2)(ii) was made at 0959 hours on November 11, 1999, Event Number 36425.
3411999008 | Fermi 2 | 11/11/1999 | 12/13/1999 | ML99355010 | <strong>Mechanical Draft Cooling Tower "C" Fan Brake Nitrogen Supply Isolated</strong><br /><i>Abstract:&nbsp;</i>October 28, 1999, the Ultimate Heat Sink Mechanical Draft Cooling Tower (MDCT) "C" overspeed fan brake nitrogen supply cylinder and pressure regulator were replaced. On November 11, 1999, Instrumentation & Control (I&C) personnel performing a pressure regulator setpoint change and gauge replacement discovered that the regulator outlet manual isolation valve had been closed since the regulator was replaced. The MDCT "C" fan brake was considered to be inoperable from October 28, 1999, 0806 hours until November 11, 1999, 1726 hours when the regulator outlet valve was reopened. This event is being reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. Investigation determined that plant personnel did not recognize that the outlet valve was closed when the regulator was replaced. Procedures, valve line ups, drawings, and post maintenance testing requirements were insufficient to ensure correct alignment of all valves in the nitrogen supply to the fan brake system. A work package for a subsequent pressure regulator replacement incorporated instructions to ensure that fan brake nitrogen supply valves would be correctly aligned. Further corrective actions relating to this event are being considered for implementation commensurate with established priorities and processes of the Fermi 2 corrective action program.
3441999001 | Trojan | 02/26/1999 | 03/29/1999 | 9904060420 | <strong>An Unanalyzed Movement of a Non-Fuel Loaded Transfer Cask</strong><br /><i>Abstract:&nbsp;</i>On February 26, 1999, in the Fuel Building of the permanently defueled Trojan Nuclear Plant, an Independent Spent Fuel Storage Installation (ISFSI) rigging crew was performing pre-operational testing of the ISFSI Transfer Cask (TC) Lift System in accordance with an approved procedure. During the test, the test-weight loaded TC was lifted above its analyzed limit while over the dry Cask Load Pit (CLP), which should also have contained water to minimize impact loading on the CLP. There was no fuel in the TC or in the CLP. The gate between the Spent Fuel Pool and the CLP was closed. There was no component failure during this event. This event is reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications. The event root causes were personnel error, inadequate training, and an inadequate procedure. A procedure limited TC height along a safe load path leading to and from the CLP, but was misinterpreted as not limiting TC height directly over the CLP. Also, the procedure did not implement a TC drop event calculation assumption that the CLP contain a level of water. A procedure change was made to clarify that TC lift height restrictions apply directly over the CLP and to require a specified CLP water depth for certain moves over the CLP. ISFSI rigging crews and engineering personnel were retrained.
3461999001 | Davis-Besse | 01/10/1999 | 02/05/1999 | 9902170250 | <strong>Failure to Comply With Technical Specification Action Statements</strong><br /><i>Abstract:&nbsp;</i>On January 10, 1999, valve CV5010E (Containment Air Sample Return line containment isolation valve) was declared inoperable following a stroke time surveillance test. Valve CV5010E was closed and its associated breaker (YF205) was opened to comply with TS 3.6.3.1 Actions Statements. At 1230 hours, when performing the tagging clearance for the CV5010E breaker, the wrong breaker (Y205) was opened which made the temperature controller for the Emergency Diesel Generator (EDG) #2 area ventilation dampers incapable of opening the dampers, which made EDG #2 inoperable. This was not recognized until 1642 hours; thus, the required actions of TS 3.8.1.1, Action h. were not taken within the required time. Also, because the Train 1 Containment Radiation Monitor and Containment Hydrogen Analyzer required by TS 3.4.6.1 and 3.3.3.6 were inoperable when EDG #2 became inoperable, TS 3.0.5 was not complied with to initiate action to place the plant in a mode in which the applicable LCO does not apply. Each of these failures to follow TS are reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's TS, and are the result of human errors to recognize that plant conditions required entry into TS action statements. Because of the short duration of the failure to follow TS and the mitigating factors regarding the EDG inoperability, public health and safety were not affected.
3461999002 | Davis-Besse | 02/08/1999 | 03/05/1999 | 9903170361 | <strong>Both Trains of Emergency Ventilation System Rendered Inoperable Due to Unattended Open Door</strong><br /><i>Abstract:&nbsp;</i>On February 8, 1999, with the unit in Mode 1 at 100 percent power, a Shield Building airtight door was discovered open and unattended. This door separates the safety-related Emergency Core Cooling System equipment from the non-safety-related equipment associated with the radioactive waste systems, and is normally kept closed to maintain Shield Building Integrity. With this door open and unattended, neither train of the Emergency Ventilation System would have been able to produce the negative pressure in the Shield Building required by the Technical Specifications. The door was immediately closed upon discovery. Based on the limited leakage design of the containment vessel, and since the Emergency Ventilation System remained capable of minimizing the unfiltered release to the environment due to containment vessel leakage during design basis accident conditions, this event had low safety significance. This condition, which is a result of human error, is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications, and in accordance with 10CFR50.73(a)(2)(vii) as condition that caused the inoperability of two independent trains of a single system designed to control the release of radioactive material.
3461999003 | Davis-Besse | 07/27/1999 | 02/13/2004 | ML04049019 | <strong>Failure to Perform Engineering Evaluation for Pressurizer Cooldown Rate Exceeding Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1999, it was determined that an excessive cool down of the pressurizer occurred during the plant shutdown for the mid-cycle outage that was conducted from April 23 to May 10, 1999. Initial resolution of the indicated overcooling condition was determined to not be valid because pressurizer pressure remained elevated. However, further review determined the observed indication was valid. The pressurizer cool down was 160 degrees F/hour, which exceeded the limit of 100 degrees F/hour permitted by Technical Specification (TS) Limiting Condition for Operation 3.4.9.2. The Actions for the TS required that an engineering evaluation be performed to determine the effects of an out-of-limit condition on the fracture toughness of the pressurizer. This was not performed prior to startup from the mid-cycle outage, and was reportable as operation in a condition prohibited by TS pursuant to 10 CFR 50.73(a)(2)(i)(B). An evaluation performed by the Nuclear Steam Supply System vendor concluded that there was no effect on the structural integrity or fracture toughness of the pressurizer. The cause of this event was determined to be inadequate procedural guidance during cool down. Required reading was provided to operators concerning the evaluation of the event. The procedure for cooling down the reactor coolant system and the pressurizer was modified to provide the necessary information.
3461999004 | Davis-Besse | 09/21/1999 | 10/21/1999 | ML99307000 | <strong>Minimum Licensed Operator Shift Staffing Deficiency Due to Inadequate Evaluation of Temporary Medical Condition</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1999, Davis-Besse Nuclear Power Station personnel identified in a Condition Report that the respiratory requirements of a Senior Reactor Operator (SRO) had not been appropriately coupled to the medical qualification requirements for performance of licensed duties. On August 8, 1999, the licensed operator was injured away from work. On August 17, the licensed operator took a biennial medical examination as required by 10CFR55.21, Medical Examination. At the medical examination, the operator was unable to pass spirometry testing. On August 31, Nuclear Operations Training received summary documentation of the licensed operator's physical results. On September 1, the operator was removed from Fire Brigade duties but remained on licensed operator duties. On September 4 and 5, the SRO stood watches in the Control Room. Since this licensed operator did not meet the required minimum medical qualification, there was no qualified SRO in the Control Room as required by Administrative Technical Specification 6.2.2.c. Since this condition is prohibited by the plant's Technical Specifications, it is reportable as a Licensee Event Report in accordance with 10CFR5O.73 (a) (2) (i) (B). The apparent cause of occurrence is that written communication and procedural guidance, for medical conditions affecting licensed duties, is inadequate. The relationship between spirometry testing and performance of licensed duties was not understood. Failure to remove the operator from licensed duties had no safety significance. The operator was removed from licensed duties pending further medical evaluation.
3461999005 | Davis-Besse | 10/27/1999 | 11/22/1999 | ML99340038 | <strong>Failure to Perform Technical Specification Required Action After Opening Breaker</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1999, with the unit in Mode 1 at approximately 100 percent power, the source breaker for Bus Tie Transformer BD was opened at approximately 1600 hours to perform preventative maintenance on the breaker. The opening of this breaker renders one of the two qualified offsite AC electrical power circuits inoperable per Technical Specification (TS) 3.8.1.1. The breaker was opened without referring to the Work Order for the maintenance and without utilizing station procedures. As a result of these errors, TS 3.8.1.1 action "a" was not initially entered when the breaker was opened, and the demonstration that the remaining AC sources remained operable was not initiated. When the need to perform the TS required actions within one hour of the breaker being opened was realized, there was insufficient time to perform the actions. While attempting to restore the breaker, a lockout of the transformer occurred, preventing restoration of the breaker to exit the TS within one hour. Since the TS required action to demonstrate the remaining AC sources remained operable was not completed within one hour, this event constitutes operation prohibited by the TS, which is reportable in accordance with 10CFR5O.73(a) (2) (i) (B). Management expectations for the operators when authorizing maintenance activities and altering plant configuration will be reinforced.
3481999001 | Farley 1 | 01/26/1999 | 02/22/1999 | 9903030292 | <strong>4160 Volt Breaker In A Non-Seismically Racked-Out Condition</strong><br /><i>Abstract:&nbsp;</i>On January 26, 1999, with Unit 1 operating at 100% power, it was determined did Farley Nuclear Plant (FNP) Unit 1 had been operating in a condition prohibited by Technical Specifications. A breaker in a cubicle adjacent to the cubicle which contains the tie breaker from an emergency diesel to the A train 4160 volt emergency bus was found to be racked in a non-seismic condition. The non-seismically racked breaker could have rendered the emergency diesel supply breaker to the A train 4160 volt emergency bus inoperable during a seismic event by impacting the tie breaker cubicle and generating vibrations which may have tripped protective relays. Even though the A train 4160 volt bus remained energized during the time in question, the bus was technically inoperable due to the potential threat from a seismic event. The non-seismically racked breaker had been racked-out in the non-qualified condition since January 14, 1999. The cause of this event was personnel error. Personnel involved failed to follow plant procedures which directed the breaker to be seismically racked-out. Contributing to this event was poor or inadequate communications between the Shift Supervisor (SS) and the System Operator (SO). Safety-related breaker cubicles that have not been modified to be seismically secure when racked-out have now been physically identified to require seismic racking. Operations personnel have been notified of the impact of non-seismically racked-out breakers on adjacent cubicles and additional training stressing the importance of complete communications has been issued. The system operator involved was coached on the importance of following procedures. The individuals involved and operating crews will be retrained on the importance of proper operational communications during operational activities and pre-job briefs. This training will be completed by April 1, 1999.
3481999002 | Farley 1 | 05/27/1999 | 06/25/1999 | 9907060154 | <strong>Unit 1 Reactor Trip Following Loss of the 1A Steam Generator Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On May 27, 1999 at 08:55, with turbine load being reduced rapidly as a result of loss of the 1A Steam Generator Feed Pump (SGFP), FNP Unit 1 Reactor tripped on Overtemperature Delta T (OT Delta T). At 08:54:15, while attempting to swap the on service SGFP oil cooler, oil pressure to the SGFP was momentarily lost resulting in a trip of the SGFP. In response to the SGFP trip, the operator performed a rapid manual turbine load reduction. Control rods inserted in automatic; however, due to the magnitude of the power mismatch, Reactor Coolant System (RCS) temperature rose rapidly and resulted in the OT Delta T Reactor Trip setpoint being reached. A pressurizer Power Operated Relief Valve (PORV) lifted prior to the trip and then closed as designed. This event was due to personnel error by the operator performing an excessive load reduction. This was complicated by the failure of the steam dump system to respond as quickly as designed. The loss of main feedwater abnormal operating procedure has been enhanced to provide additional guidance for a loss of a SGFP event. Operations and licensed personnel have been made aware of these changes. These procedure changes will be covered during appropriate simulator training on response to scenarios involving loss of a SGFP.
3481999003 | Farley 1, Farley 2 | 10/27/1999 | 11/16/1999 | ML99328030 | <strong>Control Room Ventialtion Radiation Monitors Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1008 on October 27, 1999, it was determined that Units 1 and 2 had been operated contrary to the requirements of Technical Specifications (TS). Actions of TS 3.3.3.1 require in part, with less than the minimum Control Room ventilation (CRV) radiation monitor channels OPERABLE, that compensatory actions be taken. The sampling points for the control room ventilation radiation monitors are located downstream of the computer room ventilation system inlet isolation damper, which is a source of outside air to the CRV system. Therefore, when the computer room ventilation system is secured, the control room ventilation radiation monitors are inoperable. The actual sampling location does not agree with the drawing that was used to prepare the CRV Operating procedures. Since it was not recognized that the computer room dampers being closed prevented outside air from reaching the radiation monitors, the CRV system operating procedure did not direct that actions required by TS be taken. This condition has existed since initial plant startup. The cause of this event was personnel error in that the discrepancy between design drawings was not identified, resulting in inadequate procedural guidance that has been incorrect since initial plant startup. However, the computer room HVAC has been normally maintained in continuous operation and CRV radiation monitor channels operable as required. The control room HVAC operating procedure has been revised to address the issue of radiation monitor inoperability when the computer room HVAC is shut down. Action has been initiated to correct the piping and instrument drawing and other related design document discrepancies. This action will be completed by March 1, 2000.
3521999002 | Limerick 1 | 03/03/1999 | 04/01/1999 | 9904120336 | <strong>Failure to Perform a Tech Spec Surveillance Required Locked Valve Inspection</strong><br /><i>Abstract:&nbsp;</i>On 3/03/99, during a generic implications review of Surveillance Tests (STs), station personnel found that ST-6-060-460-1, revision 29, did not contain a required inspection of one locked valve. Investigation revealed that valve HV-087-124A was properly inspected on 12/03/98, using ST-6-060-460-1, revision 28. On 12/10/98, the ST was revised and the inspection requirement for valve HV-087-124A was deleted from the procedure. ST-6-060-460-1, revision 29 was performed on 1/07/99 and 2/04/99. Failure to inspect valve HV-087-124A involves a condition prohibited by Technical Specifications. This event was caused by personnel error during the typing of the revision, and due to a less than adequate review of the typed ST revision. A temporary change to the procedure was initiated, and HV-087-124A was checked and verified to be in its required locked closed position. Completed corrective actions include revision of ST-6-060-460-1, discussion of the event with the involved personnel, and review of other surveillance tests. Planned corrective actions include an evaluation of the procedure revision process for possible improvements and communication of the circumstances of this event with personnel who revise procedures.
3521999003 | Limerick 1 | 04/20/1999 | 05/19/1999 | 9905280183 | <strong>RPS and PCRVICS Actuations due to Loss of Feedwater Flow Transient Caused by Spuriously Opening Breaker</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1999, at 1830 hours, Limerick Generating Station (LGS) Unit 1 was operating at 100% power when a loss of feedwater was experienced. The Main Control Room received a condensate filter trouble, a Reactor Low Level, and Loss of Feedwater alarms. All three Reactor Feed Pumps tripped on low suction pressure causing a reactor SCRAM when level decreased to + 12.5 inches. The Reactor Protection System actuation is reportable pursuant to 10CFR50.73(a)(2)(iv). The low reactor water level Reactor Protection System actuation occurred due to a spurious tripping of a breaker that supplies position indication to the inlet valves of the Deep Bed Condensate Demineralizer System (DBCDS). Loss of inlet position indication to the DBCDS programmable logic controller created a signal for the deep bed outlet valves to close. The resultant rapid increase in differential pressure at the DBCDS bypass valves prevented their ability to be opened and maintain flow to the Reactor Feed Pumps and the reactor. This event is bounded by the previously analyzed loss of feedwater flow transient as described in the LGS Updated Final Safety Analysis Report (UFSAR). The plant responded as designed to a loss of feedwater flow. The DBCDS breaker that spuriously tripped was replaced and the DBCDS breakers for the outlet valves were procedurally opened to prevent closure. This event resulted in High Pressure Core Injection, and Reactor Core Isolation Cooling injections into the Reactor Coolant System. SPECIAL REPORT information required pursuant to Technical Specification (TS) 6.9.2 and TS Limiting Conditions for Operation ACTION statements 3.5.1.f and 3.7.3.b is included in this report.
3521999004 | Limerick 1 | 06/06/1999 | 07/01/1999 | 9907080382 | <strong>Automatic Depressurization System (ADS) inoperable During planned maintenance and the applicable Technical Specification Action was not met</strong><br /><i>Abstract:&nbsp;</i>On 06/04/99, an engineering review of Tech Specs, UFSAR, and Design Bases Documents determined that the backup instrument gas bottles are required to support ADS valve operability. It was subsequently determined that clearances had previously been applied that removed a portion of the backup instrument gas bottles from service for greater than the TS LCO allowed outage time. On 06/2/99, an Operations Shift Manager questioned work in progress that resulted in the ADS backup bottle low pressure alarm annunciating. The operating shift determined that a clearance applied to perform a preventive maintenance test on a nitrogen (N2) supply relief valve isolated a portion of the ADS N2 back-up bottles. Based on a concern for the system's operability, the shift stopped work, removed the clearance, and restored the system. The system was out of service for 6 hours and 28 minutes which is less than the 12 hour LCO allowed outage time. The investigation of this event resulted in the discovery of the aforementioned reportable conditions. The Unit 1 and Unit 2 ADS systems were not identified as inoperable during the performance of the preventive maintenance task due to inadequate review of operability requirements and inadequate planning and scheduling of system preventive maintenance.
3521999005 | Limerick 1 | 06/11/1999 | 07/09/1999 | 9907160174 | <strong>RPS and ESF Actuations Caused by Personnel Error During Turbine Routine Testing</strong><br /><i>Abstract:&nbsp;</i>On June 11, 1999 at 19:29 hours, Limerick Generating Station (LGS) Unit 1 was operating at 100% power. An equipment operator performing a routine test, "Backup Overspeed And Power/Load Unbalance Test" in the auxiliary equipment room failed to place the backup overspeed trip interlock keylock switch to the "TEST" position before depressing the test push button. Failing to bypass the interlock resulted in a Turbine Stop Valve Fast Closure Scram signal. The weekly test verifies proper function of the Backup Overspeed Trip Circuit and Power/Load Unbalance Trip Circuit for continued reliable operation of the main turbine. The root cause for the turbine trip and subsequent reactor scram was personnel error. The plant was brought to a normal, safe shutdown condition and the appropriate notifications were made. There was no effect on the safe operation of the plant. Reactor Protection System (RPS) and Engineered Safety Feature (ESF) actuations as a result of this event are reportable pursuant to 10CFR50.73(a)(2)(iv).
3521999006 | Limerick 1 | 06/14/1999 | 07/12/1999 | 9907190224 | <strong>Late Performance of a Tech Spec Action Required Offgas Grab Sample with Offgas Hydrogen Analyzers Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 06/14/99 at 0100 hours, during plant startup an Equipment Operator on rounds determined that all three Unit 1 offgas hydrogen analyzers (EIIS:AIT) were in air purge mode and not in service as required by Technical Specifications 3.3.7.12 and 3.11.2.5 when the offgas system (EIIS:WF) is operating. The plant integrated startup procedure step which directs placing the offgas analyzers in service had been signed off in error by operations supervision. A review of plant records and Main Control Room indications was used to complete the step which directs I&C personnel to place the analyzers in service. All three offgas hydrogen analyzers had been placed in air purge mode during the previous plant shutdown as directed by approved procedure. The cause of this event was a personnel error. A contributing factor to the error was a lack of specific detail in a procedure. Completed corrective actions include restoring an analyzer to operable status, counseling the individual, briefing the operations staff on the event and revision of the affected procedures. Operator training on the lessons learned is planned.
3521999007 | Limerick 1 | 06/17/1999 | 07/14/1999 | 9907200199 | <strong>Inadvertent Emergency Service Water Pump Start During Test Equipment Installation</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1999 at 10:00 hours, while supporting a routine test for overspeed surveillance testing of the D23 Emergency Diesel Generator (EDG), an inadvertent speed signal was input to the Emergency Service Water (ESW) pump starting logic, causing the 'C' ESW pump (EIIS:BI) to start. The cause of the event was personnel error by an Instrument and Control (I&C) technician. Field test equipment had been altered by the attachment of a signal generator onto the test equipment to perform training. The signal generator inserted onto the test equipment was set to simulate a 900 revolutions per minute (rpm) signal. When the test equipment was hooked to the test circuitry as directed by the test, the 'C' ESW pump started. The ESW system responded as expected. The cause of the event was personnel error. The I&C technician failed to verify the proper set-up of test equipment prior to commencement of the test. Also, the test procedure was deficient in that it failed to contain sufficient instructions to install the test equipment or a caution to verify that no output is present prior to installing test equipment. The corrective actions included counseling the employee, and revision of the routine test to add a caution to verify that no output is present prior to installing the test equipment. Long range corrective actions include revising the remaining EDG overspeed tests to add the above caution and verify no output is present prior to installing test equipment, and checking other I&C procedures for proper test equipment installation. The start of the ESW pump is an ESF actuation, reportable pursuant to 10CFR50.72(b)(2)(ii).
3521999008 | Limerick 1 | 06/23/1999 | 07/23/1999 | 9907270252 | <strong>Unit 1 HPCI failed to start During the performance of a surveillance test</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1999, at 0407 hours, Unit 1 HPCI failed to start during the performance of a surveillance test (ST). At the time of the failure, Unit 1 HPCI was inoperable for planned maintenance. HPCI failed to start when the turbine control valve did not open in response to a manual initiation signal. Investigation into the event determined that corrosion products caused binding in the Hydraulic Actuator (EGR). The EGR was replaced, the ST was re-performed and HPCI was declared operable on June 25, 1999.
3521999011 | Limerick 1, Limerick 2 | 09/23/1999 | 10/22/1999 | ML99307000 | <strong>Unusual Event declared due to detection of toxic gas within the site area boundary.</strong><br /><i>Abstract:&nbsp;</i>On 09/23/99 at 18:45 hours, the oncoming shift of Main Control Room (MCR) operators detected a rotten egg like odor present in the Unit 2 Turbine Enclosure. At 1 9:22 hours the MCR operators, as a precautionary measure, placed the MCR ventilation system in the Chlorine Isolation mode by manual actuation of the chlorine isolation logic. At 20:00 hours the shift Manager declared an Unusual Event due to detection of toxic gas within the site area boundary in amounts that could affect normal operation of the plant. At 23:12 hours the Unusual Event was terminated when the odor was no longer detectable. The apparent source of the odor was a sewage disposal truck that arrived on site coincident with detection of the odor.
3521999012 | Limerick 1 | 09/25/1999 | 10/22/1999 | ML99307022 | <strong>Unit 1 Reactor Core Isolation Cooling (RCIC) PCIV discovered inoperable resulting in a TS non-compliance</strong><br /><i>Abstract:&nbsp;</i>On September 25, 1999 at 1 8:00 hours, an operations supervisor discovered that the Unit 1 RCIC vacuum breaker outboard primary containment isolation valve (PCIV) isolation logic had been inoperable for a period that exceeded the Technical Specification (TS) allowed outage time (AOT). This discovery occurred during a review of historical clearance data. This event was caused by personnel error when logic control fuses were removed without accounting for the effect on the isolation logic portion of the circuit.
3521999013 | Limerick 1, Limerick 2 | 10/28/1999 | 11/10/1999 | ML99324032 | <strong>Credible Bomb Threat Received Resulting in an Unusual Event Emergency Classification</strong><br /><i>Abstract:&nbsp;</i>On 10/28/99 at 02:55 hours, Montgomery County Police notified the Main Control Room (MCR) of a bomb threat they received involving Limerick Generating Station. At 03:35 hours, the bomb threat was determined to be credible and an Unusual Event was declared. The plant protected area was searched and no suspicious devices were discovered. The bomb threat was analyzed by law enforcement authorities and determined to be not credible. At 11:24 hours, the Unusual Event was terminated.
3521999014 | Limerick 1, Limerick 2 | 04/08/1993 | 11/24/1999 | ML99336022 | <strong>Fuel Shipping Cask Lifted from Rail Car Without Refueling Area Secondary Containment Integrity Established</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1999, an event investigation due to current spent fuel shipping activities determined that previous receipt and handling of 33 Shoreham irradiated fuel casks was not in conformance with the plant design bases and Technical Specifications (TS). During receipt of Shoreham irradiated fuel assemblies in 1993 and 1994, the fuel shipping casks were handled without secondary containment integrity established. In addition, a portion of the fuel shipping cask handling activity was performed without redundant rigging, contrary to the requirements specified in the plant Updated Final Safety Analysis Report (UFSAR).
3531999001 | Limerick 2 | 01/21/1999 | 02/17/1999 | 9902250333 | <strong>Unavailabilities of Safe Shutdown Equipement in the Event of a Fire Due to Inadequate Circuit Breaker Coordination for the 2B Reactor Enclosure Cooling Wate Pump</strong><br /><i>Abstract:&nbsp;</i>On 01/22/99, an Engineering review determined that in the event of a fire in Fire Area 64, "Reactor Enclosure Cooling Water Equipment Area," fire-induced damage to an auto-start pressure switch in the control circuit for the 2B Reactor Enclosure Cooling Water (RECW) pump could create a hot short that would cause the pump to auto-start, if the pump control switch is in the 'RUN' or 'AUTO' position. Additionally, the same fire could induce a fault in the 480 VAC power cable to the pump motor which could open the load center (LC) breaker to its associated motor control center (MCC). This would result in the loss of equipment required for safe shutdown in the event of a fire in that area. This condition is due to less than adequate circuit breaker coordination between the MCC and LC breakers. This represents a condition that is outside the design basis of the plant and is a violation of LGS, Unit 2, Operating License Condition 2.C.(3). This condition is reportable in accordance with the requirements of License Condition 2.E for Unit 2 and 10CFR50.73(a)(2)(ii)(B). The potential consequences of this event are minimal based on design and administrative features of the Fire Protection Program. Compensatory measures were put in place until the MCC breaker settings were reset on 01/29/99 to provide the proper coordination.
3531999002 | Limerick 2, Limerick 1 | 04/19/1999 | 05/18/1999 | 9905240111 | <strong>Various ESF Actuations Due to the Loss of Power to the 2A RPS/UPS Distribution Panel Caused by a Loose Bus Bar Connection in the RPS Breaker Panel</strong><br /><i>Abstract:&nbsp;</i>On 4/19/99, at 0438 hours, a loss of power to the 2A Reactor Protection System (RPS) / Uninterruptible Power Supply (UPS) power distribution panel occurred. The loss of power caused automatic actuations of several Unit 2 and common Engineered Safety Features, including the Primary Containment and Reactor Vessel Isolation Control System. Operations personnel responded to the event using existing procedures. All systems responded as designed during the loss of power event. The cause of this event was a loose bus-bar connection resulting from a marginal connection during initial installation combined with subsequent thermal cycling of the copper stud due to load variations during normal operation. Completed corrective actions were rework of the bus-bar connection and thermography inspection of the bus-bar connections of the other RPS/UPS panel power supply breakers. Routine thermography inspection of the RPS breaker bus-bar connections has been included in the preventive maintenance program.
3531999003 | Limerick 2 | 06/07/1999 | 07/07/1999 | 9907130111 | <strong>Bypass of Reactor Water Cleanup System Leak Detection System Isolation functions on three seperate occasions.</strong><br /><i>Abstract:&nbsp;</i>In March 1999, a review by the Nuclear Quality Assurance organization questioned the use of jumpers on the Reactor Water Cleanup (RWCU) System (EIIS:CE) at LGS in Operational Conditions 1, 2, or 3, and whether an appropriate 10CFR50.59 Review had been performed to support this activity. An investigation was initiated involving the use of the jumpers. Immediate corrective actions were taken to revise the system operating procedure to preclude the use of the jumpers in Operational Conditions 1, 2, or 3. Subsequently, on June 7, 1999, it was determined that on three occasions (i.e., July 23, 1998, September 17, 1998, and September 28, 1998), while placing the Unit 2 RWCU System in service, the RWCU System Leak Detection System isolation functions were bypassed creating a condition that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident and control the release of radioactive material. The primary cause of this event was the inadequate review and approval of a change to a system operating procedure. The actual impact of the event was limited and had low risk significance. Station personnel were informed of the immediate concerns of this event, as an interim corrective action. A multidiscipline team was assembled to perform a formal root cause analysis. A review has been completed of selected plant operating and test procedures which had the potential to be generically affected in a similar fashion. No additional instances of inappropriately bypassing required safety functions were identified wherein the plant was placed outside its design basis.
3531999004 | Limerick 2 | 07/01/1999 | 07/23/1999 | 9907270279 | <strong>Thirteen Main Steam Relief Valves (SRV) Failed to Meet 1% Setpoint Tolerance due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On 07/01/99, Engineering was informed that as-found test results for 13 of 14 Main Steam (EIIS:SB) Safety Relief Valves (SRVs) (EIIS:RV) did not meet the 1 % setpoint tolerance of Tech Spec 3.4.2. The 14 SRVs were replaced during the 5th Unit 2 refueling outage (2R05) in May 1999. The condition of the 13 SRVs resulted in more than 2 independent trains in a single safety system becoming inoperable from a common cause. The consequences were minimal since no challenges to the overpressure protection system occurred. The 21105 SRV setpoint drifts are bounded by a previous analysis performed following 2R04. The plant overpressure analysis was met. The SRVs are Target Rock Corp. Model 7567F pilot operated two-stage valves. The setpoint drift resulted from corrosion induced bonding between the pilot disc and seat. All fourteen (14) Unit 2 SRVs were replaced with three-stage Target Rock SRVs prior to restart. On Unit 1, all 1 4 SRV pilot valves were replaced with calibrated spares during 1R07. Six (6) of the 14 Unit 1 SRVs have a modified platinum surface treatment on the pilot disc which has been proven successful at the Brunswick plant.
3531999005 | Limerick 2 | 07/12/1999 | 08/10/1999 | 9908160049 | <strong>PCIV Isolation, ESF Actuation due to a Failed Fuse (cold solder joint failure)</strong><br /><i>Abstract:&nbsp;</i>On July 12, 1999, at 01:46 hours, various actuations of the Unit 2 Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) occurred due to a blown fuse. During this event, three Primary Containment Isolation Valves (PCIVs) isolated as designed. These isolations are reportable as Engineered Safety Feature (ESF) actuations. The cause of the blown fuse was a mechanical failure of a cold solder joint. Fuse replacement and isolation reset was complete within three hours and 22 minutes. The actual consequences of this event were minimal. All affected systems responded as designed and there was no release of radioactive material to the environment as a result of this event.
3541999001 | Hope Creek | 01/11/1999 | 02/08/1999 | 9902180298 | <strong>Unplanned Inoperability of the Reactor Core Isolation Cooling System</strong><br /><i>Abstract:&nbsp;</i>On January 11, 1999, Hope Creek operators received an overhead alarm associated with the Reactor Core Isolation Cooling (RCIC) System isolation actuation instrumentation system. The operators concluded that the RCIC isolation actuation instrumentation was inoperable due to a failed power supply. In response to this condition, operators took the actions delineated in Technical Specification 3.3.2.b.2 (ACTION 23) and closed the outboard RCIC steam isolation valve (F008) within the one hour timeframe specified. The closure of the outboard RCIC steam line isolation valve (F008) required the operators to declare RCIC inoperable. Since the inoperability of RCIC represented a condition that prevented the fulfillment of a safety function of a system that is needed to remove residual heat and maintain the reactor in a safe shutdown condition, a four hour notification was made to the NRC at 1901 hours in accordance with 50.72(b)(2)(iii). The cause of the unplanned RCIC inoperability was attributed to the isolation logic circuitry power supply failure. Corrective actions included the successful installation and testing of a new RCIC isolation actuation logic instrumentation power supply.
3541999002 | Hope Creek | 12/23/1998 | 03/02/1999 | 9903110245 | <strong>Missed Technical Specification Surveillance - "B" Safety Auxiliaries Cooling System (SACS)</strong><br /><i>Abstract:&nbsp;</i>On February 6, 1999, PSE&G discovered that flowpath verification for the "B" Safety Auxiliaries Cooling System (SACS) had not been performed within the periodicity required by the Technical Specifications. At 2000 on February 6, 1999 the "B" SACS was declared inoperable and the Technical Specification action statement was entered. The flowpath verification was successfully completed, "B" SACS was declared operable and the Technical Specification action statement was exited at 2051 on February 6, 1999. A determination of the extent of the problem revealed that the December 1998 and January 1999 "B" SACS flowpath verifications had not been performed as required resulting in the "B" SACS being inoperable as of December 23, 1998. The cause of this event is personnel error. Corrective actions include revision of the routine tasks and work orders that initiate the performance of flowpath verification, and review of the surveillance procedure used to perform the verification for possible enhancements. There was no impact on the health and safety of the public due to this event as the "B" SACS was properly aligned during the period of non-compliance.
3541999003 | Hope Creek | 02/28/1999 | 03/26/1999 | 9904060405 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specifications Allwoable Limits</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1999, the results of the Safety Relief Valve (SRV) setpoint testing were received. The testing revealed that, following Cycle 8, 6 of the 14 SRVs experienced setpoint drift outside of the Technical Specification limit of +/- 3%. Three of the failures were of valves with pilot discs that were modified with platinum ion implantation, and the drift for these valves appears to have been caused by friction on the sliding surfaces resulting from less than adequate maintenance performed by the valve vendor. The cause of the drift for the other three valves is most likely corrosion bonding of the pilot disc to the pilot seat. The SRVs were inspected, refurbished and satisfactorily re-tested at a test facility. SRV drift in 2 stage Target Rock valves is being addressed generically by the Boiling Water Reactor Owners Group. Platinum ion implantation was implemented on 7 SRVs during the seventh refueling outage and has been implemented on 6 of the remaining 7 SRVs during the current refueling outage. The results of the platinum ion implantation will be further evaluated after Cycle 9 for its effectiveness at reducing setpoint drift. The valve vendor has been notified of the concerns with the maintenance activities. PSE&G will work with the vendor to ensure that adequate corrective action is taken prior to allowing the vendor to perform additional work for Hope Creek.
3541999004 | Hope Creek | 03/09/1999 | 04/08/1999 | 9904130064 | <strong>Check Valves for Containment Atmosphere Control System Vacuum Breaker Isolation Valve Accumulator Did Not Meet The Leakage Requirements During Testing</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1999, the check valves for the "A" Containment Atmosphere Control System Vacuum Breaker Isolation Valve Accumulator did not meet the leakage requirements during testing. Previously, on February 23, 1999, one of the check valves for the "B" accumulator on the redundant vacuum breaker assembly had failed to meet the leakage requirements. The accumulators provide a backup to the instrument air system for opening the Containment Atmosphere Control System Vacuum Breaker Isolation Valves. The failures on March 9 coupled with the performance history of the valves and the subsequent determination of the cause resulted in PSE&G determining that there was firm evidence to believe that the condition existed during the previous operating cycle. The cause of the failures was attributed to improper selection of valve type in that the metal-seated valves that were installed were not the proper design to provide leak tight service in the low pressure air system. During the eighth refueling outage, the valve discs of the three check valves that failed the leak tests were replaced with a soft seat design allowing the valves to pass the testing. The disc of the one remaining check valve will be replaced no later than the ninth refueling outage.
3541999005 | Hope Creek | 03/24/1999 | 04/21/1999 | 9904290169 | <strong>Technical Specification Prohibited Condition - Inadequate Secondary Containment Surveillance Tests</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1999, Engineering confirmed that the 18 month Reactor Building Integrity Function Test procedure, HC.OP-ST.GU-0002, Rev. 4, did not adequately verify the leak integrity of Hope Creek's Secondary Containment. Engineering concluded that under post-LOCA conditions, with outside air temperature significantly lower than the Secondary Containment temperature, vertical variation of pressure inside and outside the Reactor Building would occur. Consequently, the differential pressure in the upper portions of the reactor building would be greater (less vacuum) than the 0.25-inch w.g. vacuum maintained by the Filtration, Recirculation and Ventilation System (FRVS) at the elevation where the reactor building differential pressure sensor penetration is located (174 foot elevation). As a result, Technical Specification Surveillance Requirements 4.6.5.1.c.1 & 2, which demonstrate Secondary Containment integrity, were not adequately satisfied. The cause is attributed to personnel error during the original implementation of design and licensing basis requirements for FRVS. Corrective actions included design calculation and surveillance procedure revisions to ensure that a 0.25-inch w.g. vacuum is maintained with the Secondary Containment volume under worst case postulated conditions.
3541999006 | Hope Creek | 05/18/1999 | 06/15/1999 | 9906220249 | <strong>Engineered Safety Function Actuation - "B" Channel Primary Containment Isolation Signal Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1999, at 0907 hours, while operators were de-energizing the "B" channel Radiation Monitoring System (RMS) to replace a power supply, an unexpected actuation of the "B" channel Primary Containment Isolation System (PCIS) occurred. The single channel actuation resulted in isolation of three containment isolation valves, electrical load shedding of two non-1E Reactor Building ventilation fans, an automatic start of the "B" channel Filtration, Recirculation and Ventilation System fans, and a start of the "B" Safety Auxiliaries Cooling System pump. The isolations and actuations occurred as designed, with minimal impact on power operation. By 1223 hours, operators re-energized the "B" channel RMS power supply and restored the affected plant systems and components. In accordance with 10 CFR 50.72(b)(2)(ii), this event was reported to the NRC as an event or condition that results in a manual or automatic actuation of any ESF. The cause of the unexpected ESF signal is attributed to a knowledge based personnel error. Operations personnel performed an inadequate review of the RMS power supply replacement. Corrective actions included the providing of additional training to Operations personnel concerning the RMS power supply replacement evolutions.
3541999007 | Hope Creek | 06/14/1999 | 07/14/1999 | 9907220110 | <strong>License Condition Violation - Class 1E Battery Charging Operation</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1999, at approximately 0720 hours, Hope Creek personnel identified that the configuration of a Class-1E battery, undergoing a single cell charge, did not conform to requirements for single cell charging. Specifically, from June 7, 1999 to June 14, 1999, a non-1E battery charger was connected to a Class-1E battery without installing at least two Class-1E fuses in series on both the positive and negative output leads of the battery charger. At approximately 0730 hours, the battery charger was removed from battery 1C-D-411. Hope Creek Technical Specification Amendment No. 114 included a license condition that required use of this double fuse protection when performing single cell charging on OPERABLE Class-1E batteries. Since the single cell charging performed during June 7-14 did not comply with this license condition requirement, a 24-hour report was made to the NRC at 1657 hours in accordance with Hope Creek Operating License Condition 2.F. The cause of this event is attributed to inadequate procedure development, use and compliance skills by the Maintenance personnel involved. Corrective actions include procedure revisions and personnel accountability for inappropriate actions in accordance with PSE&G procedures and policies.
3541999008 | Hope Creek | 08/17/1999 | 09/16/1999 | 9909270193 | <strong>License Condition Violation - Fire Protection Program</strong><br /><i>Abstract:&nbsp;</i>License Condition 2.C(7) states that Public Service Electric and Gas shall implement and maintain in effect all provisions of the approved fire protection program as described in the Final Safety Analysis Report for the facility through Amendment 15. Although one of these provisions is that the Control Equipment Mezzanine floor drains are normally closed to prevent carbon dioxide fire suppression agent dissipation, no provision had been implemented to maintain the Control Equipment Mezzanine floor drain valve in the closed position. On August 17, at 1253, the Control Room was notified that the Control Equipment Mezzanine floor drain valve was found to be in the open position. The valve was closed promptly and a 24-hour report was made to the NRC in accordance with License Condition 2.F on August 18, at 1200. The cause of this event is the failure to include the Control Equipment Mezzanine floor drain valve in the tagging control system and the failure to appropriately label it during the construction and pre-operational phase of the plant. Corrective actions included closing the valve, validating that similar valves were closed and in the tagging control system, labeling the valve, and including it in the tagging control system.
3541999009 | Hope Creek | 08/20/1999 | 09/20/1999 | 9909280380 | <strong>License Condition Violation - Minimum Feedwater Temperature Limits</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1999, at 2358 hours, a lightning strike caused a momentary loss of a 500kv offsite transmission line. The associated electrical transient resulted in trips and automatic initiation of several plant systems. These equipment malfunctions resulted in a safety lockout of the Primary Containment Instrument Gas (PCIG) compressors and the isolation of the number 6 Feedwater Heaters. As a result, the plant entered into Technical Specification 3.0.3 for two inoperable Main Steamline Isolation Valve (MSIV) Sealing System subsystems and violated the Operating License condition for required minimum feedwater heater capacity. A less than adequate operator response to the plant transient perpetuated the license condition violation for approximately six hours following the initiating lightning strike. As a result of the Operating License condition violation, a 24-hour report was made to the NRC on August 21, 1999, at 1627 hours, in accordance with Hope Creek Operating License Condition 2.F. Corrective actions included the recovery and restoration of plant systems affected by the electrical transient. The Corrective Action Program is also being utilized to investigate and evaluate the operator response to this transient.
3541999010 | Hope Creek | 08/31/1999 | 09/29/1999 | 9910130065 | <strong>Engineered Safety Feature Actuation - Reactor Core Isolation</strong><br /><i>Abstract:&nbsp;</i>On August 31, 1999, the Hope Creek Generating Station was preparing to enter Operational Condition 1, POWER OPERATION, following a maintenance outage. During warm-up of the Reactor Core Isolation Cooling (RCIC) system, an automatic isolation signal was received at 1105 hours. Although the RCIC Isolation Actuation Instrumentation was required to be operable, the RCIC system was not required to be operable at the time the isolation signal was received since reactor pressure was below 150 psig. Plant Technical Specifications require RCIC to be operable with reactor pressure above 150 psig. In accordance with procedures, operators determined that a RCIC steam line break did not occur, re-set the isolation signal, and completed the warm-up of the RCIC steam lines. At 1355 hours, a four hour report was made to the NRC for this Engineered Safety Feature (ESF) actuation in accordance with the requirements of 10CFR50.72(b)(2)(ii). The cause of the event was attributed to steam flashing resulting in spurious steam line pressure signals. Corrective actions included placing RCIC in standby service.
3541999011 | Hope Creek | 09/19/1999 | 10/19/1999 | 9910280165 | <strong>Unplanned Inoperability of the High Pressure coolant Injection System due to a Failed Trip Unit</strong><br /><i>Abstract:&nbsp;</i>On September 19, 1999, during the performance of a sensor calibration on a High Pressure Coolant Injection (HPCI) Turbine Exhaust Pressure Transmitter, an unexpected alarm, a HPCI Turbine trip signal, was received in the control room and did not clear when the sensor calibration was completed and the channel was returned to its normal condition. The HPCI system was declared inoperable at 1630. A 4-hour notification was made to the NRC at 1713 in accordance with 10CFR50.72(b)(2)(iii) for the unplanned unavailability of a single train safety system. The cause of this event is the failure of a trip unit associated with the HPCI Turbine Exhaust Pressure Transmitter. A contributing cause is the failure to include a periodic leakage check in maintenance procedures for this trip unit when the failure mode for this event was previously identified in a 10CFR21 notification. The specific failure mode of the trip unit was excess output current leakage from an output transistor on the trip unit. Corrective actions include restoring the HPCI system to an operable status and revising procedures.
3541999012 | Hope Creek | 10/17/1998 | 11/16/1999 | ML99330024 | <strong>Inadequate Performance of Primary Containment Integrity Verification</strong><br /><i>Abstract:&nbsp;</i>On October 18, 1999, PSE&G discovered that containment isolation valve position verification was not performed properly for eleven valves during several monthly verifications conducted in the last year. The eleven valves are used for Type B containment penetration leak rate testing. The apparent cause for this event was an inadequate revision to the surveillance procedure for PRIMARY CONTAINMENT INTEGRITY verification. Corrective actions included field verification that the valves were closed and revisions to the surveillance procedure for PRIMARY CONTAINMENT INTEGRITY. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications.
3611999001 | San Onofre 2 | 02/01/1999 | 03/03/1999 | 9903110295 | <strong>Automatic Start of an Emergency Diesel Generator (EDG)</strong><br /><i>Abstract:&nbsp;</i>On 2/1/1999 (event date), Unit 2 was in Mode 6 (000 percent power) for a planned refueling outage. At 0959 PST, while removing a supply breaker for a 4.16 kV Class 1E bus from its cubicle, a worker discharged the breaker's closing springs, closing the breaker. As a result, power was lost to the bus, Shutdown Cooling was lost, and the Emergency Diesel Generator started. Southern California Edison (SCE) promptly notified the NRC Operations Center (NRC Event Log Number 35336) that an Unusual Event had been declared for the loss of Reactor Coolant System heat removal capability for greater than 10 minutes (10CFR50.72(a)(i)) and an Engineered Safety Feature actuation (10CFR50.72(b)(2)(ii)). This LER is provided in accordance with 10CFR50.73(a)(2)(iv), 10CFR50.73(a)(2)(v), and 10CFR21. All equipment operated as expected. Operators restored SDC in approximately 26 minutes. SCE has implemented or planned corrective actions to prevent recurrence. The incremental increase in core damage probability was "very small." In the past 3 years, SCE has not reported an event with similar causes and corrective actions.
3611999002 | San Onofre 2 | 02/08/1999 | 03/10/1999 | 9903160351 | <strong>Pressurizer Safety Valves Above Tech Spec Limit due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>During the Unit 2, Cycle 10 refueling outage, the 2 pressurizer (AB,PZR) safety valves (PSVs) (RV) were shipped to NWS Technologies in Spartanburg, SC, for as-found setpoint tests required by the Inservice Testing Program. On 2/8 and 2/9, the valves' as-found lift setpoints were determined to be 2533 psia (2PSV-0200) and 2551 psia (2PSV-0201), which are above the Technical Specification (TS) setpoint band of 2500 psia +/-1 percent. Subsequent lift tests performed on both valves prior to rebuilding/resetting were within the TS setpoint band. Because it is likely that one, or both, were outside the TS limits longer than 15 minutes during Cycle 9, Mode 1 operation, Southern California (SCE) is reporting this event in accordance with 10CFR50.73(a)(2)(i). SCE confirmed the valves were set correctly at the beginning of Cycle 9. The cause of the high setpoint was setpoint drift. There was no safety significance to this event. Both valves' as-found setpoints are bounded by an existing analysis confirming the TS setpoint can be expanded to +3/-2 percent. SCE submitted a license amendment application on 9/4/1998 requesting the tolerance be changed to +3/-2 percent. In the last 3 years, SCE has submitted 3 LERs on out of tolerance PSVs: 3-96-002, 2-97-003, 3-97-003-01.
3611999003 | San Onofre 2, San Onofre 3 | 02/10/1999 | 03/12/1999 | 9903250219 | <strong>CCW non critical loop isolation valves inoperable due to previously unrecognized instrument air configuration anomaly</strong><br /><i>Abstract:&nbsp;</i>On February 7, 1999, while Unit 2 was shutdown for its Cycle 10 refueling outage, the Component Cooling Water Non-Critical Loop (CCW-NCL) isolation valves failed to satisfy close stroke time requirements during a pneumatic supply test. Subsequent investigations determined that the corresponding valves in Unit 3 might not satisfy stroke time requirements. On February 10, 1999, the non critical loop valves at Unit 3 were declared inoperable and the unit entered a 72-hour action statement. The cause of this condition was that instrument air failure modes other than a loss of pressure were not adequately considered in the original design of the CCW-NCL valves. Design modifications were implemented on both units to correct a previously unrecognized condition associated with a blockage of the non-seismic pneumatic supply. There was minimal safety significance to this occurrence.
3611999004 | San Onofre 2, San Onofre 3 | 07/08/1999 | 08/06/1999 | 9908100039 | <strong>Automatic Toxic Gas Isolation System (TGIS) Actuation</strong><br /><i>Abstract:&nbsp;</i>At 2035 PDT on July 8, 1999, Toxic Gas Isolation System (TGIS) Train A actuated on high ammonia concentration, greater than 100 parts per million (ppm) The recorded butane concentration increased to 24 ppm. Both analyzers subsequently trended back to background over an approximate fifteen minute period. The TGIS Train A trouble alarm (from high ammonia) cleared in approximately five minutes. In accordance with 10 CFR 50.72 (b) (2) (ii), SCE reported this event to the NRC at 2310 PDT as a valid ESF actuation. SCE is submitting this 30-day follow-up report in accordance with 10 CFR 50.73 (a) (2) (iv). Immediately prior to the TGIS actuation, an HVAC technician had been venting refrigerant R-22 (Freon) from hoses which had been recently used for maintenance. While investigating this event, SCE found a small leak in the suction side of the TGIS Train A sample pump which could provide a pathway for the Freon to enter the TGIS. Consequently, SCE believes that the Freon caused the TGIS Train A actuation. SCE repaired the leaking suction side of the TGIS Train A sample pump. This small release of Freon did not impact plant operation beyond the TGIS actuation. All TGIS Train A components performed as required. Additionally, this event was evaluated using the NRC's Significance Determination Process, and screens out as "GREEN."
3611999005 | San Onofre 2, San Onofre 3 | 08/31/1999 | 09/23/1999 | 9909270188 | <strong>Loss of Physical Separation in the Control Room</strong><br /><i>Abstract:&nbsp;</i>SCE is currently replacing the radiation monitors and associated control room instrument cabinets. To implement the new design, the old panels, 2L103, 3L103, and 2/3L104, had to be removed and new panels set in their place. On 8/31/99, shortly before midnight, the shift manager and the shift technical advisor discovered Trains A, B, and X instrumentation, control, and power cables lying adjacent to each other. The area of concern is in the "block out" where the cables come through the control room floor from the 9-foot cable spreading room. SCE declared affected equipment inoperable and placed Train A of the Control Room Emergency Air Cleanup System (CREACUS) in operation. On 9/1/99, at 1526 PDT, SCE considered that this condition was reportable in accordance with 10CFR50.72(b)(1)(ii)(B) as a condition "outside the design basis of the plant." SCE provided a one-hour report to the NRC Operations Center at 1624 PDT (Log #36112). While subsequent evaluations indicated this condition may not have been "outside the design basis of the plant," SCE is conservatively providing this report to discuss the event, its cause(s) and our planned corrective actions. SCE restored minimum Regulatory Guide 1.75 separation criteria (by applying Sil-Temp) on 9/1/99 at approximately 1240 PDT. Appropriate personnel were provided training on the separation requirements for field cabling within enclosures.
3611999006 | San Onofre 2, San Onofre 3 | 11/22/1999 | 12/10/1999 | ML99348020 | <strong>Pressurizer Heaters and EDG Power requirements - Voluntary Report</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1998, the NRC issued Amendments 141 and 133 which changed the Technical Specification (TS) allowed out of service time limit for an emergency diesel generator (EDG) (EK) from 72 hours to 14 days. Prior to November 22, 1999, TS 3.4.9 required two groups of pressurizer (PZR) heaters be capable of being powered from an emergency power supply. If one group of pressurizer heaters became inoperable, this TS required the affected group to be restored to operable status within 72 hours. Recently, SCE became aware that the TS wording "capable of being powered from an emergency power supply" could be interpreted to mean "from an Operable EDG." Consequently, SCE requested a TS amendment to remove this phrase. This request was granted by the NRC on November 22, 1999 (Amendments 161 and 152). Using the alternate TS interpretation listed above, TS 3.4.9 could have required SCE to declare a pressurizer heater group inoperable whenever its associated EDG was out of service. Because there may have been one or more instances when an EDG was out of service for more than 72 hours between the two dates listed above, SCE is voluntarily providing this report to the NRC. There is no safety significance to this issue. In amendments 161 and 152 the NRC stated that removing this phrase was acceptable because (1) the pressurizer heaters are permanently installed on the Class 1E safety-related buses, (2) this design is described in the Updated Final Safety Analysis Report and the TS Bases, (3) the relevant TMI action item requirements continue to be met, and (4) the change is consistent with the CE Standard Tech Specs. No corrective actions beyond this TS amendment are required. There have been no similar TS conflicts reported within the past 2 years.
3621999001 | San Onofre 3 | 02/11/1999 | 03/12/1999 | 9903250321 | <strong>Entry Into Tech 3.0.3 Due To Both Emergency Chilled Water Trains Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 2/11/1999 (discovery date), Unit 3 (Mode 1, 99.9 percent power) was in a Technical Specification (TS) 72 hour action for Component Cooling Water (CCW)(CC) Train (Tr) A inoperable (TS 3.7.7) caused by inoperable non-critical loop isolation (NCL) valves. See LER 2-1999-003. Because CCW is required for Emergency Chilled Water (ECW) (KM) operability, ECW Tr A was inoperable (TS 3.7.10). Units 2 and 3 share ECW, but Unit 2 was unaffected because it was in Mode 6 where neither TS applies. At 0718 PST, ECW Tr B was declared inoperable when CCW Tr B temperature fell below the minimum to support ECW operability (55 F). The cause was low ocean (BS) temperature. Two Trs of ECW inoperable requires entry into TS 3.0.3 (reportable under 10CFR50.73(a)(2)(0), and action within 1 hour to place the unit in Mode 3. CCW Tr A was made operable by transferring the NCL to Tr B. At 0800 PST and prior to initiating shutdown, CCW Tr A was verified above 55 F, ECW Tr A declared operable, and TS 3.0.3 exited. At 0845 PST, TS 3.0.3 was entered when CCW Tr A fell below 55 F, making ECW Tr A inoperable. TS 3.03 was exited at 0920 PST after ECW Tr A was aligned to Unit 2's CCW which was above 55 F. To prevent recurrence, warm main condenser (SG) discharge water was diverted into the Salt Water Cooling (SWC) (BS) intake. SWC cools CCW, so warming its intake warms CCW. This event had minimum safety significance. In the past 3 years, SCE has not reported any other condition caused by low ocean temperature.
3621999002 | San Onofre 3 | 03/28/1995 | 05/20/1999 | 9905250132 | <strong>Voluntary Report-Refueling Water Storage Tank Isolation Valve Design Basis</strong><br /><i>Abstract:&nbsp;</i>On March 28, 1995, the Refueling Water Storage Tank (RWST) outlet isolation valve (3HV9300) failed to open after being closed for testing. After inspecting the valve actuator, SCE concluded the ability of the RWST outlet isolation valves to close may have been degraded. Nevertheless, SCE concluded the valves remained capable of performing their intended function (to provide a source of borated water) and therefore remained operable. (The RWST outlet isolation valves are MOVs and are locked open during Modes 1-4.) In March, 1999, the NRC resident inspectors relayed to SCE that a 1999 NRC internal memorandum concluded the RWST outlet valve condition identified in 1995 was a "condition outside the design basis." This opinion has been reflected in Inspection Report 99-04, dated April 21, 1999, which concluded "... the RWST outlet isolation valves did not meet the design basis requirements as stated in the UFSAR." SCE has reconsidered its initial assessment and is providing this voluntary LER to document the basis of SCE's determination.
3621999003 | San Onofre 3 | 05/13/1999 | 06/11/1999 | 9906220089 | <strong>Manual Reactor Trip Due To Loss of Main Feedwater</strong><br /><i>Abstract:&nbsp;</i>On 5/13/1999, at 2144 PDT, with the unit at 97 percent power, technicians were investigating feedwater system oscillations, when a main feedwater control valve closed. Operators manually tripped the reactor,, and started the Auxiliary Feedwater System. All control rods fully inserted. The Emergency Core Cooling System was not required and was not actuated, either manually or automatically. Plant responses were as expected. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii). This Licensee Event Report is provided pursuant to 10CFR50.73(a)(2)(iv). The cause was an "open" relay contact in the output of the Feedwater Regulation Control System which is normally closed during power operation. When this contact opens, the main feedwater regulator valve closes. The contact failed when fine debris from the relay's plastic case migrated to the contact surfaces. causing high contact resistance. The faulty relay was replaced. As a result of this event, and that in LER 3-1999-004, SCE is evaluating its preventative maintenance program. This event is categorized as GREEN. SCE has not reported any related events in the past 3 years.
3621999004 | San Onofre 3 | 05/15/1999 | 06/11/1999 | 9906220090 | <strong>Manual Reactor Trip (ESF Actuation) Due To Feedwater Control Valve Opening</strong><br /><i>Abstract:&nbsp;</i>On 5/15/1999, at 2358 PDT, a main feedwater regulator valve moved to full open. The reactor was manually tripped when steam generator level reached the high level pre-trip alarm setpoint. All control rods fully inserted. No other ESF functions were required and none actuated, either manually or automatically. All systems and plant responses were as expected. This event was reported to the NRC pursuant to 10CFR50.72(b)(2)(ii). This Licensee Event Report (LER) is provided pursuant to 10CFR50.73(a)(2)(iv). The cause of this event was a faulty valve positioner. The positioner's failure was a combination by loose fasteners and the air supply nozzle restriction being plugged with dirt and dust. Plugging the supply air nozzle restriction has the same effect as the stuck pilot valve discussed above. With the restriction plugged, the pilot valve did not close and, as a result, caused 3FV1111 to open. The faulty positioner was replaced. As a result of this event, and that in LER 3-1999-003, SCE is evaluating its preventative maintenance program. This event is categorized as GREEN. SCE has reported no related events in the past 3 years.
3621999005 | San Onofre 3 | 06/30/1999 | 07/28/1999 | 9907300028 | <strong>Low Temperature Overpressure Protection (LTOP) Relief Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1999, 3PSV9349 failed its "as found" lift set point test. The valve had been replaced with alike kind valve during the Cycle 10 refueling outage and was being tested according to TS Surveillance Requirement 3.4.12.1.6. Two lifts were performed. The valve lifted at 420 psig, then 419 psig, both exceeding the TS upper limit of 416 psig. This condition likely existed prior to the Unit 3 shutdown for its Cycle 10 refueling (March 28, 1999). Consequently, this event is being reported in accordance with 10CFR50.73(a)(2)(i). The cause of the higher than expected relief set point is being investigated. 3PSV9349 Serial Number N60061-00-0001 was replaced by a like kind (Serial Number N60061-00-0002), properly set valve prior to discovering the high set point. SCE confirmed 3PSV9349 (Serial Number N60061-00-0001) was properly set prior to installation in the plant during the Cycle 9 refueling outage in April, 1997. The valve will be disassembled and inspected to determine the cause of the high setpoint.
3621999006 | San Onofre 3 | 06/23/1999 | 07/26/1999 | 9907280118 | <strong>TS 3.0.3 entry caused by an Inoperable EDG</strong><br /><i>Abstract:&nbsp;</i>At 0145 PDT on 6/23/1999, Emergency Diesel Generator (EDG) 3G003 was inadvertently made inoperable when operators aligned it to an inoperable Automatic Voltage Regulator (AVR). Because Technical Specification required actions were not performed, this event is being reported in accordance with 10CFR50.73(a)(2)(i). In addition, at 0545 6/23/1999, an opposite train battery charger was removed from service for normal maintenance; however because EDG 3G003 was inoperable, Unit 3 unknowingly entered TS 3.0.3 and failed to take the appropriate action. At 0000 PDT on 6/25/1999, the battery charger was returned to service, and the unit exited TS 3.0.3. At 0825 on 6/25/1999 (discovery date), operators identified the EDG incorrectly aligned to AVR B, selected AVR A, thereby returning EDG 3G003 to operable status at 0855. Corrective actions to prevent recurrence will include revising the process of locating tags, operator training on this event and programmatic enhancements. The safety significance of this event was very small.
3621999007 | San Onofre 3, San Onofre 2 | 11/02/1999 | 11/30/1999 | ML99337041 | <strong>Missed Technical Specification Surveillances - Aux Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On 11/2/99, SCE determined that Technical Specification Surveillance Requirement 3.7.5.2 for AFW pump 3P141 was not performed within the specified 31 day interval required by the staggered SR basis. 3P141 should have been tested by 10/11/99. Because the, required TS Surveillance was not performed in accordance with TS 3.7,5.2, SCE is reporting this occurrence pursuant to 10CFR50.73(a)(2)(t)(B) , SCE completed testing of 3P141 in accordance with TS SR 3.7.5.2 on 11/2/99, Because AFW pump 3P141 passed its required TS surveillance, the pump was able to perform its intended safety function and there was no safety significance to this issue.
3641999001 | Farley 2 | 06/12/1999 | 07/02/1999 | 9907140085 | <strong>Reactor Trip Due to Loss of Condenser Vacuum on Steam Dump Drain Line Failure</strong><br /><i>Abstract:&nbsp;</i>Unit 2 was manually tripped on June 12, 1999 at 2147 due to decreasing vacuum in the condenser. A steam dump drain line was found broken. Metallurgical analysis of the drain line determined that it had failed due to fatigue. Thermal growth of the main steam line relative to the drain line that was at ambient temperature created high stress points at several points on the drain line due to the supports not adequately allowing for this growth. These high stress points included the location of the break. During construction, installation of the steam dump drain lines was craft routed as allowed for by the applicable piping specification and quality control procedures. The piping specification did not require a stress analysis on small bore piping in the turbine building. Later in plant life, a binding problem was identified. In 1990 a design change was issued to correct the binding problem with the steam dump drain header that, due to personnel error, did not consider the most extreme service condition in the stress analysis. Therefore, the design change was inadequate in that it did not eliminate the overstress condition of the drain line which contributed to a fatigue failure of the pipe. The broken section of line was replaced. Several supports were modified to relieve the stress in the drain header. Engineering review of the new configuration by design personnel has determined it to be acceptable to operate until the next refueling outage. An additional design change, to further reduce the stress on the drain operate until header and the steam dump drain lines, will be implemented during the next refueling outage. The corresponding piping on Unit 1, which is configured differently than Unit 2, has been visually examined, and no indication of excessive stress due to binding was detected.
3641999002 | Farley 2 | 11/01/1999 | 12/07/1999 | ML99348019 | <strong>Steam Generator Tube Degradation and Tube Status</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1999, Farley Nuclear Plant steam generator inspection results were classified as Category C-3 in accordance with Technical Specification 4.4.6.2 and are being reported in accordance with Technical Specification 4.4.6.5.c. A voluntary notification report to the NRC of the C-3 inspection classification was made on November 1, 1999. Eddy current inspections were performed on one hundred percent of the available tubes in all three steam generators (S/G’s). As a result of this inspection, more than 1% of the in-service tubes during Cycle Thirteen in all three S/G’s were found to be defective, which requires inspection results in the S/G's to be classified as Category C-3. Defective indications were identified within the tubesheet, above the top of the tubesheet in the sludge pile area, in the free span, and at the tube support plates. In addition to the required tube plugging, several ongoing programs have been established to reduce the probability of future tube degradation. The S/G's are scheduled to be replaced during the next refueling, U2RF14.
3641999003 | Farley 2 | 12/11/1999 | 01/03/2000 | ML00367453 | <strong>Technical Specification 3.0.4 Not Met During Mode Changes Due to 600 Volt Load Center Room Cooler Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 12, 1999 at 2130, with Unit 2 in Mode 3, it was determined that Farley Nuclear Plant (FNP) Unit 2 had operated in a condition prohibited by Technical Specifications (TS). TS 3.8.2.1 requires that two trains of AC electrical busses and load centers be operable in Modes 1, 2, 3, and 4. While reviewing readiness for Mode 2 entry, the Shift Supervisor (SS) noted that the 600-Volt Load Center 2E Room Cooler, which is necessary attendant equipment for one of the two trains of AC busses, was tagged out. Therefore, the provisions of TS 3.0.4 had not been met when Mode 4 was entered on December 10, 1999 at 1507, or when Mode 3 was entered on December 11, 1999 at 1848. The provisions of TS 3.8.2.1 had not been met upon failure to meet the time limits of TS 3.8.2.1 action "a" on December 12, 1999 at 0507. Upon detection, action was immediately initiated to return the room cooler to service (tagged out) was performed and identified no other adverse impacts on mode changes. This event is due to inadequate procedure in that procedural guidance to verify the operability of the room cooler was not required until a later mode entry, nor did procedural guidance exist to verify the acceptability of all tagged out equipment for mode changes on startup. This event is also due to inadequate communications in that the decision to work on the room cooler at a later date was not communicated to tagging officials. The return to service checklist procedure has been revised to require reviews of active tagging orders prior to mode changes during plant startup, and performance of the ventilation system checklist prior to Mode 4. The return to service checklist procedure will be reviewed for other system alignment checklists that may be assigned to the incorrect mode and corrected. These actions will be complete by March 1, 2000. This event does not represent a Safety System Functional Failure.
3661999001 | Hatch 2 | 01/18/1999 | 02/05/1999 | 9902120193 | <strong>Personnel Error Results in Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 1/18/1999 at approximately 2300 EST, Unit 2 was in the Run mode at a power level of 2708 CMWT (98 percent rated thermal power). At that time, a plant equipment operator (PEO) re-positioned the control switch for the Unit 2C diesel generator (D/G) room louver from the automatic to the closed position. With the switch in the closed position, the louver would not open nor would 2C D/G room fans start on high room temperature. With the louver and fans disabled, temperatures in the room will become unacceptably high during D/G operation; therefore, the D/G was rendered inoperable when the louver switch was placed to the closed position. However, the D/G was not declared inoperable because the PEO did not inform anyone of his actions. As a result, the required Technical Specification Condition was not entered and the Required Actions were not taken. The D/G was inoperable until 0830 EST on 1/19/1999 when Operations personnel were informed the switch was in the incorrect position and returned it to the automatic position. The cause of this event was cognitive personnel error. The PEO moved the switch to the closed position in order to prevent the louver from opening and possibly reducing room temperature. He did not realize this action rendered the D/G inoperable. Upon discovery of the error, personnel placed the switch in the correct position returning the D/G to operable. Placards stating the unit Shift Supervisor is to be notified prior to moving the switch have been placed beside the switches for each of the five diesel generator room louvers. The involved individual has been disciplined.
3661999002 | Hatch 2 | 01/28/1999 | 02/24/1999 | 9903030317 | <strong>Water Level Transient Following Manual Reactor Scram Causes Group 2 PCIS Isolation</strong><br /><i>Abstract:&nbsp;</i>On 01/28/1999 at 1158 EST, Unit 2 was in the Run mode at a power level of 470 CMWT (17 percent rated thermal power). At that time, Operations personnel manually scrammed the reactor per procedure 34GO-OPS-013-2S, "Normal Plant Shutdown," to allow plant personnel to enter primary containment to repair grounds in the DC power supply circuit for the solenoid-operated valves on two safety/relief valves. Water level decreased due to void collapse from the rapid reduction in power, reaching a minimum of approximately one inch above instrument zero (1 59.44 inches above the top of the active fuel). The decrease in water level resulted in receipt of a Group 2 Primary Containment Isolation System (PCIS) isolation signal and closure of the Group 2 Primary Containment Isolation Valves per design. The operating Reactor Feedwater Pump restored level to normal. Personnel reset the Group 2 isolation signal and restored the isolation valves to normal per procedure 34AB-C71-001-2S, "Scram Procedure." This event was the result of the expected water level decrease from void collapse and proceduralized operator actions following a reactor scram. Operations personnel increased water level to approximately 40 inches above instrument zero, about five inches above the normal operating level, in anticipation of the level decrease. Nevertheless, water level decreased to a point approximately two inches below the Group 2 PCIS isolation setpoint. Personnel actions, procedural instructions, and equipment operation were appropriate for the situation; therefore, no corrective actions are required.
3661999003 | Hatch 2 | 01/28/1999 | 02/24/1999 | 9903030308 | <strong>Simultaneous Grounds in the DC Power Supply System Result in an Unexpected Actuation of an SRV</strong><br /><i>Abstract:&nbsp;</i>On 1/28/1999 at approximately 1628 EST, Unit 2 was in the Hot Shutdown mode with reactor vessel steam dome pressure at 352 psig. At that time, safety/relief valve (SRV) 2B21-F013K opened unexpectedly. At 1631 EST, Operations personnel closed the SRV by pulling fuses in the valve's control power and control logic circuits as directed by procedure 34AB-B21-003-2S, "Failure of Safety/Relief Valves." Steam dome pressure decreased to approximately 297 psig and water level increased from 36 'inches above instrument zero to 50 inches above instrument zero during the time the SRV was open. By 1633 EST, reactor vessel water level and steam dome pressure were stable at approximately 30 inches above instrument zero and 300 psig, respectively. The SRV opened as a result of grounds in the "A" 125V/250V DC power supply system. These grounds created a current path through the coil of the solenoid-operated pilot valve for SRV 2B21-F013K, energizing the solenoid and causing the SRV to actuate. One ground was located in the power cable to the solenoid and occurred when its insulation melted due to excessive heat, exposing the wire. Because of an inadequate drawing, personnel failed to note during SRV insulation inspection that the power cable's conduit was contacting uninsulated metal components. The other ground was located in the voltage control portion of the power distribution subsystem for the feedpump control system and occurred when a metal oxide varistor failed due to overvoltage. The varistor failed because it was incorrect for the application. The conduit and power cable have been replaced; the conduit has been routed such that it does not contact uninsulated components; the varistor has been replaced with one rated for 250 volts; and the breaker for the DC power supply to the feedpump control system has been opened under a Temporary Modification.
3661999004 | Hatch 2 | 02/01/1999 | 02/24/1999 | 9903030312 | <strong>Spurious Radiation Monitor Trip Causes Group 2 PCIS Isolation</strong><br /><i>Abstract:&nbsp;</i>On 02/01/1999 at 1610 EST, Unit 2 was in the Cold Shutdown mode with drywell venting in progress to support maintenance activities. An Instrument and Controls (I&C) technician noted the green "Safe/Reset" light on dry well wide range radiation monitor 2D11-K621B was extinguished, In an effort to determine if the extinguished light was due to the monitor being inoperable or a failed light bulb, he replaced the bulb in the "Safe/Reset" pushbutton. This action apparently induced sufficient noise in the monitor's trip circuit to produce a spurious trip signal and, at 1610 EST, drywell purge valve 2T48-F308 and vent valve 2T48-F320 isolated on a drywell high radiation signal as designed. These valves are outboard primary containment isolation valves and are part of the Group 2 Primary Containment Isolation System. This event apparently was the result of electronic noise induced by personnel replacing the light bulb in the "Safe/Reset" pushbutton. The drywell wide range radiation monitors are susceptible to noise-induced trips as evidenced by their operating histories. Their susceptibility is due, at least in part, to the fact the monitors measure electric currents on the order of 10**-11 amperes making them extremely sensitive to small amounts of noise in their detection circuits. Because noise-induced trips appear to be an inherent feature of the monitors, consideration will be given to a design modification to prevent unwanted actuations from spurious, short-lived, noise-induced trip signals. A warning label will be placed near the monitors cautioning personnel of the possibility disturbing the monitors may cause a spurious trip signal.
3661999005 | Hatch 2 | 05/05/1999 | 05/27/1999 | 9906040026 | <strong>Generator Ground Fault Causes Turbine Trip and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 05/05/1999 at 0747 EDT, Unit 2 was in the Run mode at a power level of 2716 CMWT (98.3 percent rated thermal power). At that time, the reactor scrammed and the reactor recirculation pumps tripped automatically on turbine control valve fast closure caused by a turbine trip. The turbine tripped when the main generator tripped on a ground fault. Following the reactor scram, water level decreased due to void collapse from the rapid reduction in power. However, the reactor feedwater pumps maintained water level higher than eight inches above instrument zero. Consequently, no safety system actuations on low level were received nor were any required. Pressure reached a maximum value of 1124 psig; nine of eleven safety/relief valves lifted to reduce reactor pressure. Pressure did not reach the nominal actuation setpoints for the remaining two safety/relief valves. The temperature in the vessel bottom head region decreased by more than the Technical Specification-allowed 100 degrees F in one hour before a recirculation pump could be restarted. This event was caused by a manufacturer error. Some of the turning vanes located in the discharge duct for the "B" isophase bus duct cooling fan broke loose, shorting a generator phase to ground. The manufacturer installed turning vanes that were not the proper thickness for this application thus resulting in some of their connection points failing. Pieces of the broken vanes were retrieved from the isophase bus duct and the remaining turning vanes were removed from the isophase bus duct cooling system.
3661999006 | Hatch 2, Hatch 1 | 06/15/1999 | 10/26/1999 | ML99308013 | <strong>Loss of Condenser Vacuum Leads to Manual Reactor Scram and Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On 6/15/99 at 2124 EDT, Unit 2 was in the Run mode at a power level of approximately 1540 CMWT (41 percent rated thermal power) and Unit 1 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, a manual scram was inserted on Plant Hatch Unit 2 in anticipation of receiving an automatic scram on a turbine trip due to loss of condenser vacuum. When the scram was inserted, an electric power transfer failed which should have automatically re-aligned Unit 2 4160-volt buses "C" and "D." This further resulted in a trip of the Unit 2 reactor recirculation system pumps due to loss of lube oil pressure. When the recirculation system pumps were restarted, the "B" discharge valve began opening and activated an arcing ground fault on a 600-volt bus which is fed from Unit 1. The electrical noise resulted in several Unit 1 600-volt breakers tripping, including the feeder breaker to the reactor protection system power supply. This resulted in various engineered safety features actuating on Unit 1, including automatic closure of Group 2 primary containment isolation system valves. When condenser vacuum was broken on Unit 2 following the scram, bypass switches had not been reset, so the main steamline isolation valves automatically closed. However, one Unit 2 main steam isolation valve did not close as expected. The cause for the loss of condenser vacuum on Unit 2 was a combination of factors that led to the condenser being unable to reject sufficient heat. The cause of the failure of the power transfer was a relay being out of calibration. The cause for the ESF actuations on Unit 1 was a ground in a conductor supplying a Unit 2 load. The cause for the failure of the MSIV to close on demand was the failure of an AC solenoid operated pneumatic valve to shift positions when it was deenergized. Corrective actions for this event included the addition of a level instrument in the circulating water pump pit, promulgation of an operating order on condenser operating parameters, repair of the grounded conductor, and other items.
3661999007 | Hatch 2 | 06/28/1999 | 07/27/1999 | 9908030156 | <strong>Personnel Error and Inadequate Corrective Action Cause Automatic Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 06/28/1999 at 0300 EDT, Unit 2 was in the Run mode at a power level of approximately 2708 CMWT (98 percent rated thermal power). Personnel were in the process of filling and venting the "B" cold reference leg keepfill system. At that time, the reactor shut down automatically and inboard Group 2 Primary Containment Isolation Valves (PCIVs) closed on low water level. Level decreased when Reactor Feedwater Pump (RFP) flow rate decreased in response to a false high level signal. Following the shutdown, level continued to decrease due to void collapse from the rapid reduction in power resulting in closure of the Group 5 PCIVs. Level reached a minimum of approximately 45 inches below instrument zero causing automatic initiation of the Reactor Core Isolation Cooling and High Pressure Coolant Injection systems. The low level initiation signal cleared before either system could inject makeup water to the vessel. Secondary containment automatically isolated and all four trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low level. The RFPs restored level to normal within one minute. Pressure was at its normal value at the time of the reactor shutdown and decreased thereafter; no Safety/Relief Valves lifted nor were any required to lift. This event was caused by personnel error and inadequate corrective action. Involved personnel were disciplined per the Positive Discipline Program and the calibration of a level instrument has been changed.
3681999001 | Arkansas 2 | 01/08/1999 | 03/09/1999 | 9903180380 | <strong>Technical Specifications Requirements For As-Left Lift Settings of Main Steam Safety Valves Were Not Met Due To Errors In The Determination Of Effective Seating Area By The Vendor During Test Device Qualification</strong><br /><i>Abstract:&nbsp;</i>Prior to a scheduled refueling outage, in situ testing revealed that four of ten Main Steam Safety Valves (MSSVs) had as-found lift settings greater than three percent above their setpoints. Each valve was left with a lift setting within an indicated plus or minus one percent of the required setpoint before testing another valve. A Crosby Set Pressure Verification Device (SPVD) was being used for the first time at ANO for MSSV testing. The root cause evaluation determined that errors in the determination of the effective seating area by the vendor during qualification of the SPVD on ANO-2 MSSVs resulted in the indicated lift settings being higher than the actual values. The corrected as-found lift setting was out of tolerance for only one MSSV. The test device error resulted in the final as-left lift settings of four MSSVs being outside the as-left Technical Specifications (TS) limit of plus or minus one percent of the specified setpoint. Two of those valves were in that condition for slightly longer than allowed by the TS Action requirement. All MSSVs were subsequently replaced with valves that had been inspected and certified on steam at an off-site facility. Other factors contributing to lift point reliability were also determined during the root cause evaluation.
3681999002 | Arkansas 2 | 02/02/1999 | 03/04/1999 | 9903160032 | <strong>Station Battery Cell-to-Cell and Terminal Connection Tightness Was Not Verified As Required By Technical Specifications Due to Requirements Being Inadvertently Omitted During Procedure Revisions</strong><br /><i>Abstract:&nbsp;</i>During a scheduled refueling outage, ANO-2 discovered that Station Battery cell-to-cell and terminal connection tightness had not been verified each 18 months as required by Technical Specifications (TS). The requirements for verification of connector tightness had been inadvertently omitted during procedure revisions in 1989 and 1990. The surveillance had not been verified during four previous refueling outages for each battery but had been done during performance of 60-month test procedures. Service Test procedures were revised. Connector tightness was satisfactorily verified for both batteries during the outage in which the condition was discovered. A review of other battery surveillance requirements determined that they were adequately included in existing procedures. Standard Technical Specifications do not require this surveillance for the ANO-2 battery type. There are no indications that either Station Battery was actually inoperable due to connections not being tight. Voltage tests and resistance readings are believed to have been capable of detecting loose connections.
3681999003 | Arkansas 2 | 02/24/1999 | 03/23/1999 | 9903300079 | <strong>One Excore Nuclear Instrumentation Channel Inoperable Longer Than Allowed By Technical Specifications Due To Detector Failure</strong><br /><i>Abstract:&nbsp;</i>During surveillance testing in November 1998, Channel "D" excore nuclear instrumentation upper detector failed resulting in the linear power function being inoperable. Technical Specifications (TS) require that the channel be restored to an operable status prior to startup following the next cold shutdown. The Channel "D" excore assembly, consisting of three detectors, was replaced during a scheduled refueling outage. While the plant was in Mode 3 during recovery from the outage, it was determined that the center detector was inoperable. This caused both the logarithmic and linear power functions of that channel to be considered inoperable. Enforcement discretion was obtained before entering Mode 2; however, this resulted in operation prohibited by TS. A proposed exigent TS change was submitted to allow operation until the next scheduled outage. The existing safety analysis justifies operation with three operable channels, and the increased risk associated with testing another channel with Channel "D" tripped was determined to be non-risk significant. Subsequent testing and evaluation resulted in the linear power function of Channel "D" being declared operable for Mode 1 operation only. A root cause evaluation will not be practicable for a considerable time due to radiological activity of the detector assembly.
3681999004 | Arkansas 2 | 04/14/1999 | 05/12/1999 | 9905190013 | <strong>Title (4) Two Trip Functions Of One Core Protection Calculator Channel Were Potentially Inoperable Longer Than Allowed By Technical Specifications Due To Excore Detector Drift</strong><br /><i>Abstract:&nbsp;</i>Following restoration of Channel "D" excore nuclear instrumentation to an operable status, as described in Licensee Event Report 50-368/1999-003-00, routine core monitoring activities identified a diverging trend of the raw signal (drift) from the middle fission chamber of that assembly. Evaluation of the drift against available criteria indicated that the channel remained operable. The cause of the condition appears to be a breach of the middle fission chamber fill gas volume. In reviewing the impact of detector drift on Core Protection Calculator (CPC) setpoints, it was determined that sensitivity to drift was more significant than expected. On April 14, 1999, CPC trip setpoints for Local Power Density and Departure from Nucleate Boiling Ratio were determined to have been potentially non-conservative since March 8, 1999, a duration longer than allowed by Technical Specifications. The root cause was determined to be lack of adequate detector performance criteria and inadequate understanding of the CPC axial shape synthesis performance criteria. The affected Channel "D" trip functions have remained bypassed or tripped since the condition was discovered. Additional acceptance criteria for excore detector monitoring will be developed, if possible.
3681999005 | Arkansas 2 | 08/31/1999 | 06/08/2000 | ML00372296 | <strong>Two Trip Functions Of One Core Protection Calculator Channel Were Potentially Inoperable Longer Than Allowed By Technical Specifications Due To Excore Channel Test Switch Malfunction</strong><br /><i>Abstract:&nbsp;</i>During review of core follow trends on August 31, 1999, Reactor Engineering personnel discovered anomalous behavior of Safety Channel "B" excore detector middle subchannel. Deviation from normal had begun on August 25. Channel "B" Core Protection Calculator (CPC) was declared inoperable because trip setpoints could have been non-conservative for Departure from Nucleate Boiling Ratio (DNBR) and Local Power Density (LPD) with the deviation present. When a test switch in a gain circuit of the excore linear subchannel was cycled as part of the troubleshooting, detector response returned to an acceptable value. Channel "B" operability was restored following satisfactory completion of surveillance testing. Having the CPC channel inoperable without performing the required actions resulted in operation prohibited by Technical Specifications. A method was developed and implemented to monitor excore detector signals using the Plant Monitoring System computer to allow more timely response to deviations due to hardware problems. The cause of this condition was determined to be resistance fluctuations across the test switch.
3681999006 | Arkansas 2 | 12/08/1999 | 01/07/2000 | ML00367386 | <strong>Inadequate Tracking of Work Progress Resulted in an Offsite Power Circuit Breaker Alignment Verification Not Being Performed as Required by a Technical Specification Action and Caused Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On December 8, 1999, one Emergency Diesel Generator (EDG) was removed from service to perform scheduled maintenance. The Technical Specification Action requirement for this condition is to verify offsite power circuit breaker alignment within one hour. This surveillance was not performed within the required time. The EDG was restored to an operable status in one hour and 53 minutes. When it was discovered that the surveillance had not been completed, it was satisfactorily performed on December 11, 1999. The root cause of the event was inadequate tracking of the progress and status of the maintenance activity. Contributing factors included overconfidence based on the time it had taken to perform previous similar activities, time pressure to complete the work near shift turnover, and initiation of the work within the last 15 minutes of the shift. Appropriate Operations personnel from both units will review lessons learned from this event.
3691999001 | McGuire 1, McGuire 2 | 03/06/1999 | 03/31/1999 | 9904130100 | <strong>Failure to Meet Technical Specification Requirements For Ice Condenser Lower Inlet Doors</strong><br /><i>Abstract:&nbsp;</i>Unit Status: On 3/6/99, Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 1 (Power Operation) at 82 percent power. Event Description: On March 6, 1999, Maintenance personnel performed a review of PT/0/A/4200/32, Periodic Inspection of Ice Condenser Lower Inlet Doors. It was discovered that the procedure was not conservative with respect to Technical Specifications (TS) Bases. On March 9, 1999, a review was conducted of past procedures to ensure measurements taken on the Lower Inlet Doors met past TS limits. It was discovered that on May 7, 1997, the procedure performed on Unit 1 during Refueling Outage 1EOC11 had two doors with measured values outside of TS and outside of the procedural limits. The most recently performed procedures on Unit 1 and Unit 2 were verified to meet all TS requirements. Event Cause: Failure to recognize that a recorded value was outside the acceptance criteria during both the performance of and review of the test procedure. Corrective Action: Management has reinforced expectations for procedure performance and review. NPRDS no longer exists, equipment failures will be reported through EPIX
3701999001 | McGuire 2 | 05/04/1999 | 06/03/1999 | 9906140060 | <strong>Failure to comply with the operability requirements and required actions of Technical Specification 3.7.4, Steam Generator Power Operated Relief Valves and former Selected Licensee Commitment 16.10.1.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 and Unit 2 were in mode 1 (Power Operation) at 100 percent power. Event Description: McGuire Technical Specification 3.7.4 requires three Steam Generator Power Operated Relief Valves be operable in Modes 1-3 and in Mode 4 when Steam Generators are relied on for cooldown. The BASES for Technical Specification 3.7.4 indicates that a relief valve is operable when it is capable of fully opening and closing using its handwheel. On 5/4/99, it was discovered that the manual operation of two Unit 2 relief valves was probably impaired for some period of time from 12/13/97 to 3/14/99 due to loose actuator manual override shaft keys. During this period, Unit 2 was in plant Modes where Technical Specification 3.7.4 was applicable. Therefore, it is conservatively assumed that the relief valves were inoperable for a period of time exceeding the action completion time of Technical Specification 3.7.4. This represented a Technical Specification prohibited condition. This assumed condition was also prohibited by former Selected Licensee Commitment 16.10.1. Event Cause: Design misapplication allowed actuator manual override shaft keys on the affected relief valves to loosen and impair manual operation. Corrective Action: Manual override shaft keys were reinstalled upon discovery and peened to prevent them from loosening. Actuators will be modified to provide a more positive means of retaining the keys in position. Periodic maintenance will be developed to inspect the keys for proper installation. McGuire accident analysis and Technical Specification BASES inconsistencies will be resolved as needed.
3701999002 | McGuire 2 | 03/18/1999 | 04/16/1999 | 9904270107 | <strong>Failure to comply with the required actions of TS 3.4.12, LTOP System, with two Centrifugal Charging Pumps capable of injecting into the RCS</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 5 (Cold Shutdown) at 0 percent power. Event Description: on March 18 1999, it was discovered that McGuire had failed to comply with the requirements of Technical Specification (TS) 3.4.12, Low Temperature Overpressure Protection (LTOP) System. This occurred during testing of the Unit 2 Charging and Volume Control (NV) system when each NV train's centrifugal charging pump (CCP) was capable of injecting into the Reactor Coolant System (RCS). Under these conditions, the applicable required actions of TS 3.4.12 include verifying RCS cold leg temperature > 107 degrees F. Contrary to these requirements, RCS cold leg temperature was determined to be approximately 72 degrees F during the period of time when both pumps were capable of injecting into the RCS. Event Cause: Operators were focused on Time-To-Boil margin and used RCS hot leg temperature (approximately 110 degrees F) instead of procedure specified cold leg temperature (approximately 72 degrees F) in determining compliance with required actions of TS 3.4.12. Independent self-checking of the correct parameter was not performed by operators. Corrective Action: Prior to the next McGuire refueling outage, station procedures and the operator training program will be reviewed/changed as needed and operator training will be provided to ensure that cold leg temperature is used instead of the Time-To-Boil related hot leg temperature in ensuring compliance with required actions of TS 3.4.12 during the applicable plant conditions.
3701999003 | McGuire 2, McGuire 1 | 06/16/1999 | 09/16/1999 | 9909230115 | <strong>Inadvertent Actuation of the Turbine Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 & 2 were in mode 1 (power operation) at 100 percent power. Event Description: An invalid actuation of the Unit 2 turbine driven Auxiliary Feedwater pump (TDAFWP) occurred on 6/16/99. Planned activities for removal from service of a motor control center failed to properly realign the power feeding a 120 volt AC panel board associated with the Standby Shutdown System (SSS). This resulted in de-energizing a SSS fail safe instrument valve, which opened the steam supply to the TDAFWP. The TDAFWP injected to the steam generators for approximately 3 minutes prior to the Auxiliary Feedwater System control valves being closed by operator action. Event Cause: Inadequate policy or directive (code: E1) is the primary cause. Station directives were not adequate in establishing that a technical procedure is required for operation activities involving a potential ESF actuation. Corrective Action: McGuire Nuclear Station directives will be reviewed and appropriately revised to ensure an adequate determination is performed to identify when use of technical procedures is required to coordinate evolutions involving risk significant activities.
3701999004 | McGuire 2 | 07/15/1999 | 08/12/1999 | 9908170018 | <strong>Reactor "Trip During SSPS Testing</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On July 15, 1999 at 14:44, an automatic turbine trip occurred on Unit 2 in response to an inadvertent reactor trip signal (P4). A turbine trip with the reactor power above 48 percent resulted in an automatic reactor trip. The P4 signal was generated during the replacement and testing of Reactor Trip Breaker A (RTA). SSPS Train A was in test alignment during the event; consequently and as designed Train A Auxiliary Feedwater Pump did not automatically start and the RTA breaker did not automatically open. Operations personnel manually opened Train A reactor trip breaker and started the Train A Auxiliary Feedwater Pump. Event Cause: A 'switch lever arm' was misaligned during an inspection of a refurbished breaker. The breaker was subsequently located in the RTA cubicle: Inadequate procedural guidance during breaker receipt inspection is considered the primary cause for the misalignment of the lever arm. A contributing cause is inappropriate action. The misaligned lever arm resulted in an inadvertent P4 signal during subsequent installation testing. Corrective Action: Procedure enhancements will be made to clearly direct the actions to be taken when inspecting the reactor trip breakers. The installation testing procedure will be revised to improve the sequence of steps. Management reviewed expectations for procedure performance and work practices with appropriate maintenance crews emphasizing attention to detail. NRC FORM 366 *_/NPRDS no longer exists, equipment failures will be reported through EPIX
3731999001 | LaSalle 1 | 04/07/1999 | 05/07/1999 | 9905130205 | <strong>Main Control Room, Auxiliary Electrical Equipment Room, and Switchgear Room Ventilation Systems Found Outside the Design Basis Due to Inadequate Initial Design</strong><br /><i>Abstract:&nbsp;</i>ABSTRACT: On April 6, 1999, during a review of an Operability Evaluation related to the Switchgear Ventilation (VX) Backdraft Dampers, it was discovered that a single failure of motor operated damper 1(2) VX22Y could block one of the exhaust air paths from all of the Switchgear rooms. These dampers are normally open, fail open dampers. If a single failure caused one of these dampers to fail closed, the Division 1 and 2 Switchgear and Reactor Protection System (RPS) Motor Generator (MG) Set room pressure would increase. This increase in pressure could result in a differential pressure less than +0.125 inch w.g. minimum positive pressure differential required between the Control Room Envelope and the adjacent Division 2 Switchgear Room and RPS MG Set Room. It was determined that the root cause was due to inadequate initial design. Corrective actions included placing the dampers out-of-service open, and commencing a review to determine a permanent solution to the problem. END OF ABSTRACT
3731999002 | LaSalle 1 | 06/23/1999 | 07/23/1999 | 9907280097 | <strong>Missed Technical Specification Rod Operability Surveillance Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 23, 1999, the Unit Supervisor for Unit 1 discovered that only a portion of the Rod Operability Check had been performed. The Rod Operability Check had last been performed in its entirety on June 13, 1999. Therefore, the surveillance interval on the remaining control rods had exceeded Technical Specification 4.4.1.3.1.1.b. requirements. The cause of the missed surveillance was a personnel error on the part of the Unit Supervisor on June 19, 1999, who made an erroneous assumption that a portion of the control rods had been checked previously. The surveillance was immediately performed on the remaining control rods, and all were found to be operable. Corrective actions included counseling for the responsible individual and a lessons learned briefing using the General Information Notice process for all departments performing Technical Specification surveillances. The significance of the event was minimal, since all rods were found to be operable. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as an event or condition prohibited by the plant's Technical Specifications.
3731999003 | LaSalle 1 | 09/02/1999 | 10/04/1999 | 9910120177 | <strong>Reactor Scram On Low Reactor Water Level Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1999, following preventative maintenance on the 1B Turbine Driven Reactor Feed Pump (TDRFP) hydraulic control system, a Non-Licensed Operator (NLO) restored automatic control improperly, causing a sharp drop in 1B TDRFP speed and feed flow. An automatic reactor scram was received on low reactor level. The NLO was recovering from a prior error in which he had erroneously placed the controlling subloop of the hydraulic control system in manual. This action was not prescribed by the work scope. When he became aware of the error, he failed to notify the control room of the abnormal configuration, and returned the subloop to automatic control. While in manual, an error signal had developed that reduced the feed demand to minimum. The cause of this event was a personnel error on the part of the NLO. Additional causes include a lack of supervisory oversight and a lack of adherence to administrative control procedures. Corrective actions included an all station stand down to discuss recent human performance problems, counseling the NLO and operating crew, and improving procedural guidance for transferring TDRFP hydraulic control system sub-loops and locking out control oil. The safety significance of the event was minimal. The plant responded as designed, and the Emergency Core Cooling Systems were not challenged.
3731999004 | LaSalle 1 | 11/01/1999 | 03/07/2000 | ML00369164 | <strong>Average Power Range Monitors Inoperable During Refueling Due to Improper Isolation of Local Power Range Detectors</strong><br /><i>Abstract:&nbsp;</i>On November 1, 1999, at 2005 hours, during an operating experience review, it was determined that all of the Unit 1 Average Power Range Monitors (APRMs) were inoperable. Unit 1 was in Mode 5, Refueling, and per Technical Specification (TS) Section 3.3.1, "Reactor Protection System Instrumentation," the APRM Neutron Flux Setdown, set at 15 percent power, was required to be operable. In addition, TS Section 3.3.6, "Control Rod Block Instrumentation," requires the APRM Neutron Flux-High Rod Block Instrumentation to be operable. During the removal of six Local Power Range Monitor (LPRM) strings, the operations staff did not place the LPRM mode selector switch to "Bypass." This resulted in the APRMs output being non-conservative. This condition was not immediately recognized and the actions required by TS were not performed, leading to a condition prohibited by TS. The cause of the event was determined to be a human performance error on the part of the licensed operators who prepared and approved the out-of-service for the work. The LPRM mode selector switches were immediately placed in the proper "Bypass" position. Corrective actions include writing a procedure for LPRM removal and the performance of a training needs analysis on the event. The significance of the event was minimal, since the Intermediate Range Monitor (IRM) system was operable and provided a High Neutron Flux trip set at a conservatively lower flux rate than provided by the APRM flux trip.
3731999005 | LaSalle 1 | 09/26/1999 | 10/26/1999 | ML99306002 | <strong>Lifted Leads Result in Inoperable AveragePower Range Monitor Thermal Power Upscale Trip</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1999, it was discovered that lifted leads that defeated the output of one of the Reactor Recirculation flow converters to the Average Power Range Monitors (APRM) placed the facility in a condition where a single failure would have prevented the flow biased simulated thermal power upscale Reactor Protection System trip required by Technical Specification 3/4.3.1.<br /><br /> The root cause of this event was a fundamental knowledge based error for failure to recognize the inoperable APRMs. Corrective actions include conducting tailgate sessions with operations personnel regarding APRM operability with respect to the thermal power upscale trip, and reviewing the Station training program to ensure that it includes the appropriate level of detail regarding APRM operability and the flow converter. <br /><br /> The safety significance of this event was minimal. Two flow units are routed through a low value gate to each APRM, which provides input to the thermal power upscale trip. The other flow unit was operable and provided the flow signal to the thermal power upscale trip.<br /><br /> This event is reportable per 10 CFR 50.73(a)(2)(i) as a condition prohibited by the plant's Technical Specifications.
3741999001 | LaSalle 2 | 08/04/1999 | 09/03/1999 | 9909080063 | <strong>Failure to Comply with Suppression Chamber - Drywell Vacuum Breaker Technical Specification Action Statement Due to a Management Deficiency</strong><br /><i>Abstract:&nbsp;</i>On August 4, 1999, at 1650, the Unit 2A suppression chamber - drywell vacuum breaker 2PC001A was declared inoperable after it was determined that the Station was not in compliance with the Technical Specification Action Requirement. Technical Specification 3.6.4 Action (b) requires that, with one position indicator of any operable suppression chamber - drywell vacuum breaker inoperable, the vacuum breaker must be visually verified to be closed at least once per 24 hours. The Division 1 open position indicator had been inoperable since June 30, 1999. The method in use for verifying vacuum breaker position was found to have been inadequate, and the vacuum breaker was declared inoperable. An alternate method was immediately identified and acceptably performed. The root cause of this event was a management deficiency, in that the operators were not provided adequate instructions or procedures for performing visual verification of vacuum breaker position. A permanent procedure to visually verify the vacuum breaker closed will be written. This event is reportable under 10 CFR 50.73(a)(2)(i) as an operation prohibited by Technical Specifications.
3741999002 | LaSalle 2 | 08/21/1999 | 09/20/1999 | 9909230035 | <strong>Automatic Scram Due to Failure of Reactor Water Level Control</strong><br /><i>Abstract:&nbsp;</i>On August 21, 1999, at 2251 hours, during a down power, Unit 2 feedwater flow and reactor water level began to oscillate due to a failure of the 2A Turbine Driven Reactor Feedwater Pump (TDRFP) hydraulic control system. Efforts by the reactor operator to restore level control were ineffective, and at 2255 hours the reactor automatically scrammed on low reactor water level. The root causes of the scram were inadequate maintenance on the 2A TDRFP servo valve 2FW163AA, and the failure of the control room crew to take proper action in response to a reactor level transient. Corrective actions include: repairing the servo valve; reinforcing operator standards associated with command and control, communications, and pre-job briefs; and improving operator knowledge deficiencies through training. The safety significance of the event was minimal. The plant responded as designed, and the Emergency Core Cooling Systems were not challenged.
3741999003 | LaSalle 2 | 11/16/1999 | 12/16/1999 | ML99361005 | <strong>Manual Reactor Scram Due to Electro-Hydraulic Control System Failure</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1999, at 1834 hours, Unit 2 operators manually scrammed the reactor from approximately 80 percent power due to the unexpected fast closure of the Main Turbine Combined Intercept Valves. The cause of the unexpected fast closure was subsequently identified as a failure of the intercept valve amplifier card and operational amplifier card in the electro-hydraulic control (EHC) circuitry. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the scram. The Emergency Core Cooling Systems were not challenged. The failed cards were replaced and sent to General Electric for failure analysis. The new cards were calibrated, and Unit 2 was returned to full power on November 20, 1999.
3821999001 | Waterford 3 | 01/05/1999 | 02/04/1999 | 9902080147 | <strong>Technical Specification 3.0.3 Entry Due to Less Than Adequate Chiller Thermostat Control</strong><br /><i>Abstract:&nbsp;</i>The Essential Chilled Water Chiller A tripped and the A Loop was declared Inoperable while in a 72-hour Action that was previously entered when Chiller B was tagged out for maintenance rendering the B Loop Inoperable. Technical Specification 3.0.3 was entered due to the inoperable status of both the A and B Loops of the Essential Chilled Water System. The A Loop was restored to Operable status using the A/B Chiller and Technical Specification 3.0.3 was exited. The cause of the Chiller A trip was less than adequate control of the chiller thermostat setting, which was found out of adjustment low. To improve thermostat setting control, Entergy will place a "tamper" seal on the chiller thermostats and install a label near each of the chiller thermostat control knobs to prohibit unauthorized thermostat adjustment. The event did not impact the safety and health of the public or plant personnel. The event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
3821999002 | Waterford 3 | 02/25/1999 | 03/25/1999 | 9903310093 | <strong>Waterford Steam Electric System Pressure Boundary Nozzles</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1999, during a planned inspection, Entergy discovered evidence of Reactor Coolant System (RCS) pressure boundary leakage on two Inconel 600 instrument nozzles on the top head of the Pressurizer. Subsequent inspections of the remainder of Inconel 600 nozzles identified 3 more leaking nozzles. One is on RCS Hot Leg #1 RTD nozzle, one is on RCS Hot Leg #1 sampling line, and one is on RCS Hot Leg #2 differential pressure instrument nozzle. No evidence of leaks was found on the RCS Cold Legs or Steam Generators. The apparent cause of the leaks is axial cracks near the heat-affected zone (HAZ) of the nozzle partial penetration welds resulting from Primary Water Stress Corrosion Cracking (PWSCC). The leaking Pressurizer nozzles have been repaired using a welded nozzle replacement. The leaking Hot Leg nozzles have been temporarily repaired using a Mechanical Nozzle Seal Assembly (MNSA) as an alternate repair method under 10CFR50.55a(a)(3)(i). This event did not compromise the health and safety of the public.
3821999003 | Waterford 3 | 03/11/1999 | 04/09/1999 | 9904160281 | <strong>Missed ASME Section XI Surveillance Due to Contractor Supplied Misinformation</strong><br /><i>Abstract:&nbsp;</i>On March 11, 1999, while the Waterford 3 plant was in a refueling outage, it was determined that four containment vacuum relief valves, CVR-101, CVR-201, CVR-102, and CVR-202, were not tested in accordance with ASME/ANSI OM Standard Part 1 (OM-1). Failure to test these valves resulted in a missed surveillance and is a violation of Technical Specification 4.0.5. The cause of this event is that contract individuals assigned to update the Waterford 3 IST Program to comply with ASME Section XI requirements did not specify the four CVR valves to be tested per OM-1. In addition, Entergy personnel oversight of the contractor's activities did not detect the error. To immediately address this issue, the valves were tested per OM-1 requirements. Also, the contractor assigned to update the IST Program has been made aware of this occurrence. All surveillance requirements for the valves were performed with acceptable results indicating equipment operability and functionality. The health and safety of the public and plant personnel were not adversely impacted.
3821999004 | Waterford 3 | 04/15/1999 | 05/14/1999 | 9905210135 | <strong>Missed Surveillance for ESFAS Containment Cooling Function Response Time Testing</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1999, it was discovered that complete response time testing of the Engineered Safety Features Actuation System (ESFAS) containment cooling function had not been performed. Specifically, testing of Component Cooling Water (CCW) pump and Containment Fan Cooler discharge damper response times following a Safety Injection Actuation Signal (SIAS) had not been incorporated into surveillance procedures. This was discovered while conducting an engineering review to establish design basis documentation for response times. This review was being performed as part of a corrective action for a previously identified deficiency. Consequently, Technical Specification (TS) Surveillance Requirement 4.3.2.3 had not been met. TS 3.0.3 was entered and Specification 4.0.3 was invoked. Data was collected and testing was conducted to evaluate CCW pump response to an SIAS with offsite power available. This action proved satisfactory performance and Specification 4.0.3 was exited. The root cause of the missed surveillance was identified as a Response Time Testing Program deficiency. Applicable surveillance requirements were omitted from functional testing procedures. This omission was the result of a human error. To prevent recurrence, procedures will be revised to include response time testing of the ESFAS containment cooling function. This condition did not adversely affect equipment functionality. Therefore, the health and safety of the public and plant personnel were not compromised.
3821999005 | Waterford 3 | 07/02/1998 | 06/24/1999 | 9907010170 | <strong>Inadequate Testing of Relay Contacts in Safety-Related Logic Circuits Due to Inadequate Procedure.</strong><br /><i>Abstract:&nbsp;</i>On July 2, 1998, with the plant in mode 1 at 100% power, it was determined that four contacts in control circuits of the Emergency Feed Water Control Valves (two contacts in each independent safety train) were untested. This discovery was made while performing reviews conducted as a corrective measure for other earlier discovered and reported (LER 97-029-00) untested contacts. The July 2, 1998 discovery constituted four additional untested contacts that were not identified during the earlier Generic Letter (GL) 96-01 reviews. The discovery was initially inappropriately earmarked for reporting as a revision to LER 97-029-00. Recently, Entergy Operations, Inc. concluded that this event should be reported as a standalone LER. Accordingly, the condition was not reported as a new LER within 30 days. The root cause of the failure to test the contacts was determined to be an inadequate surveillance test procedure. The failure to identify the untested contacts during the earlier GL 96-01 reviews was determined to be due to personnel error. The contacts were subsequently tested and were found to function properly. The Surveillance procedure (OP-903-047) has been revised to adequately provide for testing the contacts. Since the contacts functioned properly when tested, the failure to test the contacts did not result in significant nuclear safety impact. No further reviews are deemed necessary at this time since the discovery was made as a result of corrective measure reviews. The condition did not compromise the health and safety of the general public.
3821999006 | Waterford 3 | 06/14/1999 | 07/14/1999 | 9907200054 | <strong>Uncomplicated Automatic Reactor Trip Following Loss of 7KV Bus</strong><br /><i>Abstract:&nbsp;</i>On June 14, 1999, at 1307 hours, while at 100% power, Waterford 3 experienced an automatic reactor trip when the A1 7KV electrical bus was lost. An investigation of the event has determined the most probable cause of loss of the A1 7KV electrical bus and subsequent reactor trip to be a spurious actuation of a relay on either Reactor Coolant Pump 1A or 2A. Immediately following the trip, Operations personnel entered Emergency Entry Procedure, OP-902-000 and subsequently Uncomplicated Reactor Trip Recovery Plan Procedure, OP-902-001. The plant was stabilized in Mode 3, Hot Standby. Various plant components were walked downed and tested to determine the root cause of the event. Although the root cause of this event is indeterminate, the Reactor Protection System performed as designed. A low Departure from Nucleate Boiling Ratio (DNBR) trip was initiated due to decreasing speed of Reactor Coolant Pumps (RCPs) 1A and 2A, which was caused by the loss of the A1 7KV Bus. Required plant systems responded and the appropriate trip/actuation signals were generated. The health and safety of the general public were not compromised during this event.
3821999007 | Waterford 3 | 06/25/1999 | 07/23/1999 | 9907270217 | <strong>Operation Outside Tornado Missile Protection Licensing Basis for Turbine-Driven EFW Pump and Steam Supply Piping</strong><br /><i>Abstract:&nbsp;</i>On June 25, 1999, it was discovered that Waterford 3's licensing basis did not adequately describe the Waterford 3 plant design for tornado missile protection for the turbine-driven emergency feedwater (EFW) pump and steam supply piping. Specifically, FSAR Section 3.3 indicates that structures or components whose failures could prevent safe shutdown of the reactor, or result in significant uncontrolled release of radioactivity from the unit are either protected against or designed to withstand tornado missile loads. FSAR Table 3.5.3 lists the probability of a tornado missile strike to the EFW and main steam systems. These probability values indicate that a tornado missile strike to these systems is not credible. The root cause for this event was indeterminent. The most probable cause was identified as a failure to adequately describe the Waterford 3 plant design in the licensing basis. Entergy will submit a 10CFR50.90 submittal to change the FSAR to reference probability as the basis for not requiring tornado missile protection on some plant structures or components. There is no safety significance associated with this condition. The tornado missile strike probability is less than 10**-6 and a thermal hydraulic analysis was performed which showed that sufficient EFW flow is available to cool the RCS to shutdown conditions even without the turbine driven EFW pump.
3821999008 | Waterford 3 | 06/29/1999 | 07/29/1999 | 9908030355 | <strong>Failure to Perform Testing of Emergency Safety Features Filtration Units Per Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On June 29th, 1999, following a review of NRC Generic Letter 99-02, Laboratory Testing of Nuclear-Grade activated Charcoal, Entergy determined that past testing practices for charcoal adsorbers for the Emergency Safety Features (ESF) filtration units were not in accordance with plant Technical Specifications (TS) Surveillance Requirements (SRs). Specifically, the vendor tasked to test the adsorbers used temperature values different from those required in the SRs. This testing method has existed since initial plant start-up and no documentation could be found to determine the cause of the incorrect testing method. Although the testing methods for the charcoal adsorbers were not per Surveillance Requirements, Entergy believes that the method used fully validated the charcoal adsorbers' performance. Accordingly, the health and safety of the general public were not compromised during this event.
3821999009 | Waterford 3 | 07/27/1999 | 08/26/1999 | 9908300035 | <strong>An Appendix R Non-Compliance Condition Involving Inadequate Separation of Safe Shutdown Cables</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1999, with the plant in Mode 1 at 100% Reactor Power, it was determined that electric cables serving redundant trains of equipment required for safe shutdown (Fire Area RAB-30) were not routed in full compliance with 10CFR50 Appendix R requirements. However, existing suppression, detection and spacial separation would have ensured one train available for safe shutdown. The separation of the cables ranged from 8 feet to 120 feet. Appendix R requires a three hour barrier or a one hour barrier + detection + sprinklers or 20 feet free space between trains with no intervening combustibles +detection + sprinklers. The existing condition does not fully meet one of these options. Equipment affected includes Charging Pumps "A", "B" and "A/B"; Emergency Feedwater Pumps "A" and "B"; Low Pressure Safety Injection Pumps "A" and "B"; Shutdown Cooling Heat Exchanger "A" and "B" Component Cooling Water Flow Control Valves; and High Pressure Safety Injection Pumps "A" and "B". Compensatory measures (continuous fire watches) were implemented immediately. There was no actual fire event associated with this condition. Corrective measures are being determined under the plant Corrective Action Program. The condition did not compromise the health and safety of the general public.
3821999010 | Waterford 3 | 07/26/1999 | 08/26/1999 | 9908300049 | <strong>Inadequate Pumping Capacity in the Dry Cooling Tower Areas due to Inadequate Design Control</strong><br /><i>Abstract:&nbsp;</i>On July 26th, 1999, Entergy Operations Incorporated (EOI) determined that the pumping capacity of the pumps in the dry cooling tower areas was inadequate to preclude flooding of safety related or essential equipment during either a Probable Maximum Precipitation (PMP) event (assuming two of the four installed pumps are unavailable in accordance with the licensing basis). An investigation has determined the root cause to be an inadequate original design. Additionally, the original design of the sump system was not fully implemented. To address this condition, portable pumps were installed in each of the dry cooling tower areas to ensure sufficient pumping capacity. The above condition could result in safety related equipment associated with the Ultimate Heat Sink becoming inoperable during the PMP or the SPS. However, based on an engineering analysis, it has been determined that with the postulated loss of safety related equipment, the Ultimate Heat Sink and Emergency Feedwater System would be capable of performing its design function of dissipating heat from the reactor and its auxiliaries and safe shutdown could have been achieved. Accordingly, the health and safety of the plant and general public were not compromised during this condition.
3821999011 | Waterford 3 | 08/01/1999 | 08/31/1999 | 9909020208 | <strong>Reactor Shutdown Due to Loss of Controlled Bleed-Off Flow</strong><br /><i>Abstract:&nbsp;</i>On August 1, 1999, at 2136, with Waterford 3 operating at 100% power, an alarm for Middle Seal Pressure Low on Reactor Coolant Pump (RCP) 2B was received. Upon investigation, Operations personnel discovered lowering RCP seal pressures, along with dropping Controlled Bleed-Off (CBO) flow and increasing CBO temperature. Operations personnel entered the appropriate Off-Normal procedure for a reactor coolant pump malfunction. Initial actions were to attempt to lower CBO temperature by lowering Component Cooling Water (CCW) temperature to the RCP heat exchanger. Attempts to lower CBO temperature were unsuccessful. Within 13 minutes, CBO temperatures increased to 204 degrees F, CBO flow dropped to zero gallons per minute, and middle and upper seal pressures dropped to 100 psi. Operations personnel manually tripped the reactor and secured RCP 2B. The cause of this event is believed to be fatigue-induced failure of the rotating baffle of RCP 2B. This event did not compromise the health and safety of the public.
3821999012 | Waterford 3 | 08/12/1999 | 09/13/1999 | 9909150179 | <strong>Potential Operation with Both Control Room Normal Outside Air Intakes Valves Inoperable Due to Excessive Valve Leakage</strong><br /><i>Abstract:&nbsp;</i>On August 12, 1999, Entergy determined Waterford 3 could have been in a condition prohibited by Technical Specifications. This condition potentially existed for an indeterminate duration between October 1996 and January 1998 and between October 1998 and January 1999. During the performance of surveillances on HVC-101 and HVC-102 (control room normal outside air intake valves), at the end of the above time intervals, both of the valves failed their surveillances by having an excessive leakage rate. Specifically, on 1/19/98, HVC-101 failed its leakage rate test, and on 2/12/98, HVC-102 also failed its leakage rate test. Upon further investigation, it was identified that a similar condition occurred on 2/5/99 and 1/19/99 for HVC-101 and HVC-102, respectively. The root cause for this event was indeterminate. The most probable cause was identified as inconsistent seal tightness. Corrective actions include the refurbishment of the valves and more comprehensive testing. Additional corrective actions are being evaluated as part of the Waterford 3 Corrective Action Program. This condition is not safety significant. During accident conditions, both valves will automatically close. Past testing has verified that with both HVC-101 and HVC-102 in their closed position, the required control room in-leakage requirements were satisfied. This event did not impact the health and safety of the public.
3821999013 | Waterford 3 | 08/25/1999 | 09/23/1999 | 9909270180 | <strong>Exceeding the Technical Specifications Limits for Reactor Coolant System Cooldown Rate</strong><br /><i>Abstract:&nbsp;</i>During the Resident Inspector's review of Waterford 3's plant data following a reactor trip, it was discovered that the Reactor Coolant System (RCS) cooldown rate exceeded limits allowed by Technical Specifications (TS). Specifically, the TS limits RCS cooldown rate to 10 degrees an hour when the RCS cold leg temperature is less than 135 degrees Fahrenheit (degree F). On August 3, 1999, RCS cold leg temperature dropped approximately 17 degrees F from 135 degrees F to 118 degrees F in a one-hour period. Appropriate TS action statements were entered; however, a review of past occurrences revealed that RCS cooldown rate had previously exceeded the TS limit and the TS action statement was not entered. Upon discovery, an evaluation of the effects of these events on the reactor vessel was performed. The cause of this event has been attributed to inadequate content and inadequate implementation of Technical Specification requirements. An evaluation of the effects of the cooldown rate transients on the reactor vessel was performed. The results indicate these transients would have negligible effects on the integrity of the RCS. Accordingly, these events had no negative impact on health and safety of the public or plant personnel.
3821999014 | Waterford 3 | 09/10/1999 | 10/12/1999 | 9910200242 | <strong>Reactor Shutdown Due to Loss of Controlled Bleed-Off Flow Caused by Rotating Baffle Failure</strong><br /><i>Abstract:&nbsp;</i>On September 10, 1999, with Waterford 3 operating normally at 100% power, a Plant Monitoring Computer (PMC) alarm for Middle Seal Pressure Low on Reactor Coolant Pump (RCP) 2B was received. Upon investigation, Operations personnel discovered decreasing RCP seal pressures, along with decreasing Controlled Bleed-Off (CBO) flow. Operations personnel entered the appropriate Off-Normal procedure for a reactor coolant pump malfunction. CBO flow decreased to zero gallons per minute (gpm), and middle and upper seal pressures also decreased. Operations personnel manually tripped the reactor and secured RCP 2B. Initial disassembly involved removal of the seal for RCP 2B and inspection of the rotating baffle. Initial inspection showed the baffle's joint securely attached. However, the baffle had an observed through-wall crack 360 degrees around the inner surface of the inner cylinder. The cause of this event is believed to be fatigue-induced failure of the rotating baffle of RCP 2B. Corrective actions include replacing the one-piece rotating baffle with a more robust two-piece rotating baffle, completing and finalizing a Finite Element Analysis of the baffle, realigning RCP 2B, and revising the RCP maintenance procedure to include checking and correcting, as necessary, the RCP shaft shoulder to baffle joint for perpendicularity and flatness. This event did not compromise the health and safety of the public. A previous plant shutdown due to failure of the RCP 2B baffle was documented in LER 99-011-00 dated August 31, 1999.
3821999015 | Waterford 3 | 09/27/1999 | 10/27/1999 | ML99308004 | <strong>TS Non-Compliance While Raising RCS Pressure Due to Inadequate Shift Communication</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1999 at approximately 1755, the Control Room Operations shift at Waterford 3 was raising Reactor Coolant System (RCS) pressure during a normal plant startup. Upon reaching RCS pressure of approximately 420 pounds per square inch absolute (psia), the shift realized that Containment Spray (CS) Train B was inoperable due to failure to perform the CS system fill and Vent. This is a condition prohibited by Technical Specification (TS) 3.0.4 as TS 3.6.2.1 requires two trains of CS to be operable with RCS pressure greater than 400 psia. In addition, it was determined that all four Safety Injection Tanks (SIT) were also inoperable because the shift failed to open the SITs outlet isolation valves. This is also a condition prohibited by TS 3.0.4 as TS 3.5.1 requires that three SITs be operable when RCS pressure is greater than 392 psia. The operation's shift entered TS 3.0.3 and RCS pressure was reduced to below 392 psia within the allowed outage time of TS 3.0.3. An investigation has determined the root cause to be inadequate communication among shift personnel. To address this matter, the shift was temporarily relieved of duty pending debriefing, which occurred the following day. Shift briefing plans have been developed to enhance communication methods. CS train A was available to perform its safety function. The four closed SITs valves would have opened in response to an automatic or manual SIAS. Accordingly, safe plant shutdown could be achieved and the health and safety of the plant and the general public were not compromised during this condition.
3821999016 | Waterford 3 | 10/06/1999 | 11/08/1999 | ML99321023 | <strong>An Appendix R Non-Compliance Outside Design Basis Condition Involving An Inoperable Sprinkler System</strong><br /><i>Abstract:&nbsp;</i>On October 6, 1999, with the plant in Mode 1 at 100% reactor power, it was determined, during reviews of sprinkler system hydraulic calculations, that a fire protection sprinkler system (FPM-4B) was inoperable due to being unable to meet design dinsity (gal/sq ft) as required by the code of record (NFPA-13-1976) for a small section of the area. A three hour rated fire barrier wall between the 'A' and 'B' diesel generator rooms provides adequate Appendix R separation between the diesel generators. However a fire barrier with less than a three hour fire rating, located between the corridor ant the 'B' diesel generator room has 'A' train diesel generator cables in close proximity. Therefore, the sprinkler deficiency resulted in the potential for a fire in the 'B' diesel generator room to affect both trains of diesel generators. This constituted a condition outside the design basis of the plant with respect to Appendix R. Compensatory measures (continuous fire watches) were established immediately. The EDGs were determined to be operable in light of the compensatory measures. No actual fire event had occurred. The condition was determined to be due to an inadequate original design configuration. Corrective measures are being implemented under the plant corrective action program. The condition did not compromise the health and safety of the general public.
3821999017 | Waterford 3 | 08/11/1999 | 11/22/1999 | ML99331007 | <strong>Failure to Perform Technical Specification Surveillance Tests On a Penetration Overcurrent Protection Device.</strong><br /><i>Abstract:&nbsp;</i>On 8/11/99, with the plant in Mode 1 at 100% Reactor Power, it was determined that a Containment penetration circuit breaker had apparently not been tested per Technical specification (TS) 4.8.4.1b. The breaker (CAR EBKR 90A -18) is associated with Containment Atmosphere Release (CAR) Valve CAR ISV 200B. Reportability was indeterminate at the time of discovery since the TS excludes testing of protective devices in circuits for which credible fault currents would not exceed the electrical penetration design rating. After further review by Engineering, it was determined, on 10/21/99 that the credible fault current could exceed the electrical penetration rating. Therefore, the breaker is required to be tested. Failure to test was a violation of TS 4.0.2. There was no actual electrical fault event; therefore, there was no resulting damage to the Containment penetration. The condition occurred due to a failure to identify the breaker in the TS Table 3.8-1 in conjunction with a plant modification (SMP-1332) in 1998. A repetitive task was not established to test the breaker. The breaker had been successfully tested by an equivalent procedure on 3/22/99 (therefore operable). Currently, breakers required to be tested under TS 4.8.4.1 are identified in Technical Requirements Manual (TRM) Table 3.8-1. The TRM and test procedure will be revised. A task card will be generated. The condition did not compromise the health and safety of the general public.
3821999018 | Waterford 3 | 11/27/1999 | 12/22/1999 | ML99363043 | <strong>Operating in a Condition Prohibited by Technical Specification 3.5.2 Due a Valve Reach Rod Failure</strong><br /><i>Abstract:&nbsp;</i>On 11/27/99, with the plant in Mode 4, it was discovered that Waterford 3 Operated for 7 days in a condition prohibited by Technical Specification (TS) 3.5.2. TS 3.5.2 requires two Low Pressure Safety Injection (LPSI) Pumps to be Operable. On 11/19/99 with the plant in Mode 1, SI-417B was opened to recirculate the Refueling Water Storage Pool (RWSP); however, following completion, SI-417B was not closed due to the failure of its reach rod. The reach rod handwheel was locked closed but the valve was open. With SI-417B open, enough LPSI flow is diverted such that the TS flow requirements cannot be met. This condition occurred from 11/19/99, when the valve was left open, to 11/26/99, when the plant entered Mode 3 with pressurizer pressure < 1750 psia and Reactor Coolant System (RCS) average temperature < 500°F. The root cause of the event is failure of SI-417B reach rod due to a roll pin in the roto-hammer linkage backing out, which resulted in not identifying that SI-417B was left open. Upon discovery of this condition, SI-417B was closed and locked at the local handwheel. There is minimal safety significance associated with this event. A limited amount of inventory was drained from the RCS. Core cooling was maintained throughout the event. The health and safety of the general public were not adversely affected.
3871999001 | Susquehanna 1 | 02/28/1999 | 11/05/1999 | ML99316011 | <strong>Loss of Both Loops of Residual Heat Removal - Low Pressure Coolant Injection</strong><br /><i>Abstract:&nbsp;</i>On February 28, 1999 at 2202 hours, with Unit 1 in Mode I (Power Operation) at 100 percent power, it was determined that Unit 1 had been operated for approximately 17 hours on 2116/99 with the redundant loops of the Low Pressure Coolant lnjection (LPCI) mode of Residual Heat Removal (RHR) System inoperable. Operation Of the Unit with the loops of RHR LPCI inoperable, placed the Unit outside its design bases Two diverse subsystems (Core Spray) were available to perform the low pressure safety function. During an investigation of a potential degradation in the 'B' RHR Loop keep-fill system, a failed valve on the '(B' RHR Loop was discovered on 2/11/99. Pending further review, it is currently assumed that the 'B' RHR Loop valve had failed on 2/11/99 when the first indications that there was potentiel degradation in the 'B'RHR Loop keepfill system were noted. The 'A' Loop of RHR had been taken out of service for maintenance on 2/16199. Both loops of RHR have been restored to operable status. The cause of the failure of the RHR valve was determined to be a resuft Of environmentally assisted stress corrosion cracking due to the introduction of inadequate stem material incorporated by a 1985 modification. Taking the 'A' RHR Loopout of service and thus having both loops of RHR LPCI inoperable was due to a less than adequate investigation into the potential degradation of the '8' RHR Loop keep4ill system. Corrective actions completed include: interim replacement of the broken and cracked stem/plug assembly in Unit 1 with new like-in-kind material, issuance of modification packages to replace the stem/plug assemblies with redesigned assemblies, replacement of the stem/plug assemblies in both Unit 2 RHR loops valves with the redesigned assemblies, review of specifications to ensure that other valves are not susceptible to environmentally assisted stress corrosion cracking, and training on this event with the appropriate personnel. Corrective actions to be completed include: replacement of the Unit 1 stem/plug assemblies with lesssusceptible mater)aI, rev(sions to specifications, and evaluation of the process for troubleshooting and investigating plant problems. A reviewof the Design Basis Accident analysis concluded that there were no safety consequences or compromises to the health and safety of the public. In addition, an expanded evaluation of the safety consequences of having the 'B' loop of RHR out of service from the last time the HV-151F017B valve was stroked (November 19,1998) to March 1,1999 was performed using the new NRC event evaluation methodology. In all cases, the significance color was green. Therefore, failure of valve HV-151F017B is a low safety consequence event.
3871999002 | Susquehanna 1 | 06/02/1999 | 07/01/1999 | 9907080356 | <strong>Failure to Maintain Environmental Qualification - Acoustic Monitors Cable Sealing</strong><br /><i>Abstract:&nbsp;</i>On June 2, 1999, at 1600 hours with Unit 1 in Mode 4 (Cold Shutdown) at 0 percent power, and Unit 2 in Mode 1 (Power Operation) at 100 percent power, it was determined that the main steam safety/relief valve (SRV) acoustic monitors for both units were inoperable in that RTV sealant (sealant type recommended by accelerometer manufacturer) had not been applied to the accelerometer cable connectors of the acoustic monitors following a modification to replace the accelerometers and cables. The RTV sealant is required, per the manufacturer, to prevent moisture intrusion to the sensors, in order for the acoustic monitors to be environmentally qualified. Without this sealant, the Environmental Qualification (EQ) of the acoustic monitors is indeterminate, and the acoustic monitors were declared inoperable. On June 11, 1999, it was further determined that Unit 1 had been operating from July 14, 1998 to October 3, 1998 in a condition prohibited by the Standard Technical Specifications, which were in place at the time of the modification (7/14/98) until implementation of the Improved Technical Specifications (ITS) on October 3, 1998. It was further recognized on June 11, 1999 that this modification had also been performed on the Unit 2 "J" acoustic monitor on June 25, 1998 without the sealant. Therefore, Unit 2 had also operated in a condition prohibited by the Standard Technical Specifications, which were in place at the time of the modification (6/25/98) until implementation of the Improved Technical Specifications (ITS) on October 3, 1998. As such, these conditions are being reported pursuant to 10CFR50.73(a)(2)(i)(B). With implementation of the ITS, the acoustic monitoring requirements were relocated to the Technical Requirements Manual (TRM). The failure to apply RTV sealant was caused by the lack of identification in the EQ test report of the RTV sealant being required to meet EQ requirements, and the failure to translate the manufacturer's instructions for installing RTV sealant on the accelerometer cable connectors during equipment replacement. The RTV sealant has since been applied to all Unit 1 and Unit 2 acoustic monitor cable connectors. Actions to prevent recurrence include the training of appropriate personnel to enhance their awareness of attention to details, and evaluating and revising, as applicable, all related EQ and work planning documents to assure that RTV sealant is applied to the subject connectors.
3871999003 | Susquehanna 1 | 07/01/1999 | 08/02/1999 | 9908050162 | <strong>Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On July 1, 1999, at 0208 hours with Unit 1 in Mode 1 (Power Operation) at 100 percent power, the neutron monitoring system received a high neutron flux upscale trip, which caused a reactor SCRAM. The inadvertent closing of the "C" outboard Main Steamline Isolation Valve thus isolating one main steamline caused the high neutron flux. The other three steamlines experienced high flow that caused all MSIVs to isolate. As a result of the SCRAM, water level dropped to approximately -46 inches. Reactor water level was restored by using the High Pressure Coolant Injection (HPCI) System (auto-initiated) and the Reactor Core Isolation Cooling (RCIC) System. Reactor pressure peaked at 1048 psig and was controlled by cycling the Safety Relief Valves (SRVs). All SRVs re-seated after use. There were no diesel starts or challenges to the containment associated with this event. During this event, the "C" outboard MSIV exhibited excessive leakage, thus causing the total maximum leakage pathway Technical Specifications limit for the main steamline penetrations to be exceeded. The minimum leakage pathway for these penetrations remained below the analyzed limit. The inadvertent closing of the "C" outboard MSIV was caused by a stem-poppet separation. The cause of the "C" outboard MSIV stem to poppet failure was due to loss of pre-load on the stop plate bolting. The loss of the pre-load was due to actual clearances being less than the design tolerances, insufficient detail for assembling the stop plate to poppet connection, and inadequate torquing values for the stop plate bolting. Corrective actions that were completed include (1) the "C" outboard MSIV was repaired, (2) three additional MSIVs were inspected and reworked, and (3) the appropriate maintenance procedures were revised to include the new torquing criteria. Corrective actions remaining to be completed include (1) revisions to appropriate procedure to include revised inspection and torquing criteria, (2) inspection of similar Unit 1 MSIVs, (3) inspection of similar Unit 2 MSIVs, and (4) evaluation of potential solutions for MSIV leakage failures with a recommended course of action for improving MSIV performance. Since the plant performed as expected during this event and the total minimum pathway leakage from the main steam line penetrations was below the analyzed limit, there were no safety consequences or compromises to public health and safety.
3871999004 | Susquehanna 1 | 08/08/1999 | 09/07/1999 | 9909130092 | <strong>Reactor Core Isolation Cooling Manually Isolated Due To Failure Of Steam Leak Detection Temperature Switch Module</strong><br /><i>Abstract:&nbsp;</i>On August 8, 1999, at 0340 hours, with Unit 1 operating in mode 1 (Power Operation) at 100% power, the Unit 1 Control Room received the Reactor Core Isolation Cooling (RCIC) Steam Leak Detection Logic "B" High Temperature alarm. Control Room Operators verified that the 15-minute logic timer for the "B" RCIC Pipe Routing Area High Temperature Steam Leak Detection was energized and that corresponding temperature indicator was pegged up-scale. The circuit provides an isolation signal to the RCIC Turbine Steam Supply Inboard Isolation valve. The temperature indicator for the "A" Steam Leak Detection circuit was checked and found to be reading normal. The RCIC Pipe Routing Area was verified to have no steam leak present. Control Room Operators manually isolated the Unit 1 RCIC system at 0346 hours to preclude an automatic isolation of the RCIC system. The cause of the erroneous Steam Leak Detection signal was due to a failure of a temperature switch module. The module was replaced and the Unit 1 RCIC system was returned to service on August 8, 1999 at 0735 hours. Analysis of the failed temperature switch module revealed that "infant" failure of a power supply capacitor was the cause for the failure. Inadequate processing (human error) by PP&L of a manufacturer advisory for upgrading aging module capacitors led to installation of the subject module. All spare like-in-kind modules were inspected to ensure they did not contain non-upgraded capacitors. All like-in-kind modules that are in service will be inspected for non-upgraded capacitors also. Similar-type modules will be evaluated to ensure they have an adequate shelf life restriction to protect the capacitors from "infant" failure.
3871999007 | Susquehanna 1, Susquehanna 2 | 11/11/1999 | 12/13/1999 | ML99355009 | <strong>Incorrect Surveillance Frequency Due to Improved Technical Specifications Implementation Error</strong><br /><i>Abstract:&nbsp;</i>On November 11, 1999, with Unit 1 in Mode 1 (Power Operation) at 100% power ant Unit 2 in Mode 1 (Power Operation) at 100% power, operations personnel (utility, licensed) discovered that calculation of Reactor Coolant System (RCS) total leakage was being performed every 24 vice every 12 hours as required by Technical Specifications Surveillance Requirement 3.4.4.1. The surveillance requirement had been changed when the station implemented Improved Technical Specifications (ITS) on October 2, 1998. The more restrictive frequency was not identified in the ITS implementation, and was incorrectly classified as "Less Restrictive" during the ITS evaluation and implementation. As a result, the revision to the surveillance procedure associated with ITS implementation did not include the correct surveillance frequency for the RCS total leakage. Historical RCS leakage data shows that the limits were not exceeded. Therefore, the safety significance of this situation is low and the health and welfare of the public was not compromised. This event is reportable per 10CFR50.73(a)(2)(i)(B). Surveillance procedures for Unit 1 and Unit 2 have been revised to reflect the correct surveillance frequency. A sampling of ITS requirements characterized as "Less Restrictive" will be conducted to determine if additional categorization errors may exist.
3871999008 | Susquehanna 1, Susquehanna 2 | 11/23/1999 | 12/22/1999 | ML99363006 | <strong>Design Deficiency of Traversing Incore Probe Equipment Could Result in a Potential Release Path During Design Basis Accident Loss of Cooling Accident Conditions</strong><br /><i>Abstract:&nbsp;</i>At 1030 hours on November 23, 1999 with Unit 1 and Unit 2 in Mode 1 (Power Operation) at 100% power, engineering personnel (Utility; non-licensed) determined that a previously identified design deficiency Could result in a failure of the Traversing Incore Probe (TIP) Guide Tube Isolation Ball Valve to maintain containment isolation integrity and could potentially result in a direct pathway from the Drywell atmosphere (primary containment) to the Reactor Building (secondary containment) during postulated Design Basis Accident conditions. The cause for this condition is that the design of the TIP Guide Tube Isolation Control was provided by the NSSS supplier with a design error, which was not detected or corrected by PP&L. The design is in error by not applying the appropriate standards, namely IEEE 279-1971, to the systems and components necessary to assure that the Ball Valves remain de-energized and closed when Primary Containment isolation is required. Power to the Tip Ball Valve has been disabled to assure the TIP Ball Valves do not open due to a passive failure in the control circuitry, and may be restored under administrative control, as needed, on the basis of previous risk analyses. Long term corrective actions to resolve this condition are currently being evaluated and developed. The safety significance of this condition is low. All equipment in the TIP system remains operable because the TIP Ball Valve and the TIP Shear Valve actuation circuits remain operable and capable of operating as containment boundary devices. The TIP system remains capable of performing its LPRM calibration function.
3881999001 | Susquehanna 2 | 03/19/1999 | 04/16/1999 | 9904260248 | <strong>Main Steam Isolation Valve Excessive Leakage</strong><br /><i>Abstract:&nbsp;</i>At 1000 hours on March 19, 1999, with Unit 2 in its ninth refueling and inspection outage (Mode 5, Refueling, 0% power), an evaluation of data from the scheduled Main Steam Line (MSL) penetration Local Leak Rate Testing (LLRT) determined that the "as-found" maximum pathway leakage for the Main Steam Isolation Valves (MSIV) was in excess of the limit of Technical Specification 3.6.1.3 for the MSL containment penetration maximum pathway leakage of 300 standard cubic feet per hour (SCFH). The total "as-found" maximum pathway leakage was in excess of 1300 SCFH. However, the total "as-found" minimum pathway leakage was only 255 SCFH. The evaluation determined that the MSIV LLRT excess "as-found" maximum pathway leakage was reportable pursuant to 10CFR50.73(a)(2)(ii). The cause was determined to be that two (2) MSIVs had excessive leak rates. This excessive leakage was due to wear on the main seat for one MSIV and wear on the poppet valve seat of the other MSIV. The corrective actions included reworking of the MSIVs. Since the leakage (the minimum path leak rate - 255 SCFH) that would have actually reached the condenser is below the 300 SCFH analyzed in the, dose calculations, there were no safety consequences or compromises to public health and safety as a result of this event.
3881999002 | Susquehanna 2 | 03/25/1999 | 04/26/1999 | 9905030250 | <strong>Feedwater Penetration</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1999 at 0130 hours with Unit 2 in Mode 5 (Refueling) at 0 % Power, the leakage through the primary containment isolation valves for the 'A' Feedwater penetration exceeded the secondary containment bypass leakage and the as-found 10CFR50 Appendix J acceptance criteria. During the scheduled Local Leak Rate Test for the Feedwater penetration, both test volumes could not be pressurized. Since the test volumes could not be pressurized, the leakage through these isolation valves was in excess of the analyzed secondary containment bypass leakage criteria and the as-found 10CFR50 Appendix J acceptance criteria. This event was determined to be reportable in accordance with the provisions of 10CFR50.73(a)(2)(ii). The root cause of the leakage of the inboard isolation valve (241F010A) was determined to be wear of the valve's soft seat. In addition to the valve's soft seat wear, the hinge pin was misaligned and contributed to the leakage. The exact root cause of the leakage of the outboard isolation valve (HV-241 F032A) could not be determined. The most probable cause of the leakage of this valve is dirt/crud on the valve seat. The isolation valves have been reworked and the leakage returned to within limits. Corrective action to be completed includes for the feedwater penetration inboard isolation valves, re-evaluation of the soft seat life in the preventative maintenance program and other actions as necessary. Since the excessive leakage in the "A" feedwater penetration was discovered while Unit 2 was in Mode 5 (primary containment isolation not required) and since the isolation valves were not required to perform their safety function, there were no safety consequences or compromises to public health and safety as a result of this event.
3881999003 | Susquehanna 2 | 06/08/1999 | 07/08/1999 | 9907140154 | <strong>Unplanned ESF Actuation - Generator Load Reject and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>At 1206 hours on June 8, 1999, with Unit 2 in Mode 1 (Power Operation) at 100% power, a unit primary lockout signal, created when one of the three single-phase main transformers failed, caused a Main Turbine trip. In accordance with plant design, the Turbine Control Valves closed and an automatic reactor scram occurred. All major equipment operated per design during the transient. Emergency Core Cooling Systems (ECCS) were not challenged and no abnormal operator actions were required to place the unit in a stable condition. The cause of the event was attributed to a failure of a neutral bushing in the 'A' Main Transformer due to a defective subcomponent. Failure of the bushing caused an electrical arc in the transformer resulting in a pressure spike inside the transformer oil tank and subsequent generator load rejection. Inadequate processing (human error, other utility personnel) by PP&L, of a 1990 manufacturer advisory for the defective bushing, led to its installation. The entire 'A' Main Transformer was replaced along with an acceptable bushing. The remaining in-service Unit 1 and Unit 2 main transformers were inspected for the defective bushings and none were found. Two spare bushings were found defective and segregated to prevent use. Any defective bushings of the same type will be prevented from being procured and installed through administrative processes. Personnel that process manufacturer advisories will be provided with information on this event. A review of manufacturer advisories will be conducted. The plant was safely shutdown, and there were no safety consequences or compromises to public health or safety during this event.
3891999002 | St. Lucie 2 | 03/11/1999 | 04/07/1999 | 9904090149 | <strong>SG ECT Error Causes Operation with a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During the St. Lucie Unit 2 refueling outage 11 (SL2-11) steam generator inspection in November 1998, the tube at Row 49 Line 85 in steam generator (SG) 2B was plugged due to a wear-induced indication that penetrated 47% through wall, exceeding the plugging limit of Technical Specification 4.4.5.4.a.6. Upon review of historical data, it was determined that this indication was present, but not identified during the SL2-9 and SL2-10 examinations, and that the depth of the indication was essentially unchanged during this period of operation. Therefore, this tube exceeded the plugging limit, but remained in service during operating cycles 9 and 10. Detection and subsequent plugging of this tube indication resulted from improvements in the data analysis and controls implemented for the SL2-11 inspection. Lead analysts did not inform FPL that this indication was not identified during the prior examinations. The missed detection was identified during the post outage review activities. Corrective actions include: changing data analysis guidelines for lead analysts to report conditions to FPL that may indicate a repairable degradation was not reported in a prior examination; modifying data analysis guidelines for wear-induced degradation to include instructions to screen the 100 kHz differential and 100 kHz absolute channels in addition to the 400/100 kHz differential mix channel, and report flaw-like indications; and including the wear indications that were identified during the SL2-11 inspections, but not reported in SL2-10 inspections, in the training and testing of data analysis personnel.
3891999003 | St. Lucie 2 | 04/06/1999 | 05/06/1999 | 9905130085 | <strong>ECCS Suction Header Leaks Result in both ECCS Trains Inoperable and TS 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1999, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power. While performing a periodic inspection of the Unit 2 emergency core cooling system suction piping, FPL non-licensed personnel identified evidence of through wall leakage in both ECCS trains. Both trains of the emergency core cooling system suction piping were declared out of service at 1110 hours and a Technical Specification 3.0.3 shutdown was initiated. Based on subsequent NRC verbal agreement that Class 3 flaw evaluations can be applied to operability evaluations for moderate energy Class 2 piping, FPL declared both trains of ECCS piping operable, Technical Specification 3.0.3 was exited, and the Unit 2 down power was terminated at approximately 28 percent reactor power at 1640 hours. On April 7, 1998, FPL submitted a formal relief request from the immediate repair/replacement requirements of Section XI of the ASME Boiler and Pressure Vessel Code. Code Repairs were completed by April 16, 1999. The through wall piping defects were caused by chloride induced OD stress corrosion cracking of the piping. Corrective actions include the Code repairs, pipe coatings, and periodic inspection of the subject piping until the piping is replaced during the next scheduled refueling outage.
3891999004 | St. Lucie 2 | 04/15/1999 | 06/30/1999 | 9907070215 | <strong>As Found Cycle 10 Pressurizer Safety Valve Setpoints Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1999, St. Lucie Unit 2 was in Mode 1 at approximately 50 percent reactor power. Wyle Labs informed FPL of unsatisfactory test results for the Code pressurizer safety valves (PSVs) removed during the cycle 11 refueling outage. Wyle Labs was contracted to perform the offsite pressurizer safety valve testing and the testing was conducted within the required time restraints. Technical Specification 3.4.2.1 requires the PSVs to lift at 2500 psia (+/-1 percent). The as found settings of the removed St. Lucie Unit 2 pressurizer safety valves were from 1.6 to 3.8 percent high, outside the Technical Specification tolerance limit of +/-1 percent. The cause of the highest failed pressurizer safety valve test was a manufacturing process defect, and all pressurizer safety valves experienced mechanical setpoint drift over the operating cycle. There is no past or present operability concern as the subject pressurizer safety valves were removed and replaced with pre-tested valves during the St. Lucie Unit 2 cycle 11 refueling outage. There was no affect on the health and safety of the public during past St. Lucie Unit 2 cycle 10 power operations because the limiting overpressure analyses remain bounded when actual St. Lucie Unit 2 cycle 10 operational parameters were considered.
3891999005 | St. Lucie 2 | 06/04/1999 | 07/06/1999 | 9907120142 | <strong>CEA Drops Result in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1999, St. Lucie Unit 2 was in Mode 1 at approximately 49 percent reactor power. An event response team was in the process of trouble shooting recent control element assembly anomalies. Unit 2 was held in reduced power pending the event response team trouble shooting results. At 0313 hours, four sub group 21 control element assemblies fully inserted into the core during replacement of the sub group 21 power supply. A Utility licensed operator, the nuclear plant supervisor, immediately directed a manual reactor trip. The plant was stabilized in Mode 3 for repairs. Repairs were implemented, and plant restart and power ascension commenced on June 11, 1999. The control element assembly drop event was caused by procedural inadequacies that did not require verification of the proper seating of a power switch. This resulted in loss of power to the control element assemblies when their sub group was transferred off the hold bus. Loss of power to the sub group 21 control element assemblies was corrected by resealing the sub group 21 power switch. Procedure changes are planned to correct the lack of procedural guidance for CEA sub group power switch replacement. The event response team conducted other corrective actions related to the original control element assembly anomalies.
3891999006 | St. Lucie 2 | 06/06/1999 | 11/24/1999 | ML99340040 | <strong>Sub-Critical Reactor Trip Due to Inadvertent MSIV Opening</strong><br /><i>Abstract:&nbsp;</i>On June 6, 1999, St. Lucie Unit 2 was stable in Mode 3 with all control element assemblies fully inserted for troubleshooting of the Unit 2 control element assembly motion control system. The main steam isolation valves were closed in accordance with an equipment clearance order. During the release of the equipment clearance order following completion of maintenance, the 2B main steam isolation valve, HCV-08-lB, unexpectedly opened to approximately 90 percent of full open. Due to the resulting pressure differential between the 2A and 2B steam generators, a reactor trip signal was generated and all trip circuit breakers opened. Subsequently, the 2B main steam isolation valve was closed. The event was caused due to personnel error when the clearance was released. Procedural guidance on how to restore the main steam isolation valves was not followed. Corrective actions included Operation supervision instruction to the operating crews, stand down meetings, operator aids, and training. This revision expands on the initial unsuccessful operator attempts to close the MSIVs.
3891999007 | St. Lucie 2 | 06/10/1999 | 07/16/1999 | 9907210143 | <strong>Personnel Error During Reactor Startup Led to Unplanned Cooldown Transient</strong><br /><i>Abstract:&nbsp;</i>This voluntary LER describes an unplanned reactor plant cooldown transient that occurred on June 10, 1999. At 0345 hours on June 10, 1999, Unit 2 was in Mode 3 at normal operating pressure and normal operating temperature. A reactor startup was in progress, but temporarily suspended to trouble shoot annunciator problems. Licensed control room personnel decided to perform post maintenance testing on the number 3 throttle valve, an evolution that required latching the turbine. At 0412 hours, the turbine was latched without incident. At approximately 0420 hours, the control room was informed that the testing was complete and that the turbine could be tripped. After the turbine was locally tripped, the main feedwater 15 percent bypass valves were checked, but erroneously not reset, because the controller output had not changed. At 0423 hours, several annunciators came in which indicated a steam generator overfeed condition including letdown low pressure, steam generator high levels, and pressurizer low level. At that time, the 15 percent valves were reset, the overfeed was terminated, and levels were restored to normal conditions. This event was caused by the failure to use existing procedural guidance on turbine shutdown. Contributing factors include non-conservative reactivity management decisions, inadequate operator knowledge on the operation of the main feedwater 15 percent bypass valves, and an inadequate pre-evolution brief. Corrective actions include training, briefings, and procedure changes.
3891999008 | St. Lucie 2 | 12/14/1999 | 01/12/2000 | ML00367707 | <strong>Improper Return of RPS Channel Back in Service Results in Operation Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1999, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power. On December 14, 1999, FPL determined that channel "D" of the reactor protection system steam generator low level trip was placed back in service without the post maintenance testing required by a temporary change to procedure 2-OSP-62.02, "RPS Logic Matrix Test." The cause for this event was human error. Proper oversight was not maintained following the decision to perform the logic matrix test using a temporary change to the logic matrix test procedure. Upon discovery, FPL performed the required post maintenance testing. Operations personnel were informed of the incident to prevent recurrence.
3901999002 | Watts Bar 1 | 02/27/1999 | 03/29/1999 | ML07325032 | <strong>Ice Condenser Bay 1 Lower Inlet Door Ice Buildup</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1999, while Unit 1 was in mode 3 progressing to cold shutdown for refueling, and during an inspection of the lower ice condenser, it was discovered that ice buildup had occurred such that both lower inlet doors in bay 1 were found to exceed their maximum allowable opening force as specified in the Technical Specification Surveillance Requirement 3.6.12.4. This condition has existed such that it has exceeded the shutdown time requirement of Technical Specification 3.6.12. Therefore, this condition is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B). Inspection of the other bay doors revealed that no other doors would have been impeded from opening. Engineering judgment is that the bay 1 doors would have performed their function. The cause of this event was determined to be damage resulting from a steam generator manway cover moisture leak (secondary side) inside containment being condensed and frozen behind the bay 1 lower inlet doors. This condition was such that the resultant damage from the ice buildup would have prevented satisfactory completion of Surveillance Requirement 3.6.12.4. Corrective actions included: 1) removing the ice buildup and replacing the bay 1 doors and 2) repairing of the steam generator manway cover steam leak.
3901999003 | Watts Bar 1 | 03/09/1999 | 04/08/1999 | ML07325032 | <strong>Fire Barrier Breach Involving Removal of Fire Wrap</strong><br /><i>Abstract:&nbsp;</i>On March 9, 1999, during a fire barrier inspection while Unit 1 was in mode 6, it was discovered that a fire barrier (an electrical raceway radiant energy shield) had been breached that protects cable 1NM1333D involving one channel (1-NE-92-132-E) of the source range monitors. This fire barrier at electrical penetration 1-PENT-293-43-D is required to protect this source range cable during an Appendix R fire event. Upon discovery, fire protection impairment permit C99-0249 was issued and compensatory measures were established. It was determined through the investigation that the condition had existed during plant operation. Since the fire wrap is required for an Appendix R event and may have been in a condition where it would not have performed its function, this condition was considered outside the design basis and, therefore, TVA is reporting this condition under 10 CFR 50.73(a)(2)(ii), The cause of this event could not be exactly determined. However, it was determined to have been most likely breached during the performance of a local leak rate test during the first refueling outage and never replaced. Corrective actions included: 1) fire protection impairment permit was issued, and compensatory measures established, 2) the subject breach has been repaired, 3) caution signs have been placed on each electrical penetrations wrapped with a radiant energy shield (RES), 4) an awareness memorandum is being issued to each organization that has a potential for interfacing with the RESs, and 4) this event is being included in the 1999 continuing training for engineering support and mechanical maintenance personnel.
3901999004 | Watts Bar 1 | 04/11/1999 | 05/11/1999 | ML07325032 | <strong>Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 11, 1999, at 0042, the unit was in mode 3 at normal operating temperature and pressure performing procedures, 1-SI-85-2, Reactivity Control Systems - Moveable Control Assemblies, and 1-TRI-85-1, Reactivity Control Systems - Moveable Control Assemblies. While testing the first rod bank, shutdown bank A, by withdrawing the bank 10 steps, the operator released the In-Hold-Out switch to stop the rod withdrawal. He then noted continued outward rod motion, and the crew initiated a manual reactor trip. All systems performed as expected following the trip. TVA is reporting this event under 10 CFR 50.73(a)(2)(iv). The root cause of this event was determined to be a failed logic card in the rod control system logic cabinet. Corrective actions included replacement of failed components and subsequent testing. TVA is evaluating further corrective actions pending results of a "postmortem" on the failed logic card.
3901999005 | Watts Bar 1 | 07/14/1999 | 08/13/1999 | ML07325033 | <strong>Both Trains of Emergency Gas Treatment System Placed Out of Service</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1999, Operations tagged Train B emergency gas treatment system (EGTS) for scheduled maintenance. Two separate hold orders (clearances) were to be placed for the work. The first hold order contained an error which would have resulted in having the discharge path of both trains of EGTS isolated once the second hold order was placed. The control room crew realized the second hold order would place the unit in a Limiting Condition for Operation (LCO) 3.0.3. Both trains of EGTS would have been out of service. The control room crew suspended activities associated with the second hold order and identified the problem incorrectly as a scheduling issue. The operators were unaware that the field operator had placed a tag out of sequence with the process which resulted in isolating the second train of EGTS for less than 30 minutes. On July 14, 1999, during the investigation of a corrective action document, Operations realized that portions of the second hold order affecting the discharge path of the EGTS had been placed, thus, both trains of EGTS had been out of service for a brief period of time. The root cause of this event was an error in a hold order which allowed both trains of EGTS discharge paths to be isolated at the same time. Corrective action included counseling and training for the individuals involved with the error in the hold order, developing lessons learned by the involved individuals to discuss with other operating crews, reviewing active hold orders that had been reviewed by the involved tagging supervisor, and developing a training module on the EGTS for the licensed and non-licensed operators' requalification training.
3901999006 | Watts Bar 1 | 07/27/1999 | 08/26/1999 | ML07325033 | <strong>Alignment of Battery Charger 6-S</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1999, with unit 1 in Mode 1 operating at approximately 100 percent reactor power, Operations personnel identified that Battery Charger 6-S was being supplied from an A train AC source while it was configured to supply Battery Board II, a B train board. Upon discovery, the personnel entered Limiting Condition for Operation (LCO) 3.8.4, "DC Source - Operating", Action A. Battery Charger 6-S was removed from service and realigned such that it was supplied from a B train AC source. LCO 3.8.4 was then exited within the two hour action time limit. A subsequent investigation determined that this condition existed for approximately 18 hours. This condition is being reported in accordance with 10 CFR 50.73 (a)(2)(i)(B). The cause of this event was determined to be personnel error due to incorrect communication between operation personnel during the pre-job briefing. Contributing causes were perceived pressure to complete the task, inadequate level of supervision, inadequate post-job review, misleading labeling, and corresponding procedure nomenclature. Corrective actions included realignment of the affected battery charger, standdown meetings for Operations personnel, operating procedure revisions and disciplinary actions were taken in accordance with the TVA personnel policy.
3951999001 | Summer 1 | 03/11/1999 | 04/06/1999 | 9904130334 | <strong>Missed Surveillance Test for Electrical Equipment Protective Services</strong><br /><i>Abstract:&nbsp;</i>This report is made due to entering Technical Specifications (TS) 4.0.3. On March 11, 1999, at 1100 hours, TS 4.0.3 was entered due to a missed surveillance test for Electrical Equipment Protective Devices. A metal jumper on the back of the phase 3 relay case between terminals 2 and 3 for the Reactor Coolant Pump breakers did not have current passed through it as part of Surveillance Test Procedure (STP) 502.001, 7.2 kV Breaker Test. Presence of this jumper is needed for the instantaneous trip function of the relay. This was discovered as the result of an extent of condition look for a similar condition with the phase 3 relay metal jumper for the circulating water motor circuit breakers and electrical busses 1C1/1C2 and 1C3/1C4/1C5 feeder breakers, which were tested as a part of STP 508.001, 7.2 kV Breaker Testing. Fire watches were posted per the TS 3.8.4.3 LCO requirement. Troubleshooting plans were written, continuity testing was satisfactorily performed on the jumpers to meet TS 3.8.4.1 and 3.8.4.3, and TS 4.0.3 was exited on March 11, 1999, at 1645 hours.
3951999002 | Summer 1 | 03/16/1999 | 01/31/2000 | ML00367951 | <strong>Valve Surveillance Test Causes System to be Potentially Outside Design Basis--REVISED</strong><br /><i>Abstract:&nbsp;</i>Prior to performing a stroke test on ECCS hot leg injection valve XVG08889-SI, Operations personnel questioned whether VCSNS would be within the design basis if the test were performed in Modes 1 through 4. Condition Evaluation Report CER-99-186 was initiated on March 8, 1999, to identify this situation. The normal ECCS flow path during the injection phase is through both Residual Heat Removal (RHR) pumps, the RHR heat exchangers, through a cross connected discharge header and into the three cold leg safety injection (SI) connections to the reactor coolant (RC) loops. The system also has a cross-connected discharge path, with isolation valves, which allows full flow pump testing by recirculating the flow to the Refueling Water Storage Tank or to two hot leg injection lines. In conjunction with the CER, Engineering Information Request EIR-80016 was initiated on March 10, 1999, to evaluate the test configuration against plant design basis. An unanalyzed condition has been determined to exist whenever either the hot leg injection recirculation valve (XVG-8881) or the hot leg injection valve (XVG-8889) are opened for ASME code testing while the plant is in Modes 1 through 4. The testing configurations include closing associated cross-connect valves resulting in partial header isolation. If a LOCA were to occur with either XVG08889-SI or XVG08881-SI open, there is a potential that the required design flows might not be delivered to the three cold leg injection lines. The plant estimates that the test conditions account for 8.7 hours of operation per year. The Probabilistic Safety Assessment group performed a sensitivity run which determined that the plant could exist in the test configuration for 50 hours per year before the CDF increased above 1.00E-06. No operability concerns currently exist as testing of the hot leg injection valve (XVG-8889) and full flow recirculation pump testing using XVG-8881 will be deferred to cold shutdown, as allowed by the ASME code. Procedure revisions to implement these changes were completed by April 2, 1999.
3951999003 | Summer 1 | 04/12/1999 | 05/06/1999 | 9905130100 | <strong>Missed Surveillance on Manipulator Crane Load Cell</strong><br /><i>Abstract:&nbsp;</i>V.C. Summer Nuclear Station (VCSNS) Technical Specification (TS) surveillance requirement (SR) 4.9.6.2 requires that each auxiliary hoist and associated load indicator be demonstrated operable within 100 hours prior to start of core alterations by performing a load test. This surveillance was performed satisfactorily on the initial configuration of hoist and load indicator prior to the start of core alterations. On lifting the first control rod drive shaft to be unlatched (P-6), the crew noted that the load cell did not indicate the correct weight. The crew did not unlatch the drive shaft. The crew was not aware that the load indicator was selected for "Peak Load" instead of "Continuous" readout, giving a misleading indication. Because of the indicated load, the refueling crew suspected that the existing load cell had failed and a new (2nd) load cell was requisitioned and installed. The personnel on the manipulator crane believed that they still had permission to unlatch the first control rod drive shaft, and did so. They requested permission from the Control Room to unlatch drive shaft number two. Permission was denied because the required surveillance test for the second load cell had not been performed. Core Alterations were suspended and the required surveillance started on the replacement load cell. The results were unsatisfactory. Both the original and replacement load cells were taken to the calibration lab where it was discovered that both were set for peak load indication. The load cells were changed to continuous readout and both tested satisfactory for accuracy. The original load cell, previously tested, was reinstalled and core alteration recommenced. As the crane was operated with the untested replacement load cell on one control rod drive shaft in core location P-6, a missed surveillance event was declared by Operations. The cause of this event is attributed to the crew not being familiar with the load indicator ability to indicate peak load or continuous readout and failure to comply with the prescribed SR for the manipulator crane. No operability concerns currently exist as testing of the load cell was satisfactory, the crew is cognizant of the switch settings and crane operation has progressed with no impediments.
3951999004 | Summer 1 | 04/13/1999 | 04/12/2001 | ML01109000 | <strong>Fuel Assembly Top Nozzle Holddown Spring Failure</strong><br /><i>Abstract:&nbsp;</i>On April 13, 1999, at 2035 with core offload activities in progress, the defueling crew experienced difficulty obtaining full gripper engagement in two fuel assemblies. Subsequent visual inspection showed that one or more of the gripper fingers had not properly engaged the fuel assembly top nozzle. Withdrawal was immediately suspended and the fuel assemblies were returned to a safe location. The apparent cause of the event was failure of the holddown spring attaching screws. This failure caused the holddown spring clamp to become displaced creating an interference with the fuel handling tools. On August 24, 1999, SCE&G notified the NRC in letter RC 99-0167 that Westinghouse had not completed the root cause of the failure of the holddown spring attaching screws. The results were expected to be completed after the fall outages and submitted within 30 days after receipt from Westinghouse. On January 20, 2000, SCE&G notified the NRC in letter RC 99-0230 of the results of the Westinghouse root cause. Westinghouse letter 99CG-G-0046 states the “primary causal factor for the fractured spring screws is the top nozzle design does not accommodate the variability of Inoonel 600, a material susceptible to Primary Water Stress Corrosion Cracking (PWSCC). " On October 19, 2000, at 1500, following the offload of the Cycle 12 core, ultrasonic testing (UT), visual, and spring scale inspections confirmed 29 twice burned fuel assemblies had top nozzle holddown spring screws that were failed or degraded, as anticipated. On October 27, 2000, replacement of 24 nozzles on twice burned fuel assemblies planned for reinsertion in the Cycle 13 core was completed. To minimize the excess energy present at the end of Cycle 13, 12 twice-burned assemblies discharged after Cycle 10 were inspected, qualified and inserted for Cycle 13.
3951999005 | Summer 1 | 04/12/1999 | 09/07/2000 | ML00374891 | <strong>Engineered Safety Features (ESF) Components Potentially Outside the Design Basis of the Planet</strong><br /><i>Abstract:&nbsp;</i>While performing FSAR verification reviews and SSEI preparations, Virgil C. Summer staff identified a question regarding operator actions during various accident scenarios. Design Engineering personnel received information from Operations on February 16, 1999, regarding the swap-over from the RWST to the Reactor Building recirculation sump. Procedure EOP 2.2, Transfer to Cold Leg Recirculation, allowed draindown of the RWST to the empty alarm level (6%), if the semi-automatic swap-over failed to occur for one train of ECCS. During subsequent review of the consequences, it was determined that the resulting plant configuration was not analyzed and potentially outside the design basis of the plant due to additional water inventory. On 8/07/2000, follow-up evaluations related to this issue were completed. Through these evaluations, it has been discovered that while the physical design requirements of the RWST are satisfied, the assumed operator actions and response times, as detailed in FSAR Section 6.3.2.6 for completing the swap-over to cold leg recirculation from the ECCS injection phase cannot be demonstrated. The timeline provides for automatic and manual actions to complete the semi-automatic swap-over once the lo-lo level (18%) is reached in the RWST, and assures the ECCS pumps are guaranteed a source of borated water. The timeline in the FSAR states that the necessary actions can be completed in approximately 2 minutes, while timed simulator runs take significantly longer. Changes to the station Emergency Operating Procedures will be made to assure there will always be sufficient water to keep the core cool and protect the pumps from cavitation. Additional corrective actions are also being evaluated.
3951999006 | Summer 1 | 05/02/1999 | 05/17/1999 | 9905240114 | <strong>Substantial Safety Hazard with GE 7.2 kV Magne-Blast Circuit Breakers</strong><br /><i>Abstract:&nbsp;</i>On April 15, 1999, V.C. Summer Nuclear Station (VCSNS) submitted a potential Substantial Safety Hazard report due to 7.2 kV Circuit Breakers which failed to close. After further investigation and testing it has been identified that a Substantial Safety Hazard could exist with this failure to close. The identified problem deals with a cotter pin striking the latch check switch mounting bracket and bending it forward. This removes the factory set clearance between the bracket and the switch actuating paddle. This results in the paddle, which is bolted to the trip shaft, rolling the trip shaft to the trip position when the breaker attempts to close. The cotter pin problem is considered a defect in repair by the manufacturer. This condition represents a potential for a common mode failure of Safety-Related Magne-Blast circuit breakers. These breakers are utilized at VCSNS in many applications, including the 7.2 kV Emergency Diesel Generator electrical buses. No operability concerns currently exist as the latch check switch, latch check switch mounting bracket, and the actuating paddle have been removed from all Safety-Related circuit breakers at the station. The function of the latch check switch is to enable rapid repeated breaker closure, which is not required in the VCSNS application of these breakers.
3951999007 | Summer 1 | 05/11/1999 | 06/10/1999 | 9906150207 | <strong>Missed Surveillance - Turbine Stop Valve Closure Trip Actuating Device Operational Test</strong><br /><i>Abstract:&nbsp;</i>On May 11, 1999, while operating at 3% reactor power, surveillance test procedure STP-142.005 "Turbine Trip Actuating Device Operational Test" was performed to verify the Turbine Stop Valve closure. STP-142.005 had an identified test frequency of "prior to entering Mode 1, if not performed in the previous 31 days." The surveillance frequency of Technical Specification 3.3.1, Table 4.3-1, Item 17, specifies "S/U," "if not performed within previous 31 days." The V.C. Summer Nuclear Station (VCSNS) staff determined that the frequency requirement of STP-142.005 did not meet the literal frequency requirement, "S/U," of Table 1.2 of the Technical Specifications, "prior to each reactor startup." Because the test was performed following reactor startup, it is being considered a missed surveillance. Contributing to this is the fact that there are conflicting requirements between the surveillance frequency and the actual mode requirement for the Turbine Stop Valve Closure Trip Actuation Device Operational Test (TADOT) in Technical Specification 3.3.1. Table 4.3-1. While the TADOT frequency is required to be performed prior to reactor startup (mode 3), the actual mode for which the surveillance is required is mode 1. Therefore, even though the surveillance was performed in mode 2 (at 3% reactor power), the surveillance was actually required prior to 5% reactor power (mode 1). Successful completion of the surveillance test verified that the turbine stop valve closure interlocks were functioning properly. STP-142.005 will be revised to allow performance prior to reactor startup (Mode 3 operations). This revision will be completed by August 31, 1999. Due to the conflicting guidance described above, the reportability determination of Technical Specification 3.3.1, Table 4.3-1, is subjective. Although we feel that the surveillance was not required until entry into mode 1, and because verification of turbine stop valve closure during the recent refueling outage met the intent of the surveillance requirement, this report is conservatively being made.
3951999008 | Summer 1 | 05/18/1999 | 06/17/1999 | 9906230134 | <strong>Manual Reactor Trip due to Main Turbine High Vibration</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1999, following the completion of RF11 in which the Main Turbine HP Rotor was replaced and during the initial power escalation, plant personnel initiated a manual reactor trip at 82% in response to high vibration on Main Turbine Bearings 1 and 2. As turbine load was being increased, Operations received the Main Turbine Vibration High Annunciator. After verifying actual vibration, Operations initiated a load reduction to attempt to decrease the level of vibration. The levels of vibrations continued to increase as the load was reduced. In accordance with plant procedures, Operations initiated a manual reactor trip when the vibration on Bearing #2 increased above 12 mils. The cause of the high vibration was determined to be light rubbing within the new mono-block high turbine rotor. On May 19, 1999, the plant was restarted successfully.
3951999009 | Summer 1 | 06/04/1999 | 07/06/1999 | 9907120156 | <strong>Reactor Trip Due to Spurious High Flux Trip Signal in Power Range Nuclear Instrument Drawer N43</strong><br /><i>Abstract:&nbsp;</i>On June 4, 1999 at 1358 hours, while at 100 percent reactor power, the plant experienced a reactor trip upon receipt of 2 out of 4 logic coincidences for power range high flux trip. Prior to the trip, I&C technicians were performing surveillance STP 310.006, "NIS POWER RANGE N42 CALIBRATION." With Nuclear Instrumentation System (NIS) drawer N42 in TEST, a technician was in the process of sliding drawer N42 into its cabinet when a trip signal was generated from the output of drawer N43, completing the 2 out of 4 logic required for a reactor trip. The plant was stabilized in Mode 3. The appropriate Safety Related equipment functioned as designed. All auxiliary and secondary systems functioned as required. All control rods inserted fully into the core. The reactor remained in Mode 3, Hot Standby, until the cause was determined and corrective action was taken. The cause of the plant trip was determined to be the generation of a spurious signal from the in-service N43 channel Power Range Upper Detector Current Meter. The defective meter was replaced and, following a post trip review of the plant response, the plant was returned to service at 0922 hours on June 6, 1999.
3951999010 | Summer 1 | 07/30/1999 | 08/30/1999 | 9909030034 | <strong>Ultimate Heat Sink (UHS) Dependent Components Potentially Outside the Design Basis of the Plant</strong><br /><i>Abstract:&nbsp;</i>During a diver's follow-up inspection of the Circulating Water Pump House, it was discovered that blank flanges were present on two anti-siphon pipe stubs that are installed on the 36" diameter pipe connecting the Service Water Pond (Ultimate Heat Sink, UHS) with the Monticello Reservoir. These anti-siphon stubs prevent the draining of the Service Water Pond below the 415'-0" elevation in the event of an instantaneous loss of Monticello Reservoir. The potential condition was discovered during a review of a videotape taken by contract divers. An inspection plan was developed to inspect the flanges for features such as holes or spacers that would enable the performance of the design function of siphon prevention. The divers removed the flanges. Engineering personnel then determined visually that no anti-siphon features were present. The blank flanges were subsequently not reinstalled, thereby restoring the capability of the anti-siphon pipe stubs to perform their design basis function. It was determined that the presence of these blank flanges would have precluded the proper functioning of these anti-siphon pipe stubs and created the potential for draining the Service Water Pond below the assumed minimum level for the UHS (subsequent to an instantaneous loss of Monticello Reservoir). Reduced level impacts the maximum post-LOCA temperature of the UHS. This condition potentially placed the plant outside its design based on possibly exceeding the Service Water system design temperature of 95 degrees F during a postulated design basis LOCA event. The duration these blank flanges were installed cannot be determined.
3951999011 | Summer 1 | 08/06/1999 | 10/21/1999 | ML99307022 | <strong>10 CFR 21 on K-Line Breaker</strong><br /><i>Abstract:&nbsp;</i>On August 6,1999, during performance of a Surveillance Test Procedure on an ABB k-Line breaker removed from cubical XSW1DB1 07D, the breaker failed to trip on the long time delay setting. Non-Conformance Notice (NCN) 99-1129 was written to document the failure and disposition the failed breaker. Upon investigation and through discussions with the ABB Service Inc., Charlotte Service Center, 100820 H Independence Pointe Pkwy, Matthews, North Carolina, 28105, it was determined that the shunt trip wires were interfering with the trip shaft paddle of the breaker. This condition can prevent the breaker from either tripping or closing.<br /><br /> The cause was determined to be inappropriate routing and/or insufficient support of breaker wiring during initial manufacture and overhaul. <br /><br /> VCSNS utilizes these breakers in many applications, including the 48OVAC, Safety-Related electrical buses. The shunt trip wiring problem is considered a defect in a basic component supplied to a facility. This condition represents a potential for a common mode failure for safety-related K-Line breakers.
3951999012 | Summer 1 | 09/30/1999 | 10/29/1999 | ML99316031 | <strong>Inadvertent Start of 'B' Residual Heat Removal (RHR) Pump</strong><br /><i>Abstract:&nbsp;</i>At 1410 on September 30, 1999, during performance of Electrical Maintenance Procedure EMP-405.002 on a spare breaker in cubical XSW1DB1 05C, the four wheel roll around cart utilized for breaker removal came into contact with the manual close lever for the bottom breaker in the Motor Control Center (MCC), XSW1DB1 05D. This breaker (XSW 1DB1 05D) supplies power to the 'B' train Residual Heat Removal (RHR) pump. The breaker closed causing the 'B' train RHR pump to start. Due to the high noise level in the switchgear room, the electrician performing the maintenance task was wearing earplugs and did not hear the breaker close. The electrician exited the area with the breaker from XSW1DB1 05C. The pump ran for approximately six minutes prior to being stopped by the control room Operators. At 1416 the pump was secured and placed in pull-to-lock after verifying that no apparent demand signal was present. The pump remained in Pull-to-Lock while the investigation continued. At 1445 on September 30, 1999, it was determined that this was. an inadvertent actuation of the pump caused by human error. At this time, the pump was restored to standby which is the normal operating condition.
3951999013 | Summer 1 | 09/29/1999 | 10/29/1999 | ML99316031 | <strong>Inadequate Surveillance Test for Control Room Ventilation Technical Specification</strong><br /><i>Abstract:&nbsp;</i>V.C. Summer Nuclear Station (VCSNS) Technical Specification (TS) surveillance requirement (SR) 4.7.6.e.3 requires that the control room normal and emergency air handling system be demonstrated operable every 18 months by verifying the system starts on a simulated SI or high radiation test signal and provides a positive control room pressure with a maximum of 1000 cubic feet per minute (CFM) of outside air during system operation. This surveillance was performed on 3/9/99 just prior to a VCSNS refueling outage in accordance with surveillance test procedure STP 454.002, task sheet STTS 9900700, with data obtained through the performance of maintenance procedure MMP-460.024. The test was noted as satisfactory. Subsequent to the outage, VCSNS Plant Support Engineering (PSE) began a review of maintenance air handling procedures to assure conformance with accepted HVAC standards recognized by ASHRAE and SMACNA. PSE identified that a table in MMP-460.024 utilized to convert velocity pressure into air mass flow did not contain density corrections for the air temperature. Condition Evaluation Report CER-99-954 was initiated to identify the error in MMP-460.024. PSE initiated an evaluation of this error on air handling systems with respect to historical flow measurements. Airflow measurements taken on 3/9/99 for STP-454.002 were re-evaluated and found to exceed the 1000 CFM outside air allowed by TS for "B" train control room ventilation (CRV) system with an adjusted flow rate of 1082 CFM. Nonconformance Notice NCN-99-1289 was generated on 9/29/99 to determine system impact and corrective actions. The provisions of TS 4.0.3 were utilized. Disposition to this NCN included performance of the surveillance test under controlled conditions with the data analyzed to proper HVAC standards. Results of this test, performed on 9/30/99 were satisfactory and below the TS limit. The cause of this event is attributed to an inadequate procedure, MMP-460.024. A table used to adjust field measurements of air velocity pressure to airflow did not contain the proper density correction factors. No operability concerns currently exist, as testing of the "B" train CRV system was satisfactory An analysis of the historical data for "A" and "B" trains of CRV was performed and resulted in no additional noncompliances. Engineering evaluated the potential dose consequences associated with this issue. A minor increase in dose would have occurred, however, doses would have remained well below the GDC 19 limits.
3951999014 | Summer 1 | 12/29/1999 | 05/17/2006 | ML06142014 | <strong>Kaowool Fire Barriers Outside 10CFR50 Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>On December 28, 1999, Virgil C. Summer Nuclear Station (VCSNS) commissioned testing on Kaowool triple wrap fire barriers. The testing was conducted to confirm the fire resistance rating of typical plant specific design considerations. On December 29, 1999, engineering personnel determined, from a review of preliminary test data, that some as installed applications may not meet the current regulatory requirements for maintaining one train free of fire damage for one hour. Station Condition Evaluation Report (CER) 99-1520 was generated to document this event and to track actions for resolution. As a result of this test, all surface mounted configurations, and 4" and larger conduit and 6" x 36" raceways suspended in open air, passed the 1-hour fire rating. Some of the cables in 1" conduit, 6" x 6" raceways, and air drop cables suspended in open air failed the Generic Letter (GL) 86-10, Supplement 1 megger when subjected to an ASTM E-119 fire test. VCSNS has implemented compensatory actions (fire watches) as a conservative measure, for all Kaowool Fire Barriers that are needed to achieve and maintain post-fire safe shutdown in accordance with Appendix R and 10CFR50.48. Adjustments to these compensatory actions will be based on the results of further engineering evaluation, and the completion of plant modifications.
3971999001 | Columbia | 06/28/1999 | 07/20/1999 | 9907270226 | <strong>Failed Relay Causes ESG Signal to Close All 8 MSIV's While Plant Was Shutdown</strong><br /><i>Abstract:&nbsp;</i>On June 28, 1999 at approximately 1244 hours the plant was in Mode 4 during a fuel savings dispatch. The reactor vessel head was in place and the head bolts properly tensioned. All control rods were verified to be full in and no core alterations were in progress. The A-Train of the Residual Heat Removal System was in service and performing the shutdown cooling function. The Emergency Core Cooling System equipment that is required by technical specifications for Mode 4 operation was operable. A surveillance of the main turbine throttle valve position switches was in progress. The Nuclear Steam Supply Shutoff System (NSSSS) generated an unexpected Main Steam Isolation Valve (MSIV) closure signal, and all eight MSIV's and the inboard main steam line drain valve closed. Surveillance testing of the main turbine throttle valve position switches was stopped. An Incident Review Board was formed to investigate the event. The resident NRC inspector was notified and the NRC was notified of the unexpected Engineered Safety Feature (ESF) actuation via the Emergency Notification System. The cause of this event was the failure of Reactor Protection System relay RPS-RLY-K10D, in that contacts opened due to vibration from an adjacent relay under test. This generated a half MSIV closure signal. The other half isolation signal was generated, as expected, by the main turbine throttle valve position switch surveillance. There were no personnel errors or procedural deficiencies that contributed to this event. Relay, RPS-RLY-K10D, was replaced and tested on June 30, 1999. In addition, testing of the turbine throttle valves was completed on July 1, 1999, and did not cause an MSIV closure signal. There were no safety consequences associated with this event. This event is being reported per the requirement of 10CFR50.73(a)(2)(iv) as an event or condition that resulted in an automatic actuation of an Engineered Safety Feature. The ESF automatic actuation was not from a valid NSSSS actuation signal. However, the actuation occurred while the isolation s stem was in service.
3971999002 | Columbia | 10/27/1999 | 11/29/1999 | ML99341012 | <strong>Operation or condition prohibited by WNP-2 Technical Specifications due to a missed surveillance</strong><br /><i>Abstract:&nbsp;</i>On October 27, 1999 at 1300 hours, with the plant in Mode 1 at 100 percent power, plant operators questioned a discrepancy between indicated drywell identified leakage rate and the value of drywell identified leakage rate measured by an alternate method. Upon further investigation plant staff determined that the identified leakage rate signal to the control room indicating instrument was not being received because its signal converter was de-energized. Further investigation determined this condition existed since the signal converter batteries discharged after power was removed during an electrical bus maintenance period in the R-14 refueling outage. Total drywell leakage is required to be verified within specified limits every 12 hours in modes 1, 2, or 3 pursuant to Technical Specification Surveillance Requirement (SR) 3.4.5.1. Control room operators at WNP-2 used the erroneous indication to calculate total drywell leakage from the time the plant entered the mode of applicability for SR 3.4.5.1 on 10/22/99, until the de-energized instrument was discovered on 10/27/99. The cause of the signal converter failure is inadequate interface between project engineers and procedure writers during the design change process resulting in inadequate procedure revisions to be implemented. Upon discovery of this condition, corrective action was taken to restore power to the signal converter at which time the correct drywell identified leakage indication was immediately observed on the control room indicator. There were no adverse safety consequences associated with the lapse of identified leakage rate indication. Although the requirement of SR 3.4.5.1 to verify total leakage rate within the limit was not met during this period, the absence of the identified leakage sump fill rate monitor alarm and recorded unidentified leakage rate indicate that the limit for total leakage of 25 gpm in a 24 hour period was not exceeded.
3971999003 | Columbia | 10/22/1999 | 01/17/2000 | ML00367772 | <strong>Voluntary Licensee Event Report of Failure to comply with the Technical Specification Bases description of a Channel Check</strong><br /><i>Abstract:&nbsp;</i>On October 22, 1999 at 1309 hours, with the plant in mode 2 and power ascension in progress following the R-14 refueling outage, plant operators questioned the adequacy of the method in which a surveillance activity was being performed. Technical Specifications Surveillance Requirement (SR) 3.3.5.2.1 requires a 12-hour Channel Check for the Condensate Storage Tank (CST) [KA] level-low function. This function automatically transfers the Reactor Core Isolation Cooling (RCIC) [BN] system suction from the CST to the suppression pool when low CST level is sensed. The Channel Check for this function is performed by verifying the status of the CST level-low alarm is consistent with indications on independent CST level instruments. This method meets the Technical Specifications definition of a Channel Check; however, it is inconsistent with the Technical Specifications Bases description for SR 3.3.5.2.1 which states that performance of a Channel Check will ensure that a gross failure of instrumentation has not occurred. The Bases description does not apply to the non-indicating design of the instrumentation that performs the CST level-low function for the RCIC system. Immediate corrective action was taken to declare the RCIC CST level instruments inoperable and configure the RCIC system to take suction from the suppression pool. Further corrective actions are to revise the Bases for SR 3.3.5.2.1. The cause of this event is failure to include deletion of SR 3.3.5.2.1 for the CST level-low function in the deviations from NUREG 1434 when the Improved Technical Specifications (ITS) were implemented at WNP-2. There are no safety consequences associated with this event. The Technical Specifications permit the current configuration of the RCIC system for an indefinite period of time and the CST is still available as a source of water if needed. This voluntary report is submitted due to the generic interest this condition may hold for the staff and other licensees.
4001999001 | Harris | 01/06/1999 | 02/05/1999 | 9902090363 | <strong>Spent Fuel Pool water level not maintained greater than 23 feet above stored BWR fuel assemblies.</strong><br /><i>Abstract:&nbsp;</i>At approximately 10:30 on January 6, 1999, with the unit at 100% power, personnel performing spent fuel handling operations noticed that one of the Boiling Water Reactor (BWR) assemblies that they were moving did not fully seat in the storage rack. A question was raised regarding the administrative limit required to maintain 23 feet of water above the fuel assemblies as required by Technical Specification LCO 3.9.11. It was determined that the current limit did not consider the additional margin needed in the event of an assembly being hung on a BWR channel fastener; therefore, fuel movement was halted. An investigation revealed that eight additional assemblies in the pool were not fully seated. Measurements were taken on the nine assemblies to determine what the most limiting administrative requirement should have been. Based on these measurements, 23 feet of water had been maintained above the most limiting assembly since the problem was discovered on January 6, 1999; however, a subsequent review of the operating logs for the previous months showed that the revised administrative limit (1.25" higher than the previous limit) had not been met (by a maximum of 0.75") on more that one occasion. Therefore, the actions required by LCO 3.9.11 were not met on those occasions. The root cause of this event is that the procedure provides ambiguous guidance regarding channel fastener tolerances and the fact that the fasteners could bend under specific circumstances. Corrective actions taken have been: 1) Halted fuel movement and increased water level to ensure compliance; 2) Seated seven of the nine assemblies (i.e., these seven did not have bent channel fasteners, but were hung on the side of the fuel rack by the lower edge of the fastener); 3) Revised the administrative limit such that 23 feet of water remained above the two BWR assemblies with bent channel fasteners (i.e., not fully seated); 4) Performed an engineering analysis for a BWR assembly being suspended on a side of a rack by a channel fastener, and 5) Seated the two assemblies with bent channel fasteners. Planned corrective actions are to revise procedures and to provide additional training for fuel handling personnel.
4001999002 | Harris | 01/14/1999 | 02/12/1999 | 9902190035 | <strong>Reactor trip due to not removing a temporary device from a relay following calibration</strong><br /><i>Abstract:&nbsp;</i>At approximately 09:18 on January 14, 1999, with the unit at 100% power, personnel performing a relay calibration failed to remove a temporary blocking device prior to reinstalling the relay. This blocking device simulated a continuous trip signal on the output of the undervoltage timing relay; therefore, reinstalling the relay simulated an undervoltage trip signal to the associated bus. Loads powered from this bus included one of the plant's three Reactor Coolant Pumps (RCPs) and the feeder breaker for another bus, which also powered one Reactor Coolant Pump. This loss of power to two of the plant's three RCPs (while above 10% power) satisfied the logic for an automatic reactor trip. Safety systems functioned as required, including the automatic start of the three auxiliary feedwater pumps. Although the procedure for performing the calibration activity directed the technicians to remove the blocking device, the individuals failed to do so. The root cause of this event is human error attributed to the way the technicians were using the procedure (i.e., although one of the technicians had a copy of the procedure in his hand, the technicians were performing some steps from memory). Corrective actions taken have been: 1) Counseled the personnel involved in this event, including their supervision; 2) Conducted a stand-down meeting for site personnel on this and other recent human performance events, and; 3) Created a high-visibility device to be used as a blocking device when calibrating relays. Planned corrective actions include: 1) Revision of the applicable procedure (PIC-E070) to provide more specific guidance on steps applicable to these types of relays.
4001999003 | Harris | 01/23/1999 | 02/22/1999 | 9902260069 | <strong>Plant outside the design basis due to isolation of the fire protection containment sprinkler system.</strong><br /><i>Abstract:&nbsp;</i>At approximately 0230 on January 23, 1999, with the unit at 82% power, plant personnel isolated the containment fire protection sprinkler system. Following isolation, the containment sprinkler system was inadvertently left inoperable for approximately four and a half days. The Harris Nuclear Plant (HNP) safe shutdown analysis credits the containment sprinkler system to provide protection (in lieu of a fire barrier or the required distance for separation criteria) for the pressurizer heaters. The inoperability of the containment sprinkler system for an extended duration placed the plant in a condition outside the design basis. The root cause of this event is human error by Operations personnel in that applicable plant procedures were not used to operate the containment sprinkler system. Contributing causes include: (1) Improper communications between watch stations (2) Procedure non-compliance (3) Inadequate training (4) Inadequate management oversight of the fire protection program. Completed Corrective Actions: (1) The containment sprinkler system has been restored to operable status. (2) Interim measures have been established to heighten sensitivity to fire protection equipment inoperabilities and fire protection procedure usage. (3) Operations personnel involved were counseled. Planned corrective actions: (1) Reemphasize the expectations for Operations supervision and personnel that performance of, and adherence to, fire protection system procedures is to be commensurate with procedure performance and adherence expected for other plant systems. (2) Perform training for appropriate plant personnel on proper operation of applicable fire protection components. (3) Complete a high level investigation into the inadequate management oversight of the fire protection program.
4001999004 | Harris | 03/12/1999 | 04/08/1999 | 9904130344 | <strong>Unit Trip due to the degraded condition of a steam generator water level flow control valve.</strong><br /><i>Abstract:&nbsp;</i>At 06:39 on March 12, 1999, the unit experienced an automatic reactor trip from 100% power. The unit tripped on a high water level trip signal on one of the three steam generators. The 'hi-hi' steam generator water level signal trip setpoint is 82.4 percent on the narrow range level scale. Just prior to the automatic trip, the 'C' Steam Generator (SG) water level was observed to be increasing in an uncontrolled manner with its Feedwater Regulating Valve (FRV) in automatic control. The control room operators took manual control of the 'C' FRV, in an attempt to restore water level to its normal range. The FRV response, as observed from the controller output signal and the resulting feed flow indications, was slower and not as uniform as expected. After approximately eight minutes of attempting to control the 'C' steam generator water level in manual, the performance of the valve positioner degraded to the point where operator control was highly questionable. The operators had set a limit, at which they would initiate a manual reactor trip; however, an automatic trip occurred prior to their taking the planned action. The most probable failure mechanism for the 'C' FRV is a combination of a loose stroke adjustment screw on the air-operated valve positioner and a sticking pilot valve within that same positioner. This degradation in the material condition of the valve's positioner is attributed to an inadequate preventative maintenance program/schedule for the Feedwater Regulating Valves. Corrective actions that have been taken include: 1) replacing the positioners on all three Feedwater Regulating Valves, including a verification that the stroke adjustment screw on each is not loose, and 2) Determining that similar air operated valve positioners do not have a potential for similar failures which may jeopardize plant safety or reliability. Planned corrective actions include reviewing and revising, as applicable, the preventative maintenance schedules for Bailey air operated valve positioners.
4001999005 | Harris | 03/13/1999 | 04/12/1999 | 9904200022 | <strong>Engineered Safety Features Actuation Systems Technical Specifications exceeded</strong><br /><i>Abstract:&nbsp;</i>At 23:31 on March 13, 1999, with the Harris Nuclear Plant (HNP) shutdown in Mode 3, HNP exceeded Engineered Safety Features Actuation Systems (ESFAS) Technical Specifications (TS) 3.3.2 Action 21. Train "A" of Solid State Protection System (SSPS) was placed in test, at 17:31 on March 13, 1999, to perform corrective maintenance and post-maintenance testing of the "A" Reactor Trip Breaker. HNP Licensed Operators incorrectly determined that the most limiting Action for "A" Train SSPS inoperability was a requirement to be in cold shutdown (mode 5) in 30 hours (TS 3.3.2 Actions 14). The Licensed Operators failed to recognize that TS 3.3.2 Action 21 was in effect which required the plant to be in Hot Shutdown (Mode 4) within six (6) hours. Approximately eight (8) hours and 28 minutes elapsed before Licensed Operators recognized TS 3.3.2 Action 21 applicability and subsequently restored "A" Train SSPS to an operable status. During this time, HNP remained in Mode 3 resulting in a violation of TS 3.3.2 Action 21. Cause of this TS violation: (1.) Inadequate procedure revision preparation. (2.) Inadequate Operations review of the TS impact of the work being performed. Corrective actions include: (1.) Revised the applicable maintenance surveillance test procedure (MST-I0072) to adequately identify TS required Actions. (2.) Counseled Operations supervision concerning timely verification and documentation of Operating License/TS compliance. (3.) Complete License Operator training of TS requirements for TS 3.3.1 "Reactor Protection" and TS 3.3.2 "ESFAS". (4) Counsel shift Operations personnel concerning inappropriate acts and causal factors associated with this event.
4001999006 | Harris | 11/24/1998 | 08/04/1999 | 9908100060 | <strong>Containment Isolation Valve Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>At 16:39 on November 24, 1998, with the Harris Nuclear Plant (HNP) shutdown in Mode 4, HNP failed to comply with Technical Specifications (TS) 4.0.4 and TS 3/4.6.3 "Containment Isolation Valves." On May 6, 1999, HNP determined that Containment Isolation Valve, 1CC-176 was inoperable following preventive maintenance performed during the previous refueling outage. Post-maintenance Testing performed on 1CC-176 was inadequate in that safety related portions of the valve circuitry were not adequately tested following maintenance. Subsequent investigation determined that TS Surveillance 4.6.3.1 was not performed as required on 1CC-202 and 1CC-176 in that HNP failed to verify isolation time following maintenance on the valves control circuitry. Therefore, when HNP changed from Mode 5 to Mode 4 on November 24, 1998, HNP was in noncompliance with TS 4.0.4. In addition, with 1CC 176 inoperable, HNP violated TS 3.6.3 due to not performing the required actions within the specified action time. On December 6, 1998, 1CC-176 failed to automatically shut during an applicable slave relay test. The associated penetration was isolated within four hours as required by TS 3.6.3.b. 1CC-176 was subsequently repaired and satisfactorily retested. 1CC-202 was not restored to compliance until the isolation time was verified on December 22, 1998 during normal quarterly inservice testing. Cause of this TS violation: (1) Post-maintenance testing did not adequately test control circuitry and verify isolation time following maintenance. (2.) The procedure which specifies the required post maintenance testing was based on a non-conservative interpretation of TS 4.6.3.1 Corrective actions include: (1) Revise the plant post-maintenance testing procedure to identify appropriate testing requirements for the preventive maintenance associated with this event. (2.) Perform training with applicable site personnel on identifying proper post-maintenance testing requirements for motor operated valves.
4001999007 | Harris | 08/11/1999 | 09/09/1999 | 9909160001 | <strong>Containment Ventilation Isolation Area Radiation Monitors Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1999, with the Harris Nuclear Plant (HNP) at 100% power in Mode 1, HNP determined that containment ventilation isolation signal (CVIS) area radiation monitors (ARM) high alarm setpoints were not within the Technical Specifications (TS) limit of less than three times detector background at rated thermal power (TS 3.3.3.1, Table 3.3-6, Item 1.a.). During the ongoing TS Surveillance Review Project, a member of HNP plant staff questioned the process for ensuring that CVIS ARM high alarm setpoints did not exceed TS required values. The applicable system engineer compared the CVIS ARM high alarm setpoint values with the TS requirements and determined that the TS limit was exceeded. The main control room was notified and the containment purge system was isolated to containment as required by TS 3.3.3.1. Cause of this TS violation: HNP did not have a procedure requirement to verify CVIS ARM high alarm setpoints were within the requirements of TS. Corrective actions include: (1.) Revise the plant procedure for startup testing following a refueling outage to verify CVIS ARM high alarm setpoints are within TS limits. (2.) Revise the plant procedure that implements the digital channel operational test to verify CVIS ARM high alarm setpoints are within TS limits.
4001999008 | Harris | 06/04/1997 | 10/08/1999 | 9910210297 | <strong>Control Room Emergency Filtration System Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>During four refueling outages (RFO5, RFO6, RFO7, and RFO8) with the Harris Nuclear Plant (HNP) shutdown, HNP failed to comply with Technical Specifications (TS) 3.7.6 "Control Room Emergency Filtration System." During these four occasions, the pressure boundary doors for the HNP Control Room Emergency Filtration System (CREFS) were blocked open to allow electrical cables to pass through the opening. Blocking open pressure boundary doors for the CREFS would require additional operator actions to restore the pressure boundary in the event of an accident. HNP TS 4.7.6.d.3. requires CREFS to be demonstrated operable by verifying the system maintains the control room at a positive pressure of greater than or equal to 1/8" Water Gauge at less than or equal to a pressurization flow of 315 cfm relative to adjacent areas during system operation. With the CREFS doors blocked open, HNP would be unable to meet the requirements of this surveillance to demonstrate operability. The additional operator action of unblocking the pressure boundary doors had not been adequately reviewed with regards to design basis and to licensing basis requirements. Therefore, with the CREFS doors blocked open in modes 1-4, both trains of CREFS would be inoperable and TS 3.0.3 would be entered. This condition was identified during RFO8 and documented in HNP condition report (CR) 98-03149. The initial investigation of CR 98-03149 incorrectly determined that the CREFS remained in an operable condition. However, based on further review and evaluation, it was determined on September 8, 1999 that the configuration established during RFO8 caused the CREFS to be inoperable for approximately 2.5 hours and TS 3.0.3 should have been entered. The exact length of time that the CREFS was inoperable during RFO5, RFO6, and RFO7 could not be determined. Cause of this TS violation: Site personnel failed to recognize that blocking open Control Room Emergency Filtration System boundary doors was a change to the facility and as a result did not perform an adequate 10 CFR 50.59 review. Corrective actions include: (1) Revise HNP procedures EST-104, OP-163.01, and AP-002 to clarify CREFS pressure boundary requirements. (2) Conduct training for applicable Operations and Engineering personnel concerning events documented in this report.
4001999009 | Harris | 12/14/1999 | 01/13/2000 | ML00367642 | <strong>Reactor Trip and Auxiliary Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1999 at 0353, the Harris Nuclear Plant (HNP) manually tripped the reactor from 60% power. At 0352 on December 14, 1999 the "A" Condensate Pump tripped due to a ground fault on the associated motor. The trip of the "A" Condensate Pump resulted in subsequent trips of the "A" Condensate Booster Pump and the "A" Main Feedwater Pump. The main turbine load control circuitry sensed the trip of the "A" Main Feedwater Pump and automatically reduced turbine power to approximately 60% (turbine runback). The reactor trip coupled with the loss of the "A" Condensate and Feedwater train resulted in a reduction of steam generator water levels. The main control room staff manually started the three auxiliary feedwater pumps in accordance with the applicable abnormal operating procedure. The steam generator levels continued to lower until the main control room staff manually tripped the reactor at approximately 40% steam generator level prior to reaching the steam generator low-low level automatic trip setpoint of 38.4%. Additionally, following the trip an auxiliary feedwater (AFW) actuation signal was generated due to the low-low steam generator level. However, as stated previously, the auxiliary feedwater pumps had been manually started during the transient therefore, the AFW actuation signal did not start any additional components. Cause of this event: A ground fault on the "A" Condensate Pump motor caused a loss of the "A" Condensate and Feedwater train that resulted in low steam generator water levels and a subsequent manual reactor trip and AFW actuation. Corrective actions include: The "A" Condensate Pump motor was replaced on December 16, 1999.
4091999001 | La Crosse | 03/05/1999 | 03/29/1999 | 9904130286 | <strong>Excessive Back-Flow through FESW Return Line Check Valves</strong><br /><i>Abstract:&nbsp;</i>The La Crosse Boiling Water Reactor (LACBWR) Decommissioning Plan, SAFSTOR Accident Analysis section 9.5, Fuel Element Storage Well (FESW) Pipe Break, assumes the redundant FESW return line check valves would prevent the FESW from draining below the 679' level in the event of a break in FESW system piping, other than in the short section of piping containing the check valves which has been seismically qualified. At this level all spent fuel will remain covered. On 3/5/99, the excessive seat leakage measured in the performance of the Annual Leakage Determination of the FESW Return line Check Valves was verified as reverse flow from the check valves not seating.
4101999001 | Nine Mile Point 2 | 02/12/1999 | 05/13/1999 | 9905240069 | <strong>NMP2 Outside The Design Baisis Due to Safe Shutdown Sevice Water Pump Bay Unit Coolers Being Out-of-Service</strong><br /><i>Abstract:&nbsp;</i>While investigating a discrepancy identified on February 12, 1999, at 0700 hours, with Nine Mile Point Unit 2 (NMP2) operating at full power, NMP2 Operations personnel identified a period of time from January 3 to 31, 1999, when both the Division I and II safe shutdown unit coolers for the NMP2 service water pump bays were out of service at the same time. NMP2 Operations personnel determined that this placed NMP2 outside its design basis. Niagara Mohawk Power Corporation (NMPC) has determined that the root cause of this event was inadequate managerial methods in that the technical review requirements failed to lead procedure developers to consider the safe shutdown requirements during the initial development of the procedure for normal operations and, in 1992, preventive maintenance rotation of service water pump unit coolers. Corrective actions included interim administrative controls for safe shutdown equipment. Preventive actions will include long term administrative controls and operator training for safe shutdown equipment. Additionally, NMPC will perform a reevaluation of safe shutdown equipment, and associated procedures, to provide additional assurance that all fire protection safe shutdown equipment are identified and have proper administrative controls.
4101999002 | Nine Mile Point 2 | 03/04/1999 | 04/05/1999 | 9904130250 | <strong>Missed Technical Specifications Channel Functional Test of the Recirculation Flow Upscale Rod Block</strong><br /><i>Abstract:&nbsp;</i>On March 4, 1999, with Nine Mile Point Unit 2 in full power operation, maintenance support personnel discovered that the Technical Specification Surveillance Requirement 4.3.6, Table 4.3.6-1, Trip Function 5.a, channel functional test requirement for the recirculation flow upscale rod block function, had not been met. The cause of the missed Surveillance Requirement was that the accuracy of the applicable Surveillance Requirement procedure change was not properly verified due to deficiencies in the outage planning and implementation process, and inadequate self-checking. Corrective actions included correcting the applicable Surveillance Requirement procedure and performing the missed Surveillance Requirement test with satisfactory results. Additional corrective actions included enhancing the outage planning and implementation process, addressing the self-checking failure with the individuals involved, and reviewing the remaining refueling outage 6 modifications for similar problems.
4101999003 | Nine Mile Point 2 | 03/05/1999 | 01/07/2000 | ML00367707 | <strong>ADS Nitrogen Leakage in Excess of NMP2 Technical Specifications Surveillance Limits</strong><br /><i>Abstract:&nbsp;</i>Between March 5 and March 12, 1999, Nine Mile Point Unit 2 (NMP2) experienced two events where leakage from the Automatic Depressurization System (ADS) nitrogen storage tanks exceeded the Technical Specification surveillance criteria. Operations personnel determined that the root cause of both events was that NMPC failed to identify the causes and significance of previous events and, therefore, implemented inadequate corrective actions from those events. Corrective actions include repairing the leaks, replacing valves, providing procedural guidance concerning identification of off-normal conditions and repressurization of the nitrogen storage tanks, and reviewing this event with technical support and operations shift personnel.
4101999004 | Nine Mile Point 2 | 03/18/1999 | 04/19/1999 | 9904270191 | <strong>NMP2 Service Water Intake De-Icing Heater Control Circuits do not Meet Fire Protection Program Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1999, with Nine Mile Point Unit 2 in full power operations, engineering personnel determined that the service water system intake de-icing heater control circuits were not included in Updated Final Safety Analysis Report, Appendix 9B, Table 9B.8-3, Appendix R Control Room/Relay Room Fire Analysis. Further review of the design confirmed that a control room/relay room fire could render the intake de-icing heaters inoperable. The root cause was that the architect/engineering firm design staff did not identify the control circuit isolation requirements for service water operation during a control room/relay room fire. Corrective actions include establishing a fire watch patrol and implementing a design change. Niagara Mohawk Power Corporation is evaluating additional preventive actions to be described in a supplement to LER 99-01.
4101999005 | Nine Mile Point 2 | 04/24/1999 | 12/27/1999 | ML00367174 | <strong>Reactor Trip Due to a Main Generator Protection Vots/Hertz Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1999, Nine Mile Point Unit 2 experienced an automatic reactor scram from 100 percent power. The cause of the reactor scram was a fast closure of the main turbine stop and control valves. Operators responding to the event were challenged by several equipment concerns including: failure of the reactor core isolation cooling system to achieve rated flow, the trip of two electrical protection assemblies, an air leak on an auxiliary boiler valve, and the need to restart numerous pieces of plant equipment due to the loss of electrical power during the residual (slow) transfer of the non-vital 13.8 kV buses. The cause of the fast closure of the turbine stop and control valves was determined to be a failure of a main generator protection volts/hertz relay. Corrective actions included: stabilizing the plant, determining and correcting the cause of the equipment failures, revising procedures, training personnel and establishing longer term corrective actions. Technical Specification 3.5.1.f requires a special report when an emergency core cooling system injects water into the reactor coolant system. During this event the high pressure core spray system injected water into the reactor vessel.
4101999007 | Nine Mile Point 2 | 05/25/1999 | 06/24/1999 | 9907060401 | <strong>Violation of Technical Specifications Regarding ASME Code Section XI Class 2 Weld Inspection Requirements Due to Improper Use of A Code Exemption</strong><br /><i>Abstract:&nbsp;</i>On May 25, 1999, with Nine Mile Point Unit 2 (NMP2) at full power, engineering determined that sections of piping and pipe supports in the high pressure core spray system from the condensate storage tank to the pump were improperly exempted from the First and Second Ten Year Interval Inservice Inspection (ISI) Program Plans. As a result of improperly applying the exemptions, Niagara Mohawk Power Corporation (NMPC) did not comply with Technical Specifications Surveillance Requirement 4.0.5.a during the first ten year interval. This discrepancy was discovered during expanded corrective actions from LER 98-21. NMPC determined that the cause of the deviation was misinterpretation of the ASME Code Section XI exemption requirement during the development of both the First and Second Ten Year Interval ISI Program Plans. A contributing cause was identified as inadequate management oversight. As discussed in LER 98-21, NMPC has previously made organizational changes to enhance the oversight and control of the ISI Program. In addition, NMPC has completed an independent detailed review of the Second Ten Year Interval ISI Program Plan.
4101999008 | Nine Mile Point 2 | 05/20/1999 | 06/21/1999 | 9907010253 | <strong>Inadequate Surveillance of Reactor Core Isolation Cooling Check Valve</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1999, while the plant was at 100 percent power, Niagara Mohawk Power Corporation identified that Reactor Core Isolation Cooling Check Valve 2ICS*V249 was not being tested as required by Technical Specification 4.0.5. Technical Specification Surveillance Requirement 4.0.5 requires inservice testing of all ASME Code Class 1, 2, and 3 components in accordance with Section XI of the ASME Boiler and Pressure Vessel Code. Section XI of the ASME Boiler and Pressure Vessel Code requires a quarterly surveillance to reverse flow test Reactor Core Isolation Cooling Check Valve 2ICS*V249. NMPC's surveillance procedure did not properly set up the test condition that would reverse flow test the check valve. The root cause was determined to be that Niagara Mohawk Power Corporation did not properly evaluate the operating parameters to ensure a proper test was developed and implemented. Corrective actions include revising the surveillance procedure to properly test the valve and to include an identifier to protect inservice testing steps, verifying the adequacy of all ASME Code Section XI check valves test methods, revising an administrative procedure to provide instructions on when to obtain engineering input for the development of inservice testing surveillance procedures, and providing a case study of this event to all inservice testing generation specialists and operators.
4101999009 | Nine Mile Point 2 | 05/26/1999 | 11/24/1999 | ML99340041 | <strong>Nonconformance with Technical Specification Regarding ASME Section XI Class 2 Check Valve Reverse Flow Testing</strong><br /><i>Abstract:&nbsp;</i>On May 26, 1999, Engineering Services personnel identified that high pressure core spray (CSH) valve 2CSH*V59 had not been reverse-exercise tested during the second ten year interval as required by American Society of Mechanical Engineers (ASME) Code Section XI. The valve had been appropriately tested during the first ten year interval, but inappropriately exempted from the second ten year plan. This was discovered as a result of the investigation into LER 99-07, "Violation of Technical Specifications Regarding ASME Code Section XI Class 2 Weld Inspection Requirements Due to Improper Use of a Code Exemption," and LER 99- 08, "Inadequate Surveillance of Reactor Core Isolation Cooling Check Valve. The cause of the event has been determined to be that the level of rigor expected of technical evaluations was not communicated to our engineering organization prior to the development of the Second Ten Year Interval 1ST [Inservice testing] Program Plan. In addition, the design information contained in General Electric Specification #22A1483 regarding the safety function of 2CSH*V59 had not been incorporated into the valve design specification or the Updated Safety Analysis Report. Valve 2CSH*V59 was leak-tested and the valve checked properly. Engineering and licensing documentation will be revised to reflect the requisite function of 2CSH*V59. Finally, management expectations will be reinforced with engineering personnel.
4101999011 | Nine Mile Point 2 | 07/19/1999 | 08/18/1999 | 9908270071 | <strong>Valves Not Correctly Tested As Required by Technical Specification 4.0.5</strong><br /><i>Abstract:&nbsp;</i>On July 19, 1999, while Nine Mile Point Unit 2 was shutdown, Niagara Mohawk Power Corporation identified 26 valves in multiple systems that were not being tested as required by Technical Specification 4.0.5. The valves were misclassified as passive valves; therefore, not all required testing was being conducted. The cause of the incomplete testing of the 26 valves was misclassification of the valves due to a misapplication of NUREG-1482, "Guidelines for Inservice Testing at Nuclear Power Plants," Paragraph 2.42, as applied to American Society of Mechanical Engineers Section XI and ASME/ANSI OMa-1988 Addenda (ASME/ANSI OM-1987 Operation and Maintenance of Nuclear Power Plants), Part 10 Codes and Standards. Corrective actions include: reclassifying and testing the 26 valves, reviewing the Nine Mile Point Unit 1 program for similar discrepancies; communicating management's expectations to individuals who misclassified the 26 valves on the importance of considering all design/license bases requirements and maintaining consistency between design/license bases and Inservice Testing Programs, and reviewing all valves that are presently exempt, passive, or had testing requirements reduced in the Second Ten-Year Interval Inservice Testing Program Plan to validate the valves' classification and testing requirements.
4101999012 | Nine Mile Point 2 | 07/06/1999 | 08/28/1999 | 9909030215 | <strong>Inadequate Inservice Testing of Testable Check Valve</strong><br /><i>Abstract:&nbsp;</i>On July 6, 1999, with Nine Mile Point Unit 2 in cold shutdown, operators reported that residual heat removal system Testable Check Valve 2RHS*AOV150 failed to open during valve exercise inservice testing. During troubleshooting, a system engineer observed that the operators on at least one occasion had in the pas misinterpreted the initial movement of the valve actuator shaft to be full movement of the valve to the open position. Based on operator interviews, and review of the check valve trend data sheet, system engineering personnel determined that several previously completed inservice tests for the valve had been misinterpreted as satisfactory. As a result, inservice testing criteria of Technical Specification Surveillance Requirement 4.0.5 were not being met. Niagara Mohawk Power Corporation determined that the cause of this event was the omission of relevant information from Procedure N2-OSP-Q@002, "Residual Heat Removal System Loop B Valve Operability Test..." Corrective actions for this event included: revising Procedure N2-OSP-Q@002, reperforming the appropriate sections of the test, and reviewing this event with the operations staff.
4101999013 | Nine Mile Point 2 | 07/29/1999 | 08/30/1999 | 9909070135 | <strong>Relays in Multiple Systems Were Not Correctly Tested as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 29, 1999, while Nine Mile Point Unit 2 was at 100 percent power, Niagara Mohawk Power Corporation (NMPC) identified 4 relays in the primary containment isolation circuit that were not being tested as required by Technical Specifications. As a result, NMPC performed additional reviews of channel functional test procedures and identified an additional 8 relays in the high drywell pressure isolation and the main steam line high radiation isolation circuits that were not being tested as required by Technical Specifications. Operation of the relays was not properly verified during quarterly channel functional tests. NMPC determined that the cause of the incomplete testing of the 12 relays was due to inaccurate established test boundaries in the test procedures. Corrective actions include: revising the surveillance procedures, testing the 12 relays, training procedure writers and technical reviewers on the interpretation of the definition of channel functional test, and reviewing other channel functional test procedures for similar efforts.
4101999015 | Nine Mile Point 2 | 08/11/1999 | 09/10/1999 | 9909200037 | <strong>Inadvertent Start of Division I Diesel Generator Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1999, while at 100 percent power, Nine Mile Point Unit 2 experienced an inadvertent start of the Division I Diesel Generator while troubleshooting a speed control problem. In addition, Technical Specification Surveillance Requirement 4.8.1.1.3 requires a special report for all diesel generator failures, valid or non-valid. This event is being reported as a non-valid failure. The non-valid failure of the diesel generator was due to a faulty relay in the primary start circuit that had high contact resistance. The high contact resistance in the control circuit for the motor-operated potentiometer resulted in the inability to vary the diesel generator engine speed. During troubleshooting, the diesel generator started due to inadequate work order instructions that disabled one but not both start circuits. The independence of the review of the work order was compromised because a technical support engineer and an instrument and controls technician worked together to plan and review the work order instructions. This resulted in the failure to identify the secondary start circuit. A contributing cause was that the broad guidance for the development and review of high priority work orders in the work control procedure was not being interpreted and implemented as intended. Corrective actions include: replacing the faulty relay, satisfactory testing the diesel generator, counseling the individuals involved in the development of the work package, revising the guidance for high priority work orders, and clarifying and reinforcing management's expectations for independent reviews with the nuclear generation personnel.
4101999016 | Nine Mile Point 2 | 06/24/1999 | 10/04/1999 | 9910150197 | <strong>Technical Specification Action Statement Requirement Not Performed for the Division 1 and 2 Diesel Generators Due to a Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1999, Niagara Mohawk Power Corporation identified that on June 24, 1999, the Division 1 and 2 Diesel Generators were inoperable and the action statement requirement for Technical Specification 3.8.1.1.i was not performed while the plant was at 100 percent power. The cause was inadequate technical review of design drawings prior to the implementation of a 1987 procedure change to Procedure N2-OP-57, "Diesel Generator Building Ventilation System," that permitted manual operation of the emergency exhaust fans to cool the diesel generator rooms when the diesel generators are not running. Procedure N2-OP-57 was revised and a night order communicated this procedure change to all operating crews. This event will be reviewed with operations personnel responsible for procedure review, and training will revise licensed operator lesson plans to address proper emergency exhaust fan operation.
4101999017 | Nine Mile Point 2 | 09/02/1999 | 09/27/1999 | 9910060343 | <strong>Drywell Floor and Equipment Drain Tank Fill Rate Monitoring Systems Inoperable Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On September 2, 1999, while at 100 percent power, Nine Mile point Unit 2 operators identified that the drywell floor and equipment drain tank fill rate monitoring systems were inoperable due to recorder spiking and entered Technical Specification 3.4.3.1 (24-hour shutdown action statement). Due to the short duration of the action statement, Niagara Mohawk Power Corporation requested and was granted enforcement discretion that allowed additional time to return the drywell floor and equipment drain tank fill rate monitoring systems to an operable status. Based on the enforcement discretion, the action statement for Technical Specification 3.4.3.1 was not met. The cause of the drywell floor and equipment drain tank fill rate monitoring system recorder spiking was a failure of the input analog module of the programmable controller which is common to both systems. Corrective actions include: replacing and calibrating the input analog module, monitoring the new input analog module for a twelve-hour period, and performing a failure analysis on the failed input analog module. Additional corrective actions based on the results of the failure analysis will be developed, if appropriate.
4101999018 | Nine Mile Point 2 | 09/16/1999 | 10/20/1999 | ML99306008 | <strong>Valves in the Steam Condensing Mode Were Not Tested as Required by Technical Specification 4.0.5</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1999, a Nuclear Regulatory Commission inspector questioned Niagara Mohawk Power Corporation concerning the absence of four valves from the Nine Mile Point Unit 2 Inservice Testing Program. Niagara Mohawk Power Corporation determined that the four valves were considered to be passive, but the valves have an active safety function to provide an isolation boundary between the high-pressure reactor coolant system and the low-pressure portions of the residual heat removal system. The valves should have been tested in accordance with Section XI of the American Society of Mechanical Engineers Boiler and Pressure Vessel Code and applicable addenda. This is a nonconformance with Technical Specificafion Surveillance Requirement 4.0.5. The cause was inadequate reviews of the original design and licensing documentation while developing the Inservice Testing Programs. Operators declared the steam condensing mode inoperable. The Inservice Testing Program was revised to include the proper testing for the valves and the valves were tested satisfactorily. In addition, the design documents will be revised.
4101999020 | Nine Mile Point 2 | 11/02/1999 | 11/24/1999 | ML99340042 | <strong>Instrument Air Valves Not Tested As Required By Technical Specification 4.0.5.</strong><br /><i>Abstract:&nbsp;</i>On November 2, 1999, while at 100 percent power, Niagara Mohawk Power Corporation identified that two instrument air system valves (2IAS*SOV164 and 2IAS*SOV165) were not being stroke-time tested in the open direction as required by American Society of Mechanical Engineers (ASME) Boiler and Pressure Vessel Code Section XI. Therefore, Technical Specification Surveillance Requirement 4.0.5 was not met. The open stroke-time testing requirement was inappropriately deleted from the ASME Section XI Inservice Testing Program. This condition was discovered as a result of the corrective actions described in licensee Event Report 99-11 (Valves Not Correctly Tested as Required by Technical Specification 4.0.5). The cause was misapplication of design basis information during the development of the Second Ten-Year Interval Inservice Testing Program Plan. Contributing to the cause was an incorrect safety classification determination. Valves 2IA5*SOV164 and 2IA5*SOV165 were added to the Second Ten-Year Interval Inservice Testing Program and satisfactorily stroke-time tested in open direction. A deviation/event report was issued to address the inconsistency between the safety class determination and the Updated Safety Analysis Report. Additionally, the population of valves that are only tested in one direction will be reviewed to ensure adequate testing is being performed.
4101999021 | Nine Mile Point 2 | 11/22/1999 | 12/15/1999 | ML99355036 | <strong>Reactor Vessel Pressure Relays were not Correctly Tested as Required by Technical Specification Due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On November 22, 1999, while at 100 percent power, Niagara Mohawk Power Corporation identified that two reactor vessel pressure relays were not being tested as required by Technical Specifications. Technical Specification Surveillance Requirement 4.3.2.1-1.g for the two relays requires a channel check a channel functional test, and a channel calibration on a shiftly, quarterly, and refueling interval, respectively. The channel functional test of the relays was not being performed quarterly. The cause was omission of relevant information during procedure development. Contributing to the cause was inadequate procedure reviews. The relays were declared inoperable until the surveillance procedure was revised and the relays were satisfactorily tested. Additional guidance for performing technical reviews and the extent of the review for technical procedures has been better defined, since the last revision of the surveillance procedure was issued. The review of other channel functional test procedures is continuing and scheduled for completion by March 31, 2000.
4121999001 | Beaver Valley 2 | 02/27/1999 | 03/25/1999 | 9904060396 | <strong>Failure to Comply with Technical Specifications Due to Not Meeting the Acceptance Criteria for a Source Range Monitor During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 27, 1999 while Beaver Valley Power Station (BVPS) Unit 2 was in Mode 3 beginning the seventh refueling outage, it was discovered that Nuclear Source Range (SR) Instrumentation N32 was incorrectly declared operable during performance of a channel functional test. During the period between 0514 hours and 1104 hours, N32 was relied upon as the operable source range instrumentation channel to meet Technical Specification (TS) 3.3.1.1 Table 3.3-1 Item 6.b. Further review of the channel functional test (2OST-2.3) at 1104 hours on February 27, 1999 determined the acceptance criteria for SR N32 was not met. Specifically, the acceptance criteria of step C.8.d was 1150 to 1550 counts per second (CPS); however, the recorded indication for this step was 1100 CPS. Since this was not discovered until after the event, the applicable TS action statement could not be met. This was an operation or condition prohibited by TS and is reportable pursuant to 10CFR50.73(a)(2)(i). The apparent causes of the event were: a lack of attention to detail and lack of proper self-checking by the operator performing the test and the first Nuclear Shift Supervisor reviewing the test acceptance criteria; also a contributing cause was that the procedure lacked sufficient detail in that the steps containing the acceptance criteria did not provide detailed instructions for performing calculations and recording the calculation results. The channel functional test (2OST-2.3) was re-performed for N32 in its as-found condition and found to meet the acceptance criteria without adjustments.
4121999002 | Beaver Valley 2 | 03/05/1999 | 04/05/1999 | 9904080137 | <strong>Inadequate Pre-Fire Plan Procedure Guidance Resulting in Potential Damage to the Chargning / High Head Safety Injection (HHSI) Pumps</strong><br /><i>Abstract:&nbsp;</i>It has been determined that Unit 2 was outside the design basis requirements of NUREG-0800, Standard Review Plan 9.5.1 due to identified inadequacies in the unit 2 pre-fire plan procedures. In the event of a fire in fire areas PA-4 or PA-3, this could have led to damage to the Unit Charging/High Head Safety Injection (HHSI) pumps. This discovery was made on March 5, 1999, as part of an ongoing Fire Protection Safe Shutdown Self-Assessment, and on March 19, 1999, during a subsequent extent of condition review. These Unit 2 discoveries occurred during the Unit refueling outage 2R07. A similar concern was discovered on Unit 1 during an extent of condition review on March 17, 1999, while operating at approximately 100% power. Following discovery, appropriate 10 CFR 50.72 notifications were made. The apparent cause is that the architect engineer personnel who performed the involved fire protection safe shutdown analysis in 1987 failed to take into account periods of plant operation where the Volume Control Tank operating pressure could initially exceed the static head pressure of the Refueling Water Storage Tank. It is felt this error led to an incorrect assumption that adequate time would be available to complete the required actions inside the fire areas after the fire is extinguished. The Duquesne Light Company review of this vendor information in 1987 and during subsequent revisions of the safe shutdown analysis also failed to identify this issue. Procedures were revised addressing this issue. Unit 1 compensatory actions were implemented to also address this concern. Further detail of the Unit 1 discovery will be covered in a future LER. This event will be reviewed against the reporting criteria of 10 CFR 21.
4121999003 | Beaver Valley 2 | 03/11/1999 | 04/08/1999 | 9904200137 | <strong>Containment Equipment Hatch Not Completely Closed During Refueling Operations</strong><br /><i>Abstract:&nbsp;</i>At 0429 hours on March 12, 1999, while Beaver Valley Power Station (BVPS) Unit 2 was in Mode 6 performing refueling operations, the Nuclear Shift Supervisor (NSS) received a report that air was being drawn into the containment building past the equipment hatch. The MSS immediately halted core alterations and entered the action statement for Technical Specification (TS) 3.9.4. At 0514 hours on March 12, 1999, the action statement for TS 3.9.4 was exited after completing tightening of the equipment hatch bolts and determining that the air in-leakage had stopped. At 0519 hours on March 12, 1999, the MSS authorized continuation of the refueling operations. A four hour non-emergency notification was made to the NRC at 1258 hours on March 19, 1999, in accordance with 10 CFR 50.72(b)(2)(iii)(C), after information was received that an actual leakage path outside of containment would have existed if a postulated fuel handling accident would have occurred. The investigation into the event determined that the equipment hatch shifted after being bolted in place when the chain hoists were removed. The apparent cause of the event was that supporting function of the chain hoists in maintaining containment closure was not adequately understood, and therefore, barriers were not put in place to ensure that the chain hoists remained properly rigged. Corrective actions for the event include revising the procedure for temporary installation of the equipment hatch to post a sign near the chain hoists warning that they support containment closure and revising the applicable training program to increase awareness Of containment closure requirements during refueling conditions.
4121999004 | Beaver Valley 2 | 03/12/1999 | 04/12/1999 | 9904200148 | <strong>Inadequate Basis for Seismic Instrument Setpoints and Calibration Led to Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>During a review of a seismic instrument design change during field testing at Beaver Valley Power Station (BVPS) Unit No. 2, it was identified that compliance for the seismic monitoring setpoints identified within the BVPS Unit 2 Technical Specification 3.3.3.3 was not ensured using the current calibration tolerance band. The setpoints are identified in the footnotes of Table 3.3-7 as absolute values and do not specify any tolerance around the identified setpoints. Calibration procedures had previously left the accelerograph trigger and triaxial switch setpoints in the upper half of the field procedure allowed tolerance band, which is not in compliance with the setpoint value listed in Technical Specification LCO 3.3.3.3. A subsequent review also identified that the seismic accelerometer sensors have not been fully calibrated in accordance with Unit 2 Technical Specification 4.3.3.3.1. The sensors have an electronic self-test capability which was claimed to be equivalent to a tilt test by both the vendor's technical manual and a vendor representative in 1987. Recent reviews and discussion with the vendor regarding the exact nature of this electronic self-test indicate that the test can not detect all of the sensor's potential failure or drift mechanisms, which is not in compliance with the channel calibration definition in Technical Specification. BVPS Unit 2 operated with these seismic instrument setpoints not meeting the LCO and an inappropriate calibration invalidating the LCO for more than 30 days without issuing a Special Report which is not compliant with Technical Specification 3.3.3.3 Action Statement b. Both non-compliant issues were corrected and appropriate site procedures revised to prevent reoccurrence. Both non-compliant issues would not have prevented the installed seismic instrumentation from functioning if an earthquake had occurred at BVPS.
4121999005 | Beaver Valley 2 | 03/29/1999 | 04/28/1999 | 9905040256 | <strong>4KV-2A Bus Trip on Ground Overcurrent Relay 51-VA207X</strong><br /><i>Abstract:&nbsp;</i>On 3/29/99 at 1801 hours, the 4KV-2A bus tripped due to ground overcurrent protection relay 51-VA207G actuating due to fluctuating control power. The ground overcurrent protection relay actuated lockout relay 51-VA207X, which then opened the 4KV-2A-2A7 circuit breaker and prevented, as designed, the 4KV-2A bus from transferring to the off-site source. This resulted in the 4KV-2A emergency bus being deenergized. Emergency diesel generator EDG 2-1 then started, loaded on loss of voltage, and remained operating until normal power was restored. Prior to the ground overcurrent trip, unit 2 was in Mode 5 with the reactor coolant system at 97F and 280 psig. Core cooling was being provided by the 'B' train of the residual heat removal system and was unaffected. Both trains of residual heat removal remained operable. The cause of the ground overcurrent trip was an erratic DC supply voltage caused by a loose connection in non-safety related battery charger 2-5. The loose battery charger connection was repaired.
4121999006 | Beaver Valley 2 | 07/16/1999 | 08/16/1999 | 9908200195 | <strong>Loss of Beaver Valley power Station Unit No. 2 4KV Train "B" Emergency Bus</strong><br /><i>Abstract:&nbsp;</i>On July 16, 1999, at 1729 hours, the emergency 4kv bus tie breaker 2F7 from offsite power opened due to a detected ground overcurrent condition during the performance of post maintenance surveillance test on Emergency Diesel Generator (EDG) No.2-2. When breaker 2F7 opened, degraded EDG performance was observed on the 2DF 4kv Emergency Bus. In response to the degraded EDG performance, operating personnel subsequently opened the EDG output breaker 2F10 in order to prevent damage to the 'B' train safeguards equipment, effectively deenergizing the 2DF bus and leading to a total loss of 'B' train emergency AC power. At the time of the event, EDG 2-2 was inoperable as a result of degraded flow through the EDG's heat exchanger caused by macro biological fouling (The degraded heat exchanger flow event will be described further in Beaver Valley Power Station Unit 2 LER 2-99-007). Redundant train 'A' equipment was placed in service as applicable to maintain the Unit in a stable condition. The loss of train 'B' AC power, and subsequent loss of battery chargers 2-2 and 2-4 resulted in an entry into Technical Specification 3.0.3 which is reportable pursuant to 10CFR50.73(a)(2)(i). Subsequently, EDG 2-2 inadvertently automatically actuated when an operator transferred EDG control from REMOTE to LOCAL which is reportable pursuant to 10CFR50.73(a)(2)(iv). The 2DF emergency bus was recovered along with the associated battery chargers and batteries and the Technical Specification required plant shutdown was terminated at approximately 64% power. Since initial troubleshooting could not identify the cause of tie breaker 2F7 tripping and the subsequent low voltage from the EDG, Unit 2 remained in the EDG Technical Specification action statement, and shutdown was initiated at 2021 on July 17, 1999. Unit 2 reached Mode 5 at 1723 on July 18, 1999.
4121999008 | Beaver Valley 2 | 07/22/1999 | 08/19/1999 | 9908260152 | <strong>Failure to Comply with Technical Specifications Due to Not Meeting SR 4.8.1.1.2.f, Simultaneous Start Test of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On 7/23/99, during an industry operating experience review, a system engineer identified that BV-2 Surveillance Requirement (SR) 4.8.1.1.2.f was not fully verified during the last surveillance test performed on 9/1/96. BV-2 TS SR 4.8.1.1.2.f demonstrates diesel generator independence by starting both diesel generators simultaneously from a standby condition and verifying that each diesel generator achieves voltage and frequency within the specified ranges in </= to 10 seconds. This SR is required to be performed at least once per 10 years or after any modifications which could affect diesel generator interdependence. Both the 2-1 and 2-2 BV-2 EDGs had previously been declared inoperable on 7/19/99 and 7/14/99, respectively, due to unrelated concerns (See BV-2 LERs 50-412/99-006 and 50-412/99-007). Since both BV-2 EDGs were inoperable, the unit was already in Mode 5 with the action statement for TS 3.8.1.2 in effect. On 8/12/99, it was determined that SR 4.8.1.1.2.f was not properly satisfied at the time of initial startup of BV-2 in 1987. At the time of initial plant startup a pre-operational test was apparently credited as meeting the SR. While the test did demonstrate that both EDGs started simultaneously, the test did not verify that the EDGs accelerated to at least 514 rpm in </= to 10 seconds, which was the SR 4.8.1.1.2.f requirement at the time. The initial entry into Mode 5 during the initial plant startup in 1987 and all mode escalations until 7/23/99, without full compliance to SR 4.8.1.1.2.f was a condition prohibited by SR 4.0.4. Therefore, this event constitutes a condition and operation prohibited by TS and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The apparent cause of the inadequate test on 9/1/96 was human error. The cause of the inadequate verification of SR 4.8.1.1-2.f in 1987 cannot be determined due to the extended time since the event. SR 4.8.1.1.2.f was satisfied by the performance of a revised surveillance test on 7/23/99.
4121999009 | Beaver Valley 2 | 10/12/1999 | 02/22/2000 | ML00368706 | <strong>Missed Performance of Technical Specification Surveillance Requirement 4.8.1.1.1a Following Failure to Re-Establish Auto Bus Transfer Capability of 4KV Bus 2A</strong><br /><i>Abstract:&nbsp;</i>At approximately 1730 hours on 10/12/99, the input power supply to Unit 2 4KV Bus 2A was realigned from Unit Station Service Transformer (USST) 2C to the System Station Service Transformer (SSST) 2A to support startup of a Cooling Tower pump. The pump was started and the input power supply to the bus was realigned back to USST 2C, at approximately 1741 hours (same day). On 10/13/99, at approximately 0322 hours, it was discovered that the auto bus transfer capability to the off-site A.C. power source had not been reestablished during the bus realignment. The bus was then properly aligned for auto bus transfer capability. This event had rendered one of two offsite A.C. power sources inoperable and required entry into ACTION a of Technical Specification (TS) 3.8.1.1 within 1 hour, which had not been performed. The TS implications of this event were recognized at approximately 1700 hours on 10/13/99. This event is reportable per 10CFR50.73(a)(2)(i)(B). This event resulted from personnel error by the Balance of Plant Operator (PO) (utility, licensed Operator) when the auto-closure circuit logic for input power supply breaker ACB-42A of SSST 2A to the bus was not properly aligned, contrary to procedure 20M-36.4.B. Event contributors: inadequate self-checking, and TS consequences not understood by the 0000-0800 Operating Shift on 10/13/99. Licensed Operators on the Operating Shift of 0000-0800 hours on 10/13/99 were appropriately counseled, removed from licensed shift duties, and received remedial training in license review of TS and timeliness of reporting plant conditions. 20M-36.4.B was revised to emphasize TS 3.8.1.1. By 3/31/2000 licensed and non-licensed Operators will receive subsequent training to address this event.
4121999010 | Beaver Valley 2 | 10/26/1999 | 11/26/1999 | ML99337059 | <strong>Inoperable Containment Seismic Monitor</strong><br /><i>Abstract:&nbsp;</i>During a containment entry on 10/26/99 following a forced outage of Beaver Valley Power Station (BVPS) Unit No. 2, the containment seismic monitor 2ERS-RRA-1 was found with its error light flashing. A review of the instrument's recorder information determined that 55 events had been reocrded and the recorder had run out of memory on 04/02/99. This instrument provides no external indication of its status. This instrument is self contained and requires entry into containment to view the instrument status and alarms. Per BVPS Unit 2 Technical Specification 3.3.3.3, Action Statement "a" states that the inoperable seismic instrument should be restored within 30 days. Action statement "b" states "With one or more seismic moniotring instruments inoperable for more than 30 days, prepare and submit a Special Report in accordance with 10CFR50.4 within the next 10 days outlining the cause of the malfunction and the plans for restoring the instrument to operable status." The Special Report was not submitted within the time fram as required by the Technical Specification 3.3.3.3, because the condition was not discovered until after the time frame had elapsed. The cause of this condition involves a probelm with equipment sensitivity. Five other similar seismic instruments at BVPS Unit 2 were not influenced by the conditions associated wit the affected seismic accelerograph and remained functional. These instruments provide monitoring and reocrding of the magnitude of any seismic activity which is used to subsequently analyze the effects of a seismic event. The seismic activity which is used to subsequently analyze the effects of a seismic event. The seismic instruments that remained operable were sufficient to perform this function had a seismic event occurred. In addition, no seixmic events exceeding the 0.01 setpoint were experienced at BVPS Unit 2 during this period in 1999.
4131999001 | Catawba 1, Catawba 2 | 02/15/1999 | 03/17/1999 | 9903260084 | <strong>Inoperable Refueling Water Storage Tank Level Channels results in Operation Outside of the Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 15, 1999, at approximately 0850, during the implementation of a Unit 1 modification of the Refueling Water Storage Tank (FWST) instrumentation, the Unit 1 FWST Channel 3 level transmitter was not placed in the bypass position as required by Technical Specifications. Instead, the channel was in a tripped condition. The oncoming Operations crew questioned the Control Room annunciator and status light indication and the error was noted. The channel was put in bypass at 2147 (approximately 13 hours later). The unit remained at 100 percent power during the event. A review of previous work orders related to this modification identified 2 additional instances where a FWST channel was not placed in bypass as required by Technical Specifications. Inadequate Program design was determined to be the root cause for each incident, leading to vagueness in procedures and the design process; with a contributing cause of inadequate communications between Operations, Engineering and Maintenance groups. Corrective actions include procedure reviews and communication improvements between groups.
4131999002 | Catawba 1, Catawba 2 | 02/25/1999 | 03/29/1999 | 9904080101 | <strong>Three Residual Heat Removal System Valves did not meet their Engineered Safety Features Response Time Requirement due to a Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 25, 1999, at 1450 hours with Unit 1 and Unit 2 operating in Mode 1, Power Operation, at 100% power it was discovered that three valves of the Residual Heat Removal System did not meet the required Engineered Safety Features (ESF) response time. These problems were discovered while investigating discrepancies found by the Technical Specification Surveillance Review Team. This team was reviewing surveillance requirements of the Improved Technical Specifications and ensuring that procedures or work orders were in place to implement each surveillance requirement. The valves were declared inoperable and actions were taken to secure the valves in their safety positions. The problem was caused by a procedural deficiency which had existed for the life of the plant. Corrective actions include an evaluation to determine if ill be necessary to ensure that the 12 second response time is met. If the response time is revised, applicable station documents will be revised to specify the correct response time.
4131999003 | Catawba 1 | 03/05/1999 | 04/05/1999 | 9904140281 | <strong>Violation of Technical Specifications due to Inoperable Ice Condenser Lower Inlet Doors Caused by Ice/Frost Buildup Restricting Door Movement</strong><br /><i>Abstract:&nbsp;</i>On March 5, 1999 with Unit 1 in Mode 1 at 15% power, an inspection of the support beam coolers and associated glycol lines in the ice condenser revealed excessive frost/ice buildup. Each bay of the ice condenser has one beam cooler located inside the ice condenser above the inlet doors. The frost/ice was built up sufficiently thick in 6 of the 24 bays to create an obstruction that interfered with the opening of 8 inlet doors. This is a violation of Technical Specification (TS) 3.6.13 since this condition existed for a time period greater than the allowed Completion Time for restoring the doors to operable status while the unit was in operation. The cause was an inadequate design that allowed frost buildup to impede inlet door opening. The frost/ice was cleared from the coolers and associated glycol lines to restore the ice condenser to operable status. Insulation will be installed on the beam coolers and associated glycol tubing to prevent future frost/ice buildup problems.
4131999004 | Catawba 1, Catawba 2 | 03/10/1999 | 04/12/1999 | 9904200371 | <strong>Inappropriate Technical Specification Requirements for Control Room Area Ventilation System and Auxiliary Building Filtered Ventilation Exhaust System Actuation Instrumentation Resulted in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1999, at 1805 hours, with both units operating in Mode 1 at 100% power, Catawba declared both trains of the Control Room Area Ventilation System (CRAVS) Actuation Instrumentation and both trains of the Auxiliary Building Filtered Ventilation Exhaust System (ABFVES) Actuation Instrumentation inoperable for both units. This declaration was made in response to a discovery that Technical Specification (TS) Surveillance Requirements for this instrumentation were inappropriate for the Catawba plant design and could not be complied with. The root cause of this event was determined to be incorrect TS requirements for the CRAVS and ABFVES Actuation Instrumentation. Catawba subsequently requested enforcement discretion from the NRC concerning the TS requirements for this instrumentation and the NRC granted this request. Following receipt of the enforcement discretion, Catawba submitted a license amendment request to delete the TS requirements for this instrumentation.
4131999005 | Catawba 1, Catawba 2 | 03/17/1999 | 04/26/1999 | 9905030221 | <strong>Surveillance Requirements for Turbine Trip-Reactor Trip Functions Incorrectly Performed Due to Lack of Understanding of Test Requirements</strong><br /><i>Abstract:&nbsp;</i>During a structured review to assure that the Improved Technical Specification Surveillance Requirements (SR) would be properly implemented, the Review Team formalized the concern that administrative controls may not be adequate to ensure SR 3.3.1.15 is properly performed. SR 3.3.1.15 requires performance of a Trip Actuating Device Operational Test (TADOT) prior to reactor startup if not performed in the previous 31 days for the Reactor Trip-Turbine Trip Functions on Stop Valve Electrohydraulic Pressure Low and Turbine Stop Valve Closure. Credit had been taken for the monthly exercise test of the Turbine Stop Valves to satisfy this Surveillance. On March 17, 1999, it was determined that this test did not fulfill the TADOT requirements because it did not verify both trains of the Solid State Protection System received the proper signals. The Trip Functions for Unit 2 were operable because of the channel calibration (which satisfies the TADOT) performed during the last Refueling Outage. However, the Trip Functions for Unit 1 were inoperable because the TADOT had not been performed prior to the most recent reactor startup. The required TADOT was promptly performed, restoring the functions to operable status on March 17. The inadequate administrative controls to ensure improper implementation of the SR have been attributed to insufficient understanding of the TADOT requirements for this application. A formal review of SR implementation at Catawba has been conducted, and discrepancies identified by this review are being resolved by the Corrective Action Program.
4131999006 | Catawba 1 | 04/08/1999 | 11/03/1999 | ML99314043 | <strong>Control Room Ventilation System inoperable due to spurious closure of intakes resulting in an entry into TS 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On April 8,1999, at approximately 1506 hours, a spurious high chlorine alarm closed the Unit 2 Control Room Area Ventilation System (CRAVS) intake. A Maintenance technician had been working on the Unit 1 chlorine detector and mistakenly thought this was the detector in alarm. At approximately 1514, the technician reset the Unit 1 alarm1 shutting the Unit 1 intake, placing both units in Technical Specification (TS) 3.0.3. The Unit 1 intake was re- opened and TS 3.0.3 was exited at 1515 hours on April 8, 1999. On April 9, 1999 at approximately 0428 hours, a spurious high chlorine alarm closed the Unit 1 CRAVS intake. The Unit 2 intake was still closed for investigation of the spurious closure of April 8, 1999. Both units entered TS 3.0.3. The Unit 2 intake was sampled for chlorine and the detector was calibrated. The Unit 2 intake was opened and TS 3.0.3 was exited at 0526 hours on April 9, 1999. The root cause for the first event was failure to stop when unusual system conditions were encountered and failure to follow expectations that work should be performed by the guidance of a work order or procedure. This event has been covered with Maintenance personnel. The root cause of the spurious failures (second event) of the chlorine detectors is still being investigated. The apparent cause may be insufficient cleaning of the electrodes. A long-term solution to the detector failures is being evaluated by Engineering. Both units were at 100% power during the events.
4131999007 | Catawba 1 | 04/26/1999 | 05/26/1999 | 9906030200 | <strong>Operation Prohibited by Technical Specification 3.4.7 caused by an Inoperable Train of Residual Heat Removal due to Inadequate Work Sequencing</strong><br /><i>Abstract:&nbsp;</i>On April 26, 1999 at 10:00 hours with Unit 1 operating in Mode 5, Cold Shutdown, Operators discovered that the Residual Heat Removal System was not properly aligned for plant conditions. Further analysis showed that Technical Specification 3.4.7 had been violated for approximately 28 hours. A tagout had been placed on a valve which was interlocked with the two Residual Heat Removal System Pump B Suction Isolation Valves. This removed the ability to operate Suction Isolation Valve 1ND36B from the Control Room, making B Train of the Residual Heat Removal System inoperable. Later Steam Generator levels were reduced below the level required by Technical Specification 3.4.7 and immediate action was not taken to restore the second heat sink as required by the Technical Specification. A root cause investigation determined that the root cause of the event was inadequate work scheduling/sequencing. Contributing causes were procedural deficiencies and weaknesses in tagout preparation, review and approval. Corrective actions include changing the outage sequencing ties for placing the tagout that was involved in the event, evaluating other valve interlocks for similar problems, and training for those involved in outage scheduling. Improvements will be made to Operations procedures and the tagouts which involve valve interlocks. This event was not safety significant since adequate Steam Generator inventory was available in two Steam Generators to meet safety analysis assumptions.
4131999008 | Catawba 1 | 06/10/1999 | 12/09/1999 | ML99361008 | <strong>Operation Prohibited by Technical Specification 3.5.2 Due to an Inoperable Centrifugal Charging Pump and Operation Prohibited by Technical Specification 3.7.12 Due to Inadequate Control of the Auxiliary Building Filtered Ventilation Exhaust System Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>On June 8, 1999 at 2350 hours Centrifugal Charging Pump lB (CCP lB) failed. On June 11, 1999 at 2350 hours with Unit 1 operating in Mode 1, Power Operation at 100% power, Technical Specification 3.5.2 (ECCS - Operating) was violated when repairs to CCP lB were not completed within the 72 hour allowable outage time. It had been foreseen that the pump repair could not be completed within 72 hours and a Notice of Enforcement Discretion (NOED) had been obtained to extend the allowable outage time to seven days. On June 10, 1999 at 0000 hours with Unit 1 operating in Mode 1, the doors to the pump room were propped open to allow installation of a temporary ventilation duct. This resulted in operation prohibited by Technical Specification 3.7.12 (Auxiliary Building Filtered Ventilation Exhaust) since the open doors were a breach of the ventilation system pressure boundary. Corrective actions for the pump problem included replacing the pump rotating element. The root cause of the pump failure will be addressed as a long term corrective action. The root cause of the ventilation system breach was that workers were not aware of the significance of opening the pump room door for an extended period due to unclear management expectations. Corrective actions include labeling plant doors to warn workers of the significance of opening the door and communicating the method of identification to plant personnel.
4131999009 | Catawba 1 | 05/18/1999 | 09/15/1999 | 9909210045 | <strong>Inoperability of Containment Valve Injection Water System Valve in Excess of Technical Specification Limits Due to Inadequate Retest Following a Surveillance Test Failure</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1997, Containment Valve Injection Water System (CVIWS) valve 1NW-237B failed its Engineered Safety Feature (ESF) response time testing. During troubleshooting the problem was not identified or corrected and subsequent testing did not reveal this. On May 18, 1999, with Catawba Unit 1 in Mode 5, Cold Shutdown, Valve 1NW-237B failed its ESF response time testing. On June 1, 1999, it was concluded that the valve had been inoperable since the test failure in 1997. On June 21, 1999, it was determined that this occurrence was reportable. Inoperability of this valve causes one train of CVIWS to be inoperable. The Technical Specifications require two trains of CVIWS to be operable. Valve 1NW-237B is required to open to supply sealing water between the discs of containment isolation valve 1NI-178B, Residual Heat Removal Pump B to Reactor Coolant System Loop A and B cold legs isolation valve. The malfunctioning interlock was repaired by adjusting a switch striker screw in the control circuit for 1NI-178B. The valve was retested and restored to service on May 18, 1999. This event occurred due to inadequate testing following the December 1997 surveillance test failure. The Retest Manual will be revised to provide additional information regarding testing of these valves. Leakage values assumed in the offsite dose calculation would not have been exceeded.
4131999010 | Catawba 1, Catawba 2 | 05/04/1999 | 07/22/1999 | 9907270146 | <strong>Both Catawba Units Operated Outside Their Design Basis and Unit 2 Experienced a Forced Shutdown as a Result of Flow Restriction Caused by Corrosion of the Auxiliary Feedwater System Assured Suction Source Piping Due to Inadequate Testing</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1999, a small leak was discovered in a section of Train B Nuclear Service Water System (NSW) piping on Unit 1 during operator rounds. On May 4, after follow-up inspection and testing, all three Unit 2 Auxiliary Feedwater System (AFW) pumps were declared inoperable due to flow restriction caused by corrosion discovered in the assured safety related (backup) supply piping from the NSW System. The corrosion was also determined to exist on Catawba Unit 1, which had since entered its End-of-Cycle 11 refueling outage. Engineering completed an evaluation that showed sufficient flow capacity existed to support the two motor driven AFW pumps. The NSW supply to the turbine driven AFW pump was isolated. Unit 2 was then shut down per Technical Specification (TS) 3.7.5 to Mode 4. Throughout this event, all normal sources of AFW supply remained fully operable. This event was caused by undetected corrosion buildup in the NSW to AFW supply piping due to inadequate testing of this piping. Subsequent corrective actions included cleaning the NSW to AFW piping, installing flow testing capability, flow testing the piping, and assessing the generic impacts of the event on other NSW supplied systems.
4131999011 | Catawba 1, Catawba 2 | 07/23/1999 | 08/16/1999 | 9908240289 | <strong>Missed Surveillance on Both Trains of Control Room Area Ventilation System Resulted in a Technical Specification Violation Due to a Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On July 23, 1999, at 1300 hours, a missed surveillance was declared concerning both trains of the Control Room Area Ventilation System (CRAVS) as a result of a relay in the CRAVS actuation logic not being adequately tested. The function of the affected relay is to start the non-running pressurizing filter train and fan in the event of an accident condition. Catawba subsequently utilized the 24-hour allowance of Technical Specification (TS) Surveillance Requirement (SR) 3.0.3 in order to implement a procedure modification and conduct the test of the affected relay for both trains. Following successful completion of the required testing, the SR 3.0.3 condition was exited at 1723 hours. The root cause of this event was determined to be a defective procedure, in that procedural guidance did not exist to ensure that the relay was adequately tested. Corrective actions included a procedure revision to ensure adequate testing of the relay and completing the test for both CRAVS trains.
4131999012 | Catawba 1, Catawba 2 | 07/27/1999 | 08/26/1999 | 9908310175 | <strong>Adverse System Interaction between the Annulus Ventilation System and the Auxiliary Building Ventilation System due to an Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1999 at 0600 with Unit 1 operating in Mode 5, Cold Shutdown and Unit 2 operating in Mode 4, Hot Shutdown; an adverse system interaction was discovered in which the Auxiliary Building Ventilation System could pressurize the Electrical Penetration Rooms in the Auxiliary Building. It was determined that this could affect the instrumentation that controls the operation of the Annulus Ventilation System since the reference legs for these instruments are located in the area that could become pressurized. Temporary measures were taken to open doors to the Electrical Penetration Rooms to prevent the rooms from becoming pressurized. On July 15, 1999 during Engineering analysis of this problem it was determined that an accident scenario existed in which, if the Electrical Penetration Rooms were to pressurize; the Annulus Ventilation System would not achieve the -0.5 inches water gauge negative pressure required by Technical Specification Surveillance Requirement 3.6.16.2. The cause of this problem was that this potential system interaction was not identified during the development of the modifications which installed cooling to the Electrical Penetration Rooms. These modifications were completed approximately ten years ago. Corrective Action was to relocate the instrument reference legs to an area which is always at atmospheric pressure. A planned corrective action is to review other plant systems for similar problems.
4131999013 | Catawba 1, Catawba 2 | 08/03/1999 | 09/02/1999 | 9909030211 | <strong>Residual Heat Removal exchanger bypass valves not verified per Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>In June 1999, during a NRC inspection, a question was raised whether the position of the Residual Heat Removal (ND) Heat Exchanger (HX) Bypass valves 1(2)ND27 and 1(2)ND61 was required to be verified per Technical Specification (TS) 3.5.2.2. A review of the TS Bases indicated that the valve could be verified in either the opened or closed position. An evaluation of the TS requirement concluded in August 1999 that the ND HX Bypass valves did meet the criteria for verification in the TS. The cause of this situation has been determined to be historical. The TS surveillance to verify the position of the ND HX Bypass valves has never been performed. The valves have been added to the surveillance procedures to verify the valve position on a 31-day frequency. Both units were maintained in Mode 1 at approximately 100 percent power throughout this evaluation.
4131999014 | Catawba 1, Catawba 2 | 08/16/1999 | 09/01/1999 | 9909080060 | <strong>Missed Surveillances and Operation Prohibited by Technical Specifications Occurred as a Result of Defective Procedures or Programs and Inappropriate Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>In 1996, five events occurred which involved missed Technical Specification (TS) surveillances and therefore constituted operation prohibited by the TS. The circumstances surrounding these events were initially discovered during a review performed in response to Generic Letter 96-01, "Testing of Safety-Related Logic Circuits." At the time of their discovery, they were documented in the Catawba Problem Investigation Process (PIP); however, the reportability implications of these events were not recognized. The reportability implications were ascertained during a review that Catawba recently performed for all Generic Letter 96-01 related PIPs. This LER is therefore being written from a historical perspective to report these events. These events were caused by either failing to specify testing requirements in applicable procedures or programs, or by failing to recognize TS requirements that were inappropriate for the given plant design. In all cases, the affected procedures/programs were subsequently revised and the testing requirements were performed, or the inappropriate TS requirements were ultimately deleted. Catawba will evaluate additional changes to the TS and submit these as necessary to the NRC for review and approval.
4131999015 | Catawba 1 | 06/16/1999 | 02/21/2000 | ML00368702 | <strong>Inoperability of Auxiliary Building Ventilation System in Excess of Technical Specification Limits Due to Improperly Positioned Vortex Damper</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1999, during surveillance testing, it was discovered that the Auxiliary Building Filtered Ventilation Exhaust System (ABFVES) Train 1A was not maintaining the Emergency Core Cooling System pump rooms at a negative pressure relative to adjacent areas as required by Technical Specifications (TS). The cause of the event was that a vortex damper had been incorrectly reassembled following maintenance on June 16, 1999. On August 26, 1999, it was concluded that ABFVES Train 1A had been inoperable since that time. In addition, a review determined that ABFVES train 1B was inoperable on 4 separate occasions during this time frame. These events exceed the TS Required Action Time. This event was reportable per 10 CFR 50.73(a)(2)(i). The damper was repositioned correctly, the system was retested successfully, and the system was restored to operable status on August 5, 1999. The root cause of this event was inadequate procedural guidance in the procedure used to lubricate the vortex damper. A contributing cause was a failure to require a. post maintenance retest. A new procedure was developed and approved to provide detailed instructions for vortex damper positioning. The Post Maintenance Retest Manual has been revised to require a retest of the system after maintenance on the vortex damper. An evaluation has determined that this event did not pose a threat to the health and safety of the public.
4131999016 | Catawba 1 | 11/19/1999 | 08/30/2000 | ML00374891 | <strong>Operation Prohibited by Technical Specification 3.8.1 and 3.7.8 Due to Inoperable Diesel Generator 1B for Greater than 72 Hours</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1999 at 0415, with Unit 1 at 100% power, diesel generator (DG) 1B was declared inoperable to perform maintenance activities. This placed Unit 1 in a 72-hour action statement for DG 1B and Nuclear Service Water System (NSWS) pump 1B. During the post maintenance test of the DG 1B , the DG breaker tripped on overcurrent. Trouble shooting and repair activities were unsuccessful in restoring operability to DG 1B within 72 hours. A Notice of Enforcement Discretion (NOED) was requested from the NRC so that the completion times of the Required Actions for TS LCO 3.8.1 and 3.7.8 could be extended from 72 hours by an additional 48 hours. This was requested to allow necessary repairs and testing activities to be completed. The NRC granted the NOED on November 19, 1999 at 0200. The DG 1B electronic governor (EGA) was replaced, tested, and DG 1B was declared operable at 2309 on November 20, 1999. The replaced EGA was sent back to the manufacturer for analysis. The manufacture found no problems with the replaced EGA. They concluded that the EGA installed on DG 1B was not properly tuned to compensate for the changes that were made to DG 1B during maintenance. Appropriate procedure revisions have been made to correct the root cause. The event is being reported as any operation or condition prohibited by TS, 10 CFR 50.73(a)(2)(i)(B), and TS LCO not met, 10 CFR 50.36(c)(2).
4131999017 | Catawba 1 | 10/02/1999 | 11/01/1999 | ML99314026 | <strong>Operation Prohibited by Technical Specification 3.8.4 and 3.8.1 concerning DC Power Supply to Diesel Generator 1A due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 7, 1999 at 1450 hours with Catawba Unit 1 operating in Mode 1, Power Operation, at 100% power it was determined that Technical Specification Surveillance Requirement (SR) 3.8.4.2 concerning DC Power Sources had not been met when the quarterly battery surveillance was performed on October 2, 1999. Two cells of diesel battery 1DGBA were found below the required per cell voltage and the actions required by Technical Specifications 3.8.4 and 3.8.1 were not taken. This problem was discovered when Engineering was reviewing results of the quarterly battery surveillance. The root cause of this event was an inadequate procedure. The procedure directed technicians to measure and record cell voltages but did not clearly list the Technical Specification acceptance criteria or give clear instructions on actions to take when low cell voltage readings were found. Corrective Actions included placing the battery on an equalize charge. One of the affected cells recovered after the equalize charge. The other cell was removed from the battery. Improvements will be made to procedure IP/0/A/3710/017 and similar procedures to clearly state the acceptance criteria.
4141999001 | Catawba 2, Catawba 1 | 01/15/1999 | 07/08/1999 | 9907210073 | <strong>Unanalyzed Condition Associated with a Relay Failure in the Auxiliary Feedwater System due to an Inadequate Single Failure Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1999 at 0630 hours, with Unit 2 operating in Mode 1, Power Operation, at 100% power, a relay failure occurred which resulted in degradation of the Auxiliary Feedwater System. The Turbine Driven Auxiliary Feedwater Pump Train A controls were degraded and the 2A Train of Motor Driven Auxiliary Feedwater was inoperable. A similar event occurred on January 29, 1999 at 1500 hours with Unit 2 operating in Mode 1, Power Operation, at 100% power. In the second event the same relay failed. The cause of both events was determined to be equipment failure (shorted relay coil). After the first event the relay coil was replaced and after the second event the entire relay was replaced. A failure analysis was performed to determine the root cause of the failures. The relay failures were determined to be an isolated event. Additional testing and analysis was determined not to be necessary. Although there was no operation prohibited by technical specifications, this event is being reported as a voluntary LER due to its similarity to an unanalyzed condition which was reported in LER 413/97-009. The unanalyzed condition is the inability to terminate Auxiliary Feedwater flow to a ruptured Steam Generator from the Control Room. A compensatory measure which was developed and implemented for LER 413/97-009 is adequate for this event also. The compensatory measure is to limit specific activity in the reactor coolant system to ensure that offsite doses are bounded by previous analyses. The root cause determined for LER 413/97-009 was a less than adequate single failure analysis.
4141999003 | Catawba 2 | 06/12/1999 | 08/31/1999 | 9909080066 | <strong>Unplanned Actuation of Engineered Safety Features Actuation System Due to 'A' Steam Generator High Level Caused by Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On June 12, 1999, with the Unit in Mode 4, Hot Shutdown, while attempting to open the 2A Steam Generator Main Steam Isolation Valve (MSIV), Steam Generator level increased to the high-high level setpoint, causing Turbine Trip, Feedwater Isolation and Main Feedwater Pump Trip Signals. Equipment affected by these signals was already in its safeguards position. As expected, no equipment repositioned as a result of these signals. Additional actions were taken to equalize pressure across the MSIV's and the MSIV's were subsequently opened without further Engineered Safety Features (ESF) Actuations. The cause of this event was determined to be that the controlling procedure was inadequate to ensure that a high-high steam generator level indication and the resulting ESF actuation would not occur for the given plant conditions. At the time of this event, main condenser vacuum had been established and the steam generators were at low pressure. The procedure specified a minimum differential pressure across the Main Steam Isolation Valves that was difficult to achieve and difficult to measure. Corrective actions include an engineering review to determine an optimum method for opening the MSIV's under these conditions.
4141999004 | Catawba 2 | 06/16/1999 | 09/01/1999 | 9910050161 | <strong>Containment Isolation Valve 2NM-221A Returned to Service without Testing due to Procedure Deficiency Resulting in Violation of Technical Specification 3.6.3</strong><br /><i>Abstract:&nbsp;</i>Valves 2NM-221A and 2NM-220B are the two containment isolation valves in the 'D' Steam Generator sample line containment penetration. On November 3, 1998, with Unit 2 at 100% power, 2NM-220B was declared inoperable due to intermediate position indication. Per Technical Specification (TS) 3.6.3, Action A.1, valve 2NM-220B was isolated by closing and de-activating valve 2NM-221A, thereby restoring containment integrity. On June 8, 1999, Maintenance stroked and measured the response time of valve 2NM-220B and found no problems. Both 2NM-220B and 2NM-221A were returned to service on June 8, 1999. On June 16, 1999 it was discovered that 2NM-221A had been placed in service without required testing being completed. Technical Specifications require that all automatic power-operated containment isolation valves be stroke time tested every 92 days. Valve 2NM-221A had not been tested since October 7, 1998 although the work management system indicated that the testing had been performed on January 21 and March 19, 1999. Valve 2NM-221A was tested successfully and returned to operable status. The cause of the event was a programmatic deficiency resulting from a change in responsibility for updating test completion information in the work control system for selected relay and valve stroke time testing. The test procedures have been revised to include the necessary information.
4141999005 | Catawba 2 | 07/27/1999 | 09/20/1999 | 9909270160 | <strong>Missed Emergency Diesel Generator Technical Specifications Surveillance Concerning Verification of Availability of Offsite Power Sources Resulted from Defective Procedure</strong><br /><i>Abstract:&nbsp;</i>On July 27, 1999 at 0400, emergency diesel generator (EDG) 1B was declared inoperable and removed from service in support of maintenance activities. Because of the shared nature of the Nuclear Service Water System (NSWS) and certain essential motor control centers, this rendered Train B of the NSWS inoperable for both units. It also rendered EDG 2B inoperable as a result of its NSWS supply being inoperable. Technical Specification (TS) Surveillance Requirement (SR) 3.8.1.1, which requires a verification of correct breaker alignment and indicated power availability for each associated offsite circuit, was not performed within one hour of EDG 2B becoming inoperable as required. This event has been attributed to a defective procedure. The procedure for removing an EDG from service lacked sufficient detail to ensure that the appropriate surveillance was performed. When the surveillance was subsequently performed, all required equipment was operable. Corrective action included revising the affected procedure. Planned corrective actions include a review of all procedures that remove an EDG from service for potential revision.
4161999001 | Grand Gulf 1 | 01/12/1999 | 02/09/1999 | 9902190005 | <strong>Plant Shutdown Due to Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1999, during routine surveillances on our division I emergency diesel generator, an electrician noted a small puddle of red material on the floor of the D/G output breaker cubicle. The cubicle is located in the main division 1 4160 v bus. Investigation determined that the material resulted from the reversion (liquefaction) of the epoxy encapsulant of a current transformer (CT) for the D/G feeder breaker. Asea Brown Boveri (ABB) provided information on the potential reversion of the CT insulation in a 10CFR21 notification to the NRC dated April 17, 1989. The notification basically recommends the CTs be inspected on an appropriate periodic interval. The degradation occurs on an apparent random basis given the relatively slow progression of the liquefaction, and the recommended inspection provides adequate warning to allow routine parts replacement. The plant shut down and inspected all safety-related equipment containing CTs subject to the notice and selected non-safety related equipment. Where necessary, CTs were replaced. In some cases CTs were electively replaced with CTs from a modified product line incorporating a polyurethane compound not susceptible to reversion. Future actions will assure that susceptible CTs are inspected appropriately or replaced with CTs not susceptible to liquefaction. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(A).
4161999002 | Grand Gulf 1 | 02/07/1999 | 03/01/1999 | 9903100221 | <strong>ESF Actuation Due to Inattention to Detail</strong><br /><i>Abstract:&nbsp;</i>On February 07, 1999, GGNS (Grand Gulf Nuclear Station) Instrumentation and Calibration (I&C) technicians were performing a calibration surveillance for the Reactor Core Isolation Cooling (RCIC) Steam Pipe Tunnel High Temperature Switch. During restoration from the surveillance an Engineered Safety Feature (ESF) [JE] actuation occurred resulting in closure of the RCIC Inboard Steam Isolation Valve. The ESF actuation requires a 30 day written report per 10CFR 50.73 (a)(2)(iv). Performance of this surveillance required the use of a digital volt meter (DVM) in the ohms mode. The technicians did not recognize the possible shorting/shunting of the meter in ohms mode. During restoration from the surveillance, the meter shorted causing an ESF [JE] actuation which resulted in closure of the RCIC Inboard Steam Isolation Valve (1E51 -F063). Closure of the 1E51-F063, RCIC Inboard Steam Isolation Valve caused the RCIC system to become inoperable. Following closure of the RCIC isolation valve, the ESF actuation [JE] signal was reset and the RCIC system returned to operable status. The total time that the RCIC system was unavailable was approximately two hours. GGNS Technical Specifications allow a 14 days Limiting Condition for Operation with the RCIC system inoperable provided the High Pressure Core Spray (HPCS) system is operable. The HPCS system was operable during the time of the RCIC isolation. Therefore the health and safety of the general public were not compromised by this event.
4161999003 | Grand Gulf 1 | 02/21/1999 | 03/19/1999 | 9903300336 | <strong>Manual Reactor Scram Due to Decreasing Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On February 21, 1999, a reactor SCRAM was manually inserted as part of a preplanned sequence based on specific plant conditions related to the condenser system. Failure of a condenser expansion joint resulted in rapid condenser vacuum decrease that led to a rapid plant shutdown. Continued decreasing main condenser vacuum following the reactor SCRAM led operators to close the main steamline isolation valves. Reactor pressure and level were controlled using several safety relief valves and the reactor core isolation cooling system. All control rods inserted fully and reactor level did not decrease below the automatic Emergency Core Cooling System actuation set point. The Reactor Core Isolation Cooling system was manually initiated for vessel level and pressure control and several SRVs were manually cycled for pressure control. The health and safety of the general public were not compromised by this event. Because the reactor was manually SCRAMMED in anticipation of a possible automatic trip due to loss of vacuum, this event is being reported pursuant to 10CFR50.73(a)(2)(iv).
4161999004 | Grand Gulf 1 | 09/09/1999 | 12/10/1999 | ML99362014 | <strong>HPCS System Declared Inoperable Because of a Generator Shaft Bearing Failure</strong><br /><i>Abstract:&nbsp;</i>On September 9, 1999, Emergency Diesel Generator (EDG) 13 was run for a 24-hour load surveillance test. Soon after load was raised to 110 percent as required, a noise was heard and a load dip was observed. The "Generator RTD TEMP HI" alarm and all 6 stator temperature indicators came in. All but one of the alarms cleared. Operators observed sparks coming from the east generator end. The EDG was tripped using the emergency stop pushbutton. Investigation revealed that the east end generator bearing failed. The cause of the generator bearing failure was inadequate lubrication as a result of lowering oil level. Concerns with bearing oil "frothing" drove the decision to lower the oil level. Immediate corrective actions were initiated to repair the generator and resolve any safety concerns. A Significant Event Response Team was formed to determine the root cause and establish corrective actions to prevent reoccurrence. The health and safety of the general public were not compromised as a result of this event. This event is being reported pursuant to 10CFR50.73 (a)(2)(v) and 10CFR50.73(a)(2)(i)(B).
4161999005 | Grand Gulf 1 | 10/19/1999 | 11/18/1999 | ML99330024 | <strong>Containment Isolation Valve P41F169B Failed Repeatedly</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1999, the cooling water inlet isolation stop check Valve for Drywell Purge Compressor B, a division 2 containment isolation valve, failed its increased frequency monthly surveillance test. This was one month after the valve had been reoriented to a nearly vertical plane and replaced with a new one from stock. Troubleshooting was performed, then the new valve was disassembled in place. Small machining high spots were found and hand sanded. Retest of this work failed. The valve had performed acceptably for years, but began to fail its surveillance recently and with increasing frequency. The cause appears to be binding either between the stem and plug, the plug and barrel, or a combination of all three. The plant has tried machining and polishing to correct irregularities, but that has not precluded the most recent failures. Although root cause analysis is in progress, the decision has been made to replace the valve with one of a different design not as sensitive to disc orientation, with a helper spring to close, and able to perform satisfactorily in raw service water. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(i)(A).
4161999006 | Grand Gulf 1 | 11/02/1999 | 03/03/2000 | ML00369148 | <strong>Main Steam Lines Exceeded Leakage Limits</strong><br /><i>Abstract:&nbsp;</i>On November 2 and 13, 1999, with the reactor shutdown, Main Steam Line (MSL) Local Leak Rate Testing data indicated that the as-found leakage through the inboard and outboard Main Steam Isolation Valves (MSIVs) in the A and C MSLs exceeded the acceptance limit. Technical Specification (TS) 3.6.1.3 specifies a total leakage limit of 100 standard cubic feet per hour (scfh) for all four MSL penetrations. The acceptance leakage limit for individual MSIVs is 25 scfh (minimum pathway leakage). The as-found leakage rate through the inboard MSIV on the A MSL was approximately 442 scfh and unquantifiable through the outboard MSIV and both C MSL MSIVs due to excessive leakage beyond the measuring capability of the test equipment. Thus, leakage through the A and C MSLs exceeded the total allowable leakage limit specified in TS. Since the MS1Vs are designed to automatically close following a level 1 reactor water level signal indicative of a LOCA, total leakage would be expected to have been limited to the leakage rate of the valve in each affected MSL penetration with the least amount of leakage (minimum pathway leakage). Additionally, the Main Steam Shutoff Valves (MSSVs) were available to limit radiological releases to the environment. The MSSVs successfully passed leak rate testing. All MSIVs have been reworked and retested satisfactorily. Although the design basis MSIV leakage limits would have been exceeded given a postulated LOCA, there were no actual safety consequences or compromises to public health and safety as a result of this event.
4161999007 | Grand Gulf 1 | 11/18/1999 | 12/16/1999 | ML99361019 | <strong>ESF Acutation - Invalid Level 1 Signal</strong><br /><i>Abstract:&nbsp;</i>On November 18, 1999, an invalid level 1 (-150.3 inches) signal was generated. Because the plant was in a refueling outage, the majority of Division I equipment was removed from service. The Division 1 Drywell Purge Compressor did actuate from the invalid signal. Additionally, the Division 1 Load Shedding and Sequencing actuated. The RHR A shutdown cooling pump and Standby Service Water A pump were shed and reloaded. The signal also caused the opening of the RHR A injection valve and started the Division 1 Diesel Generator, which is not considered an ESF system at GGNS. The RHR pump re-started after 5 seconds. The sequence of events for the Division 1 ECCS initiation has been reviewed, interviews were conducted and plots of key parameters were reviewed. No definite single cause could be found that would explain the initiation with certainty. Possible root causes include a radio frequency of unknown origin or the purge system isolation valve may have been leaking or partially open. This event is being reported pursuant to 10CFR50.73(a)(2)(iv).
4231999001 | Millstone 3 | 01/16/1999 | 02/12/1999 | 9902260246 | <strong>Entry Into Technical Specification 3.0.3 As The result Of A High Energy Line Break Boundary Door Latch Failure.</strong><br /><i>Abstract:&nbsp;</i>On January 16, 1999 and on January 26, 1999, with the plant operating in Mode 1 at 100 percent (%) power, the East Main Control Room Door (#352) became inoperable as the result of the door latch sticking in the withdrawn position. This door is credited as a portion of the High Energy Line Break (HELB) boundary between the Main Control Room (MCR) and a potential harsh environment. The MCR equipment is not qualified for a harsh environment. As a result, Technical Specification 3.0.3 was entered. This requires that, when a Limiting Condition for operation cannot be met, action must be initiated within one (1) hour to place the unit in a mode in which the specification does not apply. Therefore, this condition is reportable pursuant to 10CFR50.73(a)(2)(i)(b) as an operation or condition prohibited by the plant's Technical Specifications. The cause of these events was attributed to mechanical failure of the East Main Control Room Door latch resulting from bending of the throw latch bolt which caused the latch mechanism to be retained within the door. The HELB of concern relative to Door # 352 is a Steam Line Break (SLB) in the Turbine Building which is a low probability event. When combined with the short period of inoperability, there is a relatively low safety significance and consequence for this event. The door latch was repaired on January 16, 1999 in one (1) hr and fifteen (15) minutes and on January 26, 1999 in less than one (1) hour, following the failure. Station personnel have been notified of the need to not apply force to plant doors prior to the electronic locking mechanism releasing the door latch.
4231999002 | Millstone 3 | 01/15/1999 | 06/27/2001 | ML01190029 | <strong>Inadvertent Carbon Dioxide Fire Suppression System Actuation In The Cable Spreading Room</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1999, at 1749, with the Unit operating in Mode 1 at 100 percent power, spurious actuation of a control circuit caused an inadvertent discharge of the carbon dioxide (CO2) fire suppression system in the Cable Spreading Room (CSR). The plant operated at 100% power throughout the event. During the event, CO2 concentrations in the adjacent control room and the adjoining east and west switchgear rooms exceeded OSHA limits due to leakage across penetration seals, ventilation dampers and CO2 supply piping leaks. Ongoing evaluations of the conditions associated with this event also identified non-conservative Technical Specification ACTION statements associated with Specification 3.7.8, Control Room Envelope Pressurization System. These conditions are reported as historical operation in a condition that was outside the design basis of the facility. Additionally, a voluntary report is being made for a related matter in that some control room operators had not maintained qualification in the use of self contained breathing apparatus (SCBA). The root cause was determined to be that previous corrective actions for various fire protection system related events were inadequate. The CSR CO2 system has been locked-out to preclude operation. The Shift Manager and Fire Brigade Captains have been informed that CO2 initiation into the CSR is not to be included as part of the strategy to fight a fire in this room. Changes to Technical Specification 3.7.8 have been submitted for NRC approval. Repair and/or upgrade of penetration seals and ventilation access door and damper seals has been accomplished. Alternative fire suppression strategies are also being investigated for use in the CSR.
4231999003 | Millstone 3 | 05/05/1999 | 06/04/1999 | 9906100037 | <strong>Inadequate 18 Month Surveillance Test On The Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On May 5, 1999, an individual from the Oversight organization identified that the 18 month Emergency Diesel Generator (EDG) surveillance test for the Loss-of-Offsite Power (LOP) with Engineered Safety Features (ESF) start did not initiate the test from the required "standby conditions." Technical Specification (TS) surveillance requirement (SR) 4.8.1.1.2.g.6.b requires that, at least once per 18 months during shutdown, that each diesel starts from "standby conditions" on receipt of a simulated LOP signal in conjunction with an ESF actuation test signal. However, it was determined that since initial licensing, the 18 month LOP/ESF surveillance tests had not been performed from the required "standby conditions", but instead had been performed at hot engine conditions following the 24-hour load test (SR 4.8.1.1.2.g.7) as part of the hot restart demonstration. Both EDGs were declared inoperable. Failure to perform the LOP/ESF test from the proper initial conditions constitutes a missed TS surveillance and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The root cause of this condition was an inadequate understanding of the regulatory guidance related to this Technical Specification which resulted in incorrect requirements being translated into the implementing surveillance procedures associated with the EDG 18 month surveillances. There were no consequences to this condition. Both the 18 month LOP and ESF surveillance tests have been performed from "standby condition" conditions since the plant was licensed. The LOP/ESF start surveillance test was subsequently successfully completed for both EDGs from 'standby conditions" during this refueling outage. The "A" and "B" EDG were returned to operable status following successful performance of the 18 month LOP/ESF surveillance tests from "standby conditions."
4231999004 | Millstone 3 | 05/16/1999 | 06/14/1999 | 9906230042 | <strong>ESF Actuation of Numerous Plant Components on Restoration of A Train Sequencer</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1999, at 2353, with the Unit in a refueling outage, an invalid loss of power (LOP) signal actuation occurred and a number of components repositioned. The post-event review has identified that the procedure being used failed to reset the Emergency Generator Load Sequencer Train A LOP memory during the restoration of the sequencer and resulted in an inadvertent LOP signal actuation. This is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(B) as any event or condition that results in a manual or automatic actuation of any Engineered Safety Features (ESF), including the Reactor Protection System.
4231999005 | Millstone 3 | 05/10/1999 | 06/08/1999 | 9906150140 | <strong>Failure to Perform Surveillance On RCS Pressurizer Heater Penetration Breakers</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1999, with the plant operating in Mode 6, a review of a group of Containment Penetration Breakers that were scheduled to be surveilled after the refueling, identified that ten (10) breakers within the group that comprised the primary and secondary containment penetration protection for one of the pressurizer heater groups had been last tested in December 1991. As a result, the plant operated for a period of approximately 5 months with devices inoperable without complying with the requirements imposed by Technical Specifications. Therefore, this condition is reportable pursuant to 10CFR50.73(a)(2)(i)(b) as an operation or condition prohibited by the plant's Technical Specifications. The root cause of this event has been determined to be lack of management support of the program in that the responsible individual/group did not receive the resources, direction or oversight to properly implement sample selection and scheduling. These breakers are all non-safety related and when they were subsequently removed from service for testing, it was verified that they met the surveillance acceptance criteria and would have been capable of interrupting the fault current had they been called upon to do so. The required surveillance on the identified 10 breakers has been completed. Additionally, the Required Completion Date (RCD) within PMMS will be adjusted to reflect the date the surveillance will lapse for the containment penetration breaker surveillance prior to January 1, 2000.
4231999006 | Millstone 3 | 05/16/1999 | 06/15/1999 | 9906230129 | <strong>Failure of Both Reactor Plant Aerated Drains Safety-Related Air Driven Sump Pumps During a Technical Requirements Manual Surveillance</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1999, with the Unit in Mode 6, the Reactor Plant Aerated Drains (DAS) air driven sump pumps, 3DAS*P15A and *P15B, located in the Engineering Safeguards Building Features Containment Recirculation Cubicle Sumps, failed to pump water during the performance of a Technical Requirements Manual Surveillance On May 20, 1999, pumps 3DAS*P15A and *P15B were declared inoperable when they were still unable to pump water after a revision was made to the surveillance to increase the air pressure to the pumps. This condition was reported per 10CFR50.72(b)(2)(i) on May 20, 1999 at 10:23. The root cause of the equipment failure was determined to be an inadequate preventive maintenance program design in that the vendor technical manual and qualification testing requirements were not adequately incorporated during the procurement nor design change processes for pumps 3DAS*P15A and *P15B. Additionally, the root cause evaluation concluded that for both pumps the Hylum blades in the sump pump air motor became affixed to the inner liner of the air motor housing following design change testing on June 29, 1998 and before the initial preventive maintenance was performed on September 29, 1998. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as any event or condition that resulted in the nuclear plant being in a condition that was outside the design basis of the plant.
4231999007 | Millstone 3 | 05/18/1999 | 06/17/1999 | 9906290068 | <strong>Reactor Plant Aerated Drains Safety-Related Air Driven Sump Pump Design Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On May 18, 1999, with the Unit in Mode 6, the discharge filter associated with Containment Recirculating Spray System cubicle sump pump 3DAS-8A, was determined to be contaminated. The cause of the contamination was back leakage from contaminated drains feeding into an Emergency Core Cooling System pump area sump. The discharge piping from 3DAS-8A had been modified to eliminate this back leakage in support of estimating ground water in-leakage. The subsequent design change activity associated with the installation of safety related air driven sump pumps 3DAS*P15A/B inappropriately assumed that this modification could be credited to preclude back leakage during a design basis accident. Additionally, during the investigation associated with LER99-006-00, it was discovered that the initial design of the air driven safety related sump pumps 3DAS*P15A/B did not adequately address the long term effects of calcium carbonate plate out/build up on the operability of the air driven pumps. Operating experience derived from the effects of this phenomena on the non-safety related sump pumps indicates that accumulation could be sufficient to significantly degrade the air driven safety related sump pump performance late in the post accident operability period. These conditions are both reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B) as any event or condition that resulted in the nuclear plant being in a condition that was outside the design basis of the plant.
4231999008 | Millstone 3 | 09/28/1999 | 10/27/1999 | ML99316016 | <strong>Inadequate Surveillance Porcedure Results in 125 VDC system Operated Outside of its Licensing and Design Bases</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1999 engineering performed a review of surveillanCe procedure SP 3712 NC Rev. 3 "Vital Battery Charger Surveillance Load Testing." This review was prompted as a result of a technical concern raised by an electrical maintenance worker familiar with this surveillance procedure. The results of engineering's review revealed the following deficient conditions existed when testing in accordance with applicable surveillance procedures with the Unit at power; (1) unanalyzed D.C. loads were placed upon station battery numbers 14, (2) a Non-Class lE load bank utilized during testing was not electrically isolated from the 125 VDC bus and (3) the heat load associated with the load bank was not accounted for relative to provisions for adequate ventilation. Condition numbers I and 2 are reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B) as operation in a condition prohibited by Technical Specifications and 10 CFR 50.73(a)(2)(ii)(B) as a condition outside the design bases of the Unit. Condition number 3 has been determined to be not reportable. The cause of this event is attributed to procedural inadequacies due to a historical lack of an understanding of the licensing and design bases of the Unit. To correct this deficiency, surveillance procedure SP 3712 NC will be revised to reflect the licensing and design bases of the Unit to ensure that no unanalyzed electrical loads are placed upon the 125 VDC Class 1 E systems during performance of this procedure.
4241999001 | Vogtle 1 | 01/11/1999 | 02/09/1999 | 9902170212 | <strong>Containment Sump Operation Outside Of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On December 16, 1998, personnel inside the containment building noticed that water had overflowed from the north containment sump into an adjacent trench and piping. The control room was notified and the sump was pumped down. A review of computerized sump level records for 1998 found a trend, beginning in the August time frame, where sump level would rise to a near-maximum height, and then flatten out for periods of days to weeks prior to being pumped down. The periods of flattening were interpreted to represent the times that water flowed out of the sump into the adjacent trench and piping. On January 11, 1999, it was determined that the sump level monitors may not have been capable of meeting Technical Specification (TS) requirements for detection of reactor coolant system (RCS) leakage during those periods when water in the sump had flowed into the adjacent trench and piping. These periods represented unit operation in a condition prohibited by the TS. The cause of this event was the failure of a limit switch to automatically actuate the sump pump prior to the sump overflow. An investigation found that the switch calibration had drifted so that it started the pump at a water level approximately 2-3 inches higher than intended. The level switch was replaced.
4241999002 | Vogtle 1, Vogtle 2 | 06/30/1999 | 01/21/2000 | ML00367946 | <strong>High-Energy Line Break Instrument Channels Inadequately Calibrated</strong><br /><i>Abstract:&nbsp;</i>On June 30, 1999, an Instruments and Controls (I&C) procedure writer and assistant team leader (ATL) were reviewing a draft procedure revision. The procedure writer and ATL discovered that existing procedures did not adequately test several relays in a portion of the process control system. These relays send a signal to close steam generator blowdown (SGBD) isolation valves, and failure of these valves to close would defeat the high-energy line break (HELB) isolation function. Further investigation revealed that a similar condition existed for all of the SGBD instrument channels as well as the chemical volume and control system letdown isolation functions. The control room was notified. Testing of all the affected relays was performed and found no failures. The failure to adequately test these relays represents plant operation in a condition prohibited by the TS. The cause of this event was inadequate surveillance testing procedures. These procedures, written during initial plant startup, were inadequate because they did not fully verify proper operation of the HELB instrumentation channel circuits. Procedure revisions to add relay testing have been completed. On January 3, 2000, broadness review actions to find similar insufficiently tested components determined that testing for interlock relay contacts in the Cold Overpressure Protection System was inadequate. Testing was performed and no inoperable relay contacts were found.
4241999003 | Vogtle 1, Vogtle 2 | 09/22/1999 | 10/22/1999 | ML09153040 | <strong>Control Room Door Painting Results In Loss of Positive Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1999, personnel were painting the pair of control room entry doors that adjoin the east side of the control room. Both the inner and outer doors were opened to facilitate painting the edges of the doors. The shift superintendent noticed that both doors were open and confirmed with the shift support supervisor (SSS) that only one door should be opened. Shortly thereafter, the doors were closed. Review of this event determined that this represents a condition that alone could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident since opening the doors degrades the ability of the CREFS units to create a positive pressure. Technical Specification (TS) surveillance requirement SR 3.7.10.5 requires each control room emergency filtration system (CREFS) train to be capable of maintaining positive pressure in the control room. The plant operated in a condition prohibited by the TS when the capability for maintaining positive pressure in the control room was lost. The cause of this event was an inadequate pre-job briefing. The pre-job briefing did not advise personnel of the limitation of opening only one control room door at a time. This event will be discussed in meetings with plant support personnel emphasizing the need for compliance with all work instructions.
4241999004 | Vogtle 1, Vogtle 2 | 12/01/1999 | 12/29/1999 | ML00367332 | <strong>Inadequate Technical Specification Surveillances Due to Error in Calibrations</strong><br /><i>Abstract:&nbsp;</i>On December 1, 1999, a review of as-left calibration data from steam generator (SG) level transmitters determined that five (5) transmitters in Unit 1 and five (5) transmitters in Unit 2 were suspected to have been left outside of calibration tolerances. This was due to a mis-application of static shift compensation incorporated during recent procedure revisions. TS SR 3.0.3 was invoked to allow 24 hours to perform adequate surveillances on the ten level transmitters involved. Procedures were revised and level transmitters were re-calibrated and returned to service within the necessary 24 hours. The calibration error was found to be on the order of 0.5%, which is well within the Technical Specification (TS) allowable value for actuating both low and high SG water level signals. Operation of the plant while relying on the inadequately performed surveillances represented a condition prohibited by the TS. The cause of this event was inadequate procedure revisions. In 1998, a program was instituted to revise the methodology for transmitter calibrations to eliminate the task of performing a transmitter zero-shift, test at each calibration interval. In some cases, the revised procedures utilized the incorrect value for the static shift compensation. All affected procedures have been identified and the impact to each function assessed. This error did not result in the as-left calibrations for any transmitters, other than those described above, being outside of acceptable calibration tolerances.
4251999001 | Vogtle 2 | 03/21/1999 | 03/31/1999 | 9904070062 | <strong>Reactor Trip When Installing Clearances in Wrong Unit</strong><br /><i>Abstract:&nbsp;</i>On March 2, 1999, two plant equipment operators (PEOs) were given a clearance package to install Unit 1 clearances in support of the ongoing Unit 1 refueling outage. The PEOs went to the control room and witnessed the reactor operator place the required tags on the handswitches. Next, they went to level A of the control building and pulled fuses in Unit 1 panels. Finally, they proceeded to level 2, intending to enter into the cable spreading room above the Unit 1 control room. However, they instead went into the adjacent cable spreading room above the Unit 2 control room. The clearance required main feedwater isolation valve (MFIV) fuses to be pulled from cabinet 1BCPT20. The PEOs located the identical Unit 2 panel, 2BCPT20, and pulled the loop 3 MFIV fuses, allowing the MFIV to close. In the Unit 2 control room, personnel received steam/feed flow mismatch alarms and noticed steam generator (SG) level decreasing with low feed flow. Due to the loss of feedwater flow to SG #3, the unit shift supervisor (USS) ordered a manual reactor trip, which occurred at 0206 EST. A normal trip response occurred with the unit stabilizing in Mode 3 (hot standby). The direct cause of the reactor trip was personnel erroneously pulling the MFIV control power fuses in the wrong unit. The root cause of the error is attributed to inappropriate work practices. Various corrective actions addressing human performance are being implemented.
4251999002 | Vogtle 2 | 09/26/1999 | 12/03/1999 | ML99342019 | <strong>Safety Injection Pumps Declared Inoperable Due To Air Intrusion</strong><br /><i>Abstract:&nbsp;</i>On September 26, 1999, a monthly ECCS flowpath verification test was performed. As part of the testing, operators opened the Train B Safety Injection (SI) pump casing vents and noticed air exiting from the vent valves. The unit shift supervisor then directed operators to vent the Train A SI pump casing vents and a lesser amount of air exited from these vent valves. Both SI pumps were declared inoperable and a Technical Specification (TS) 3.0.3 entry was made. Each pump was vented again, but no more air was found. Pump runs of five (5) minutes each were performed with no anomalies observed and TS 3.0.3 was exited. The inadequate venting of both trains of SI also represented a condition that alone could have prevented the performance of the safety function of a system needed to mitigate the consequences of an accident. Several more ventings were conducted over the next two days with no anomalies and only insignificant amounts of air vented. The causes of this event were inadequate filling and venting following SI train outages in the days before the discovery of this condition. Corrective actions include changes to the work planning process for maintenance involving filling and venting, along with revisions to appropriate procedures.
4251999003 | Vogtle 2 | 10/04/1999 | 12/07/1999 | ML99348019 | <strong>Unplanned Mode Changes While Cooling Down For Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On October 4, 1999, operators were cooling down the reactor coolant system (RCS) at the start of a refueling outage. At approximately 0020 EDT, system cooldown stopped for operators to investigate an anomaly with residual heat removal (RHR) flow rates. After consulting with engineering and management personnel, it was determined that the RHR flow rate was acceptable and operators resumed the cooldown. A follow-up review of plant computer trends from the unit shutdown found that the RCS temperature, as measured by the auctioneered high wide range RCS average temperature (computer point UT5468), had dipped to approximately 199 degrees F when the cooldown was stopped for the RHR flow rate investigation. After approximately six minutes, RCS temperature, as indicated by UT5468, raised above 200 degrees F while the flow rate issue was being resolved. Therefore, because Mode 5 entry occurs when RCS average temperature is at or below 200 degrees F, the unit had entered Mode 5 for approximately six minutes prior to returning to Mode 4. The cause of the unplanned mode changes is ambiguity in the procedural guidance. The applicable procedure requires monitoring and recording of a variety of temperature parameters. This includes monitoring the UT5468 computer point. However, the procedure does not provide adequate guidance for what parameter is to be utilized for determination of mode changes. Appropriate procedures are being reviewed for necessary clarifications.
4401999001 | Perry | 03/17/1999 | 04/16/1999 | 9904230037 | <strong>Control Complex Building Architectural Walls Not Included in Tornado Differential Loading Design</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1999, at 1800 hours, the Perry Nuclear Power Plant (PNPP) engineering staff determined that the original design for architectural walls interior to the Control Complex building had not considered tornado differential pressure loads. This issue was identified through the review of an Operating Experience Report from another plant. The architectural walls that are installed for security and/or fire protection purposes inside of this safety related building would be subject to differential pressure loads, and if they failed they could present a hazard to plant equipment contained in the Control Complex. The NRC was notified at 1835 hours (ENS No. 35482) in accordance with 10 CFR 50.72(b)(1)(ii)(2) because the architectural walls do not meet the requirements for the Design Basis Tornado (DBT) load conditions described in the PNPP Updated Safety Analysis Report (USAR). The condition was evaluated in accordance with NRC guidance regarding resolution of degraded and nonconforming conditions and interim compensatory actions were implemented to allow for continued operation. The Control Complex building exterior doors and openings are being reinforced to withstand the effects of a DBT and prevent building depressurization effects on the internal architectural walls. The cause of this issue is that the design of the architectural walls interior to Control Complex building did not consider tornado differential pressure loads. As a result, the design may not be adequate to withstand a direct hit by a DBT.
4401999002 | Perry | 03/27/1999 | 04/26/1999 | 9904300098 | <strong>Limiting Condition for Operation 3.0.3 Entered Due to Technical Specification Bases Statement Interpretation</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1999, the Perry Nuclear Power Plant was in Mode 3 and cooling down to establish the plant conditions for Refueling Outage 7. The main condenser was in-service removing decay heat. At 0605, while attempting to start the Residual Heat Removal pump A subsystem for Shutdown Cooling (SDC) operations, the RHR A pump failed to start. Operations conservatively declared both Shutdown Cooling (RHR A and RHR B) subsystems inoperable. According to Technical Specification 3.4.9, Required Action A.2, when one or two RHR/SDC subsystems are inoperable, an alternate method of decay heat removal must be verified for each inoperable RHR/SDC subsystem within one hour. At the time, the main condenser was not considered to meet the requirements for an alternate decay beat removal (ADHR) system due to the interpretation of the Technical Specification Bases, and the necessary verification could not be accomplished. At 0704, Limiting Condition for Operation (LCO) 3.0.3 was entered based upon the understanding that the required action could not be completed within the required completion time. Upon further review, it was determined that the main condenser had met the requirements for an ADHR method. Therefore, sufficient alternate decay heat removal methods were available at all times during this period, and the plant was not in a condition that required entry into LCO 3.0.3. However, this report is being made due to the administrative entry into LCO 3.0.3 by the plant staff.
4401999003 | Perry | 02/18/1999 | 09/27/1999 | 9910010124 | <strong>Post-accident Dose Limits Exceeded for Relief Valve Leakage Outside of Containment</strong><br /><i>Abstract:&nbsp;</i>On February 18, 1999, Perry Nuclear Power Plant reported that leakage outside of containment exceeded the operating limit criteria required to maintain post-accident dose limits within the criteria specified in 10 CFR 50 Appendix A and 10 CFR 100. The leakage was measured at approximately 135 gph. The leakage source was determined to be a relief valve on a connecting line between the Residual Heat Removal heat exchangers to the Reactor Core Isolation Cooling system. As an immediate corrective action, the valve was gagged, and the rate of leakage outside containment was verified to be within the operational limit as required by operating procedures. This event was initially reported via the Emergency Notification System under notification ENF #35383 at 2139 hours on February 18, 1999. Postulated post-accident doses from engineering calculations were later determined to be within the design basis, and NRC notification was retracted. The NUREG-1465 methodology, "Accident Source Terms for Light Water Nuclear Power Plants," which had not been fully approved as part of the plant's licensing basis until March 26, 1999, was used initially for verifying compliance with 10 CFR 50 Appendix A and 10 CFR 100. Upon recognition that NUREG- 1465 was inappropriate to use at the time of the event, a sensitivity study utilizing Regulatory Guide 1.3, "Assumptions Used for Evaluating The Potential Radiological Consequences of a Loss of Coolant Accident for Boiling Water Reactors," was conducted. The study concluded that the limits in 10 CFR 50 Appendix A and 10 CFR 100 would have been exceeded. Therefore, based on exceeding the dose limits, this constitutes a condition that was outside the design basis of the plant, which is reportable in accordance with 10 CFR 50.73(a)(2)(11). This condition was caused by a leaking relief valve. The corrective action involved the removal of the relief valve on September 13, 1999, by a Design Change Package implemented under 10 CFR 50.59.
4401999004 | Perry | 09/16/1999 | 10/18/1999 | 9910260095 | <strong>Loss of Safety Function Results In Technical Specification 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On September 16, 1999 at 1829 hours, personnel at the Perry Nuclear Power Plant observed a funnel-shaped cloud to the northeast of the plant. The plant was in Mode 1 at 100% power at the time of the sighting. The sighting was immediately reported to the Control Room. In accordance with plant procedures, contingencies for a possible tornado strike were implemented. These actions are part of proceduralized storm contingencies involving in part the temporary opening of cable chase doors in the area of the Control Room. These actions are necessary to prevent a severe tornado-generated depressurization event from failing architectural walls, which could impact equipment required for safe shutdown. However, breaching these boundaries renders both trains of the Control Room Emergency Recirculation system inoperable and constitutes the loss of a safety function. Technical Specification 3.7.3(D) states that an immediate entry into Technical Specification 3.0.3 is required, if both Control Room Emergency Recirculation Trains are lost in Modes 1,2 or 3. Technical Specification 3.0.3 was entered at 1850 hours on September 16, 1999. Entry into Technical Specification 3.0.3 is reportable under 10 CFR 50.73(a)(2)(i)(B). The loss of a safety function of structures or systems that are needed to mitigate the consequences of an accident is reportable under 10 CFR 50.73(a)(2)(v)(D). No mode changes or power changes were made as a result of this event. The NRC was notified via Emergency Notification System phone message at 1859 hours on September 16, 1999, (ENF #36181). When severe weather had moved away from the plant at 1927 hours on September 16, 1999, all Control Complex boundaries were re-established, and Technical Specification 3.0.3 was exited. An actual tornado was not sited.
4401999005 | Perry | 11/04/1999 | 12/22/1999 | ML00367034 | <strong>Control Rod Moved Without Re-establishing a More Restrictive Rod Withdrawal Limit During Testing</strong><br /><i>Abstract:&nbsp;</i>On November 5, 1999, following initial review of post-maintenance test data from routine control rod speed and drift calibration, an operability determination concluded that that rod movement had been made with the rod withdrawal limiter function of the Rod Control and Information system apparently inoperable. Plant procedures require that the deselect/reselect button be depressed following any rod insertion, in order to re-initialize the rod withdrawal limit. This would have produced an alarm and a rod block (preventing further withdrawal) at two notches withdrawn. The deselect/reselect button was not depressed initially, and so the rod withdrawal limit was not re-established as required procedurally. When the operator recognized that the control rod was withdrawn two notches without an expected alarm or rod block function, the operator immediately stopped withdrawal. The rod settled at three notches withdrawn, one notch beyond the desired limit, but within bounded, analyzed limits. The event was initially reported to the NRC via telephone per ENF # 36397 on November 4, 1999. Subsequent analysis determined that the rod withdrawal limiter was operable at the time of the rod withdrawal, and that no condition prohibited by plant Technical Specifications existed. A retraction was issued on November 30, 1999. This event is submitted as a voluntary report in accordance with guidance in NUREG 1022, Revision 1 as an event having generic interest to the industry. The root cause of this event was determined to be man-machine interface difficulties in operating the rod withdrawal limiter function. Re-initializing the rod withdrawal limiter following any rod insertion was determined to be a conservative operating practice, as it is currently controlled in plant instructions. Roles and responsibilities during rod movement were re-established, and the balance of rod testing was completed successfully. Procedural controls for the rod withdrawal limiter will be enhanced to minimize future errors.
4401999006 | Perry | 11/24/1999 | 12/22/1999 | ML00367034 | <strong>Disengaged Locking Spring on Relay Renders One Train of Standby Liquid Control System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 24, 1999, at 1015 hours, personnel at the Perry Nuclear Power Plant discovered that a relay in the Standby Liquid Control system circuitry had a locking spring that was disengaged from the relay. The locking spring prevents the relay, which is part of the circuit for firing the explosive squib valves, from becoming dislodged from its mounting in a seismic event. A review of work orders from several months preceding this discovery revealed that no other work activities were conducted in the cabinet, and so there was a reasonable assurance that the Standby Liquid Control system Train A had been inoperable for seven days or more in the current operating cycle. Technical Specifications require that two Standby Liquid Control subsystems be operable in Modes 1 and 2. The associated Limiting Condition for Operation states that an inoperable SLC subsystem must be restored to operability within seven days. Exceeding this limit constitutes the loss of a safety function of structures or systems that are needed to mitigate the consequences of an accident, and is reportable under 10 CFR 50.73(a)(2)(v)(D). This would also constitute operation of the plant in a condition outside of its design basis, which is reportable under 10 CFR 50.73(a)(2)(ii)(B), and operation in a condition outside of Technical Specifications, reportable under 10 CFR 50.73 (a)(2)(i)(B). Accordingly, the NRC was notified via Emergency Notification System phone message at 1411 hours on November 24, 1999, (ENF #36461). Standby Liquid Control Train A was immediately declared inoperable upon discovery of the loose locking spring. The locking spring was re-installed, and the train was declared operable at 1223 hours on November 24, 1999.
4431999001 | Seabrook | 03/29/1999 | 04/28/1999 | 9905040269 | <strong>Emergency Diesel Generator Inoperability Due to Westinghouse AR Relay Failures</strong><br /><i>Abstract:&nbsp;</i>On March 31, 1999 at 1100, during the sixth refueling outage, North Atlantic Energy Service Corporation (North Atlantic) determined that the Train B Emergency Diesel Generator (EDG) may not have been operable during portions of the previous operating cycle. Specifically, during 18 month EDG testing on March 29, 1999, it was determined that an AR relay associated with the Train B EDG Emergency Power Sequencer (EPS) was incapable of opening the breaker to the Unit Auxiliary Transformer (UAT). This could have prevented the Train B EDG from powering the emergency bus if called upon to do so. Additional testing on March 30, 1999, revealed that another AR relay associated with the Train B EDG EPS was incapable of starting a Containment Building Spray (CBS) pump. This would have prevented the Train B CBS pump from automatically starting if called upon to do so. This event was caused by a combination of two factors; formation of corrosion products on the relay contacts and other surfaces resulting from age related degradation of the relays' molded neoprene cover gaskets and improper relay calibration settings. The AR relay internals and covers in both trains of the EDG EPS will be replaced with new units prior to startup from the current refueling outage. The procedure utilized for testing the AR relays has been revised to clarify techniques and acceptance criteria. The AR relays in the EDG EPS will be periodically inspected for signs of corrosion and gasket degradation.
4431999002 | Seabrook | 09/21/1999 | 10/21/1999 | 9910280156 | <strong>Non-Compliance With Technical Specification 3.8.1.1 Action Requirements Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On September 21, 1999 at 2000 with the plant operating at 100% power (operational mode 1), it was determined that the performance of a Technical Specification required action was not met within the required time period. The Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.8.1.1 (AC Sources) requires that two separate independent diesel generators be operable during operational modes 1, 2, 3, and 4. TS 3.8.1.1 action b. specifies that with a diesel generator inoperable, the operability of the remaining A.C. (alternating current) sources be verified within 1 hour and at least once per 8 hours thereafter. Contrary to the requirements of TS 3.8.1.1 action b., the 1 hour action requirement was exceeded without verifying the operability of the remaining A.C. sources. The requirements of TS 3.8.1.1.b were subsequently met by the completion of the test required by Specification 4.8.1.1.1a. at 2020 on September 21, 1999. This event is reportable pursuant to the requirements of 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by the plant Technical Specifications. The cause of this event was personnel error. There were no adverse safety consequences as a result of this event. A number of corrective actions have been initiated as a result of this event. This is the first event of this type reported by Seabrook Station during the past 4 years.
4451999001 | Comanche Peak 1, Comanche Peak 2 | 05/10/1999 | 06/09/1999 | 9906150203 | <strong>Some Electrical Contacts for the Reactor Coolant System Pressure Relief Valves Were Not Included In the Surveillance Testing Procedures</strong><br /><i>Abstract:&nbsp;</i>The Comanche Peak Steam Electric Station (CPSES) Technical Specification(TS) section pertaining to Reactor Coolant System (TS 3/4.4.4 and 3/4.4.8) and the Inservice Testing Program (TS 4.0.5) require calibration, and/or Analog Channel Operational Test (ACOT) and valve testing. On May 10, 1999, during a review of procedures pertaining to the Reactor Coolant System (RCS) it was discovered that certain contacts in the valve circuitry influencing the pressure and/or temperature process signals were not included in the testing procedures. The probable cause of the missed surveillance was deemed to be less than adequate procedures. Immediate corrective actions were to determine operability of the RCS system. The RCS was determined to be operable for the current mode. The circuit is required to be operable in modes 4, 5 and 6. Procedures pertaining to the circuit testing are being revised, testing will be performed consistent with the existing LCO as warranted.
4451999002 | Comanche Peak 1, Comanche Peak 2 | 05/18/1999 | 06/10/1999 | 9906150211 | <strong>Missed Technical Specification Surveillance For Steam Generator Gross Activity Composite Sampling</strong><br /><i>Abstract:&nbsp;</i>At approximately 12:15 a.m., on May 18, 1999, Comanche Peak Steam Electric Station (CPSES) Unit 1 was in Mode 1, Power Operation, with reactor power at approximately 100 percent, and Unit 2 was in Mode 1, Power Operation, with reactor power at approximately 100 percent. The Unit 1 Steam Generator Composite sample for gross activity was previously collected on May 14, 1999 at 12:05 a.m. and collected again on May 18, 1999 at 12:05 a.m. This was 96 hours between samples. Unit 2 Steam Generator Composite sample was previously collected on May 14, 1999 at 12:40 a.m. and collected again on May 18, 1999 at 12:20 a.m. This was 95 hours and 40 minutes between samples. Technical Specifications require the Steam Generator Composite sampling to occur every 72 hours with a 25 percent allowable extension period of 18 hours. The missed surveillance was not in accordance with Technical Specification 4.7.1.4 and Table 4.7-1, which requires gross activity sampling of the secondary system at least once per 72 hours. TXU Electric has evaluated the circumstances concerning the missed surveillance, and believes that the missed surveillance was caused due to cognizant personnel being distracted from their normal duties. Corrective actions are to issue lessons learned with the cognizant individuals, and management expectations with respect to adherence to surveillance procedures have been reemphasized.
4451999003 | Comanche Peak 1 | 05/19/1999 | 06/10/1999 | 9906150218 | <strong>Unit 1 Battery Surveillances Were Not Performed With the Proper Periodicity As Required By the Plants Technical Specification</strong><br /><i>Abstract:&nbsp;</i>Comanche Peak Steam Electric Station (CPSES) Technical Specification (TS) section 4.8.2.1d requires that the 125V D.C. station batteries be demonstrated operable by performing a battery service test at least once per 18 months, during shutdown. Surveillance Requirement (SR) 4.8.2.1e, states that a battery performance discharge test is allowed in lieu of the service test once per 60 month interval. For Unit 1 battery BT1ED2, the performance discharge test was incorrectly used twice within a 60 month interval in lieu of the service test. In accordance with Surveillance Requirement 4.0.3, this failure to perform the Surveillance Requirement constituted a noncompliance with the operability requirements for the Limiting Condition of Operation (LCO). On May 19, 1999, during the process of conducting reviews of battery surveillances, CPSES discovered that credit had been taken for the performance of a battery performance discharge test in lieu of a service test more frequently than is permitted by SR 4.8.2.1e. TXU Electric believes that crediting the performance discharge test in 1RFO6 (Unit 1 sixth refueling outage) was acceptable and that compliance with the requirements of SR 4.8.2.1d for battery BT1ED2 was re-established by the performance of that test. However, due to the ambiguity of the situation TXU Electric has conservatively chosen to consider that the surveillance is not current. Immediate actions were to enter the appropriate LCO, A Notice of Enforcement Discretion (NOED) was requested via Reference 1 and a onetime license amendment request has been submitted via Reference 2 and 3.
4451999004 | Comanche Peak 1 | 08/30/1999 | 10/06/1999 | 9910140067 | <strong>Voluntary Report for Issues Relating to Qualification of The Platform Grating and Clip System</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1999 after a review of a seismic test report, TXU Electric Engineering (utility, non-licensed) conservatively determined that some grated surfaces at CPSES were outside the design basis by the use of friction type of grating fasteners . Even though the as tested grating fastener did not replicate the as installed grating fasteners, engineering judgement was that the test results rendered the current plant qualification of the grating and clip system indeterminate, when considering occupant live loads . This was initially reported on to the NRC on August 2, 1999 . This condition related to whether or not the grating has confinement based on qualification questions related to the grating clamp being capable of resisting the horizontal loads from a seismic event in conjunction with the live loads. Examples of potential configurations of concern included cantilevered gratings, and elevated platforms with toe plates that may not provide external confinement.
4461999001 | Comanche Peak 2, Comanche Peak 1 | 12/26/1998 | 01/19/1999 | 9901270150 | <strong>Technical Specification Surveillance for Containment Integrity Verification Was Not Performed On A Penetration Due To Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 26, 1998, while performing primary containment integrity verification, Operations Plant Equipment Operator (PEO) (utility, non-licensed) identified that a penetration used for Comanche Peak Steam Electric Station (CPSES) Unit 2 integrated leak rate testing was not listed on the verification data sheet. The PEO performed the required verification and notified Operations shift management (utility, licensed) about the procedure anomaly. On December 28, 1998, it was concluded that a violation of CPSES Technical Specifications had transpired. TU Electric's evaluation of the event deemed that an adequate design modification impact review was not performed by the responsible organization. Immediate corrective action was to perform the required surveillance. The applicable procedures have been revised to incorporate the penetration in the verification data sheet.
4461999002 | Comanche Peak 2, Comanche Peak 1 | 01/03/1999 | 01/20/1999 | 9901270180 | <strong>Manual Reactor Trip Due To Turbine Load Swings</strong><br /><i>Abstract:&nbsp;</i>At approximately 11:14 a.m., on January 3, 1999, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, with reactor power at approximately 100 percent, main turbine generator control valves suddenly and unexpectedly closed while at 100 percent rated power. As designed, all steam dumps immediately opened and rods automatically stepped in to control the reactor coolant system temperature transient. The reactor plant, designed to withstand a 50 percent load rejection without a trip, experienced an equivalent 80 percent load rejection event. The cause of the load rejection was not apparent. In response to the loss of turbine load control, the Unit 2 Operations Shift Supervisor (utility, licensed) made a conservative decision to manually trip the reactor. The cause of the event could not be determined. A data acquisition system (minidas) has been connected to the Electro-Hydraulic Control (EHC) control system to monitor and collect data and provide additional diagnostic information, should the failure repeat.
4461999003 | Comanche Peak 2, Comanche Peak 1 | 04/21/1999 | 05/20/1999 | 9905270107 | <strong>Control Room HVAC Train A Was Found Outside Technical Specification Allowed Outage Time Limits Due To A Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>Comanche Peak Steam Electric Station (CPSES) Technical Specification 3.3.2 requires that the Control Room Emergency Recirculation be operable in all modes by operating the train(s) manually. On April 18, 1999, while placing both trains of control room emergency filtration in emergency recirculation Train B actuated; however, Train A failed to actuate. Subsequently it was discovered that a relay control power fuse had blown in the control room circuitry. After a review of the event and associated circuits on April 21, 1999, it was conservatively determined that the fuse may have been blown due to work performed on April 13, 1999. It was postulated that Train A of the Control Room HVAC System may have been inoperable when CPSES Unit 2 changed from Mode 6 (April 13, 1999) to Mode 3 (April 18, 1999). The probable cause of the blown fuse was attributed to incorrect landing of wires that provide relay control power for control room ventilation circuitry. Corrective actions were to replace the fuse. The unit was declared operable after a successful surveillance test.
4461999004 | Comanche Peak 2, Comanche Peak 1 | 05/22/1999 | 06/18/1999 | 9906280258 | <strong>A Lockout Relay Actuation Caused the CPSES Unit 2 Train "A" Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On May 22, 1999, at approximately 07:15 a.m. CDT, Unit 2 Train "A" safeguard supply breaker experienced a lockout relay actuation. Train A emergency diesel generator 2-01 started and its breaker closed to re-energize the bus. The blackout sequencer actuated and restored the safeguard equipment as expected. Comanche Peak Steam Electric Station Unit 2 entered the applicable limiting conditions for operations (LCO), and the appropriate procedures to respond to the loss of normal power to the Train "A" bus and restore from the blackout sequencer actuation. Plant operation was unaffected by this condition. Troubleshooting was performed to determine the cause of the relay actuation. A conclusive cause could not be determined. The relay was replaced and all affected systems were considered functional, and the applicable LCO was exited.
4541999001 | Byron 1 | 04/22/1999 | 05/21/1999 | 9905270238 | <strong>Depressing Both Feedwater Isolation Reset Pushbuttons Leads To LCO 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>On 4/22/99, during control rod drop testing in Mode 3, prior to reactor startup following refueling (B1R09), the reactor trip breakers were cycled numerous times. The reactor trip permissive interlock (P-4) signal associated with the trip breakers opening results in a feedwater isolation signal. To prevent this unwanted feedwater isolation, Byron Station's past practice had been to temporarily depress and hold feedwater isolation reset pushbuttons while opening the reactor trip breakers. This action blocks both trains of feedwater isolation from occurring during the P-4 interlock actuation, and also effectively renders 2 trains of feedwater isolation actuation instrumentation inoperable, because a feedwater isolation cannot occur during the time the pushbuttons are depressed. Prior to implementation of the Improved Standard Technical Specifications (ITS), the feedwater isolation function was only required in Modes 1 and 2, and thus rendering feedwater isolation actuation instrumentation inoperable during control rod drop testing was not an issue. After implementation of ITS, the feedwater isolation actuation instrumentation function is required in Modes 1 through 3, and rendering 2 trains inoperable in Mode 3 resulted in an entry into Limiting Condition for Operation (LCO) 3.0.3. This was determined to be a condition prohibited by the Technical Specifications, reportable under 10CFR50.73(a)(2)(i)(B). The cause of the event was determined to be that the procedure review before implementing ITS did not make the necessary changes to this procedure. It was determined that there was minimal safety significance to the event. Procedures will be changed to use alternative testing methods that avoid the LCO 3.0.3 entry.
4541999002 | Byron 1, Byron 2 | 05/09/1999 | 01/16/2001 | ML01023011 | <strong>Design Package Fails To Classify Feedwater Vent Valves as Containment Isolation Valves and Results in Missed Technical Specification Surveillance</strong><br /><i>Abstract:&nbsp;</i>On 5/9/99, at 0115 hours, with Byron Station Unit 1 operating at 100% power, Operations personnel performed Byron Operating Surveillance 6.3.3-1, "Primary Containment Integrity Verification of Outside Containment Isolation Devices." This monthly surveillance verifies each containment isolation manual valve, remote manual valve and blind flange, located outside containment that is not locked, sealed, or otherwise secured and is required to be closed during accident conditions, is closed. While performing the surveillance, Operations personnel questioned the absence of four high point vent valves from the surveillance procedure since other valves similar in design and function were included in the surveillance procedure. The four valves were immediately verified closed with pipe caps installed. The four high point vent valves were added to the Feedwater System in Byron Station Unit 1 Refueling Outage 08 that ended 03/09/98. On 05/10/99, Engineering personnel reviewed the design for the four valves in question and determined they met the criteria for containment isolation valves and should have been included in the surveillance procedure. Failure to verify the four valves closed every month was determined to be a condition prohibited by the Technical Specifications and reportable in accordance with 10 CFR 50.73(a)(2)(I)(B) The cause of the event was determined to be an error in the design package. The design package did not identify the vent valves as containment isolation valves. It was determined that there was no safety significance to the event. Corrective actions include changing the monthly surveillance procedure for containment isolation valves to include these four manual vent valves. A recurring events search found no events where previous corrective actions should have precluded this event.
4541999003 | Byron 1 | 05/13/1999 | 06/11/1999 | 9906180061 | <strong>Automatic Reactor Trip Due To Human Error During Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1999, at 0810 hours, with Byron Station Unit 1 at 100% power, an Instrument Maintenance Technician (IM) inadvertently caused a Reactor Trip System (RTS) automatic actuation. This occurred during the performance of the Technical Specification Surveillance Requirement (SR) for the Power Range Neutron Flux Instrumentation channel. The SR being performed was the 92 day frequency Channel Operational Test (COT). The IM mistakenly removed instrument fuses from a channel adjacent to the channel he had placed in test for the surveillance procedure. This action caused the two of four coincidence logic to be satisfied for the generation of an automatic reactor trip. Operators responded using appropriate procedures. The cause of the trip was a human performance error by the IM conducting the surveillance procedure. There were no safety consequences impacting plant or public safety as a result of the event. The FITS functioned as designed. Corrective actions include appropriate Management action with the IM involved and re-enforcement of human performance expectations with all Maintenance Department personnel. There was one previous occurrence involving an RTS actuation due to a human performance cause reported in Byron Station Licensee Event Report 454-96-17. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv).
4541999004 | Byron 1, Byron 2 | 09/28/1999 | 10/26/1999 | ML99307021 | <strong>Solid State Protection System (SSPS) Slave Relay Response Time Untested Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>During review of Westinghouse WCAP-l403~-P-A1 "Elimination of Periodic Protection Channel Response Time Tests," to explore the possible reduction of response time testing, it was determined that the slave relay portion of the response time in the Solid State Protection System (SSPS) was not properly verified, contrary to Technical Specification (TS) Surveillance Requirement (SR) 3.3.2.12. The Shift Manager was notified and SR 3.0.3 was entered for the missed surveillance requirement at 1245 hours on September 28, 1999. In lieu of actual measurement during the re-performance of the surveillance, the TS allows response time to be assigned for selected components provided that the components and methodology for verification have been previously reviewed and approved by the NRC. The NRC had previously approved WCAP-14036-P-A and associated references that address the slave relays in question. Changes were made to the affected surveillance procedures to allocate a bounding response time for the relays and the surveillance response time compilation was satisfactorily re-performed within the allowed 24-hour time period. SR 3.0.3 was exited at 1930 hours for both Units. The slave relay response time was correctly tested during the original pre- operational testing, but was first omitted in the initial 18-month TS surveillance procedure for an unknown reason. This event is being reported pursuant to 10 CFR 50.73 (a) (2) (i) (B).
4551999001 | Byron 2 | 10/19/1999 | 11/16/1999 | ML99330004 | <strong>Six of 20 Main Steam Safety Valve Relief Tests Exceeded Required Tolerance Due to Disk to Nozzle Metallic Bonding</strong><br /><i>Abstract:&nbsp;</i>During relief testing of the Unit 2 Main Steam Safety Valves (MSSVs) on October 19 and 20, 1999, six of 20 MSSVs failed to meet Technical Specification surveillance requirements. Operations entered the applicable Technical Specification Action Condition until each valve was tested satisfactorily. Because the MSSVs were tested sequentially, only one valve was inoperable at any one time. These failures resulted in no personnel injury or equipment damage. An evaluation performed indicates that limits for the three design basis accident scenarios that could be affected by an MSSV setpoint drift were not exceeded. The cause of the failures has been determined to be a form of metallic bonding between the disk and the nozzle resulting in an increase in the valve's setpoint. This phenomenon is characterized by recently refurbished MSSVs experiencing a high initial lift setting followed by satisfactory subsequent lift setting, with no intervening adjustments, as occurred in this event. Corrective actions include not refurbishing any MSSVs until a disk made of material less susceptible to this phenomenon is procured. This condition is reportable in accordance with 10 CFR (a)(2)(i)(B).
4551999002 | Byron 2 | 11/10/1999 | 12/09/1999 | ML99355011 | <strong>Inadvertent Reactor Protection and Engineered Safety Feature Systems Actuations in Mode 5 due to Unexpected Steam Generator Level Response When Stroking Feedwater Isolation Vavle</strong><br /><i>Abstract:&nbsp;</i>Byron Station Unit 2 was in Mode 5 and making preparations for restart after successfully refueling the reactor. At this point in the refuel outage, activities are in progress to begin filling the secondary side and to perform necessary surveillances required per Technical Specifications. At 2220 hours on November 10, 1999, the priming of the hydraulic pump for the Main Feedwater Isolation valve (2FW009B) was in progress. The priming activity caused as expected, the 2FW009B valve to open. As the valve opened water back flowed from the B Steam Generator into the feedwater lines. The B Steam Generator level dropped more than expected, approximately 15%, to below the Reactor Trip System (RTS) and Engineered Safety Feature (ESF) setpoints. The RTS and ESF signals were generated as designed and all plant systems and components responded normally for Mode 5 plant conditions. The extent of the possible consequences of allowing the 2FW009B valve to be stroked with the feedwater lines not filled was not fully understood by Licensed Operators. This Outage evolution will not be allowed in the future until a specific procedure is developed to control the evolution. There were no safety consequences from this event. The steam generator protection features were not required to be operable in this plant condition. This event is reportable in accordance with 10CFR 50.73 (a)(2)(iv).
4561999001 | Braidwood 1 | 05/16/1999 | 06/15/1999 | 9906220122 | <strong>Both Trains of Low Pressure Safety Injection Delcared Inoperable Due to A Gas Pocket in the B/C Cold Leg Injection Piping</strong><br /><i>Abstract:&nbsp;</i>While performing a Technical Specification (TS) surveillance requirement for venting the high points in the Emergency Core Cooling System (ECCS) piping outside containment, Ultrasonic Testing (UT) revealed a gas pocket in the "1B" ECCS train piping that could not be removed. The "1B" ECCS train was declared inoperable on 5/13/99. After installing a vent valve to vent this gas pocket, UT inspection of the remaining high point locations without installed vent valves revealed another gas pocket in a section of discharge piping common to both Low Pressure Safety Injection trains of ECCS. Because this gas pocket could not be vented, both trains of ECCS were declared inoperable. Since no actions are provided in TS Limiting Condition for Operation (LCO) 3.5.2, "ECCS-Operating," for this condition, TS LCO 3.0.3 was entered on 5/16/99 requiring a unit shutdown. To avoid the undesirable effects of a thermal transient associated with shutdown, a Notice of Enforcement Discretion (NOED) was requested and approved by the NRC on 5/16/99. A compensatory action of the NOED was to vent and UT inspect the ECCS piping inside containment. This inspection revealed very small gas pockets. An Operability Determination addressed this nonconforming condition of ECCS piping inside containment and justified continued operation with compensatory measures. Design changes were initiated to install vent valves in the common ECCS discharge piping outside containment. This allowed the ECCS venting surveillance to be completed satisfactorily; the NOED and the TS LCOs were exited on 5/19/99. The cause of the gas pockets was leakage of Safety Injection (SI) Accumulator water and subsequent evolution of nitrogen through check valve 1SI8818D, and to a lesser extent through check valves 1SI8818A and 1SI8818C. A contributing cause to the leakage across check valve 1SI8818D was an operating procedure change that resulted in a reduction in the differential pressure across this valve. Corrective actions include installation of vents in the affected ECCS piping outside of containment, changes to operating procedures for running the ST pumps on miniflow or for filling accumulators in a manner such that the differential pressure across the affected check valves is maximized, and the inspection and repair as necessary to check valve 1SI8818D. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i).
4561999002 | Braidwood 1, Braidwood 2 | 09/28/1999 | 10/26/1999 | ML99308007 | <strong>Solid State Protection system (SSPS) Slave Relay Response Time Untested Due to Inadequate Procedures.</strong><br /><i>Abstract:&nbsp;</i>During review of Westinghouse WCAP-14036-P-A, "Elimination of Periodic Protection Channel Response Time Tests," to explore the possible reduction of response time testing, it was determined that the slave relay portion of the response time in the Solid State Protection System (SSPS) was not properly verified, contrary to Technical Specification (TS) Surveillance Requirement (SR) 3.3.2.12. The Shift Manager was notified and SR 3.0.3 was entered for the missed surveillance requirement at 1245 hours, on September 28, 1999. In lieu of actual measurement during the re-performance of the surveillance, the TS allows response time to be assigned for selected components provided that the components and methodology for verification have been previously reviewed and approved by the NRC. The NRC had previously approved WCAP-14036-P-A and associated references address the slave relays in question. Changes were made to the affected surveillance procedures to allocate a bounding response time for the relays and the surveillance response time compilation was satisfactorily re-performed within the allowed 24-hour time period. SR 3.0.3 was exited at 1715 hours for Unit 2 and at 1810 hours for Unit 1. The slave relay response time was correctly tested during the original pre-operational testing, but was first omitted in the initial 18-month TS surveillance procedure for an unknown reason. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
4571999001 | Braidwood 2 | 04/14/1999 | 05/14/1999 | 9905190249 | <strong>Unit 2 Generator and Subsequent Reactor Trip due to an Spurious Generator Stator Ground Relay (GIX-104) Actuation and Subsequent Rod Control Problems</strong><br /><i>Abstract:&nbsp;</i>On 4/14/99 at 0433, the Braidwood Station Unit 2 reactor tripped due to a main generator and turbine trip. The generator trip was due to a spurious Generator Stator Ground Relay, GIX-104 relay, actuation. There was no identified personnel error or inappropriate action. The Digital Fault Recorder (DFR) records showed no evidence of a generator ground. The DFR showed a higher than normal third harmonic voltage before and after the reactor trip. The Sequence of Events Recorder (SER) showed two alarms, GIX-104 relay and voltage regulator, prior to the generator trip. A failed Minimum Excitation Limiter (MEL) card on the voltage regulator caused the card output to fail high raising the excitation of the generator. The plant equipment responded as designed, with the opening of the generator output breakers, tripping of the turbine, tripping of the reactor, and initiation of Auxiliary Feedwater. On 4/15/99 during startup following these repairs, a Rod Control Urgent Failure alarm was received. This resulted in the Control Rod Drive System being incapable of control rod movement. The control rods remained trippable. During the repair efforts control banks C and D became misaligned such that the overlap limits were not met. Actions of Limiting Conditions of Operation (LCO) 3.1.6, "Control Bank Insertion Limits" , were entered due to the failure to meet the required overlap specified in the Core Operating Limits Report. Actions of LCO 3.1.6 requires verification of shutdown margin within 1 hour and that the overlap limits be met otherwise the unit must be placed in mode 2 with Keff< 1.0 within the next 6 hours. A Unit 2 shutdown was initiated to complete repairs due to the Control Rod Drive Systems, inability to move control rods. The shutdown was accomplished by opening the reactor trip breakers. The cause of the Control Rod Drive System failure is attributed to several card failures, which were subsequently identified and replaced. Following repairs to the Control Rod Drive System, the unit was returned to operation. This event is being reported pursuant to 10CFR50.73(a)(2)(i) and 10CFR50.73(a)(2)(iv).
4571999002 | Braidwood 2 | 04/24/1999 | 05/21/1999 | 9906070211 | <strong>Engineered Safety Feature Actuation (P-14) due to High Water Level in the 2C Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On April 24, 1999, during cooldown of Unit 2 for refueling outage A2R07, an increase in Steam Generator (SG) water levels was recognized by operators. During efforts to identify and stop the source of in-leakage to the steam generators, a P-14 (SG Water Level High-High) Engineered Safety Feature (ESF) actuation occurred at 1936. As a result of the actuation signal, 2FW002A-C (Feedwater Pump Discharge Isolation Valves) closed. No other components changed status because other equipment receiving the actuation signal were in their actuated positions. The increasing steam generator water levels were determined to be caused by gravity feed from Unit 2 Condensate Storage Tank (CST) to the steam generators through the Auxiliary Feedwater (AF) System. The primary cause of this event is attributed to a procedural deficiency which allowed a flowpath to exist from the Condensate Storage Tank to the steam generators via the 2AF013A-H, Steam Generator Isolation Valves. Following the event, the Steam Generator Blowdown System was placed in operation and the steam generator water level was returned to the normal operating range. In addition, an Emergency Notification System (ENS) notification was made in accordance with 10CFR50.72(b)(2)(ii), "Any event or condition that results in a manual or automatic actuation of any engineered safety feature (ESF), including the reactor protection system (RPS)..." Corrective Actions to be taken include revising the station's Shutdown procedure for both units to address identified deficiencies and discussing the event with operations personnel in Licensed Operator Requalification Training. This event is being reported in accordance with 10CFR50.73(a)(2)(iv), "Any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature (ESF)..."
4571999003 | Braidwood 2 | 05/19/1999 | 12/21/1999 | ML00367283 | <strong>Unit 2 Reactor Trip caused by spiking of Intermediate Range Neutron Flux Channel N36 due to unknown reasons</strong><br /><i>Abstract:&nbsp;</i>At 1917 on 05/19/99, spurious spiking of indication on the Intermediate Range Neutron Flux Channel N36 resulted in a Unit 2 reactor trip. The unit was in reactor startup following a refueling outage when the Reactor Coolant System (RCS) was being diluted to increase reactor power. At approximately 3% reactor power, as indicated by the four Power Range Nuclear Instruments, erratic behavior was noted on the startup rate meter for Intermediate Range Neutron Flux Channel N36. The Main Control Room (MCR) personnel were investigating the erratic behavior when the reactor trip signal occurred. The MCR personnel stabilized the reactor in a shutdown condition using appropriate emergency procedures. All systems functioned as designed. All appropriate notifications were made.
4581999001 | River Bend | 01/15/1999 | 02/01/2000 | ML00368389 | <strong>Inadquate Drywell Air And Suppression Pool Average Water Temperature Surveillance During a Plant Modification of Control Room Recorders Due to Communication Failures and Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On January 15, 1999, with the plant in mode 1, inadequate performance of the suppression pool average temperature surveillance was identified. The inadequate performance occurred during implementation of a Containment Monitoring System (CMS) (*I K*) recorder modification. On the morning of January 11, 1999, the modification removed indication at the Division Il CMS recorders in the main control room but did not affect back panel indication availability. On January 12, 1999, Control Room operators recorded notes on Surveillance Test Procedure (STP)-000-0001, Daily Operating Logs, which noted that Division I I CMS recorders were out-of-service due to the recorder modification. The suppression pool average water temperature surveillance was performed using five indicators available from Division 1. The bases for the surveillance requires the use of all functional indicators . Since the back panel information was not accessed, this resulted in an inadequate surveillance for suppression pool average temperature in that all functional indicators were not used . Upon discovery, the Control Room Supervisor (CRS) directed the operators to use back panel indications. The suppression pool average temperature surveillance was performed properly. During the investigation for the suppression pool average temperature, discovery was made that the drywell average temperature surveillance, SR 3 .6.5 .5 .1, was also incorrectly performed during the modification. These events were not safety significant.
4581999002 | River Bend | 02/04/1999 | 07/15/1999 | 9907220225 | <strong>Discovery of Unanalyzed Air Filters on Containment Unit Coolers</strong><br /><i>Abstract:&nbsp;</i>On February 4, 1999, with the plant in Mode 1 at 92% power, engineering personnel were reviewing the applicability of NRC Information Notice (IN) 99-01, "Deterioration of High-efficiency Particulate Air Filters in a Pressurized Water Reactor Containment Fan Cooler Unit." A condition was discovered that potentially rendered safety-related unit coolers in the primary containment inoperable. It was found that dust filters installed on the unit coolers were not consistent with the Updated Safety Analysis Report (USAR). That discovery was reported in accordance with 10CFR50.72(b)(2) as a condition that alone could have prevented the fulfillment of a safety function. In order to restore compliance with the USAR, the filters were promptly removed from the containment unit coolers. The apparent root cause of this condition is that station personnel, on multiple occasions since before power operations commenced in 1985, did not recognize that unqualified dust filters were installed on the primary containment unit coolers. The filters are not allowed by the USAR to be installed during power operation, and should have been removed at the end of the construction period. Station activities related to design and maintenance of the system conducted since that time presented opportunities to recognize the discrepancy. However, the condition went unnoticed until it was identified in February 1999. While the potentially degraded containment unit coolers may represent a deviation from the analyses reported in the USAR, the limiting case of a loss of heat removal via the containment unit coolers has been demonstrated to result in a maximum containment pressure which does not exceed the design limit. Therefore, this condition is not considered safety significant.
4581999003 | River Bend | 03/24/1999 | 04/25/1999 | 9905030158 | <strong>Division I Diesel Generator Failure Due to Inadequate Reassembly of Fuel Pump</strong><br /><i>Abstract:&nbsp;</i>On March 24, 1999, with the plant at 79% power, the Division I emergency diesel generator exhibited erratic electrical loading during a scheduled surveillance test. An investigation found that the coupling on the engine-driven fuel pump had failed. A review of the maintenance history for the pump coupling found that it had been incorrectly reassembled on February 24, 1999. In this condition, the diesel generator was considered inoperable for the intervening period. The root cause of this event was the failure to adequately stake the fuel pump coupling taper pin during the maintenance activity on February 24, 1999. Also, the work instructions being used did not require the use of sealing compound on the taper pin as specified in a vendor service memorandum. The fuel pump coupling was repaired and the diesel generator was returned to service. An evaluation of the safety significance of this event has found that there was some degradation of defense in depth of systems used to mitigate accidents analyzed in the River Bend USAR. A probabilistic risk assessment found that the event was non-risk-significant.
4581999004 | River Bend | 03/25/1999 | 04/26/1999 | 9904300204 | <strong>Automatic Actuation of Containment Isolation Valve Due to Inadvertent Water Movement</strong><br /><i>Abstract:&nbsp;</i>On March 25, 1999, with the plant at 78% power, an automatic actuation of a primary containment isolation valve (*ISV*) occurred in the suppression pool cleanup (SPC) system. The actuation signal originated at a level transmitter on the reactor steam dryer storage pool in the containment building. A low level in the dryer pool was caused by an inadvertent transfer of water during preparations to vacuum the bottom of the pool. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an event that resulted in the automatic actuation of an engineered safety feature (ESF). This event resulted from a failure to coordinate separate activities of different workers. The actions of two different workers performing different tasks in the preparation to vacuum the dryer storage pool inadvertently established a siphon that transferred water out of that pool. The vacuum attachment on the suction hose was lifted out of the water to break the siphon. The dryer pool was restored to its normal level, and the SPC system was returned to service. The SPC system performs a non-safety function, so its isolation did not impact safe plant operation. The dryer pool has racks for holding fuel during refueling operations, but there was no fuel in the racks. No other nuclear material was in the pool. Had the operator not intervened and the two pools been allowed to equalize, the dryer pool level would have decreased a maximum of two-thirds of the total level difference, or approximately eight inches. Therefore, this event was of no consequence to the health and safety of the public.
4581999005 | River Bend | 02/28/1999 | 05/03/1999 | 9905100127 | <strong>Standby Service Water Pump Inoperable for Greater Than 30 Days</strong><br /><i>Abstract:&nbsp;</i>The standby service water pump 2C was inoperable for 35 days because of an electrical breaker malfunction. A solenoid in the breaker became bound against a brass washer, and thus failed to charge the closing springs, rendering the breaker unable to provide power to the pump. River Bend Technical Specification 3.7.1, "Standby Service Water (SSW) System and Ultimate Heat Sink (UHS)," requires two (of two) SSW subsystems to be operable during MODE 1, 2, and 3 operation. If one pump is inoperable in one SSW subsystem (Action E of Technical Specification 3.7.1), the pump must be restored within 30 days, or the plant must be shutdown. Contrary to this requirement, the standby service water pump 2C was inoperable for 35 consecutive days. This condition is reportable, pursuant to 10 CFR 50.73(a)(2)(i), as operation prohibited by the plant's Technical Specifications. The condition was discovered during a routine operator surveillance, performed weekly, and was corrected within a few days. However, four previous weekly surveillances failed to identify the inoperable breaker, and thus caused the allowed outage time in the limiting condition for operation to be exceeded. The corrective actions will address additional ways to identify the status of this type of electrical breaker. The safety significance of this event is low, due to the availability of the remaining standby service water pumps.
4581999006 | River Bend | 04/06/1999 | 07/15/1999 | 9907210036 | <strong>Unplanned Automatic Standby Service Water Initiation Due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>On April 6, 1999, with the plant in a refueling outage, an automatic initiation of the Division I standby service water (SSW) system occurred during the performance of surveillance testing. The same initiation signal also caused the isolation of motor-operated valves in the reactor plant component cooling water (CCP) system. This event was caused by procedural inadequacy. The valve actuation sequence specified in the test procedure was incorrect. Also, use of the bypass switches to deactivate the automatic start and realignment of the SSW system during the test was not specifically required by the procedure, but left to the discretion of the operator. The CCP and Division I SSW systems responded to the CCP low pressure signal as designed. Operators implemented the appropriate response procedures and restored the systems to their normal alignment within 16 minutes of the automatic actuation. The CCP subsystem being tested was not performing its function to remove decay heat from the spent fuel pool cooling system. Those portions of the CCP system not affected by the realignment to the SSW supply continued to operate as designed. Therefore, this event was not safety significant.
4581999007 | River Bend | 04/10/1999 | 05/10/1999 | 9905180147 | <strong>Tagging Deficiency Resulted in Inadvertent Containment Isolation Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On April 10, 1999, with the plant in Mode 5 (0% Power) for a scheduled refueling outage (RF-8), five containment isolation valves closed as a result of loss of power to an electrical bus during preparation for a bus outage. This inadvertent isolation was reported in accordance with 10CFR50.72(b)(2)(ii) as an automatic actuation of an Engineered Safety Feature (ESF). The root cause of this event was determined to be less than adequate work practices in that RBS personnel did not perform a sufficiently adequate review to identify that the incorrect requirements were included on an equipment clearance. Corrective actions included, in part, restoring the bus power supply to return the valves to the desired configuration, resolution of deficiencies with the clearance, and reviewing other bus clearances to capture lessons learned. In addition, the expectations for reviewing clearances will be evaluated and clarified, as necessary. The plant was shutdown for a scheduled refueling outage and the subject valves shifted to the closed safety function position. Therefore, this event was of no safety significance.
4581999008 | River Bend | 04/18/1999 | 05/18/1999 | 9905270087 | <strong>Unplanned Automatic Closure of Division III Diesel Generator Output Breaker Due to Loss of Normal Power to Division III Switchgear During Testing</strong><br /><i>Abstract:&nbsp;</i>On April 18, 1999, with the plant in a refueling outage, the normal feeder breaker to the Division III standby 4160 volt switchgear unexpectedly tripped during surveillance testing. The Division III standby diesel generator (DG) was already running with its output breaker open as part of the test. The DG output breaker automatically closed in response to the switchgear undervoltage condition. The automatic closure of the DG output breaker in response to the valid actuation signal was as designed, and the DG restored power to the Division III switchgear. The cause of the normal supply breaker trip cannot be positively determined. Given the lack of any identified equipment failure, and considering an identified vulnerability to inadvertently contacting the wrong relay terminations with meter probes during the procedure, the most likely cause of this event is personnel error. The test was suspended, and permanent test jacks were installed prior to resumption of the test. At the time of this event, the reactor pressure vessel head was removed and the reactor cavity water level was greater than 23 feet above the vessel flange. In this condition, no ECCS systems are required to be operable. The HPCS system and Division III DG had been declared inoperable in preparation for testing. This event had no adverse effects on the health and safety of the public.
4581999009 | River Bend | 04/22/1999 | 05/24/1999 | 9906030246 | <strong>Technical Specifications Non-Compliance Due To Inappropriate Action Statement Exit</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1999, with the plant in Mode 5 (Refuel), noncompliance with the Limiting Condition for Operation (LCO) action requirements of Technical Specification 3.7.2, "Control Room Fresh Air (CRFA) System," was identified. LCO 3.7.2 requires two CRFA subsystems to be operable during core alterations or during movement of irradiated fuel in the containment or in the secondary containment. If one CRFA subsystem is inoperable, acceptable alternative actions are identified. However, for about 34 hours from April 20-22, 1999, River Bend Station did not meet the alternative action requirements of LCO 3.7.2. The root cause of the event was determined to be inadequate written communications due to the omission of relevant information requiring over-reliance on user knowledge and skills for the application of Technical Specifications. Prompt actions included restarting the Division 2 CRFA system filter train in the emergency mode, thereby returning to compliance with the action requirements of LCO 3.7.2. To preclude recurrence, licensed operators will receive lessons-learned training on this event. Clarification will also be provided to the procedural requirements for documentation of conditions that must be resolved before equipment is declared operable. This event resulted in no impact to overall plant safety and no impact to the health and safety of the public.
4581999010 | River Bend | 04/28/1999 | 05/28/1999 | 9906150077 | <strong>Inadvertent Breach of Fuel Building Integrity Due to Failure to Self-Check</strong><br /><i>Abstract:&nbsp;</i>On April 28, 1999, with the plant in mode 5 for a refueling outage, Fuel Building integrity was inadvertently lost when door SH-113-01 between the Fuel Building and Annulus was opened for a maintenance activity. The main control room received a Fuel Building high pressure alarm and upon receipt of the alarm, irradiated fuel movement was suspended immediately pending investigation. Investigation revealed the open door between the Annulus and the Fuel Building and the maintenance activity in the Annulus was terminated. The Fuel Building to Annulus door, SH-113-01, was secured. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by Technical Specifications. IEEE Standard system numbers are given by the indication (*No.*). Work practices for failure to self-check was identified as the root cause of this event. The senior reactor operator who authorized the door to be opened has been counseled and an administrative control instituted. Fuel Building ventilation was running in the emergency mode during this event. Due to prompt action to close door SH-113-01 and the immediate suspension of fuel handling, the safety significance of this vent is minimal.
4581999011 | River Bend | 05/10/1999 | 06/09/1999 | 9906150068 | <strong>Division I Diesel Generator Automatic Start and Emergency Core Cooling System injection due to an electrical transient caused by a capacitor failure</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1999, at 1658 with the plant in Mode 5 for a refueling outage, an initiation of the Division I diesel generator (DG) (*EK*) and Emergency Core Cooling System (ECCS) injection into the reactor vessel (RPV) occurred. Main control room (MCR) operators verified reactor cavity level and closed the injection valves to stop the injection. An electrical transient in one of the ECCS power supplies (*JE*) was experienced which caused the initiation of the Division I DG and injection to the RPV via low pressure core spray (LPCS) (BM) and low pressure coolant injection (LPCI) 'A' (*BO*). When the LPCS injection valve (*INV*) was closed, the minimum flow valve (*20*) did not open as expected. MCR operators manually opened the minimum flow valve to provide proper protection for the LPCS pump. Additionally, indication for the LPCI/RHR 'A' injection check valve (*V*) closure failed during the event. The root cause of the electrical transient was determined to be a failed, unsealed capacitor (*CAP*) on a Rosemount trip unit (*PS*) (*JC*). Corrective actions include replacement of the failed trip unit and evaluation of methods to reduce the consequences of similar failures. These events are not safety significant.
4581999012 | River Bend | 05/20/1999 | 06/21/1999 | 9906280283 | <strong>Inadequate Surveillance Testing of Diesel Generator Trip Functions Due To Improper Implementation of Improved Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 20, 1999, with the plant in a refueling outage, an engineering review related to emergency diesel generator operation discovered a potential problem regarding compliance with Surveillance Requirement (SR) 3.8.1.12, as described in the Technical Specification (TS) bases. The specific concern was that the Division I, II, and III diesel generator (DG) differential current trip function circuitry may not have been fully tested. Upon identification of the condition, SR 3.0.3, which allows up to 24 hours to perform a missed surveillance, was applied and test procedures were prepared. When testing of one diesel was not completed within 24 hours, TS Limiting Condition for Operation (LCO) 3.8.2 actions were taken until one DG was fully tested approximately three hours later. Testing of all DGs was completed by May 29, 1999. Three factors were determined to be the causes of this condition:(1) Unclear/complex wording in the TS surveillance requirement that does not clearly discuss actions for the two "essential" trips, (2) Insufficient information in the original TS Bases for DG surveillance testing, and (3) Inadequate change management in the development and implementation of the more detailed information included in the TS Bases for this surveillance requirement.
4581999013 | River Bend | 09/28/1999 | 10/28/1999 | ML99308019 | <strong>Unplanned Automatic Actuation of Primary Containment Isolation Valve During Maintenance Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 28, 1999, with the plant operating at 100 percent power, an unplanned automatic isolation of a primary containment isolation valve in the suppression pool cleanup (SPC) system occurred during the scheduled performance of a preventive maintenance (PM) procedure. The purpose of the PM was to calibrate a containment fuel pool level transmitter. When the transmitter was removed from service using the PM procedure, an unexpected isolation signal was generated which caused the closure of the Division II SPC system suction valve. The isolation valve responded to the closure signal as designed. The root cause of this event was that the responsible design engineers did not revise the loop calibration reports affected by the design of the controls for the containment isolation valve. These reports are used to revise the PM procedure. The lack of relevant information caused the omission of procedural guidance with respect to the expected effects of removing the level transmitter from service. The normal operation of the SPC system is not a safety related function. The safety function of the containment isolation valve is to close in response to predetermined actuation signals, and the valve responded to one of these signals as designed. This event was of no consequence to the health and safety of the public.
4581999014 | River Bend | 10/29/1999 | 11/29/1999 | ML99340026 | <strong>Automatic Reactor Scram Due to Inappropriate Work Activities in the Plant Substation</strong><br /><i>Abstract:&nbsp;</i>On October 29, 1999, with the plant in Mode 1 (Power Operation) at 100 percent power, an automatic reactor scram occurred following a trip of the main generator. Plant systems responded to the event as expected, with the exception of Reactor Recirculation Pump 'A.' (**ADIC2**). This pump tripped from fast speed to "off," failing to downshift to slow speed as expected for this event. The scram is being reported in accordance with 10 CFR 50.73(a)(2)(iv) as an event that resulted in the automatic actuation of the reactor protection system. The cause of this event was the inadvertent initiation of a trip signal in the main generator breaker protective relay circuit (**EL/C38**) by inappropriate work activities in the substation relay house. Contributing to the inappropriate action was poor labeling of the pilot wire terminal boards at the substation. A warning sign identifying the pilot wire cables has been installed at the termination board. The reactor scram signal originated with the closure of the main turbine control valves (**JK/C18**). The event scenario is analyzed by the River Bend Updated Safety Analysis Report. This event was of no consequence to the health and safety of the public.
4581999015 | River Bend | 12/09/1999 | 03/02/2000 | ML00369162 | <strong>Residual Heat Removal 'C' and Reactor Core Isolation Cooling Operability affected by an unsealed wall penetration between their rooms in the Auxiliary Building</strong><br /><i>Abstract:&nbsp;</i>On December 10, 1999, with the plant in Mode 1 at full power, an unsealed penetration in the wall between the Residual Heat Removal (RHR) (*BO*) 'C' and Reactor Core Isolation Cooling (RCIC) (*BN*) rooms in the Auxiliary Building (AB) was determined to impact operability. The condition resulted in the declaration of RHR `C' and RCIC as inoperable. The open penetration has existed since initial plant startup in 1985. The condition is reportable according to 10 CFR 50.73(a)(2)(vii) due to a single fault causing a train in multiple systems to become inoperable and according to 10 CFR 50.73 (a)(2)(i)(B) as operation prohibited by Technical Specifications. The subject penetration was sealed. RHR ‘C’ and RCIC were declared operable after completion of this work. The root cause was determined to be inadequate design documentation RC1C and one train of RHR were potentially impacted by the reported unsealed penetration. Other emergency core cooling systems, including the other two trains of RHR, were not affected. Except for the moderate energy line cracks (MELC) and high energy line breaks (HELB) scenarios, the ability of RHR 'C' and RCIC to respond to other postulated plant events was not impaired.
4581999016 | River Bend | 04/20/1999 | 03/01/2000 | ML00369215 | <strong>Thermally-Induced Accelerated Corrosion of BWR Fuel</strong><br /><i>Abstract:&nbsp;</i>On April 20, 1999, with the plant in Mode 5 for a refueling outage, plant personnel documented an unusually heavy deposition of crud on fuel bundles (*AC*) removed following the preceding operating cycle (Cycle 8). A root cause investigation was performed. The information gathered and conclusions reached during the root cause process are of such relevance to the industry and the NRC that a voluntary report was deemed appropriate. An exact root cause was not identified, but the investigation indicates that multiple factors contributed to an accelerated corrosion of the fuel cladding in the highest-powered fuel bundles during Cycle 8. The heaviest deposition was discovered on the first-cycle fuel. Corrective actions were developed through River Bend's root cause analysis process, and these will aid in preventing recurrence of the crud deposition which induced the corrosion by thermally insulating the fuel rods. Safety significance was evaluated for the increased crud level and for the clad perforations. The significance of the perforations was low, since they are considered in the licensing basis. Significance of the elevated crud level was determined to be acceptable through a process which included engineering judgment, combined with analyses of various plant conditions.
4611999001 | Clinton 1 | 01/29/1999 | 03/01/1999 | 9903100003 | <strong>Improper Assembly of Motor Causes Degradation of Bearings in Two Divisions of Shutdown Service water System</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1999, it was determined that the Division 1 and 2 shutdown service water (SX) pump motors could both have suffered similar upper guide bearing failures prior to fulfilling their design basis heat removal functions. The cause of this event could not be positively identified. The most likely cause of this event was determined to be improper assembly of the bearing thermocouple and bearing insulating gasket. This improper assembly allowed shaft currents to flow to the bearings resulting in bearing damage. The damaged bearings for both SX motors were repaired and reassembled. Corrective actions for this event include: revising vendor manuals and procedures to address shaft current concerns for susceptible motors, evaluating operating and maintenance history for susceptible motors to determine other potentially affected motors, developing a training seminar describing why and how components are insulated to protect against shaft currents and the importance of maintaining the insulating properties, and conducting a briefing to maintenance planners on this issue.
4611999002 | Clinton 1 | 01/06/1999 | 02/04/1999 | 9902100089 | <strong>Offisite Fault on In-Service Offsite Electrical Supply Line Causes Loss of Offsite Power to Safety-Related Electrical Buses</strong><br /><i>Abstract:&nbsp;</i>On January 6, 1999, the plant was in Mode 4, and one of the two transformers that provide offsite power to the safety-related electrical buses was out-of-service for a scheduled outage. A fault occurred offsite on the feed to the in-service transformer, causing a loss of offsite power to the safety-related electrical buses. All three emergency diesel generators started and supplied the safety-related electrical buses. The cause of this event is attributed to a guy wire for an offsite power line pulling out of the ground causing the associated pole to lean. The leaning pole created a fault that tripped the line supplying the only source of power for the transformer that was feeding the safety-related electrical buses. The non-safety related electrical buses were unaffected by this event. Repairs were made to the faulted line, and the leaning support structure. Power was restored to the electrical supply line.
4611999003 | Clinton 1 | 01/18/1999 | 02/16/1999 | 9902260120 | <strong>Manual Reactor Scram Required to Insert a Control Rod Caused by a Failed Transponder Circuit Board</strong><br /><i>Abstract:&nbsp;</i>On January 18, 1999, the plant was in Mode 4 with reactor temperature being maintained between 95 and 115 degrees Fahrenheit and reactor pressure was atmospheric. Control rod venting operations were in progress and the Reactor Mode Switch was locked in Refuel. A failure of the Rod Control and Instrumentation System (RCIS) occurred with control rod 24-17 fully withdrawn at Position 48 (all other control rods were fully inserted). This failure resulted in the inability to move control rod 24-17 through normal means. After investigation of this condition, the Shift Manager determined that the most prudent means for inserting control rod 24-17 was to perform a reactor scram. The Mode Selector Switch was turned to Shutdown and control rod 24-17 was scrammed. The cause for this event was a failure of hydraulic control unit (HCU) 24-17 transponder circuit board. The corrective actions for this event include replacing HCU 24-17 transponder circuit board, and revising procedure CPS No. 3304.02 to provide additional guidance for inserting a control rod when RCIS fails while venting control rods.
4611999004 | Clinton 1 | 01/26/1999 | 02/25/1999 | 9903050404 | <strong>Failure to Understand the Requirement to Consider Single Failure Criteria of the Control Room Ventilation System When Determining Control Room Ventilation System During a Design Basis Accident Leads to the Plant Operating Outside of its Design Basis</strong><br /><i>Abstract:&nbsp;</i>A review of the calculation associated with the radiological dose received by the control room operators following a design basis accident (DBA) determined that the calculation did not consider certain postulated, credible, single failures where manual operator action would be required to manually restart the system. If the current licensing basis methodology is used to determine the main control room operator dose following a DBA while considering the time delay associated with performing a manual restart of the system, the resulting calculation would not demonstrate that the requirements of Criterion 19 of Appendix A to 10CFR50 are satisfied. The cause of this event is that the design did not consider a single failure of the control room ventilation system. The corrective action for this event was to revise the control room operator dose calculation to include an allowance for single failure criteria and the time delay for performing a manual restart of the system, and to submit the results of this calculation and its methodology to the NRC for approval.
4611999005 | Clinton 1 | 09/29/1986 | 03/15/1999 | 9903250388 | <strong>Inoperability of Standby Gas Treatment System Train "A" Caused by Inadequate Design of Control Circuit</strong><br /><i>Abstract:&nbsp;</i>On January 29, 1999, Clinton Power Station (CPS) was in the process of revising calculation 19-AJ-70, "MCC Control Circuit Voltage Requirement," Revision 1. During this process engineers discovered that the in-rush current value used in calculation 19-AJ-70 was incorrect for ITT Barton Actuator NH95 Solenoids. On February 5, 1999, while reviewing this discrepancy, it was determined that circuit 0AP56E-2A did not have adequate voltage to support the circuit's end devices under degraded voltage conditions. This condition could prevent proper operation of Standby Gas Treatment System train "A". A condition report was initiated to investigate and track this issue, and a mode restraint was established to prevent entering Modes 1, 2, and 3 until resolution of this issue. Further evaluation of this condition on February 11, 1999, determined that this condition was reportable per the requirements of 10CFR50.73. The cause of this event is inadequate initial design of circuit 0A56E-2A. The corrective actions for this event include: determining the correct in-rush current for ITT Barton Actuator NH95 Solenoids and revising calculation 19-AJ-70 to reflect the proper in-rush current; upgrading the 480/120 volt alternating current control power transformer for circuit 0AP56E-2A and changing the degraded voltage relay setpoints to support operation of circuit 0AP56E-2A; and performing an extent of condition review to determine what effect a higher in-rush current for ITT Barton Actuator NH95 Solenoids has on other safety-related circuits.
4611999006 | Clinton 1 | 04/19/1999 | 05/17/1999 | 9905250141 | <strong>Containment and Drywell Free Volumes Smaller that Originally Analyzed Due to Inadequate Calculation Control During Initial plant Construction Could Result in Over-Pressure of Containment</strong><br /><i>Abstract:&nbsp;</i>With the plant in COLD SHUTDOWN, engineers discovered discrepancies in the design input parameters for the Containment and Drywell analysis. Specifically the values used for the Containment and Drywell free volumes were found to be slightly smaller than originally analyzed. Bounding analyses performed to determine the effect of the smaller volumes on the accident analysis found that the maximum Containment design pressure could be exceeded for a small line break Loss of Coolant Accident (LOCA) due to possible leakage paths between the Drywell and Containment air space that bypass the pressure suppression capability of the Suppression Pool. When the slightly smaller Containment and Drywell volumes are applied to the analysis using the existing allowable Drywell bypass leakage limit, the maximum Containment design pressure could be exceeded. However, history demonstrates that Drywell bypass leakage has been maintained significantly less than the previously existing allowable limit and the new administrative leakage limit. The cause of this event was inadequate calculation control during initial plant construction. Corrective action for this event includes administratively changing the allowable Drywell bypass leakage limit and validating the design input parameters of the design documents.
4611999007 | Clinton 1 | 05/13/1999 | 06/12/1999 | 9906180044 | <strong>Design Error Causes Main Steam Isolation Valve Leakage Control System to be Outside of its Design Basis</strong><br /><i>Abstract:&nbsp;</i>On May 13, 1999, plant personnel were performing a design basis verification review of the main steam isolation valve leakage control system (MSIV-LCS) as part of an ongoing review. During this review, plant personnel discovered that the "A" inboard MSIV-LCS flow measurement channel was calibrated to an incorrect setpoint that was outside the design basis. The cause of this event is attributed to a design error that occurred when the setpoint for the MSIV-LCS flow measurement channel was determined. Apparently, the engineer applied the instrument uncertainty in an inappropriate direction during the development of the instrument setpoint. The other three MSIV lines were not affected because their identified leakage would have been accommodated by the incorrect setpoint. Corrective action for this event is to revise the setpoint for each MSIV-LCS flow measurement channel to meet the design basis of the plant.
4611999008 | Clinton 1 | 05/14/1999 | 06/12/1999 | 9906180039 | <strong>Failure of the Motor Driven Reactor Feedwater Pump Regulating Valve Results in a Level transient and the Insertion of a Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On May 14, 1999, the reactor was in Mode 2 operation with feedwater being supplied to the reactor vessel by the Motor Driven Reactor Feed Pump (MDRFP). At approximately 0723 hours the MDRFP flow control valve, 1FW004, failed causing a reactor vessel level transient. Control room operators took manual control of feedwater flow but were unable to maintain reactor vessel level. Reactor vessel level increased to the level 8 trip setpoint and the MDRFP tripped on high vessel water level. A manual scram was initiated and all control rods fully inserted. The cause for this event was failure of the 1FW004 valve's hydraulic control system. This failure was due to inadequate written guidance used when performing maintenance on the valve earlier in the year. The corrective actions include: fixing the discrepancies that caused the 1FW004 valve to fail; replacing the hydraulic system fluid with new, filtered fluid; and developing a maintenance procedure for performing maintenance on the valve which will include the lessons learned from this investigation.
4611999009 | Clinton 1 | 06/17/1999 | 07/15/1999 | 9907220067 | <strong>Failure to Properly Classify Containment Penetrations Leads to Failure to Satisfy Secondary Containment Bypass Leakage Rate Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On June 17, 1999, a review of previous containment penetration leak rate tests determined that from March 24, 1995, until September 6, 1996, the secondary containment bypass leak rate exceeded the leak rate limit in Technical Specification SR 3.6.1.3.8. This review was performed as a part of a condition report investigation after it was discovered that six containment penetrations were not classified in the Updated Safety Analysis Report (USAR) as secondary containment bypass leakage paths, and therefore, were not included in the procedure that totaled the combined secondary containment bypass leak rate. The cause of this event is a failure to understand what constitutes a qualified water seal. The containment penetrations identified were configured such that it was interpreted that a water seal preventing leakage outside the secondary containment existed. However, the configuration did not meet the requirements for consideration as a qualified water seal. Corrective actions for this event include revising the USAR and plant procedures to properly reflect the six penetrations as secondary containment bypass leakage paths.
4611999010 | Clinton 1 | 08/09/1999 | 09/08/1999 | 9909140063 | <strong>Inoperability of Division 2 Emergency Diesel Generator Caused By Fuel Leaking Into the Lube Oil</strong><br /><i>Abstract:&nbsp;</i>On August 9, 1999, plant personnel determined that the 16 cylinder Division 2 emergency diesel generator (EDG) had a diesel fuel leak on the fuel return line from the engine's number 12 cylinder. This caused fuel to leak into the lube oil. The leak was at a ball and socket connection on the fuel line. Inspection of the connection revealed that there was damage on the ball end of the connection. The leak was discovered through the use of oil analysis that revealed a decreasing trend in viscosity and flashpoint values of the engine lube oil. The concentration of fuel in the lube oil caused the engine to be inoperable. Based on previous lube oil analysis, the fuel leak has existed since maintenance on the Division 2 EDG was completed on December 18, 1998. The cause and corrective actions for this event will be detailed in a revision to this report.
4611999011 | Clinton 1 | 08/16/1999 | 09/10/1999 | 9909160039 | <strong>Improper Restoration of "A" Average Power Range Monitor Causes Monitor to Not Meet Seismic Qualification Requirements</strong><br /><i>Abstract:&nbsp;</i>On August 16, 1999, during performance of surveillance procedure 9031.12, "Average Power Range Monitor (APRM) Channel Functional," Main Control Room Operators discovered a page for the "A" APRM loose. The page is a hinged rack which holds circuit boards Used in the instrumentation and logic circuitry for the APRM. Due to seismic concerns the "A" APRM was declared inoperable and the Technical Specification Limiting Condition for operation Action Statement for an inoperable APRM was entered. Investigation into this event determined that the "A" APRM page was loose due to not completely engaging the page's latching mechanism following a surveillance performed on the monitor on August 7, 1999. The cause for this event was inadequate knowledge on the importance of completely engaging the page latching mechanism to ensure seismic qualification of the monitor. The corrective actions for this event include verifying that other APRM page latching mechanisms are fully engaged, revising a surveillance procedure to ensure the page is properly latched upon completion and providing training to maintenance personnel.
4611999012 | Clinton 1 | 10/26/1999 | 12/20/1999 | ML99362011 | <strong>Failure of Original Design Supplier to Provide Sufficient Breaker Trip Setting Margin Results in Potential for High Pressure Core Spray Minimum Flow Valve to Fail Open and Less Than Design Flow to Reactor During Loss of Coolant Accident</strong><br /><i>Abstract:&nbsp;</i>Operators were performing a High Pressure Core Spray (HPCS) system valve operability test and the system was inoperable. While stroking the HPCS to Suppression Pool minimum flow valve from the closed position to the open position, operators noted the Main Control Room indicator lights for the valve de-energized and a HPCS power loss status light energized. Local indication showed that the valve stayed in the open position. Operators manually isolated the affected containment penetration and shut the Reactor Core Isolation Cooling (RCIC) System storage tank suction valve to prevent draining the RCIC storage tank. Investigation determined that the breaker tripped during reversal of valve movement from the opening to the closing stroke due to a large inrush current. During a Loss of Coolant Accident the loss of power to the minimum flow valve could result in the failure of the HPCS minimum flow valve to close, providing less than design injection flow to the reactor. The cause of this event is attributed to the failure of the design supplier to provide sufficient margin in the trip setting of the breaker feeding the valve to prevent trips of the breaker from high inrush currents during reversal of valve movement. Corrective actions taken include changing the design trip setting of the breaker feeding the valve and reviewing other potentially affected circuit breakers for similar issues.
4821999001 | Wolf Creek | 01/28/1999 | 05/20/1999 | 9906030345 | <strong>Missed Surveillance Because Valve Was Not Considered Within the Scope of Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On January 28, 1999, Wolf Creek Generating Station (WCGS) personnel identified that Technical Specification Surveillance 4.7.3a had been missed for Component Cooling Water (CCW) valve EGV0105 (CCW to Excess Letdown Heat Exchanger). Surveillance Requirement 4.7.3a requires that unlocked valves be verified in their proper position every 31 days. However, Valve EGV-0105 was not considered within the scope of Surveillance Requirement 4.7.3a and the verification was not included in the initial nor subsequent revisions of the surveillance procedure. The root cause of this event is indeterminate because of the time frame in which the error occurred. Procedure AP 21G-001, "Control of Locked Component Status," which was written in 1980, did not include valve EGV-0105 as a locked component, which resulted in a missed Technical Specification 4.7.3a surveillance. This valve is located inside containment. Corrective actions for this event include locking open of valve EGV-0105, applicable procedure revisions, a review of CCW system valves, and training for operations and Engineering personnel. This event constitutes a reportable event in accordance with 10 CFR 50.73(a)(2)(i)(B). The safety significance of this event was minimal because the valve was verified to be in the proper position and therefore, the systems would have functioned as designed. Supplement 1 Information: On April 22, 1999, during performance of corrective action for LER 1999-001-00, WCNOC identified additional CCW valves that are required to be locked or verified in the correct position every 31 days.
4821999002 | Wolf Creek | 03/12/1999 | 12/28/1999 | ML00367285 | <strong>Testing of Phase "A" (CISA) CTMT Isolation Valves Performed in the Wrong Mode Because the Surveillance Procedure Was not Properly Developed</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1999, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel identified that the Surveillance Test Master Cross Reference identified STS KJ-001A/B, "Integrated D/G Safeguards Actuation Test," as the only procedures that satisfy the testing requirements specified in Technical Specification Surveillance Requirement 4.6.3.2.a. However, procedures STS KJ-001A/B only verify satisfactory movement of a small portion (approximately 10 percent) of the valves associated with a phase “A" isolation signal. The failure to correctly develop STS KJ-001A/B to support Technical Specification Surveillance Requirement 4.6.3.2.a has resulted in WCNOC not fully meeting technical specification testing requirements. This failure resulted in portions of the testing being performed in Mode other than those specified in the technical specification. For example, during the 18 month testing cycle, five (5) Phase "A" slave relay test procedures (affecting 21 valves) were performed in Modes other than 5 or 6. Corrective action ear this event includes revision of the applicable procedures. The safety significance of this event was minimal because operability testing on all of the containment isolation valves was successfully completed during the required 18 month cycle. Supplement 1 information: On June 25. 1999, WCNOC identified that three valve, which were anticipated to have been tested during the recently completed refuel outage had not been tested. The root cause and corrective action sections of the LER have been updated to reflect this information. Supplement 2 corrects the implementation date of procedure revisions to match the WCNOC corrective action plan.
4821999003 | Wolf Creek | 04/09/1999 | 05/10/1999 | 9905170080 | <strong>Source Range Instrumentation Not Tested Prior to Entering Mode 6 due to Inadequate Training</strong><br /><i>Abstract:&nbsp;</i>On Friday, April 9, 1999, at 1002 hours, Wolf Creek Generating Station (WCGS) entered MODE 6 without completing the surveillance requirements associated with Technical Specification 3.9.2, "Instrumentation." To meet Surveillance Requirement 4.9.2.c, procedures STS IC-231A, "Source Range N-31 High Flux At Shutdown ACOT," and STS IC-232A, "Source Range N-32 High Flux At Shutdown ACOT," should have been performed prior to entering MODE 6. A historical search of procedure STS IC-231A identified one other instance where it was not completed prior to entering MODE 6. Additionally, it was identified that on one occasion the seven day retest requirement specified in Surveillance Requirement 4.9.2.c was not met. The Technical Specification violation was caused by inadequate training resulting in an improper assumption being made. Coaching and training are part of the corrective actions for this event. The safety significance of this event was minimal because operability testing of the source range instrumentation was successfully verified upon discovery of the error.
4821999004 | Wolf Creek | 04/12/1999 | 05/12/1999 | 9905180292 | <strong>Failure to Maintain Closure of Containment Penetration During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On April 12, 1999, at 1118, with the plant in MODE 6, Refueling, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel discovered that a direct flow path had been created between the Containment Building atmosphere and the Auxiliary Building during fuel movement. This is contrary to the requirements of Technical Specification 3.9.4.c. The direct flow path was created by a Clearance Order which was placed to support "A" train Residual Heat Removal (RHR) outage work. This event was caused by a series of personnel errors in the implementation of the work control process. Immediate corrective actions included a suspension of fuel movement, verification of all placed Clearance Orders against procedure STS GP-006, "Containment Closure Verification," and closure of valve EJV0154 (which closed the penetration). The safety significance of this event is minimal as: 1) failure to maintain effective Containment closure during the event would not have resulted in a significant release of radioactive material had a fuel handling accident or loss of RHR occurred during this time, and 2) the duration of this condition was short lived.
4821999005 | Wolf Creek | 05/12/1999 | 06/11/1999 | 9906160102 | <strong>Engineered Safety Feature Actuation Because of Loss of Number 7 Transformer</strong><br /><i>Abstract:&nbsp;</i>On May 12, 1999, at approximately 0038 hours, Wolf Creek Generating Station (WCGS) Number 7 Transformer locked out, causing a loss of the East Bus and actuation of "A" Shutdown Sequencer. The fault on Number 7 Transformer caused an under voltage condition on Safeguards Bus NBO1. Emergency Diesel Generator NE01 started on an under voltage signal. The Shutdown Sequencer started and sequenced on applicable loads. Investigation in the switchyard identified a dead raccoon on the ground near the Number 7 Transformer. Investigating personnel determined that the animal had accessed the lightning arrestors on Number 7 Transformer causing the faulted condition. Number 7 Transformer was checked for damage by investigating personnel. No equipment damage was found, and the breaker was reset. The plant's electrical line-up was restored to the normal configuration. Root cause of this event was the intrusion of a raccoon into the switchyard. WCNOC personnel investigated potential avenues to keep small animals out of the switchyard and off of energized equipment. No cost-effective measures were identified to prevent recurrence. The WCGS switchyard has been in operation for over 15 years. WCGS has not had a previous Engineered Safety Feature (ESF) Actuation caused from an animal intrusion in the switchyard. Therefore, no additional corrective actions are considered necessary.
4821999006 | Wolf Creek | 05/24/1999 | 09/15/1999 | 9909210264 | <strong>Procedures Allowed Loss of Containment Integrity Without Entering Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 24, 1999, WCNOC personnel identified that during certain sampling processes of the Post Accident Sampling System (PASS) and Hydrogen Analyzer System, Technical Specification 3.6.1.1 should have been entered. The design is such that a single failure of Solid State Protection System (SSPS) could prevent isolation of the Hydrogen Analyzers. This design feature was not recognized and therefore not translated into administrative controls for certain sampling processes. Supplement I information. On August 27, 1999, it was identified that isolation valves in a second containment penetration had been left open for more than ten hours on at least two occasions in 1996 for (PASS) sampling of the reactor coolant system. The valves in the second penetration have the same design feature regarding the SSPS. The failure to translate Containment Hydrogen Control System (GS) and PASS system design bases into plant procedures is historical, occurring during the construction to operation transition phase. The root cause for the procedure deficiencies therefore, is indeterminate. Corrective actions for this event include revising procedures and training programs that govern sampling of containment atmosphere while at power. Supplement 1 information. These corrective actions will also address the second example found. These events are reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The safety significance of these events are minimal because at no time when the affected penetrations were open did a single failure of SSPS occur, and no radioactive release through these pathways greater than regulatory limits occurred.
4821999007 | Wolf Creek | 05/19/1999 | 06/18/1999 | 9906230118 | <strong>Action Statement #19 of Technical Specification 3.3.2 was Violated, Due to Inadequate Work Practices</strong><br /><i>Abstract:&nbsp;</i>On May 19, 1999, Wolf Creek Generating Station (WCGS) personnel identified a failure to correctly assess the effect of de-energizing of the NBO1 Channel 1 Grid Degraded and Under-voltage Instrumentation power supply on the status of the NBO1 4 KV under-voltage channel. Because de-energizing of the power supply did not result in tripping the under- voltage channel, WCGS Technical Specification 3.3.2, Table 3.3-3, Action Statement #19 for Functional Units 6.f.1 and 8.a, was not met. The causes of this event were identified as inadequate work practices, including a lack of knowledge of the effect of the work activities on the component and a failure to adequately perform verification and validation of the system circuitry. Corrective actions include procedure revision, discussion of expectations with maintenance and Operations personnel, and review of potential generic aspects. There was no impact to the health and safety of the public or to plant equipment as a result of this event.
4821999008 | Wolf Creek | 08/05/1999 | 09/03/1999 | 9909090134 | <strong>Engineered Safety Feature Actuation Because of Closure of 'D' Steam Generator Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>At 1258 hours, Wolf Creek experienced an automatic reactor trip following closure of valve AEFCV-540, 'D' Steam Generator Feedwater Regulating Valve. When the valve closed steam generator level decreased below the reactor trip setpoint of 23.5 percent, initiating a reactor trip. The unit received a feedwater isolation and auxiliary feedwater actuation (both motor and turbine driven) because of the low-low steam generator levels. All control rods fully inserted, and all safety equipment performed as designed. The Reactor Protection System (RPS) and the Engineered Safety Features (ESF) performed as required. The cause of the Main Feedwater Regulating Valve closure was the failure of a Westinghouse 7300 Process Control NCB Group 1 controller card that provides control for the Main Feedwater Regulating Valve for Steam Generator 'D'. The Westinghouse 7300 Process Control NCB Group 1 controller card was replaced. The safety significance of this event has been evaluated and determined to be low. This event is bounded by the current licensing basis analysis as reported in USAR Section 15.2.7. All safety equipment performed as designed and there were no adverse effects on the health and safety of the public.
4821999009 | Wolf Creek | 08/11/1999 | 11/22/1999 | ML99334043 | <strong>Inadequate Fire Separation Could Result in Loss of Charging Water Capability</strong><br /><i>Abstract:&nbsp;</i>On August 11, 1999, while reviewing a Licensee Event Report from another plant, WCNOC personnel determined that volume control tank (VCT) outlet isolation valves EGLCV112B and C, and VCT level transmitters BGLT112 and BGLT185, do not meet 10 CFR 50 Appendix R Section III.G minimum separation criteria for redundant components required for safe shutdown following a fire. Due to the inadequate separation, in the event of a fire, a potential exists for gas intrusion into the suction of the centrifugal charging pump (COP). The preliminary root cause is that the Electrical Fire Hazards Analysis (EFHA), performed in 1984, contained several un-validated engineering judgments regarding safe shutdown equipment. Those judgments were apparently used as the bases for not providing adequate protection for the VCT outlet valves and level transmitters from a fire. Immediate actions taken include establishing a continuous fire watch and implementing procedure revisions to address operator actions to take in the event of a fire in the affected area. Long-term actions are being evaluated. This issue is of low safety significance since the plant could have been placed in a safe shutdown condition even if all the assumed failures occurred. The reported condition is outside Wolf Creek's licensing basis for protection of components required for safe shutdown. However, the plant was not challenged by a fire in the affected fire area. Since compensatory measures have been established, the condition no longer poses a potential threat to the safety of the public, plant personnel, or the plant. Supplement 1 to this LER revises the completion date for the evaluation/design modification related to fire protection of the VCT outlet valves and level transmitters.
4821999010 | Wolf Creek | 08/17/1999 | 09/16/1999 | 9909220199 | <strong>Failure to Perform Technical Specification Surveillance 4.3.3.6 Due to Inadequate Procedure Revision.</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) Surveillance Requirement 4.3.3.6, Table 4.3-7, Item 14, requires that a monthly channel check be performed on the Post Accident Monitoring (PAM) Neutron Flux instruments while in modes 1, 2, and 3. On August 17, 1999, during a review of the Wolf Creek Generating Station (WCGS) Surveillance Test Procedure STS ML-001 "Monthly Surveillance Log", it was determined the PAM Neutron Flux instruments, SE NI-60A, SE NI-60B and SE NIR-61 were not included in the surveillance procedure and that channel checks had not been performed on these instruments during the performance of STS ML-001. The root cause of this noncompliance was the incorrect revision of procedure STS ML-001 when incorporating TS Amendment Number 89. Corrective actions included the correct performance of the surveillance procedure STS ML-001, revision of procedures STS ML-001 and STS CR-001, and review of other procedures affected by changes resulting from TS Amendment Number 89 to assure that no other errors remained unidentified. Subsequent successful performance of the surveillance verified the instruments' operability. There was no safety significance to this event, and the health and safety of the public and plant safety were not affected.
4821999011 | Wolf Creek | 08/20/1999 | 09/17/1999 | 9909240100 | <strong>Missed Surveillance Because the Centrifugal Charging Pump Flow Rate Specified in Technical Specification Was Exceeded.</strong><br /><i>Abstract:&nbsp;</i>On August 20, 1999, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel determined that Wolf Creek Generating Station (WCGS) Technical Specification Surveillance 4.5.2.h.1)b) had not been met for Centrifugal Charging Pump line flow rate. Surveillance Requirement 4.5.2.h.1)b) requires that total pump flow rate be less than or equal to 556 gpm. However, historically the surveillance test that balances Reactor Coolant seal injection and return flow was performed with a procedure that set the seal injection flow in a non-conservative direction. This would exceed the total allowable flow by as much as 2 gpm. The root cause of this event is indeterminate because of the time frame in which the error occurred, but is due to an inadequate procedure. The content and methodology of procedure STS BG-004, "CVCS Seal Injection and Return Flow Balance," resulted in a missed Technical Specification 4.5.2.h surveillance requirement. Corrective actions for this event include revising procedure STS BG004, and reviewing similar system configurations and the associated surveillance procedures. This event constitutes a reportable event in accordance with 10 CFR 50.73(a)(2)(i)(B). The safety significance of this event was minimal because, although the surveillance was not met, the pump flow rate would not have reached run out conditions and therefore would have met its intended safety function.
4821999012 | Wolf Creek | 10/14/1999 | 11/12/1999 | ML99328038 | <strong>Failure to Perform Technical Specification 3.8.1.1, Action b, within the Required Time Limits.</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) Requirement 3.8.1.1, Action b requires that, with one diesel generator inoperable, the licensee demonstrate the OPERABILITY of the offsite A.C. sources by performing Specification 4.8.1.1.1. within one hour and at least once per eight hours thereafter. Wolf Creek Nuclear Operating Corporation (WCNOC) personnel correctly performed this verification up to and including 0525 on October 14, 1999, but failed to correctly perform the verification when it was again due at 1325 hours on October 14, 1999. The verification was subsequently performed satisfactorily at 1430 hours on October 14, 1999. The evaluation performed for PIR 99-3369 determined that this event was the result of a personnel error. The existing tracking mechanisms available for this evolution were not effectively utilized in this instance. In addition, the investigation concluded that involved individuals became distracted by collateral duties. These distractions led to reduced supervisory presence in the Control Room "at the controls” area. Corrective actions included completion of the required action, enhancement of existing aids, and coaching/counseling of involved individuals. This event had minimal plant safety significance, and did not affect the health and safety of the public.
4821999013 | Wolf Creek | 11/16/1999 | 12/16/1999 | ML99363034 | <strong>Missed Surveillance (Technical Specification 4.5.1.1.b) on Accumulator Boron Concentration Verification Due to Inadequate Tracking Mechanism</strong><br /><i>Abstract:&nbsp;</i>On November 16, 1999, a Wolf Creek Nuclear Operating Corporation (WCNOC) Chemistry technician discovered that the accumulator boron concentration on all four accumulators had not been verified since August 26, 1999. The Chemistry Data Management (CDM) system provides worksheets directing performance of this surveillance. The CDM did not perform this function, as expected, to alert Chemistry personnel that the accumulator boron concentration verification surveillance was required. The Chemistry Data Management system was modified in August, 1999. This missed surveillance event is reportable per 10 CFR 50.73 (a) (2) (i) (B) and per NUREG-1022, Revision 1. The root cause is an inadequate tracking mechanism to ensure the Technical Specification surveillance frequency was being met. Boron samples of each accumulator were taken and verified to be within specification limits on November 16, 1999. Verification of completed surveillances was performed, and a manual tracking method was developed to ensure that required surveillances are completed. The manual tracking method will continue to be utilized until the corrective action is complete. The Chemistry Surveillances for Accumulators A, B, C, and D boron will be incorporated into the Surveillance Test Master Cross Reference Database.
4821999014 | Wolf Creek | 12/02/1999 | 12/30/1999 | ML00367383 | <strong>Computer Leak Rate Calculation for Containment Sump Leakage Indication Does Not Meet Design</strong><br /><i>Abstract:&nbsp;</i>On December 2, 1999, during readiness activities associated to conversion to improved Technical Specifications, Wolf Creek Nuclear Operating Corporation (WCNOC) determined that the current computer leak rate calculation for the instrument tunnel sump and the containment normal sumps would not always detect a 1 gpm leak in one hour. The 1 gpm per hour criterion provides the basis for the Technical Specification. Therefore, inability to properly measure reactor coolant leakage constitutes a condition outside the design basis and is reportable per 10 CFR 50.73 (a) (2) (ii) (B) and NUREG-1022, Revision 1. This condition has existed since 1991 when the Nuclear Plant Information System (NPTS) computer was replaced. The software for the replacement NPIS computer was not properly programmed to calculate the leak rate start time. The root cause of the programming error cannot be identified due to the historical nature of the condition. When discovered, the computer point was modified to provide correct indication. Safety significance is minimal since there are other means of detecting Reactor Coolant Leakage.
4821999015 | Wolf Creek | 12/14/1999 | 01/12/2000 | ML00367704 | <strong>Failure to Comply with the Requirements of Technical Specification Limiting Condition of Operation 3.5.2 due to Inadequate Verification</strong><br /><i>Abstract:&nbsp;</i>On December 14, 1999, Wolf Creek Generating Station personnel identified that on February 11, 1999, while Wolf Creek Generating Station (WCGS) was in Mode 1 at 100% power, a combination of maintenance activities resulted in a condition prohibited by Technical Specification 3.5.2 for eight minutes. At the time this event occurred, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel failed to comply with Technical Specification 3.5.2 and also failed to enter Technical Specification 3.0.3, as required. The root cause of this event was inadequate identification of components capable of affecting operability of multiple Emergency Core Cooling System (ECCS) trains and the absence of a programmatic mechanism to prevent activities incompatible with plant conditions from occurring on these components. Corrective actions include review for generic applications and impact, procedure and form revisions, and training. Interim corrective actions include the implementation of operator aids. This event was determined to be of minimal safety significance because there was no loss of safety function.
4821999016 | Wolf Creek | 12/23/1999 | 01/21/2000 | ML00367892 | <strong>Potential for Both Trains of Safety Injection to be Inoperable Due to Erroneous Valve Test Procedure Linup</strong><br /><i>Abstract:&nbsp;</i>On December 23, 1999, Wolf Creek Nuclear Operating Corporation (WCNOC) determined that the procedure line up for the Safety Injection (SI) System Train Inservice Valve Test, in conjunction with an out-of-service SI pump, would have rendered both trains of SI inoperable. Wolf Creek Technical Specifications do not address a condition where both SI trains are inoperable while in Modes 1, 2, or 3; therefore, entry into Technical Specification 3.0.3 was required. An example of this condition was found to have existed on January 6, 1999. This condition is reportable in accordance with 10 CFR 50.73 (a) (2 ) (i) (B) and NUREG-1022, Revision 1. The condition was caused by out-of-sequence procedure steps. The procedure error has been in existence since June, 1984. When discovered, the procedure was corrected to ensure the valve line up does not render SI trains inoperable. Safety significance is based on a large break Loss of Coolant Accident (LOCA). The Wolf Creek Generating Station probabilistic safety assessment does not include any consideration for operation of the SI pumps for event mitigation. Accordingly, there would be no core damage frequency impact due to loss of SI pump function following a large break LOCA. Therefore, the safety significance is minimal.
4831999001 | Callaway | 01/19/1996 | 03/08/1999 | 9903180375 | <strong>Failure to Implement Operating License Amendment 106 Requirements Within 30-day Implementation Period</strong><br /><i>Abstract:&nbsp;</i>During reviews of the implementation process for approved Operating License (OL) Amendments to Technical Specifications (T/S), it was discovered that not all surveillance requirements modified by OL Amendment 106 were satisfied within the allowed 30 day implementation period following amendment approval. Specifically, the flow rate for the "B" train of the Control Room Emergency Ventilation System (CREVS) did not meet the requirements of T/S 4.7.6.c.3 and 4.7.6.e.1 following amendment approval. In addition, "B" CREVS train penetration and bypass leakage testing was not performed at the revised flow rate requirements of T/S 4.7.6.c.1 following amendment approval. The cause of these events was due to a programmatic deficiency which was previously identified and revised to preclude recurrence (LER 98-001). As a result of the above mentioned reviews, OL Amendments issued since January 1, 1993 have undergone reevaluation to verify that operability of plant equipment was maintained upon amendment approval. It was also noted that flow rates greater than T/S 4.7.6.c.3 requirements were accepted during "B" CREVS train flow rate testing following amendment approval. The cause of this event is personnel error. Training will be provided to appropriate personnel to preclude recurrence.
4831999002 | Callaway | 03/09/1999 | 04/08/1999 | 9904140287 | <strong>Missed Technical Specification Surveillance Due To Misinterpretation of Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (T/S) 4.3.2.2 requires Engineered Safety Features Actuation System (ESFAS) response time testing every 18 months. On 3/09/99, Callaway Plant Utility Engineers, while reviewing ESFAS response time test procedures, identified errors in the performance of certain response time test requirements. Response time testing for Steam Generator (S/G) water level low-low initiation of Motor-Driven Auxiliary Feedwater Pumps (MDAFP) actuation and Containment Phase 'A' Isolation (CISA) initiation of Containment Purge Isolation Signal (CPIS) has not been performed completely since initial Plant startup. S/G water level low-low MDAFP and CISA CPIS actuation response time testing incorrectly omitted the Balance of Plant (BOP) ESFAS portion of the response time circuit. This occurred due to misinterpretation of response time test criteria during initial surveillance test procedure development. S/G water level low-low MDAFP and CISA CPIS actuation circuits were tested satisfactorily within 24 hours of identification of this discrepancy. Testing included the BOP ESFAS portion of the circuit. Surveillance procedures were revised to reflect complete response time testing for S/G water level low-low MDAFP and CISA CPIS actuation.
4831999003 | Callaway | 08/11/1999 | 05/01/2000 | ML00371277 | <strong>Manual Reactor Trip due to Heater Drain System Pipe Rupture Caused by Flow Accelerated Corrosion</strong><br /><i>Abstract:&nbsp;</i>At approximately 0917 on August 11, 1999 with the plant operating at 100 percent power, a pipe rupture occurred in a six inch drain line located between the "D" Moisture Separator Reheater first stage reheater drain tank and the "6B" feedwater heater. The reactor was manually tripped and fast closure of the Main Steam Isolation Valves was manually initiated. No personnel were injured during this event and all safety related systems operated per design. Some non-safety related equipment failures were observed for components located in the vicinity of the pipe rupture. The location of the pipe rupture was determined to be immediately downstream of a 45 degree elbow. Root cause analysis indicates that the failure was attributed to Flow Accelerated Corrosion (FAC) with an abnormally high wear rate. The ruptured piping was replaced with Chromium - Molybdenum piping. Additional piping inspections were performed on locations with similar operating conditions/configurations with no other abnormal wear rates observed. Lessons learned from this event will be incorporated into FAC program guidelines for determining inspection points.
4831999004 | Callaway | 08/08/1999 | 09/07/1999 | 9909130045 | <strong>Missed Technical Specification Surveillance Due to Erroneous Procedure Guidance</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (T/S) 4.0.5, In-Service Test (IST) program requires quarterly closure capability testing of BG8497, Chemical Volume and Control System (CVCS) Normal Charging Pump (NCP) Discharge Check Valve. On 8/08/99, Utility Operations personnel discovered surveillance test procedure OSP-BG-V001C, NCP Discharge Check Valves Closure Test did not adequately test closure of BG8497. The procedure was immediately revised and BG8497 closure test was performed with satisfactory results on 8/08/99. The surveillance test was last performed satisfactorily on 2/19/99. This condition was caused by an error in the surveillance test procedure. Operations personnel revising the procedure on 3/17/99 were not aware the revision invalidated BG8497 closure verification results. This event was discussed with Operations department personnel involved in the revision of OSP-BG-V001C. This event will also be discussed with Operations department personnel during retraining classes.
4831999005 | Callaway | 08/12/1999 | 04/17/2000 | ML00370631 | <strong>Operating Conditions Exceeding Previously Analyzed Values Results in Inoperability of Both Offsite Sources</strong><br /><i>Abstract:&nbsp;</i>On August 17, 1999, with the plant in Mode 3 (Hot Standby), switchyard voltage was observed to decrease below the minimum operability limit established in station procedures. During investigations, it became apparent that large amounts of power were being transported across the United States grid. The magnitude of power being transported had not been previously observed concurrent with near peak service territory loads, and it was far in excess of typical levels. This resulted in system conditions above previously analyzed design basis values. It was determined that inadequate administrative controls existed to ensure the station's design analysis encompassed these conditions. Corrective actions taken include:1) Load flow analyses were re-performed, 2) Plant electrical lineup restrictions were implemented, 3) An on line computer program, which models grid conditions given a loss of plant generation, was implemented to monitor offsite source operability, 4) Programs were established to evaluate the grid load flow analysis prior to each peak loading season, and 5 ) Administrative controls were established between onsite and offsite organizations to maintain grid voltages within design basis requirements. Modifications are under development to install capacitor banks and load tap changing transformers to improve voltage regulation to each of the plant's safety related 4.16 kV buses.
4831999006 | Callaway | 08/13/1999 | 09/13/1999 | 9909200087 | <strong>Manual Actuation of Engineered Safety Feature Components Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>10CFR50.72(b)(2)(ii) and 10CFR50.73(a)(2)(iv) require the reporting of any event or condition that results in a manual or automatic actuation of any Engineered Safety Feature (ESF), including the Reactor Protection System (RPS) except when: (A) The actuation results from and is part of the preplanned sequence during testing or reactor operation or, (B) The actuation is invalid. On 8/13/99, with the plant in operating mode 3, hot standby, Utility Licensed Reactor Operators (URO) observed an automatic trip of the startup feedwater pump. The startup feedwater pump was being used to maintain steam generator level. The startup feedwater pump trip resulted from the inadvertent closure of the pump suction valve. URO's responded to the loss of feedwater by starting both motor driven auxiliary feedwater pumps. The motor driven auxiliary feedwater pumps are ESF components. A workman protection assurance (WPA) program tag created in error resulted in the inadvertent closure of the startup feedwater pump suction valve. URO's assigned to WPA generation did not recognize the error at the time the tag was generated or at the time of issue to the field. This event has been discussed with personnel involved. This will be addressed during Operations department training. The plant procedure describing reporting requirements will be revised.
4831999009 | Callaway | 12/03/1999 | 01/10/2000 | ML00367706 | <strong>RCS Leakage Detection Systems are Outside of Design Basis Because a 1 gpm Leak Can Not Be Detected within 1 Hour</strong><br /><i>Abstract:&nbsp;</i>At 1200 CST on 12/3/99, it was identified that the Containment Normal Sump Level Measurement System and Containment Air Cooler Condensate Flow Rate System may not be capable of performing their design function because they could not in all cases detect a 1 gpm leak within 1 hour. This design basis requirement, which is described within the plant1s Final Safety Analysis Report, is derived from Regulatory Guide 1.4.5. These systems are part of the Reactor Coolant System Leakage Detection Systems required by Technical Specifications. They calculate leakage rates by converting a change in sump or standpipe level to gallons, and then dividing this value by the time interval between pump runs or cycling of the standpipe drain valve. If a leak occurs following a long period of little or no leakage, initial calculated leak rates may be low due to the relatively large amount of time between pump runs/valve cycling. Therefore, a 1 gpm leak may not be detected within the 1 hour requirement. The root cause of this event was attributed to a design error from plant startup. Software revisions to the leak detection program were implemented to correct this error and procedures for manually calculating these leakage rates were revised to reflect the revised methodology. Calculations that use similar time-dependent methodology are being reviewed to ensure that similar errors do not exist.
4981999001 | South Texas 1 | 03/11/1999 | 04/12/1999 | 9904220291 | <strong>Residual Heat Removal System Found in a Condition Outside Design Basis</strong><br /><i>Abstract:&nbsp;</i>On February 10, 1999, during review of operating procedures for the Residual Heat Removal System it was discovered that the procedures included no steps or lineups to implement the design basis requirement for the Residual Heat Removal Heat Exchanger Flow and Bypass control valves to be secured in their safe position. Because these valves are assumed to be in their safe position to allow emergency core cooling flow from the Low Head Safety Injection pumps during plant modes 1, 2, and 3 (to support Appendix K requirements), the potential of the nonqualified positioners to misposition the control valves was determined to be outside the design basis. On February 13, 1999, the condition was remedied by opening the disconnect switches per a revision to plant procedures. The root cause of the condition was determined to be inadequate implementation of design requirements. Analysis has shown at this condition would not have prevented the fulfillment of the safety functions needed to mitigate the consequences of an accident. Emergency core cooling acceptance criteria would be satisfied in spite of a random failure of the non-safety positioners. Therefore, the safety significance of this condition was minimal, and there were o resulting adverse safety or radiological consequences.
4981999002 | South Texas 1, South Texas 2 | 03/27/1999 | 04/26/1999 | 9905040170 | <strong>An inadequate performance of Technical Specification surveillance when evaluating source range nuclear instrument discriminator bias curve results</strong><br /><i>Abstract:&nbsp;</i>On March 27, 1999, at 1028 CST, Unit 1 was in Mode 5 preparing for refueling operations. Unit 2 was at 100% power. Both Unit 2 source range nuclear instruments had been declared inoperable based upon an unsatisfactory channel check performed during shutdown of the unit. During a review of source range discriminator bias curve procedures for resolution of the channel check discrepancy, it was discovered that the bias curves in the procedure used to satisfy Technical Specification Surveillance 4.3.1.1.6 were incorrect. The curves in the procedures used for evaluation and comparison were not the initial bias curves as required by Technical Specifications. It was determined that this condition had existed since the source range detectors had been replaced in 1995. A similar condition was found to exist in Unit 2. The cause of this event was the lack of a process to incorporate information regarding establishment of baseline data for Source Range Nuclear Instrumentation. Corrective actions include comparing the discriminator bias curves with initial bias curves for each source range nuclear instrumentation detector in both units, plans to revise the Master Equipment Database for source range nuclear instrumentation to include a requirement to notify surveillance procedure writers regarding impact of obtaining new baseline data and initial discriminator bias curves, and plans to revise surveillance procedures to incorporate the initial discriminator bias curves for source range nuclear instrumentation into data packages.
4981999003 | South Texas 1 | 03/29/1999 | 04/29/1999 | 9905040304 | <strong>Control Room HVAC Placed in Filtered Recirculation Mode of Operation Instead of Being Placed in Recirculation and Make-up Filtration Mode</strong><br /><i>Abstract:&nbsp;</i>On March 29, 1999, Unit 1 was in Mode 6, Refueling. Unit 1 was in a 48-hour action statement per Technical Specification 3.3.2.10.c, Action 27, because the C train battery was inoperable due to maintenance. The control room heating, ventilation and air conditioning was required to be put in the recirculation and make-up filtration mode by 2201 on March 29, 1999. The control room heating, ventilation and air conditioning was placed in the filtered recirculation mode at 2129 on March 29, 1999. This incorrect condition was identified and corrected at 0635 on March 30, 1999. This resulted in a non-compliance with Technical Specification actions, which is a condition prohibited by Technical Specifications per 50.73 (a)(2)(i)(B); and a 24-hour notification is required by section 2G of the Operating License. The root cause of the event was inadequate verbal communications. Corrective actions include briefing crews on attention to detail during three-way communications and covering this event in operator requalification lessons learned training.
4981999004 | South Texas 1 | 05/16/1999 | 06/15/1999 | 9906220274 | <strong>Automatic Reactor Trip Due to a Reactor Coolant Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On May 16, 1999, Unit 1 was operating in Mode 1 at 100% power. At 0452 hours CDT, Unit 1 experienced an automatic reactor trip due to a low flow condition in Reactor Coolant Loop 3 (C). The low flow condition was caused by the trip of Reactor Coolant Pump 1C due to a low voltage condition in the control circuit on 13.8kv switchgear 1H. The undervoltage condition was caused by the degradation of a fuse in a potential transformer circuit. All control rods fully inserted and all systems functioned as required. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. Computer data shows that the potential transformer fuse began to degrade at 0335 on the same day and that at 0452 the potential transformer secondary side voltage reached the setpoint for undervoltage relay 27/A1HB-C. Actuation of the relay tripped Reactor Coolant Pump 1C. The degrading fuse opened completely at 0740 on May 16, 1999. Troubleshooting under a work document found that a fuse on the primary side of the potential transformer on the "C" phase had failed. Repair activities included checking accessible connections, verifying Potential Transformer insulation resistance, verifying fuses in the secondary circuit for proper size and functionality, and installing four new fuses in the primary side of the Potential Transformer. Reactor coolant pump 1C was successfully restarted at 1411 on May 16, 1999.
4981999005 | South Texas 1 | 05/19/1999 | 06/17/1999 | 9907010243 | <strong>Auxiliary Feedwater Train D Inoperable for Greater Than 72-hour Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On May 10, 1999 at 0500 Auxiliary Feedwater Pump 14 ("D" train) was taken out of service for preplanned maintenance. As part of the preplanned maintenance a static diagnostic test was performed on Motor Operated Flow Control Valve D1AF-FV-7526. The operability test for the valve was completed satisfactorily at 2011 on May 10, 1999, and Auxiliary Feedwater Pump 14 was returned to service at 0920 on May 11, 1999. At 1532 on May 13, 1999 the Auxiliary Feedwater Pump 14 Inservice Test was commenced and Auxiliary Feedwater Pump 14 was started at 1610. At 1615, when D1AF-FV-7526 was attempted to be stroked open, the valve failed to open. Auxiliary Feedwater Pump 14 was declared inoperable at this time and Unit 1 entered Technical Specification 3.7.1.2 Action b, which requires the pump be restored within 72 hours or be in at least Hot Standby within the next six hours and in Hot Shutdown within the following six hours. Investigation determined that the "L-Bracket" associated with the open torque switch bypass limit switch (LS-11) for Motor Operated Valve D1AF-FV-7526 had been misadjusted during the preplanned maintenance on May 10, 1999, which prevented the valve from opening under a load. Therefore, Auxiliary Feedwater Pump 14 had been inoperable for a period greater than allowed by Technical Specifications. The cause of this event is less than adequate work instructions for performance of the static diagnostic testing. The procedure instructions did not contain steps to verify continuity of the torque bypass switch after static testing. A contributing factor is a less than desired questioning attitude during performance of a critical work activity. Corrective actions include revising the associated procedure, verification of the open torque switch bypass circuit continuity for eight other valves in which the same static diagnostic test procedure was performed, and discussion of this event with Motor Operated Valve personnel.
4981999006 | South Texas 1 | 06/27/1999 | 07/26/1999 | 9908030135 | <strong>Automatic reactor trip due to an over-temperature delta-temperature actuation</strong><br /><i>Abstract:&nbsp;</i>At approximately 1059 hours on June 27, 1999, Unit 1 experienced an automatic reactor trip due to an overtemperature delta-temperature actuation. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. All systems functioned as required. The plant was stabilized utilizing the Emergency Operating Procedures as expected. The over-temperature delta-temperature actuation resulted from spurious actuation of the main turbine overspeed protection control circuit momentarily causing the main turbine governor and intercept valves to shut. The closing of the main turbine valves removed the primary heat sink from the reactor coolant system and resulted in a rapid increase in average reactor coolant temperature. The root cause of the spurious actuation was a degraded flag-lug connection for the -15 VDC power supply to the printed circuit card racks. Corrective action included re-crimping the failed flag-lug connection.
4981999007 | South Texas 1 | 08/12/1999 | 01/03/2000 | ML00367416 | <strong>Unit 1 Train 'B' Control Room Makeup and Cleanup Filtration System Inoperable for Greater Than Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On August 2, 1999, Unit 1 was in Mode I at 100% reactor power. On July 19, 1999, in accordance with Technical Specification Surveillance Requirement 4.7.7.c.2, carbon samples were removed from the Unit 1 Train `B' Control Room Makeup and Cleanup Filtration System and sent off-site for laboratory analysis. On August 2, 1999 the South Texas Project was notified that the as-found methyl iodide penetration for the makeup and cleanup filter unit samples were 1.62% and 1.13% respectively, which exceeded the required 1.0% Technical Specification acceptance criteria. On August 2, 1999, at 1400 hours, the Train `B' Control Room Makeup and Cleanup Filtration System was declared inoperable, and Limiting Condition for Operation 3.7.7.a was entered, which allowed seven days to restore the train to an operable condition . Maintenance was initiated to replace the charcoal, and on August 5, 1999 work was completed and Train `B' was declared operable. On August 12, 1999, a review of this event concluded that this event was reportable. NUREG-1022. Rev.1, "Event Reporting Guidelines 10 CFR 50.72 and 50.73" provides guidance and clarification to the implementation of the 10 CFR 50.72 and 50.73 reporting criteria. NUREG-1022 Section 3.2.2, "Technical Specification Prohibited Operation or Condition", Discussion Item 3 states: "For the purpose of evaluating the reportability of discrepancies found during TS surveillance tests, an operation or condition prohibited by the TS existed and is reportable if the time of equipment inoperability exceeded the LCO allowed outage time . It should be assumed that the discrepancy occurred at the time of discovery unless there is firm evidence, based on review of relevant information (e .g., the equipment history and cause of failure) to believe that the discrepancy existed previously ." Although Surveillance Requirement 4 .7.7.c.2 allows up to 31 days to obtain charcoal sample analysis results, the allowed outage time for the respective train per Technical Specification 3 .7 .7 is 7 days. The charcoal samples were removed on July 19, 1999, and results were received on August 2, 1999 (14 days later). Replacement of the charcoal was completed and the train was returned to operable status on August 5, 1999. Because the date and time the samples were removed is known, it is assumed for reportability considerations that the discrepancy (methyl iodide penetration values outside the surveillance acceptance criteria) occurred at the time of sample removal, rather than at the time of notification of the charcoal analysis results . Therefore, the Unit 1 Train `B' Control Room Makeup and Cleanup Filtration System was in a condition prohibited by Technical Specifications for approximately 10 days greater than the allowed outage time.
4981999008 | South Texas 1 | 09/12/1999 | 10/12/1999 | 9910200132 | <strong>Turbine Trip While Performing Main Turbine Emergency Trip Test</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1999, Unit 1 was operating in Mode 1 at 100% power. At approximately 0344 the unit tripped during the performance of the Main Turbine Emergency Trip Test procedure. Operators had successfully performed Channel One Low Bearing Oil Pressure, Low Vacuum, and Electrical Overspeed tests. Subsequently, during the Low Stator Cooling Water Differential Pressure test, the operator depressed the "Test Trips" pushbutton, at which time an electrical overspeed trip signal was generated resulting in a turbine trip/reactor trip. The shift crew entered the emergency operating procedures and stabilized the plant. The cause of this event was a failure in the turbine trip test circuitry causing an inadvertent actuation of the electrical overspeed trip. This failure may be attributed to dust and lint contamination of the turbine trip test selector switch. Corrective actions include cleaning the Main Control Board switches in both units, inspecting other panels to ensure any dust and lint was removed, and evaluating the preventive maintenance frequencies of existing main control board cleaning. In addition, STP currently has a task force that is addressing balance of plant equipment reliability and material condition.
4981999009 | South Texas 1 | 04/22/1999 | 11/30/1999 | ML99341020 | <strong>Insertion of Incore Flux Thimbles with Core Altaeration Requirements Not Satisfied</strong><br /><i>Abstract:&nbsp;</i>On April 22, 1999, Unit 1 was in refueling outage 1RE08. At approximately 2100 hours the incore thimbles were inserted into the reactor core after core alterations were suspended. On June 29, 1999, an issue was raised to evaluate whether the insertion of the incore thimbles during 1RE08 constituted a core alteration and whether a reportable event had occurred. It was determined that the event was not reportable based on the fact that the insertion had no reactivity impact, and thus was not considered a core alteration based on South Texas Project's interpretation of the definition of core alterations in the Technical Specifications. During 2RE07 on October 19, 1999, the Nuclear Regulatory Commission (NRC) Resident Inspector questioned the Station's interpretation of the definition of core alterations and the issue was reevaluated. On October 27, 1999, after discussions with the Nuclear Regulatory Commission, the conclusion was made that inserting incore thimbles into the core would be considered a core alteration using the NRC's interpretation. Because the thimbles were inserted in 1RE08 when core alteration requirements were not established, this was a condition prohibited by Technical Specifications. The root cause of the violation of Technical Specifications during 1RE08 was that insertion of the incore flux thimbles was not understood to be a core alteration based on the South Texas Project's interpretation of the definition of core alterations in Technical Specifications. Corrective actions include reviewing the current outage schedule to ensure incore flux thimbles were inserted while core alteration requirements were in place and revising the maintenance procedure for inserting/withdrawing incore flux thimbles to identify movement of incore thimbles as a core alteration.
4991999001 | South Texas 2 | 01/12/1999 | 02/09/1999 | 9902190134 | <strong>Failure to meet the requirements of Technical Specification Surveillance 4.8.2.1d</strong><br /><i>Abstract:&nbsp;</i>On January 12, 1999, Unit 2 was operating at 100 percent power. During a review associated with the qualified life of the A and C train Class 1E batteries, it was determined that the testing performed on the Unit 2B and D train batteries did not meet the requirements of Technical Specification 4.8.2.1d. Technical Specification 4.8.2.1d requires a service test on the Class 1E batteries every 18 months. The service test is a discharge test that demonstrates the ability of the battery to meet the design load profile of the dc system under accident conditions. The records for the Unit 2 Class 1E batteries B and D identified that a performance discharge test had been conducted on each Unit 2 battery in 1995 and 1997 in lieu of the service test. Credit for the service test was taken based on the performance discharge test in accordance with plant procedures. Technical Specification 4.8.2.1e requires a performance discharge test on the Class 1E batteries every 60 months. The performance discharge test is a discharge test that measures the capacity of the batteries against the manufacturer's rated capacity. Technical Specifications only allow a performance discharge test to be performed in lieu of a service test once per 60 month interval. The cause of this event is incorrect interpretation of the Technical Specification surveillance requirements. A review of the Class 1E batteries currently installed in both units confirmed they meet their surveillance requirements. Corrective actions include revising the surveillance procedure to state when a performance discharge test can be substituted for a service test, and reviewing the Technical Specifications to identify surveillance requirements that can be periodically used to take credit for another surveillance requirement.
4991999002 | South Texas 2 | 01/21/1999 | 02/18/1999 | 9903050371 | <strong>Automatic Reactor Trip Due to Loss of Power to the Turbine Control System</strong><br /><i>Abstract:&nbsp;</i>On January 21, 1999, Unit 2 was in Mode 1 at 100% power. At 0607 hours CDT, Unit 2 experienced an automatic reactor trip due to closure of the turbine throttle valves. The throttle valves closed due to a loss of power to the turbine control circuitry resulting from an inadvertent opening of a 120-volt supply breaker. All control rods fully inserted. The Engineered Safeguards Features System actuated the Auxiliary Feedwater System and Feedwater Isolation as expected for a reactor trip. Efforts were underway to isolate a ground on 480-volt Load Center 2G1. The individual performing the ground checks opened breakers in Distribution Panel DP0408 when he should have been in Distribution Panel DP0407. The root cause for being in the wrong panel was inadequate self-verification by the individual. The inadequate verification was due to fatigue and overconfidence in performing an evolution perceived as being low risk. A contributing factor was inadequate guidance for ground isolation. Actions taken or planned in response to the cause of the trip include addressing personnel performance issues with the individuals involved in accordance with the Constructive Discipline Program, reviewing self verification training with plant operators and reactor operators, development of guidance for ground isolation, and guidance for identifying and discussing error-likely situations in pre-job briefings, and training on electrical theory for licensed operators.
4991999003 | South Texas 2 | 03/12/1999 | 04/09/1999 | 9904200098 | <strong>Engineered Safety Feature Actuation and Entry into Technical Specification 3.0.3 Following a Partial Loss of Offsite Power, and Failure to Verify ESF Power Availability per Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 12, 1999, Unit 2 was operating at 100 percent power. Failure of a switchyard breaker resulted in lockout of the 345 KV South Bus, leading to a Loss of Offsite Power signal and Engineered Safety Feature system actuation. The Train B ESF diesel generator output breaker did not close because of a failed cell switch in the Essential Chilled Water system. The cell switch should have been included in a functional check during breaker racking performed on February 28, 1999, but was not. A surveillance to ensure availability of offsite power sources while the Train B ESF diesel generator was inoperable was not performed until the diesel generator output breaker failed to close. With two sources of offsite power unavailable as well as an inoperable diesel generator, Unit 2 entered Technical Specification 3.0.3. The remaining ESF diesel generators were verified as being operable, and offsite power was restored. Exiting Technical Specification 3.0.3 as performed was determined to have been premature because the offsite power source had not yet been connected to the onsite Class 1E bus but was available. Corrective actions include providing additional training on the importance of conducting appropriate functional tests and revising procedures to clarify required actions.
4991999004 | South Texas 2 | 04/06/1999 | 05/05/1999 | 9905130151 | <strong>Power Not Available to Enable Closure of Personnel Air Lock within 30 Minutes Per Technical Specification 3.9.4</strong><br /><i>Abstract:&nbsp;</i>On October 8, 1998, Unit 2 was in a refueling outage. A temporary modification was implemented to provide power to the Reactor Containment Building Personnel Air Lock during a train switchgear outage. However, the modification did not include all components necessary to enable the Instrument Air solenoids to be opened. Consequently, instrument air could not be supplied to the airlock seals to enable door closure within 30 minutes as required by Technical Specification 3.9.4.b. Because the condition was not observed at the time of occurrence, core offload commenced at 1042 on October 9, 1998, resulting in violation of the requirements of Technical Specification 3.9.4. This condition was identified as a result of a similar planned loss of power to the solenoids that occurred during the Unit 1 refueling outage in April 1999. However, core alterations were not performed in Unit 1 while power to the solenoids was not available. Power was restored to the solenoids in Unit 2 on October 10, 1998, when the train switchgear was returned to service. The cause of the power loss was that the temporary modification to provide power to the personnel airlock did not include the basis for the modification as required by procedure, which would have identified the need for temporary power to the air supply valve solenoids. Corrective actions include: adding a reminder to the outage notes that the air supply valves also need to have power supplied to maintain Personnel Air Lock door seal availability during refueling outages; and revising affected electrical prints to more accurately describe the Personnel Air Lock Discussions will be held with affected plant staff to address requests for electrical temporary modifications and use of one-line and elementary drawings when determining affected loads.
4991999005 | South Texas 2 | 08/24/1999 | 09/20/1999 | 9909270199 | <strong>Engineered Safety Feature Actuation Following a Loss of Power to Standby Transformer 2 due to an Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>On August 24, 1999 at 1438, Unit 2 was at 100% power and experienced a loss of power to two of the three 13.8 kV standby busses. The loss of power resulted in the loss of Engineered Safety Features (ESF) 4.16 kV bus E2C. As a result of the power loss to E2C, Standby Diesel Generator (SDG) 23 started and loaded per design. Power was restored to 13.8 kV standby bus 2G, 2H and the ESF busses via Standby Transformer 1. The cause of the event was the failure of the C phase surge arrester on South Texas Project Standby Transformer 2. The failure caused a ground on phase C causing the operation of the C phase differential relay to isolate the transformer. The C phase arrester failure was caused by an internal fault. Corrective Actions include replacement of all surge arresters for Standby Transformer 2 completed September 7, 1999 and replacement of the remaining Westinghouse SMX surge arresters on 1A Main Transformer during Unit 1 Refueling Outage 9 by May 30, 2000.
4991999006 | South Texas 2 | 09/01/1999 | 09/30/1999 | 9910080186 | <strong>Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On September 1, 1999, Unit 2 was operating in Mode 1 at 100% power. At 1521 on September 1, 1999, a reactor pre-trip alarm for steam generator 2D low-low water level occurred and the channel 2 (L-0549) steam generator 2D low-low level bistable status lamp began flashing in the control room. Steam generator 2D low-low level channel 2 was declared inoperable and the channel was placed in a tripped condition as required by Technical Specification 3.3.2, Table 3.3-3, Functional Unit 6.d. The steam generator 2D low-low level channel 2 was untripped at 1949 on September 1, 1999 to determine if the cause could be due to a failed Engineered Safety Features actuation logic circuit. Unit 2 entered Technical Specification 3.0.3 for this condition. The channel 2 input relay to the actuation logic circuitry was determined to be the cause of the failed channel. The actuation logic circuitry was determined to be operable. The failed relay was replaced and steam generator 2D low-low level channel 2 was declared operable at 2055 on September 1, 1999. Unit 2 exited Technical Specification 3.0.3. The cause of the Technical Specification 3.0.3 entry is attributed to insufficient procedural guidance for the use of Technical Specification 3.0.6 as it applies to the ability to return equipment to service in order to demonstrate the operability of other equipment. The failure of the steam generator 2D low-low level channel 2 input relay to the Engineered Safety Features actuation logic circuitry is attributed to "tin whisker" phenomena. Corrective actions include replacement of the failed relay and modification of procedures for responding to the type of condition described in this event report.
4991999007 | South Texas 2 | 10/24/1999 | 11/02/1999 | ML99314029 | <strong>Steam Generator 2C Classified as Category C-3</strong><br /><i>Abstract:&nbsp;</i>On October 24, 1999, South Texas Project Unit 2 Steam Generator 2C eddy current inspection results for the end-of-cycle 7 (2RE07) inspection fell into Category C-3 per STP Technical Specification Surveillance Requirement 4.4.5.2. The NRC was notified within four hours pursuant to 1OCFR5O.72(b)(2) and Technical Specification Table 4.4-2. In most cases, the area of degradation is the tube4o-tube support p1 ate intersections. The cause of the damage, as indicated by the eddy current data (supported by tube pull results from tubes with sirnilar indications at the previous inspection of this unit) is outer diameter stress corrosion cracking (ODS CC). Eddy current inspections were conducted on 100% of in-service tube-to-tube support plate intersections on all four Unit 2 steam generators. As a result of these inspections, a total of 187 steam generator tubes were plugged in the four Unit 2 steam generators. Of these, 162 were plugged due to detected defects, while 25 others were preventively plugged due to the existence of alloy properties preventing eddy current inspection in areas most susceptible to degradation. Of the 162 defective tubes, 152 were plugged due to the detection of distorted support plate indications with bobbin voltage in excess of 1.0 Volts that were subsequently confirmed by plus point inspection. The cause is summarized as the selection of tube material and the design of the tube-to-tube support plate intersection locations. A contributing factor is the high Reactor Coolant System hot leg temperature. All defective tubes identified during the current refueling outage have been plugged. South Texas will evaluate submitting a license amendment for application of the 3-Volt voltage-based repair criteria to Unit 2.
5281999001 | Palo Verde 1 | 03/10/1999 | 04/09/1999 | 9904200382 | <strong>Reactor Trip On HIgh Pressurizer Pressure Due To A Loss Of Heat Removal</strong><br /><i>Abstract:&nbsp;</i>On March 10, 1999 at approximately 1325 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 100% power, when a reactor trip occurred due to a loss of heat removal capability caused by improper operator intervention following a spurious closure of the main turbine control valves. An electrical malfunction caused the main turbine control valves to close decreasing the electrical load on the turbine. The steam bypass control system (SBCS) responded to maintain the loss of heat removal caused by the load shed. The control room supervisor directed the secondary operator to place the SBCS to emergency off which initiated a reduction in heat removal and resulted in a reactor coolant pressure increase to the high pressurizer pressure setpoint, subsequently tripping the reactor. In addition to the reactor trip, the unit received an engineered safety feature actuation system actuation of the main steam system (MSIS) on high steam generator-2 level due to the steam generator-2 economizer valve not staying fully closed and allowing level to reach the MSIS setpoint. At approximately 1335 MST, the unit was stabilized in Mode 3 (HOT STANDBY) and the shift manager classified the event as an uncomplicated reactor trip. All safety systems functioned as required. There were no other safety system actuations and none were required. The preliminary cause of the turbine control valves going closed was a failure of the throttle pressure sensing circuit. An equipment root cause of failure is in progress. The cause of the reactor trip was attributed to supervisory methods that did not ensure sufficient information was collected to support an operational decision. No previous similar events have been reported pursuant to 10CFR50.73.
5281999002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 07/30/1999 | 08/27/1999 | 9909090236 | <strong>Test Mode Trip Bypass for Emergency Diesel Generator Output Breakers Not Surveilled</strong><br /><i>Abstract:&nbsp;</i>On July 30,1999, at 1530 MST, Palo Verde Units 1, 2 and 3 were in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when operations personnel entered surveillance requirement (SR) 3.0.3. The SR 3.0.3 entry was based on an engineering assessment that concluded that surveillance test procedures did not verify that emergency diesel generator (EDG) output breaker test mode trips are bypassed during emergency mode of operation of the EDG. The engineering assessment identified that since April 1, 1996, the bypass function of these trips had been verified during testing performed under a maintenance procedure. Prior to April 1, 1996, testing of the EDG output breaker test mode bypass trips had not been performed. A plant review board was convened to review the condition and after examining the six most recent performances of the maintenance testing results (two from each unit), it was determined that surveillance requirements had been met by the maintenance procedure. Prior to April 1, 1996 however, the bypass trips had not been tested in accordance with technical specification requirements. At approximately 1640 MST, on July 30, 1999, operations personnel exited SR 3.0.3 for the missed surveillances. A previous similar event was reported in LER 50-528/97-006-00.
5281999003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 03/17/1999 | 04/14/1999 | 9904220205 | <strong>Required Surveillance Requirement Not Completed Due to Deficient Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 17, 1999, with Units 1, 2, and 3 operating in Mode 1 at approximately 100 percent power, Engineering personnel determined that the test procedures used to meet the essential chilled water system valve verification Technical Specification surveillance requirement were not adequate. The procedures did not properly verify that the oil cooler outlet valve for each chiller was in the correct throttled position to ensure the essential chillers would operate when called upon. The procedural deficiency had existed since the procedures were initially implemented. The Unit 3 oil cooler outlet valves were only affected by the procedure deficiency prior to January 1997. The Unit 3 valves were locked in January 1997 and were then not required to be verified. The cause of the deficient procedure was determined to be cognitive personnel error. The Unit 1 and 2 test procedures have been revised to require the chillers to be started and oil temperature checked to verify the oil cooler outlet valves are in the required throttled position. Previous events reported in the last three years related to missed surveillance requirements did not have similar causes to this event.
5281999004 | Palo Verde 1 | 09/11/1999 | 10/07/1999 | 9910140027 | <strong>Missed Required Actions for Inoperable Instrument Channel Caused by Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On September 12, 1999 at approximately 0700 MST, with Unit 1 operating in Mode 1 (Power Operation) at approximately 100 percent power, Operations personnel determined that a Technical Specification (TS) non-compliance had occurred on September 11, 1999. The non-compliance was for not placing a Plant Protection System channel for Steam Generator 2 Wide Range Level into bypass or placing the unit in Mode 3 after a TS required channel check had indicated that the difference between two of the four steam generator wide range level channels exceeded the acceptance criteria. The channel check had been completed on September 11, 1999 at 0943 however, the performer and reviewers did not recognize the out-of-tolerance condition and no action was taken. A subsequent review of the performance of the four channels of level indication determined that the channel deviation was the result of the methodology used in taking the readings and was not an accurate indication of channel performance. As a conservative action channel B was placed into bypass on September 12, 1999 at 0738 MST pending further investigation. The channel was determined to be functioning properly and was restored on September 13 at 1633 MST. No similar occurrences have been reported to the NRC in the last 3 years
5281999005 | Palo Verde 1 | 09/22/1999 | 10/19/1999 | 9910290168 | <strong>Main Steam Safety Valve Lift Pressures Outside of Technical Specification Limits Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On September 22, 1999, during lift pressure verification testing conducted in accordance with surveillance procedure requirements, two (of twenty) Unit 1 main steam safety valves (MSSVs) were identified as having as-found settings which were outside of the Technical Specification limits of +/- 3 percent of design lift pressure. The out of tolerance as-found MSSV condition appears to be the result of setpoint drift. The affected Unit 1 valves were adjusted and retested in accordance with procedure requirements and were returned to service on September 22, 1999. APS engineering has implemented an augmented testing program to gather additional data on MSSV performance and is evaluating industry operating experience for actions that may assist us in improving MSSV performance and reliability. Previous similar events have been reported in LERs 50-529/99-002, 50-530/98-003, 50-528/98-004, 50-529/97-001, and 50-530/97-003.
5281999006 | Palo Verde 1 | 10/02/1999 | 10/29/1999 | ML99314035 | <strong>Reactor Coolant System Pressure Boundary Leakage Due to Degraded Alloy 600 Instrument Nozzle</strong><br /><i>Abstract:&nbsp;</i>On October 2, 1999, at approximately 0300 mountain standard time, Unit 1 was in Mode 3, Hot Standby, cooling down for a refueling Outage when engineering personnel, who were performing a routine boric acid walkdown, discovered a small accumulation of boric acid residue on a reactor coolant system loop 2 hot leg instrument nozzle. The boric acid had accumulated on the exterior of the hot leg piping around the outer perimeter of the instrument nozzle. The nozzle was visually inspected during the last refueling outage in March of 1998 and no leakage was identified at that time. Visual inspections of other Alloy 600 hot leg nozzles have not identified other degraded components. The nozzle has been repaired and testing will be completed during startup (Mode 3) at normal operating pressure and temperature. The remaining Alloy 600 hot leg nozzles in all three units are scheduled to be replaced during future outages. No previous similar events have been reported pursuant to 10CFR50.73 in the past three years.
5281999007 | Palo Verde 1 | 10/19/1999 | 11/18/1999 | ML99334003 | <strong>Half-Leg ESFAS Actuation Due To Loose Power Supply Jumper</strong><br /><i>Abstract:&nbsp;</i>On October 19, 1999, at approximately 0049 mountain standard time (MST), Unit 1 was in the eighth refueling outage, in Mode 6 with the core off-loaded to the spent fuel pool, when a momentary loss of power to a portion of the train A engineered safety feature actuation system (ESFAS) auxiliary relay cabinet occurred. The momentary loss of ESFAS power caused the train A emergency diesel generator (EDG) to start and actuated many train "A" components to a post safety injection actuation. The train A ESFAS actuations reset within one second of initiation and the effected equipment had been restored by approximately 0128 MST on October 19, 1999. Preliminary investigation results indicate that a loose input power selection jumper on an ESFAS power supply was the cause of the event and the faulty power supply was replaced. A previous similar event was reported in LER 50-529/97-005-00.
5291999001 | Palo Verde 2 | 01/03/1999 | 03/01/1999 | 9903110117 | <strong>TS Violation for Power Dependent Insertion Limit Alarm Inoperable Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 31, 1999 at approximately 0219 hours MST with Unit 2 operating at approximately 100 percent power, operations personnel discovered that the Power Dependent Insertion Limit (PDIL) alarm was INOPERABLE. This alarm is computer generated and is used to alert the operators to a condition in which the regulating Control Element Assemblies (CEA) may be outside the required insertion limits. The alarm had last been tested satisfactorily on January 3, 1999. However, on restoring from the test the circuit was left in a condition that prevented it from performing its function. When discovered on January 31, the Technical Specification Required Action for the PDIL circuit was completed within the required time limit and all regulating CEA group positions were verified to be within insertion limits. The PDIL alarm was returned to OPERABLE status at 0342 MST on January 31, 1999. The cause of the INOPERABLE alarm was attributed to personnel error in that control room personnel did not recognize the computer was not placed back into the scan mode of operation following the completion of the alarm testing performed on January 3, 1999. As corrective action the procedure has been revised to clarify how the computer point is to be returned to the scan mode. No similar events have been reported pursuant to 10CFR50.73 during the last three years.
5291999002 | Palo Verde 2 | 03/18/1999 | 04/19/1999 | 9904270238 | <strong>Main Steam Safety Valve Lift Pressures Outside of Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On March 18, 1999, prior to Unit 2's eighth refueling outage, lift pressure verification testing was completed on the Main Steam Safety Valves per surveillance procedure requirements. The testing revealed that as-found lift pressures for four Unit 2 MSSVs were outside of the Technical Specification limits of +/- 3 percent of design lift pressure. The out of tolerance as-found MSSV condition appears in some cases to be the result of the valve disc bonding with the nozzle seat and in some cases the result of setpoint drift. APS engineering has implemented an augmented testing program to gather additional data on MSSV performance. Concurrently, APS is evaluating industry operating experience for actions that may assist us in improving MSSV performance and we may implement additional actions if they can be demonstrated to be effective. Previous similar events have been reported in LERs 50-530/98-003, 50-528/98-004, 50-529/97-001, and 50-530197-003.
5291999003 | Palo Verde 2 | 03/26/1999 | 04/25/1999 | 9910150169 | <strong>Unit 2 Spent Fuel Assembly Stored in Wrong Location</strong><br /><i>Abstract:&nbsp;</i>On March 26, 1999, at approximately 1139 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 92 percent power, when reactor engineering personnel notified operations that fuel assembly P1B241, which was stored in the spent fuel pool (SFP) region 3, location C36, should have been placed in region 2 of the SFP based on the initial enrichment and assembly burn-up factors. The assembly was stored in this region from approximately August 27, 1997 to March 26, 1999. Operations personnel entered Technical Specification (TS) 3.7.17 condition A, to restore the fuel assembly to the correct SFP region. On March 26, 1999 at approximately 1727 MST, the fuel assembly was moved and secured in SFP region 2, location S01. An engineering evaluation determined that there was not an immediate safety concern with respect to reactivity control in that Keff remained less than 0.95. The evaluation concluded that up to four new 4.3 percent enriched assemblies can be placed incorrectly in a 4/4 configuration with 2150 PPM boron, and Keff would remain less than or equal to 0.95. The preliminary cause of the misplaced assembly was due to personnel error in preparing the material balance area transfer form set, which was also not detected by independent verification. No previous similar events have been reported pursuant to 10CFR50.73.
5291999004 | Palo Verde 2 | 04/08/1999 | 05/07/1999 | 9905190030 | <strong>Pressurizer Safety Valve Lift Pressures Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On April 8, 1999, during Unit 2's eighth refueling outage, lift pressure verification testing was completed on the Unit 2 pressurizer safety valves (PSVs). The testing revealed that as-found lift pressures for two of the four Unit 2 PSVs were outside of the Technical Specification limits of +3/-1 percent of design lift pressure. The out of tolerance as-found PSV condition appears to be the result of lift pressure setpoint drift. An analysis of the safety consequences of the Unit 2 as-found PSV testing results is being conducted in accordance with PVNGS procedures. The preliminary analysis results indicate this condition would have no effect on the consequences of UFSAR chapter 15 events and additional safety analysis. Within the last three years, one previous similar event was reported in LER 50-528/98-004.
5291999005 | Palo Verde 2 | 06/18/1999 | 07/16/1999 | 9907280252 | <strong>Reactor Trip on Low DNBR</strong><br /><i>Abstract:&nbsp;</i>On June 18, 1999, at approximately 2229 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when an automatic reactor trip occurred on low Departure from Nucleate Boiling Ratio (DNBR). The four Core Protection Calculators (CPC) generated a reactor trip on low DNBR due to CPC sensor failures. By approximately 2245 MST, the reactor was stabilized in Mode 3 (HOT STANDBY). The Shift Manager classified the event as an uncomplicated reactor trip. No engineered safety feature actuations occurred during the event and none were required. Required safety systems, including Steam Bypass Control, responded to the event as designed. Although additional investigative activities remain to be completed, the cause of the reactor trip appears to be a hardware induced calculation error that resulted in an erroneous penalty factor being generated in control element assembly calculator (CEAC) #2. A previous similar event was reported in LER 50-529/94-006-00.
5291999006 | Palo Verde 2 | 07/21/1999 | 08/20/1999 | 9909090170 | <strong>Reactor Protection and ESFAS Instrumentation Not Bypassed Within One Hour Required by TS</strong><br /><i>Abstract:&nbsp;</i>On July 21, 1999 at approximately 14:10 MST, Palo Verde Unit 2 was in Mode 1 (power operations), operating at approximately 100 percent power, when it was discovered that from July 15, 1999 to July 21, 1999, the seismic fasteners were not engaged on the PPS channel D bi-stable control panel drawer, rendering the drawer inoperable. TS require that inoperable PPS channels be placed in bypass or tripped within one-hour. The cause of the event is attributed to personnel error for not adequately reinstalling the seismic fasteners after the performance of a quarterly surveillance test. As corrective action, maintenance personnel were coached on the expectations for system restoration following surveillance and maintenance testing. A previous similar event was reported in LER 50-528/98-001-00.
5301999001 | Palo Verde 3 | 01/25/1999 | 02/24/1999 | 9903080022 | <strong>Loss of Automatic Closure for Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 23, 1999 at approximately 0108 MST, Palo Verde Unit 3 was in Mode 1 (power operations), operating at approximately 100% power, when APS control room personnel (licensed operators) identified that inboard containment hydrogen control supply isolation valve (3JHPAUV0001) failed to close as required by Technical Specification (TS) 3.6.3. The condition was discovered during the performance of A train, ESFAS subgroup relay surveillance testing 36ST-9SA01-3. Operations personnel declared the valve inoperable and entered "Condition A" of LCO 3.6.3. On January 23, 1998, at approximately 03:01 MST, control room personnel (licensed operators) isolated the affected penetration flow path by de-activating the automatic function for the outboard hydrogen control supply isolation valve (3JHPAUV0003) for compliance with Action Al of LCO 3.6.3. Subsequent troubleshooting efforts were conducted and on January 25, 1999 at approximately 1530 MST, maintenance personnel (utility non- licensed) discovered that 3JHPAUV0001 was incorrectly wired and was not discovered by retest. On January 25, 1999, at approximately 2218 MST 3JHPAUV0001 was declared operable. This event is being reported as a condition prohibited by Technical Specification and a condition that was outside of the design basis of the plant from October 22, 1998 at 0301 MST to January 23, 1999 at 0301 MST. The cause of the event is attributed to personnel error for inadequate documentation, performed with second party verification, during the wiring determination which resulted in incorrect wiring re-termination. In addition, the post maintenance retest did not include a functional test of the containment isolation actuation signal (CIAS) circuitry. No previous similar events have been reported pursuant to 10CFR50.73.