## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
0292001001 | Yankee-Rowe | 06/26/2001 | 08/22/2001 | ML01239009 | <strong>Spent Fuel Pit Area Radiation Monitor Alarm Setpoint Set Above Limit Allowed by Technical Specification 3.3</strong><br /><i>Abstract:&nbsp;</i>Yankee Nuclear Power Station ceased power operation in February 1992 and is being decommissioned. On 06/26/01 during the conduct of a Nuclear Safety (Quality Assurance) Audit a discrepancy regarding the alarm setpoints for the Spent Fuel Pit (SFP) Area Radiation Monitor (ARM) was identified. The SFP ARM is an instrument required by Technical Specification 3.3 to ensure early detection of inadvertent criticality during fuel handling activities. The Technical Specification requires the alarm setpoints for the ARM be set at less than 5 mr/hr or two times the background radiation level, whichever is greater, while moving irradiated fuel, control rods or sources. The discrepancy identified was that the background radiation level annotated on procedure OP-4816, "Functional Test and Alarm Setting of the Area Radiation Monitoring System" was 2 mr/hr while the alarm setpoint for both the alert and high alarms was set at 7 mr/hr, thus greater than the Technical Specification requirement. As such, this LER is submitted in accordance with 10CFR50.73(a)(2)(i)(B) as a condition of non-compliance with a Technical Specification. No fuel handling evolutions were in progress at the time of discovery of this issue.
2192001001 | Oyster Creek | 11/12/2001 | 01/07/2002 | ML02032003 | <strong>Completion of Reactor Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2001, a 4160 VAC cable failure de-energized the 1B2 Unit Substation of the 480 VAC system. Due to the equipment which was declared inoperable, it was determined that a reactor shutdown would be required. On November 12, 2001, at 3:33 am, the reactor was placed in the COLD SHUTDOWN CONDITION. The cause of the cable failure was determined to be a localized insulation weakness aggravated by water intrusion into the cable conduit. The safety significance of this occurrence was determined to be minimal. Although the 1B2 Unit Substation of the 480 VAC system was lost, the redundant electrical division remained fully operable at all times. At no time during this event did a functional failure of any safety system occur. The plant remained within Technical Specifications limits at all times, and achieved a COLD SHUDOWN CONDITION within the allowed time limits. The failed portion of the cable was replaced, the plant was restarted and resumed POWER OPERATION. Long term actions include evaluating a new design cable and possible rerouting of the cable run.
2202001001 | Nine Mile Point 1 | 08/22/2001 | 10/22/2001 | ML02016023 | <strong>Reactor Scram Due to Failure of Generator Protective Relay</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2001 at 0508 hours, Nine Mile Point Unit I experienced an unplanned scram due to a generator trip from approximately 100 percent power. The reactor was operating at steady state conditions prior to the scram. The Immediate cause for the generator trip was actuation of the Negative Phase Sequence Current Relay in response to a grid perturbation. All control rods fully inserted. In response to the generator trip, reactor pressure rose to 1115 pounds per square inch gage (psig). The increase in pressure resulted in all six Electromatic Relief Valves (ERVs) opening briefly, as designed. Approximately 37 seconds post scram the Main Steam Isolation Valves (MSIVs) automatically closed due to the mode switch being in RUN and reactor pressure at 850 psig, Approximately six minutes after closing, the MSIVs were re-opened. The cause of the generator trip was a grid perturbation coupled with a malfunction of the Negative Phase Sequence Current Relay. The relay malfunction was due to a design flaw. A contributing cause was failure to utilize previous external operating experience. The MSIV closure was caused by lack of specific direction regarding when the mode switch should be taken to SHUTDOWN post scram. Corrective actions included replacing the relay with one of a new design and briefing the operating crews of the management expectation that the first immediate action after a scram is to place the mode switch in SHUTDOWN. Preventive action will involve reviewing General Electric Operating Experience not previously evaluated.
2202001002 | Nine Mile Point 1 | 09/07/2001 | 11/06/2001 | ML02058031 | <strong>15 Kilovolt Line 4 Inoperable Due to Inadequate Analysis of Design Change</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2001, at 2040 hours with Nine Mile Point Unit 1 (NMP1) at approximately 100 percent power, 115 kilovolt (kV) Line 4 was declared inoperable. Technical Specification 3.6.3.b Limiting Condition for Operation (LCO) was entered, allowing continued operation for seven days with Line 4 inoperable. Two 115 kV offsite power sources, Line 1 and Line 4, serve NMP1. The Technical Specification Bases 3.6.3/4.6.3 state that either line can provide the power required for a Loss of Coolant Accident (LOCA). On September 7, 2001, Niagara Mohawk Power Corporation (NMPC) determined that Line 4 could not provide the power required for a LOCA when Line 1 is out of service. The voltage on Line 4 during a unit trip with a LOCA, with Line 1 out of service, would decrease and actuate the Degraded Voltage Relays (DVR) transferring the Unit 1 Emergency Core Cooling System (ECCS) loads to the diesel generators. The voltage decrease is due to the additional load applied during a unit trip with a LOCA as compared to normal plant operation. On September 12, 2001, at 1803, Line 4 was returned to operable following tap changes to reserve station service transformers XF-101 N and XF-101 S and procedure changes to boost Line 4 voltage and secure non-essential loads when Line 1 is inoperable. The cause of the inoperability of Line 4 was inadequate review of the design change installed in March of 1995 that raised the DVR setpoints. Contributing causes were inadequate consideration of design basis and inadequate communications between NMPC Power Control, the offsite organization that maintains voltage on the 115 kV lines, and NMP1 Design Engineering. Detailed requirements were not provided to Power Control, and NMP1 Design Engineering failed to verify that Power Control could maintain sufficient Line 4 voltage with Line 1 out of service. Corrective actions include tap changes to reserve station service transformers XF-101 N and XF-101 S, implementing the Power Control State Estimator Program for monitoring 115 kV bus voltage, and procedure changes to address Line 4 voltage concerns when Line 1 is out of service. Additionally, more rigorous design and review processes have been implemented since 1995.
2372001001 | Dresden 2 | 12/21/2000 | 01/19/2001 | ML01029010 | <strong>Primary Containment Isolation System Valve Adjusted During VOTES Test with No LLRT Performed</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2000, during the performance of a plant work request, "VOTES" testing was performed on Motor Operated Valve (MOV) 2-1402-25B in accordance with appropriate plant procedures. During the performance of this test the closing torque switch setting on this MOV was raised, resulting in an increase in thrust of about 20.4%. This change in torque switch settings resulted in the valve becoming inoperable due to the fact that a change in the torque switch setting of this magnitude potentially affects the leakage rate of the valve. On December 21, 2000, the MOV Engineer identified that Local Leakage Rate Testing (LLRT) had been performed on this MOV in the past. The engineer immediately recognized that this MOV had recently been adjusted on December 19, 2001, and suspected that no LLRT had been performed. Subsequent investigation revealed that the As Found and As Left LLRT required by the 10CFR50 Appendix J, "Primary Reactor Containment Leakage Testing for Water-Cooled Power Reactors", program had not been performed. The 2-1402-25B was declared inoperable, and Technical Specification (TS) 3.7.D was entered. The 2-1402-25B MOV was then re-tested and returned to the previously established seating force. This eliminated the need to perform an As Left LLRT for this MOV. The MOV was then returned to service, and the LCO exited. Corrective actions include, the valve being re-tested, and returned to the previously established seating force, a review of the current schedule was performed to verify that no work packages will perform thrust adjustments to 10 CFR 50 Appendix J, "Primary Reactor Containment Leakage Testing for Water-Cooled Power Reactors", valves without the LLRT requirements being addressed and revise appropriate VOTES procedure to include LLRT allowable thrust adjustments to Appendix J MOVs.
2372001002 | Dresden 2 | 04/03/2001 | 06/04/2001 | ML01162011 | <strong>Manual Reactor Scram Due to Reactor Recirculation Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2001 at 2008 hours, the 2B Motor Generator (MG) Set tripped causing a 2B Reactor Recirculation (RR) pump trip due to a loose connection in the control circuit in the operating oil pump (2B1) Motor Control Center (MCC) cubicle. This resulted in the plant being placed in single loop operation with the 2A RR pump in service. Approximately four hours after trip of the 2B MG Set, a bearing oil filter high differential pressure (dP) caused a trip of the 2A RR MG Set on low bearing header oil pressure. Operations observed the 2A breaker had tripped and manually inserted a reactor scram at 2358 hours per station procedures. The oil system was found to be contaminated with non-metallic particulate. An investigation of the MG Set oil system did not identify any material in the system design that could have been the cause of the contamination. The root cause for the multiple trips of the MG Sets is the inadequate design of the system circuitry that does not provide for automatic starting of the non-operating (standby) oil pump when the running oil pump trips. Corrective actions to prevent recurrence include revising the MCC bus and MCC cubicle model work orders, preventative maintenance work orders, and associated procedures to address tightening of the stationary terminal block female clips and wire terminations during bucket and bus maintenance, Review and revise as necessary the FME procedures used on RR MG Set coupler and cooler maintenance to provide more rigorous controls, install the auto start modification for the oil pumps in Unit 2 in D2R17, and Operations to institute practice of periodically rotating equipment (pumps, coolers) on oil systems to ensure reliable operation, including comprehensive monitoring practices (pressure, flow, oil sampling, etc.) following equipment swaps. The safety significance of this event has been determined to be minimal.
2372001003 | Dresden 2 | 09/02/2001 | 10/31/2001 | ML01365039 | <strong>Failure of Recirculation Pump Discharge Valve to Close Causes LPCI Inoperability</strong><br /><i>Abstract:&nbsp;</i>On September 2, 2001, the 2B Recirculation Pump Discharge Valve, 2-0202-5B, did not close upon demand. Troubleshooting revealed a normally closed auxiliary contact stuck open, which prevented the valve from closing. In the event of a Loss Of Coolant Accident (LOCA), the Low Pressure Coolant Injection loop select logic determines the appropriate recirculation loop for injection based on differential pressure sensed between the "A" and "B" loops. If, during a LOCA, the "B" loop would be selected for injection, a signal would be sent to the "B" discharge valve to close, allowing the injection path to be completed through the jet pumps and into the core. Thus, with the "B" discharge valve open, full injection into the core would not be achieved. Therefore, this event is being reported pursuant to 10 CFR 50.73 (a)(2)(v)(B) and (D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat or mitigate the consequences of an accident. Maintenance freed the stuck contact and the valve was subsequently stroked twice. During repair, an auxiliary contact plunger arm was found to be off its normal plastic stop, which caused the contact to bind. A new auxiliary contact assembly including the lock washer on the plunger arm was installed and successfully tested with no evidence of binding. The cause of the failed plunger arm was a loosened plunger post due to a missing lock washer. The root cause of this event was determined to be inadequate procedural guidance, which led to equipment failure. The auxiliary contact plunger post was found not to have a lock washer installed. The station procedure does not clearly direct that the plunger post be verified tight or to check for the installation of a lock washer. The safety significance of this event has been determined to be minimal.
2372001004 | Dresden 2 | 10/21/2001 | 12/20/2001 | ML02043002 | <strong>Unit 2 Torus High Water Level Switches Failed Calibration Surveillance Due to Historical Poor Post-Modification Testing and Overly Conservative Technical Specification Allowable Value</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2001 during the performance of surveillance testing for the Torus high water level switches, the "As Found" condition of both Unit 2 Torus high water level switches were outside of the Technical Specification (TS) Allowable Value (AV). The Torus high water level switches automatically realign the High-Pressure Coolant Injection (HPCI) system suction to the Torus. The risk to the station was minimal, as the switches would have operated below the limits for safety relief valve operation specified in the General Electric calculations. The setpoints for these switches were configured by a modification in 1985. This modification did not test the effect of the modification on the setpoints. Post Modification Testing (PMT) issues were historical in nature. The modification process has undergone a significant change since 1985. Current standards and procedures mandate that PMT be performed on all potentially affected portions of the station, when a modification is implemented. The root cause of the event was determined to be historically poor PMT and an overly conservative Technical Specification (TS) Allowable Value (AV). Corrective actions included revising calculations to incorporate a new setpoint for increased margin and implementation of a plant modification.
2372001005 | Dresden 2 | 11/07/2001 | 01/07/2002 | ML02032055 | <strong>Unit 2 Scram Due to Increased First Stage Turbine Pressure</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2001, during start-up from D2R17 refueling outage, Dresden Nuclear Power Station Unit 2 automatically scrammed from 8 percent power in Mode 2. Initial investigation revealed that the high-pressure turbine first stage pressure had risen during shell warming activities, which defeated the stop valve closure scram bypass. As shell warming increased, a reactor scram was initiated when this high-pressure was sensed along with the turbine stop valves being closed. The Root Cause has been determined to be inadequate human performance in that the turbine first stage pressure setpoint was inadequately monitored (as required by procedure) due to it not being considered a critical parameter required for turbine startup. The corrective action to prevent recurrence was to train Operations on this event regarding the effect on Unit 2 with respect to turbine first stage SCRAM setpoint changes due to implementation of Extended Power Uprate and the relationship between shell warming and its impact on RPS logic. Included in the training was the relationship between the pressure versus power. All automatic protection responses, including reactor trip and its associated actuations were verified to have functioned properly as a result of the reactor trip signal. Based on the above, it is concluded that the event did not adversely impact the health and safety of the public. The safety significance for this event is considered minimal.
2452001001 | Millstone 1, Millstone 2, Millstone 3 | 02/05/2001 | 03/06/2001 | ML01072041 | <strong>Security Event Report: Site Vehicle Access Point Gate Open During Snowstorm Without Compensatory Measures</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2001, at approximately 1720 hours, during a snowstorm, Gate 14 A at the Vehicle Access Point (VAP) was found in the fully open position. Following classification, the NRC Operations Center was notified at 1916, on February 5, 2001, pursuant to 10 CFR 73.71(b)(1) and 10 CFR 73.71 Appendix G, "Reportable Safeguards Events." At the time of this condition, Unit 2 was in Mode 1 at approximately 100 percent power, Unit 3 was in Mode 5, shutdown for refueling (0.0 percent power), and Unit 1 was defueled and shutdown for decommissioning. The apparent cause was determined to be snow and wind creating conditions such that the drive belt on VAP Gate 14 A stretched, the electro-magnetic locks failed to engage, and wind caused Gate 14 A to blow open. This event had low safety significance because there was no undetected access to the protected area nor was there any evidence of contraband or sabotage within the protected area. The immediate corrective action involved posting a compensatory Security Officer at the open Vehicle Access Point gate (Gate 14 A) upon discovery. Subsequently, the VAP Protected Area gates were secured with additional Protected Area padlocks.
2472001001 | Indian Point 2 | 01/02/2001 | 02/01/2001 | ML01037017 | <strong>Turbine Trip During Startup Results in Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 2, 2001, at about 1524 hours, during preparations for main turbine start-up and with the reactor at 6.5 percent power, a turbine trip occurred due to high water level in 21 Steam Generator. This event resulted in the initiation of the Auxiliary Feedwater System, which is an Engineered Safety Feature (ESF) actuation. Prior to the turbine trip, control room operators had started 21 Condensate Pump in accordance with Plant Operating Procedure (POP) 1.3, "Plant Start-up from Zero Power Condition to Full Power Operation," to compensate for increased feedwater demand during the main turbine start-up and subsequent power escalation. As designed, the trip signal also resulted in the closure of the main feedwater pump discharge valves, and the steam generator blow down isolation valves. The cause for the high steam generator water level condition was attributed to an off-normal secondary system condition resulting in low main feed pump suction pressure, along with untimely operator action. During this event no Technical Specification requirements or safety limits were exceeded. In accordance with 10CFR50.72(b) (2) (ii), the NRC was notified of this event at 2205 hours on January 2, 2001; however, this notification was not made within the required time. This report is being made pursuant to 10CFR50.73(a) (2) (iv) as an event resulting in an Engineered Safety Feature (ESF) actuation.
2472001002 | Indian Point 2 | 02/14/2001 | 04/13/2001 | ML01107060 | <strong>Personnel Error Results in Loss of 480V Bus and Automatic Start of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2001, at about 0150 hours, during surveillance testing of 480 volt Bus 3A undervoltage relays, with the reactor at 100 percent power, 480-volt Bus 3A was lost. This resulted in the automatic start of all three emergency diesel generators; and is a reportable system actuation per 50.73 (a) (2)(iv)(B)(8). A technician performing the test was required by procedure to simultaneously hold a switch in the bypass position while two test buttons were pressed. The switch was not held in as required by procedure. This resulted in loss of Bus 3A, placing the plant in a shutdown action statement of Technical Specification 3.0.1. Limiting Conditions for Operation (LCO) was entered for the de-energized Engineered Safety Features (ESF) equipment. Power was restored within 25 minutes (0215 hours), satisfying the Technical Specification 3.0.1 action statement. At 0219 hours, all ESF equipment powered by Bus 3A was returned to AUTO and all LCOs exited. All equipment functioned as designed in response to the loss of Bus 3A. With the successful start of the emergency diesel generators, and the prompt return of power to Bus 3A, there were no adverse safety implications to the public associated with the event. There was no injury to plant personnel or damage to equipment. In accordance with 10CFR50.72(b)(3)(iv), the NRC was notified of this event at 0251 hours on February 14, 2001.
2472001003 | Indian Point 2 | 08/17/2001 | 10/16/2001 | ML01295022 | <strong>Instrument Calibration Error Results in Operation in Excess of Maximum Rated Thermal Power</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2001, at approximately 1442 hours, Indian Point 2 exceeded its full, steady state, licensed power level of 3071.4 MWt. Control room personnel were increasing reactor power following a power reduction to perform maintenance on a main feed pump [EIIS:SJ:P]. The power increase was stopped at 94 percent (indicated) to perform a heat balance and nuclear instrumentation [EIIS:IG] (NIS) calibration. The power increase was then resumed. At 1442, the overpower delta-temperature alarm [EIIS:IG:ALMJ actuated indicating an overpower condition. As required by procedure, reactor power was reduced to clear the alarm. Another heat balance was performed indicating that reactor power was at 101.5 percent. Reactor power was further reduced to less than 100 percent. Personnel initially believed that indications of greater than 100 percent power were incorrect. Subsequent analysis concluded that reactor power had reached 102.7 percent for approximately five minutes. As a result of exceeding 102 percent of the full steady state licensed power level, this event is reportable as a violation of License Condition 2.C.(1).
2472001004 | Indian Point 2 | 10/15/2001 | 12/14/2001 | ML01358018 | <strong>Human Performance Error Resulted in Missed Technical Specification Requirement</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2001, at approximately 1512 hours with the unit at 100 percent power the Steam Generator Blowdown Flow Instrument [EIIS:WI:FI] (FI-1241) was declared inoperable. Per Technical Specification Section 3.9 and Table 3.9-1, with the number of channels operable less than required by the Minimum Channels Operable requirement, effluent releases via this pathway may continue provided the flow rate is estimated at least once per four hours during actual releases. The Watch Engineer considered the requirements of Technical Specification Section 3.5 and Table 4.1-1 and System Operating Procedure (SOP) 15.1 Heat Balance, both focused on the impact on the heat balance calculation. The Watch Engineer did not consider the requirements of Technical Specification Section 3.9 or Table 3.9-1. The Instrumentation and Control (I&C) Technicians informed the Shift Manager-in-training of the failed surveillance Test. The Shift Manager (SM) on duty delegated signature authority to the Shift Manager-in-training, a qualified Control Room Supervisor. Per Operations Administrative Directive (OAD) 15 Revision 51 Section 4.5.2 the SM is responsible for signing all documentation specifying SM. This responsibility may be delegated to any management Senior Reactor Operator qualified as the Field Support Supervisor, Watch Engineer, SM or Control Room Supervisor. The SM may NOT delegate this responsibility when signature indicates authorization as Emergency Director. The Shift Manager-intraining recognized the impact on heat balance but not on the Technical Specification Section 3.9 and Table 3.9-1. On October 15, 2001, at approximately 2015 hours the oncoming watch crew identified the missed Technical Specification and took the appropriate actions. The four-hour time requirement for estimating flow was missed by approximately 30 minutes. During the time when compensatory actions were not in effect, primary to secondary reactor coolant leakage was zero and no changes to blowdown flow occurred. Based on this, no unmonitored release occurred and the safety significance was determined to be minimal.
2472001005 | Indian Point 2 | 10/23/2001 | 12/19/2001 | ML01365006 | <strong>Non-compliance with Overpressure Protection System Technical Specification</strong><br /><i>Abstract:&nbsp;</i>While performing an engineering review of instrumentation setpoints associated with the Overpressure Protection System (OPS) [EIIS:JC], it was determined that there were past occasions during which Indian Point Unit 2 may have operated in a condition prohibited by the plant's Technical Specifications. At the time, plant personnel were unaware of these non-compliant conditions because it was believed that the OPS requirements were being met. The OPS is designed to relieve the Reactor Coolant System (RCS) [EIIS:AB] pressure for certain overpressure transients when RCS temperature is less than or equal to 305F to prevent these incidents from causing the peak RCS pressure to exceed 10 CFR 50, Appendix G limits. Indian Point Unit 2 Technical Specification 3.1.A.4 specifies the requirements for the OPS. Furthermore Technical Specification Figures 3.1.A-2 and 3.1.A-3 define operational restrictions (pressurizer pressure, pressurizer level, and RCS temperature), which must be met if OPS is unavailable. Engineering review has concluded that on past occasions, OPS operational restrictions may not have been satisfied if instrument errors are conservatively assumed. The cause for this condition is attributed to procedural deficiencies. Procedural changes were implemented to account for the appropriate OPS instrument uncertainties.
2472001006 | Indian Point 2 | 10/29/2001 | 12/21/2001 | ML02009059 | <strong>Pipe Erosion Results in Service Water System Leakage in Containment</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2001 during a scheduled mid-cycle maintenance outage, with the plant at cold shutdown conditions, a Service Water (EIIS:BI) leak was observed inside containment located on the motor cooler outlet discharge piping from Fan Cooler (EISS:CLR) Unit No. 22. The source of the leakage was a hole (approximately 1/8 to 3/16 inch diameter) near a pipe-to-elbow weld on a two inch diameter, copper nickel Alloy 706 service water pipe, upstream of the containment penetration. No indication of leakage was detected prior to plant shutdown. At the time of discovery, this condition did not adversely impact Technical Specification requirements for containment integrity. The leak was corrected by the replacement of the elbow fitting in accordance with American Society of Mechanical Engineers (ASME) Section XI requirements prior to the plant's return to service from the outage. The root cause for this condition was excessive wear/erosion of the copper nickel material due to high, localized fluid flow rate (eddy currents) induced by the root pass weld extending into the flow path. Subsequent inspection of similarly susceptible service water piping was performed. They were found to be free of any measurable wall loss.
2472001007 | Indian Point 2 | 12/26/2001 | 02/25/2002 | ML02063015 | <strong>Automatic Reactor Trip Initiated by a Main Turbine Trip on Auto Stop Oil</strong><br /><i>Abstract:&nbsp;</i>On December 26, 2001 at 0720 hours Indian Point Unit 2 experienced an automatic reactor trip with all control rods fully inserting. The trip was initiated by a main turbine trip on auto stop oil. The auto stop oil turbine trip was caused by a trip of over frequency relays actuated by a disturbance associated with the 345 Kv Bus W93. This disturbance caused generator output breaker 9 to open. The cause of the over frequency relays actuation was failure of the blocking relay [EIIS:FK:68] on Consolidated Edison's 345 Kv feeder Y94. This failure caused the breakers on Y94 to open causing loss of load to the main generator and an over frequency trip. The over frequency trip caused the turbine trip. The turbine trip resulted in the generator trip. The generator trip caused the Indian Point 2 345 Kv generator output breaker 7 to open. The resultant trip placed the plant in natural circulation with 480-volt buses 2A and 3A de-energized as per design. All three Emergency Diesel Generators (EDGs) started and buses 2A and 3A were manually energized by 22 EDG, this was an expected response. 480-volt buses 5A and 6A remained energized from off-site sources during this event. No steam generator or pressurizer safety valves lifted and actuation of the Safety Injection System was not required. No radioactive release to the environment occurred as a result of this transient.
2492001001 | Dresden 3 | 01/09/2001 | 09/28/2001 | ML01282034 | <strong>Supplement to High Flow Differential Pressure Switches Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2001, during the performance of a Technical Specification (TS) Surveillance, "Unit 3 Isolation Condenser Steam/Condensate Line High Flow Calibration," both condensate return line high flow switches were found outside TS limits. Two differential pressure indicating switches are installed on the steam supply line and two differential pressure switches are installed on the condensate return line to automatically isolate the Isolation Condenser in the event of a line break. A trip signal from the four differential pressure switches will close motor-operated valves and isolate the Isolation Condenser from the reactor pressure vessel. The root cause of the event was determined to be that the installed switches on the Isolation Condenser condensate return lines exhibit unacceptable setpoint drift due to the current Technical Specification Surveillance Requirements being overly conservative. The corrective action to prevent recurrence is to revise the associated setpoint calculations to account for the observed drift for the Unit 2 and Unit 3 ISCO condensate line high flow switches. Immediate corrective actions included calibration of the switches to meet the TS surveillance acceptance criteria. The isolation function provided by the pressure switches was not lost; therefore, the safety significance of this event is minimal.
2492001002 | Dresden 3 | 04/27/2001 | 06/26/2001 | ML01183003 | <strong>Reactor Scram Due to Reactor Recirculation Run-up and Trip</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2001, at 14:49, approximately 10 minutes after a minor Reactor Recirculation (RR) flow increase demand, the 3B RR Motor Generator (MG) increased from 94 percent until it reached its electrical stop for speed control. This runup was due to debris in the RR MG scoop tube positioner motor. This resulted in the RR MG output frequency operating in an unstable region for the RR MG voltage regulator. This caused RR MG output frequency to vary significantly. Several attempts to trip the RR MG were unsuccessful due to the RR MG drive motor breaker logic's (52 H) relay contact not having continuity. The unstable RR MG operation caused its field breaker to trip on high excitation current. Without field excitation, the RR pump was not magnetically coupled to the RR MG's momentum. Therefore, the RR Pump quickly slowed, dynamically braking the 3B RR pump flow. The Reactor Water Level (RWL) increased due to the decrease in RR pump flow resulting in the Feedwater Level Control System (FWLCS) decreasing feedwater flow. A feedwater / steam flow mismatch occurred resulting in a decrease in RWL. RWL reached the automatic scram setpoint and Dresden Unit 3 scrammed on low RWL as designed. The debris in the RR MG Scoop Tube Positioner Motor has been removed. RR MG operation is not normally permitted in the unstable operating region for the RR MG voltage regulator. The drive motor breaker logic relay 52 H contact has been correctly aligned and verified by post maintenance testing. The safety significance of this event has been determined to be minimal.
2492001003 | Dresden 3 | 07/05/2001 | 09/04/2001 | ML01253021 | <strong>Reactor SCRAM Due to Increasing Drywell Pressure</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2001, at 1006 hours, a manual Scram was initiated on Dresden Nuclear Power Station (DNPS) Unit 3 due to increasing drywell pressure. Drywell pressure increased because of rising containment temperature due to a disc to stern separation of the Reactor Building Closed Cooling Water (RBCCW) Temperature Control Valve (TCV) that supplies cooling water to the RBCCW heat exchangers. One of the RBCCW loads is the drywell coolers. After the manual scram was initiated, drywell pressure continued to increase to a value above the Emergency Core Cooling System (ECCS) initiation setpoint. ECCS systems automatically initiated at 1.7 psig drywell pressure. The High Pressure Coolant Injection (HPCI) was placed in pull-to-lock to prevent a cold water injection. A Group 2 and Group 3 isolation also occurred during this event and all isolation valves successfully closed or isolated. All ECCS initiated and performed as designed. A General Station Emergency Plan (GSEP) Alert was conservatively declared based on the assumption that the drywell pressure increased due to Reactor Coolant System (RCS) leakage. Subsequently, containment sampling and sump data determined that drywell atmospheric activity levels had remained normal, and no abnormal sump inputs had occurred (no indication of RCS leakage). The GSEP Alert was terminated on July 5, 2001 at 1602 hours. The root cause of this event was the inappropriate torqueing of the valve stem into the valve disc by the manufacturer of the plug assembly. The cause of the manufacturer's failure to properly assemble the valve is unknown. The contributing causes of this event are poor communication of a similar previous event at Quad Cities, improper pin material being supplied by the vendor and Dresden's dependency on a single RBCCW train. The safety significance of this event has been determined to be minimal.
2502001001 | Turkey Point 3 | 06/08/2001 | 08/01/2001 | ML01219001 | <strong>Control Room Emergency Ventilation System Inoperable Due to Mispositioned Damper</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2001, with both Unit 3 and 4 in Mode 1, operating at 100% power, during the performance of the monthly Control Room Emergency Ventilation System Operability Test, the backup emergency supply fan did not start on simulated failure of the primary emergency supply fan. When placed in emergency recirculation mode, the Control Room Emergency Ventilation System is designed to operate with one supply fan in operation providing sufficient air flow through the cleanup filters. If the primary emergency supply fan fails to start, the backup supply fan will automatically start on detection of low flow. Troubleshooting determined that the cause of the fan start failure was due to a recirculation volume control damper providing too much air flow from the Control Room Ventilation System Air Handlers to the emergency recirculation system. This did not allow the system low flow actuation setting to be reached when the primary emergency supply fan was stopped. The design basis of the Control Room Emergency Ventilation System is to be capable of automatically starting under accident conditions to initiate control room pressurization and filtration, assuming the occurrence of a single damper or supply fan failure. The system was determined to be inoperable in the as-found condition. The exact time the damper was mispositioned could not be determined. The probable root cause for this event was mispositioning of the recirculation volume control damper due to inadequate administrative control.
2502001002 | Turkey Point 3 | 08/03/2001 | 09/25/2001 | ML01278017 | <strong>Both Trains of Auxiliary Feedwater Rendered Inoperable by a Single Event</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2001, with Turkey Point Unit 3 at 100% power, during a shift turnover control board walkdown, the reactor control operator discovered three of the six auxiliary feedwater (AFW) flow control valve hand indicating controllers (HIC) were not set at the correct flow for automatic operation of the AFW system. Both AFW trains were declared out of service on discovery. The correct HIC setpoints were re-established and the system was returned to service. This event is being reported in accordance with 10 CFR 50.73(a)(2)(vii) due to both trains of AFW being rendered inoperable by a single event. The root cause of the event was failure to follow procedure 0-ADM-200, Conduct of Operations, and at risk behavior by placing material on the instrument panel. Personnel involved in the event were held accountable and training briefs were issued to all plant personnel. In addition, protective covers have been placed over the AFW HIC stations.
2502001003 | Turkey Point 3 | 08/15/2001 | 10/07/2001 | ML01289039 | <strong>Manual Reactor Trip in Response to Low Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2001, at 4:49 AM, with the unit operating at approximately 16% reactor power, a manual reactor trip was initiated in response to low condenser vacuum. Prior to the event, Unit 3 was operating at full power but reduced generation due to a known condenser tube leak in the 3A South Waterbox. Condenser tube leakage resulted in chemistry conditions which forced a unit downpower. At approximately 16% reactor power, a manual reactor trip was initiated in response to indicated low vacuum in the condenser. The root cause of this event was inadequately designed sensing lines for the control room condenser vacuum instrumentation and the turbine low vacuum alarm. Contributing causes were diaphragm leakage in the turbine trip block and inadequate operating procedures for dealing with high condenser air in-leakage events. Corrective actions include upgrading of sensor lines for condenser vacuum trip and indication instrumentation to eliminate the buildup of condensate and revisions to operating procedural guidance.
2502001004 | Turkey Point 3 | 10/16/2001 | 12/13/2001 | ML02018035 | <strong>Condition Prohibited by Technical Specifications: Boron Injection Flow Path Inoperable During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2001, Turkey Point Unit 3 was in Mode 6 (Refueling) with core reload in progress. Contrary to Technical Specification (TS) requirements, fuel movement continued without an OPERABLE boration flow path as defined by TS 3.1.2.1. The condition was discovered on October 16, 2001. Although a boric acid transfer pump was OPERABLE and capable of supplying borated water to the Reactor Coolant System through an idle charging pump, the idle charging pump was not capable of being powered by an OPERABLE emergency power source, in verbatim compliance with TS 3.1.2.1. The emergency power source for the 3A Charging Pump is the 3A Emergency Diesel Generator (EDG). The 3A EDG was paralleled to the grid, rendering it inoperable. The root causes of this event were inadequate procedures and misinterpretation of TS 3.1.2.1. Because the emergency power source was available (even though inoperable), the safety significance and risk significance of the event were very low. Corrective actions include revision of procedures, counseling of personnel involved, and retraining of operating personnel and other non-licensed plant staff.
2512001001 | Turkey Point 4 | 01/25/2001 | 03/12/2001 | ML01079037 | <strong>Manual Reactor Trip Due to Two Dropped Rods</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2001, Turkey Point Unit 4 was at 100% power performing periodic rod exercises. At 1535, while driving in Shutdown Bank B, rod H-6 of Shutdown Bank B partially dropped into the core to about 120 steps. At 1545, reactor power was reduced to less than 75% power, in accordance with Technical Specification 3.1.3.1. FPL decided to not recover the partially dropped rod or withdraw Shutdown Bank B, requiring shutdown of Unit 4. At 1950, rod H-4 in Control Bank D dropped to about 150 steps while Control Bank D was being inserted as part of the reactor shutdown. At 1951, the reactor operator manually tripped the reactor due to a single dropped rod in two different banks. All systems operated as designed and the plant was stabilized in Mode 3. The root cause of the initial partially dropped rod was an open circuit in the Movable Gripper circuit caused by a dark green substance. The substance is being analyzed to determine its nature and origin. The root cause of the second dropped rod and the manual reactor trip is human error in communicating real time configuration while troubleshooting in-service equipment, due to weakness in the troubleshooting plan. Personnel involved in the event were counseled and training briefs were issued to all plant personnel. Procedures will be revised to enhance the communications during troubleshooting on in-service equipment.
2512001002 | Turkey Point 4 | 09/30/2000 | 01/16/2001 | ML00374515 | <strong>Containment Ventilation System Inoperable due to Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>During the Unit 4, Cycle 18/19, refueling outage, reactor core offload was started on September 30, 2000, with the containment purge system in operation. However, all of the required testing of the containment purge system was not completed. Generation of the isolation signal was tested, and the valves were stroked manually, but the automatic isolation function was not tested as required by Technical Specification 4.9.4. The root cause was inadequate procedures. The purge valves were not originally intended to be opened during core alterations. When plans changed, the impact of the change was not adequately reviewed since the controlling procedures did not trigger a re-review. Because containment (including purge valve closure) is not credited in the fuel handling accident analysis, the health and safety of the public were not affected by the inadequate surveillance test. The two procedures identified as inadequate will be revised. Implementing procedures for all of the refueling section of Technical Specifications will be reviewed to determine if there are other instances where a procedure provides condition options and does not provide a barrier to reconsider the impact if the condition changes. Personnel involved have been counseled. This event has been I discussed with each operating crew.
2552001001 | Palisades | 02/08/2001 | 04/05/2001 | ML01101014 | <strong>10CFR20.2201(b) Report - Loss of a Low Activity, Mixed Isotope Source</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2001, at approximately 1430 hours with the plant at 100% power, during a routine inventory of licensed radioactive sources, one low activity, mixed isotope source could not be accounted for. The source contained a total of approximately 0.992 microcurie, of which approximately 0.154 microcurie was Americium-241. (Typical home smoke detectors contain a one microcurie Americium-241 source.) Since the quantity of Americium-241 in this source was more than ten times the quantity specified in Appendix C of 10 CFR 20, a telephone report was made on March 9, 2001, in accordance with 10 CFR 20.2201(a)(1)(ii). None of the other isotopes in the source exceeded the reportable quantities as specified in Appendix C. The low activity and relatively large size of the source (2.25" dia by 1" thick) are such that it would not be a significant radiological hazard. A search of the site failed to locate the source. It is unlikely that a person could have inadvertently carried the source out of the radiologically controlled area (RCA) since the source would have caused the RCA exit monitors to alarm. It was concluded that the source was most likely discarded by mistake, inside the RCA, into a yellow trash bag with other radioactive waste. The low level radioactive waste from the time period in question was shipped off-site to a licensed vendor and final disposal has been completed.
2552001002 | Palisades | 03/31/2001 | 05/30/2001 | ML01156003 | <strong>Control Rod Drive Seal Housing Leak and Crack Indications</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2001, during an inspection of the reactor head area following shutdown for a refueling outage, a boric acid deposit and a small amount of water were found on the Control Rod Drive Mechanism (CRDM ) seal housing for Control Rod Drive (CRD)-22. The CRD seal housing assemblies comprise a portion of the ASME Class 1 Primary Coolant System (PCS) pressure boundary. The housing was removed from the reactor vessel head when conditions permitted. Subsequent investigation confirmed the presence of reactor coolant system through-wall leakage through a small (approx. 0.70 inches long) circumferentially oriented crack on the inside diameter of the seal tube. The housing also contained a confirmed axial crack (approx. 0.05 inches long) that was not through-wall. All 44 remaining seal housings were removed for examination. 100% of the seal tubes were inspected using visual and/or fluorescent dye penetrant non-destructive examination (NDE) methods. In addition to CRD-22, the inspections confirmed a circumferentially oriented crack (approx. 0.15 inches long) in CRD-8 that was not through-wall. No other crack-like indications were confirmed. A total of 13 seal housings were not returned to service due to NDE indications, confirmed cracks (in CRD-22 and CRD-8), or mechanical seal performance deficiencies. Thirteen new Inconel (Alloy 600) housings were installed on the reactor vessel head. The cracking confirmed in CRD-22 and CRD-8 has been determined to be transgranular stress corrosion cracking (TGSCC), most likely resulting from inadequate post-weld heat treatment which left residual stresses of sufficient magnitude to support cracking.
2552001004 | Palisades | 06/21/2001 | 03/14/2002 | ML02087035 | <strong>Control Rod Drive Mechanism Upper Housing Assembly Crack Indications</strong><br /><i>Abstract:&nbsp;</i>On June 21, 2001, with the plant in Mode 3, a pressure boundary leak was identified in the upper housing assembly for control rod drive mechanism (CRDM) number 21. The leak was observed near the weld of the upper housing assembly pipe to the eccentric reducer. Upon identification, the plant was placed in Mode 5 to effect repairs. Non-destructive examination of the CRDM-21 upper housing assembly revealed a through-wall axially oriented crack through the weld. Subsequently, the CRDM-21 upper housing assembly was destructively examined, revealing axial as well as circumferential indications. Further non-destructive examinations identified recordable indications in the same weld location on the upper housing assemblies for 42 of the 45 CRDMs. The cause of the through-wall crack in CRDM-21 and the crack indications in the other upper housings is attributed to transgranular stress corrosion cracking. All 45 CRDM upper housing assemblies were replaced prior to start-up from the plant outage with new CRDM upper housing assemblies which were modified to decrease their susceptibility to transgranular stress corrosion cracking. The safety significance of the CRDM-21 through-wall crack was determined to be very low. This condition was reported as a principal safety barrier being seriously degraded in accordance with 10 CFR50.73(a)(2)(ii)(A).
2602001001 | Browns Ferry 2 | 04/03/2001 | 06/01/2001 | ML01159002 | <strong>Reactor Scram While Shutdown Due to High Scram Discharge Instrument Volume Caused by Scram Outlet Valve Leakby</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2001 2351 CDT, during a refueling outage, Unit 2 received a reactor scram signal due to a west scram discharge volume high water level signal. All expected alarms and actuations were received. All control rods [AA] were initially in the "full in" position, therefore, no control rod movement occurred. The applicable immediate and subsequent actions specified in Abnormal Operating Instruction 2-AOI-100-1 were carried out. The cause of the scram was the Scram Discharge Volume (SDV) exceeding the high level setpoint due to scram outlet valve leakby and the SDV vent and drain valves being shut to support plant maintenance. The leaking scram outlet valves have been repaired and the SDV vent and drain valves returned to service. TVA is reporting this event in accordance with 10 CFR 50.73 (a)(2)(iv) as an event that resulted in a automatic actuation of an engineered safety feature, including the reactor protection system.
2602001002 | Browns Ferry 2, Browns Ferry 3 | 07/02/2001 | 08/30/2001 | ML01249023 | <strong>Non-Conservative Analysis for Oscillation Power Range Monitoring Scram Setpoint for Unit 2 and Unit 3</strong><br /><i>Abstract:&nbsp;</i>On July 2, 2001, TVA confirmed that a potential 10 CFR Part 21 condition related to the use of non conservative parameters associated with calculation of Oscillation Power Range Monitor (OPRM) upscale trip setpoint was applicable to BFN. At approximately 1100 hours Central Daylight Time the OPRM upscale trip function was declared inoperable. Technical Specification (TS) Actions 3.3.1.1.1.1, and 3.3.1.1.1.2 were entered on both Units 2 and 3. TS Action 3.3.1.1.1.1 requires initiation of alternate method to detect and suppress thermal-hydraulic instability oscillations within 12 hours. Action 3.3.1.1.1.2 requires that the OPRM upscale trip be returned to service in 120 days. The OPRM upscale trip function has been inoperable on Unit 2 since May of 1999, and on Unit 3 since May of 2000. Hence, TVA is reporting this event pursuant to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant's Technical Specifications. The root cause of this event is the original analysis performed by General Electric (GE) that defines the generic Delta Critical Power Ratio/Initial Versus Oscillation Magnitude curve was inadequate. GE identified a non-conservative deficiency for the high peak bundle power-to-flow ratios in the generic DIVOM curves. GE has proposed the development and licensing of a revised methodology for determining OPRM upscale trip setpoint. However, the revised methodology approval is not expected to meet the TS Action 120 day time limit. Subsequently, TVA proposed a TS change to delete TS Action 3.3.1.1.1.2. This change has been approved for Unit 2.
2602001003 | Browns Ferry 2 | 07/25/2001 | 09/21/2001 | ML01274020 | <strong>Automatic Reactor Scram Due to a Turbine Trip During Routine Testing</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2001, at 1047 hours Central Daylight Time (CDT) Unit 2 received an automatic scram from 100 percent power due to a main turbine trip from a power-load unbalance that occurred during Combined Intermediate Valve (CIV) testing. Vendor (General Electric Global Services) developed software contained a numerical error that resulted in an inadvertent turbine trip. The reactor scam caused the water level to go below the low level setpoint (level 3) which generated an additional scram signal and initiated Primary Containment Isolation Signals. All systems responded as expected and all control rods fully inserted. The root cause of this event was a weakness in the process for procurement of non-safety related SSCs that potentially impact generation. TVA will review procedures controlling software requisition, and revise as necessary, the requirements for non-safety related software that potentially impacts generation. TVA is reporting this event in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in manual or automatic actuation of any systems listed in paragraph (a)(2)(iv)(B), (i.e., Reactor Protection System (RPS) including reactor scram or reactor trip).
2602001004 | Browns Ferry 2, Browns Ferry 3 | 07/27/2001 | 09/24/2001 | ML01271031 | <strong>Inoperable Control Room Emergency Ventilation System Due to a Door Being Blocked Open During Maintenance Activities</strong><br /><i>Abstract:&nbsp;</i>On July, 27, 2001, at 0813 hours, a control room boundary door 642 (2A electric board room) was blocked open for painting in accordance with a general maintenance work order. A security officer was posted at door 642 since the door had a card reader for access. However, this door was blocked open without knowledge of Operations. At 1050 hours, the NRC Resident Inspector notified the Unit 2 Unit Supervisor that the door was blocked open and door 642 was closed. Since both CREV A and B were rendered inoperable without Operations knowledge, TVA failed to take the required actions after one hour of entering into a technical specification LCO 3.0.3 condition. The root cause for this event was that a contractor foreman did not know that a control room habitability breach permit was required. Corrective actions included: (1) door 642 was closed, (2) foreman was counseled, (3) maintenance group had a stand-down meeting to review this event, (4) the contractor included this event on a "lesson learned" handout for new hires, and (5) Maintenance Support and Facilities Maintenance Contractor foremen and supervisors will receive initial and annual maintenance required training which will include this event. In accordance with 10 CFR 50.73 (a) (2) (i) (B), this report is being submitted as any operation or condition prohibited by the plant's technical specifications.
2612001001 | Robinson 2 | 01/22/2001 | 03/20/2001 | ML01086030 | <strong>Reactor Protection System Low Reactor Coolant System Flow Channel Inoperable for Greater than Technical Specification Allowable Time</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2001, while the plant was in MODE 1 operating at 100% RATED THERMAL POWER, technicians determined during a scheduled surveillance test that the Reactor Coolant System Loop 3 Channel Flow Comparator (FC-434) setting was not within the allowable value of Technical Specifications, Table 3.3.1-1, Low Reactor Coolant Flow. The flow comparator is part of the Reactor Protection System. The associated Loop 3 channel was inoperable for longer than the six or ten hour completion times required by TS 3.3.1, Required Actions N.1 or N.2. The ten turn vernier dial potentiometer (flow comparator) setting was lower than specified in test procedures. The comparator was recalibrated. Corrective actions include the revision of maintenance procedures and work practices by April 6, 2001. Because the channel was inoperable for greater than the allowed completion time, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The apparent cause of this event was inattention to detail by non-licensed utility personnel.
2632001001 | Monticello | 01/10/2001 | 03/23/2001 | ML01101000 | <strong>Deficient Procedures Fail to Require Independent Verification Following Return to Service of Individual Channels During Instrument Surveillance</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2001, while following up on questions from the Monticello Senior NRC Resident Inspector, it was discovered the Technical Specification requirements for minimum number of operable channels per trip system and number of trip systems were violated due to deficiencies in instrument test and calibration procedures. Independent verification of the return to service of instrument channels following test and calibration was in some cases not performed until the last step in the procedure. Following calibration, each instrument channel should be independently verified to have been properly restored to operability prior to removing the next channel from service. Instrument test and calibration procedures that are potentially affected have been placed on hold. They will be revised prior to their next use to require independent verification of operability following return to service of each individual channel.
2632001002 | Monticello | 01/19/2001 | 03/29/2001 | ML01094006 | <strong>Failure to Comply with Technical Specification and ASME Code Section XI Inservice Inspection Requirements</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2001, following a request by the NRC resident inspector for work documentation related to a snubber replacement on the High Pressure Coolant Injection (HPCI) system, the Monticello plant staff became aware that the requisite NIS-2 form had not been generated as required by paragraph IWA-7520 of the 1986 Edition of the ASME Code Section XI. Further investigation revealed repair and replacement plans and NIS-2 forms had not been generated for replacement activities involving other ASME Code Section XI snubbers and safety-relief valve topworks. Monticello Technical Specification 3.15.A requires that components in quality groups A, B, and C (Class 1, 2, and 3) be declared inoperable if they do not comply with requirements of ASME Section XI. On January 24, 2001, the Limiting Condition for Operation (LCO) described in Technical Specification Section 3.15.A was entered for the snubbers not meeting code requirements. The snubbers were considered inoperable. Technical Specification 3.6.H was entered which allows 72 hours to perform an engineering evaluation to demonstrate snubber acceptability. On January 25, 2001, it was determined the LCO should have been entered on January 19, 2001, when the problem was first identified. On January 29, 2001, safety relief valve (SRV) topwork replacements were found to have been performed without complying with code requirements. Therefore, the SRVs were declared inoperable and Technical Specification LCO 3.6.E.2 was entered. A Notice of Enforcement Discretion was requested and verbal approval granted on January 30, 2001. This LER supplement addresses items found after the original reported items.
2632001003 | Monticello | 02/20/2001 | 04/13/2001 | ML01113018 | <strong>Inadequate Procedures Result in Failure to Recognize Entry Into 36-Hour Limiting Condition for Operation Required When Standby Gas Treatment System Doors Opened for Access</strong><br /><i>Abstract:&nbsp;</i>On February 20, 2001, during normal full power operation, it was discovered that maintenance practices used for on-line maintenance of a Standby Gas Treatment System (SBGT) filter train may degrade the performance of the redundant train. In the past, during on-line maintenance, an individual SBGT train was declared inoperable and isolated, a seven-day Limiting Condition for Operation was entered, and the system doors were opened to access components in the filter train. During an engineering review of this practice, it was determined that when any filter unit door is opened and control panels were deenergized, flow pathways are created through the open door and into the standby train. These flow paths, while small, were not analyzed for adverse effects on the performance of the standby train. It was determined that procedures needed to be revised to prevent both trains from being affected by maintenance activities on one train, or if this is not possible, to observe a Limiting Condition for Operation which is appropriate for inoperability of both SBGT trains.
2632001004 | Monticello | 02/16/2001 | 04/17/2001 | ML01114027 | <strong>Testing of Recombiner Space Heaters Not Performed Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>During review of an operations manual change, the system engineer recognized space heaters for the Combustible Gas Control (CGC) System recombiner reaction chamber and the recombiner blower motor had not been tested as required by plant Technical Specifications. It was concluded this condition does not meet the requirements of the Technical Specification 4.7.E.1.b which is to perform a resistance to ground test on all heater electrical circuits.
2632001005 | Monticello | 02/19/2001 | 04/19/2001 | ML01120002 | <strong>Ten Minute Torus Cooling Design Assumption Not Achievable</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2001 with the reactor operating at 100% power, the Monticello Nuclear Generating Plant (MNGP) staff determined that there was reasonable doubt that plant operators could manually establish torus cooling following a DBA LOCA within the 10 minute design assumption. The containment cooling system was declared inoperable. To restore operability, a dedicated operator was stationed in the control room with the sole purpose of initiating torus cooling during a LOCA. Following an unrelated reactor shutdown on February 25, 2001, a solution team was assembled to study torus cooling issues and recommend corrective actions. The team determined that the plant procedures used to initiate torus cooling were not streamlined for emergency conditions and were not written with the purpose of satisfying the 10 minute design assumption. On March 15, 2001 with the reactor shutdown, the solution team was evaluating operator actions to support torus cooling. It was determined by a calculation of post-accident drywell conditions that the potential for flashing of the fuel zone reactor water level reference leg during a DBA LOCA, although slight, was more probable than had been previously thought. This flashing could further delay operator actions to initiate torus cooling. Prior to startup on April 2, 2001, a modification to relocate nearly all of the fuel zone instrument reference leg piping from the drywell to the reactor building was completed. In addition, changes were made to the torus cooling procedures to directly support the 10 minute requirement and the operators were trained on these changes.
2632001006 | Monticello | 02/22/2001 | 04/19/2001 | ML01120002 | <strong>Alternate Shutdown System Design Deficiencies Result in Vulnerability to Single Hot Shorts During Postulated Control Room or Cable Spreading Room Fire</strong><br /><i>Abstract:&nbsp;</i>During an engineering review, hot short vulnerabilities were discovered in the Alternate Shutdown System (ASDS) in the event of loss of offsite power. The ASDS maintains the plant in a safe shutdown condition in the event of a severe Control Room or Cable Spreading Room fire. The first of these vulnerabilities affects the ASDS when powering Bus 16 from 12 Emergency Diesel Generator (EDG) and could lead to the inability to operate 12 Residual Heat Removal (RHR), 12 Core Spray, and 12 RHR Service Water pumps from the ASDS panel. The other vulnerabilities involve Bus 14 and Bus 16 breakers which receive a load shed signal on transfer of 12 EDG and associated controls to the ASDS panel. Hot shorts have the potential to reclose these breakers following the load shed causing the EDG or 1 AR transformer sources to be overloaded. This could result in a lockout or possible damage to the source. Design changes were completed prior to startup from a recent maintenance outage to eliminate these hot short vulnerabilities.
2632001007 | Monticello | 02/24/2001 | 04/23/2001 | ML01120012 | <strong>Failure to Comply with Technical Specification and ASME Code Section XI Inservice Testing Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2001 while operating at 100% power, the Monticello Nuclear Generating Plant staff discovered that the High Pressure Coolant Injection system and both divisions of the Low Pressure Coolant Injection mode of the Residual Heat Removal system were inoperable due to the failure to test the testable check valves as required by the Technical Specification and ASME Code Section XI. Since the LPIC mode of the RHR system and the HPCI system were declared inoperable, the Limiting Condition for Operation for Technical Specification 3.5.A was entered and the plant was required to be in a condition for which the inoperable equipment is not required to be operable (in this case less than 212 degrees). The plant reached shutdown conditions on February 25, 2001 within the 24 hour LCO. During the review to determine the extent of condition for this event, additional items were discovered to not comply with the Technical Specification and ASME Code Section XI inservice testing requirements. There was no safety significance associated with these events since all components were subsequently demonstrated to be in compliance with the Technical Specification and ASME Code Section XI requirements.
2632001008 | Monticello | 03/12/2001 | 05/11/2001 | ML01138038 | <strong>High Energy Line Break Barriers Found in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2001 with the reactor at cold shutdown, plant personnel identified an unanalyzed condition related to structural adequacy of two High Energy Line Break (HELB) barrier walls located on the 931ft elevation of the Turbine Building. The HELB barriers separate two redundant divisions of essential 480V Motor Control Centers (MCC), and are required to withstand differential pressure forces due to a postulated HELB. A postulated HELB of a feedwater pump discharge line or a main steam line in the Turbine Building and a consequent failure of these walls could damage both divisions of 480V MCCs. Modifications were installed to ensure that the affected HELB barriers would withstand the postulated HELB pressure forces.
2632001009 | Monticello | 03/28/2001 | 05/25/2001 | ML01152009 | <strong>Construction Error Results in Failure to Perform Periodic Testing of One Instrument Line Excess Flow Check Valve</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2001, a discrepancy was discovered between the Piping & Instrumentation Diagram (P&ID) and the as-built piping associated with the B reactor vessel fuel zone water level channel. The discrepancy was discovered while working on a design change to connect the two reactor vessel fuel zone instrument channels to upgraded reference columns. It was found that two instrument lines between instrument racks on elevations 935 feet and 962 feet in the Reactor Building had been crossed in a vertical pipe run during original plant construction. As a result, some instrumentation connected to containment penetration X-29A via excess flow check valve XFV-26 was actually connected to excess flow check valve XFV-57 and vice versa. This error presented no operability concerns for the affected instrumentation. However, a review of the procedure used to periodically test these valves revealed that the piping error prevented a valid test of XFV-57 from being performed. The B leg piping was rerouted to conform to the P&ID. XFV-57 was tested and was found to be operable. Technical Specification 4.7.D.1.b requires excess flow check valves to be tested every operating cycle. The fact that XFV-57 had not been properly tested since original plant startup constitutes a violation of this Technical Specification.
2632001010 | Monticello | 04/11/2001 | 06/08/2001 | ML01170031 | <strong>Standby Gas Treatment System Train A Fails to Meet In-Place Halogenated Hydrocarbon Leakage Test Acceptance Criterion Due to Slight Distortions in Filter Frame</strong><br /><i>Abstract:&nbsp;</i>During normal full power plant operation on April 11, 2001, filter leakage testing was performed following routine maintenance and testing on Standby Gas Treatment System Train A. During this testing the charcoal adsorber assembly failed to meet the Technical Specification in-place halogenated hydrocarbon (freon) leakage test acceptance criterion of less than 1% penetration. The charcoal adsorber unit was inspected and repaired to seal small gaps and irregularities between the tray gaskets and the filter frame. Standby Gas Treatment System Train A was satisfactorily retested following repairs and declared operable on April 13, 2001. Train A charcoal filter leakage data from previous tests was reviewed and found to be acceptable. However, Train A leakage measurements were found to be significantly higher than the corresponding Train B leakage measurements beginning in 1996, when the charcoal was replaced. Slight distortion of the Train A filter frame is believed to have created the opportunity for charcoal filter leakage to exceed the Technical Specification acceptance criterion in the time interval following the previous satisfactory filter test.
2632001011 | Monticello | 10/23/2001 | 12/21/2001 | ML02024038 | <strong>Worker Jarred Sensitive Instrument Rack Causing Scram</strong><br /><i>Abstract:&nbsp;</i>While in coastdown for refueling, at 1712 on October 23, 2001, a human performance error caused a reactor scram. The scram was a result of inadvertent contact of a support brace attached to a sensitive instrument rack by an individual performing work in the area. The primary cause of the event was determined to be inadequate work practices. Although the worker was aware of the sensitive nature of the instrumentation on the rack in the area in which he was working, the worker elected to transport heavy barrier stanchions through the narrow pathway immediately adjacent to a sensitive instrument rack. The worker lost his balance and bumped a support brace for the instrument rack.
2632001012 | Monticello | 11/08/2001 | 01/07/2002 | ML02043003 | <strong>Refueling Testing Identifies Containment Isolation Valve Leakage Greater Than Allowed by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Local leak rate testing during a refueling outage indicated that the following limits established in the Technical Specifications for Containment Isolation Valve leakage were exceeded: 1) the main steam isolation valve leakage limit and 2) the combined maximum flow path leakage rate for all containment penetrations and valves subject to Type B and C tests. Five valves with excessive leakage were identified, inspected and repaired as necessary. The valves were retested satisfactorily. The total minimum flow path leakage was not exceeded, therefore, this event did not affect the health and safety of the public.
2652001001 | Quad Cities 2, Quad Cities 1 | 08/02/2001 | 04/10/2002 | ML02119040 | <strong>Reactor Scram Due to Failure of Main Power Transformer</strong><br /><i>Abstract:&nbsp;</i>On August 2, 2001, at 0813 hours, lightning struck a 345 kV line that connected to the Quad Cities switchyard. This resulted in failure of the Unit 2 Main Power Transformer (MPT), an automatic reactor scram on Unit 2 and loss of normal offsite power to Unit 2. An Unusual Event was declared, the Unit 2 and 1/2 Emergency Diesel Generators started, and the Reactor Core Isolation Cooling system and the Safe Shutdown Makeup Pump were manually started to maintain reactor vessel level. The MPT fire was extinguished at 0845 hours and normal offsite power was restored to Unit 2 at 1047 hours. The safety significance of this event was minimal. All safety systems operated as designed to shut the Unit 2 reactor down and maintain it in a safe shutdown condition. Offsite power was available to Unit 2 from the Unit 1 Reserve Auxiliary Transformer through the emergency bus crosstie throughout the event. The root cause of the MPT failure was mechanical failure of the bus bar clamps due to original equipment manufacturer design and construction errors. The root cause of the loss of normal offsite power was age degradation in a Static Breaker Failure (SBF) relay. The SBF relay was replaced and the preventive maintenance program has been upgraded concerning local breaker backup schemes. The MPT Specification Development Lessons Learned Review Checklist has been upgraded and a comprehensive transformer monitoring strategy will be implemented.
2652001002 | Quad Cities 2, Quad Cities 1 | 05/01/2001 | 11/12/2001 | ML02028034 | <strong>Potential Common Cause Inoperability of Emergency Diesel Generator Fuel Oil Transfer Systems</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2001, at 2036 hours and on May 3, 2001, at 2012 hours, a solenoid valve in the Unit 2 Emergency Diesel Generator (EDG) Fuel Oil Transfer (FOT) system failed to open approximately 12 hours after the start of the EDG endurance test due to thermal pressurization of an isolated section of the FOT pump discharge piping. The root cause of this condition is the inadequate original design of the FOT system in that thermal effects in the piping volume between the discharge check valve and solenoid valve were not accounted for, allowing a pressure increase in the isolated volume beyond the operating capability of the FOT solenoid. The design of the FOT piping on the Unit 1 and Unit 1/2 EDGs is similar to the Unit 2 design. Although the solenoid valves on the Unit 1 and Unit 1/2 EDGs had a larger actuator (15.4 watts versus 6 watts), and have been shown in tests to be capable of opening against a larger differential pressure, these valves may still have been susceptible to failure to open due to thermal pressurization. The solenoid valves have subsequently been removed or replaced with manual valves. The safety significance of this event was minimal. Equipment and procedural guidance was in place to allow the manual transfer of fuel oil from the main diesel oil tanks to the day tanks. This LER is being submitted as a voluntary report.
2662001001 | Point Beach 1, Point Beach 2 | 01/12/2001 | 02/13/2001 | ML01057005 | <strong>Technical Specification Surveillance Requirements for Testing RPS Actuation System Logic Not Satisfied</strong><br /><i>Abstract:&nbsp;</i>This report describes the discovery on January 12, 2001, while conducting procedural reviews for the implementation of the Improved Technical Specifications, that testing of the power range low power trip logic and the intermediate range high flux trip logic was not being conducted within 24 hours after reducing power below 10% after having operated in excess of 10% power for greater than the monthly surveillance frequency specified in TS Table 15.4.1-1, Item 44. Although the surveillance testing of these trip logics was being accomplished prior to the next unit start up, and thus established the operability of the trips, a more conservative interpretation of the TS would have been to complete this surveillance within 24 hours of proceeding below 10% of full power. However, since the power range low power trip logic and intermediate range high flux trip logic testing can be accomplished at power, our corrective action will be to revise the plant procedures to require the monthly logic testing. The event had no impact on the health and safety of the public or the plant staff.
2662001002 | Point Beach 1, Point Beach 2 | 04/17/2001 | 05/18/2001 | ML01145020 | <strong>Use of the Steam Generator Blowdown Isolation Interlock Defeat Switch Could Result in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>This event discusses the results of an engineering evaluation which determined that under specific conditions the use of the steam generator blowdown isolation interlock defeat switch could result in the inability of the auxiliary feed water system to provide adequate steam generator (SG) inventory control to assure removal of decay heat following a loss of external AC event. This condition is reportable under 10 CFR 50.73(a)(2)(v) as; "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove residual heat." Paragraph 50.73(a)(2)(vi) states that events covered in Paragraph (a)(2)(v) may include discovery of design, analysis, and/or procedural inadequacies. A plant modification has been completed to initiate blowdown SG isolation on an auxiliary feedwater system initiation signal instead of a AFW pump start signal. Based on the low probability for this event and the availability of operator actions which would have served to mitigate the consequences of this event, the safety impact of this condition was of very low significance.
2662001003 | Point Beach 1, Point Beach 2 | 06/07/2001 | 11/27/2001 | ML02016049 | <strong>Containment Response for MSLB May Exceed Design Pressure of 60 PSIG</strong><br /><i>Abstract:&nbsp;</i>This report documents our preliminary evaluation that in the event of a main steam line break accident (MSLB) with a coincident failure of a main feedwater regulating valve (MFRV) to close, the internal pressure of the containment structure may briefly exceed the FSAR design pressure of 60 psig. The MSLB with MFRV failure to close has not been previously evaluated for PBNP at the presently licensed thermal power. However, an analysis of this accident under up-rated licensed power conditions has been completed. Based on an evaluation of the information provided in that analysis, the plant may be in an unanalyzed condition. Our evaluation of this condition indicates that the integrity of the containment structure would not be challenged by this postulated event, and; therefore, the safety significance of this condition is low. We are conservatively providing this event report as a follow-on to our June 7, 2001, 10 CFR 50.72 notification. A revised calculation for the MSLB with MFRV failure to close has been performed with the results indicating a peak containment pressure of 59.8 psig. This calculation included changes to the initial conditions for initial containment pressure and end of cycle shutdown margin which will be administratively controlled until suitable Tech Spec changes have been implemented.
2662001004 | Point Beach 1, Point Beach 2 | 06/24/2001 | 08/01/2001 | ML01222031 | <strong>Failure to Comply with LCO Action Statement to Start Redundant Standby Emergency Power Supplies</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2001, with both Point Beach Nuclear Plant (PBNP) Units operating at full load, one of the PBNP standby emergency power supplies, emergency diesel generator (EDG) G-03, tripped from near full power during performance of a monthly surveillance test. The redundant standby emergency power supplies were aligned to the proper safeguards buses in accordance with plant procedures and the Technical Specifications. G-03 was declared out of service and investigated for the cause of the trip. Contrary to the statements in the bases for TS 15.3.7, neither the common cause evaluation of the G-03 trip nor the requirement to start the redundant standby emergency power supplies were completed within 24 hours of the failure. This constitutes a condition prohibited by the TS and is reportable under 10 CFR 50.73. The evaluation of the G-03 trip determined that the components which caused the trip, which occurred while the EDG was in the exercise mode, would not have prohibited the EDG from performing its safety function in the event of an actual demand. Proposed corrective actions, including additional procedure remarks and implementation of ITS, should make it unlikely to overlook these testing and evaluation requirements in the future. The safety significance of this event was negligible.
2662001005 | Point Beach 1, Point Beach 2 | 11/29/2001 | 01/28/2002 | ML03076008 | <strong>PRA Assessment of Auxiliary Feedwater System Reveals Procedural Vulnerability related to Loss of Instrument Air</strong><br /><i>Abstract:&nbsp;</i>While conducting a self-initiated, voluntary review and revision of the Point Beach Nuclear Plant (PBNP) PRA model, including the auxiliary feedwater system (AFWS) portion of that model, NMC identified that the air-operated valves in the minimum flow recirculation piping for the AFWS pumps were not included in the PRA model. These valves fail closed on the loss of instrument air. While examining the significance of this failure, in conjunction with initiating events that require AFWS flow, NMC identified a misalignment between system design and EOPs. If the AFWS pump discharge or flow control valves were throttled closed with the minimum recirculation valve failed closed, it is possible that the AFW pumps could be placed in a condition of insufficient flow. This could result in pump damage in a short interval of time. The operators were trained on the significance of maintaining adequate AFW recirculation flow. However; early in the post reactor trip emergency operating procedures, the operators were directed to control AFWS flow without specific written guidance to maintain minimum AFW flow. It was postulated that the loss of instrument air together with a common operator response to high steam generator level or overcooling of the RCS had some probability to result in failure of one or all of the AFWS pumps. This could cause the loss of a safety function to mitigate the consequences of the accident and was determined to be reportable under 10 CFR 50.72. The PRA evaluation of this event sequence indicated that the potential consequences of this hypothesized failure were significant. Corrective actions included procedure changes to alert the operator to this potential failure sequence and additional operator training.
2662001006 | Point Beach 1, Point Beach 2 | 12/05/2001 | 02/04/2002 | ML02058039 | <strong>Appendix R Requirements Not Satisfied for Unanalyzed Fire Induced Damage to the Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>While conducting reviews of possible impacts on the auxiliary feedwater system (AFWS) for loss of instrument air, Point Beach Nuclear Plant engineers identified several previously unanalyzed 10 CFR 50, Appendix R safe shutdown equipment concerns. Specifically, a review of the availability of the motor-driven AFWS pumps (MDAFP) following an Appendix R design basis fire with a coincident loss of instrument air identified potential concerns with meeting Appendix R performance requirements. Four specific fire areas were affected. These fire areas are the Central Area of the 26' Primary Auxiliary Building (PAB), the safety injection and containment spray pump room, north AFW pump area, and south AFW pump area. In each of these fire areas, a MDAFP is relied upon as the means of getting feed water to at least one steam generator for at least one of the units. AFW flow to a minimum of one steam generator per affected unit is necessary to support the Appendix R performance objective of reactor coolant system (RCS) heat removal. This discovery was reported as an unanalyzed condition that had the potential to significantly degrade plant safety. Upon identification of this condition, compensatory fire rounds were initiated in the affected fire zones. An analysis of the conditions in these fire areas established that except for the AFWS pump room fires, alternative means are available to assure the availability of AFW flow. For Appendix R fires in the AFWS Pump Room, plant modifications will be necessary to assure minimum AFW pump recirculation flow.
2692001001 | Oconee 1, Oconee 2, Oconee 3 | 01/17/2001 | 02/16/2001 | ML01163034 | <strong>Revised Analysis Does Not Pass 10 CFR 50.46 Acceptance Criterion</strong><br /><i>Abstract:&nbsp;</i>On 1-11-01, Oconee Nuclear Station (ONS) was informed by Framatome Technologies Inc. (FTI) that the preliminary results of an analysis did not meet the 10 CFR 50.46 maximum peak clad temperature acceptance criteria. The scenario was a core flood line break from operation at 75% Rated Thermal Power (RTP) in a Technical Specification condition for two operable High Pressure Injection (HPI) pumps. Assumptions were an additional single failure of one HPI pump, no loss of power, and Operator action to trip Reactor Coolant Pumps (RCPs) at two minutes after loss of sub-cooled margin (LSCM). At 1145 hours, on 1-17-01, ONS conservatively reported under 10CFR 50.72(a)(2)(ii). All ONS Units were in Mode 1 with all three HPI pumps available. Unit 1 was at 18% RTP following a refueling outage. Units 2 and 3 were at 100% RTP. The root cause was a historical Analysis Deficiency. Interim guidance was provided to Operations. When FTI finalizes the analysis, Oconee will evaluate options and implement appropriate corrective actions. This event is considered to have no significance with respect to the health and safety of the public.
2692001002 | Oconee 1 | 09/12/2001 | 11/05/2001 | ML02009004 | <strong>Reactor Trip After Auto Main Turbine Trip Due to Isolated Phase Bus Problem</strong><br /><i>Abstract:&nbsp;</i>On September 12, 2001, Oconee Unit 1 was operating in Mode 1 at 100% power. At approximately 1813 hours Unit 1 tripped due to problems with the Isolated Phase Bus disconnect switch. During the plant trip, due to difficulties with the Z phase of the Isolated Phase Bus, an indication of a loss of power (as monitored on Z phase) actuated the 4kV switchgear undervoltage relays. This resulted in the loss of the Hotwell and Condensate Booster Pumps, which in turn caused the Main Feedwater (MFW) Pumps to trip. The Emergency Feedwater System actuated on loss of both Main Feedwater pumps. Steam Generator levels were correctly maintained by the Emergency Feedwater System. The unit post trip response was normal except for the MFW not being available. The plant was maintained in Mode 3. Investigation determined that the electrical generator disconnect switch on the "Z" phase had failed. Corrective actions to prevent recurrence were to replace the damaged disconnect switch and to improve the performance of the Isolated Phase Bus cooler. The health and safety of the public was not compromised by this event.
2702001002 | Oconee 2 | 04/28/2001 | 06/25/2001 | ML01183002 | <strong>Reactor Pressure Vessel Head Leakage Due to Stress Corrosion Cracks Found in Several Control Rod Drive Nozzle Penetrations</strong><br /><i>Abstract:&nbsp;</i>At approximately 1500 hours on April 28, 2001, a visual inspection of the top surface of the Oconee Nuclear Station Unit 2 (ONS-2) Reactor Pressure Vessel (RPV) head found evidence of small accumulations of boric acid deposited at the base of Control Rod Drive Mechanisms (CRDMS) Nos. 4, 6, 18, and 30. This RPV head inspection was performed as part of a normal surveillance during a planned refueling outage. Subsequent surface dye-penetrant test (PT) inspections of the weld area and nozzle outside diameter (OD) identified several axial cracks on four CRDM nozzles that initiated near the toe of the fillet weld and had propagated radially into the nozzle material as well as axially along the OD surface. These cracks are believed to be the leakage pathway for the boric acid deposits on the Unit 2 RPV head. Eddy current (EC) examination revealed two shallow axial flaws on CRDM nozzle 16 and craze cracking on all four CRDM nozzle ID surfaces. Supplemental ultrasonic test (UT) examinations were used to size the EC indications and determine the through-wall extent of other indications that EC could not resolve. The UT results confirmed the existence of some cracks (none through wall) predominately axial with one short OD initiated circumferential crack on CRDM Nozzle 18. The most probable root cause of the Alloy 600 CRDM Nozzle leaks is primary water stress corrosion cracking based on comparison of the PT, EC and UT results from the four ONS-2 CRDM nozzles and the documented NDE and metallurgical results of the previous ONS-1 and ONS-3 CRDM analyses, material samples and repairs. Prior to exiting the refueling outage, these nozzles were repaired. Additional short and long-term corrective actions to address potential future recurrences of this event are being managed via the Oconee Corrective Action Program.
2712001001 | Vermont Yankee | 03/19/2001 | 04/25/2001 | ML01127048 | <strong>Worn Protective Circuit Auxiliary Contact Results in an Invalid Protective System Actuation - Plant Trip</strong><br /><i>Abstract:&nbsp;</i>On 3/19/01, Instrument and Control Technicians were performing an Average Power Range Monitoring (APRM) System Functional Test. Per the procedure, the technicians had placed the "A" APRM (APRM-A) logic in the "bypass" condition, 'blocking any associated protective signals from the Reactor Protection System (RPS). The balance of in-service APRM's provide the required protection system outputs during testing. When required by the test procedure, a licensed operator restored the APRM-A bypass switch to "normal" to allow the APRM-A to deliver a trip signal to the RPS. This step is intended to verify proper circuit operation by actuating half of the logic necessary to insert an automatic shutdown. Restoration of the APRM-A bypass switch resulted in an automatic insertion of all control rods. Upon observing the insertion of control rods, the licensed operator initiated a manual plant trip. The cause of the trip was a worn auxiliary contact plunger in the "B" trip system circuitry that had remained in the tripped condition following previous testing. The half trip signal inserted by the APRM-A testing, combined with the closed "B” trip system contact, opened one of the backup scram valves, initiating an automatic insertion of all control rods. The worn auxiliary contact has been replaced. A temporary modification has been installed to verify that the affected auxiliary contact in the "B" trip system (as well as similar auxiliary contacts in the "A" and "B" trip systems) reset properly following future actuations. VY management has established a requirement to use the temporary modification to monitor the contacts for proper operation. Permanent configuration/process changes are being considered. The worn contact failed in the safe condition (initiating a protective action), plant safety systems operated as designed, and the operating crew operated plant systems in accordance with procedures bringing the plant to a stable shutdown condition. Therefore, this event caused no significant increase in risk to public health and safety.
2712001002 | Vermont Yankee | 05/02/2001 | 09/20/2002 | ML02283032 | <strong>HPCI Turbine Exhaust Line Check Valve Testing Results in Primary Containment Leak Rate in Excess of Allowable Due to Valve Design</strong><br /><i>Abstract:&nbsp;</i>On 05/02/01, Vermont Yankee (VY) determined, by containment isolation valve leak rate testing of the High Pressure Coolant Injection (HPCI) steam turbine exhaust line nozzle check valves, that each of the redundant containment isolation nozzle check valves allowed leakage beyond the prescribed limit. VY primary containment isolation valves are tested in accordance with 10CFR50 Appendix J. The plant condition (refueling outage) at the time of the discovery did not require that primary containment integrity be maintained. VY made modifications and repairs to the nozzle check valves and satisfactorily tested them to restore primary containment integrity prior to restart of the plant. The cause of this event is concluded to be the design of the internal nozzle check valve components. Leakage through this pathway would be into the HPCI system piping, which is contained within secondary containment. Leakage out of the HPCI system piping would be treated by the Standby Gas Treatment System prior to discharge. The VY design basis LOCA predicts radioactive releases based upon conservative assumptions. The predicted doses are in the millirem range, are 3-4 orders of magnitude below 10CPR100 criteria, and any additional leakage through the HPCI steam turbine exhaust line nozzle check valves would not have resulted in a significant increase in risk to public health and safety.
2712001003 | Vermont Yankee | 06/20/2001 | 07/18/2001 | ML01212027 | <strong>Denial of Unescorted Access Authorization Due to Withholding Information</strong><br /><i>Abstract:&nbsp;</i>On 06/20101, with the reactor at full power, Vermont Yankee (VY) denied unescorted access authorization to a contractor employee. The denial followed the disposition of a previously undisclosed criminal history received on 06/04/01. On 06/04/01, the contractor was flagged In the Personnel Access Data System (PADS) with an entry, which would alert other sites to contact VY prior to granting site access to this contractor. On 06/15/01, the contractor initiated a request for unescorted access authorization at the Seabrook Nuclear Power Station (SNPS). SNPS contacted VY In reference to the flagged PADS entry. VY requested an interview with the contractor. The contractor then stated that he withheld reporting the criminal record, mistakenly believing it to be out of the five-year scope for reporting. VY directed the contractor to produce documentation that would indicate the status of the record. While waiting to receive the documentation, VY consulted the psychological screening provider pertaining to the contractor's withholding of the criminal history. Upon re-screening of the MMPI test data and follow up interview, the psychological screening provider determined he would not have recommended unescorted access authorization, if the criminal history record had been known to him at the time access was granted. The contractor had temporary access authorization at VY from 04/20/01 to 05/13/01. There were no human performance, behavioral or work related performance issues identified with the contractor during the period of access.
2712001004 | Vermont Yankee | 08/21/2001 | 10/19/2001 | ML01365036 | <strong>Exceeded Core Thermal Power Limit Due to Feedwater Flow Nozzle Fouling</strong><br /><i>Abstract:&nbsp;</i>During the period of August 17-21, 2001 Core Thermal Power (CTP) was exceeded by 3.5 Megawatts Thermal (MWTh). This was discovered on August 21, 2001 while performing a calibration of the feedwater nozzles after the control rod pattern exchange down power on August 16-17, 2001 to 65%, using the Crossflow Ultrasonic Flow Meter. Nozzles FE-6-11A&B were found to be out of calibration, indicating 0.22% lower than actual flow. This caused the calorimetric calculation to indicate 0.22% lower than actual. Reactor power as adjusted by plant operators was higher than the licensed power level of 1593 and calculated power of 1592.56 by 3.5 MWTh. Following this discovery, reactor power was decreased by 4 MWTh. New calibration numbers for the nozzles were calculated which allowed for the return to 100% CTP. Before the down power, the nozzles were reading within calibration. The root cause for this measured flow discrepancy was due to changes to fouling on the feed water nozzles during the down power to 65% CTP. A contributing cause is the first application of noble metal chemistry during RFO-22. Prior history indicates that nozzle fouling was stable for any percentage down power that did not take the unit off-line. The maximum power level achieved during this event (100.22%) was fully bounded by plant analysis. Therefore, this event has no effect on public health and safety.
2712001005 | Vermont Yankee | 10/25/2001 | 12/20/2001 | ML02024046 | <strong>Primary Containment Breach Due to Broken Tubing at Hydrogen/Oxygen Monitor</strong><br /><i>Abstract:&nbsp;</i>On October 25, 2001 at 0900 with the reactor at full power, the "B" Containment Hydrogen/Oxygen (H2/O2) Analyzer (SAH-VG-5B) pump was discovered exhibiting excessive noise during weekly I&C minor maintenance. A black residue was observed in the cabinet due to deterioration of the coupling spider. A Work Request was initiated to investigate the cause of the pump noise. At 1225 the Control Room received a trouble alarm on the "B" H2/O2 Analyzer. Inspection revealed that the sample pump discharge tubing had broken off below the fitting to the regulator (R-2), causing a breach in Primary Containment. The Shift Supervisor was notified and the system was isolated at 1244. The System Engineer determined this breach to be in excess of the maximum allowable accident leak rate (La) and reported this to the Shift Supervisor. The appropriate10CFR50.72 notifications were made. Due to the short duration of the breach (nineteen minutes), there was no increased risk to public health and safety. The Root Cause Analysis determined the tubing break was due to the cumulative effects of strains and stresses exerted on the tubing at this connection, amplified by vibration from a failing pump coupling. Three of four set-screws which hold the coupling together had failed. Subsequent leak rate testing demonstrated the leak to be in excess of the Technical Specification limit of 0.6 La (La equals 0.8% of Primary Containment air wt./day) and greater than the analytical limit of 1.5% wt./day.
2722001001 | Salem 1 | 01/06/2001 | 01/26/2001 | ML01033013 | <strong>Auxiliary Building Ventilation System Fire Damper Found Out of Position Limiting the Ability of the System to Perform Its Safety Function</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2001, at 1410 hours, the number 12 auxiliary building exhaust fan {FAN} was removed from service to perform preventive and corrective maintenance. Upon completion of the work on January 6, during the operability retest of the exhaust fan, utility non-licensed operators noted that the emergency flow rate (air flow being discharged through the HEPA-Charcoal adsorber {FLT}) was less than the 21,400 SCFM ± 10% required by Technical Specifications. Investigation into this flow shortage revealed that the 1ABS-8 and 1ABF-13 dampers {DMP} were closed. The apparent cause for the 1ABF-13 damper being closed is attributed to the manual arm lever attached to the shaft, which holds the damper in the desired position, was found with the locking wing nut loose. The apparent cause for the closure of the 1ABS-8 damper is attributed to the closure of the 1ABF-13 damper, which caused the flow set point of the 1ABS-8 damper to be exceeded, thereby closing the damper as designed. Corrective actions taken were: (1) Fire Protection personnel walked down all accessible dampers to ensure that the wing nuts were tight, (2) 1ABF-13 was opened and the wing nut was re-tightened. The Technical Specification required flow test was completed satisfactorily, thus assuring proper position of the ABV system's dampers, (3) The PSEG Fire Department is presently checking all accessible dampers, similar to the ABF-1 3, once per week. The position of the dampers is being verified locally and the wing nuts tightened, as necessary.
2722001002 | Salem 1 | 07/14/1999 | 07/27/2001 | ML01219008 | <strong>Past Non-Compliance with the Auxiliary Building Ventilation Technical Specification Flow Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2001, during the root cause investigation associated with LER 272/01-001, "Auxiliary Building Ventilation System Fire Damper Found Out of Position Limiting The Ability of The System To Perform Its Safety Function." PSEG personnel determined that fire damper 1ABF11 {DMP} had closed on July 14, 1999. Similar to the event described in LER 272/01-001, closure of this damper could have resulted in flows from Emergency Core Cooling System (ECCS) areas being below the minimum required by Technical Specifications. Thus, the Auxiliary Building Ventilation would have been incapable of performing its safety function due to the reduced emergency flow rate (air flow being discharged through the HEPA-Charcoal adsorber {FLT}). The root cause of the closure of the 1ABF11 damper was attributed to the locking wing nut being loose due to the improper restoration of the damper after the functional test. Corrective actions proposed and taken as a result of LER 272/01-001 were: (1) To revise the surveillance test procedures to ensure setscrews are tightened and standardized hardware configuration is used, including improving the procedure wording to stress proper tightening of the locking mechanism, (2) Loss prevention personnel to perform a field validation of all appropriate fire dampers in Salem Unit 1 and Unit 2. This condition is being reported in accordance with the requirements of 10CFR50 .73(a)(2)(v).
2722001003 | Salem 1 | 04/13/2001 | 06/12/2001 | ML01169022 | <strong>As Found Value for Main Steam Safety Valve Lift Setpoint Exceeds Technical Specification Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2001, with Unit 1 in Mode 6 (Refueling) one of five Main Steam Safety Valves (MSSV) that was tested in accordance with the requirements of Technical Specifications and the ASME Operational and Maintenance (OM)-1 Code failed. The valve failed to meet the Technical Specification required acceptance criteria, as established in Technical Specification Table 3.7-1. The MSSV testing scope was expanded (in accordance with ASME OM- 1) to two additional valves. Both additional MSSVs tested satisfactorily. The apparent cause of the MSSV 11MS11 failing to meet the acceptance criteria was attributed to excessive seat leakage. From a process point of view, there were no processes or program deviations that contributed to this event. A setpoint variance of greater than ± 1.0% but less than ± 3.0% is not unusual for these valves, as described in AEOD/S92-02, Safety and Safety/Relief Valve Reliability. Corrective action taken was to replace the failed valve with a refurbishes valve and retest to ensure compliance with the ± 1% Technical Specification. A license change request to increase the setpoint tolerance from ± 1% to ± 3% has been submitted to the NRC. This event is reportable in accordance with 10CFR 50.73 (a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
2722001004 | Salem 1 | 04/13/2001 | 06/01/2001 | ML01166004 | <strong>Core Alterations Performed While Boration Flow Path Was Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2001, at 2315, removal of the upper internals from the reactor vessel (a core alteration) commenced and continued until the upper internals were placed in their stand at 0052 on April 14. At 2335 on April 13, the 1B emergency diesel generator (EDG) {EK/DG} was rendered inoperable when the equipment hatch for the EDG was removed. At the time that core alterations were being performed, the 11 Charging Pump {CB/P} was being relied upon as the only OPERABLE boron injection flow path to meet the requirements of Technical Specification (TS) 3.1.2.3. When the 1B EDG was rendered inoperable, the 11 Charging Pump could no longer be considered OPERABLE per the Technical Specifications due to a lack of emergency power source. The apparent cause for the performance of core alterations with no operable boration flow path is attributed to a human error in not properly linking in the outage schedule that the removal of the EDG equipment hatch impacted the operable boration flow path. A contributing cause of this event is also a human error; the SRO approving the work activity to remove the EDG equipment hatch did not recognize that removal of the equipment hatch rendered the EDG inoperable thereby rendering the 11 Charging Pump inoperable. Immediate corrective actions consisted of restoring the EDG to operable status and reviewing the outage schedule to ensure the Technical Specifications are complied with. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(i)(B).
2722001005 | Salem 1, Salem 2 | 04/18/2001 | 06/15/2001 | ML01176000 | <strong>Control Room Emergency Air Intake Dampers Inoperable During Spent Fuel Pool Moves</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2001 the B 125 VDC battery disconnects were open rendering inoperable the isolation dampers on an outside emergency air conditioning air intake. No isolation dampers were secured closed at this time and at 1400 and again at 1409 fuel moves occurred in the Salem Unit 1 spent fuel pool. The required actions were missed. Technical Specification 3.7.6.1 action f (modes 5 and 6) requires that with one or both series isolation damper(s) on an outside emergency air conditioning air intake duct inoperable, immediately suspend CORE ALTERATIONS and movement of irradiated fuel assemblies until the affected duct is closed by use of at least one isolation damper secured in the closed position. This condition was caused by weakness in the understanding, by all individuals' involved (licensed operators, outage control center), of all requirements for operability versus availability of the Control Area Ventilation (CAV) system. This was compounded by the recent installation of battery disconnect switches and accompanying procedure changes. Appropriate Operations and Maintenance procedures will be revised to provide clarification on CAV operability requirements associated with use of the battery disconnect switches. A root cause analysis was performed which was associated with defense in depth for station power. This analysis provides additional Corrective Actions, which would have assisted to preclude the occurrence of a similar event. This condition is being reported in accordance with the requirements of 10CFR50.73(a)(2)(i)(B) as "Any operation or condition that was prohibited by the plant's Technical Specifications..."
2722001006 | Salem 1 | 05/22/2001 | 07/20/2001 | ML01207016 | <strong>Reactor Trip Due to a Degraded Termination on Phase "A" Neutral Current Transformer Field Wiring</strong><br /><i>Abstract:&nbsp;</i>At approximately 0616 hours on May 22, 2001, Salem Unit 1 automatically tripped from full power. The direct cause of the reactor trip was the generator lockout relay operation resulting from a main generator phase "A" differential current relay trip. Extensive troubleshooting determined that there was a degraded termination associated with the field wiring to the "A" phase main generator neutral current transformer. The affected field wiring was replaced. Follow-up testing determined the current transformer itself was also degraded. A modification was installed to rewire the protective relaying and metering circuits to alternate current transformers. The unit was returned to power operation (synchronized to the grid) on May 26, 2001.
2722001008 | Salem 1 | 09/24/2001 | 11/15/2001 | ML02016009 | <strong>Salem Unit 1 - Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>At 2351, on September 24, 2001 a manual reactor trip was initiated in accordance with operating procedures due to the loss of condenser vacuum. At approximately 2243 hours on September 24, 2001 the number 2 Station Power Transformer {XFMR} (SPT) in the Salem Switchyard experienced an electrical fault on one of its associated surge arresters {LAR}. The electrical transient initiated by the fault resulted in the loss of the # 2 station power transformer, and for Salem Unit 1, in the loss of three of the six condenser circulating {NN} water pumps {PMP}, the loss of its circulating water traveling screens {SCN}, as well as the sensing instrumentation for the differential pressure across the traveling screens. With only three of six circulating water pumps operating per unit, both Salem units reduced electrical load to maintain main condenser vacuum. Following the restoration of electrical power to the circulating water bus, one of the remaining Salem 1 circulating water pumps tripped on high differential pressure. As condenser vacuum could not be maintained, Salem Unit 1 licensed control room operators manually tripped the reactor per the guidance of the abnormal operating procedure. The loss of the SPT is attributed to a failed arrester. Some of the corrective actions taken were: (1) The failed arrester was replaced, and (2) Similar arresters in other transformers were also replaced. This condition is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv).
2752001001 | Diablo Canyon 1, Diablo Canyon 2 | 04/05/2001 | 06/04/2001 | ML01163037 | <strong>Automatic Emergency Diesel Generator Start Upon Loss of Startup Power Due to 230-kV Line Arcing in Heavy Smoke from Escaped Fire Caused by Inadequate Administrative Controls</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2001, at 1500 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent reactor power, the Emergency Diesel Generators (EDGs) on Units 1 and 2 started as designed when power was lost on the 230-kV startup power system. During a prescribed burn in Diablo Canyon, intense heat ignited nearby green brush and generated heavy smoke that accumulated near the 230-kV lines, causing a phase-to-phase arc. Protective relays functioned as designed to deenergize the lines. Units 1 and 2 remained in Mode 1 at 100 percent power during the event. At 1526 PDT, the shift manager made a Notification of Unusual Event (NUE) to the NRC due to the fire being out of control for greater than 15 minutes. By approximately 1535 PDT, the fire had self-extinguished. At 1615 PDT, the 230-kV lines were returned to service, and at 1645 PDT, startup power was returned to both units. At 1700 PDT, the NUE was terminated, and by 2226 PDT, all EDGs had been secured and placed in standby. The cause of the event was inadequate administrative controls and Diablo Canyon Power Plant personnel oversight of California Department of Forestry (CDF) activities during cutting and burning of brush in the transmission corridor. PG&E will develop procedural guidance to formalize the administrative control and oversight of CDF activities during cutting and burning operations.
2752001002 | Diablo Canyon 1, Diablo Canyon 2 | 08/04/2001 | 10/04/2001 | ML01288036 | <strong>System Actuation Unplanned Diesel Start Due to Loss of Startup Power</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2001, at 1522 PDT, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, all six emergency diesel generators started but did not load, as designed, when a loss of Startup Power occurred due to a tripped differential relay protecting the Unit 1 230/12kV Startup Transformer (SUT) 1-1. The differential relay tripped as a result of multiple phase to ground faults in the 12kV SUT 1-1 ground resistor fuse box that resulted in damage to the fuse box and the 12kV bus duct. During this event, both units remained at 100 percent power. This event constitutes a valid system actuation. In accordance with 10 CFR 50.72(b)(3)(iv)(A), an 8-hour non-emergency report was made to the NRC on August 4, 2001 at 1655 PDT. The primary cause of this event was condensation (moisture) build-up inside the SUT 1-1 fuse box. PG&E will develop and install modifications to minimize moisture build-up inside the fuse box.
2752001003 | Diablo Canyon 1 | 09/13/2001 | 11/13/2001 | ML02024018 | <strong>Technical Specification 3.7.6 Not Met When the Fire Water Storage Tank Was Isolated from the Auxiliary Feedwater Pumps Suction Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2001, with Unit 1 in Mode 1 (power operation) at 100 percent power Technical Specification (TS) 3.7.6, "Condensate Storage Tank (CST) and Fire Water Storage Tank (FWST)," was not met when the allowed outage time was. exceeded due to a manual valve isolation between the FWST and the CST. On September 13, 2001, PG&E identified that closure of manual valve MU-1-297 on June 22, 2001, to isolate a raw water leak through valve 1-FCV-437 was a violation of the TS 3.7.6 licensing basis. Supplemental Safety Evaluation Report (SSER) 8, dated November 15, 1978, "... require(s) that redundant flow paths be provided to bypass any assumed single valve failure (valve jammed shut),"between the FWST and the auxiliary feedwater (AFW) Pumps suction as a result of a seismic event. On September 12, 2001, valve 1-FCV-297 was opened, restoring the flow path between the FWST and CST. Valve MU-0-1 557 was closed to isolate the raw water leak through 1-FCV-437. Plant personnel have been trained to include a comprehensive review of licensing basis documents when evaluating changes in plant configuration and procedures. The Bases for TS 3.7.6 will be revised to include the critical valve line-up between the FWST and the AFW Pumps suction.
2752001004 | Diablo Canyon 1 | 11/07/2001 | 01/18/2002 | ML02044021 | <strong>PAM Report 01-06 - Post-Accident Monitoring (PAM) Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2001, with Unit 1 in Mode 1 (Power Operation) at 100 percent power, PG&E identified that Unit 1 Steam Generator Level Indicator, LI-528 Westinghouse model VX-252, was in a degraded condition with all four case to frame mounting screws missing. This condition could have prevented the indicator from performing its required function following a seismic event, as the case containing the indicator could slide horizontally within its enclosure. On November 26, 2001, following completion of seismic evaluations, this condition was determined to be reportable. In accordance with Technical Specification (TS) 3.3.3, "Post Accident Monitoring (PAM) Instrumentation," and TS 5.6.8, "PAM Report," a written report is required within the following 14 days. The root cause of the LI-528 degraded condition has been attributed to the poor work practices when the indicator was last mounted. The immediate corrective actions were to replace the mounting screws for LI-528 and inspect all model VX-252 meters in the control room vertical boards for missing case to frame mounting screws. Corrective action verified that since the 1980s, when the case to frame mounting screws were presumed to have been left out, adequate procedures have been established in order to prevent such incidents.
2772001001 | Peach Bottom 2, Peach Bottom 3 | 06/18/2001 | 08/17/2001 | ML01222017 | <strong>Loss of Offsite Power Source Results in Specified System Actuation and Safety System Functional Failure</strong><br /><i>Abstract:&nbsp;</i>On June 18, 2001 at approximately 0315 hours, the 343SU-E offsite power source experienced an electrical fault causing it to trip. Two emergency 4160 VAC buses on both Units 2 and 3 transferred to their respective alternate power supply (2SU-E offsite power source). As a result, an invalid actuation of primary containment isolation valves in multiple systems occurred as expected for the loss of power. After the affected emergency buses transferred to the 2SU-E emergency power source, the operating crew entered procedure "Response to a Loss of #343 Off-site Startup Source." The procedure directed the crew to "flag" all "tripped" breaker control switches to their actual position; however, it did not address the alternate breaker control switches. This resulted in the normal power supply (tripped) breaker control switches being taken to open and the alternate power supply breaker control switch being left in the open position (with actual breaker position being closed). With both the normal and alternate breaker control switches in the open position, an interlock would have prevented the emergency diesel generator associated with two emergency 4160 VAC buses on each unit from automatically supplying power to their respective bus in the event of a loss of offsite power/LOCA. This condition existed for approximately three hours, when the operating crew took the control switch for the alternate power supply breaker to the closed position.
2772001002 | Peach Bottom 2 | 07/01/2001 | 08/30/2001 | ML01239004 | <strong>Main Turbine Trip Results in Actuation of the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2001 at approximately 1900, the operating crew noticed erratic indications on the main turbine control valve servos, pressure set, and various EHC indicators. I&C was contacted and a troubleshooting plan was developed to determine the cause of the fluctuations. On July 1, 2001, at approximately 0206 hours, an EHC power supply failed and the Unit 2 Main Turbine tripped causing the reactor to automatically scram on a turbine control valve fast closure signal. As a result of the main turbine trip and reactor scram, reactor pressure increased to approximately 1140 psig and reactor water level decreased to approximately -13 inches. This resulted in four safety relief valves lifting to control reactor pressure and PCIS group II and III isolations occurring, as expected. Additionally, both Reactor Recirculation pumps received a trip signal when reactor pressure exceeded 1106 psig. No Emergency Core Cooling System actuations occurred due to this event. The operating crew stabilized the plant per applicable procedures.
2772001003 | Peach Bottom 2 | 09/14/2001 | 10/24/2001 | ML02009055 | <strong>Condition Prohibited by Technical Specification - Required Actions Not Completed When LCO Not Met</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2001 at approximately 0840, the operating crew received an alarm, "Drywell Radiation Monitor Trouble." Further investigation determined that the drywell radiation gas sampler had isolated due to a failed relay to the solenoid on the isolation valve. The crew entered Technical Specifications and initiated the required actions for a loss of the drywell radiation monitor. The Technical Specification action required that a grab sample of the primary containment atmosphere be analyzed once per twelve hours. Technicians initiated the surveillance procedure steps for performing and analyzing a primary containment grab sample. Samples were obtained and analyzed at 1654 on September 14, 2001 and later at 0159 on September 15, 2001. Both surveillances were completed and documented as satisfactory. At 0830 on September 15, 2001, during preparations for performing the surveillance a third time, it was noted that the existing flow path being used for the grab sample was downstream from the closed isolation valve. Since neither of the first two surveillances resulted in analyzing primary containment atmosphere and the atmosphere was not sampled and analyzed within the time period required by Technical Specifications, the plant was in a condition prohibited by Technical Specifications.
2772001004 | Peach Bottom 2 | 10/23/2001 | 12/06/2001 | ML02008019 | <strong>Automatic Reactor Scram Due to Electrical Fault on Generator Conductor</strong><br /><i>Abstract:&nbsp;</i>On 10/23/01, at approximately 1102 hours, an automatic reactor scram occurred as a result of a main turbine trip caused by a generator lockout. As expected when the turbine tripped, reactor pressure increased resulting in five safety relief valves lifting initially to control reactor pressure. Reactor water level decreased resulting in expected containment isolations and a standby gas treatment start. There were no actual safety consequences as a result of this event. Plant equipment responded as designed to the event. It was discovered that the Main Generator A phase isophase bus ventilation damper became detached from the bus compartment and fell onto the Main Generator A phase conductor resulting in a ground fault. The investigation into the cause of this event determined that tapped holes in the ductwork were stripped during previous maintenance. The isophase bus ductwork damper was repaired. Other similar dampers on Unit 2 were inspected and no similar concerns were noted. Similar dampers on Unit 3 will be inspected during an outage of sufficient duration to permit inspections. Maintenance procedures will be upgraded. There were no previous similar events identified.
2772001005 | Peach Bottom 2 | 10/27/2001 | 12/27/2001 | ML02045015 | <strong>E-2 Diesel Generator Not Operable During Unit 2 Entry Into Mode 2</strong><br /><i>Abstract:&nbsp;</i>During testing of the E-2 emergency diesel generator (EDG) on 10/30/01, the diesel tripped due to low jacket coolant pump discharge pressure. Investigation revealed that the low-pressure condition was due to the gravity feed block valve on a line from the diesel generator coolant expansion tank being in the closed position. With the valve in this position, the jacket coolant pump did not have sufficient net positive suction pressure available for the pump to operate properly. As a result, adequate cooling of the diesel could not be assured. Upon discovery of the condition, the block valve was reopened and the impact of the low-pressure condition was thoroughly evaluated. The EDG was subsequently tested and declared operable on 10/31/01 at 0535 hours. This condition was determined to be reportable because the evaluation determined that the E-2 EDG was inoperable on 10/27/01 when Unit 2 entered Mode 2 (Startup) following forced outage 2F0102. Technical Specification limiting condition for operation (LCO) 3.8.1.c requires that four diesel generators be operable to supply the Unit 2 onsite Class lE AC Electrical Power Distribution system when in Mode 2. The entry into this mode without satisfying LCO 3.8.1.c is not permitted by Technical Specification LCO 3.0.4 and is reportable in accordance with 10CFR50.73(a)(2)(i)(B). The cause of the valve being closed was due to personnel error and was most likely associated with the manual adjustment of coolant levels in the expansion tank due to known leaks in the system. Actions are being taken to include the valve in the locked valve program to ensure the component is maintained in the correct position.
2782001001 | Peach Bottom 3 | 07/25/2001 | 09/19/2001 | ML01269013 | <strong>High Pressure Coolant Injection System Inoperable Due to Leaking Check Valve</strong><br /><i>Abstract:&nbsp;</i>On 07/25/01, at approximately 1530 hours, HPCI was removed from service and declared inoperable. Operations personnel conservatively decided to remove HPCI from service due to the potential of a water hammer condition if HPCI were to start. This potential condition was as a result of the HPCI discharge line not being completely full with water. Troubleshooting was performed and it was determined that there was leakage back through the HPCI suction check valve while on the alternate suction source. At approximately 1700 hours, the HPCI suction source was swapped back to its normal source (condensate storage tank). The HPCI discharge line was verified to be full and the system was returned to service. The HPCI system was declared operable on 07/28/01 at approximately 1300 following an engineering evaluation of the operability of the system with the leaking check valve. The cause of the HPCI system being inoperable was due to a leaking check valve in the alternate suction path. Additionally, it was determined that the safety function of the check valve needing to be closed was not appropriately identified in engineering documents that form the basis for determining appropriate leak testing. The check valve is planned to be repaired during the current refuel outage in progress on Unit 3. Actions were initiated to ensure that appropriate engineering documents are updated as necessary.
2782001002 | Peach Bottom 3 | 11/16/2001 | 01/11/2002 | ML02044031 | <strong>Less Than Adequate Test Review Results in Low Pressure Emergency Core Cooling Safety Function Degradation</strong><br /><i>Abstract:&nbsp;</i>On 11/16/01, the Low Pressure Emergency Core Cooling safety function was degraded for approximately 2 hours. This degradation occurred as a result of the combination of having the `A' loop of Low Pressure Coolant Injection (LPCI) out of service due to an inoperable isolation valve and the concurrent inoperability of other ECCS equipment during the performance of a Logic System Functional Test (LSFT). This condition was discovered on 11/16/01, at approximately 1300 hours, when the Control Room Supervisor (CRS) identified that the plant had previously entered and exited a Technical Specification Limiting Condition for Operation (LCO) action 3.0.3. This was identified as a result of an inquiry by the Unit 3 licensed reactor operator when he was attempting to perform an independent verification required at the conclusion of the LSFT. The cause of this event was inappropriate review of the LSFT test procedure by licensed individuals. A contributing cause to this event was less than adequate turnover between the nightshift and dayshift operating crew members. An evaluation was initiated to analyze licensed operator human performance behaviors to identify appropriate interventions required to resolve the human performance issues. There were no previous similar events. This event was evaluated to not be risk significant.
2802001001 | Surry 1, Surry 2 | 04/23/2001 | 06/22/2001 | ML01179000 | <strong>Inoperable Emergency Diesel Generator Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2001 at 0500 hours with Unit 1 and Unit 2 at 100% reactor power, the #3 emergency diesel generator (EDG) was taken out of service to investigate an increase in silver content in EDG oil samples. An inspection found three cylinders with excessive wear on the piston wrist pin and wrist pin bearing. All twenty power packs (cylinder, cylinder head, piston, rod) were replaced and the #3 EDG was tested and returned to service on April 28, 2001. The cause for the excessive wear was identified to be inadequate lubrication. The cause of the inadequate lubrication is continuing to be pursued. In the interim, the lubrication oil silver content of all the EDGs is being closely monitored. An evaluation concluded that the #3 EDG was inoperable for a period that exceeded the Technical Specification action statement. In addition, with #3 EDG inoperable, one train of Unit 2 auxiliary feedwater did not have emergency power while the other train was removed from service for a short period of time for testing. Both of the above conditions were therefore reportable pursuant to 10CFR50.73 (a)(2)(i)(B). No conditions adverse to safety resulted from this event and the health and safety of the public were not affected.
2802001002 | Surry 1, Surry 2 | 09/14/2001 | 11/09/2001 | ML02016016 | <strong>Control Room Chillers Breakers Improper Trip Rating Resulted in Potential for Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2001 at 11:41 hours with Unit 1 at 98% reactor power and Unit 2 at 100% reactor power, engineering review determined that main control room and emergency switchgear room (MCR and ESGR) chillers “A" and "B" motor control center feeder breakers could potentially trip at degraded voltage levels. As a result, chillers "A" and “B" were declared inoperable, and a 7-day action statement was entered. The other MCR and ESGR chillers, "C","D" and "E" were not affected and remained operable. After procedures were revised and training was completed on restrictions for operating the chillers, the "A" and "B" chillers were declared operable on September 14 at 19:07 hours and the 7-day action statement was exited. The cause of this condition was that in the 1986 timeframe engineering work requests that replaced the chiller compressors failed to ensure that the station electrical load list was updated for the increased loads. A subsequent design change package in the 1993 timeframe specified incorrect breaker trip ratings based on the incorrect values from the station electrical load list. The MCR and ESGR "A" and "B" chiller breaker trip rating deficiencies could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. This condition is therefore reportable pursuant to 10CFR50.73(a)(2)(v)(D).
2802001003 | Surry 1 | 10/28/2001 | 12/19/2001 | ML02052034 | <strong>NRC Bulletin 2001-01 Inspection of Surry Unit 1 Reactor Pressure Vessel Head</strong><br /><i>Abstract:&nbsp;</i>With Unit 1 at Refueling Shutdown conditions, a "bare head" visual inspection of the reactor pressure vessel (RPV) head was performed as requested by NRC Bulletin 2001-01. Liquid penetrant examinations revealed surface indications in the J-groove weld of two control rod drive mechanism (CRDM) penetrations (Nos. 27 and 40). Based on the nature of these indications, it was determined that repairs were required. On October 28, 2001, a non-emergency 8-hour notification was made to the NRC in accordance with 10CFR50.72(b)(3)(ii)(A) and 10CFR50.73(a)(2)(ii)(A) reporting apparent through-wall indications on these two penetrations. Subsequent examinations revealed unacceptable indications on four additional penetrations (Nos. 18, 47, 65, and 69) that also required repair. On November 2, 2001, two addenda to the initial 8-hour notification were made reporting these four additional penetrations. The six penetrations were modified and repaired, and Unit 1 was returned to power operation. This event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(ii) (A).
2812001001 | Surry 2 | 02/09/2001 | 04/09/2001 | ML01106003 | <strong>Extended Snubber Results in Technical Specifications Violation</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2001, with Unit 2 operating at 100% reactor power, it was determined that a support snubber on the "B" pressurizer safety valve discharge pipe was fully extended. Analyses concluded the snubber would be loaded beyond its faulted load under design dynamic loading conditions and therefore, could not be considered operable. Due to Technical Specifications requiring snubbers to be operable during reactor operation, a 72-hour limiting condition of operation was entered at 1049 hours. Unit 2 was shut down and the snubber in question was replaced. Further investigation determined the snubber had been inoperable beyond the allowed outage time, therefore, this event is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. Field verification will be conducted and necessary corrective actions implemented as unit operation and exposure levels permit. The station snubber program will be revised to include criteria for verification of snubber cold piston settings. With the snubber in the fully extended condition, calculations of stress levels in the piping indicated that piping components (other than the snubber) would maintain structural integrity in all loading conditions. Therefore, this event resulted in no safety consequences or significant implications and the health and safety of the public were not affected.
2822001001 | Prairie Island 1, Prairie Island 2 | 03/14/2001 | 05/14/2001 | ML01141021 | <strong>Failure to Physically Lock Valves Associated with Technical Specification Required Safety Injection Flow Path</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2001, with the reactor at 100% power, the duty Reactor Operator was giving a license trainee a check-off on the procedure for alternating the in-service Boric Acid Storage Tank (BAST). At this time it was noted that the procedure did not address re-locking the manual outlet isolation valve in position as required by Technical Specification 3.2.B.7. The 121 BAST was lined up for safety injection on Unit 1 due to a problem with level indication on the 11 BAST. An operator was dispatched to determine the status of manual valve SI-8-2 (121 BAST SUPPLY TO SI PUMPS). The operator reported to the control room that the valve was open (in the correct position), but not locked as required by Technical Specifications. A chain and lock was delivered to the operator and the valve was locked into position. Upon further investigation, valve SI-8-1 (11 BAST SUPPLY TO SI PUMPS), which was in the correct position, was also locked. On April 16, 2001, the NRC issued to Prairie Island, License Amendment No. 156 to Facility Operating License No. DPR-42 and Amendment No. 147 to Facility Operating License No. DPR-60, which removed the affected requirement from the Prairie Island Technical Specifications. Implementation of the amendment will preclude any future violations of the affected Technical Specification.
2822001002 | Prairie Island 1 | 06/18/2001 | 08/17/2001 | ML01233017 | <strong>Auto Actuation of Unit 1 4160 Volt Safeguards Bus 16 Source Sequencer Following Grid Disturbance Caused by Severe Weather</strong><br /><i>Abstract:&nbsp;</i>On June 18, 2001, while operating at 100% power, severe weather resulted in an electrical grid disturbance that caused 4KV Breaker CT11-1 to open. This resulted in the loss of the normal offsite source (CT11) to safeguards Bus 16. The load sequencer for Bus 16 operated as designed and transferred Bus 16 to its backup 4KV offsite source (1R).
2822001003 | Prairie Island 1, Prairie Island 2 | 07/10/2001 | 04/12/2002 | ML02116030 | <strong>Plant in Unanalyzed Condition Due to Flood Panel Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2001, with both units at 100% power, an inspection per site preventive maintenance procedure PM-3586-10 identified a number of deficiencies with flood panels such that 16 of 17 panels could not adequately meet their design function without compensatory measures. [Note: subsequent evaluation noted deficiencies in all 17 flood panels and identified an additional flood protection issue]. The deficiencies include deteriorated gasket material, physical obstructions, and deficient bolting. Per analysis, flooding severe enough to require flood panels would only be the result of snow melt concurrent with heavy rains. There was no immediate operability concern at the time of discovery because there was no snow cover. Corrective actions have restored the flood panels to a condition where they meet their design function. The additional flood protection issue (one dealing with removable panels on the D5/D6 building) has been resolved.
2822001004 | Prairie Island 1 | 08/01/2001 | 10/01/2001 | ML01282019 | <strong>Water Intrusion Into a Control Rod Electrical Cabinet Results in Dropped Rods Causing a Negative Flux Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 1, 2001, Prairie Island Unit 1 experienced an automatic reactor trip due to negative flux rate. Following the trip, several control rods initially failed to provide rod bottom position indication. This required the operating crew to enter emergency operating procedures and initiate boration to compensate for the apparent loss of shutdown. With the exception of the erroneous rod position indication, the plant response and operator actions subsequent to the trip were as expected. The event was initiated by water intrusion into a control rod drive power supply cabinet. The water caused varistors in the 12 AC Control Rod Power Cabinet to malfunction. This, in turn, caused the Control Bank C2 control rods to drop into the core, resulting in the negative flux rate trip. The source of the water was spillage from an overhead room cooler drip tray. A partially plugged drip tray drain, combined with high ambient humidity, led to a condensation rate from the cooler coils that exceeded the capacity of the drain until the drip tray overflowed onto the control rod drive power supply cabinet below. Corrective actions include development of a preventative maintenance task to periodically inspect and clean the drip tray drains. The control rod position indication error was caused by an unanticipated bias (equating to approximately 8 steps) that was introduced by a revised calibration procedure. The control rod position indications were recalibrated using the previously accepted methodology.
2822001005 | Prairie Island 1, Prairie Island 2 | 08/03/2001 | 10/02/2001 | ML01283046 | <strong>Fault and Fire in Non-Safeguards Circuit Breaker Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2001, with Unit 2 at 100% power, Unit 1 was undergoing an orderly startup following the reactor trip that occurred on August 1, 2001. At about 8:40 pm CDT, with Unit I at approximately 25% power, operators were transferring the power supply to the non-safeguards 4 kV buses from the Unit 1 Reserve transformer to the Unit 1 Main Auxiliary transformer. Within seconds of closing the source breaker from the Main auxiliary transformer to 4 kV Bus 12, the breaker failed. The breaker failure initiated a fire in Cubicle 12-4 of Bus 12. The failure actuated the Generator Transformer protective relaying scheme, including a lockout of Bus 12. The bus lockout opened the Breaker 12-1, Bus 12 source from the 1 RX transformer, and actuated the protective relaying scheme. The protective relaying scheme caused a turbine/reactor trip and actuation of the Auxiliary Feedwater System. To support firefighting, Bus 11 was deliberately de-energized, thus, both reactor coolant pumps were unpowered and the unit was cooled down via natural circulation. The fire was extinguished about one hour and 30 minutes after the event. The unit was brought to cold shutdown within the time allowed by Technical Specifications. Remaining unit equipment responded as expected and, overall, the organization effectively responded to the event (although some improvements were recommended following an evaluation of organizational response). A root cause evaluation is complete, the damaged equipment has been repaired, and actions are being taken to prevent recurrence of the event and to improve organizational response to events.
2822001006 | Prairie Island 1, Prairie Island 2 | 08/03/2001 | 09/04/2001 | ML01250020 | <strong>Security Responders out of Position due to Plant Fire</strong><br /><i>Abstract:&nbsp;</i>During the evening of August 3, 2001 an electrical fault in non-safeguards Bus 12 started a fire. An offsite response from the Red Wing Fire Department was required to assist the plant staff in the control of that fire. During the event, two responders were outside of their timelines for periods of approximately 2 hours/15 minutes and 16 minutes, respectively. While they were outside of their timelines, they were still within the plant's protected area, able to respond, and were supported by the fact that staffing levels that night were above the Security Plan minimum requirements. Additionally, during the course of the event 3 fully qualified supervisors arrived on site and would have been able to provide some assistance in a contingency event.
2852001001 | Fort Calhoun | 03/26/2001 | 04/25/2001 | ML01120002 | <strong>Primary Safety Valves Outside Lift Setting Acceptance Range</strong><br /><i>Abstract:&nbsp;</i>At 1117 hours on March 26, 2001, during a scheduled refueling outage, it was discovered that the "as-found" lift pressure of primary safety valve (PSV) RC-142 was outside its specified lift setting acceptance range. Fort Calhoun Station (FCS) Technical Specification (TS) 2.1.6(1) specifies that this valve is to have its lift setting adjusted to ensure valve opening at 2485 pounds per square inch gauge (psig)+/-1 percent (i.e., a range of 2460.2 to 2509.8 psig). The "as-found" lift pressure was 2459.9 psig, which is 1.01 percent below the nameplate lift pressure. At 1225 hours on March 29, 2001, it was discovered that the "as-found" lift pressure of PSV RC-141 was outside its specified lift setting acceptance range. TS 2.1.6(1) specifies that this valve is to have its lift setting adjusted to ensure valve opening at 2530 psig +/-1 percent (i.e., a range of 2504.7 to 2555.3 psig). The "as-found" lift pressure was 2485.9 psig, which is 1.74 percent below the nameplate lift pressure. It has been concluded that the root cause of this event was normal setpoint variance. Corrective actions included additional lift testing of RC-142 to obtain repeatable lift pressures within the +/-1 percent tolerance range.RC-141 was disassembled, cleaned, inspected, and refurbished, followed by testing and adjustment to obtain repeatable lift pressures within the +/-1 percent tolerance range.
2862001001 | Indian Point 3 | 05/10/1999 | 06/01/2001 | ML01162016 | <strong>Inattention to Detail in FSAR and Design Basis Maintenance Caused Bypass of Isolation Signals to Steam Generator Blow-Down Isolation Valves that Could have presented the SG Decay Heat Removal Safety Function</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2001, at approximately 2133 hours, with steady state reactor power at approximately 100 percent, surveillance test 3PC-R49A required that the eight switches to the Steam Generator (SG) blow-down isolation valves be placed in the RAD Bypass position. Inadequate inventory results since one motor driven auxiliary feedwater (AFW) pump would not be inadequate to maintain SG inventory with the blow-down isolation valves open. The evaluation of Rad Bypass usage during operation over the past three years found one event on May 10, 1999 where the 31 AFW pump was removed from service for 2 hours and 12 minutes during the performance of 3PC-R49A. When Rad Bypass was used during other tests over the last three years, the events were not reportable because two motor driven auxiliary feedwater pumps were available and sufficient to assure adequate inventory (single failure is not assumed in determining whether a function is lost). The cause of the inappropriate use of the Rad Bypass switches was lack of guidance due to inattention to detail by the engineers responsible for developing and maintaining the FSAR and the design bases document. Immediate corrective action was taken to direct the operators not to use the Rad Bypass switch position. The FSAR and design basis documentation will be updated to describe blow down isolation. The procedures allowing Rad Bypass are being revised prior to next use until design changes (modifications or analysis) allow bypass. This event had minimal effect on the public health and safety since no transient occurred and the conditional core damage probability is estimated to be 1.52E-7.
2872001001 | Oconee 3 | 02/18/2001 | 08/18/2005 | ML05238042 | <strong>Reactor Pressure Vessel Head Leakage due to Stress Corrosion Cracks Found in Nine Control Rod Drive Nozzle Penetrations</strong><br /><i>Abstract:&nbsp;</i>At 2100 hours on February 18, 2001, a visual inspection of the top surface of the Oconee Nuclear Station Unit 3 (ONS Unit 3) Reactor Pressure Vessel (RPV) head found evidence of small accumulations of boric acid deposited at the base of several control rod drive mechanisms (CRDMs). This RPV head inspection was performed as part of a normal surveillance during a planned maintenance outage. The boric acid deposits were identified around nine (Nos. 3, 7, 11, 23, 28, 34, 50, 56, and 63) of the sixty-nine total CRDM nozzles. The amount of boric acid around each of the CRDM nozzles was estimated to be no more than a few cubic inches but ultimately signified that reactor coolant system pressure boundary leakage had occurred. After confirming that the Reactor Coolant System (RCS) pressure boundary had been compromised, a February 18, 2001, 8-hour notification was made to the Staff in accordance with 10CFR50.72(b)(3)(ii)(B) reporting requirements. Subsequent non-destructive testing was performed on a total of eighteen CRDMs in order to effectively evaluate, characterize the leak mechanism, and determine extent of the condition. Visual inspection of the reactor vessel head surface revealed a small area of head surface corrosion adjacent to nozzle 34. No other significant areas of corrosion were observed. Subsequent structural analysis of the area of corrosion concluded that slight degradation to the RPV head did not adversely affect the structural integrity of the component. The apparent root cause of the nine CRDM Nozzle leaks is primary water stress corrosion cracking (PWSCC). The nine leaking CRDMs have been repaired. This event is considered to have minimal safety significance with respect to the health and safety of the public.
2872001002 | Oconee 3 | 03/07/2001 | 05/15/2001 | ML01142001 | <strong>Containment Cooler Inoperable Due to Design, Exceeds Tech Spec Time</strong><br /><i>Abstract:&nbsp;</i>On 3/7/2001, while Oconee Unit 3 was in Mode 6, the Unit 3 "B" Reactor Building Cooling Unit (3B RBCU) stator temperature exceeded the operability limit during a special test. The 3B RBCU was declared inoperable. An investigation team concluded that a manufacturing deficiency of the 3B RBCU motor, installed on 12/19/1999, might have prevented proper operation under certain accident conditions. This event is being reported as operation in a condition prohibited by Technical Specifications. The root cause of this event is vendor design/manufacturing deficiency. Corrective actions include replacement of the affected motor and a specification change for future replacement motors. This event is considered to have no significance with respect to the health and safety of the public.
2872001003 | Oconee 3 | 11/12/2001 | 01/09/2002 | ML02035029 | <strong>Minor Reactor Pressure Vessel Head Leakage From Several Control Rod Drive Nozzle Penetrations Due to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2001, a visual inspection of the top surface of the Oconee Nuclear Station Unit 3 Reactor Vessel (RV) head found evidence of small accumulations of boric acid deposited at the base of several control rod drive mechanism (CRDM) nozzles. This RV head inspection was performed as part of a planned surveillance activity during the end-of-cycle 19 refueling outage. Following this visual inspection, nondestructive examination of the suspect nozzles revealed that seven (Nos. 2, 10, 26, 31, 39, 49, and 51) of the sixty-nine total nozzles required repair. Five of the seven repaired nozzles were confirmed to have a leakage pathway to the top of the RV head. The amount of boric acid around the five leaking nozzles was estimated to be no more than a few cubic inches. After confirming that the Reactor Coolant System pressure boundary had been degraded during power operations, an 8-hour notification was made at 0335 hours on November 12, 2001 in accordance with 10CFR50.72(b)(3)(ii)(A) reporting requirements. The apparent root cause of the CRDM Nozzle leaks is primary water stress corrosion cracking. The seven CRDMs were repaired and the remaining 43 nozzles that [historically] had neither been previously examined nor repaired were inspected using an ultrasonic circumferential blade probe prior to exiting the refueling outage. This event is considered to have minimal safety significance with respect to the health and safety of the public.
2892001001 | Three Mile Island 1 | 02/01/2001 | 03/12/2002 | ML02084039 | <strong>Emergency Feedwater Pump 2A Inoperable Greater than the Technical Specification Allowable Outage Time Due to an Incorrect Operability Determination</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2001, it was determined that EF-P-2A had been inoperable from February 1, 2001 through February 14, 2001. Following further analysis of this event, it was determined on April 20, 2001 that the period of inoperability for EF-P-2A started on January 6, 2001 and lasted till February 14, 2001. Technical Specifications provides a 72-hour allowable outage time, thus this event is reportable as a condition prohibited by Technical Specifications. It has been determined that the bolts fastening a cover of the outboard bearing housing had loosened sufficiently on January 6, 2001 to impact operability. EF-P-2A may not have been able to perform its intended safety function, due to oil leakage and shaft vibration concerns, until the bolts were tightened on February 14, 2001. Operability determinations regarding the oil leakage and vibration conditions made previous to April 2, 2001 concluded incorrectly that EF-P-2A remained operable. The root cause of the incorrect operability determination was a failure to consider all the available information regarding the status of the component against its design basis requirements. Immediate corrective actions include: (1) procedure for operability determination revised, (2) initiated briefings for operating crews, (3) verified that the bearing housing bolts on all three emergency feedwater pumps were tight, and (4) reviewed the status of all safety related pumps and verified no similar concerns. The long-term corrective actions include revision of the operability determination process and establishment of recurring training regarding the revised operability determination process. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2892001002 | Three Mile Island 1 | 10/12/2001 | 12/05/2001 | ML02016039 | <strong>Reactor Coolant System Pressure Boundary Leakage Due to Stress Corrosion Cracks Found in Several Small Bore Reactor Vessel Head Nozzle Penetrations</strong><br /><i>Abstract:&nbsp;</i>On October 11 and 12, 2001, following shutdown for a scheduled refueling outage, Three Mile Island Unit 1 (TMI-1) performed a visual inspection of the Reactor Pressure Vessel (RPV) Head Nozzle Penetrations per NRC Bulletin 2001-01. The inspection revealed evidence of boric acid buildup around all eight (8) Thermocouple (TIC) nozzles and boric acid buildup around twelve (12) Control Rod Drive Mechanism (CRDM) nozzles. Based on the visual examination, engineering evaluation determined that all eight of the TIC nozzles were a source of Reactor Coolant System (RCS) pressure boundary leakage. Additional non-destructive examinations on the CRDM nozzles identified that five CRDM nozzles were also a source of RCS pressure boundary leakage and one non-leaking CRDM nozzle that contained unacceptable flaws. The cause of the cracks was determined to have been Primary Water Stress Corrosion Cracking (PWSCC). Prior to exiting the refueling outage, these nozzles were repaired. The RCS unidentified leak rate before the shutdown did not indicate any significant leakage. A safety assessment concluded that the nozzle cracks did not pose any risk for catastrophic nozzle failure or boric acid damage to the RPV head. Routine qualified visual inspections were determined to be adequate to detect future similar cracks before any significant impact on safe operations can occur. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2892001003 | Three Mile Island 1 | 10/20/2001 | 12/14/2001 | ML02016009 | <strong>Degraded OTSG Tube</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2001, TMI-1 determined that consequential degradation from the sever of a plugged tube in the "B" once through steam generator (OTSG) [AMC] had resulted in degrading an adjacent in-service tube. The damage was such that the degraded tube may not have remained intact under accident conditions. Three (3) other adjacent in-service tubes were damage by the severed plugged tube but would have remained intact under accident conditions. The degradation of tube B65-130 was caused by the fretting of the severed plugged tube B66-130 against B65-130. The 360 degree sever of the B66-130 was caused by the combined effects of leak by of water past the mechanical plug into the plugged tube followed by subsequent "trapping" of the water in the plugged tube (that resulted in over-pressurization of the plugged tube), low amplitude high cycle fatigue and the presence of an existing flaw on the outer diameter of the plugged tube. The extent of condition in the "A" and "B" OTSGs was evaluated and found one circumferentially severed plugged tube in the "A" OTSG and found no other circumferentially severed plugged tubes in the "B" OTSG. The severed plugged tube in the "A" OTSG did not degrade any of the adjacent in-service tubes because the sever was captured in the tube support plate. The corrective actions taken in response to the discovery of the condition were de-watering of 870 mechanically plugged tubes prior to plugging/re-plugging, the insertion of stabilizers into plugged tubes or the surrounding of plugged tubes with stabilized plugged tubes.
2932001001 | Pilgrim | 01/02/2001 | 02/28/2001 | ML01065022 | <strong>Swing Bus B6 Potentially Inoperable Under Certain Conditions Due to Installation of Incorrect Relays</strong><br /><i>Abstract:&nbsp;</i>Two incorrectly configured relays were installed during the 1999 refueling outage (RFO 12) in the B6 480 VAC bus transfer scheme as part of the Pilgrim Station seismic upgrade program. These relays would have prevented swing bus B6 from transferring to the alternate supply under certain design basis conditions. The inability of B6 to transfer would have prevented the low pressure coolant injection isolation valves from opening to perform their safety function. The cause for installation of the nonconforming relays was failure to detect the mismatch between the relay label and contact configuration by the manufacturer and by a commercial dedication organization during the qualification process. Corrective actions restored the design basis requirements for the B6 transfer scheme. This report meets the reporting requirements of 10 CFR 21 for nonconforming materials installed in safety-related applications. This event occurred at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was about 1035 psig with the water temperature at the saturation temperature for that pressure. This event posed no threat to public health and safety.
2932001002 | Pilgrim | 01/30/2001 | 04/21/2004 | ML04120068 | <strong>CRHEAFS Unable to Maintain Control Room Positive Pressure at One Location</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2001, the Pilgrim Station Control Room high efficiency air filtration system (CRHEAFS ) failed to adequately pressurize one door of the Control Room during a test to support plant design change PDC 99-18. Troubleshooting determined the ventilation pressure in the access control area outside the Control Room was higher than expected. The root cause determined the original plant designers did not recognize that a non-safety related HVAC system could cause a safety related system to fail to meet its design condition. Corrective actions included revision of procedures to have operators secure the ventilation to the access control area outside the Control Room when CRHEAFS is required to operate. A review of safety related HVAC systems has determined that no additional safety related HVAC systems would be adversely affected by non-safety related HVAC systems. This condition occurred at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was about 1035 psig with the water temperature at the saturation temperature for that pressure. This condition posed no threat to public health and safety.
2932001003 | Pilgrim | 04/21/2001 | 06/20/2001 | ML01177030 | <strong>ESF Actuations Due to Invalid Water Level Indications</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2001, Pilgrim Station was cooling down to begin refueling outage 13. At approximately 8:52 A.M. an invalid Group 1 isolation signal closed the main steam isolation valves. The reactor vessel pressure had decreased to approximately 100 psig when vessel level indication notching caused the isolation and subsequent Group 2 and Group 6 isolations. The Reactor Core Isolation Cooling and High Pressure Coolant Injection systems were used in the pressure control mode to reduce reactor pressure. This condition occurred after a reactor scram that was part of a controlled shutdown to begin refueling outage 13. The reactor mode selector switch was in the SHUTDOWN position. The reactor vessel pressure varied from about 100 psig to about 230 psig with the water temperature at the saturation temperature for those pressures. The cause of the notching is believed to be inadequate venting of the pump casing and associated piping during recent control rod drive pump maintenance. Corrective actions completed before reactor restart and procedure clarifications should preclude recurrence. This condition posed no threat to public health and safety.
2932001004 | Pilgrim | 04/30/2001 | 06/28/2001 | ML01184024 | <strong>Target Rock Relief Valves' Test Pressures Exceed Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>Two Target Rock pilot assemblies for the Pilgrim Station main steam relief valves were removed during refueling outage (RFO) 13 for ASME Section XI testing. On April 30, 2001, Pilgrim Station was notified by Wyle Laboratories that the as-found relief pressures of both pilot assemblies exceeded the Technical Specification 3.6.D.1 limit of 1115 psig ± 11 psi (± 1%). The test pressures, however, were within the code allowed value of ± 3%. The cause for the as-found relief pressures exceeding the Technical Specification (TS) limit is believed to be setpoint drift. The as-installed condition of these pilot assemblies had been within the ± 1% requirement of the Technical Specifications. These assemblies will be reworked and certified for future installation. Pilot assemblies previously certified to be within ± 1% replaced the assemblies tested. The test results were received while Pilgrim Station was shut down for RFO 13. The as-found condition would not have affected performance of the valves' safety function and posed no threat to public health and safety.
2932001005 | Pilgrim | 05/16/2001 | 07/16/2001 | ML01218020 | <strong>Manual Scram While Subcritical Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2001 at 1557 hours, a reactor protection system scram signal was manually initiated due to increasing reactor water level. The event occurred during a plant startup with the reactor in a sub-critical condition. The signal resulted in the insertion of all control rods that were withdrawn at the time of the event. The root cause was the failure to follow procedure. A test engineer changed the preferred lineup for a leak test of a valve. The lineup resulted in the isolation of the reactor water cleanup system due to air introduced into the system during the test. The isolation resulted in an increase in reactor water level. Corrective action taken included satisfactory completion of the leak test. Training and test procedure revision are planned. The event posed no threat to public health and safety.
2932001006 | Pilgrim | 08/13/2001 | 10/12/2001 | ML01292055 | <strong>Automatic Scram During Surveillance Test and Subsequent Reactor Water Level Anomalies</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2001, during a transient that began at 100 percent power, an automatic scram occurred at 49 percent reactor power. The scram included automatic insertion of the control rods. About 40 minutes after the scram, safety-related reactor water level instrumentation began to trend anomalously from actual water level and caused level instrumentation to be inoperable for approximately 36 minutes. The root cause of the scram was concurrent trip of RPS channels "A" and "B". Channel "A" tripped due to a loss of Bus "A" power resulting from a surveillance procedure error. Channel "B" tripped due to high neutron flux resulting from a trip of both recirculation MG sets/pumps. The root cause of the anomalous water level indication was unique hydraulic conditions that allowed water to drain from reference legs "A" and "B". Corrective action taken included the replacement of a fuse in the recirculation MG set field circuit, and isolating the reference leg backfill system. Corrective action planned includes revising the surveillance procedure, and evaluating options to preclude reference leg water draining. The events posed no threat to public health and safety.
2932001007 | Pilgrim | 12/27/2001 | 02/25/2002 | ML02123032 | <strong>Automatic Scram During Transient Caused by Failure of Calibrating Unit</strong><br /><i>Abstract:&nbsp;</i>On December 27, 2001 at 1321 hours, an automatic Reactor Protection System scram signal and scram occurred during a surveillance test performed while at 100 percent reactor power. The scram resulted in the automatic insertion of all control rods. The direct cause of the scram was an automatic trip of both Recirculation System motor-generator sets that caused decreased core flow resulting in a trip signal from the neutron monitoring system flow control trip reference circuits. The root cause of the scram was an internal failure, during the required surveillance test, of an analog trip system calibrating unit that was not reproducible. Circuit analysis identified the most likely failed component within the unit was an intermittent micro-switch. A failed micro-switch would apply a voltage from the calibrating unit to a selected master trip unit while rotating the same rotary selector switch between channels. Corrective action taken included replacement of the suspect calibrating unit. The event posed no threat to public health and safety.
2982001001 | Cooper Station | 01/17/2001 | 03/12/2001 | ML01079038 | <strong>Confusing or Incomplete Standards and Administrative Controls Resulted in Failure to Test an Excess Flow Check Valve</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2001, it was determined that an excess flow check valve (EFCV) located on the Reactor Vessel head seal leak detection line had not been tested in the last 18 months, as required by Cooper Nuclear Station (CNS) Technical Specification (TS) Surveillance Requirement (SR) 3.6.1.3.8. The EFCV was declared inoperable and the appropriate TS action was entered. This event resulted from decisions based on a past standard (confusing standard) which permitted exceptions described in TS Bases to be used as justification for not complying with a TS SR. Also, the Improved TS conversion project only required the review of new TS Bases which did not ensure that there were no exceptions described in the pre-Amendment 178 TS Bases (incomplete administrative controls). Immediate corrective actions included completing a review of the individual TS Bases sections effective just prior to Improved TS conversion (Amendment No. 178, issued July 31, 1998) for wording that could lead to a similar TS violation. The long term corrective actions consist of further evaluation of the EFCV to determine its safety function, and to revise the appropriate CNS Policy document(s) to clearly state a TS verbatim compliance policy.
2982001002 | Cooper Station | 03/03/2001 | 04/30/2001 | ML01127017 | <strong>Ineffective Operating Crew Performance in Maintaining Positive Reactor Water Level Control During a Reactor Shutdown Resulted in an Automatic Actuation of the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2000, the plant was proceeding with a planned shutdown in preparation for a Mid-Cycle Outage (MCO). Following the planned manual scram at 0942 Central Standard Time (CST), positive reactor water level control was not continuously maintained. The "B" feedwater pump turbine tripped at the vessel high water level set point at approximately 0945 CST. Reactor Water Cleanup (RWCU) blowdown to the main condenser isolated on high heat exchanger discharge temperature. Digital Electro-Hydraulic control was initiated to lower pressure. Then the Reactor Core Isolation Cooling (RCIC) system was initiated and began injection. An automatic reactor scram signal actuated at approximately 1028 CST due to low water level. As water level began to rise, RCIC flow was reduced. Water level began to lower and a manual scram was initiated. Positive level control was then re-established. The cause of the event was ineffective operating crew performance exacerbated by equipment problems and weaknesses in procedures and training. Immediate corrective actions included inspection, testing, and repair of equipment, revisions to procedures, re-assignment of selected crew personnel, and additional simulator training. These actions occurred prior to startup from the MCO. Long term corrective actions include development of new crew selection criteria, and implementation of planned high intensity training and self-assessment activities for the operating crews.
2982001003 | Cooper Station | 05/09/2001 | 07/06/2001 | ML01191015 | <strong>Failure to Adequately Revise Procedures Resulted in Inadequate Fire Watches Under Certain Battery/Battery Charger Configurations and an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>The station's direct current (DC) electrical system (EIIS:EJ) consists of two independent banks of 125 volt and 250 volt batteries (Division I, "A" and Division II, "B" trains) with associated battery chargers. When a battery charger(s) is removed from service for maintenance, a substitute charger(s) ("C") is then connected so that both independent banks of batteries can remain in service. The "B" charger(s), with qualified repair procedures, support post-fire 10CFR50, Appendix R safe shutdown requirements in certain fire zones. The station is required to post a fire watch whenever the "C" charger(s) is used in lieu of the "B" charger(s) because equivalent repair procedures do not exist for the "C" charger(s). On May 9, 2001, it was determined that inadequate compensatory fire watches were posted after placing the 125/250 volt "C" battery charger(s) in service on three separate occasions during the time frame from December 1998 to July 2000. The lack of a fire watch was not analyzed in the station's fire protection safe shutdown analysis. The cause was determined to be human error resulting in a failure to incorporate all the required compensatory fire watches in station procedures when they were revised in 1992. Immediate corrective actions included the generation of a Standing Order to address the necessary fire watches and then revision of the appropriate plant procedures to require fire watches in all the necessary fire zones whenever the "C" battery charger is substituting for the "B" charger. The individual responsible for the procedural inadequacies completed a training lesson on human performance including information on error prevention tools.
2982001004 | Cooper Station | 09/07/2001 | 11/06/2001 | ML02016047 | <strong>Loss of Both Offsite Power Sources Due to Lightning</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2001, the plant was operating at 100% power during an early evening lightning storm. A combination of a lightning strike occurring on a 161 kilovolt (kV) transmission line, with equipment malfunctions, resulted in the loss of the preferred offsite alternating current (AC) source at 1750 Central Standard Time (CST). Subsequent voltage perturbations, due to the storm, on the 69 kV sub-transmission system which supplies the emergency offsite AC source, resulted in the loss of the second offsite AC source at 1754 CST due to low voltage. A complete loss of the second offsite AC source occurred at 2230 CST. The cause of the loss of both offsite power sources during the lightning strikes was that standards, policies and administrative controls to ensure maintenance and testing of switchyard equipment were not adequate to detect degradation of certain key equipment important to offsite power prior to failure. Thus, the offsite power switching circuitry was vulnerable to perturbations and failure. Immediate corrective actions included inspection, testing, restoring equipment to service, replacing and repairing equipment and revising equipment testing. Long term corrective actions include determining acceptance criteria, identifying major switchyard equipment important to offsite power and reviewing procedures for test adequacy, acceptance criteria and test frequency.
2982001005 | Cooper Station | 10/17/2001 | 12/17/2001 | ML02024033 | <strong>High Pressure Coolant Injection (HPCI) Overspeed Trip Reset Valve Spring Failure Results in HPCI Unavailability</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2001, at 14:30 Central Standard Time, the High Pressure Coolant Injection (HPCI) System was declared inoperable when the HPCI trip mechanism did not automatically reset during the quarterly Inservice Test (IST) and Technical Specification (TS) surveillance. At the time when the system was declared inoperable, the plant was operating at approximately 99 percent power. The inability to reset the trip mechanism resulted from a failure of an actuator spring associated with the system mechanical hydraulic overspeed trip auto-reset control valve. The cause of this event was age degradation of the spring. Immediate actions consisted of replacement of the valve actuator spring and diaphragm, re-running the IST and TS surveillances, and declaring HPCI operable. Long term corrective actions include preparing a preventive maintenance order to replace the valve assembly at ten year intervals from date of manufacture.
2982001006 | Cooper Station | 11/02/2001 | 12/28/2001 | ML02045018 | <strong>Scheduling Error and Oversight Results in Loss of Reactor Building-to-Suppression Chamber Vacuum Relief Function</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2001, the plant was operating at 94 percent power during end-of-cycle coast down when both reactor building-to-suppression chamber vacuum relief lines were made inoperable for opening. The control switches for the air operated vacuum breaker valves in each line were simultaneously placed in the "Close" position thereby precluding the ability to automatically relieve vacuum in the suppression chamber. This action was taken in conjunction with performing a tagout for a local leak rate test (LLRT) which was to be performed while the plant was operating. The planned LLRT would have affected only one vacuum relief line at a time, necessitating only one switch at a time to be placed in "Close." However, the action to place both control switches from "Auto" to "Close" was specified on the clearance order, which would have been appropriate for only cold shutdown or refueling conditions. This improper planning was identified as the first root cause. Subsequently, the senior reactor operator responsible for authorizing the clearance did not recognize the impact on the vacuum relief function of placing both control switches to "Close." This personnel error was identified as the second root cause. Immediate corrective action involved returning the vacuum breaker control switches to "Auto." Interim corrective actions were taken to prevent recurrence during the current outage. Additional corrective actions to prevent recurrence involve process and procedure improvements. Reference LER 2000-009 for similar event.
2982001007 | Cooper Station | 11/09/2001 | 01/08/2002 | ML02031038 | <strong>Excessive Primary Containment Leakage Discovered During Local Leak Rate Testing of Reactor Feedwater Check Valves</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2001 during refuel outage RE20, due to exceeding the test equipment capability, local leak rate tests (LLRTs) could not quantify the valve leakage through three of the four reactor feedwater check valves (RFCVs). As a result the Primary Containment Leak Rate requirements of the Cooper Technical Specifications Administrative Controls Section 5.5.12 were exceeded. The plant was in Mode 5, refueling operations, at the time of discovery. All three valves were declared inoperable. The fourth RFCV passed as-found LLRT, but subsequently failed LLRT following maintenance. The root cause for the RFCVs LLRT failures is that the technical understanding of the dual (soft) seat design was incorrect. This resulted in not maintaining the metal-to-metal hard seats in a condition to provide adequate sealing capability at higher differential pressure. Immediate corrective action taken was to restore valve condition. Three RFCVs were reconditioned with the soft seat design maintained. The remaining RFCV was reconditioned with the soft seat removed. As-left LLRTs were satisfactory. Long term corrective action will be to: 1) revise the maintenance procedure to reflect lessons learned, 2) revise preventive maintenance to have the maintenance procedure actions performed each cycle, and 3) review historical LLRT records to determine if there are other primary containment isolation valves that have a history of repetitive failure.
3012001001 | Point Beach 2 | 02/06/2001 | 03/07/2001 | ML01073022 | <strong>Ground Fault Relay Actuation Causes Generator Lockout and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2001, at approximately 2150, the Point Beach Nuclear Plant (PBNP) Unit 2 tripped from 100% power. The trip was the result of a turbine generator lockout apparently caused by one of the generator stator neutral ground fault detection devices (27/59N relay). System and components required to perform following the reactor trip operated as designed with the possible exception of the cross over steam dump system. This system actuated as expected to minimize the turbine over speed; however, main condenser vacuum was lost when the dump valves apparently failed to reseat promptly. The reactor coolant system was maintained in hot standby following the trip with temperature maintained via the steam generator atmospheric steam dump valves. Following extensive trouble shooting and a thorough incident investigation, PBNP Unit 2 was restarted on February 8th. Since the exact cause for the actuation of the 27/59N relay could not be determined, the plant was returned to operation after completing a temporary modification to change the relay circuit from a generator lock out actuation to a common alarm function. Prior to 1987, the PBNP units had operated without these relays. Other installed protective relaying is available to minimize the risk of faulting due to a stator ground. The NRC was notified of this event via the ENS at 2244 on February 6, 2001. The safety and welfare of the public and the plant staff was not impacted by this event.
3012001002 | Point Beach 2 | 06/27/2001 | 08/17/2001 | ML01233012 | <strong>Manual Reactor Trip Due to Decreasing Water Level in Circulating Water System Pump Bay</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2001, at approximately 18:20, the Point Beach Nuclear Plant (PBNP) Unit 2 reactor was manually tripped with reactor power at approximately 70%. This trip was directed by procedure (AOP-13A) when the water level in the Circulating Water (CW) System pump bay decreased to less than -11 feet (normal pump bay level with four CW pumps in service is about -7 feet). The Service Water (SW) pumps also take a suction from the pump bays and -11 feet is a conservative minimum water level to assure that components serviced by the SW system will remain capable of performing their safety functions. The decrease in pump bay water level was attributed to the influx of a large number of small forage fish (Alewives) on the Unit 2 traveling water screens. This influx caused a high differential water level across the screens and ultimately resulted in the disabling of the traveling screen drive mechanism. Following the trip one of the two running Unit 2 CW pumps was secured. This action; in conjunction, we believe, with a screen failure that permitted increased water flow into the pump bay; resulted in a rapid recovery of the pump bay level. The preliminary root cause report has identified the following causal factors: ineffective implementation of previously identified corrective actions from related events, delays in operator response while in the AOP, and problems with the sequence of action steps within the procedure. With the exception of two minor equipment problems identified in the report, the operator and equipment responses to the transient were as expected and the unit was stabilized in the hot shutdown condition. Unit 2 returned to normal operation on July 1, 2001.
3022001001 | Crystal River 3 | 05/13/2001 | 07/09/2001 | ML01197003 | <strong>Installation Error Results in Containment Isolation Valve Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2001, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 85 percent RATED THERMAL POWER. While investigating a difference in main feedwater pump (MFP) discharge pressures, FPC personnel determined that feedwater check valve FWV-46 may not close as required to perform its containment isolation design function. At 1648, on May 14, 2001, FWV-46 was declared inoperable. The Actions of Improved Technical Specification (ITS) 3.6.3, Condition C, were entered. Upon disassembly, the as-found condition of FWV-46 showed that the disc had separated from the valve and wedged in the valve body outlet. FPC personnel concluded that FWV-46 became inoperable at 1525, on May 13, 2001, during an unplanned power reduction. FWV 46 was inoperable for approximately 25 hours and 23 minutes before entering the Actions of ITS 3.6.3, Condition C. This is a condition prohibited by ITS and is reportable under 10CFR50.73(a)(2)(i)(B). This condition does not represent a reduction in the public health and safety. The cause for this condition was lack of procedural guidance to ensure proper installation of the check valve disc. FWV-46 has been repaired. Changes to Maintenance Procedure MP-120 have been initiated. Three previous similar LERs have been identified.
3022001002 | Crystal River 3 | 09/26/2001 | 11/19/2001 | ML02016046 | <strong>Main Steam Safety Valve Setpoints Outside Required Tolerance Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2001, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. While performing surveillance procedure SP-650, "ASME Code Safety Valve Test," on the ‘A' Once Through Steam Generator (OTSG) main steam safety valves (MSSVs) MSV-33 and MSV-42 setpoints were found outside their required tolerance. Improved Technical Specification (ITS) 3.7.1 states that the MSSVs shall be operable as specified in Table 3.7.1-1 in MODES 1, 2 and 3. With one or more required MSSVs inoperable, THERMAL POWER shall be reduced to less than the reduced power limit of Table 3.7.1-1 within 4 hours and the nuclear overpower trip setpoint shall be reduced in accordance with Table 3.7.1-1 within 12 hours. The existence of similar discrepancies in multiple relief valves is an indication that the discrepancies may have developed over a period of time. Therefore, FPC concludes that the condition existed during plant operation and the event is reportable under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by ITS. This condition does not represent a reduction in the public health and safety. The most probable causes for this condition were disc/seat bonding and/or aging. MSV-33 and MSV-42 were adjusted and/or retested satisfactorily. Previous similar occurrences within the last three years have been identified that were not reported to the NRC.
3022001003 | Crystal River 3 | 10/04/2001 | 12/03/2001 | ML02043019 | <strong>Small Pressure Boundary Leak Found in Reactor Coolant Pump Heat Exchanger Resulting in Radionuclide Intrusion Into Closed Cycle Cooling System</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2001, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) at zero percent RATED THERMAL POWER. While investigating the source of elevated levels of radionuclide activity in the Nuclear Services Closed Cycle Cooling System (SW), CR-3 personnel identified a small leak in the drilled-hole heat exchanger on Reactor Coolant Pump 1B (RCP-1 B), which is part of the Reactor Coolant System (RCS) pressure boundary. Although this leakage was not identified during power operation, FPC concludes that the condition is RCS pressure boundary leakage and is reportable under 10CFR50.73(a)(2)(i)(B) and 50.73(a)(2)(ii)(A). This condition does not represent a reduction in the public health and safety due to the small size of the leak (less than 0.02 gallons per minute). The location of the leakage site precluded direct observation or acquiring metallurgical samples. Consequently, the root cause of the leak and failure mechanism is uncertain. The leak site was isolated by plugging the RCP-1 B drilled-hole heat exchanger and verified by post-modification testing. CR-3 resumed power operation on October 25, 2001. Since startup, radionuclide activity levels in the SW system have been decreasing, providing confirmation that the RCS leakage has been eliminated. There have been no previous occurrences of an RCS leak to the SW system through an RCP heat exchanger.
3022001004 | Crystal River 3 | 10/01/2001 | 11/28/2001 | ML02016022 | <strong>Reactor Pressure Vessel Head Leakage Due to Control Rod Drive Mechanism (CRDM) Nozzle Degradation</strong><br /><i>Abstract:&nbsp;</i>At 1300, on October 1, 2001, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 5 (COLD SHUTDOWN) at 0 percent RATED THERMAL POWER. While performing a visual inspection of the reactor vessel head (RVH), FPC personnel identified one potential leaking CRDM nozzle (nozzle #32). The RVH inspection was performed to satisfy a commitment made by FPC in response to NRC Bulletin 2001-01, "Circumferential Cracking of Reactor Pressure Vessel Head Penetration Nozzles." At approximately 1748, on October 8, 2001, CR-3 was in MODE 6 (REFUELING) at 0 percent RATED THERMAL POWER. Ultrasonic testing (UT) examination of RVH nozzle #32 identified the leakage path as two (2) axially oriented cracks that were through-wall. An 8-hour notification was made to the NRC in accordance with 10CFR50.72(b)(3)(ii)(A) due to confirmation of Reactor Coolant Pressure Boundary leakage while at power. The cracks were caused by primary water stress corrosion cracking. Eight (8) additional CRDM nozzles were examined using UT. No evidence of cracking was observed in the additional CRDM nozzles inspected. RVH nozzle #32 was repaired using the repair technique described in CR-3 Relief Request 01-0002-RR. CR3 is developing a long-term strategy to deal with the CRDM nozzle-cracking issue. No previous similar CR-3 occurrences have been reported to the NRC.
3022001005 | Crystal River 3 | 10/24/2001 | 02/26/2004 | ML04065044 | <strong>Loss of Steam to the Operating Main Feedwater Pump Results in Actuation of the Emergency Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2001, Florida Power Corporation's (FPC) Crystal River Unit 3 (CR-3) was in MODE 3 (HOT STANDBY) at 0 percent RATED THERMAL POWER. Once through steam generator (OTSG) levels were being maintained by the "B" steam-driven main feedwater pump (FWP-2B). Auxiliary steam (AS) (motive steam) to FWP-2B was being supplied from the Crystal River Unit 1 (CR-1) coal-fired plant. The Crystal River Unit 2 (CR-2) coal-fired plant, which can also supply AS to CR-3, was in a scheduled maintenance outage. At approximately 1000, CR-1 tripped, causing a loss of AS to FWP-2B. The loss of steam resulted in a loss of main feedwater(FW) and the actuation of the emergency feedwater system (EFW) on low OTSG levels. EFWactuated and functioned as designed to restore OTSG levels. CR-1 was restarted and AS fromCR-1 was restored to CR-3 at approximately 1643. FW was reestablished to the OTSGs and EFW was secured at approximately 1748. The cause of the event was the unexpected loss of the only available source of AS during plant startup. The planned corrective actions have been modified to limit activities which could reduce the availability of systems needed to respond to a loss of FW if a CR-3 shutdown occurs simultaneously with a shutdown of CR-1 or CR-2. Previous similar events at CR-3 were reported in LERs 50-302/86-021-00 and 50-302/99-004-00.
3052001001 | Kewaunee | 01/18/2001 | 05/01/2001 | ML01127028 | <strong>Single Barrier Appendix R Fire Door Failed to Close - Door Had Not Been Part of a Periodic Test Program</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2001, with the reactor at 97 percent power, an Appendix R fire barrier door failed to close completely. The door separates A and B trains of the service water (SW) system equipment. The door failed during the performance of a maintenance procedure (PMP 08-19). Immediate actions were taken to close the door. This event is being reported because an Appendix R required door failed to close and no documentation exists to demonstrate past door performance. Consequently, there is no evidence to indicate that the door was capable of fulfilling its design function since a test last performed in 1993. A protective feature of the door is that when a fusible link melts, the door automatically closes to assure separation of the SW trains in the event of a fire. The root cause investigation determined that a lack of door operation and maintenance caused the door to fail. It also determined that failure to adequately manage changes to the fire protection program plan resulted in not developing adequate guidance for operating and testing the door. Corrective actions will include reviewing program plan requirements and ensuring procedures are adequate and making procedure revisions where necessary. The risk analysis of a fire in the screenhouse with an inoperable fire door shows an increase in risk of 2.2E-7.
3052001002 | Kewaunee | 02/14/2001 | 08/26/2003 | ML03252060 | <strong>Non-Rated Fire Barrier Separating Redundant Appendix R Safe Shutdown Capabilities</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2001, with the reactor at 96 percent power, Kewaunee Engineering staff determined there was insufficient test documentation available to support the fire rating of a 10CFR50, Appendix R, fire barrier. The barrier, Identified as PB 2105, was constructed to separate Train "A" (dedicated) safe shutdown equipment cables that are routed in a Train "B" (alternate) safe shutdown equipment room. This event is being reported because barriers constructed to demonstrate conformance with 10CFR50, Appendix R, are required to have a three-hour fire rating. The barrier was installed in the 1984 to 1985 time frame. Subsequent inspections of the barrier also recognized the configuration not being in accordance with Appendix R. The root cause analysis of the event determined that Kewaunee plant staff failed to provide adequate fire protection program monitoring and management because the significance of fire protection as a licensing basis program was not emphasized. Significant contributing factors identified were; 1) Fire Protection lacked in-house expertise, which contributed to inadequate verification of contractor-supplied engineering evaluations, and 2) fire protection program engineering evaluations did not require independent review. A fire hazards analysis calculated the equivalent fire loading in the area of PB 2105 to be thirty minutes. Underwriters Laboratory approved testing was conducted on an identical enclosure design. The testing showed that the enclosure would survive an equivalent fire for the area. Analysis and testing showed the condition to be of very low safety significance. Compensatory measures required by the Kewaunee fire plan for an inoperable fire barrier were in place and remained in place until the pull box was redesigned to comply with Appendix R requirements. Corrective actions to address the root cause analysis have been completed.
3052001003 | Kewaunee | 02/21/2001 | 04/23/2001 | ML01116011 | <strong>Single Barrier Appendix R Doors Installed Improperly - The Closure Actuation System Did Not Conform to Code</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2001, with the reactor at 97% power, plant engineering staff discovered that two Appendix R single barrier doors had their actuation equipment installed improperly. As a result, the doors would not operate according to design and National Fire Protection Association (NFPA) 80, the standards for fire doors and fire windows. The doors are designed to close when any one of three fusible links melt. As installed, one of the three, fusible links would not have caused the door to close, due to improper actuation chain routing. Additionally, no fusible links were installed at the ceiling as required by the Code. Consequently, the doors may not have fulfilled their intended design function to separate dedicated equipment from alternate equipment in the event of an Appendix R design basis fire. The doors were installed in the fall of 1984. It is likely that the condition existed since their installation. The doors were installed incorrectly due to a lack of detailed installation instructions and a lack of familiarity with the code requirements. Corrective actions were to keep the doors closed to remove any reliance on the automatic closure design. A fire hazards review of the vulnerability of the doors failing to close revealed a likely minimal impact. The effects of a small volume oil fire, the hazard of concern, revealed the impact would at most only cause a loss of one of two available service water pumps needed to meet Appendix R requirements.
3052001004 | Kewaunee | 06/20/2001 | 08/20/2001 | ML01233024 | <strong>Air Volume Booster Diaphragm Failure Results in RPS Actuation and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On 6/20/01 at 0011 CDT, while the plant was operating at ninety-six percent power, a Reactor Protection System (RPS) actuation occurred when the feedwater (FW) regulating valve (FW-7B) to the "B" steam generator failed to the closed position. All other safety-related equipment operated as expected. Feedwater is regulated by 12-inch air-operated valves (AOV) (FW-7A and FW-7B). An Air Volume Booster is in line with each valve actuator to assist in air bleed off during a feedwater isolation signal. During the post-trip recovery, plant personnel inspected the Air Volume Booster for FW-7B and identified a tear in the diaphragm. The root cause of this event is the "running to failure" maintenance schedule for FW Regulating Valve Volume Booster Relays. This event was reported in accordance with 10CFR50.72(b)(1)(iv)(B) as a valid RPS actuation. This event was analyzed from a Probabilistic Risk Assessment (PRA) perspective. The incremental core damage probability (ICDP) and incremental large early release probability (ILERP) were 4.66E-09 and 5.26E-12, respectively. Thus, this event was of negligible safety significance. The Air Volume Boosters for both FW-7A and FW-7B were replaced. Following repairs, the reactor became critical on June 21 at 0225 CDT, and the plant output breaker was closed at 1205 CDT. Full power was reached on June 22, 2001 at 1050 CDT.
3052001005 | Kewaunee | 10/09/2001 | 03/21/2002 | ML02092053 | <strong>Unanalyzed Condition: Non-Safety Related Service Water Header Flows Affects Safety Related Components</strong><br /><i>Abstract:&nbsp;</i>On 10/9/01, while the plant was in refueling shutdown, Nuclear Management Company (NMC) determined that an analyzed Service Water (SW) flow to the non-safety related turbine building SW header may be exceeded under postulated accident conditions. The increased turbine building SW flow (and subsequent decreased safety related SW flow) could have impacted the ability of the safety related SW flow to remove the design basis heat loads from safety related components. Due to the length of time since plant design, NMC did not determine whether 1) the original designers failed to realize this potential design interaction or 2) they considered manual isolation of the turbine building as a design input, thus negating the impact of the non-safety related SW flow in the turbine building on the safety related components. NMC installed a design change to the turbine building SW header isolation valves to automatically isolate on a Safety Injection sequence signal concurrent with low SW header pressure. Also, NMC implemented administrative controls to require appropriate plant configuration in the event an affected component becomes inoperable. NMC plans to submit a License Amendment Request to change the KNPP Technical Specifications to include these controls. This event was characterized by the KNPP PRA as having very low risk significance.
3062001001 | Prairie Island 2 | 04/10/2001 | 06/06/2001 | ML01141021 | <strong>Failure to Meet Technical Specification Limiting Condition for Operation Verification Within Eight Hour Limit Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2001, testing of the Unit 2 emergency diesel generator D6 was being performed. At 0845, surveillance procedure SP2307, "D6 Diesel Generator 6 Month Fast Start Test" was begun as part of the requirement to complete surveillance procedure SP2335, "D6 DG 18 Month 24 Hour Load Test". At 0930, at the normal step in SP2307, D6 was removed from service and Technical Specification 3.7.B.1 was entered. Technical Specification (TS) 3.7.B.1. Limiting Condition for Operation (LCO) requires, in the event of the inoperability of one of the unit's two emergency diesel generators: "One diesel generator may be inoperable for 7 days provided ... (d) the OPERABILITY of the two required paths from the grid shall be verified OPERABLE within 1 hour and at least once per 8 hours thereafter." For item (d), the OPERABILITY of the two required paths from the grid was verified at approximately 0855 and 1505 via SP2118, "Verifying Paths from the Grid to Unit 2 Busses." However, at 0130 on April 10, 2001, it was discovered that the eight hour limit for the next verification had been exceeded. Eleven minutes later, at 0141, SP2118 was completed satisfactorily and within the eight hour limit thereafter until D6 was returned to service on April 17, 2001. Several corrective actions to improve the surveillance procedures involved in grid verification, to improve clock management, and to improve shift turnover communications have been initiated to address issues determined to have contributed to this event.
3062001002 | Prairie Island 2 | 04/16/2001 | 06/15/2001 | ML01171003 | <strong>Emergency Diesel Generator Out of Service Longer than Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2001, the Prairie Island D6 emergency diesel generator (EDG) exceeded the Allowed Outage Time (AOT) of Technical Specification 3.7.B.1, which allows one EDG to be inoperable for up to seven days. D6 was declared out of service on April 9, 2001, for a 24-hour surveillance run. That run was terminated by operators when D6 engine 2 developed high crankcase pressure. On April 16, 2001, Prairie Island requested a Notice of Enforcement Discretion (NOED) to extend the D6 AOT to ten days to allow completion of the necessary repair and testing to restore D6 operability. The NRC granted the NOED on April 16, 2001. D6 was repaired, tested, and declared operable on April 17, 2001. Subsequent events dealing with D6 (and D5) will be addressed in LER 2-01-03.
3062001003 | Prairie Island 2 | 05/09/2001 | 11/30/2001 | ML02009011 | <strong>Technical Specification Required Shutdown of Unit 2 Due to Declared Inoperability of Both Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>At approximately 3:00 PM on May 9, 2001, Prairie Island personnel declared the Emergency Diesel Generators (EDGs) for Unit 2 (D5 and D6) inoperable based on a suspected lube oil/fuel oil incompatibility that had the potential for affecting the ability of the EDGs to perform their design basis safety functions. A Unit 2 shutdown was commenced at approximately 5:00 PM on May 9, 2001 pursuant to the Prairie Island Technical Specifications. Following the May 9, 2001 shutdown, Prairie Island personnel performed detailed inspections, surveillance testing, and maintenance on both D5 and D6, including replacing the lube oil with the type now recommended by the EDG vendor for use with the low sulfur fuel oil currently used at Prairie Island. An outside diesel expert was contracted to perform an investigation of the problems encountered on D6, including laboratory analyses of some replaced components. Upon completion of the inspections, maintenance, investigation, analyses, and surveillance testing, D5 and D6 were declared operable and Unit 2 was subsequently restarted (left Mode 5) on June 1, 2001. Subsequent analysis of the conditions of the EDGs versus the limiting design basis parameters concluded that the EDGs had been degraded but not inoperable.
3062001004 | Prairie Island 2 | 05/09/2001 | 07/06/2001 | ML01193009 | <strong>Manual Turbine Trip/Reactor Trip due to High Differential Condenser Backpressure</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2001, Unit 2 was undergoing an orderly shutdown as a result of the declared inoperability of D5 and D6 Diesel Generators (Unit 2 LER 01-03). At about 2006, with the reactor at 12% power, the turbine was manually tripped when 2A/2B Condenser differential pressure reached 2.5" Hg. The reactor tripped automatically as a result of the turbine trip. After the trip, vacuum continued to decrease in both condensers until vacuum was completely lost by 2047. After the vacuum loss, water was observed coming from the condenser air ejector discharge to atmosphere. Additional operator checks of the air ejectors noted water in the air ejector flowmeter, and that the 2B Condenser air ejector suction piping was hot while 2A Condenser piping was at ambient temperature. Actions were taken to drain the water from the air ejector discharge. At approximately 2243, condenser vacuum began a slow recovery without any significant operator intervention other than draining the discharge line. Vacuum was fully recovered by approximately 0945 on May 10.
3062001005 | Prairie Island 2 | 10/31/2001 | 12/21/2001 | ML02032041 | <strong>Manual Reactor Trip on Unit 2, Initiated in Response to a High Differential Pressure Between the Turbine Steam Condensers, Caused by an Inadvertent Venting of One Condenser While Isolating a Steam Leak</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2001, at approximately 1409, Unit 2 Reactor was manually tripped from 100% power when 2A/2B Condenser differential pressure reached 2.5 inches Hg. A steam leak on the body of 21 air ejector main steam supply control valve had been identified on October 24, 2001. Plans were made to temporarily repair the steam leak by installing an enclosure box around the valve and its proximate piping and injecting leak sealant. As part of this planning a contingency action plan was developed to isolate the leak if further degradation of the valve occurred. On October 31, 2001, temporary repairs to stop the leak were started by installing an enclosure box and injecting leak sealant. While preparing to inject the last stick of sealant, the enclosure box unexpectedly shifted. Due to a concern that the valve may have degraded further, with a potential for a steam release, the Shift Supervisor made a conservative decision and ordered an immediate evacuation of the Unit 2 Turbine Building. While performing the steps of the contingency action plan to isolate and bypass the control valve, vacuum was lost faster in 2A condenser than in 2B condenser. When the vacuum differential pressure between the condensers reached 2.5 inches Hg the reactor/turbine was manually tripped as required by procedure. The post-trip recovery was normal.
3112001002 | Salem 2 | 06/06/2001 | 08/06/2001 | ML01219008 | <strong>Containment Spray Additive Tank Exceeded Technical Specification Limit Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2001, it was identified that Salem Unit 2 operated with the Containment Spray (CS) system Spray Additive Tank (SAT) Sodium Hydroxide (NaOH) concentration below the TS 3.6.2.2 lower concentration limit of 30% weight/weight (w/w) for greater than the LCO of 72 hours. During the performance of a scheduled TS Surveillance of the SAT on May 7, 2001, it was identified that the NaOH concentration was 28.4% w/w. The SAT concentration was returned to appropriate TS NaOH concentration on May 8, 2001. Follow-up investigation of this event identified that the tank had been below the lower concentration limit for greater than the AOT of 72 hours. Based on the SAT isolation valve leakrate, the SAT Sodium Hydroxide concentration could have been out of spec for as much as 109 days. The apparent cause of the concentration dilution was a combination of gradual backleakage through the isolation valves from the RWST and inadequate SAT level trending. Corrective actions to be completed include repair of leaking isolation valve(s) and review of operational trending practices of the SAT parameters. There were no actual safety consequences associated with this event. The consequences of identified reduced NaOH concentration (28.4% w/w) would have had no impact on the radiological consequences of an accident. An analysis performed concluded that with a concentration as low as 28 % w/w the system was capable of meeting all required design functions in the event of a Large Break Loss of Cooling Accident (LB LOCA).
3112001003 | Salem 2 | 06/06/2001 | 08/13/2001 | ML01229006 | <strong>Containment Spray Additive Tank Exceeded Technical Specification Limit Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2001, it was identified that Salem Unit 2 operated with the Containment Spray (CS) system Spray Additive Tank (SAT) Sodium Hydroxide (NaOH) concentration below the TS 3.6.2.2 lower concentration limit of 30% weight/weight (w/w) for greater than the LCO of 72 hours. During the performance of a scheduled TS Surveillance of the SAT on May 7, 2001, it was identified that the NaOH concentration was 28.4% w/w. The SAT concentration was returned to appropriate TS NaOH concentration on May 8, 2001. Follow-up investigation of this event identified that the tank had been below the lower concentration limit for greater than the AOT of 72 hours. Based on the SAT isolation valve leakrate, the SAT Sodium Hydroxide concentration could have been out of spec for as much as 109 days. The apparent cause of the concentration dilution was a combination of gradual back leakage through the isolation valves from the RWST and inadequate SAT level trending. Corrective actions to be completed include repair of leaking isolation valve(s) and review of operational trending practices of the SAT parameters. There were no actual safety consequences associated with this event. The consequences of identified reduced NaOH concentration (28.4% w/w) would have had no impact on the radiological consequences of an accident. An analysis performed concluded that with a concentration as low as 28% w/w the system was capable of meeting all required design functions in the event of a Large Break Loss of Cooling Accident (LB LOCA).
3112001004 | Salem 2 | 07/26/2001 | 09/21/2001 | ML01271028 | <strong>Missed Technical Specification Requirement for Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On August 10, 2001, PSEG Nuclear identified that a failure to comply with Salem Unit 2 Technical Specification (T/S) 3.6.3, Containment Isolation Valves had occurred on July 26, 2001. T/S 3.6.3 requires that an inoperable penetration be isolated by use of at least one deactivated automatic valve. Maintenance on the 2SJ12 Boron Injection Tank Outlet Valve, a listed containment isolation valve, was conducted. Redundant automatic valves 2SJ4/5 were placed in the closed position to support the maintenance. Contrary to T/S 3.6.3, the redundant automatic valves were not deactivated. The apparent cause of the failure to comply with T/S was due to inconsistent information in the Salem UFSAR and Salem In Service Testing (IST) manual valve data sheets in that valve 2SJ12 was not clearly identified as a containment isolation valve. Corrective actions include: • The licensing and design basis of valve 2SJ12 and other valves included in Salem USFAR Table 6.2-10 will be reviewed in order to identify similar problems. • An analysis of previously identified T/S compliance and administration issues over the past two years at Salem will be conducted. • A review of this event will be conducted with licensed operators. The safety significance of this event was minimal in that the affected penetration was isolated and its safety function is to open upon a safety injection signal. This condition is being reported in accordance with the requirements of 10OCFR50.73(a)(2)(i)(B) as "Any operation or condition that was prohibited by the plant's Technical Specifications..."
3112001006 | Salem 2 | 09/06/2001 | 11/01/2001 | ML02032037 | <strong>ECCS Leakage Outside Containment Exceeded Dose Analysis Limits</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2001, elevated temperatures were identified on the 2CV49 valve leak off line. The 2CV49 valve is a manual valve on the suction of the 22 Charging/Safety Injection pump (high-head safety injection). At this same time the Reactor Coolant System (RCS) unidentified leakage rate had increased to 0.26 gpm. The packing for valve 2CV49 was adjusted on September 6, and an RCS leakage was measured. The RCS unidentified leakage rate following the packing adjustment to 2CV49 was determined to be 0.15 gpm. Equating the amount of unidentified RCS leakage before and after the packing was adjusted on the 2CV49 valve would conservatively quantify the leakage through the 2CV49 packing at 0.11 gpm. The leakage from 2CV49 is classified as unfiltered leakage since it is not directed through a charcoal filter. The 0.11 gpm of unfiltered leakage exceeds the LOCA dose analysis assumption for emergency core cooling system leakage outside containment. The cause of this event is attributed to having the wrong packing configuration and torque requirements specified on the packing data sheet for valve 2CV49. Although the torque on the packing was adjusted and the leakage through the valve diminished, a work order was initiated to repack the 2CV49 valve to the correct packing configuration. The packing data sheet for 2CV49 will also be corrected to reflect the correct packing configuration and torque requirements. This event is reportable in accordance with 10CFR50.73(a)(2)(v), "any event or condition that could have prevented the fulfillment of the safety function of structures or system that are needed to.... (C) control the release of radioactive material; or (D) mitigate the consequences of an accident."
3112001007 | Salem 2 | 09/23/2001 | 11/21/2001 | ML02017030 | <strong>Inadequate Verification Results in Technical Specification 3.6.3 Not Being Met</strong><br /><i>Abstract:&nbsp;</i>The containment isolation valves for No. 22 Containment Fan Coil Units (CFCU) {BI/ISV} are 22SW58 and 22SW72. On September 24, 2001 at 0600 it was identified that valves 22SW58 and 22SW72 had been inoperable since September 23, 2001 at 1610. This inoperability was caused by the tagging of 125 VDC breaker 2BDC2AX27 open in preparation for scheduled work to support an 85-hour maintenance window. At 0645 hours on September 24, 2001, operators closed valves 22SW54 and 22SW646, 14 hours and 35 minutes after Containment Isolation valves were rendered inoperable, isolating the penetration and exiting TS 3.6.3. This event was attributed to human error; failure to properly evaluate the impact of tagging the 125-volt breaker after changes had modified the extent of maintenance window work scope. Corrective actions include properly isolating the Containment Fan Coil Units (CFCU) and adding further clarification to plant documents rolling lessons-learned out to those organizations involved with tagging of equipment. There were no actual safety consequences associated with this event. At the time of event, the service water system was in operation, with system pressure higher than any potential high pressure within the containment. There would have been no impact on the radiological consequences of an accident, even with the containment isolation valves being open. This condition is being reported in accordance with the requirements of 10CFR50.73(a)(2)(i)(B) as "Any operation or condition that was prohibited by the plant's Technical Specifications..."
3112001008 | Salem 2 | 12/31/2001 | 02/28/2002 | ML02071067 | <strong>Reactor Trip Due to Pressurizer Spray Valve 2PS3 Failure</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2001, at approximately 0009 hours, with Salem Unit 2 operating at 100 percent power, an automatic reactor trip followed by a safety injection (SI) actuation occurred. Earlier, the Reactor Coolant System Pressurizer "low pressure/heaters on" alarm had annunciated and the operators observed Pressurizer pressure decreasing. The Pressurizer master controller called for no sprays and more heaters. Both spray valve controllers demanded closing. Spray valve 2PS1 indicated full closed (green light), but 2PS3 indicated mid-position (no red or green lights). The control room operator attempted to manually close the 2PS3 spray valve from the control console, but the valve failed to respond. The control room supervisor (CRS) directed the reactor operator to take the master controller to manual and attempt to close the valve, but the valve still did not respond. The CRS entered the abnormal operating procedure (AOP) for Pressurizer pressure malfunction and the operations superintendent recommended initiation of a manual reactor trip and stopping No. 23 reactor coolant pump (RCP). As the CRS was acknowledging the recommendation, the unit tripped on over-temperature delta-T (OTDT) followed shortly thereafter by a safety injection on low Pressurizer pressure signal. The cause of this event was the Pressurizer spray valve 2PS3 failing to an open position. The valve failed to this open position because of a broken position feedback linkage. The position feedback linkage was replaced on both Unit 2 Pressurizer spray valves and Unit 2 returned to service. This event is reportable in accordance with 10CFR50.73 (a)(2)(iv)(A).
3132001001 | Arkansas 1 | 01/05/2001 | 02/05/2001 | ML01040016 | <strong>Manual Reactor trip Due to Excessive Main Generator Hydrogen leakage Caused by a Failed Generator Vent Line</strong><br /><i>Abstract:&nbsp;</i>On January 5, 2001, at approximately 0848, the reactor was manually tripped due to excessive hydrogen leakage from the main generator. A small hydrogen leak was detected at approximately 0445 on January 4, 2001, and a small increase in the leak rate was noted that night. A significant change in leakage occurred at approximately 0830 on January 5, 2001, and a rapid plant shutdown in accordance with pre-planned contingency plans was initiated. During the power reduction operators near the generator reported that significant leakage and loss of hydrogen was occurring. The reactor was then manually tripped to allow a rapid depressurization of the generator via the vent pathway to the turbine building roof. All control rods inserted into the core well within the expected drop time. The post trip plant response was normal and the plant was placed in a stable hot shutdown condition. The cause of the leak was a failed pipe support in the main generator hydrogen cooling system that allowed excessive vibration and ultimate failure of a vent pipe. Following completion of corrective actions the reactor was restarted and tied to the grid at 1853 on January 7, 2001.
3132001002 | Arkansas 1 | 03/24/2001 | 05/08/2001 | ML01135019 | <strong>Reactor Coolant System Pressure Boundary Leakage Due To A Crack In A Control Rod Drive Mechanism Nozzle Reactor Vessel Head Penetration</strong><br /><i>Abstract:&nbsp;</i>Indication of boric acid crystals were noted in the area of one Control Rod Drive Mechanism nozzle on the Reactor Vessel (RV) head during routine visual inspection at the start of a scheduled refueling outage. The other nozzles did not exhibit indications of leakage. Non-destructive examinations confirmed that a crack in the nozzle had resulted in Reactor Coolant System (RCS) pressure boundary leakage. The cause of the crack was determined to have been Primary Water Stress Corrosion Cracking. The crack was repaired before the unit was returned to service. The RCS unidentified leak rate before the shutdown did not indicate any significant leakage. A safety assessment concluded that the crack did not pose any risk for catastrophic failure of the nozzle or boric acid damage to the RV head. Routine visual inspections were determined to be adequate to detect future similar cracks before any significant impact on safe operation can occur.
3132001003 | Arkansas 1, Arkansas 2 | 04/17/2001 | 06/14/2001 | ML01177024 | <strong>Control Room Emergency Ventilation System Radiation Monitors Were Inoperable Due to an Inadequate Procedure Change Caused by Training and System Knowledge Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2001, the Control Room Emergency Ventilation System (CREVS) dampers were closed for maintenance without either Emergency Ventilation Supply Fan in operation, as allowed by the system operating procedure. A subsequent engineering review determined that this configuration resulted in both channels of CREVS radiation monitors being inoperable. The condition resulted from a revision to the system operating procedure in 1996 that inappropriately changed wording to indicate that the configuration was acceptable. The root cause of the condition was deficient training that had been provided to Operations personnel on CREVS, particularly on the relationship between the inlet air monitors and airflow. The resulting knowledge deficiencies affected the procedure revision and allowed the situation to remain undetected for an extended period of time. The procedure was changed and Operations personnel were informed. Additional procedure enhancements and training for operations personnel from both units are planned.
3132001004 | Arkansas 1 | 07/24/2001 | 09/20/2001 | ML01264040 | <strong>Automatic Reactor Trip on High Reactor Coolant System Pressure Due to Failure of a Card in the Main Turbine Electro-Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>An automatic reactor trip occurred on high Reactor Coolant System pressure due to rapid closure of the Turbine Generator governor valves. All control rods fully inserted and no Engineered Safety Features actuations occurred. The root cause was determined to be failure of a chip in the reference up-down counter card in the Electro-Hydraulic Control (EHC) System. Another card in the EHC System was also found to have failed. A common failure mode could not be identified. The unit returned to power operation after the cards were replaced. An EHC reliability study is being conducted to determine the need for system upgrades and improved maintenance strategies. This event had minimal safety significance. There have been no previous similar events reported by Arkansas Nuclear One as Licensee Event Reports.
3152001001 | Cook 1 | 02/15/2001 | 04/06/2001 | ML01081023 | <strong>Reactor Trip Due to Loss of Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2001 at 1417 hours, while at approximately 100 percent power, a low vacuum trip on the Unit 1 east main feedwater pump turbine occurred. The operator manually tripped the reactor in accordance with plant procedures. The post trip investigation indicated that all safety related systems performed as designed. Prior to the event, the main feedpump water box differential pressure and backpressure was being monitored on an increased frequency due to a rising trend on both parameters. The previous shift had attempted to improve this condition by flushing the circulating water side of the main condenser waterboxes. A downpower had been previously scheduled to allow cleaning of the main feedwater condenser. However, the fouling occurred more rapidly than anticipated. In accordance with 10 CFR 50.72 (b)(3)(iv)(B)(1), a four-hour ENS notification was made to the NRC at 1545 hours on February 15, 2001, as an event or condition that resulted in an actuation of the reactor protection system when the reactor is critical. The cause of the feedwater pump trip was loss of condenser vacuum as the result of corrosion scales obstructing flow at the condenser's inlet-side tubesheet. This condition lead to an elevated condenser backpressure and a subsequent low vacuum trip of the east main feedwater pump. The feedwater pump turbines are non-safety related, non-safety interface, balance of plant equipment. The function of providing feedwater flow to support power operation is not a safety related or accident mitigating function. Therefore, with respect to the main feedwater system, this condition has no safety significance. Following the reactor trip, both the east and west main feed pump condensers were opened and cleaned. Between March 30 and April 1, 2001, Units 1 and 2 respectively were reduced to approximately 60 percent power to clean and inspect the feed pump condensers. No new scale formation was observed.
3152001002 | Cook 1, Cook 2 | 06/22/2001 | 08/17/2001 | ML01234011 | <strong>Power Range Nuclear Instrumentation Calibration Procedure Not in Conformance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2001, the power range nuclear instrumentation (PRNI) functional test for the Unit 1 quarterly calibration was not conducted in accordance with Technical Specification (TS) 3.3.1.1. This TS requires placing the inoperable PRNI channel in the tripped condition within one hour. To meet TSs, the PRNI channel is placed in trip before the detectors are disconnected. Contrary to TSs, the calibration procedure for the PRNI's returns the bistables to an un-tripped state while the detectors are still disconnected and after the channel has been inoperable for greater than one hour. The TS non-compliance was introduced into the procedure in 2000, when it was revised to allow testing of the remote alarms. Procedure reviews and test performances since the change had not detected the TS non-compliance. On June 26, 2001, a Condition Report (CR) was written which identified the potential TS non-compliance; however, the concern was evaluated as a procedural enhancement. The potential reportability of this event was not realized until July 9, 2001, when a procedure writer identified the CR while updating the PRNI test procedures. A second CR was written July 11, 2001, because the first CR did not recognize the significance of the condition. On July 11, 2001, this event was determined to be reportable in accordance with 10 CFR 50.73. The apparent cause of the event was an inadequate implementing procedure. The failure to recognize the significance of the event initially reported is being addressed through the Cook Nuclear Plant (CNP) corrective action program. This condition did not represent a significant degradation of plant safety, or prevent the fulfillment of safety-functions needed to shutdown the reactor, or mitigate the consequences of an accident. CNP received NRC approval of a license amendment to revise TS 3.3.1.1 to increase the amount of time allowed to place an inoperable power range neutron flux channel in the tripped condition from one hour to six hours. On August 9, 2001, the functional test and calibration procedures were revised to implement this TS change.
3152001003 | Cook 1 | 07/18/2001 | 09/14/2001 | ML01261008 | <strong>Emergency Diesel Generator Inoperable Due to Degraded Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2001, D.C. Cook personnel identified that the Unit 1 CD Emergency Diesel Generator (EDG) Ventilation System supply fan tempering damper was open about 30 percent instead of being fully closed as required. This condition was reevaluated on July 18, 2001, and determined to be an abnormal configuration. With this damper in the partially open position, the minimum room supply airflow requirements may not have been met on July 10, 2001, thus rendering the CD EDG inoperable to perform its intended safety function. This condition was considered to be a violation of Technical Specification (TS) TS 3.8.1.1, which requires that two independent diesel generators be operable in Modes 1, 2, 3 and 4. The TS also states that if one diesel generator becomes inoperable, the inoperable diesel generator must be restored to operable status within 72 hours. As such, this event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) for an operation or condition that was prohibited by the plant's TS since the condition existed for a period of time greater than 72 hours. The cause of the event was failure to recognize the operability condition of the tempering damper and take action within 72 hours as required by TS. Troubleshooting revealed that the EDG supply fan tempering damper drive linkage was out of adjustment. The safety significance of this event was considered to be low. With the EDG supply fan damper partially open, the airflow in the room may only be slightly below the minimum required. For the peak temperature recorded during this event, it was concluded that the EDG room temperature would increase a few degrees over the 130 degree F room design temperature. The short duration of this increase would not significantly affect the electrical components in the room. Corrective actions initiated include: issuance of an immediate lessons learned memorandum and providing specific training on the topic of ventilation operability issues. The tempering damper linkage was properly adjusted and the CD EDG was declared operable.
3152001004 | Cook 1 | 09/27/2001 | 11/21/2001 | ML02022018 | <strong>Unit 1 Entered Mode 3 With Remote Shutdown Panel Pressurizer Level Instrument Channel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2001, during Unit 1 startup activities, the unit was taken from Mode 4 to Mode 3 with the remote shutdown pressurizer level instrument inoperable. The inoperable instrument was identified in Mode 4, during performance of normal control room panel walkdowns. Despite this discovery, the unit was taken to Mode 3 in violation of Technical Specification (TS) 3.0.4. . During the extent of condition review for this event, it was identified that during Unit I startup activities on December 12, 2000, the required monthly channel check had not been performed for the pressurizer pressure instrumentation prior to transition to Mode 3. This condition was also determined to be a violation of TS 3.0.4. Both events were determined to be reportable per 10CFR50.73(a)(2)(i)(B) as conditions that are prohibited by TS. The cause of the September 2001 violation was human error. Corrective actions included counseling of the responsible personnel and distribution of lessons learned. The cause for the December 2000 event was incorrect procedure guidance. Corrective actions included the establishment of a Unit 1 Mode 3 constraint as a barrier to prevent additional violations while a change to the TS is processed that will permit the remote shutdown instrumentation (TS 3.3.5.5) to be excepted from TS 3.0.4. The significance of the TS violations is considered minimal since the probability of an event requiring the Remote Shutdown System is low, and because the equipment can generally be repaired during operation without significant risk of spurious trip.
3152001005 | Cook 1, Cook 2 | 11/19/2001 | 01/11/2002 | ML02016016 | <strong>RCCA Tool Over Spent Fuel Pool Racks Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2001, at approximately 1146 hours, Technical Specification (TS) 3.9.7 "Crane Travel-Spent Fuel Storage Pool Building" was violated when the Rod Control Cluster Assembly (RCCA) tool was mistakenly moved over the fuel racks in the spent fuel pool. The potential impact energy of the RCCA tool during this event was in excess of the 24,240 in-lbs. limit specified in TS 3.9.7. Surveillance Requirement (SR) 4.9.7.2, to determine potential impact energy less than or equal to 24, 240 in-lbs. prior to moving each load over racks containing fuel, was also not performed. Prior to each outage, Operations Refueling modifies the bottom of the shared portable RCCA tool to accommodate either 15 X 15 (Unit 1) or 17 X 17 (Unit 2) fuel assemblies. In order to remove the RCCA tool from the water, the RCCA tool must be raised above the hoist travel interlock in an area not over racks containing fuel. In this event, the interlock was engaged and the tool moved into the transfer area to change the RCCA bottom piece. The hoist height interlock was then disengaged to perform work on the RCCA tool. After completion of the tool modification but prior to reinstating the hoist height interlock, the Spent Fuel Crane Operator mistakenly moved the load over the spent fuel pool racks containing fuel. The operator had successfully performed this maneuver on several occasions, however he failed to reinstate the interlock prior to moving the crane. The Spent Fuel Pool Area Supervisor (SFPAS) immediately alerted the spent fuel crane operator to stop, and directed the load back into the weir gate area of the transfer canal. The load was lowered to below the hoist travel interlock and the interlock was reinstated. Movement of loads with impact energies in excess of TS 3.9.7 limits and the failure to perform surveillance testing (TS 4.9.7.2) prior to moving the load over fuel racks containing fuel are violations of Technical Specifications. This LER is being submitted in accordance with 10CFR50.73(a)(2)(i)(B), for a condition prohibited by TS.
3162001001 | Cook 2 | 01/23/2001 | 03/16/2001 | ML01081023 | <strong>Plant Shutdown Due to Control Rod Shutdown Bank Misalignment</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2001, while troubleshooting the rod control system for shutdown bank "C" for failing to move on demand during testing, shutdown bank "D" as inserted eight steps. During the subsequent withdrawal action, the demand counter moved out eight steps but the rod position indication did not show movement. Technical Specification (T.S.) 3.1.3.5, states that all shutdown rods shall be limited in physical insertion as specified in the Core Operating Limits Report (COLR). The action statement of this T.S. allows for a maximum of one shutdown rod inserted beyond the insertion limit specified in the COLR. The insertion limit specified in the COLR for shutdown bank "D" is the fully withdrawn position. When shutdown bank "D" is fully withdrawal attempt failed and with all four shutdown bank 'D' rods beyond the COLR insertion limit, T.S. 3.1.3.5 could not be met and T.S. 3.0.3 was entered. T.S. 3.0.3 requires that, within one hour, actions shall be initiated to place the unit in Hot Standby within the next 6 hours. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(A), for completion of a plant shutdown required by the Technical Specifications. The required unit shutdown was initiated on January 23, 2001 at 0619 hours and T.S. 3.0.3 was exited at 1102 hours when the unit entered mode 3. Troubleshooting activities revealed that a terminal connection in the shutdown "CD" power cabinet was loose. This connection is in the signal path that would have prevented the generation of a full current signal to the rod lift coil, thus preventing demanded rod motion. The apparent cause for this event was determined to be an inadequate cleaning and inspection program that failed to ensure proper tightening of terminal connections. It was concluded that while the loose connection prevented positioning of shutdown bank "D", this condition would not have prevented the rods from inserting into the core in the event of a reactor trip thus, the shutdown margin was not affected. As such, there was minimal safety significance as a result of this event. Immediate corrective actions were implemented to inspect terminal board connections in all rod control cabinets in Unit 2. In addition, actions are being formulated to address the problems associated with loose electrical connections in the rod control system.
3162001002 | Cook 2 | 01/23/2001 | 10/26/2001 | ML02024031 | <strong>Failure of Lower Containment Airlock Door Interlock Results in Inadvertent Opening of Both Doors</strong><br /><i>Abstract:&nbsp;</i>This LER supplement is being submitted to include revised information related to the completed root cause evaluation. This LER revision replaces the previous LER in its entirety. On January 23, 2001, during the removal of plant equipment from the Unit 2 lower containment personnel airlock, the airlock doors' interlock failed. This allowed the inadvertent opening of both the inner and outer lower containment airlock doors at the same time for approximately 5 seconds. Technical Specification 3.6.1.3 requires both containment airlock doors to be closed; except during normal transit entry and exit through containment, then at least one airlock door shall be closed. Because both lower containment airlock doors were open at the same time, an 8-hour ENS notification was made to the NRC in accordance with 10 CFR 50.72 (b)(3)(v)(C), for a condition or event that could have prevented the fulfillment of the safety function of a system needed to control the release of radioactive material. The root cause for the containment airlock door interlock failure was the interlock mechanism slipping out of adjustment. The specific failure involved a gradual loosening of the setscrews that hold the interlock gears in place. Both the inner and outer lower containment airlock doors were immediately closed to restore containment integrity. The airlock door interlock was repaired and satisfactorily tested. Preventive maintenance (PM) activities for the airlock doors were evaluated and the root cause recommendations and vendor recommendations have been incorporated into the appropriate procedures. A detailed design analysis is presently being performed and is being tracked in accordance with the site Corrective Action Program. The appropriate procedure has been revised to include directions on the operation of the containment airlock doors and the consequences of improper airlock door configuration, including radiological and industrial safety concerns. This condition is not considered to be safety significant due to the extremely low probability of a Loss of Coolant Accident or Main Steam Line Break occurring during the 5-second time interval in which both airlock doors were open. A review of plant events during the past three years did not identify any conditions in which the containment doors were opened simultaneously. Therefore, this is considered an isolated event.
3162001003 | Cook 2, Cook 1 | 08/29/2001 | 03/12/2002 | ML02073008 | <strong>Degraded ESW Flow Renders Both Unit 2 Emergency Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>This supplemental LER was issued to identify the correct the reporting requirement for submittal of the LER. No other changes were made. On August 29, 2001, Donald C. Cook Nuclear Plant (CNP) Unit 1 was in MODE 5 for a planned maintenance outage and Unit 2 was in MODE 1. Unit 2 Operations personnel were performing a routine surveillance test of the Essential Service Water (ESW) system in accordance with approved plant procedures. At approximately 2255 hours, Unit 2 Operations personnel noted low ESW flow to both of the Unit 2 Emergency Diesel Generator (EDG) heat exchangers. The Unit 1 ESW flows were also checked and it was determined that ESW flow to both Unit 1 EDG heat exchangers was low. All four EDGs were declared inoperable. Unit 2 entered Technical Specification (TS) 3.0.3, and Unit 1 entered TS 3.8.1.2. After flushing the ESW side of the associated heat exchangers both Unit 2 EDGs were declared OPERABLE at 2350 hours. Based on conservative decision making, Unit 2 was shut down on August 30, 2001, to facilitate the identification and correction of the causes for the low ESW flow conditions. The U.S. Nuclear Regulatory Commission was notified of the decision to commence a Unit 2 shutdown. A common mode failure of the EDGs was reported in accordance with 10 CFR 50.72(b)(3)(v), "Non-Emergency Events - 8-Hour Reports." The cause of the low flow conditions was pre-existing material failure of the Unit 1 East ESW strainer basket, which created a bypass flow path around the strainer. The bypass flow path allowed large debris to enter the ESW system. The cause of the EDG common mode failure was the station design and operational practices that allowed aligning the ESW supplies to each EDG from both ESW headers on the associated unit. Corrective actions included inspection and replacement of all baskets, revision of the applicable maintenance procedures which detail installation requirements, and modification to the design and operating procedures to maintain the alternate ESW valves to the EDGs normally shut during normal and accident conditions.
3162001004 | Cook 2 | 10/07/2001 | 12/05/2001 | ML02018024 | <strong>Reactor Protection System Actuation Initiated by Power Range, Neutron Flux, High Negative Rate</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2001, a reactor trip occurred at 8 percent reactor power. The trip was the result of a loss of rod control system voltage. The cause of the loss of rod control system voltage was an open resistor at the input to the north control rod drive motor generator (CRD-MG) voltage regulator. The open resistor caused a low voltage transient when the north CRD-MG field collapsed. A protective auxiliary relay removed power from the south CRD-MG voltage regulator resulting in a loss of rod control system voltage. The loss of voltage caused all control rods to rapidly insert, thereby, initiating a Power Range, Neutron Flux, High Negative Rate trip from the reactor protection system (RPS). The RPS actuation was initiated by actual plant conditions that satisfied the requirements for the initiation of the trip, and was, therefore, a valid RPS actuation. The failed resistor was determined to be the result of a random component failure. The resistor was original equipment and inspection revealed no evidence of overheating or manufacturing defect. The defective resistor was replaced and, as a precaution, the remaining series resistor in the north CRD-MG along with the identical resistors in the south CRD-MG were replaced. This event was reported in accordance with 10 CFR 50.72(b)(1)(iv)(B).
3172001001 | Calvert Cliffs 1 | 05/16/2001 | 07/13/2001 | ML01198010 | <strong>Auxiliary Feedwater Pump Turbine Bearing Failure Caused by Sealant Intrusion</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2001, at 1338 hours, Calvert Cliffs Unit 1 experienced a failure of an auxiliary feedwater pump turbine bearing during a surveillance test. At the time of the failure, the plant was in Mode 1 with power at 100 percent rated thermal power. The cause of the bearing failure was the introduction of Permatex 2 sealant into the bearing. The vendor technical manual specified the use of too much sealant on the bearing housing sealing surfaces. This caused some sealant to extrude inside the housing at the sealing surface edges and eventually into the lubricating oil that supplies the babbited bearing. The sealant was then able to migrate into the bearing and cause its failure. The vendor technical manual will be revised and applicable maintenance procedures are being updated to ensure less sealant is used in the future. Training on this issue will be conducted with appropriate maintenance personnel.
3172001002 | Calvert Cliffs 1 | 09/05/2001 | 10/31/2001 | ML01319024 | <strong>Appendix R Steam Generator Dry-Out Calculation Omited Blowdown Flow</strong><br /><i>Abstract:&nbsp;</i>On September 5, 2001 it was determined that steam generator blowdown (SGBD) flow was not credited in the calculation developed to determine the time to steam generator dry-out during an Appendix R event. The calculation provides the basis for the required completion time of critical steps in the Abnormal Operating Procedures (AOPs) used to achieve and maintain decay heat removal (i.e., restore auxiliary feedwater) during an Appendix R event. This calculation determined dry-out would occur in approximately 47 minutes. However, a preliminary analysis indicates that dry-out could occur in 26 minutes if maximum allowed SGBD flow (180 gpm) is assumed and in approximately 31 minutes if SGBD flow is limited to 100 gpm. During a recent timed walkthrough of AOP-9B-1 "Safe Shutdown Due To A Severe Cable Spreading Room Fire, Unit 1," auxiliary feedwater restoration exceeded 26 minutes. As a result, compensatory actions were established to limit maximum blowdown flow to 100 gpm and the significant deficiencies were immediately removed from AOP-9B-1.
3182001001 | Calvert Cliffs 2 | 05/16/2001 | 07/12/2001 | ML01198011 | <strong>22 Saltwater Air Compressor Appendix R Handswitch Fuses Shunted</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2001 during performance of a causal analysis, a condition was discovered at Calvert Cliffs that could have prevented the Instrument Air System from fulfilling its Appendix R safety function. Specifically, the analysis identified that the effects of an extra wire in the Instrument Air System's 22 Saltwater Air Compressor's (SWAC's) control circuit could, in the event of a fire, shunt out the protective fuses. This could result in loss of local operation of the 22 SWAC as required in the event of an Appendix R (Control Room) fire. The 22 SWAC could have been incapable of performing its Appendix R function from the time when a plant modification was completed (February 25, 1999) until the additional wire was ultimately removed (February 14, 2001), a period of about two years. The additional wire was removed and 22 SWAC was tested with satisfactory results on February 14, 2001. An inspection was performed for the other SWACs (11, 12, and 21) and the additional wire had been removed as required at the time of the modification.
3182001002 | Calvert Cliffs 2 | 04/04/2001 | 08/30/2001 | ML01249041 | <strong>Misunderstood Technical Specifications Causes Containment Closure Deviation</strong><br /><i>Abstract:&nbsp;</i>On July 2, 2001, it was discovered that the shutdown cooling pumps were removed from operation for local leak rate testing of containment penetration 41 with the normal containment sump valves open during the 2001 Calvert Cliffs Unit 2 refueling outage. This condition is not allowed by Technical Specification (TS) 3.9.4. The plant was in Mode 6 with the Reactor Coolant System (RCS) at 105 degrees Fahrenheit and atmospheric pressure, refueling pool water level was greater than 23 feet above the fuel in the reactor vessel, core alterations had been suspended, no operations were permitted that would cause a reduction to RCS boron concentration, and a spent fuel pool cooling loop was providing RCS decay heat removal. The root cause of this event was that TS containment penetration closure requirements were not accurately understood and implemented. These requirements have now been properly implemented in procedures. The inaccurate TS implementation was limited to the normal containment sump valves. A review of all deleted TS interpretations is underway to ensure that TS requirements are being accurately implemented. The safety significance of this event is very low.
3212001001 | Hatch 1 | 03/09/2001 | 05/03/2001 | ML01129001 | <strong>Component Failure in Station Service Battery Charger Leads to Inoperability of HPCI System</strong><br /><i>Abstract:&nbsp;</i>On 03/09/2001 at 0645 EST, Unit 1 was in the Run mode at a power level of approximately 2763 CMWT (100 percent rated thermal power). At that time, the High Pressure Coolant Injection (HPCI) system was rendered inoperable when the DC-to-AC inverter powering the system flow controller began to trip randomly, resetting automatically within a few seconds of tripping. The cycle of random tripping followed within seconds by an automatic reset of the inverter made the controller unreliable and personnel therefore concluded that the HPCI system was inoperable. This cycle continued until 0713 EST when personnel removed 125/250 volt station service battery charger 1R42-5031 from service after having observed fluctuations in charger voltage and current output readings and two alarms on the charger control panel. Removing the battery charger from service restored the HPCI system to an operable status by eliminating the bus voltage fluctuations that had caused the HPCI system inverter to trip. This event was the result of component failure. A fuse internal to the charger developed an intermittent connection that caused the charger to cycle rapidly off and on. These rapid off-on cycles caused charger output voltage at times to exceed momentarily the HPCI system inverter input voltage trip setpoint. Per its design, the inverter automatically reset when its input voltage, that is, charger output voltage, dropped below the inverter trip setpoint. Corrective actions included removing charger 1R42-5031 from service and replacing the bad fuse. As a precaution, the fuses in the battery chargers will be replaced and a repetitive task to replace the fuses periodically will be established.
3212001002 | Hatch 1 | 03/28/2001 | 05/21/2001 | ML01149022 | <strong>Component Failure Causes Turbine Trip and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 03/28/2001 at 1853 EST, Unit 1 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, the reactor scrammed on turbine control valve fast closure caused by a turbine trip. The turbine tripped when actuation of phase 2 and 3 differential relays for unit auxiliary transformer lB resulted in actuation of a lockout relay, generating a direct turbine trip signal. Following the scram, water level decreased due to void collapse from the rapid reduction in power resulting in closure of Group 2 and the outboard Group 5 primary containment isolation valves and automatic initiation of the Reactor Core Isolation Cooling and High Pressure Coolant Injection systems. The low level initiation signal cleared before either system could inject water to the vessel. The outboard secondary containment dampers automatically isolated, and all trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low water level. Level reached a minimum of 37 inches below instrument zero. The Reactor Feedwater Pumps restored level to its pre-event value of approximately 35 inches above instrument zero within 30 seconds of the scram. Pressure reached a maximum value of 1127 psig; five of eleven safety/relief valves lifted to reduce pressure. Pressure did not reach the nominal actuation setpoints for the remaining safety/relief valves. This event was caused by an internal fault in unit auxiliary transformer 113. The fault occurred on the high side winding of transformer phase 3. The transformer was removed from service; its loads will continue to be supplied from their alternate supply until a new transformer can be procured and installed.
3212001003 | Hatch 1, Hatch 2 | 06/25/2001 | 08/23/2001 | ML01240031 | <strong>Error in Generic Analysis Results in Potentially Nonconservative Oscillating Power Range Monitor Setpoint</strong><br /><i>Abstract:&nbsp;</i>On 6/25/01 at 1935 EDT, Unit I and Unit 2 were operating in the Run Mode at 100% of rated thermal power (2763 CMWt). At that time, the Oscillating Power Range Monitors (OPRMs) for both units were declared inoperable when it was determined that the Hatch reload licensing analysis provided by General Electric (GE) potentially failed to protect against violation of the Safety Limit Minimum Critical Power Ratio during thermal-hydraulic instabilities. An alternate method of detecting and suppressing thermal-hydraulic instabilities was then initiated, as required by the Technical Specifications. The cause of the event was the failure of the generic industry analysis to account for certain operating conditions. Among the corrective actions are the following: 1) The alternate method of manually detecting and suppressing core oscillations was implemented upon declaring the OPRMs inoperable. 2) On 7/12/01, new OPRM setpoints were provided by GE and input into the hardware. As a result, the OPRMs were declared operable. 3) GE is working with the Boiling Water Reactor Owners' Group to determine new data that will be bounding for all future operating conditions.
3232001001 | Diablo Canyon 2, Diablo Canyon 1 | 03/22/2001 | 11/16/2001 | ML01324026 | <strong>Degraded Wires in 4.16-kV Vital Buses Due to Bending at Cubicle Door Hinges</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2001, a broken wire was identified in a trip circuit for the Containment Spray Pump (CSP) 2-2 Breaker. As part of continued inspections, additional degraded wires were found on March 22, 2001, in the CSP 1-1 Breaker. While Units 1 and 2 were in Mode 1 (Power Operation) at 100 percent power, PG&E determined the cause of degraded wires could have prevented the fulfillment of a safety function of two or more trains or channels in different systems. The condition is reportable per 10 CFR 50.73(a)(2)(ix)(A). On March 25, 2001, during wire repairs on Unit 2 Bus H, with Unit 2 in Mode 1 at 100 percent power, Technical Specification (TS) 3.8.1, "AC Sources - Operating," was violated when all three power sources to Vital Bus H were inoperable for greater than 1 hour, and operators did not enter TS 3.0.3 as required by condition J of TS 3.8.1. This condition is reportable per 10 CFR 50. 73(a)(2)(i)(B). The wires degraded due to age embrittled insulation and as a result of short radius bending when the cubicle doors are closed. Corrective actions include replacing all existing wiring on 4.16-kV cubicle doors and supporting this new wiring in a way that prevents short radius bending. Operators did not enter TS 3.0.3 due to incomplete and inconsistent procedural guidance. Applicable procedures will be revised and operators will be trained on the condition that made the power system inoperable.
3232001002 | Diablo Canyon 2 | 05/20/2001 | 07/13/2001 | ML01205026 | <strong>System Actuation - Unplanned Diesel Start During Testing Due to Inadequate Equipment Status Control</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2001, at 0056 PDT, with Unit 2 in Mode 5 (Cold Shutdown), Vital Bus H unexpectedly lost power during surveillance testing. At 0100 PDT, plant operators placed emergency diesel generator (EDG) 2-2 in auto to allow the EDG to auto start to restore power to the bus. EDG 2-2 automatically started on a valid undervoltage signal, and the loads were automatically sequenced onto the bus. At 0331 PDT, PG&E made an 8-hour nonemergency report to the NRC in accordance with 10CFR50.72(b)(3)(iv)(A). The cause of the unplanned loss of power to Bus H was inadequate equipment status control. During performance of an earlier section of the surveillance test, the startup feeder breaker was placed in TEST, which prevented it from powering the bus. However, the breaker was not removed from the TEST position, nor its condition communicated to subsequent crews who performed subsequent sections of the test that required the breaker to be out of the TEST position. When the breaker failed to power the bus during the subsequent testing, operators were required to take the contingency action of starting the associated EDG. Corrective actions include: • Revising the surveillance test procedures to add steps to remove the startup feeder breakers from the TEST position in part one of the STP, and • Verifying information tags are hung on breakers in TEST.
3232001003 | Diablo Canyon 2 | 05/30/2001 | 07/27/2001 | ML01219019 | <strong>Technical Specification 3.3.3 Not Met Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2001, at 15:23 PDT, Unit 2 transitioned from Mode 4 (Hot Shutdown) to Mode 3 (Hot Standby) and Technical Specification 3.3.3, "Post Accident Monitoring (PAM) Instrumentation," became applicable. On May 26, 2001, the intent of TS 3.3.3 was not met when both containment hydrogen monitors (CELs 82 and 83) were improperly aligned for more than 72 hours. PG&E discovered this event on May 30, 2001, while performing surveillance test procedure I-46A, "Containment Hydrogen Monitor Ch 82(83) Channel Calibration," on Unit 2 CEL 82. VAC-2-672, which isolates reagent gas from CELs 82 and 83, was identified in the closed position. The reagent gas is required for the CELs to work as designed. In an event requiring use of CELs 82 and 83 with the reagent gas isolated at VAC-2-672, the channels may not have been available in 30 minutes as discussed in DCPP's Final Safety Analysis Report Update. Therefore, PG&E believes CELs 82 and 83 were inoperable since entry into Mode 3 on May 23, 2001. This condition was caused by an inadequate procedure. As immediate corrective action, VAC-2-672 was opened and the operability of CELs 82 and 83 restored on May 30, 2001. As corrective action to prevent recurrence, Chemistry Analysis Procedure P-16, "Sampling of Containment Atmosphere Hydrogen on a Safety Injection," was revised to add a step to verify the correct alignment of VAC-2-672.
3232001004 | Diablo Canyon 2 | 06/26/2001 | 08/27/2001 | ML01248011 | <strong>Technical Specification 3.4.10 Not Met During Pressurizer Safety Valve Surveillance Testing Due to Random Lift Setting Spread</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2001, during a routine scheduled performance of Surveillance Test Procedure M-77, "Safety and Relief Valve Testing," PG&E identified the second of three pressurizer safety valves (PSVs) outside the Technical Specification (TS) 3.4.10, "Pressurizer Safety Valves," tolerance lift setting of greater than 2460 psig and less than 2510 psig. The PSVs were disassembled, inspected, and reset within TS lift setting at the offsite test facility. PG&E believes the cause of the PSV lift setting being outside the TS allowance is random lift setting spread. PSV lift setting repeatability has been recognized as an industry-wide problem. PG&E has participated in extensive investigative test programs, both jointly with the Nuclear Steam Supply System, Westinghouse Owners Group, and independently. The results of the industry investigations are documented in WCAP-1 2910, "Pressurizer Safety Valve Set Pressure." PG&E has enhanced the PSV maintenance activities and testing procedures resulting in improved performance. No further corrective actions are required.
3242001001 | Brunswick 2 | 02/23/2001 | 04/18/2001 | ML01114021 | <strong>EHC System Malfunction Results in Specified System Actuations</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2001, at 2220 hours, with a shutdown of Unit 2 for a refueling outage in progress, a false high turbine speed signal in the Electro-Hydraulic Control (EHC) system resulted in turbine control valves/combined intermediate valves closing and bypass valves opening followed by a generator/turbine trip from approximately 37 percent of rated thermal power. The four emergency diesel generators automatically started as designed when the generator tripped. Operators inserted a manual trip of the reactor protection system (RPS) to shut down the reactor, and the associated reactor vessel coolant low level transient resulted in the actuation of an automatic RPS signal as well as closure of containment isolation valves in groups 2 and 6. The plant responded as designed to the event. The cause of the event is attributed to an intermittent electrical connection that resulted in a false high turbine speed signal being detected by the frequency-to-voltage converter card in the EHC system. Maintenance personnel identified a wire termination with a loose crimped ring lug in a junction box located on the front standard of the turbine. Evaluation of the lug/wire termination determined that the wire had not been fully inserted into the barrel of the lug at the time the termination was crimped. The termination appeared to be from original construction of the plant. The lug was replaced and terminated in accordance with plant procedures. The other electrical terminations in the junction boxes on the turbine were checked for loose terminations and none were identified. The safety significance of this event is considered to be minimal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3312001003 | Duane Arnold | 08/12/2001 | 10/11/2001 | ML01289041 | <strong>Manual Reactor Scram Inserted Due to Failed Open Feed Pump Minimum Flow Valve</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2001, while operating at 100% power, operators inserted a manual reactor scram due to decreasing reactor water level. The low level was caused by a reactor feedwater pump minimum flow bypass valve failing open. The "B" (affected) feed pump tripped on low suction pressure as operators attempted to restore level. All control rods fully inserted upon receipt of the manual scram signal. Primary containment isolations initially occurred as expected. A Group 1 isolation also occurred, after which all main steam isolation valves closed. This isolation was due to the decreasing reactor pressure with the mode switch in RUN and occurred quicker than expected. The root cause of the event was a failed resistor in the flow indicating controller that operates the minimum flow valve. Corrective actions include repair of the failed controller, preventive maintenance to the controller for the "A" feed pump, replacements of similar installed controllers, engineering analysis of the receipt of the Group 1 isolation, and a revision to the procedure for immediate actions in response to a reactor scram. There were no actual safety consequences or impact on public health and safety as a result of this event. The plant was re-started and returned to power operation on August 15, 2001.
3312001004 | Duane Arnold | 09/02/2001 | 11/01/2001 | ML02031045 | <strong>Unplanned High Pressure Coolant Injection Inoperability Due to Steam Leak in Drain Trap</strong><br /><i>Abstract:&nbsp;</i>On September 2, 2001, while operating at 100% power, the High Pressure Coolant Injection (HPCI) steam supply line drain trap developed a steam leak that required the drain trap to be manually isolated. The steam leak was due to the outlet plug failing on the drain trap. After the trap was isolated, the HPCI steam supply drain pot high level alarm was received and the HPCI system was declared inoperable. The cause of the plug failure was the eroded state of the plug and plug threads due to flow accelerated corrosion (FAC). The FAC resulted from steam leaking by the valve seat. The root cause is ineffective preventive maintenance (PM). A contributor is less-than-adequate past corrective action. Corrective actions will include repair/replacement of the drain trap and evaluation of the rebuild frequency. There were no actual safety consequences associated with this event. There was no impact on public health and safety. There were no systems, structures, or components that were inoperable at the start of the event that contributed to the event. This event is reportable under 50.73(a)(2)(v)(D).
3312001005 | Duane Arnold | 10/03/2001 | 11/30/2001 | ML02009044 | <strong>Licensed Power Level Exceeded Due to Use of Non-conservative Constant in Heat Balance</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2001, with the plant at 100 percent (%) power, plant personnel discovered that the input constant for the moisture carryover fraction used in the process computer for heat balance calculation was non-conservative. The constant used was 0.1 %, whereas, a report from the fuel vendor states that the value is close to zero. In addition, based on recent plant Sodium-24 test data, the value is less than 0.007%. This error caused the reactor power calculation to be 1.3 megawatts thermal (MWth) lower than actual. The reactor power was administratively reduced by 2 MWth to ensure the licensed maximum power level was not exceeded. The heat balance calculation software has been subsequently revised to use a more accurate value for the moisture carryover fraction. As a long-term corrective action, a comprehensive review of the reactor heat balance calculation in the process computer will be performed. Although the error resulted in a non-conservative reactor power calculation, the event was not significant due to its small magnitude (less than 0.1% of rated thermal power). In addition, per the fuel vendor report, use of the carryover fraction of 0.1 %, while non-conservative, does not represent a safety issue. The event did not have an adverse consequence to the public health and safety.
3312001006 | Duane Arnold | 10/17/2001 | 12/12/2001 | ML02036040 | <strong>Manual Reactor Scram Due to Loss of Instrument AC</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2001, while operating at 100%power, operators inserted a manual reactor scram due to decreasing reactor water level. The low level was caused by a sequence of events initiated by a loss of Division 1 Instrument AC bus 1Y11 due to a failure of inverter 1D15 coincident with the alternate power supply, regulating transformer 1Y1A, being out of service for preplanned maintenance. The loss of 1Y11 caused a plant transient that required the operating crew to insert a manual scram in anticipation of reaching an automatic scram setpoint on low Reactor Pressure Vessel (RPV) level. All control rods fully inserted upon initiation of the manual scram. Reactor level dropped low enough (+119.5") to initiate High Pressure Coolant Injection (HPCI), Reactor Core Isolation Cooling (RCIC), Low Pressure Coolant Injection-Loss of Offsite Power (LPCI-LOOP) select, and Reactor Water Cleanup (RWCU) outboard isolation. Reactor level was recovered using RCIC and "B" Reactor Feed Pump (RFP). HPCI was out of service for preplanned maintenance. "B"RFP and RCIC received trips when reactor level reached the high level trip setpoint (211"). RCIC was restarted for level control and a second manual scram was inserted in anticipation of a low level automatic scram. The "B" RFP was restarted for level control and was used to restore level. At 195"RCIC was secured, and at 211" the "B"RFP tripped for the second time. Three circuit boards in the inverter were determined to be the likely cause of the failure and were replaced. The three original boards were removed and sent to the vendor for failure analysis. No problems were detected. There were no actual safety consequences associated with this event. There was no impact on public health and safety.
3312001007 | Duane Arnold | 10/30/2001 | 12/21/2001 | ML02031037 | <strong>Unplanned High Pressure Coolant Injection System Inoperability Due to an Oil Leak Caused by a Missing Front Ferrule in a Compression Fitting</strong><br /><i>Abstract:&nbsp;</i>At 1820 hours on October 30, 2001, with the plant operating at 100% power, the High Pressure Coolant Injection (HPCI) system was declared inoperable due to an oil leak. The leak was discovered during a walkdown by the system engineer. The leak was located on a compression fitting in the oil supply line to the HPCI turbine overspeed trip device. The amount of leakage (estimated at 90 drops per minute) was smaller than the oil system's makeup capacity, but the proximity of the leak to nearby high temperature steam piping resulted in the unplanned inoperable condition. The cause of the oil leak was a missing front ferrule in the compression fitting. The root causes were improper initial installation of the fitting and poor workmanship during re-assembly of the oil line during the last refuel outage (May, 2001). Contributing Factors include needed improvement in vendor work control and oversight, and inadequate detail in the turbine overhaul procedure. The leak was repaired and HPCI was returned to an operable status at 0306 hours on October 31, 2001. There were no actual safety consequences nor was there any impact on public health and safety as a result of this event.
3332001001 | FitzPatrick | 02/21/2001 | 04/20/2001 | ML01115004 | <strong>Conflicting Design Requirements for Reactor Building Equipment Hatchway Configuration Resulted in the Plant Being in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2001, with the reactor at approximately 100 percent power, it was discovered that conflicting design analyses existed for the configuration of an equipment hatchway, located in the Reactor Building Secondary Containment, at the 326 foot elevation. Specifically, the hatchway is credited as being open for the high energy line break (HELB) analysis, which models a flow path to upper elevations in the event of a break, and establishes Environmental Qualification (EQ) profiles for surrounding equipment. The Fire Protection Program (10CFR 50 Appendix R) analysis assumes that a cover is installed on the hatchway. The as-found configuration identified the hatchway cover to be installed. With this flow path closed, the existing temperature and pressure EQ profile models indicate that the EQ limits for 600 volt emergency switchgear 71LI5 and 71L16, located on the 300 foot elevation, could have been exceeded in the event of a HELB. The most probable cause for the conflicting design analyses was inadequate work practices. Corrective actions include the removal of the hatchway cover, completing an evaluation to resolve the conflicting design analyses, and performing a review of the plant modification package which originally installed the hatchway cover to assure that no other missed program or analyses considerations exist.
3332001002 | FitzPatrick | 02/26/2001 | 04/27/2001 | ML01122008 | <strong>Failure to Satisfy Techincal Specifications Requirements Due to Inoperable Support Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2001, with the reactor mode switch in the RUN position, the plant operating at approximately 100 percent rated power, and with the flow unit D of the Power Range Monitoring System in an inoperable condition, it was identified that the appropriate Technical Specifications (T.S.) Actions for the inoperable flow unit had not been entered. Specifically, it was not recognized that the inoperability of the flow unit made the associated Average Power Range Monitor (APRM) Flow Referenced Neutron Flux High Scram Trip Function vulnerable to single failure, and thus necessitated declaring its associated required APRM Flow Referenced Neutron Flux High Scram Trip Function inoperable and entering the appropriate T.S. Action Statement. The causal factor leading to this event was inadequate training/qualification content. Immediate corrective actions include communicating the details of this event to the Senior Reactor Operators and reviewing current equipment Limiting Conditions for Operation (LCOs) for potential similar conditions.
3332001003 | FitzPatrick | 03/01/2001 | 04/26/2001 | ML01121004 | <strong>Failure to Satisfy Technical Specifications Table 4.2-8, Primary Containment Hydrogen/Oxygen Concentration Analyzer Calibration Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 01, 2001, during a review of instrument calibration requirements for the primary containment system's Containment Atmosphere Dilution (CAD) System, it was identified that Technical Specifications (T.S.) surveillance requirements were not being met. Specifically, the test scope and acceptance criteria contained in the procedure used to perform T.S. required once per three months calibration of the Primary Containment Hydrogen/Oxygen Monitoring System did not include the entire instrument channel or calibration of the full instrument range as defined in the T.S. At the time of the discovery, the reactor mode switch was in the RUN position and the plant was operating at 100 percent power. The cause for this omission of the calibration requirements was inadequate procedure development. Corrective actions include revising the calibration procedure, retesting of the equipment in accordance with T.S. requirements, and conducting a root cause evaluation. The safety significance of this event was minimal. The completion of calibration of both channels of the Containment H2/02 Monitoring System to the revised test methods and parameters on March 09, 2001 demonstrated assurance that the equipment was capable of performing its intended safety function.
3332001004 | FitzPatrick | 03/20/2001 | 05/18/2001 | ML01144039 | <strong>Failure to Meet Auxiliary Electrical Systems Technical Specifications Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2001 at 0400 hours, Low Pressure Coolant Injection (LPCI) Motor Operated Valve (MOV) Independent Power Supply Inverter 71 INV-3B was removed from service for scheduled maintenance. Subsequently, at 1100 hours the same day, one of two Emergency Diesel Generator (EDG) subsystems was removed from service for scheduled inspection and surveillance testing. On March 20, 2001 at 1430 hours, it was determined that the plant configuration of having both 71 INV-3B and the EDG subsystem inoperable did not meet the design basis Loss-of-Coolant Accident (LOCA) analysis assumptions. Reactor operators entered Technical Specifications (T.S.) Section 3.0.E LCO Action Statement requiring the plant to be in Cold Shutdown within 24 hours. On March 21, 2001 at 0054 hours, the 24 hour LCO was exited following the return to service of 71INV-3B. At the time, the reactor mode switch was in the RUN position with the plant operating at approximately 100 percent power. The cause for the event was inadequate guidance within the T.S. and T.S. Bases. Corrective actions include the issuance of a T.S. Interpretation and implementation of Improved Technical Specifications.
3332001005 | FitzPatrick | 06/19/2001 | 08/17/2001 | ML01236004 | <strong>Safety Relief Valve Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Review of the as-found setpoints for 11 Safety Relief Valve (SRV) [SB] pilot assemblies, removed during Cycle 14, determined that 2 SRVs were outside the allowable as-found tolerance of 1145 psig +/-3 percent required by Technical Specification (TS) requirement 4.6.E. TS 3.6.E requires a minimum of 9 SRVs to be operable; therefore the requirements of TS 3.6.E were satisfied. Additional requirements pertaining to the Anticipated Transient Without Scram (ATWS) High Pressure actuation setpoint (TS Table 3.2-7, Note 3) were not satisfied, however. This report documents this Technical Specification non-compliance. The effect of 2 SRVs being out of tolerance during Cycle 14 is also analyzed in this report. The results of this analysis shows that Reactor Pressure Vessel (RPV) overpressure protection and nuclear plant safety were not adversely affected. The cause of the out of tolerance SRV setpoints was determined to be corrosion bonding between the SRV pilot disc and seat, a recognized industry generic problem. Modifications consistent with BWR Owner's Group SRV Committee corrective action recommendations were installed during Refueling Outage (RO) 14. These modifications provide pressure switch SRV actuation as a second means of SRV actuation that is not susceptible to pilot disc-seat bonding.
3342001001 | Beaver Valley 1 | 06/22/2001 | 08/13/2001 | ML01233026 | <strong>Manual Reactor Trip Due to Loss of Station Instrument Air</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2001, at approximately 0924, Beaver Valley Power Station Unit No. 1 received an alarm for Station Instrument Air Receiver Tank Discharge Pressure Low. Operators entered the Abnormal Operating Procedure and initiated action for Loss of Station Instrument Air. At 0930, the degrading instrument air pressure caused an air-operated isolation valve in the cooling water flow path to two Reactor Coolant Pumps (RCPs) to close, eliminating component cooling water flow to these RCPs. At 0931, the reactor was manually tripped due to the loss of cooling to two RCPs and the potential loss of cooling water to the third RCP. All RCPs were then secured and natural circulation was established in the Primary System. All control rods fully inserted into the reactor core and all required safety systems operated as designed. Emergency Operating Procedures for Reactor Trip were performed and the plant was stabilized in Mode 3. The initiation of a manual reactor trip is reportable pursuant to 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73 (a)(2)(iv)(A). The root cause of the rapid Instrument Air System depressurization was mechanical aging/cyclic fatigue of the spring in a blowdown valve associated with the air dryer for the Instrument Air System. This failure caused the output from the operating air compressor to be vented off rather than entering the Instrument Air System Receiver Tank, resulting in an Instrument Air System breach. The safety significance for this event was small.
3342001002 | Beaver Valley 1 | 10/06/2001 | 11/29/2001 | ML02016022 | <strong>Manual Reactor Trip During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2001, Beaver Valley Power Station Unit No. 1 testing personnel and the Control Room operators were performing a Control Rod Drop Testing surveillance in preparation for reactor startup following Unit 1's fourteenth refueling outage. The plant was in a sub-critical condition in Mode 3 with Shutdown Bank B control rods withdrawn. At 1959 hours, the Control Room operators observed indications of two dropped control rods (via rod position indication reading zero steps and rod bottom lights on), and entered Unit 1 Abnormal Operating Procedure (AOP) 1.1.8 for Rod Inoperability. The Reactor Operator opened the reactor trip breakers in accordance with the AOP and the Reactivity Management Plan. Emergency Operating Procedure E-0 for Reactor Trip was performed and the plant remained in Mode 3. The manual initiation of a reactor trip via the Reactor Protection System by the BVPS Unit 1 control room operator on October 6, 2001, was a valid manual reactor trip signal and was not part of a pre-planned sequence during testing or reactor operation. Therefore this event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). It was subsequently discovered that the two dropped control rod indications were caused by the testing personnel repositioning knife switches to place the rod drop computer in service. There were no dropped control rods. This action by the testing personnel and resulting expected indications were not communicated to the Control Room operators prior to their occurrence. The opening of the reactor trip breakers was caused by a lack of good communication practices and a lack of procedure adherence by an inexperienced test engineer. This engineer failed to read a step in the test procedure which required the engineer to inform the Reactor Operator that the control room would be losing indication on control rod Shutdown Bank B. The safety significance of the manual reactor trip on October 6, 2001 was small.
3342001003 | Beaver Valley 1 | 11/06/2001 | 12/21/2001 | ML02018026 | <strong>Automatic Reactor Trip Due to Low Steam Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>At 1416 hours on November 6, 2001, Beaver Valley Power Station Unit No. 1 reactor automatically tripped from 100% power due to low-low level in the C Steam Generator. The Feedwater Level Control Valve on the C Steam Generator unexpectedly failed closed causing the C Steam Generator water level to rapidly drop and reach the low-low water level reactor trip setpoint. Prior to the reactor trip, the Control Board Operator attempted to open the Feedwater Level Control Valve in manual control and observed no increase in the demand signal indicator or feedwater flow. After the reactor trip, Emergency Operating Procedure E-0 for Reactor Trip was performed and the plant was stabilized in Mode 3. The automatic initiation of a reactor trip from 100% power via the Reactor Protection System on November 6, 2001, was a valid reactor trip and was not part of a pre-planned sequence during testing or reactor operation. Therefore this event is reportable pursuant to 10 CFR 50.72(b)(2)(iv)(B) and 50.73(a)(2)(iv)(A). The cause of the unexpected closure of the C Main Feedwater Regulating Valve was a random failure of a diode in the 7100 process rack module that controls the valve actuator. The safety significance of the automatic reactor trip on November 6, 2001 was small.
3342001004 | Beaver Valley 1 | 12/07/2001 | 02/04/2002 | ML02037067 | <strong>Manual Reactor Trip Due to Loss of Station Instrument Air</strong><br /><i>Abstract:&nbsp;</i>At 1353 hours on December 7, 2001, the operating station air compressor 1SA-C-1A tripped while station air compressor 1SA-C-1B was de-energized for preventive maintenance. The running compressor tripped due to a blown fuse in its control circuitry. The blown fuse was caused by a short circuit that was the result of uninsulated screwdriver contact in an energized circuit between compressors 1SA-C-1A and 1SA-C-1B. The on-shift operations crew responded per the appropriate alarm response procedure, and entered Abnormal Operating Procedure (AOP) 1.34.1, “Loss of Station Instrument Air”. Operators were dispatched locally to compressor 1SA-C-1A, the compressor’s supply breaker and to the backup diesel air compressor 1SA-C-2. A local start of 1SA-C-1A was unsuccessful due to the blown control power fuse. The backup diesel air compressor was started and placed in service; however, system pressure had already reached an abnormally low level and the backup diesel compressor was unable to restore system pressure due to insufficient capacity. The low system air pressure caused Loop 1C main steam trip valve, TV-1MS-101C, to begin to close as indicated by alarm “Steamline Stop Valve Not Fully Open”. At 1401 hours, Beaver Valley Power Station (BVPS) Unit 1 reactor was manually tripped due to the loss of station air in accordance with AOP-1.34.1. All control rods fully inserted into the reactor core and all required safety systems operated as designed. Emergency Operating Procedure E-0 for Reactor Trip was performed and the plant was stabilized in Mode 3. The direct cause for the manual trip was a loss of station air due to the unavailability of both station air compressors. The root cause of the event was determined to be the failure of the station work process to adequately plan, review, control, assign risk significance, and provide adequate oversight for work activities. This event is reportable pursuant to 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73(a)(2)(iv)(A) as a valid reactor trip and was not part of a pre-planned sequence during testing or reactor operation. The safety significance of this event was low.
3352001001 | St. Lucie 1, St. Lucie 2 | 01/09/2001 | 08/13/2002 | ML02228032 | <strong>Control Room Ventilation Emergency Recirculation Procedures Inadequate</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2001, St. Lucie Units 1 and 2 were in Mode 1 at 100 percent reactor power. St. Lucie began investigating issues related to the procedural requirements for operating the control room ventilation system in the emergency mode. On January 31, 2001, St. Lucie determined that existing equipment issues with the control room differential pressure instrumentation, along with the inadequate procedural guidance for operation of the control room ventilation system during the emergency recirculation mode, could have led to inadequate control room pressurization. This event was caused by procedural inadequacies that could have allowed operation of the control room ventilation system without proper alignment of outside air make up to the control room envelope. Procedure changes have been made to correct the condition. Changes to the EOPs are in progress. Revision 1 added additional information concerning the adequacy of previous surveillances. Revision 2 adds information regarding the cause of the high steady state St. Lucie Unit 2 control room pressure and the additional corrective actions associated with that condition.
3352001002 | St. Lucie 1 | 04/03/2001 | 05/22/2001 | ML01150022 | <strong>Technical Specification Minimum Shutdown Cooling Loop Operation Requirement Violation</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2001 St. Lucie Unit 1 was shutdown in Mode 4 operations during the beginning of the SL1-17 refueling outage. At 0440 hours the 1A and 1B shutdown cooling loops were removed from service when at the same time both the 1A1 and 1A2 reactor coolant pumps were out of service. This left only one cooling loop (i.e., the "B" reactor coolant loop) operable and in operation. Technical Specification 3.4.1.3 requires two operable cooling loops with one loop in operation. At 0645 hours when control room personnel identified this configuration actions were immediately initiated to restore the minimum required cooling loops to service. The 1A1 reactor coolant pump was restored to operable status at 1036 and the action statement for Technical Specification 3.4.1.3 was exited. Both the 1B1 and the 1B2 reactor coolant pumps remained in service during the event. The cause of this event was a personnel error that authorized the implementation of an equipment clearance order that removed both of the shutdown cooling loops when the "A" reactor coolant loop was out of service. Procedure changes are planned to strengthen the clearance order process to preclude recurrence to this event.
3352001003 | St. Lucie 1 | 04/14/2001 | 06/12/2001 | ML01170021 | <strong>Reactor Coolant System Instrument Nozzle Leakage Caused by Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2001, Unit 1 was in refueling Mode 6 following shutdown for a scheduled refueling outage. During maintenance to replace fixed insulation with removable insulation at the 3/4-inch 1B hot leg instrument nozzle RC-126, a minor through wall reactor coolant system (RCS) leak was indentified at the nozzle. A review of the alloy600 nozzle material used at RC-126 indicates that heat NX-003 was used. There is no industry failure history for this heat; however, Alloy 600 is susceptible to primary water stress corrosion cracking (PWSCC) and has occurred in similar conditions in the RCS hot leg at St. Lucie Unit 1 and six other Combustion Engineering (CE) Nuclear Steam Supply System (NSSS) units. There are nine uses of this heat in Unit 1, including the one that failed at RC-126. Visual inspection of the other eight nozzles of the susceptible heat NX-0003 was completed and no leakage was identified. Corrective actions include replacement of RCS nozzle RC-126 under ASME Section XI IWA-7000 with a half nozzle design prior to startup. The RCS inspection procedures were reviewed and are effective at identifying the leakage associated with the small-bore PWSCC failures and no changes were required. FPL is developing a replacement schedule for the remaining eight nozzles.
3352001004 | St. Lucie 1 | 04/28/2001 | 06/27/2001 | ML01184021 | <strong>Mode 2 Entered Without Both Hydrogen Recombiners Operable</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2001, at 1327 hours, St. Lucie Unit 1 entered Mode 2 following the St. Lucie spring 2001 refueling outage (SL1-17). Contrary to Technical Specification 3.6.4.2, the lB hydrogen recombiner was not in service during the mode change. FPL discovered that the lB hydrogen recombiner was out of service on an equipment clearance order on April 29, 2001, at which time actions were immediately initiated to release the equipment clearance order and restore the 1B hydrogen recombiner to service. This event was caused by personnel errors and procedural weaknesses that lead to the inadvertent removal of the lB hydrogen recombiner from the equipment out of service log when the equipment clearance order was still in effect. Long term corrective actions include procedure revisions and training.
3352001005 | St. Lucie 1 | 04/22/2001 | 06/19/2001 | ML01177023 | <strong>Faulty CSAS Re-Sequencing Circuit Led to Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2001, St. Lucie Unit 1 was in the spring 2001 refueling outage (SL1-17) in Mode 5. FPL identified a safeguards test failure of the "A" train containment spray actuation signal (CSAS) re-sequence circuit due to a sticking CSAS actuation relay. St. Lucie Unit 1 experienced a similar CSAS re-sequence circuit safeguards test failure during the previous refueling outage (SL1-16). Although no definitive cause was determined during the SL1-16 outage, a sticking CSAS actuation relay would have accounted for the observed behavior during the SL1-16 safeguards testing. Therefore it is reasonable to assume that the CSAS actuation relay was inoperable during the last St. Lucie Unit 1 operating cycle. This test failure was caused by a sticking relay. The subject relay was replaced, and forensic analysis will be performed to determine if any other corrective actions are necessary based on the results of the analysis.
3352001006 | St. Lucie 1 | 05/22/2001 | 07/19/2001 | ML01205019 | <strong>Degraded EDG Radiator Lead to Operation of Facility Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2001, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. During the performance of the monthly Technical Specification (TS) surveillance run, FPL discovered that the 1B2 emergency diesel generator (EDG) had a radiator leak. Corrosion of the EDG radiator cooling fins resulted in a loss of structural support of the radiator flat tubes that ultimately caused the failure of the soldered mechanical tube joints. Corrective actions included replacement of the 1B2 EDG radiator, preventive maintenance program and procedure revisions, training, and planned replacement of the lA2 EDG radiator.
3352001007 | St. Lucie 1 | 06/05/2001 | 08/01/2001 | ML01218011 | <strong>Reactor Coolant Pump Trip Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2001, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. At 1048 hours, St. Lucie Unit 1 experienced an unexpected trip of the 1A2 reactor coolant pump (RCP). This was immediately followed by an automatic reactor trip from the reactor protection system (RPS) on low reactor coolant flow. The Unit 1 turbine generator tripped following the reactor trip. Plant electrical distribution systems automatically transferred from the unit auxiliary transformers to the unit start up transformers as required for onsite power. Approximately one minute later, the 1B main feedwater pump (MFP) tripped and the auxiliary feedwater system actuated to provide cooling flow to the steam generators. All safety-related equipment operated per design. FPL determined that the most probable cause of the 1A2 reactor coolant pump trip was the spurious actuation of a Westinghouse SA-1 motor protective relay device. This determination was based on vendor notifications, known industry history, and the symptoms of the trip. FPL replaced the SA-1 relay and a main feedwater recirculation valve positioner, and at power operations for St. Lucie Unit 1 resumed on June 7, 2001.
3352001008 | St. Lucie 1 | 06/11/2001 | 11/21/2001 | ML01332007 | <strong>Operation with Concurrent Inoperable EDG and Opposite Train Feature Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2001, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. During the performance of a surveillance run of the 1B EDG, the EDG developed a radiator leak. The 1B EDG was declared out of service and returned to service on June 17, 2001. Concurrent with the EDG inoperability, the 'A" channel reactor vessel level monitoring system (RVLMS) was out of service and Action b of Technical specification 3.8.1.1 was not entered because FPL did not consider RVLMS to be a required critical safety-related system. This TS position was documented in Condition Report 01-1237. On October 9, 2001, FPL was informed, via the telephone, that the NRC Staff did not agree with the documented St. Lucie TS position regarding opposite train verification requirements with an inoperable EDG. The NRC believed that the literal wording of the subject TS did not support FPL's interpretation. To correct this condition, FPL submitted a TS change to align the St. Lucie TS with the CE Standard Technical Specification (STS) wording. The CE STS wording clearly allows continued operation with concurrent EDG (subject to the EDG allowed outage time) and opposite train feature inoperability, as long as the inoperable feature does not provide a critical safety function. Because the TS amendment allows operation comparable to FPL's former interpretation of the current TS, this event had no impact on the health and safety of the public.
3352001009 | St. Lucie 1 | 09/04/2001 | 11/29/2001 | ML01339039 | <strong>Inoperable Accident Monitoring Instrument Led to Operation Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On September 4, 2001, St. Lucie Unit 1 was in Mode 1 operation at 100 percent reactor power. LI-1103, the pressurizer cold calibrated level instrument, was taken out of service on October 12, 2001 to replace a power supply. At the time, LI-1103 was credited as a post accident monitoring instrument. Based on a review of LI-1103's instrument history, on October 13, 2001 St. Lucie determined that the instrument should have been declared out of service during the surveillance performed on September 4, 2001. The cause of this event, failing to declare LI-1103 out of service due to increasing degradation, was personnel error, with inadequate surveillance procedure requirements contributing to the event. However, prior to this event FPL recognized that pressurizer level instrument LI-1103 was never intended to be qualified as post accident monitoring instrumentation, and submitted a change to the Technical Specifications to correct this error. The NRC subsequently approved the license amendment on October 18, 2001. Therefore, this event had no impact on the health and safety of the public.
3362001001 | Millstone 2 | 01/07/2001 | 02/06/2001 | ML01044007 | <strong>Security Event Report: Vital Area Security Breach in the Auxiliary Building Roof Without Compensatory Security</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2001 at 0300, the Millstone Unit No. 2 Shift Manager questioned the lack of compensatory measures in place for a 20 inch x 20 inch hole in the Auxiliary Building roof. No security guard or fire watch was posted at the hole. The Shift Manager contacted Protective Services at 0500 with what he felt was a potential fire issue. A Security Shift Supervisor was dispatched to the scene. The Security Shift Supervisor determined that a breach in a vital area boundary existed at 0514 due to the size of the hole, which could potentially have allowed undetected access into the area, and remained at the scene until another guard was formally posted. An immediate (1 hour) notification was made on January 7, 2001, pursuant to 10 CFR 73.71(b)(1) and 10 CFR 73.71 Appendix G, "Reportable Safeguards Events." The cause of the event was that the planner did not include the necessary structural barrier breach notification requirements or security guard requirements in the automated work orders (AWOs) in accordance with the established procedures. As a result of this event training will be given to all planners and team leaders to re-enforce the requirement to use the Millstone work control procedures during the preparation and review of AWOs. An interim compensatory action was implemented requiring AWOs that breach a system or boundary to receive a peer check by a qualified planner to ensure that all design functions are considered and proper implementation requirements are incorporated into the AWO. The interim compensatory action will be terminated upon completing the training of the planners and team leaders.
3362001003 | Millstone 2 | 04/29/2001 | 06/26/2001 | ML01199003 | <strong>Unit 2 Reactor Trip Resulting from Loss of "C" Circulating Water Pump</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2001, with the plant at 97 percent power an automatic plant trip occurred due to a degraded condenser vacuum caused by both Circulating Water pumps (CWP) in one condenser not operating. In preparation for testing the "D" CWP following maintenance activities performed on it, electricians inadvertently caused the "C" CWP to trip when attempting to install a jumper in the "D" CWP breaker cubicle. The loss of circulating water resulted in a degrading condenser vacuum which then caused an automatic turbine trip. The turbine trip caused the reactor to automatically trip. Following the trip, all safety systems functioned as required. The auxiliary feedwater system auto started due to low steam generator (S/G) level caused by S/G level shrink following the reactor trip. The root cause of this event was determined to be inadequate procedures that did not include the correct information or require the correct verifications. Following the plant trip, work was stopped and briefs were conducted with the appropriate groups to reinforce work expectations. All lifting of leads or installation of jumpers not controlled by an approved procedure will require additional supervisor review. To prevent recurrence a procedure is being developed to provide guidance to control the running/bumping of motors following on-line maintenance.
3362001004 | Millstone 2 | 05/07/2001 | 07/03/2001 | ML01198017 | <strong>Manual Reactor Trip Following "B" Circulating Water Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On Monday May 7, 2001, with the plant at 96 percent power, preventive maintenance work was being performed in the Unit 2 "A" Circulating Water bay. The "A" Circulating pump, "A" travelling screen, and travelling screen in the adjacent "B" bay were tagged off for diver protection which allowed an accumulation of seaweed on the "B" screen over a period of several hours. When the "B" screen differential pressure reached its setpoint of 30 inches, the "B" Circulating Water pump automatically tripped. The reactor was then manually tripped per procedure at approximately 1433 hours due to the loss of two Circulating Water pumps in one condenser. There were no significant complications following the trip and all safety systems functioned as designed. The root cause of this event was determined to be that the risks and consequences of non-safety related work management decisions are not completely identified or assessed. To prevent recurrence a risk assessment process is being developed that utilizes the collective knowledge of plant personnel to identify those activities having the potential to jeopardize the safe and continuous operation of the plant. Additional corrective actions are being addressed via the Millstone Corrective Action Program.
3362001005 | Millstone 2 | 08/23/2000 | 07/13/2001 | ML01205037 | <strong>Turbine Driven Auxiliary Feedwater Pump Inoperable Without Meeting Action Statement Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2001, as a result of additional analysis in response to NRC Unresolved Item 50-336/2001-003-01, it was determined that the turbine driven auxiliary feedwater pump (TDAFP) had been inoperable from August 23, 2000, until September 20, 2000, without meeting the requirements of Technical Specification 3.7.1.2, "Auxiliary Feedwater Pumps." At the time of discovery, the plant was in Mode 1 at 100% power. During the time that the TDAFP was inoperable from August 23, 2000, until restored on September 21, 2000, the plant operated in Mode 1. The cause of the inoperable TDAFP was a failed spring in the governor speed control. The cause of not recognizing that the pump was inoperable is due to a failure to effectively implement the corrective action program. (These weaknesses in implementation of the corrective action program are documented in NRC Inspection Reports 50-336/2001-017 and 50-336/2001-003.) More specifically, plant personnel failed to aggressively investigate the degraded condition of the TDAFP on August 23, 2000. Corrective actions included: 1) The spring was replaced. 2) Direction and training have been provided to Millstone 2 Senior Reactor Operators which emphasized the need for conservative decision making when dealing with degraded equipment.
3362001006 | Millstone 2 | 06/12/2001 | 08/13/2001 | ML01232007 | <strong>Turbine Driven Auxiliary Feedwater Pump Enclosure Door Inoperable Without Compensatory Measures</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2001, a Condition Report was generated to document a concern expressed by the NRC Resident Inspector relating to a work activity conducted on May 11, 2001 at Millstone Unit No. 2 (MP2). On May 11, 2001, with the unit operating in Mode 1 at 100% reactor power, welding was performed on the MP2 Turbine Driven Auxiliary Feedwater [BA] Pump [P] (TDAFWP) enclosure door [DR]. This door is designated as a High Energy Line Break (HELB) barrier due to the four inch steam supply line feeding the TDAFWP. The nature of the work required the door to be open for approximately 45 minutes. During this time, although operators remained cognizant of the work activity, no compensatory measures were taken to protect equipment credited for safe shutdown in the event of a HELB originating from within the enclosure and no Technical Specification ACTION statements were acknowledged during the work evolution. The cause of this event is under investigation and will be reported in a supplement to this report. Corrective actions to date include the revision of existing plant procedures governing work on hazard boundary doors to require entry into applicable Technical Specification ACTION Statements. The safety significance of this event is judged to be low on the basis of the short exposure time and low probability of the initiating event.
3362001007 | Millstone 2 | 10/22/2001 | 12/17/2001 | ML02037026 | <strong>Movement of Heavy Loads Not Addressed in Procedure</strong><br /><i>Abstract:&nbsp;</i>It has been identified that no safe load path exists for lifts of new fuel shipping containers and spent resin casks at Millstone Unit No. 2 in the area of the cask washdown pit and the associated lifting device is not single failure proof. Safety related commodities are located both in the pipe trench below the cask pit floor and on the west wall of the railroad access bay. Load lifts on the order of 24 feet are required to bring material into and out of the spent fuel pool area via this load path. Previously it was identified that a 50 ton reactor coolant pump motor was stored in the cask washdown pit and that the drop of this motor would result in failure of the floor and potential damage to safety related components in the pipe trench. The root cause for the failure to identify heavy load paths is inadequate work practices in the Millstone engineering department in the area of programs. Remedial corrective actions taken to date include marking the location of the pipe trench on the railroad access bay floor and removal of the reactor coolant pump motor from the cask washdown pit using a NUREG-0612 compliant lift. Additional corrective actions are being addressed in accordance with the Millstone Corrective Action Program.
3382001001 | North Anna 1 | 01/24/2001 | 03/12/2001 | ML01075027 | <strong>Ventilation Flow Outside Technical Specification Limits Due to Inadequate Test Techniques</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2001, with Units I and 2 operating at 100% and 96.5% power respectively, testing of the control room emergency ventilation system revealed that the flow rate from emergency ventilation supply fan 2-HV-F-42 was less than Technical Specification (TS) 4.7.7.1.b.3 limits. Technical Specification 4.7.7.1.b.3 requires a flow rate of 1000 +l- 10% cubic feet per minute (cfm) from each of the emergency ventilation supply fans. The measured flow rate was 834 cfm. This testing was performed as a corrective action from a November 2000 test where the flow rate from emergency ventilation supply fan 2-HV-F-41 was measured to be only 794 cfm. This event is being reported for Unit 2 pursuant to 10CFR50.73(a)(2)(i)(B), for a condition prohibited by TS and 10CFR50.73(a)(2)(vii), for a single cause that rendered two trains of a single system inoperable. Based on 2-HV-F-42 test results, the Unit 1 control room emergency ventilation supply fans were tested in an expeditious manner. Testing of emergency ventilation supply fan 1-HV-F-42 was satisfactory with a flow rate of 1046 cfm. Testing of emergency ventilation supply fan 1-HV-F-41 revealed a flow rate of 733 cfm which is less than TS requirements. Therefore, this event is also being reported for Unit 1 as a condition prohibited by TS per 10CFR50.73(a)(2)(i)(B). The cause of the ventilation flow rates not meeting TS requirements was due to previous inadequate test techniques. The ventilation flow rate for each of the fans that did not meet TS requirements (3 out of 4) was adjusted and testing was satisfactorily performed to verify as-left ventilation flow was within TS requirements.
3392001001 | North Anna 2 | 01/19/2001 | 02/16/2001 | ML01052041 | <strong>Unit Shutdown Required Due to Identified Reactor Coolant Leakage Exceeding Limits</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2001, at approximately 1145 hours, with Unit 2 in Mode 1 at 99 percent power, a Notification of Unusual Event (NOUE) was declared, as a result of ramping Unit 2 off line due to identified Reactor Coolant System leakage greater than the Technical Specifications (TS) limit of 10 gallons per minute (gpm). Actual leakage was measured at 10.0015 gpm. At 1215 hours, a 1 hour report was made to the NRC Operations Center in accordance with 10 CFR 50.72(a)(1)(i). Unit 2 was ramped off line in accordance with the TS and placed in hot standby. The source of the identified leakage was determined to be from the valve stem stuffing box on the C reactor coolant loop bypass valve. The valve was placed on its backseat and leakage stopped at 2145 hours. The C reactor coolant loop bypass valve was successfully repaired by 1640 hours on January 20, 2001. Subsequent leak rate testing verified leakage to be 0.0839 gpm. Following successful testing of the C reactor coolant loop bypass valve the unit was brought back on line at 0254 hours on January 21, 2001. This event is reportable per 10 CFR 50.73 (a)(2)(i)(A) for completion of a nuclear plant shutdown required by the plant's Technical Specifications. No significant safety consequences resulted from this event since the leakage was contained and there was no release of radioactive material.
3392001002 | North Anna 2 | 03/11/2001 | 04/24/2001 | ML01121004 | <strong>Manual Reactor Trip Due to Control Bank "B" Group 2 Step Counter Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2001, at 0109 hours, with Unit 2 at 0 percent power (Mode 3) and shutting down for refueling, the control bank "B" group 2 step counter demand position indicator stopped moving at 53 steps. The Limiting Condition for Operation (LCO) for Technical Specification 3.1.3.3 requires the rod group step counter demand position indicator to be within plus or minus 2 steps of the demand position from the logic cabinet for each shutdown or control rod group not fully inserted. The control bank "B" group 2 step counter demand position indicator was greater than 2 steps from the demand position from the logic cabinet. The action requirements of TS 3.1.3.3 require the reactor trip breakers to be opened within 15 minutes if the LCO requirements cannot be met. At 0119 hours, a manual reactor trip was initiated by opening the reactor trip breakers. At 0428 hours, an 8 hour report was made to the NRC Operations Center in accordance with 10 CFR 50.72(b)(3)(iv)(A). The cause for the control bank "B" group 2 step counter demand position indicator not moving was determined to be a defect in the down counter gear. This event is reportable per 10 CFR 50.73 (a)(2)(iv)(A) for any event or condition that resulted in the manual actuation of the reactor protection system. No significant safety consequences resulted from this event since the reactor was already subcritical, with the control banks fully inserted, when the reactor trip breakers were opened and the shutdown banks inserted into the core. Therefore, the health and safety of the public were not affected at any time during this event.
3392001003 | North Anna 2 | 11/13/2001 | 03/20/2003 | ML03085064 | <strong>Reactor Vessel Head Nozzle Through-Wall Leakage Due to Lack of Weld Fusion During Original Fabrication</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2001, North Anna Unit 2 was shutdown to perform a qualified, visual barehead inspection of the reactor vessel head penetrations for evidence of leakage as required by NRC Bulletin 2001-01. On November 13, 2001, with Unit 2 in Mode 6, an apparent through-wall leak on penetration number 63 was identified based on the presence of boric acid deposited at the base of the penetration and the results of a subsequent liquid penetrant examination of the associated J-groove weld area. A non-emergency 8-hour notification was made to the NRC, at 0859 hours, on November 13, 2001, in accordance with 10CFR50.72(b)(3)(ii)(A). The event is also reportable in accordance with 10CFR50.73(a)(2)(i)(B). The cause of the event was hot-short cracking, which occurred during original fabrication of the reactor vessel head. Repairs to the welds were performed in accordance with NRC verbally approved relief requests to eliminate any leakage path. No significant safety consequences resulted from this event since RCS unidentified leakage was well below TS limits. An evaluation also determined that a complete lack of fusion in the zone between the weld and the head would not result in rod ejection accident because the weld to the tube would prevent it. The health and safety of the public were not affected at any time during this event.
3392001004 | North Anna 2 | 12/10/2001 | 02/01/2002 | ML02045018 | <strong>Technical Specification Missed Surveillance Due to Test Procedure Error</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2001 with Unit 2 in Mode 5 cold shutdown, intersystem LOCA leakage testing of the reactor coolant system (RCS) pressure isolation valves was in progress. The "B" low head safety injection (LHSI) hot leg injection isolation valve failed to meet its required seat leakage criteria of 1 gallon per minute (gpm). A 3.0 gpm flow rate was measured. While investigating this problem it was noted that Type C testing had been conducted with an incorrect valve line-up configuration rendering the previous Technical Specification (TS) surveillance tests invalid. As such, a TS missed surveillance had occurred. Subsequently, a Type C test was performed with the correct valve line-up and did not achieve acceptable results. Following valve disc and seat repairs the Type C test was performed satisfactorily. The cause of the incorrect valve line-up configuration in the test procedure is attributed to inadequate reviews during procedure revision. Acceptable RCS pressure and Type C leakage testing of the check valves directly downstream of the LHSI hot leg injection isolation valves ensure there would be no leakage out of containment. Therefore, the health and safety of the public were not affected at any time during this event.
3392001005 | North Anna 2 | 12/22/2001 | 02/15/2002 | ML02065035 | <strong>Automatic Reactor Trip Due to Turbine Control System Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2001, at 1542 hours, with Unit 2 in Mode 1 operating at 100% power, an automatic reactor trip occurred due a to failure in the turbine control electro hydraulic control (EHC) power supply system. A momentary fault on the control system power supply created a situation where the EHC system controller changed operating modes and reset its demand to zero. Consequently, the turbine valves drifted closed. The loss of load transient caused a reactor trip on low-low steam generator level. The reactor trip signal initiated a turbine trip. A non-emergency 4-hour notification was made to the NRC, at 1920 hours, on December 22, 2001, in accordance with 10CFR50.72(b)(2)(iv)(B). During the event, the auxiliary feedwater (AFW) system and accident mitigation system actuation circuitry (AMSAC) actuated. A non-emergency 8-hour notification was also made to the NRC, at 1920 hours, on December 22, 2001, in accordance with 10CFR50.72(b)(3)(iv)(A). The cause of the event was a failure of components in both the normal and backup turbine control EHC power supplies. Repairs to the components in both the normal and backup turbine control EHC power supply were performed prior to unit startup. No significant safety consequences resulted from this event because the reactor protection system and ESF systems functioned as designed following the reactor trip. The health and safety of the public were not affected at any time during this event.
3412001001 | Fermi 2 | 03/28/2001 | 05/24/2001 | ML01150026 | <strong>Emergency Diesel Generator 14 Inoperable for Greater Than the Technical Specifications Allowed 7 Days</strong><br /><i>Abstract:&nbsp;</i>The Emergency Diesel Generator (EDG) 14 generator outboard bearing failed approximately 12 hours into a 24-hour endurance run. Detroit Edison determined that the extensive work required to replace the affected bearing and to perform the associated post-maintenance testing would extend beyond the Technical Specification required Completion Time, and therefore, requested that the NRC grant a request for enforcement discretion to extend the required Completion Time from 7 days to up to 14 days on a one-time basis. The NRC granted the enforcement discretion. The EDG 14 generator outboard bearing was subsequently replaced, SR 3.8.1.13 was successfully performed and EDG 14 was declared Operable on March 31, 2001, 3 days beyond the Technical Specification allowed outage time, but within the additional 7 days granted by the NRC notice of enforcement discretion. This event resulted from a lower than adequate oil level in the bearing housing. There were two primary causes associated with this event. The design modification control process was improperly used in 1984, allowing the EDG oil sight glass piping configuration to be incorrectly modified and left uncorrected. The second cause was an inadequate process used to install oil level operating bands in 1999. Several corrective actions have been taken to reduce the probability of similar events occurring in the future. These corrective actions are related to the identified causes and are further addressed in the LER.
3412001002 | Fermi 2 | 01/23/1988 | 10/26/2001 | ML02011012 | <strong>Licensed Power Limit Exceeded Due to a Non-conservative Moisture Carryover Fraction</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2001, Detroit Edison determined that a non-conservative bias existed in the reactor heat balance methodology for calculating core thermal power. Specifically, the main steam moisture carryover fraction used in the heat balance calculations was found to overestimate the actual moisture content of the steam. Due to this condition, it is possible that Fermi 2 exceeded its licensed power limits on one or more occasions; however, this bias represents an insignificant portion of the total thermal power (less than 0.1 percent) and is also small compared to the overall precision of the core thermal power evaluation. Exceeding the thermal power limit in Fermi 2 License Section 2.C.(1) is a reportable condition under Section 2.F. of the Fermi 2 Operating License. Based on the low order of magnitude of the calculation bias and conservatism inherent in the power levels used for safety analyses, this condition did not result in any adverse impact on the health and safety of the public. The moisture carryover fraction in the heat balance calculations will be revised to reflect the plant test data. As an interim measure, the maximum reactor power level was administratively reduced by three megawatt thermal.
3412001003 | Fermi 2 | 11/09/2001 | 12/13/2001 | ML02031035 | <strong>Pressure Isolation Valve Leak Test Failure</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2001, leak testing of Pressure Isolation Valve (PIV) El 100F050A, Division 1 Residual Heat Removal (RHR)/Low Pressure Coolant Injection (LPCI) System injection line inboard isolation check valve, was performed in accordance with Technical Specification (TS) Surveillance Requirement SR 3.4.5.1. The resultant leak rate was determined to be in excess of the specified leakage criteria of 10 gpm. The valve and its air-operated test actuator were disassembled and inspected. It was determined that the disk was being prevented from fully closing by the actuator. The cause of the failure of the disk to fully close was determined to be improper reassembly of the actuator during the previous refueling outage because of inadequate craft skills and insufficient craft supervision during this period. The actuator was rebuilt properly, the soft seat was replaced and the valve was successfully leak rate tested. The opposite division counterpart, E1100F050B, successfully passed its as-found leak test this outage; however, it was also disassembled, inspected, and its soft seat replaced. With both actuators properly assembled, and with new soft seats installed, historical performance indicates that both valves should pass their as-found leak rate tests at the end of the next operating cycle.
3412001004 | Fermi 2 | 12/06/2001 | 01/31/2002 | ML02050050 | <strong>Manual Reactor Scram Due to Loss of Stator Water Cooling</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2001, at 0350 hours operators inserted a manual scram from 100 percent power due to a leak on the Stator Water Cooling system upper heat exchanger. The leak occurred when a vent line separated from the heat exchanger during removal of the pipe cap from the vent line. All systems responded as expected and all control rods fully inserted. Reactor level was recovered with the Feedwater/Condensate System. No Emergency Core Cooling Systems initiated and no Safety Relief Valves lifted. The cause of the vent line failure was inadequate problem documentation and resolution that dates back to 1996. The original vent line design was a contributing factor. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in manual or automatic actuation of any systems listed in paragraph (a)(2)(iv)(B), (i.e., actuation of the Reactor Protection System including reactor scram or reactor trip). The original vendor supplied heat exchanger vent lines were strengthened and an unsupported length was reduced. Schedule 80 steel was used to replace the schedule 40 steel and the connection to the heat exchangers was welded vice threaded.
3482001002 | Farley 1, Farley 2 | 05/23/2001 | 07/19/2001 | ML01205026 | <strong>Penetration Fire Seals Do Not Meet 3-Hour Fire Rating</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2001 it was determined that a condition had existed resulting in an unanalyzed condition that could potentially degrade plant safety in that separation requirements between trains of safe shutdown equipment were not met. An evaluation of twenty-nine large penetration fire seals concluded that there is insufficient industry and test data to ensure that they can be rated as three-hour fire barriers as is required by 10 CFR Part 50 Appendix R. Appendix R defines required separation requirements for safe shutdown equipment to protect the plant in the event of a fire. These penetrations are located throughout both units. The cause of this event is inadequate design in that the fire penetration seals associated with this event were designed and installed without sufficient verification of their rating as three-hour fire barriers. Fire watches have been established since November 8, 2000 in the areas affected by these seals and will continue until this condition is corrected. Modifications are being planned to upgrade these seals to provide a three-hour fire barrier as is required by Appendix R. On June 20, 2001 Southern Nuclear Operating Company's (SNC's) designers identified additional large seals that needed further evaluation. Additional fire watches were established to address these seals. Of these, sixteen have been subsequently determined not to meet three-hour fire barrier rating requirements. Appropriate compensatory actions will be maintained until upgrades are completed. Additional review of fire barrier penetrations in question will be completed by 180 days from the report date of this LER.
3482001003 | Farley 1 | 10/29/2001 | 12/26/2001 | ML02042025 | <strong>B Train LOSP Sequencer Failed to Sequence Loads During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2001 at 1234, the B train loss of offsite power (LOSP) sequencer failed to operate during surveillance testing. Evaluation determined that the sequencer had likely been inoperable since August 2, 2000 when a new mechanically operated contacts (MOC) switch was installed in the lB emergency diesel generator (EDG) output breaker cubicle during routine preventive maintenance. Subsequent evaluation determined that the MOC switch had a bent contact that prevented the sequencer from operating. This is a condition prohibited by Technical Specifications 3.8.1 "AC Sources-Operating" and could have prevented the completion of the safety function of the EDG. Had an LOSP event occurred without a coincident safety injection (SI), the emergency bus would have been re-energized but some of the required B train equipment would not have automatically started. If an LOSP had occurred, plant operators would procedurally check for proper equipment operation and manually start needed equipment. At the time of the surveillance test, plant conditions did not require the 1B EDG to be operable. This event was caused by inadequate post maintenance testing (PMT). To correct the condition, the MOC switch was repaired and tested. To prevent recurrence, the MOC switch repair procedure has been revised to include as-left continuity checks of all pairs of contacts and 2 mechanical alignment check on reinstalled or replaced MOC switches. Other MOC switch maintenance work packages completed since the last integrated safeguards test on both units have been reviewed to determine if appropriate PMTs on MOC switches were performed. All required additional testing has been completed.
3522001001 | Limerick 1 | 07/11/2001 | 09/10/2001 | ML01261001 | <strong>Emergency Diesel Generator (EDG) Fuel Oil Water Removal Missed Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>During D 12 Emergency Diesel Generator (EDG) testing, the underground fuel oil storage tanks for D11 and D12 EDGs were identified to contain water. Open fuel oil storage tank access pit drain valves allowed storm drain water to enter the access pits and cover the fuel oil storage tank breather vent valves. Leakage through the breather vent valves allowed water in the fuel oil storage tanks. Routine surveillance testing failed to detect the water. The failure to identify and remove accumulated water in the underground fuel oil storage tanks for Emergency Diesel Generators D11 and D12 is a violation of Technical Specification 4.8.1.1.2.b.2. A new detection medium is now being used to identify the presence of water in the storage tanks.
3522001002 | Limerick 1, Limerick 2 | 07/20/2001 | 09/18/2001 | ML01264012 | <strong>Unanalyzed Condition - Fire Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>During a review of the replacement of Topaz inverters with NLI inverters for the 125/250 VDC distribution system, it was discovered that the existing NLI design (designed in 1995 and installed in Unit 1 in 1998 and Unit 2 in 1999) introduced a new aspect of a failure mode which was not compatible with the center tap design of the DC system. This was not recognized during the original modification analysis. This failure mode, that would result from a ground on the negative 125 VDC portion of the system, would result in a potential across the inverters' surge suppression devices in excess of the design rating causing DC supply fuses to blow. This failure mode would disable credited fire safe shutdown equipment and methods. The affected NLI inverters were replaced with Topaz inverters for Unit 2 and the circuitry was altered on Unit 1 to prevent the failure mode. The cause of the condition was failure to identify that the design of the NLI inverters was not compatible with the center tap design of the ungrounded DC system.
3532001001 | Limerick 2 | 02/23/2001 | 04/24/2001 | ML01117006 | <strong>Manual Scram Following MSRV Failing Open Due to Erosion and Oxidation of the First Stage Pilot Valve Disc Seating Area</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2001, operators were performing a planned Unit 2 shutdown to repair the 2N Main Steam Relief Valve (MSRV) due to first stage pilot valve seat leakage. During power reduction the 2N MSRV inadvertently lifted and remained open. The cause was a sudden loss of material from the first stage pilot valve due to erosion and oxidation of the Stellite disc material in the area of the seating surface. A manual scram was initiated as required by Technical Specifications (TS). Suppression Pool Cooling was placed in service. The Main Steam Isolation Valves (MSIVS) were manually closed in response to the reactor depressurization but the cooldown rate exceeded the TS limit of 100 Fahrenheit degrees per hour due to the open MSRV. The reactor level response to the scram resulted in a valid low-level signal to the Reactor Protection System (RPS) and Primary Containment and Reactor Vessel Isolation Control System (PCRVICS) systems. Group 2A and 2B isolation valves were in the closed position but received a valid isolation signal from the reactor low-level condition. The 2N and 2M MSRVS were subsequently replaced and Unit 2 was returned to power operation. The SRV Leakage Determination Monitoring Process was revised to provide added margin and improved direction on actions associated with pilot valve leakage.
3532001002 | Limerick 2 | 06/26/2001 | 08/20/2001 | ML01236038 | <strong>Failed lug on Main Generator Alterex Exciter protective relay system caused generator lockout and reactor scram</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2001 at 13:39 hours Unit 2 experienced a reactor scram on turbine trip and generator lockout . This event was caused by a failed wire lug in the Alterrex phase differential current protective relay system . The connection lug failed due to cyclic fatigue . The connection was repaired, and the unit was returned to power on June 28, 2001 .
3532001003 | Limerick 2 | 08/28/2000 | 07/27/2001 | ML01212022 | <strong>2B Containment Hydrogen Recombiner Temperature Controller Failure</strong><br /><i>Abstract:&nbsp;</i>Failure analysis of the 2B Containment Hydrogen Recombiner temperature controller determined that the controller failed to respond to temperature setpoint adjustments following restoration of control power. This controller had failed following power restoration on three occasions prior to identification of this failure mode. It was later determined that the 2B Containment Recombiner was inoperable for a period that exceeded the 30 day LCO specified in TS 3.6.6.1.Further investigation determined that the 2A Containment Recombiner had been inoperable for approximately eleven days during planned maintenance activities concurrent with the 2B recombiner inoperability.
3542001001 | Hope Creek | 05/08/2001 | 07/06/2001 | ML01194001 | <strong>Plant Shutdown due to Main Steam Isolation Valve Sealing System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2001, Technical Specification 3.0.3 was entered when both trains of the Main Steam Isolation Valve Sealing System (MSIVSS) were declared inoperable. The inboard ("A") MSIVSS was inoperable due to excessive leakage into the system through normally closed isolation valves. A failure of a Class-1E 4.16 kV bus potential transformer (PT) removed power from the "C" Emergency Diesel Generator (EDG) synchroscope. As a result, the "C"EDG could not be synchronized with the offsite power source in accordance with Surveillance Requirements. Since the "C"EDG is the standby electric power source for the "B" MSIVSS, both MSIVSS subsystems were considered inoperable. The PT failure had no effect on the "C"EDG's ability to automatically start and load in response to a loss of offsite power. The plant shutdown was completed at 1502 hours on May 8, 2001. This event is reportable as the completion of a plant shutdown required by Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(A), and as a condition prohibited by Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(B). The failure of the PT was due to a shorted primary winding. There were no actual safety consequences associated with this event. The "B" MSIVSS subsystem remained capable of performing its safety function. The failed PT and inboard MSIVSS header isolation valve were replaced.
3542001002 | Hope Creek | 06/22/2001 | 08/17/2001 | ML01236041 | <strong>Both Trains of Control Room Emergency Filtration System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2001, the 'C' emergency diesel generator (EDG) heat exchanger cooling water outlet relief valve opened when two pumps were operating in the 'A' Safety Auxiliaries Cooling System (SACS) loop. The relief valve was set to open at 120 psig instead of the design setpoint of 150 psig. During a postulated design basis event, pressure could have exceeded the lift setpoint, causing the valve to open. If automatic makeup to the 'A' SACS loop head tank was not available, operator action would be required to identify and correct the condition before loss of inventory resulted in loop inoperability. At the time of discovery, scheduled maintenance prevented the 'B' train of the Control Room Emergency Filtration (CREF) System from performing its design function. Thus, it is possible that neither CREF train would have been available during a postulated design basis event. The root cause was the failure to update the Bill of Material for relief valve 1 EGPSV-2409C as part of a design change package. Upon discovery, the 'A' SACS loop was placed in a configuration that ensured system pressure would not exceed the lift setpoint for 1 EGPSV-2409C. The relief valves on the 'A', 'B', and 'D' EDGs were verified to have the correct lift setpoint. The 'B' CREF train was returned to OPERABLE status. Relief valve 1 EGPSV-2409C was replaced with a valve with the correct lift setpoint.
3542001003 | Hope Creek | 10/10/2001 | 10/31/2001 | ML02011015 | <strong>Potential to Exceed Licensed Power Level Due to Reactor Heat Balance Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2001 PSEG Nuclear LLC received a General Electric (GE) report titled, 'Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations, September 2001,' from the Boiling Water Reactor Owners Group (BWROG). This report documents a non-conservative assumption for moisture carryover used in the calculation of core thermal power. The assumed carryover fraction of 0.1% was discovered to be closer to 0.0% (non-conservative) in later model GE BWRs. Hope Creek Generating Station may be affected by the non-conservative core thermal power calculation with an estimated bias of less than 4 MWt. As a result, there is a potential that Hope Creek Generating Station has operated at power levels in excess of 100 percent of rated power as stated in License Condition 2.C (1). This event is being reported as a Special Report in accordance with the requirements of License Condition 2.F. The apparent cause, as described in the GE report, is that a non-conservative assumption for moisture carryover was used in the calculation of core thermal power. The design specification for the steam separator/steam dryer of 0.1 % carryover was assumed to be correct and was used in the plant process computer for many BWR units. The immediate corrective action was to limit shift average power to not exceed 99.9% of rated.
3542001004 | Hope Creek | 10/08/2001 | 12/07/2001 | ML02007040 | <strong>Reactor Building Differential Pressure Controller Incorrectly Set</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2001, reactor building pressure failed to meet the acceptance criteria during the reactor building integrity functional test. The acceptance criteria were selected to ensure the minimum pressure difference across all locations of the reactor building wall will be greater than or equal to 0.25 inches of vacuum water gauge under all postulated environmental conditions. Both reactor building differential pressure controllers were found to be set incorrectly to 0.50 inches of vacuum water gauge. Per the system operating procedure, they should be set to 0.55 inches of vacuum water gauge. The controllers were reset to the correct setpoint and the reactor building integrity functional test was completed satisfactorily. Based on a review of maintenance records, PSEG Nuclear believes the reactor building differential pressure controllers were set incorrectly during a maintenance or surveillance testing activity performed at some time after the previous reactor building integrity functional test completed on April 21, 2000. There were no safety consequences associated with this event. Under postulated worst case temperature differences, all primary containment leakage would still exhaust through the filtered FRVS pathway. There was no impact to the public health and safety.
3542001005 | Hope Creek | 10/10/2001 | 12/07/2001 | ML02007039 | <strong>Reactor Vessel Level - Low (Level 3) Scram</strong><br /><i>Abstract:&nbsp;</i>On October 10, 2001 at 0245 a reactor scram occurred due to low water level (12.5"), although the reactor was already in a shutdown condition with all control rods inserted. The cause of the scram signal was Reactor Vessel Level dropping below the level 3 trip set point. The Start Up Level Control Valve was unable to adequately respond to the level changes in automatic control. Minutes earlier at 0239 a trip of both Reactor Water Cleanup (RWCU) pumps tripped on low flew. This was a distraction to the operating crew, and resulted in loss of reactor water conductivity indication and vessel water cleanup. The apparent cause for the tripping of the RWCU pumps was flashing of the water in the instrument lines associated with flow detection for the pumps. A review of the procedures for the depressurization was performed; no discrepancies were identified in the performance of the procedure or with the actions described in the procedure. Corrective actions include revising the RWCU procedure, training and repairing the start up level control system. The reactor vessel dropping below the level 3 trip setpoint caused an automatic actuation of the Reactor Protection System {JC}, therefore, this event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A).
3542001006 | Hope Creek | 10/10/2001 | 12/07/2001 | ML02022023 | <strong>Discovery of a Pressure Boundary Leak During the Outage</strong><br /><i>Abstract:&nbsp;</i>At approximately 0332, on October 10, 2001, while performing a primary containment walk down at the beginning of the 10th refueling outage, plant personnel observed a leak on the 'A' Reactor Recirculation {AD} Pump {PMP} suction pipe elbow taps. The observed leak was producing a 3-4 inch spray with the reactor vessel pressure at approximately 300-400 psig. The leak was located where a one-inch pipe is welded to the 28-inch suction line of the "A" recirculation pump. Further investigation revealed that the leak was coming from the weld area and was, therefore, a through-wall leak breach of the reactor coolant system pressure boundary. The apparent cause of the leak was attributed to a weld failure due to vibration induced fatigue of the weld. Some of the corrective actions taken were: (1) Station personnel walked down (a) all recirculation lines for any other failure indications and (b) the equipment in the area of the leak was inspected to ensure no damage from leak impingement, (2) Performed technical evaluation of leak - potential for full failure with "A" recirculation pump in service, (3) Performed radiographic examination (RT's) on other extrados lines and penetrant tests (PT's) on all other susceptible welds - for extent of condition, and (4) Fix the cracked weld. This event was reported in accordance with 10CFR50.72.(b)(3)(ii).
3542001007 | Hope Creek | 10/24/2001 | 12/13/2001 | ML02024030 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specification Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2001 Hope Creek Engineering personnel received the initial results of the Target Rock Model 7567F Safety Relief Valve (SRV) setpoint testing required by Technical Specification 4.4.2.2. This testing revealed that following Hope Creek Cycle 10, three of the fourteen SRVS experienced setpoint drift outside of the Technical Specification 3.4.2.1 limit of +l- 3%. The apparent cause for all three valve failures is sticking of the pilot disc. The valves were replaced with tested and certified spare valves. Since the number of SRVs outside of the setpoint tolerance limit (three) was greater than the number of SRVs (one) allowed to be inoperable by Technical Specification 3.4.2.1, this condition was determined to be reportable under 10CFR50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant Technical Specifications. These three valves will be disassembled and inspected to document the cause of the failure. In addition, since this failure mechanism could be present in all the valves, PSEG Nuclear LLC, will test all fourteen pilot valves at the next refueling outage.
3542001008 | Hope Creek | 10/30/2001 | 12/21/2001 | ML02042010 | <strong>Unplanned Nuclear Steam Supply Shutoff System Isolation During Function Testing</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2001 at 1859, during the performance of electro-hydraulic control (EHC) testing, an actuation of the Nuclear Steam Supply Shutoff System (NSSSS) occurred. This actuation was due to the Low Condenser Vacuum Trip bypass becoming un-bypassed during the performance of testing of the EHC system logic for turbine overspeed protection. The apparent cause of this event was improper execution of a test procedure step that resulted in the main turbine reset push button on the EHC section of the Main Control Panel (MCP) being depressed and held (the normal method of turbine reset). Corrective actions include a review of this event to facilitate proper interface between technicians and operators during testing, a review of the associated functional test, and a review of human performance traps. There was no safety significance to this event. The Nuclear Steam Supply (NSS) system was removed from service per station procedures and was not capable of producing steam. All valves that were expected to close from this signal were already closed with the exception of the main steam line drain inboard and outboard isolation valves. These containment isolation valves closed as expected. The condition is being reported in accordance with the requirements of 10CFR 50.73 (a) (2) (iv, A) As "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).."
3542001009 | Hope Creek | 12/12/2001 | 02/11/2002 | ML02058001 | <strong>Rod Block Monitor Channel Inoperable Due to Failed Local Power Range Monitor Card</strong><br /><i>Abstract:&nbsp;</i>On 12/20/01, it was noted that local power range monitor (LPRM) 48-41A was providing an upscale input to the rod block monitoring (RBM) system despite being bypassed. LPRM 48-41A failed low on 12/12/01 and had been bypassed in accordance with plant procedures. The cause of the erroneous input to the RBM was a failed LPRM card in the 10-C-608, Power Range Monitoring Panel. The LPRM card was pulled to eliminate the erroneous signal. The effect of the erroneous upscale output from LPRM 48-41A was to cause the RBM channel "A" gain change circuit to produce a lower than required gain, so that RBM channel "A" may not have been capable of imposing a rod block when required for 15 control rods in the vicinity of LPRM 48-41A. Since this condition existed for longer than the time permitted by TS 3.1.4.3, it is reportable as a condition prohibited by plant Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(B). There were no safety consequences associated with this event. The applicable operating procedure will be revised to add a step requiring that the four rod display be checked when bypassing an LPRM to confirm that the output for the bypassed LPRM is zero.
3542001010 | Hope Creek | 12/12/2001 | 02/28/2002 | ML02077003 | <strong>Rod Block Monitor Channel Inoperable Due to Failed Local Power Range Monitor Card</strong><br /><i>Abstract:&nbsp;</i>On 12/20/01, it was noted that local power range monitor (LPRM) 48-41A was providing an upscale input to the rod block monitoring (RBM) system despite being bypassed. LPRM 48-41A failed low on 12/12/01 and had been bypassed in accordance with plant procedures. The cause of the erroneous input to the RBM was a failed LPRM card in the 10-C-608, Power Range Monitoring Panel. The LPRM card was pulled to eliminate the erroneous signal. The effect of the erroneous upscale output from LPRM 48-41A was to cause the RBM channel "A" gain change circuit to produce a lower than required gain, so that RBM channel "A" may not have been capable of imposing a rod block when required for 15 control rods in the vicinity of LPRM 48-41A. Since this condition existed for longer than the time permitted by TS 3.1.4.3, it is reportable as a condition prohibited by plant Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(B). There were no safety consequences associated with this event. The applicable operating procedure will be revised to add a step requiring that the four rod display be checked when bypassed an LPRM to zero.
3612001001 | San Onofre 2, San Onofre 3 | 02/22/2001 | 04/16/2001 | ML01110002 | <strong>More Conservative Understanding of EDG Automatic Voltage Regulator TS Surveillance Testing Results in TS Violation</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2001, SCE recognized that at times in the past, one or more of the four Emergency Diesel Generators (EDG) have been aligned to an automatic voltage regulator (AVR) that was not included in all of the Technical Specification (TS) surveillance testing for the EDG. Consequently, even though this discrepancy is considered administrative in nature and surveillance testing in itself does not impact the operability of an EDG, SCE is reporting this condition in accordance with 10 CFR 50.73(a)(2)(i)(B) as this occurrence does not consist solely of a case of a late surveillance. The cause was an inappropriate assumption that the AVR could be adequately tested as a sub-component to demonstrate its operability in support of the EDG. When the applicable surveillance procedure was developed, SCE did not incorporate the most conservative application of these TS surveillance requirements. TS compliance was achieved by selecting an AVR that had been tested or completing the required surveillance testing. Subsequently, operator training was provided on the revised methodology for performing EDG surveillance testing. On April 6, 2001, SCE submitted a TS amendment application to clarify the applicable EDG surveillance requirements for ensuring AVR operability. Because the AVRs were found operable when tested, SCE concludes this occurrence has no safety significance.
3612001002 | San Onofre 2, San Onofre 3 | 02/28/2001 | 04/25/2001 | ML01116025 | <strong>Incorrect Technical Specification Surveillances on Reactor Protection System Logic</strong><br /><i>Abstract:&nbsp;</i>The San Onofre Nuclear Generating Station (SONGS) Reactor Trip Circuit Breakers (RTCBs) are General Electric (GE) model AK-2-25 and are actuated via both shunt and undervoltage coils. Southern California Edison (SCE) implements Technical Specification (TS) Surveillance Requirement (SR) 3.3.4.2 and TS SR 3.3.4.4 (as they apply to the RTCBs) by verifying the loss of voltage across the undervoltage coil circuit and by verifying the presence of voltage across the shunt coil circuit. On 2/28/01, SCE recognized that the breaker auxiliary contact was in series with the shunt coil between the two points used to verify voltage across the coil circuit. The RTCB Switchgear design contains a resister and a light that provide a parallel pathway around both the RPS Logic K -relay contact and the manual push button contact. Therefore, because of this parallel voltage path and series auxiliary contact, SCE's test method did not satisfactorily implement TS SR 3.3.4.2 or TS SR 3.3.4.4. SCE is reporting this event in accordance with 10 CFR 50.73(a)(2)(i)(B). SCE performed the verification of the K-relay contacts and the manual push button contacts after removing the parallel voltage pathway. Because the RTCBs contain redundant trip devices (i.e., both a shunt trip coil and an undervoltage trip coil) and the successful completion of the TS SRs, this issue has no safety significance.
3612001003 | San Onofre 2, San Onofre 3 | 10/22/2001 | 12/19/2001 | ML01358014 | <strong>One Train of CREACUS Inoperable Due to Unlatched Circuit Board</strong><br /><i>Abstract:&nbsp;</i>At 2020 PDT on October 22, 2001, a control room operator while making his rounds discovered the CREACUS Train B flow control system was inoperable (indicated flow upscale while system shutdown). SCE determined the flow-indicating controller (and CREACUS Train B) had been inoperable from the time the Train B recorder paper was last changed (October 4, 2001). Because Unit 2 increased Mode during this period (an action prohibited by the Tech Specs), this condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B). The cause of the failure was a dislodged circuit board in the Train B flow recorder (Westinghouse Veritrak Model 75RE2010). SCE concluded the flow recorder's service module was likely inadvertently unlatched when the recorder paper was last changed on October 4, 2001. The dislodged card was immediately reseated. As an interim action while reviewing and implementing long term corrective actions, an independent verification that the service module is properly latched will be required following each recorder paper change. These conditions would not have impacted the ability of the control room operators to take appropriate accident mitigation actions. SCE concludes that there is no increase in calculated Core Damage Frequency or Large Early Release Frequency.
3622001001 | San Onofre 3, San Onofre 2 | 02/03/2001 | 04/02/2001 | ML01095001 | <strong>Fire and RPS/ESF Actuations Caused by the Failure of a Non-Safety-Related 4.16 kV Circuit Breaker</strong><br /><i>Abstract:&nbsp;</i>On 2/3/01, plant operators were increasing Unit 3's power following completion of its Cycle 11 refueling outage. At about 1513 PST, when switching offsite power sources for Unit 3, a feeder breaker (3A0712) faulted and started a fire. This resulted in a loss of power to non-1 E systems at Unit 3, a turbine/generator trip, a reactor trip, and a start of both Unit 3 Emergency Diesel Generators. Containment emergency coolers were also started. Anticipating the fire would last more than 15 minutes, an Unusual Event was declared at 1527 PST. The failure of a DC breaker to function properly resulted in the unavailability of the turbine/generator lubricating oil system, causing damage to the turbine/generator. The event was caused when breaker 3A0712 faulted, and started a fire within the breaker cubicle. Ionized gases and smoke diffused through cable passages between adjacent cubicles and entered the Reserve Aux Transformer (RAT) feeder breaker 3A0714 cubicle and caused a ground fault with the 3A0714 cubicle, which resulted in the RAT trip and loss of non-safety-related offsite AC power to Unit 3. The fire consumed much of breaker 3A0712's non-metallic parts and caused substantial melting of current carrying components. Consequently, the exact cause of the breaker fault could not be conclusively determined. SCE will implement modifications to appropriate preventive maintenance procedures to address the apparent failure causes. SCE has replaced/rebuilt 5 electrical cabinets in bus 3A07. This includes replacement of electrical equipment and cables that were either burned directly or damaged by the fire. Damage to the turbine/generator is being repaired.
3622001002 | San Onofre 3 | 01/20/2001 | 03/27/2002 | ML02091022 | <strong>Starting the Movement of Irradiated Fuel With One Train of PACU Inoperable Causes TS Violation</strong><br /><i>Abstract:&nbsp;</i>On 1/18/2001, during refueling, Southern California Edison began moving fuel (new and irradiated) from the Fuel Handling Building to the reactor vessel inside containment. At that time, both trains of Post Accident Cleanup Unit (PACU) were operable. On 1/20/2001 (event date), at about 0330 PST, PACU train B was removed from service, placing the unit in Technical Specification (TS) 3.7.14, Action A. Prior to train B being returned to service, fuel movements were stopped on January 20, 2001, 1339 PST due to an equipment failure. Fuel movement re-started that same day at about 1358 PST. At that time, train B PACU was still inoperable and train A was not placed into service, as required by TS 3.7.14 Action B. and TS 3.0.4. Consequently, this event is being reported in accordance with 10CFR50.73(a)(2)(i)(B). The event was discovered while reviewing records on March 8, 2002. The event occurred because the requirements of the TSs with respect to PACU and the movement of irradiated fuel in the Fuel Handling Building had not been correctly reflected in a plant procedure (cognizant personnel error). The procedure was corrected and operating crews will be briefed to prevent recurrence. This event had minimal safety significance.
3642001001 | Farley 2 | 06/23/2001 | 08/14/2001 | ML01232015 | <strong>Reactor Trip due to Main Generator Neutral Connecting Bolt Failure</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2001, with the reactor at 100% power, Unit 2 experienced an automatic reactor trip due to a main generator neutral overcurrent trip, which resulted in a turbine trip/reactor trip. The generator neutral transformer electrical connection bolt had been overtorqued during previous refueling outages and subsequently failed, resulting in a main generator trip. The failure of the bolted electrical connection on the generator neutral overcurrent transformer was due to a combination of personnel error and inadequate procedure in that on three occasions workers misidentified the silicon bronze bolt as steel and consequently overtorqued it. The main generator tagging and backfeed procedure did not provide guidance for distinguishing between coated bronze and steel bolt materials which are visually similar but have different torque requirements. This overtorquing was further aggravated on two of three occasions by failure to follow procedure in the use of metric values with a wrench calibrated in English units. A contributing cause was inadequate procedure in that no guidance on evaluating an overtorquing was established. The main generator tagging and backfeed procedures will be revised by September 1, 2001 to specify the exclusive use of silicon bronze bolts in this application, to specify only a single torque value, and to require replacement of the generator neutral transformer connecting bolts every refueling outage. Appropriate personnel will be made aware of this event and of the above procedure changes by October 1, 2001. Appropriate training and procedure changes will be provided by October 1, 2001 to create a standard requiring that, if a bolt is ever overtorqued, it will be evaluated for suitability for continued service.
3642001002 | Farley 2 | 06/26/2001 | 08/14/2001 | ML01232012 | <strong>Reactor Trip Due to Turbine Trip from Turbine Latch Mechanism Problem</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2001, at 0646, with the reactor at 100% power, Unit 2 experienced an automatic reactor trip due to turbine trip. At 0646, the reactor operator reinstalled the turbine latch pushbutton in the turbine control panel on the main control board after changing the light bulbs in the pushbutton. This action requires the pushbutton to be depressed in order to lock it in place. Depressing the turbine latch pushbutton actuates the turbine latch mechanism at the turbine (even if the turbine is already latched). When the latch pushbutton was released, the latch mechanism overtraveled from the latch position through the neutral position to the trip position, resulting in a direct turbine trip and consequently a reactor trip. This event was caused by an equipment deficiency in that the latch mechanism overtraveled to the trip position when released from the latch position. A contributing cause was that operators incorrectly concluded that depressing the pushbutton would not initiate additional actions since the turbine was latched, and therefore did not constitute a risk to continued operation. Administrative controls have been placed on the latch pushbutton on both units to preclude actuation when the turbine is already latched. The latch mechanism will be repaired or modified, or the remote latching feature disabled, at the next outage of sufficient duration. Training material has been revised and will be covered in licensed personnel requalification training by December 14, 2001.
3662001001 | Hatch 2, Hatch 1 | 03/08/2001 | 04/30/2001 | ML01127027 | <strong>Poor Work Practice Results in Trip of Emergency 600-Volt Bus "2C" and Unplanned System Actuations</strong><br /><i>Abstract:&nbsp;</i>On 03/08/2001 at 0306 EST, Unit 2 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, the supply breaker to Unit 2 emergency 600-volt bus "2C" opened on a false over-current signal. As a result, Reactor Protection System (RPS) bus "2A" lost power. Logic systems powered by the RPS bus include the RPS trip logic, the Main Control Room Environmental Control System (MCRECS) initiation logic, Primary Containment Isolation System (PCIS) trip logic, and Steam Packing Exhauster trip logic. All affected systems responded per design on the loss of power, producing a half scram signal, several PCIS valve isolations, MCRECS pressurization mode initiation, and other actuations. In addition, the "A" subsystems of the Core Spray, Residual Heat Removal (RHR) containment spray, RHR suppression pool spray, and RHR service water systems were rendered inoperable. By 0540 EST, personnel had re-energized 600-volt bus "2C" and returned affected safety-related systems to their normal lineups. The cause of the supply breaker trip was a poor work practice causing personnel calibrating an over-current relay to short two trip contacts in the relay case, generate a false over-current signal, and trip the bus supply breaker. Corrective actions included revising calibration procedures to eliminate the poor work practice.
3662001002 | Hatch 2, Hatch 1 | 10/26/2001 | 12/14/2001 | ML01353014 | <strong>Reactor Recirculation Pump Flow Rate Changes Cause Reactor Scram on APRM High Flux</strong><br /><i>Abstract:&nbsp;</i>On 10/26/2001 at 1917 EDT, Unit 2 was in the Run mode. At that time, the reactor scrammed on Average Power Range Monitor high neutron flux caused by a rapid increase, after an unexpected decrease, in the flow rate of the 2B reactor recirculation pump. Following the scram, water level decreased due to void collapse from the rapid reduction in power resulting in closure of Group 2 and Group 5 primary containment isolation valves and automatic initiation of the Reactor Core Isolation Cooling and High Pressure Coolant Injection systems. The low level initiation signal cleared before either system could inject water to the vessel. The secondary containment dampers automatically isolated and all trains of the Unit 1 and Unit 2 Standby Gas Treatment systems automatically started on low water level. Level reached a minimum of 40 inches below instrument zero. The Reactor Feedwater Pumps restored level to its pre-event value of approximately 35 inches above instrument zero within 35 seconds of the scram. Reactor vessel pressure did not exceed its normal value of approximately 1035 psig; therefore, no safety/relief valves lifted nor were any required to lift to reduce pressure. The cause of this event is not known conclusively, although the available evidence indicates a problem with the amplifier board in the 2B reactor recirculation pump scoop tube positioner logic circuit is the most likely cause. Corrective actions include replacing the amplifier board; temporarily requiring the 2B recirculation pump scoop tube to be locked when pump speed is not being changed; monitoring selected parameters in the pump speed control system; and performing a failure analysis of the amplifier board.
3662001003 | Hatch 2 | 12/25/2001 | 02/14/2002 | ML02052030 | <strong>Sudden Closure of Main Steam Line Isolation Valve Causes Pressure Increase and Reactor Scram on APRM High Flux</strong><br /><i>Abstract:&nbsp;</i>On 12/25/2001 at 1819 EST, Unit 2 was in the Run mode. At that time, the reactor scrammed on Average Power Range Monitor high neutron flux caused by a rapid increase in reactor pressure vessel pressure. Pressure increased quickly as a result of the unexpected and sudden closure of main steam line isolation valve 2B21-F028B. The closure of the main steam line isolation valve isolated one of the four main steam lines. Although the flow rates in the remaining three steam lines increased to compensate partially for the isolated line, the sudden isolation of one line was sufficient to cause reactor vessel pressure to increase from a nominal value of 1035 psig to 1041.2 psig within 0.3 seconds. This rapid rate of change in pressure caused reactor power to increase to 120.5 percent rated thermal power and the reactor to scram on high neutron flux level. Following the scram, water level decreased due to void collapse from the rapid reduction in power resulting in closure of Group 2 primary containment isolation valves. Level reached a minimum of 33.5 inches below instrument zero, a level not low enough to initiate other protective actions. Therefore, no systems other than the Group 2 primary containment isolation valves actuated or were required to actuate. The Reactor Feedwater Pumps restored level to its pre-event value of approximately 36 inches above instrument zero within 30 seconds of the scram. Reactor pressure reached its maximum value of 1048.2 psig less than one second after the scram. It decreased thereafter and was maintained below 975 psig by the main turbine bypass valves. No safety/relief valves lifted nor were any required to lift to reduce pressure. This event was the result of component failure caused by high-cycle fatigue. The stem in valve 2B21-F028B failed completely, causing the valve to close and reactor vessel pressure to increase. Corrective actions include replacing the stem and determining the feasibility and cost of options to reduce or eliminate stem vibration.
3682001001 | Arkansas 2 | 05/11/2001 | 10/16/2001 | ML01296047 | <strong>Crediting a Designated Operator For Manual Action During Surveillance Tests Affected Operability of the Emergency Feedwater System if Condensate Pumps Had Been Lost During the Tests</strong><br /><i>Abstract:&nbsp;</i>Surveillance testing of the Emergency Feedwater (EFW) pumps has been conducted utilizing the Startup and Blowdown Demineralizer effluent as a suction source. The procedure required a designated Operator in communication with the Control Room with a duty to close a manual isolation valve if conditions developed during the test potentially affecting operability. Whether a Technical Specifications action statement should be entered while in this configuration was questioned. An Engineering evaluation determined that under worst-case conditions following a loss of all condensate pumps the operability of the EFW pumps could be affected. The action by the designated operator may not have been timely to ensure EFW System operability under all conditions. The surveillance test method has been revised. The root cause of this condition was inadequate establishment and communication of management expectations regarding evaluations crediting manual actions that are used to maintain operability. Written guidelines are being developed. An assessment of this condition determined it to be non-risk significant.
3682001002 | Arkansas 2 | 11/01/2001 | 12/20/2001 | ML01355006 | <strong>An Improperly Positioned Mode Select Switch Resulted in an Automatic Actuation of the Reactor Protection System Whille Troubleshooting a Dropped Control Element Assembly</strong><br /><i>Abstract:&nbsp;</i>While troubleshooting a dropped Control Element Assembly (CEA) with reactor power approximately 24 percent, an automatic actuation of the Reactor Protection System (RPS) occurred. The CEA Operator (CEAO) inadvertently selected the Mode Select Switch to a position that resulted in insertion of all CEAs in one group (consisting of two subgroups) instead of only the CEA that had dropped. This resulted in a deviation between the positions of the two subgroups and generated a penalty factor that caused a trip of the Core Protection Calculators. Plant response to the trip was normal and uncomplicated. All CEAs fully inserted and the plant was stabilized in hot standby conditions. Work practice root causes were that the CEAO did not monitor diverse CEA positions during CEA movement and did not apply self-checking to verify that the Mode Select Switch was in the correct position. A management methods root cause was that management expectations concerning peer checking during reactivity manipulations were not adequately understood and applied. The event was determined to have had minimal safety significance.
3692001001 | McGuire 1 | 06/21/2001 | 12/05/2001 | ML02028035 | <strong>Emergency Personnel Hatch (EPH) not fully secured in the closed position</strong><br /><i>Abstract:&nbsp;</i>Unit Status: On 6/21/01, Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On June 21, 2001, the tamper seals were discovered missing and the handwheel misaligned on the Unit 1 Emergency Personnel Hatch (EPH) between upper and lower containment. At 1330 hours, Technical Specification 3.6.14 was entered which requires the unit to be in Mode 3 within seven (7) hours in the event the hatch is not restored to closed status. The hatch was fully closed/sealed at 1415 hours. The surveillance requirements per Technical Specification 3.6.14.2 and 3.6.14.3 were successfully completed at 1630 hours. Event Cause: The root cause for the EPH seal integrity compromise could not be conclusively determined. The most likely cause for the compromise is traffic in the vicinity of the EPH during performance of an Extra High Radiation Lamp (EHRL) inspection/replacement procedure. No evidence exists to indicate that the EPH was opened for personnel transit entry between the date of discovery and the last required surveillance. Corrective Action: Radiation Protection procedure HP/0/B/1006/009 will be evaluated for potential enhancements.
3702001001 | McGuire 2 | 07/16/2001 | 09/04/2001 | ML01253022 | <strong>Unit 2 Reactor Trip and Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>Unit Status: On 7/16/01, Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On 7/16/2001, Maintenance personnel were performing routine maintenance on pressure instrumentation associated with the Unit 2 Main Steam Lines. Maintenance personnel in the Control Room area placed Channel 2 of 2B steam line pressure in test in the 7300 process protection cabinets as required per the test procedure. Maintenance personnel in the field then incorrectly isolated Channel 3 steam line pressure transmitter. This satisfied the 2 of 3 protection logic initiating a Main Steam Isolation Signal. Closing the Main Steam Isolation Valves resulted in a Reactor Trip and a Main Turbine Trip. An automatic start of the three Auxiliary Feedwater Pumps (CA) occurred as a result of decreasing Steam Generator levels. Event Cause: Lack of attention to detail has been determined to be the cause of the wrong pressure transmitter being isolated. Corrective Action: The Maintenance personnel were counseled on the importance of maintaining a high level of attention to detail. Component verification process enhancements were implemented.
3732001001 | LaSalle 1, LaSalle 2 | 01/31/2001 | 03/22/2001 | ML01087027 | <strong>Reactor Scram Due to Electrical Fault on Transformer Yard 345 KV Line C Phase Insulator</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2001, at 2147 hours, current from the "C" phase of the 345 KV power line between the Unit 1 main power transformer and the switchyard flashed to ground across a support insulator. The phase-to-ground fault activated the transformer protective relays, resulting in a turbine generator trip and reactor scram. The cause of the phase-to-ground fault was determined to be an excess of bird excrement that had built up on the support insulator. Corrective actions included replacement of the damaged insulator, and inspection and cleaning of the other insulators. An evaluation to determine how to prevent birds from roosting on the equipment was begun. The safety consequences of this event were minimal. All safety systems operated as expected. A turbine generator trip is an analyzed condition of moderate frequency. The reactor was safely shut down and recovery performed without incident.
3742001001 | LaSalle 2 | 04/06/2001 | 05/25/2001 | ML01150035 | <strong>Reactor Scram Due to Blown Fuse in Feedwater Control System During Maintenance</strong><br /><i>Abstract:&nbsp;</i>At 0909 hours on April 6, 2001, LaSalle County Station, Unit 2 automatically scrammed from 100 percent power due to a blown fuse in the feedwater (FW) control system that occurred during maintenance. The blown fuse resulted in multiple failures in the FW control logic, and caused both Reactor Recirculation (RR) pumps to downshift to slow speed. The FW control failures and the level swell from the RR pump downshifts caused a high reactor water level, and the main turbine stop valves to close. This caused an automatic reactor scram due to turbine stop valve closure with reactor power above 25 percent power. The root cause of this event was an inadequate maintenance risk assessment performed for the work. The corrective action to prevent recurrence is to revise the Exelon Nuclear Conduct of Maintenance Manual, 0.5, Maintenance Risk Assessment, to require an evaluation of the risk to the plant for maintenance activities that involve work on an energized circuit with the potential to create a fault in the circuit. The safety consequences of this event were minimal. A RR pump trip, a turbine generator trip, and a loss of FW flow are analyzed conditions of moderate frequency (Updated Final Safety Analysis Report (UFSAR) Chapter 15). The plant responded as described in the referenced UFSAR Chapter. The reactor was safely shut down and recovery performed without incident.
3742001002 | LaSalle 2 | 05/27/2001 | 07/16/2001 | ML01205022 | <strong>Reactor Scram Due to High Turbine Vibration During Testing</strong><br /><i>Abstract:&nbsp;</i>At 0618 hours on May 27, 2001, LaSalle County Station, Unit 2 automatically scrammed from 80 percent power. The automatic reactor scram occurred during main turbine control valve (TCV) testing. The root cause of this event was Electrohydraulic Control fluid contamination of a connector for TCV #3 in combination with higher than normal baseline vibration during TCV testing. The contamination resulted in an incorrect TCV #3 position indication which caused TCV #3 to be mispositioned and the remaining TCVs to open further than usual to maintain pressure. When TCV #1 was closed for testing, the combination of the abnormal position of the remaining control valves and an existing main turbine "A" coupling misalignment created an unbalanced load across the high pressure turbine. This resulted in increased vibration, which reached the trip setpoint for the turbine. The corrective action to prevent recurrence included cleaning and replacement of the seal of the fouled connector during the forced outage. The safety consequences of this event were minimal. The turbine generator trip is described as an event of moderate frequency in Chapter 15 of the Updated Final Safety Analysis Report (UFSAR). The plant response was consistent with the referenced UFSAR chapter.
3742001003 | LaSalle 2 | 09/03/2001 | 10/25/2001 | ML01362034 | <strong>Reactor Scram Due to Undervoltage Protective Circuit Actuation on Division 1 ESF Bus</strong><br /><i>Abstract:&nbsp;</i>On September 3, 2001, Unit 2 ESF Bus 241Y lost power due to actuation of the Division 1 undervoltage (UV) protective circuit. This caused the feedwater level control circuits to lose power. At 1728 hours, the operators inserted a manual scram because reactor water level could not be controlled. Following the scram, reactor level continued to decrease until High Pressure Core Spray and Reactor Core Isolation Cooling automatically initiated and injected to restore level. All systems operated as designed. Safety relief valves were manually actuated to control reactor water level. All control rods fully inserted. The root cause of this event was that fuses failed in the potential transformer portion of the Division 1 UV protective circuit. This scram was inserted due to loss of feedwater flow at 100% power. This transient is bounded by loss of feedwater event with a single failure. The loss of a single ESF bus caused the loss of some ESF systems. The redundant systems were available and operated as necessary to remove decay heat and control reactor vessel level and pressure.
3742001004 | LaSalle 2 | 09/07/2001 | 10/26/2001 | ML01365034 | <strong>Manual Reactor Scram Due to Heater Drain Isolation</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2001, at 0024 hours, during power ascesion from a forced outage, at 75 percent power, LaSalle Unit 2 was manually scrammed due to 2 low pressure heater string isolations. All systems operated as designed. There were no ECCS actuations or primary containment isolations. The lowest reactor water level reached was minus 20 inches. All control rods fully inserted. The cause of the event was that the 21A and 21C low pressure heaters were lined up to use the emergency heater drains instead of the normal heater drains. At high power levels the emergency heater drains can not pass the full condensate flow required which caused the feedwater heaters to isolate when the high level trip set points were reached. The manual scram was initiated per procedure to prevent a loss of feedwater flow at less than 100% power due to low pressure heater string isolation. This transient is bounded by loss of feedwater event even if the event occurred at 100% power.
3822001001 | Waterford 3 | 01/08/2001 | 02/12/2001 | ML01047014 | <strong>Violation of TS 3.3.1 because a TS channel check was not performed as required by TS 4.3.1.1</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2001, it was discovered that a channel check required by Technical Specification (TS) 4.3.1.1 for the Pressurizes Pressure Narrow Range had not been properly completed, and the corresponding channel was not declared inoperable. The surveillance log entry contained a notation indicating that the Core Protection Calculator (CPC), required to perform the channel check, was inoperable. Since the involved operating crews did not realize the channel check was not completed as required, TS 3.3 .1 for the high pressure reactor trip was not entered as required. The cause of this event was change management, where procedure OP-903-001, "Technical Specification Logs, "was not properly revised. Subsequent evaluation noted two additional occurrences where the channel check was inadequately performed. This event did not compromise the health and safety of the public or plant personnel. This event is not considered a Safety System Functional Failure (SSFF).
3822001002 | Waterford 3 | 01/28/2001 | 03/29/2001 | ML01093007 | <strong>Common Mode Failure of Containment Isolation Valves Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2001 at 2245, with the plant operating in Mode 1 at 100% reactor power, both the inside (PSL-303) and outside (PSL-304) Containment isolation valves for the Pressurizer steam space sample line failed to close when attempted from the Control Room. The valves had been open since 1455 that same day to perform degassing of the Pressurizer. The valves were immediately declared inoperable. The outside Containment isolation valve was manually closed using a gagging device and its breaker was opened to comply with Technical Specification actions. The breaker was danger tagged to ensure compliance was maintained. Inspections and tests were performed. Evidence of internal binding (galling) was found. The root cause was determined to be inadequate design clearances to allow for thermal growth of internal valve components. The vendor (Flowserve Engineering) has been contacted for review of the failures for 10CFR21 reporting considerations and agreed that the failures meet the criteria for 10CFR21 reporting. They have agreed to file the required report. The condition is herein being reported pursuant to 10CFR 50 .73(a)(2)(v) and 10CFR50 .73(a)(2)(vii)(C). The inability of the valves to close was determined to have low safety significance due to other available valves, operator actions credited, a closed system, and available thermal margin. The condition did not compromise the health and safety of the general public. The current licensing and design bases remained bounding. This event is considered a Safety System Functional Failure (SSFF).
3822001003 | Waterford 3 | 02/13/2001 | 04/12/2001 | ML01107000 | <strong>Reactor Protection System Trip Caused by Turbine Governor Valve Oscillation</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2001 with reactor power at approximately 80% power, a secondary transient resulted in a reactor trip. During power escalation following replacement of a Tracker Driver Card on Steam Generator Feed Pump 'A' Speed Controller, turbine valve testing was being performed. Turbine Governor Valve (GV) #3 oscillated twice during testing. The resulting secondary transient caused a reactor trip initiated by a Core Protection Calculator generated Variable Over Power Auxiliary Trip. Emergency Feedwater Actuation Signals (EFAS) 1 and 2 automatically initiated on Steam Generator (SG) Level-Low starting all 3 Emergency Feed Water (EFW) pumps but no flow was delivered to the SGs. This is expected, following a reactor trip. The root cause of this event was determined to be failure of the GV #3 PARC 7300 Card. The circuit card was replaced and sent to the vendor for analysis. This event is reportable pursuant to 50.73(a)(2)(iv)(A) as an automatic actuation of the Reactor Protection System. This event did not compromise the health and safety of the public. This event is not considered a Safety System Functional Failure (SSFF).
3822001004 | Waterford 3 | 02/21/2001 | 04/23/2001 | ML01121009 | <strong>Failure to Enter TS ACTION Statement Due to Inadequate Surveillance Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2001 at 1138, with the plant operating in Mode 1 at 100% power, it was discovered that Waterford 3 was in a condition involving a failure to complete the actions required by TS 3.3.1,Table 3 3-1, item 10. This condition existed since May 25, 2000 following performance of TS 4.3.1.3 required surveillance test. The total RPS Core Protection Calculator (CPC) Channel D response time of 0.259 sec. for Reactor Coolant System Cold Leg Temperature (T-Cold) exceeded the Technical Requirements Manual (TRM) Table 3.3-2 (item 10c) response time allowable limit of =0.258 sec. This condition is being reported pursuant to 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the TS. CPC Channel D was declared inoperable in accordance with TS 3 .3.1,Table 3 .3-1 on February 21, 2001 at 1500. The root cause was determined to be a human performance error resulting in a non-conservative (inadequate) surveillance procedure. Two immediate actions were taken: (1) the RPS response time test of the CD matrix was re-performed. The plant was presently in compliance with the TS 3.3.1 LCO; and (2) an analysis was performed and determined the response time allowable limit specified in the TRM was overly conservative. Based on TS LCO compliance, CPC Channel D was returned to operable status on February 22, 2001 at 1730. In addition, the TRM was amended to reflect a total RPS CPC response time allowable limit of =0.300 sec. for the RCS T-Cold parameter. The condition did not compromise the health and safety of the general public. This is not considered a safety-system functional failure.
3822001005 | Waterford 3 | 05/01/2001 | 06/28/2001 | ML01184003 | <strong>Potential For Loss of Both EDG Fuel Oil Transfer Pumps By a Single Fire</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2001, at 0809, with the plant operating in Mode 1 at 100% Reactor power, it was discovered that a fire in Fire Area RAB 27 could result in the loss of both trains of Emergency Diesel Generator (EDG) Fuel Oil Transfer Pumps. The condition existed due to a failure to wrap certain essential 'B' train equipment cables located in that fire area. Assuming a loss of off-site power in conjunction with the fire could result in both Emergency Diesel Generators becoming inoperable in approximately 3 hours, following depletion of fuel oil in the Day Tanks. This condition could significantly impact the ability of the plant to achieve and maintain cold shutdown. The condition is believed to have been caused by a design analysis deficiency during preparation of the original safe shutdown analysis. Fire impairments were generated and compensatory measures (hourly fire watches) were established pending resolution .The condition constitutes an unanalyzed condition that significantly degrades plant safety and is therefore reportable under 10 CFR 50 .73(a)(2)(ii)(B). There was no actual fire event involved. Therefore, the condition did not compromise the health and safety of the general public. This event is not considered a Safety System Functional Failure (SSFF).
3872001001 | Susquehanna 1, Susquehanna 2 | 03/01/2001 | 05/18/2001 | ML01144003 | <strong>Standby Liquid Control System Unable to Meet Requirements of the ATWS Rule for a LOOP/ATWS Event</strong><br /><i>Abstract:&nbsp;</i>During Unit 1 and Unit 2 operation at 100% power, a discrepancy was discovered between the Standby Liquid Control System (SLCS) design pressure and the maximum pressure expected during a Loss Of Offsite Power l Anticipated Transient Without Scram (LOOPIATWS) event. In the LOOP/ATWS scenario, the SLCS would not be able to inject the 82.4 gpm required by the ATWS rule, 1 OCFR50.62. The SLCS design is acceptable for all other ATWS scenarios. The cause of the SLCS design deficiency was a lack of coordination between the ATWS analysis and the SLCS design evaluation. This allowed a disparity to exist between system design and expected system performance. Corrective actions include modification of Unit 1 and 2 SLCS to allow injection of sodium pentaborate solution into the reactor at rated flow during a LOOP/ATWS. An assessment was performed to evaluate the ability of the SLCS to achieve the objectives of the ATWS rule for a LOOP/ATWS event. The assessment shows that there is reasonable assurance that the ATWS rule objectives will be achieved, and that there were no adverse consequences to the health and safety of the public as a result of this event.
3872001003 | Susquehanna 1, Susquehanna 2 | 08/07/2001 | 10/08/2001 | ML01285044 | <strong>Licensed Power Limit Exceeded Due to Reactor Heat Balance Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2001 with Unit I and 2 at 100% power, engineering personnel discovered an error in the reactor heat balance calculation that resulted in a 6 MegaWatt-thermal (MWth) error. Specifically, the main steam moisture fraction value was found to be non-conservative. Operation greater than the licensed maximum power level is reportable as a violation of license condition. The cause of the error was confusion over similar, closely related terms associated with entrained water in steam (moisture fraction, percent moisture). The maximum power level of Unit 1 and Unit 2 was administratively reduced by 7 MWth upon discovery of the error. The reactor heat balance calculations have been subsequently corrected to use an accurate moisture fraction value, and procedures associated with an upcoming turbine replacement project that could affect the reactor heat balance will be revised to ensure that plant test data is accurately used in the reactor heat balance calculation. Although the calculation error resulted in a non-conservative reactor power level indication, the event was not significant due to the small magnitude (0.2%) of the error. Based on consideration of the margin to analyzed maximum power level, there were no adverse consequences to the health and safety of the public as a result of this event.
3872001004 | Susquehanna 1 | 11/11/2001 | 01/09/2002 | ML02031037 | <strong>High Pressure Coolant Injection Solenoid Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2001, with Unit 1 in Mode 1 (Power Operation) at 100% power, the Control Room received the High Pressure Coolant Injection (HPCI) steam line drain pot high level alarm. Operations personnel observed that valve position indication was lost on the HPCI steam line drain to condenser inboard isolation valve and the HPCI barometric condenser pump discharge drain valve. Operations declared HPCI inoperable due to the formation of condensate at the turbine inlet with no drain path available. Maintenance personnel investigated the loss of indication and found a failed fuse. The failed fuse was caused by high current draw to a failed solenoid valve. The cause of the solenoid valve failure was accelerated aging due to a normally energized coil. The failed Unit 1 solenoid valve has been replaced. This event was of very low safety significance since redundant equipment was operable. HPCI was returned to service within the allowed outage time given by the Technical Specifications.
3882001001 | Susquehanna 2 | 01/31/2001 | 03/31/2001 | ML01100028 | <strong>Main Steam Line Containment Penetration Maximum Path Leakage Total Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2001, at 23:30, with Unit 2 in Mode 1 (Power Operation) at 100% power, the Reactor Core Isolation Cooling (RCIC) inboard steam supply Primary Containment Isolation Valve (PCIV) HV249F007 was closed to support planned maintenance work on the Unit 2 RCIC system. The valve failed to close fully and it was determined that the total Main Steam Line (MSL) containment penetration leakage would have exceeded the 300 Standard Cubic Feet per Hour (SCFH) maximum pathway leakage Technical Specification limit. The RCIC outboard steam supply PCIV, HV249F008, was closed and deactivated as required by Technical Specifications. It was determined that high resistance across the HV249F007 valve motor torque switch contacts was preventing the valve from closing fully. A 250 VDC voltage was applied across the motor torque switch contacts via a low current megger and HV249F007 was stroked multiple times to improve the electrical continuity of the motor torque switch contacts. After HV249F007 was confirmed to close fully, a qualitative leak test was performed to ensure that the valve was properly seated. HV249F007 was restored to operable status on 02/08/01. The cause of the high resistance condition was due to grease/oil intrusion from the actuator gear compartments. Electrical resistance across the motor torque switch contacts was periodically measured from 02/08/01 to the start of the current Unit 2 10th refueling outage to ensure that the high resistance condition had not recurred. The valve actuator will be overhauled to replace the torque switch and reoriented to reduce grease/oil intrusion. Maintenance practices/requirements will be reviewed for any necessary changes. There was no compromise to the health and safety of the public due to this event since the automatic isolation function of the primary containment penetration was maintained by HV249F008, and the minimum pathway leakage for MSL containment penetrations remained below the Technical Specification limit.
3882001002 | Susquehanna 2 | 03/02/2001 | 04/30/2001 | ML01127003 | <strong>Both Trains of Suppression Chamber Hydrogen Recombiners Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2001 at 01:15 with Unit 2 in Mode 1 (Power Operation) at 100% power, the 'B' Emergency Diesel/Generator (D/G) was declared inoperable when a DC control power relay failed and multiple control room alarms were received. Operations personnel responded to the 'B' D/G and observed multiple local alarms and several auxiliary system pumps running that would normally be in standby. Operations personnel shutdown the auxiliary pumps and placed the 'B' DIG control switch in "local" to prevent an automatic start. Prior to this event the 'A' Suppression Chamber Hydrogen Recombiner had been removed from service for planned maintenance. The 'B' D/G is the emergency onsite power supply for the 'B' Suppression Chamber Hydrogen Recombiner. Therefore, there was a potential for a complete loss of the Unit 2 Suppression Chamber Hydrogen Recombiner safety function while emergency onsite power supply to the 'B' Suppression Chamber Hydrogen Recombiner was inoperable. The emergency onsite power supply to the 'B' Suppression Chamber Hydrogen Recombiner was restored via the spare 'E' D/G at 15:08 on March 2, 2001. It was determined that the cause for the multiple 'B' D/G alarms and auxiliary equipment starts was a failed relay coil in the DC control power circuitry for the 'B' D/G. Preliminary analysis has attributed the relay failure to "infant mortality" of the electrical component. The failed relay was replaced. It was determined that no generic concerns/common mode failure mechanisms exist with other like-in-kind relays installed at the station. The failed relay will be sent to an independent lab for failure analysis. During any postulated design basis accident, one of the two recombiners would have been restored prior to requiring its operation. There were no actual safety consequences or compromises to the public health and safety as a result of this event.
3882001003 | Susquehanna 2 | 03/19/2001 | 05/18/2001 | ML01142028 | <strong>U2 Secondary Containment Bypass Leakage Exceeded</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2001, at 0803 hours, with Unit 2 in Condition 5 (Refueling) at 0 percent power, it was determined that the as-found minimum pathway Secondary Containment Bypass Leakage (SCBL) Technical Specification limit had been exceeded during regularly scheduled Local Leakage Rate Testing. The Technical Specification SCBL limit is 9 scfh and the measured bypass leakage was 9.14 SCFH. At that time, additional SCBL pathways remained to be leak rate tested. After completion of all leak rate testing, the total SCBL was determined to be 11.13 scfh. The major contributor to the SCBL was the RHR Loop B Drywell Spray outboard isolation valve. This event was determined to be reportable in accordance with 10CFR50.73(a)(2)(ii) in that the total as-found minimum pathway SCBL leakage rate limit exceeded the Technical Specification limit. The cause of the high leakage through the RHR Loop B Drywell Spray outboard isolation valve (HV251 F016B) was due to the gland follower and stem being in contact. In addition, a small area of pitting on the disc contributed to the high leakage. The valve was reworked and successfully passed its leak rate test. There were no safety consequences or compromise to the public health or safety as a result of the additional SCBL leakage since the dose consequences from the additional leakage would not have exceeded 10CFR100 or 10CFR50 Appendix A, GDC 19 limits.
3882001004 | Susquehanna 2 | 03/20/2001 | 05/18/2001 | ML01144004 | <strong>U2 Control Rod Drive Seismic Island Exceeded</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2001, at 0803 hours, with Unit 2 in Condition 5 (Refueling) at 0 percent power, both of the in-series Control Rod Drive System (CRD) Seismic Island Check Valves (non 10CFR50, Appendix J, Option B valves) failed their leakage acceptance criteria. The Minimum Pathway leak rate was 858 ml/hr as compared to the acceptance criteria of 508 ml/hr. The valves were disassembled. The cause of the failure for the check valves was due to oxide buildup on the valve internals (body and disc) and the seating surface. This buildup resulted in the valve disc not seating properly. The valves were replaced with in-line check valves. A leak test was performed successfully on each of the new valves. There were no safety consequences or compromise to the public health or safety as a result of the check valves not passing their leak test since the dose consequences from the additional leakage would not have exceeded 10CFR100 or 10CFR50 Appendix A, GDC 19 limits.
3882001005 | Susquehanna 2 | 04/12/2001 | 06/11/2001 | ML01169025 | <strong>Multiple Test Failures of Main Steam Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2001, with Unit 2 in Mode 5 (Refueling) at 0 percent Power, 6 of 8 Main Steam Safety Relief Valves failed their as-found actuation pressure test required by Technical Specification Surveillance Requirement 3.4.3.1. The acceptable band for as-found actuation pressure is +l-1 % of the nameplate setpoint pressure. Four valves actuated below the acceptable band (-1.25%, -1.66%, -1.66% and -2.18%) and two valves actuated above the acceptable band (+1.16% and +1.53%). The cause of the event is expected drift of the valve actuation setpoints due to exposure to in-service operation. The Unit 2 reactor vessel did not reach a pressure that challenged the safety function of any of the valves and no valves opened inadvertently. All of the failed valves would have functioned below the reactor vessel design pressure and the vessel overpressurization analysis was valid for the as-found conditions. The safety significance of this event is low and the health and safety of the public was not compromised.
3892001001 | St. Lucie 2 | 03/14/2001 | 05/11/2001 | ML01135015 | <strong>Reactor Scram Due to CEA Drops</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2001, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power. At 1752 hours, the reactor automatically tripped when both control element assembly motor generator sets output breakers opened. With the exception of a few minor equipment issues, the trip was uncomplicated. Control room operators performed standard post trip actions. Long term thermal degradation caused the failure of the 2B control element assembly motor generator set voltage regulator, and subsequently lead to the opening of both motor generator sets output breakers. The 2A and 2B motor generator sets voltage regulators were replaced, and the unit was on-line on March 18, 2001.
3892001002 | St. Lucie 2 | 11/25/2001 | 01/18/2002 | ML02024041 | <strong>As-Found Cycle 12 Main Steam Safety Valve Setpoints Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2001, St. Lucie Unit 2 was in Mode 1 and holding at approximately 68 percent reactor power for Technical Specification testing of the main steam safety valves setpoints. Four main steam safety valves lifted outside the Technical Specification limits of +1 percent to -3 percent. Two of the valves (V8208 and V8212) were retested and/or adjusted and placed back in service, another was left out of service since it was scheduled for an overhaul (V8213), and the last valve was left out of service because its as-found setting exceeded 3 percent high (V8201). With the exception of V8201, the cause of the high setting was setpoint drift. V8201's test failure was due to aging effects. V8201 and V8213 were overhauled and reinstalled during the refueling outage. The preventative maintenance overhaul frequency for main steam safety valves were reviewed and FPL determined that no changes needed to be made to the scheduled valve maintenance. Operation of the facility with the as-found setting was within analytical bounds, therefore, this event had no impact on the health and safety of the public.
3892001003 | St. Lucie 2 | 12/07/2001 | 02/26/2002 | ML02064045 | <strong>Steam Generator Tube That Exceeded Plugging Criteria Remained In-Service</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2001, St. Lucie Unit 2 was in Mode 6, shutdown for the SL2-13 refueling outage. During steam generator (SG) eddy current testing, FPL determined that an error was made during the previous refueling SG eddy current testing that allowed a defect in a steam generator tube (Row 118 Column 64) to remain in service during Cycle 12 operation. This event was caused by personnel error and a failure to follow procedures. Corrective actions included plugging of the subject tube, with any process enhancements to be made once the root cause determination is completed. In situ pressure testing during the SL2-13 outage demonstrated that the defective tube met the structural integrity and accident induced leakage performance criteria of NEI 97-06, "Steam Generator Program Guidelines." Therefore, there was no impact to the health and safety of the public. Revision 1 corrects the event date associated with this event.
3902001001 | Watts Bar 1 | 06/29/2001 | 08/17/2001 | ML01239006 | <strong>Manual Reactor Trip Due to Reduced Circulating Water Flow</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2001, at 1728, Watts Bar Unit 1 was in Mode 1 at 100% power. At this time the unit was manually tripped when the main condenser back-pressure reached procedure limits. The rise in the back-pressure was caused by reduced condenser circulating water (CCW) flow which resulted from cooling tower fill material obstructing the intake flume screens to the CCW pumps. All safety systems responded as required during the event. Auxiliary Feedwater initiated due to reactor trip with low Tavg, as required. All control rods inserted properly. The root cause of this event was inadequate design output. The design allowed support schemes other than those in the issued design document to be used as needed for cooling tower fill repairs and/or replacement. The supports installed most likely failed in this event due to a combination of various loads. Corrective actions included inspection and removal of the loose cooling tower fill material, clarification of design output, and enhanced program controls for intake flume screen cleaning.
3902001002 | Watts Bar 1 | 09/04/2001 | 02/04/2002 | ML02039005 | <strong>Manual Reactor Trip Due to a Loss of the 1-I Vital AC Inverter</strong><br /><i>Abstract:&nbsp;</i>While operating at 100% power, the Watts Bar Unit 1 reactor was manually tripped at approximately 1305 EDT on September 4, 2001, due to the level of steam generator (SG) number 1 approaching the Lo-Lo level setpoint. The immediate cause of the trip is considered to be the loss of the 1-I Vital AC Inverter which caused the SG number 1 feedwater regulating valve to close. All control rods inserted properly in response to the reactor trip. The Auxiliary Feedwater (AFW) System actuated in response to the trip, as expected. However, subsequent to the initial actuation signal, additional operator action was required to start the 1A-A and 1B-B motor driven AFW pumps. The root cause for this event was determined to be the failure of the 5 watt resistor R12 on the sensing and current limiting card installed in Vital Battery Charger 6-S. Corrective actions include the replacement of the blown inverter fuses, the replacement of the failed card with subsequent load testing performed, some operating instruction revisions to provide verification of AC input breaker closure and DC output before closing DC output breakers, and a revision to the procurement data sheet for sensing and current limit board requiring additional factory burn in of new boards.
3902001003 | Watts Bar 1 | 09/29/2001 | 11/28/2001 | ML01362034 | <strong>Blocked Sense Line for Loop 4 Steam Header Pressure</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2001, a blockage in an instrument sense line was discovered. A review of computer trend data for the Watts Bar Unit 1 #4 steam generator pressure transmitter loop, determined the channel may not have performed its design function, and thus had been inoperable without being placed in the "trip" position for about 8 hours and 40 minutes longer than the 6 hour period allowed by the ESFAS technical specifications. Although the channel had been providing the correct pressure value to the ESFAS system and the control room, the blockage had slowed the time response to pressure changes beyond the time assumed in the FSAR. The other two channels which were part of the two out of three logic circuit were operable during the time period to provide the required signal to the ESFAS system. The clearing of the blockage corrected the immediate cause, and recurrence control actions included: Back filling of a sampling of the main steam pressure and flow transmitters during the upcoming refueling outage, and providing information to Operations and Engineering on this event and symptoms of a sense line blockage.
3902001004 | Watts Bar 1 | 12/19/2001 | 02/19/2002 | ML02053019 | <strong>Turbine/Reactor Trip Initiated by an Invalid AMSAC SIgnal</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2001, an invalid AMSAC signal was initiated that resulted in a turbine/reactor trip. The unit was operating at 100% power at the time of the event and work was in process for the placement of a clearance (tagout) to support the implementation of a design change to the control instrumentation for the Turbine Driven Auxiliary Feedwater (TDAFW) pump. The clearance activities opened the breakers which supply power to the instrumentation. The loss of power to the instruments resulted in an invalid steam generator (SG) lo lo level (12%) signal and satisfied the logic (3 out of 4 SGs less than 12% level) for the initiation of an AMSAC signal. All control rods inserted properly and the Auxiliary Feedwater (AFW) system started, as required, in response to the AMSAC signal and the reactor trip. The cause of the event was inadequate interface requirements in the planning and scheduling of trip sensitive activities along with inadequate implementation of the clearance preparation process. The corrective actions included the review of open on-line clearances, development of a standard for the tagging of low voltage equipment, establishment of a formal process which reviews plant work activities for trip sensitive actions, counseling of involved personnel, training on the lessons learned from the event, identification and labeling of trip sensitive breakers, development of an instruction to define the expectations for independent review and to provide controls for the operation and tagging of low voltage breakers.
3952001001 | Summer 1 | 01/26/2001 | 03/27/2001 | ML01094004 | <strong>Failed Diodes in Diesel Generator Field Flash Circuit Render Diesel Inoperable with Other Diesel Not Fully Operable</strong><br /><i>Abstract:&nbsp;</i>On 01/10/2001 at approximately 03:00 during surveillance testing of "B" emergency Diesel Generator (EDG), the engine came up to speed but no voltage or frequency was observed. Trouble shooting determined that the cause was a short circuit in two diodes of a diode rectifier bridge, which caused a protective fuse to open. This prevented the generator field from flashing. At this same time, the "A" EDG was inoperable due to testing. The plant was shutdown with all fuel removed from the reactor vessel and a time to boil of greater than 25 hours for the Spent Fuel Pool. The same problem was discovered previously on the "A" EDG on 12/24/00 but was thought to be a random failure and the other train of ESF power was still operable. At that time the diodes and fuse were replaced. The rectifier bridge is a generator component that assured DC power was supplied as input power for the manual voltage regulator motor operated potentiometer (MOC-2). The rectifier provided DC output regardless of whether AC or DC input power was supplied. After their failure, these diodes were removed and sent off for analysis. The cause of failure was determined to be an over-voltage condition that could not be replicated either on the EDG or in the Electric Shop. The diode rectifier bridges have been removed from these circuits on both EDGs since they are not necessary. V. C. Summer uses only DC power as the input to the MOC.
3952001002 | Summer 1 | 02/22/2001 | 04/20/2001 | ML01120005 | <strong>Inappropriate Mode Change During RTD Cross Calibration of the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On 2/22/01, a Resistance Temperature Detector (RTD) cross calibration for the Reactor Protection System was in progress during plant start-up. Plant instrumentation and control procedure ICP-340.048 directs all narrow range RTDs to be disconnected from their associated instrument channels to perform RTD cross calibration. The plant had proceeded from Mode 4 to Mode 3 during the calibration process. SCE&G Operations realized that Technical Specifications (TS) Table 3.3-3, Item 9.b, should have prevented entering Mode 3. Table 3.3-3 item 9.b is the P-12 interlock, and its action statement 20 requires verification that the interlock is in its proper condition within 1 hour, which could be done, and was done. However since T.S. 3.0.4 applies, the plant should never have entered Mode 3 with this instrumentation out of service. With the plant in Mode 3, the calibration was performed satisfactorily and the system returned to service. The cause of this event is attributed to inadequate administrative control of operational restrictions within plant modes. ICP-340.048 will be revised prior to refueling outage 13 to prevent performance during mode changes.
3952001003 | Summer 1 | 03/01/2001 | 04/25/2001 | ML01121005 | <strong>Manual Reactor Trip due to Two Rods Failing to Respond to a Withdrawal Demand</strong><br /><i>Abstract:&nbsp;</i>At 0017 hours on March 1, 2001, operations personnel initiated a manual reactor trip when two control rods remained fully inserted during control rod withdrawal. All systems functioned as designed following the trip. While in the process of low power physics testing and trouble shooting a misaligned Shutdown Bank "B" control rod (G-9), the rods were fully inserted into the core. After the step counters and rod control system were reset, Shutdown Bank "B" was withdrawn. At this time, it was discovered that two rods had not moved with 14 steps demanded. The shutdown bank was reinserted into the core, and a manual trip was initiated. The two rods that did not move were G-9 and L-5, both in Shutdown Bank "B". The cause was determined to be the result of demanding control rod insertion beyond the fully inserted position (000 steps). This, in conjunction with geometric factors, placed the control rods in a position where the movable grippers would not properly engage to lift the rod when the lift coil energized. Multiple attempts to lift the control rods caused the spring at the top of the control rod assembly to re-position the control rods and allowed the movable grippers to engage. An evaluation performed by Westinghouse documented that the negative stepping of the control rods had no adverse impact on the geometric or frictional characteristics of the control rods. The temporary misalignment did not affect the critical desiqn function of the control rod mechanisms.
3972001001 | Columbia | 02/06/2001 | 04/10/2001 | ML01107029 | <strong>Traversing Incore Probe System Was Operated Without Administrative Controls As Required by Technical Specification LCO 3.6.1.3, Note 1</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2001, a Local Power Range Monitor calibration surveillance was being performed which required the operation of the Traversing Incore Probe (TIP) System. While the TIP System was energized the requirement of Technical Specification LCO 3.6.1.3, Note 1 for administrative control of containment penetration flow paths was not met. An individual was not assigned to be the dedicated operator of TIP System control switches to ensure isolation of containment penetration flow paths in the event of a valid containment isolation signal. The cause of this event was the lack of a procedural standard for establishing administrative controls in accordance with the Technical Specifications and Bases. A standard was not available when changing the method of administrative control of TIP System containment isolation valves from the use of a clearance order and tags to a revised procedure for operating the TIP System. There are no safety consequences associated with this event. The procedure for operating the TIP System has been revised to provide instructions for satisfying the TS LCO 3.6.1.3 requirement for administrative controls.
3972001002 | Columbia | 05/02/2001 | 06/21/2001 | ML01178057 | <strong>Non-Compliance with Technical Specification LCO 3.3.1.1 Due to a Scram Discharge Volume Level Instrument Isolation Valve Misconfiguration</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2001 Columbia Generating Station was at 88% power and coasting down for a refueling outage when a condition prohibited by Technical Specification LCO 3.3.1.1 was discovered. The noncompliance was due to a condition in which less than the required number of channels per trip system were operable for the Scram Discharge Volume [JC] (SDV) Water Level - High function described in Technical Specification Table 3.3.1.1-1, Function 7.b. The instrument was inoperable for a period longer than the 12 hour Completion Time allowed in LCO 3.3.1.1 Condition A. This in turn, led to non-compliance with Required Action G. 1 of LCO 3.3.1.1 to be in Mode 3 within 12 hours. The SDV instrument channel had been inoperable since an instrument isolation valve was left in the closed position on February 5, 2001 following a Channel Functional Test. The valve was misconfigured due to a personnel error. There were no system failures associated with this event. There were no safety consequences associated with this event because redundant instruments were capable of performing the safety function of actuating the Reactor Protection System if an actual SDV high water level condition had occurred. Following discovery of the inoperable SDV level instrument, the instrument isolation valve was placed in the open position and the requirements of LCO 3.3.1.1 were subsequently met.
3972001003 | Columbia | 05/21/2001 | 01/20/2004 | ML04029059 | <strong>Inoperable High Pressure Core Spray (HPCS) System due to Low System Pressure</strong><br /><i>Abstract:&nbsp;</i>At 1247 on May 21, 2001, Columbia Generating Station was in Mode 3 when the HPCS pump (HPCS-P-1) and the HPCS System were declared inoperable due to low pressure in the HPCS water leg pump discharge piping. Operations was in the process of transferring water from the condensate storage tanks to the-suppression pool when the suction path to HPCS-P-1 was isolated. HPCS-P-1 was immediately secured. HPCS System discharge pressure subsequently dropped to the low-pressure alarm setpoint, requiring Operations to declare HPCS-P-1 inoperable. After filling and venting the HPCS System, HPCS-P-1 and the HPCS System were declared operable at 1322 on May 21, 2001. This condition is reportable under 10 CFR 50.73(a)(2)(v)(D) because HPCS is a single train safety system that was unable to perform its required safety function for approximately 35 minutes. The plant remained in compliance with technical specifications, and was in a condition where both low pressure coolant injection and low pressure core spray were capable of providing flow to the reactor pressure vessel. Although this event occurred over two years ago, Energy Northwest did not discover that the event should have been reported as a single train safety system failure until November 20, 2003.
4002001001 | Harris | 12/05/2000 | 04/25/2001 | ML01121032 | <strong>Emergency Core Cooling Throttle Valves Nonconforming Condition</strong><br /><i>Abstract:&nbsp;</i>On 12/5/00, with Harris Nuclear Plant (HNP) in Mode 1 at 100% power, Engineering analytically determined that the Emergency Core Cooling System (ECCS) throttle valves were further shut than previously determined. The valve openings were determined to be less than the containment sump screen minimum opening, creating the potential for clogging of the high head safety injection lines during the recirculation phase of a design basis LOCA.HNP determined that the ECCS remained operable. HNP is reporting this condition as a voluntary LER due to this issue having a potential safety significance. Cause of this event: The original design of the HNP High Head Safety Injection lines did not adequately consider the potential for the throttle valves to become clogged due to flow clearances being less than the containment sump screen openings. The condition was not identified earlier due to an error in the vendor drawing for the ECCS throttle valves. Corrective actions: Complete the ECCS throttle valve modification to ensure that ECCS throttle valve openings are greater than the containment sump screen openings. Correct applicable drawings and documents associated with ECCS throttle valves.
4002001002 | Harris | 04/18/2001 | 06/15/2001 | ML01170054 | <strong>Unanalyzed Condition Due to Inadequate Fuse Coordination</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2001, with the Harris Nuclear Plant (HNP) in Mode 1 at 100% power, HNP engineering personnel determined that fuses intended to maintain safe shutdown train separation, in the event of a fire in the "A" Switchgear Room, are not capable of performing their intended function due to a design error. A fire in one fire area could result in the inability to isolate a Pressurizer Power Operated Relief Valve (PORV) and associated block valve. These fuses were intended to protect against this condition by isolating the PORV Block Valve control circuit on an electrical short due to a fire. The fuses provide power to the plant computer for PORV Block Valve position indication. The power to reposition the PORV Block Valves and the position indication on the PORV Block Valve control switch is not powered by these fuses. Cause of this event: Inadequate analysis during design of the applicable circuit. Corrective actions: 1) The applicable fuses were pulled as a temporary compensatory measure to provide safe shutdown train separation. 2) The design analysis has been corrected. 3) HNP has implemented a design change to install the correct fuses.
4002001003 | Harris | 10/08/2001 | 11/27/2001 | ML02016037 | <strong>1A-SA Residual Heat Removal Suction Line Debris - Nonconforming Condition</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2001, with the Harris Nuclear Plant (HNP) defueled for Refueling Outage 10, work: was being performed on 1SI-310, "Containment Vessel (CV) Sump To Residual Heat Removal Pump (RHRP) 1A-SA Downstream Isolation Valve." During the job, the mechanics observed foreign material in the RHR system piping. The mechanics removed the material and reported the discovery to management. Additional debris was found in the A train RHR and Containment Spray system lines during the event investigation. An Engineering Analysis of the material concluded that lA-SA RHRP could have been impacted by the larger pieces of debris if they moved to the pump suction. The pump may then experience a loss of capacity and become inoperable. Cause: "Work Practices (improper work methods used in the performance of the task); Workmanship, substandard cleanliness" was the root cause for this event. Corrective actions: Remove the foreign material. Perform visual inspections of: RHR and Containment Spray (CT) systems suction piping, the Containment Recirculation Sump piping, the Refueling Water Storage Tank (RWST), the CT discharge lines near Containment Isolations, and the IA-SA RHRP impeller eye. Incorporate industry best practices into HNP Foreign Material Exclusion (FME) Program (i.e. Procedure, Training, Barriers, Management Oversight, and site culture), (Corrective Action to Prevent Recurrence)
4002001004 | Harris | 12/25/2001 | 02/25/2002 | ML02072006 | <strong>Reactor Coolant Loops Mode 4 Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On December 25, 2001 at 0503, with the Harris Nuclear Plant (HNP) shutdown for Refueling Outage 10 (RF010), the plant entered Mode 4 from Mode 3 without satisfying Technical Specification (TS) 3.4.1.3. The TS requires at least two reactor cooling loops operable with one of these loops in operation. Two residual heat removal loops were operable but not in operation and no reactor coolant loops were operable since all steam generator levels indicated below the TS Mode 4 operability limit of 74% wide range. The TS 3.4.1.3 was revised as part of the Steam Generator (SG) replacement in RFO10. The requirement to maintain Wide Range (WR) SG level greater than or equal to 74% in Mode 4 was added as a result of the license amendment to replace SGs. Previously, SG level was monitored using narrow range level with an operability limit of 10% narrow range. Therefore, this event was the initial failure to meet this operability requirement. Cause: Mindset. No one in the control room anticipated that steam generator water inventory would have to be increased above the normal narrow range band in order to maintain operability in transitioning from Mode 3 to Mode 4.Corrective actions: (1) Revise plant procedures to clarify Mode 4 steam generator operability requirements. (2) Coached licensed operator supervisors and reactor operators on this event.
4102001001 | Nine Mile Point 2 | 05/16/2001 | 05/02/2002 | ML02158041 | <strong>Reactor Scram Due to Relay Failure in Electro Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2001, at 1019 hours, Nine Mile Point Unit 2 automatically scrammed from 90 percent core thermal power due to Turbine Stop Valve closure. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an automatic actuation of the Reactor Protection System that resulted in a reactor scram. The cause of the reactor scram was high resistance in a normally closed contact of relay KT106. A contributing cause was inadequate preventative actions associated with GE TIL 1212-2 recommendations for relay KT106. The immediate corrective action was to replace the KT106 relay. Preventive actions are establishing a replacement frequency for the KTI 06 relay, and evaluating methods for reducing the susceptibility to reactor scrams as a result of KT106 relay failure.
4102001002 | Nine Mile Point 2 | 05/24/2001 | 09/11/2001 | ML01267032 | <strong>Rated Thermal Power Exceeded When Recirculation Flow Control Valve Malfunctioned</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2001, at 2016 hours and at approximately 100 percent power, Nine Mile Point Unit 2 experienced a malfunction of the B reactor recirculation system flow control valve (FCV) position feedback signal, which resulted in recirculation FCV cycling and reactor power cycling. The FCV cycling lasted approximately 90 seconds and was stopped when hydraulics to the B recirculation FCV were secured. A post event data analysis determined that the estimated core thermal power reached a maximum of 103 percent and a minimum of 73 percent. A post event evaluation concluded that the transient did not result in violation of any thermal-mechanical design limits. Reactor water samples taken and analyzed shortly after the event showed no detectable increase in activity. The event is reportable in accordance with license condition 2.F. in that the maximum authorized thermal power level was exceeded. The cause of the B recirculation FCV position indication malfunction was a failure of the rotary variable differential transformer (RVDT) coupling. The cause of the coupling failure was high lateral vibration and displacement of the valve feedback rod coupled with harmonic resonance of the control system A-frame caused by flow induced vibration caused by the reactor recirculation pump. The root cause evaluation also identified weaknesses in the implementation of the Corrective Action Program. Short term corrective actions included securing hydraulics to the FCV and reducing power to balance flow between recirculation loops. Root cause and design teams were established utilizing industry failure analysis experts to determine the cause of the failure and identify actions needed to prevent recurrence. Further corrective actions included replacing the RVDT couplings and modifying the RVDT support structure's vibrational response.
4102001003 | Nine Mile Point 2 | 06/29/2001 | 08/24/2001 | ML01243011 | <strong>Methodology Error Results in Inoperable Oscillations Power Range Monitors</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2001, Nine Mile Point Unit 2 was operating at approximately 100 percent power when a Part 21 notification was received from General Electric (GE) informing Niagara Mohawk Power Corporation (NMPC) that the Oscillation Power Range Monitors (OPRM) setpoints could be non-conservative. The OPRMs were declared inoperable and the action statement of Technical Specification 3.3.1.1, "Reactor Protection System Instrumentation," was entered. As required by the action statement, alternate methods to detect and suppress thermal-hydraulic instabilities were implemented, which allowed continued operation for 120 days with the OPRMs inoperable. On July 2, 2001, GE informed NMPC that the Unit 2 OPRMs could be returned to operable by limiting the rod line to less than or equal to 102 percent. On July 12, 2001, after administrative controls were established to limit the rod line to less than or equal to 102 percent, the OPRMs were returned to operable. On July 19, 2001, GE provided NMPC with revised OPRM setpoints that would allow removing the rod line limitation. The revised OPRM setpoints were implemented on July 25, 2001, and the 102 percent rod line limitation was removed. At the time of the Part 21 notification, procedural guidance directed operators to terminate thermal hydraulic events by manually tripping the reactor. The apparent cause of the methodology error is inadequate design input considerations, because the strong dependency on bundle power was not recognized in the OPRM setpoint methodology. This event is reportable in accordance with 10CFR 50.73(a)(2)(i)(B), 10CFR 50.73(a)(2)(v)(A) and 10CFR 50.73(a)(2)(vii)(A) in that the potential non-conservatism could result in OPRM setpoints that may not provide Minimum Critical Power Ration (MCPR) Safety Limit protection for thermal hydraulic stability events.
4102001004 | Nine Mile Point 2 | 10/15/2001 | 12/14/2001 | ML02024038 | <strong>Reactor Scram Due to Inadequate Main Steam Isolation Valve Surveillance Procedure</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2001 at approximately 0959, Nine Mile Point Unit 2 (NMP2) scrammed from approximately 100 percent power due to closure of the Main Steam Isolation Valves (MSIVs). Post scram the Safety Relief Valves (SRVs) were used for reactor pressure control until the MSIVs were re-opened. The scram occurred while restoring a steam flow transmitter after surveillance testing. Post scram two high reactor water level conditions occurred that resulted in level 8 conditions. The first level 8 condition caused the "A" and "B" feedwater pumps to trip, as designed. The "A" feedwater pump was later re-started. The second level 8 condition resulted in the operating "A" feedwater pump tripping, as designed. Reactor pressure was then reduced so that the condensate booster pumps could be used for inventory control. While reducing pressure, a low reactor water level condition occurred. A level 2 condition occurred that resulted in actuation of the Reactor Core Isolation Cooling (RCIC ) System and the High Pressure Core Spray (HPCS) System and closure signals to Primary Containment Isolation Valve groups 2,3,6,7,8 and 9. Reactor water level was recovered using RCIC and HPCS. Reactor pressure was reduced and the condensate booster pumps were used to provide inventory control. RCIC and HPCS were then returned to standby. Reactor pressure was reduced to approximately 150 pounds per square inch; the MSIVs were re-opened and reactor pressure control was shifted to the Turbine Bypass valves. The cause of the reactor scram was an inadequate surveillance procedure. The causes of the low reactor water level condition were training issues relative to transient operation of RCIC and selection of a less than optimum event mitigation strategy. Corrective actions include benchmarking methods of restoration of similar transmitters, reviewing activities performed at power that are classified as trip sensitive, reviewing the event with operating crews and developing training on the effect of SRV opening on reactor water level.
4102001005 | Nine Mile Point 2 | 11/06/2001 | 12/05/2001 | ML02016051 | <strong>Maximum Licensed Power Exceeded Due to Non-conservative Moisture Carryover Fraction</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2001, with Nine Mile Point Unit 2 (NMP2) at approximately 100 percent power, Nine Mile Point Nuclear Station, LLC (NMPNS) determined that NMP2 had exceeded licensed thermal power (eight hour average) due to an inaccurate moisture carryover fraction used in the thermal power Calculation. On October 1, 2001, NMP2 became aware that General Electric (GE) had identified a condition that could result in plants exceeding their licensed thermal power. GE had determined that the moisture carryover fraction could be non-conservative for BWR 4 and later plants. When informed of this information NMP2 reduced thermal power by 2 MegaWatts Thermal (MWt) and limited maximum thermal power to 3465 MWt providing a 2 MWt margin to the licensed power limit of 3467 MWt. This condition was also entered into the corrective action program to determine if NMP2 had exceeded licensed thermal power. On November 6, 2001, after having determined that the actual moisture carryover fraction was lower than the value that had been assumed and after having reviewed historical operating data, NMPNS concluded that the licensed thermal power rating (eight hour average) had been exceeded by as much as 2 MWt. The cause is inadequate design inputs by GE. The moisture carryover fraction constant is specified by GE, which is used in the plant's computer to determine core thermal power. Corrective actions included reducing power by 2 MWt and modifying the moisture carryover fraction after determining that the NMP2 moisture carryover fraction was approximately 0.0 percent.
4102001006 | Nine Mile Point 2 | 12/02/2001 | 03/15/2002 | ML02085059 | <strong>Manual Scram Due to Feedwater Pump Motor Failure</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2001, at approximately 1449 hours, operators manually scrammed Nine Mile Point Unit 2 (NMP2) from approximately 75 percent power after the "A" Feedwater Pump tripped due to a motor failure. Prior to the Feedwater Pump motor failure a power reduction was in progress for rodline adjustments. The motor failure created a voltage transient that resulted in the loss of hydraulic power to the "A" Recirculation Flow Control Valve (FCV), which prevented its runback operation. The runback of the "B" Recirculation FCV was not sufficient to reduce power to within the capacity of the "B" Feedwater Pump. A manual scram was inserted to preclude an automatic scram because of decreasing reactor vessel water level. After the scram, none of the Emergency Core Cooling System equipment started or should have started. During the post scram recovery the "B" Feedwater pump tripped due to high reactor water level. Approximately 2.5 hours after the manual scram, a low reactor water level scram signal occurred with no rod motion, due to level shrink as operators were closing a Turbine Bypass Valve to control cooldown rate. An inspection of the motor concluded that it had experienced a phase-to-phase fault and phase-to-ground fault. This resulted in a voltage transient and the tripping of the motor breaker. The causes of the motor failure were failure to effectively implement the Corrective Action Program and a faulty motor design that led I to corona induced damage. Contributing causes include inadequate communication and insufficient motor monitoring. Corrective actions include revising the Corrective Action program, disseminating lessons learned to site management and appropriate staff, correcting the motor design flaw, rewinding pump motors and establishing a motor testing program.
4102001007 | Nine Mile Point 2 | 12/15/2001 | 08/23/2002 | ML02254063 | <strong>Manual Reactor Scram Due to Unidentified Drywell Leakage</strong><br /><i>Abstract:&nbsp;</i>On December 15, 2001, with Nine Mile Point Unit 2 (NMP2) at approximately 100 percent power, Nine Mile Point Nuclear Station, LLC (NMPNS) identified drywell floor drain leakage approaching the maximum limits of Technical Specification (TS) 3.4.5 for unidentified drywell leakage. Plant shutdown was commenced before reaching any of the limits of TS 3.4.5. Additionally, a strategy was developed to manually scram the reactor if leakage increased to 4 gallons per minute (gpm). With leakage continuing to rise above TS 3.4.5 limits, the applicable limiting conditions for operation (LCOs) were entered. At 2046 hours, with reactor core thermal power at approximately 60 percent, a manual reactor scram was initiated after the leak rate exceeded 4 gpm. The cause of the drywell leakage was determined to be failed packing in a gate valve in the reactor coolant (recirculation) system (RCS). The primary purpose of this valve is to isolate the RCS pump for maintenance. The immediate corrective actions included repacking the valve to stop the leakage and retorquing the remaining similar valves in the RCS to protect against leakage. Plant restart and reactor criticality occurred on December 17, 2001. The primary cause of the packing failure was that management direction was inadequate to ensure a sufficient commitment to implementation of the valve packing program. Consequently, the knowledge level of personnel implementing the program was deficient. A contributing cause was inadequate management follow-up of equipment deficiencies, in that, the need for timely repair was not identified. Opportunities to repair the valve were therefore not utilized. Corrective actions include clarifying ownership of the valve packing program, developing a site valve packing procedure, and reviewing previous valve repacking activities to identify and correct instances that are unacceptable.
4122001001 | Beaver Valley 2 | 03/17/2001 | 05/09/2001 | ML01135015 | <strong>Automatic Reactor Trip Due to Loss of Condensate Pump</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2001, at approximately 2113, Beaver Valley Power Station Unit No. 2 received alarms for steam flow/feedwater flow mismatch and 4160 volt motor overcurrent alarms. It was recognized that steam generator water levels were decreasing, a condensate pump had tripped, and a main feedwater pump had tripped. Implementing Abnormal Operating Procedure 2.24.1, Loss of Feedwater, the Nuclear Shift Supervisor ordered a manual reactor trip. However, while this action was being conducted, an automatic reactor trip properly initiated in response to a low-low steam generator water level in the "B" steam generator. All control rods fully inserted into the reactor core and all required safety systems operated as designed. Emergency Operating Procedure E-0 for Reactor Trip was performed and the plant was stabilized in Mode 3. The automatic initiation of a reactor trip by the Reactor Protection System is reportable pursuant to 10 CFR 50.72 (b) (2)(iv)(B) and 10 CFR 50.73 (a) (2) (iv) (A) . The cause of the automatic trip was the tripping of the "A" Condensate Pump, 2CNM-P21A, due to electrical joint failure of its "C" phase power lead. This failure was attributed to a deficient joint configuration whereby a combination of long term heating, accelerated oxidation, and marginal sizing of the motor cable and terminal lugs resulted in an ultimate catastrophic failure of the joint. The safety significance for this event was small.
4122001002 | Beaver Valley 2 | 10/05/2001 | 12/04/2001 | ML01344019 | <strong>Trip of One Service Water Pump Caused Automatic Actuation of Emergency Service Water System</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2001 at 0026 hours, Beaver Valley Power Station (BVPS) Unit No. 2 experienced a trip of the "C" Service Water Pump (2SWS-P21C) which was operating on the "A" Service Water System (SWS) header. The "A" Service Water Pump (2SWS-P21A) was unavailable due to cleaning of the pump's intake bay. The "A" and "B" Standby Service Water System (SSWS) Pumps (2SWE-P21A and 2SWE-P21B) automatically started on low Service Water header pressure on each of their respective trains. The "B" Service Water Pump (2SWS-P21B) continued to operate normally during this event. An investigation revealed the motor circuit breaker for 2SWS-P21C opened on ground over current as a result of a winding failure in the motor for 2SWS-P21C, which was caused by an insulation breakdown. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the automatic actuation of an Emergency Service Water system that does not normally run and that serves as ultimate heat sink. The SSWS operated as designed in response to the loss of a running SWS pump. This event is considered to be of Low Safety Significance.
4122001003 | Beaver Valley 2 | 11/20/2001 | 01/16/2002 | ML02018042 | <strong>Condition Inadvertently Exceeds Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>At 1049 hours on November 20, 2001, a Relay Crew at Beaver Valley Power Station Unit No. 2 began a routine performance of a maintenance surveillance procedure (MSP) to functionally test a 4 KV Underfrequency Relay used in the Reactor Protection System. Unexpected indications during the setup of the test caused the surveillance to be terminated and the system was restored to normal status. The unexpected indications were attributed to plant computer problems. The MSP was again attempted later in the day with the same unexpected indications causing the termination of the test and the restoration of the system. Subsequent evaluation of the unexpected indications the following day (November 21, 2001) by knowledgeable Instrumentation and Control personnel determined that an interposing relay was failed between the Underfrequency Relay being tested by the MSP and the solid state circuitry. The Underfrequency Relay channel of the Reactor Protections System was immediately declared inoperable and Technical Specification 3.3.1.1, Item 17, Action Statement 7 was entered. The interposing relay was replaced and the Underfrequency Relay channel was returned to service within the 6 hours allowed by the Technical Specification Action Statement. Subsequent evaluation of the condition determined that the unexpected indications received during the test setups on November 20, 2001 were firm evidence that the interposing relay was inoperable at that time and the subject Underfrequency channel of the Reactor Protection System was not put into a trip condition or returned to an operable status within the following 6 hours as required by Technical Specification 3.3.1.1, Item 17, Action Statement 7. This was a condition prohibited by the plant's Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). This event was caused by a human performance error of Operations and Relay Crew personnel not recognizing the importance of the unexpected status light indications which were signaling a failed solid state input. This lack of recognition resulted in a delay in declaring the channel inoperable. This event was also caused by an interposing relay failing in an unexpected manner which caused its failure to be non-detectable. The safety significance of this event was small.
4132001001 | Catawba 1 | 01/17/2001 | 02/16/2001 | ML01052038 | <strong>Reactor Trip Caused by a Turbine Trip Due to Incomplete Troubleshooting Analysis</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2001 at 1618 hours with Catawba Unit 1 operating in Mode 1 at 99.8% power, a reactor trip caused by a turbine trip occurred. The Mechanical Trip Solenoid Valve (MTSV) in the Main Turbine Protection System had been replaced in late November 2000 during refueling outage 1EOC12. Since that time a mechanical "Sequence Halt" was experienced when Turbine Trip Testing was performed. Troubleshooting focused on the limit switch associated with the Mechanical Trip Piston and failed to note that the Mechanical Trip Piston was not fully reset. Replacement of the limit switch required adjustment of the limit switch to the Mechanical Trip Piston. This adjustment produced a false reset signal for the test circuitry while the mechanical trip assembly was not fully reset thus causing a Turbine trip. A root cause investigation determined that the root cause of the event was incomplete troubleshooting analysis. The MTSV was replaced. A planned corrective action is for Engineering to develop "at power" troubleshooting guidelines for components of the Main Turbine Controls and the Main Feedwater Pump Turbine Controls.
4132001002 | Catawba 1 | 05/03/2001 | 06/28/2001 | ML01052038 | <strong>Both Units were in a condition prohibited by Technical Specifications due to both trains of Control Room Area Chilled Water System inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2001, at 0101 hours, both trains of Control Room Area Chilled Water System (CRACWS) were inoperable when A-train CRACWS was out of service for planned maintenance and testing and B-train CRACWS automatically tripped. With both trains of CRACWS inoperable, Technical Specification (TS) 3.0.3 applies. Technical Specification 3.0.3 states that action shall be initiated within 1 hour to place the unit in MODE 3 within 7 hours. Contrary to TS 3.0.3, a dual unit shutdown was not initiated within 1 hour because A-train of CRACWS was incorrectly declared operable 54 minutes after the event initiation. The B-train of CRACWS was restored to operable status after 6 hours and 50 minutes. The root cause of the incorrect declaration of CRACWS operability was the over reliance on one supporting piece of information.
4132001003 | Catawba 1, Catawba 2 | 10/11/2001 | 12/10/2001 | ML02031045 | <strong>Control Room Ventilation System Inoperability Due to Accuracy of Flow Measurements Resulting in Non-Compliance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2001, Engineering review of recent past performance tests for the control room area ventilation system (CRAVS) determined that on at least two separate occasions A train of CRAVS did not meet the Technical Specification (TS) requirement for system flow. The tests were conducted on 2/25/00 and 4/13/00. This is not in compliance with TS requirements and resulted in A train of CRAVS being inoperable longer than allowed by TS. During the time frame that A train of CRAVS was not in compliance with TS, B train of CRAVS was taken out of service on 33 separate occasions. This resulted in both trains of CRAVS being inoperable at the same time which is also not in compliance with TS. The most probable cause was that during the startup testing of the system the results from the air flow monitor devices (AFMDs) for both trains were not validated to ensure the accuracy of the installed flow instrumentation. Pitot traverse ports were installed in the CRAVS to ensure accurate airflow readings and the CRAVS was tested, balanced and declared operable. The airflow values reviewed did not adversely affect the dose analysis for the control room, the CRAVS filter efficiencies, or the ability to pressurize the control room.
4142001001 | Catawba 2 | 09/14/2001 | 11/08/2001 | ML02058063 | <strong>Main Feedwater Isolation Valve 2CF60 Failed to Close</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2001, during the shutdown for the refueling outage, the main feedwater isolation valve 2CF60 failed to close from the control room. Technicians locally closed the valve in accordance with Technical Specification 3.6.3 and 3.7.3. Prior to September 14, 2CF60 was considered operable and within its surveillance testing frequency. The valve 2CF60 failure was due to the hydraulic solenoid valves being stuck in their energized position. The solenoid valves failure was due to hydraulic fluid unintentionally entering the coil section of the solenoids forming a sticky adhesive bond between the coil rod and coil housing. The solenoid valves were replaced and valve 2CF60 is operable. The exact time of the valve 2CF60 failure could not be determined but an evaluation concluded that the condition most likely existed longer than the 72 hours allowed by the Limiting Condition for Operation of Technical Specifications 3.6.3 and 3.7.3. This event is being reported as a condition prohibited by Technical Specifications 10CFR50.73(a)(2)(i)(B).
4142001002 | Catawba 2 | 09/19/2001 | 11/12/2001 | ML01191016 | <strong>Reactor Coolant System Pressure Boundary Leakage Due to Small Cracks Found in Steam Generator Channel Head Bowl Drain Line on 2B Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2001, with Catawba Unit 2 in MODE 5 preparing to enter a refueling outage, a walk down of steam generator (SG) 2B lower head bowl drain indicated boron residue buildup on the half inch piping immediately below the SG. The origin of the residue appeared to be adjacent to the bowl drain nozzle at the partial penetration weld between the nozzle coupling and the outer channel head surface. The pressure boundary leakage path was suspected to be the nozzle coupling to vessel weld. This event was reported to the NRC at 2212 on September 19, 2001 as an eighthour non-emergency phone call pursuant to 10 CFR 50.72 (b) (3)(ii)(A). The root cause of the SG 2B bowl drain leak is primary water stress corrosion cracking (PWSCC) of Alloy 600 material. The 2B SG bowl drain leak was repaired and tested satisfactorily. The remaining three SGs on Unit 2 were visually inspected and liquid penetrant tests were performed. No similar leaks were detected. Long term corrective actions include evaluating SG drain line enhancements to preclude leakage and development of a program to address Alloy 600 issues. This issue is not applicable to Unit 1 because the SGs are of a different design that does not have a similar drain line.
4142001003 | Catawba 2 | 12/07/2001 | 02/04/2002 | ML02065027 | <strong>Electrical Fault in Reactor Coolant Pump Motor Stator Causes Automatic Reactor Trip, Autostart of Emergency Diesel Generator, and Autostart of Auxiliary Feedwater</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2001 at 2350 hours with Catawba Unit 2 operating in Mode 1 "Power Operation" at 100% power, an automatic reactor trip occurred. The reactor trip was caused by low flow in the D loop when the 2D reactor coolant pump (RCP) 6900VAC feeder breaker opened in response to protective relay actuation caused by an electrical fault internal to the RCP motor. The electrical fault in the RCP motor also caused protective relaying to open the normal feeder breaker supplying power to the essential bus 2ETB, creating an undervoltage condition on 2ETB. The associated emergency diesel generator (EDG) automatically started and powered the bus and required equipment as designed. The 2B motor-driven and the turbine driven auxiliary feedwater pumps automatically started in response to the 2ETB blackout as designed. The 2A motor-driven auxiliary feedwater pump automatically started in response to lo lo water level in the 2D steam generator (S/G). All systems responded as designed to shut down the reactor and maintain it in a safe shutdown condition. Corrective actions included replacing the failed 2D RCP motor and verification of proper operation of the protective relaying associated with the breakers that opened. The RCP motor failure was determined to be a "turn-to-turn" failure of a single coil. The damaged coil is on the line end of the stator core and appears to be the first coil in the Z-phase (T3) coil group. A possible cause of the coil failure is a manufacturing defect of the magnet wire.
4162001001 | Grand Gulf 1 | 02/21/2001 | 04/16/2001 | ML01114021 | <strong>Tech Spec LCO Time Exceeded Due to Two Sequential Equipment Failures</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2001, a 24-hour load surveillance was being performed on the Division I Emergency Diesel Generator (EDG 11) when a water leak in the engine’s left turbocharger return jacket water pipe was discovered. EDG 11 was declared inoperable while the leak was repaired. According to Technical Specification (TS) 3.8.1 ACTION B.4, the time allowed for continued operation would have ended on February 22 at 0100 (72 hours later). Following the pipe repair, the surveillance was recommenced. However, a fuel oil leak occurred which required another shutdown of EDG 11. Since there was insufficient time to restore EDG 11 to operable status per the TS LCO, a Notice of Enforcement Discretion (NOED) to extend the LCO from 72 to 108 hours was requested and approved by the NRC. The 24-hour surveillance was commenced at 1542 on February 21 and EDG 11 returned to operable status at 1606 on February 22. Successful completion of the surveillance indicates EDG 11 was functional prior to entering the NOED. The event was caused by two sequential and unrelated equipment failures: return jacket water pipe crack caused by low stress high cycle fatigue induced by misalignment during maintenance and a fuel oil leak caused by a loose air bleed screw that subsequently backed out which has been determined to be an isolated, random event on a recently installed vendor-supplied injector pump.
4162001002 | Grand Gulf 1 | 04/06/2001 | 06/04/2001 | ML01158025 | <strong>Containment Air Lock Leakage in Excess of Technical Specification Allowable Rate</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2001, a pressure decay surveillance on the outer containment air lock on the 119 Foot Elevation indicated that seal air system leakage exceeded the technical specification (TS) limit of greater than 2 pounds per square inch gauge (PSIG) for a period of 48 hours. The excess leakage was attributed to a clevis valve failure and a regulator valve leaking through. These components were reworked and the door was restored to OPERABILITY on April 5, 2001. On April 6, 2001, a pressure decay surveillance on the containment inner air lock on the 119 Foot Elevation indicated that the seal air system leakage rate exceeded the same TS limit. The excess leakage was attributed to a clevis valve failure and a minor pressure leak on a switch fitting. These components were reworked and the door was restored to OPERABILITY on April 7, 2001. Engineering evaluation of test results indicated that the condition would not have prevented the fullfillment of the containment safety function. Therefore, this condition did not constitute a safety system functional failure. Engineering evaluation indicated that the containment inner air lock would have failed the surveillance if only the clevis valve had failed. Thus, GGNS is reporting the April 6, 2001, occurrence under 10CFR50.73(a)(2)(vii) for a single cause or condition causing two independent trains to become inoperable in a single system.
4162001003 | Grand Gulf 1 | 08/07/2001 | 10/04/2001 | ML01282010 | <strong>Automatic Reactor Scram Due to Offsite 500 KV Switchyard Problem and EOC-RPT Failure</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2001 at approximately 2017 hours, while operating at steady state conditions, a reactor scram occurred. The scram was the result of a reactor protection system actuation from a Turbine Control Valve fast closure signal. This signal was the result of a generator load transient caused by failure of a 500 kV disconnect. The disconnect that failed is located in an offsite switchyard which directly feeds the GGNS switchyard. A generator load reject was sensed due to the grid transient, causing generator load demand and valve rate limiters to automatically switch off. A turbine control valve fast closure response was sensed as Turbine Control Valves moved in the closed direction. The reactor scrammed but the End of Cycle Recirculation Pump Trip did not occur, as expected. This event is bounded by the current analyses, as discussed in the safety assessment, Section G. No major equipment was out of service at the time of this occurrence. The Reactor Core Isolation Cooling system was inoperable due to the performance of corrective maintenance, however the maintenance had been completed and the system was functional at the time of the scram. All control rods inserted and all other equipment responded as expected. The Condensate/Feedwater System was lost shortly after the scram occurred due to hotwell level problems. The Reactor Core Isolation Cooling system was manually initiated and used for reactor water level control.
4162001004 | Grand Gulf 1 | 12/04/2001 | 12/20/2001 | ML01355029 | <strong>Violation of Operating License Condition 2.C (1) Maximum Power Level</strong><br /><i>Abstract:&nbsp;</i>General Electric (GE) recently provided information related to methodology used to calculate core thermal power (CTP). On October 3, 2001, GGNS performed an evaluation which identified the potential for an error related to moisture carryover. GGNS had applied the generic moisture carryover assumption provided by GE and currently uses 0.1 percent for the moisture carryover fraction in the CTP. GE now recommends a value of 0.0 percent be used. Changing the fraction to 0.0 percent results in an increased calculated CTP of 0.082 percent (3.1MWt). Further evaluation by GE revealed that an older version of steam table data was used to calculate the saturated steam enthalpy. As a result, GGNS unknowingly operated at a core power level slightly in excess of the CTP limit (3833 megawatts thermal). Such operation was in violation of Operating License (OL) Condition 2.C (1) and is being reported pursuant to OL Condition 2.F. Immediate actions were to administratively limit reactor CTP to account for the error in the calculated CTP. Programs/procedures were revised to assume a 0.0 percent moisture carryover value in the plant calorimetric heat balance. The GE report stated the error in CTP, although non-conservative, does not represent a safety issue. Therefore, this condition was of minimal safety consequence and the health and safety of the general public were not compromised.
4232001001 | Millstone 3 | 02/01/2001 | 03/30/2001 | ML01100029 | <strong>Quench Spray System Manual Valve Misalignment</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2001, with the unit in Mode 1 at approximately 78% power, an operability test of the A Train Quench Spray System (QSS) pump, 3QSS*P3A, was performed. During test performance, personnel detected an abnormal noise near manual valve 3QSS*V945. The source of the abnormal noise could not readily be determined. On February 2, 2001, radiography was performed on 3QSS*V945 to aid in locating the source of the abnormal noise. 3QSS*V945, designated by plant configuration as a locked open valve in the discharge piping of 3QSS*P3A, was discovered to be locked closed. This condition was not previously detected because an unrestricted bypass line around 3QSS*V945 had allowed sufficient flow for 3QSS*P3A to successfully pass the current, as well as all previous operability tests. A subsequent review to determine the extent of condition revealed that the B Train QSS manual valve, 3QSS*V946, was also locked closed contrary to the established plant configuration designation as a locked open valve. 3QSS*V945 and 3QSS*V946 were opened to restore the QSS to the proper configuration. This issue is reportable under both 10 CR 50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications, and 10 CFR 50.73(a)(2)(vii), for common-cause inoperability of independent trains. The cause of this event, 3QSS*V945 and 3QSS*V946 in the closed position, was determined to be due to deficiencies in the initial plant startup program. Since this event did not result in a loss of any QSS safety function, and did not adversely impact accident dose consequences, it is of low safety significance.
4232001002 | Millstone 3, Millstone 2 | 05/09/1999 | 06/18/2001 | ML01177031 | <strong>Incomplete Post-Maintenance Testing for Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2001, it was determined that incomplete post-maintenance testing had been performed for maintenance activities which occurred on May 5, 1999 for 3CCP*MOV45A, a Millstone Unit No. 3 (MP3) Reactor Plant Component Cooling Water supply header isolation valve. This valve, which also functions as a Containment Isolation Valve (CIV), did not receive a post-maintenance isolation time test as required by MP3 Technical Specification (TS) 4.6.3.1. On February 23, 2001, during the investigation of the extent of condition for the MP3 event, it was determined that a Millstone Unit No. 2 (MP2) CIV also did not receive post-maintenance testing as required by TSs. This CIV, a Steam Generator Blowdown Control Valve (2-MS-220A), also did not receive a post-maintenance isolation time test as required by MP2 TS 4.6.3.1.1.b. after maintenance activities which were completed on July 16, 1999. The cause of this event was an incomplete component database used in identifying post-maintenance testing requirements for CIVs. Corrective actions include: 1) Verification of acceptable Containment Isolation Valve isolation times; 2) Issuance of interim guidance on Technical Specification CIV testing requirements; and 3) Enhancements to the database utilized for work planning to include additional information on CIV TS test requirements.
4232001003 | Millstone 3 | 07/10/2001 | 09/04/2001 | ML01255036 | <strong>Failure of Containment Air Lock Results in Entry Into Tech Spec 3.0.3</strong><br /><i>Abstract:&nbsp;</i>At 1550 on July 10, 2001, with the reactor power at 100 percent, Technical Specification 3.0.3 and 3.6.1.3 action statement a.3 were entered due to both containment personnel air lock doors being considered inoperable. A shutdown was initiated because the overall restoration and retest activity for the air lock was expected to take approximately 3 hours. A 4-hour notification was made to the NRC in accordance with the requirement of 10CFR50.72(b)(2)(i), initiation of a shutdown required by Technical Specifications. The cause of this event is the application of excessive grease to the outer air lock door o-rings and the incomplete implementation of Technical Specification changes in License Amendment 186. Based on the fact that the inner air lock door had been functionally operable during the entry into Technical Specification 3.0.3, there was no loss of safety function. During the brief period of time when the possibility existed that both doors might have been inoperable, i.e., approximately half an hour, the inner door could have been reclosed in less than a minute. Therefore, this event is of low safety significance. The immediate corrective actions taken were to restore operability of the air lock outer door by performing the appropriate repairs and satisfying a full volume leak rate test. Corrective actions to prevent recurrence include revising the maintenance procedure to provide a caution on the use of too much grease on the o-rings and providing a technical briefing sheet to Operations identifying the changes in Appendix J testing methods and frequencies implemented by License Amendment 186.
4232001004 | Millstone 3 | 08/23/2001 | 10/11/2001 | ML01295036 | <strong>Failure of Neutron Flux Accident Monitoring Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2001, with reactor power at 100 percent, Technical Specification 3.3.3.6 Action Statement a. was entered due to the Channel 1 Gamma Metrics Neutron Flux Monitor exhibiting erratic indication. The Channel 1 Gamma Metrics Neutron Flux Monitor was restored to operable status on August 24, 2001. Subsequent investigation identified that the Channel 1 Gamma Metrics Neutron Flux monitor began exhibiting the erratic behavior as early as August 12, 2001. As a result, the Channel 1 Gamma Metrics Neutron Flux Monitor was inoperable for more than 12 days. This exceeded the 7 day allowed outage time. This issue is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications. The cause of the erratic indication was a loose wiring lug fastener on the output of the isolator in the signal processor. The root cause for this event was identified as a Man-Machine Interface issue in that no alarm warning is available to the plant operators to immediately identify potential equipment problems. Daily monitoring of the Gamma Metrics Neutron Flux Monitoring Channels was established to ensure equipment operability. During the time period that the Channel 1 Gamma Metrics Neutron Flux Monitor was inoperable, the redundant channel and additional backup indications were available to monitor neutron flux level. Sufficient indications would have been available for use by the plant operators to ensure the reactor remained subcritical following a design basis event. This event did not result in the loss of any safety function, and is of low safety significance.
4242001001 | Vogtle 1 | 08/24/2001 | 03/28/2002 | ML02093016 | <strong>Reactor Trip Due to Loss of Generator Excitation</strong><br /><i>Abstract:&nbsp;</i>On August 24, 2001, with the unit at 100% power, personnel were returning to service the Main Generator Rectifier Bridge 1 after performing corrective maintenance. Upon closure of the disconnect switch, a trip of the main generator occurred on loss of field excitation, causing an automatic turbine/reactor trip at 2307 EDT. All control rods were observed to fully insert, and control room operators acted properly to control steam generator water levels and stabilize the unit in mode 3 (hot standby). An investigation found that, upon returning Rectifier Bridge 1 to service, silicon controlled rectifiers (SCRs) in Rectifier Bridge 4 failed due to a short circuit. This led directly to the loss of the generator excitation field and the generator/turbine/reactor trip. The malfunctioning rectifier bridges were repaired and the unit was returned to service. The failed SCRs that were removed from the rectifier bridges were sent to a laboratory for failure analysis. The analysis was unable to determine the root cause of the failure.
4252001001 | Vogtle 2 | 04/07/2001 | 05/29/2001 | ML01155028 | <strong>Reactor Trip While Testing Main Feedwater Pump Trip Signals</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2001, Unit 2 was reducing power, preparing to enter a refueling outage. While steam generator (SG) feedwater pump A was out of service, personnel were testing the SG feedwater pump turbine (SGFPT) A trip signal. However, upon simulating a SG high water level signal, a trip of SGFPT B occurred. This resulted in both SGFPTs being out of service. Therefore, control room operators performed a manual reactor trip at 2123 EDT. A normal trip sequence ensued and plant operators transitioned the unit to stable operation in Mode 3 (hot standby). An investigation of this event found that, prior to the SGFPT B trip, I&C technicians had opened a sliding link to disable the feed pump trip signal. A review determined that the sliding link had not been fully opened, thereby leading to the SGFPT B trip when a simulated high water level signal was processed. The root cause of the event was the man-machine interface that prohibited the technicians from visually determining the link position. The link position could only be determined by feel using a nut driver. Corrective actions include performing an engineering review to determine if the link should be moved to a more accessible location in the cabinet. Additionally, until completion of this review, this surveillance will only be performed when the SGFPTs are out of service.
4402001001 | Perry | 04/29/2001 | 06/14/2001 | ML01170044 | <strong>Manual SCRAM Due to Decreasing Main Condenser Vacuum and Invalid Division 2 and 3 ECCS Actuations</strong><br /><i>Abstract:&nbsp;</i>On 4/28/01 at 2101 hours, a main generator field ground annunciator was received due to a Stator Water System leak and actions were taken to remove the main generator from service at 2323 hours. Following generator removal/turbine trip, the main condenser vacuum degraded and was determined non-recoverable. A manual reactor scram was inserted by procedure at 0050 hours, on 4/29/01. Following insertion of the reactor scram, as a result of one turbine steam bypass valve, which stuck one half open for four minutes, invalid Division 2 Emergency Closed Cooling System (ECCS) actuation signals were received on a combination of low sensed level and high pressure signals. Then shortly after MSIV closure at 0249 hours, during the first of a series of manual SRV operations for controlling pressure, an invalid Division 3 ECCS actuation signal was received. Though the signals were invalid, all systems responded as designed to their logic actuation. Also in response to the Division 3 actuation signal, the High Pressure Core Spray System pump was over-ridden off in accordance with plant procedures. Subsequently, the A and B loops of Residual Heat Removal were required by procedure to be placed in suppression pool cooling mode of operation as a result of SRV operations. This resulted in entry into Technical Specification 3.0.3, "Limiting Condition for Operation Applicability." The cause of the loss of vacuum was a process error that resulted in two moisture separator drain tank manways being improperly torqued during the recent refueling outage and becoming unseated when the pressure was reduced in the tank following the turbine removal from service. The cause of the reactor level/pressure actuations was determined to be localized flashing and pressurization of the sensing lines in the affected instrument reference legs. The stator water cooling lines were repaired. The affected manways were re-worked, gaskets repaired and the remaining manways were properly retorqued; RPV level instrument reference legs were filled and vented, and operators were provided with awareness briefings and lessons learned from the event. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv), as a condition that resulted in multiple specified system actuations, and 10CFR50.73(a)(2)(i)(B), as a condition prohibited by the plant's Technical Specifications.
4402001002 | Perry | 06/27/2001 | 08/21/2001 | ML01240009 | <strong>Oscillation Power Range Monitors Inoperable Due to Non-Conservative Setpoints</strong><br /><i>Abstract:&nbsp;</i>The Perry Nuclear Power Plant staff was notified by General Electric (GE) via a Boiling Water Reactor Owners Group (BWROG) conference call on June 27, 2001, at approximately 1130 that the Oscillation Power Range Monitor (OPRM) instrumentation SCRAM setpoints are non-conservative due to non-conservative analysis. The OPRM instrumentation is an input to the Reactor Protection System. The OPRM instrumentation provides a safe shutdown safety function when operating during an unstable power to flow condition. The OPRM equipment was therefore considered inoperable since first placed into service following the scheduled refueling outage in March 2001. The plant is currently operating within its Technical Specifications 3.3.1.3 Required Action using an off-normal instruction as an alternate method to monitor and suppress thermal hydraulic instability oscillations. GE has issued a 10 CFR Part 21 Interim Report and Transfer of Information to formally notify licensees with an evaluation pending. GE will also provide a 10 CFR 21 Report to be submitted to the NRC, as well as re-analysis to provide new setpoints through BWROG involvement. This event was reported to the NRC (ENF # 38099) in accordance with 10 CFR 50.72(b)(3)(v)(A), as a condition that at the time of discovery could have prevented the fulfillment of the safety function of a system needed to shut down the reactor and maintain it in a safe shutdown condition. This report is submitted in accordance with 10 CFR 50.73 (a)(2)(v)(A) as a loss of safety function, since the trip function was effectively inoperable. It is also being reported as an event in which a single cause or condition caused two independent trains or channels to become inoperable in a single system designed to shut down the reactor and maintain it in a safe shutdown condition (10 CFR50.73 (a)(2)(vii)).
4402001003 | Perry | 07/11/2001 | 08/20/2001 | ML01236032 | <strong>Loss of Feedwater Scram and Specified System Actuations including ECCS injection</strong><br /><i>Abstract:&nbsp;</i>On 7/11/01, at 2223 hours, the plant was operating at 100 percent reactor power when a loss of feedwater occurred resulting in an automatic reactor scram, an automatic trip of the Reactor Recirculation Pumps, an automatic initiation and injection of the High Pressure Core Spray System (HPCS) and the Reactor Core Isolation Cooling System (RCIC) and a Balance of Plant Isolation due to a valid Reactor Pressure Vessel (RPV) water low level signal. Subsequently, at 0400 on 7/12/01, an invalid low RPV water level signal occurred resulting in an invalid automatic initiation of the HPCS pump, HPCS diesel and associated support systems, however no injection occurred. All systems responses were as expected to the valid and to the invalid signals. The cause of the loss of feedwater event was determined to be a blown fuse that supplies 24-Volt DC electrical power to the Loop B Analog Instrument Panel, which contains instrumentation for the feedwater control system. The cause of the invalid RPV low level actuation was determined to be due to a thermal hydraulic perturbation coincident with decreasing reactor pressure. The power supply fuse was replaced and a thermographic examination was performed of all fuses located in the Control Room. A thermographic examination of the Control Room fuses was again performed following plant restoration at approximately 60 percent power. Although no additional failures were identified, fuses indicating above normal temperatures were replaced. To address the invalid HPCS initiation, the signal dampening for the HPCS RPV level instruments was increased in order to reduce the instrument vulnerability to short duration pulses. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv), an event or condition that resulted in specified system actuations.
4402001004 | Perry | 10/01/2001 | 10/30/2001 | ML02018029 | <strong>Licensed Power Limit Exceeded Due to a Non-Conservative Moisture Carryover Fraction</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2001, it was determined that a non-conservative assumption for the steam carryover fraction of main steam has been applied in the General Electric methodology for calculating reactor core thermal power at the Perry Nuclear Power Plant (PNPP). This was documented in a General Electric Report entitled, "Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations, September 2001." This report states that the assumed carryover fraction in later model Boiling Water Reactors is non-conservative with respect to heat balance calculations. The potential effect of this non-conservative assumption is that the calculated core thermal power could be as much as approximately 0.082% lower than the actual core thermal power. Consequently, it is assumed that the plant has operated at reactor core power levels in excess of the licensed power level by approximately 0.082%, or approximately 3 megawatts thermal (MWth). Due to the small magnitude of the carryover fraction input and the conservatism present in the core thermal power levels used for the safety analyses, the use of the non-conservative steam carryover fraction does not represent a safety issue. As a measure of conservatism, however, an administrative reactor power reduction of 4 MWth was implemented until the process computer thermal power calculation was modified to reflect the revised moisture carryover fraction. This issue was reported to the NRC Operations Center via the Emergency Notification System at 1914 on October 1, 2001 (Notification number 38337). This written report is being submitted in accordance with PNPP Operating License Condition 2.F., as a potential violation of the Maximum Power Level specified in PNPP Operating License Condition 2.C.1.
4402001005 | Perry | 12/15/2001 | 02/13/2002 | ML02107043 | <strong>Automatic RPV Level Scram, Specified System Actuations and Inoperability of the Division 3 Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On December 15, 2001, at 2228 hours, with the plant operating at 100 percent reactor power, an excessive feedwater demand transient occurred resulting in a high Reactor Pressure Vessel (RPV) water level scram. Following the feedwater pump trip on high RPV level, RPV level decreased causing actuation of High Pressure Core Spray System (HPCS), Reactor Core Isolation Cooling System and containment isolation as designed. A Reactor Protection System (RPS) actuation occurred on low RPV water level at 2304 hours when level inadvertently drifted low. Additionally, the HPCS diesel governor was misadjusted during diesel shutdown resulting in inoperability that was later identified during the review of normal surveillance testing results on December 21, 2001. The cause of the feedwater transient was determined to be a failed logic card that has since been replaced. The cause of the RPS actuation and the failure to meet Technical Specifications was determined to be operator performance deficiencies. Lessons learned from the event were presented to operators and the HPCS diesel procedure was revised. This event is being reported in accordance with the requirements of 10CFR50.73(a)(2)(iv), an event or condition that resulted in specified system actuations, 10CFR50.73(a)(2)(i)(B), a condition prohibited by Technical Specifications, and also satisfies Perry Plant's Operational Requirements Manual (ORM) section 7.6.2.1, special report for an Emergency Closed Cooling System (ECCS) injection into the RPV. This was the fourteenth HPCS injection to date. The injection nozzle usage factor is less than 0.70, therefore no further data is required by the ORM.
4432001001 | Seabrook | 02/01/2001 | 03/29/2001 | ML01094003 | <strong>Non-Compliance with Technical Specifications Due to Installation of Unqualified Test Equipment</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2001, with the plant operating at 100% power, two non-safety related chart recorders were discovered installed and connected across the coils of solenoid valves which provide the safety-related functions for opening and closing the "D" main steam [SB] line atmospheric steam dump valve (1 MS-PV3004). The subject recorders were not qualified for use in safety-related applications and no qualified isolation devices were used to provide the necessary separation from the safety-related equipment. The installation of the subject recorders caused 1 MS-PV3004 to be inoperable. The subject recorders were subsequently removed. 1 MS-PV3004 was required to be operable by Technical Specifications (TS) 3.6.3 and 3.7.1.6 during operational modes 1, 2, 3, and 4. Seabrook Station entered Mode 4 on January 24, 2001. Additionally, TS 3.0.4 requires that entry into an operational mode or another specified condition shall not be made when the conditions for the limiting conditions for operation are not met and the associated action requires a shutdown if they are not met within a specified time interval. Since these requirements were not met, this is a condition prohibited by the Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The cause of this event is human error. There were no adverse consequences as a result of this event. During the period that the subject recorders were installed, 1MS-PV3004 was capable of operation. Corrective action has been initiated to prevent recurrence. This is the first event of this type reported by Seabrook Station.
4432001002 | Seabrook | 03/05/2001 | 05/04/2001 | ML01131049 | <strong>Reactor Trip Due to Power Arc Flashover Across the "B" Phase 345 kV Transmission Line Bushings</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2001 at 2324, with the plant at 100% power, Seabrook Station experienced a plant trip during a severe winter storm. Prior to this event, the plant was experiencing difficulty with the off site power supplies to the plant. At 2238 on March 5, 2001, the 345 kV breakers for the Scobie line opened disabling one of the three off-site supplies. At 2248 on March 5, 2001, the 345 kV breakers for the Newington line opened disabling the second of three off-site lines. At 2324 on March 5, 2001, off-site 345 kV electrical supply via the Newington line was restored. However, the breaker alignment prevented this line from powering station buses. Shortly thereafter, the Tewksbury line tripped. Almost immediately after the trip of the Tewksbury line, a reactor trip occurred. An unusual event was declared on March 5, 2001 at 2336 since the supply of off site power was not considered reliable due to the adverse weather conditions. The unusual event was terminated on March 7, 2001 at 1046 when offsite power was restored to emergency Bus 5. The State of New Hampshire, the Commonwealth of Massachusetts and the Nuclear Regulatory Commission were notified of the event. The cause of the event is power arc flashover from the line to ground across the "B" phase 345kV bushings that connect the sulphur hexafluoride (SF6) gas insulated 345 kV bus sections to the 345 kV overhead lines. The power arc flashover was due to the severe weather conditions and subsequent buildup of snow on the "B" phase bushings, which exceeded their capability. The consequences of this event were minimal. However, certain components did not operate as expected. Corrective actions have been identified to prevent recurrence.
4432001003 | Seabrook | 10/15/2001 | 12/14/2001 | ML02016003 | <strong>Reactor Trip Due to a Dropped Rod</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2001 at 1:07 PM, with the plant at 100% power, North Atlantic Energy Service Corporation (North Atlantic) experienced an automatic reactor trip. The reactor trip occurred when rod N11 dropped into the reactor core and a power range high flux rate trip (negative) signal was initiated. At the time of the rod drop event, rod N11 was being moved out from step 229 to step 231 during the performance of a quarterly rod operability check. The plant systems functioned properly during the initial reactor trip and subsequent transition to Mode 3, with two minor system issues that were not the result of the event. Operator response to the automatic trip was appropriate with no human performance issues identified. The rod drop occurred while moving rod N11 out at step 230 when the stationary gripper did not fully engage prior to the movable gripper releasing. The root cause of the N11 Dropped Rod Event is particulate deposits in the rod drive housing and/or on the drive rod. These deposits inhibited the stationary gripper engagement on the drive rod. A four hour and eight hour notification to the Nuclear Regulatory Commission (NRC) was made pursuant to the requirements of 10CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A). The event notification was 38390. A change to Control Rod Drop Testing procedure will be made to obtain acceptable coil current traces for all control rods during the performance of rod drop testing that is preformed at the end of the refueling outage. This License Event Report is being submitted pursuant to the requirements of 10CFR 50.73(a)(2)(iv)(A).
4432001004 | Seabrook | 10/16/2001 | 12/07/2001 | ML02015020 | <strong>Non-Compliance with the Technical Specifications Due to MSIV Stroke Time Calculation Human Error</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2001 at 1100, with the plant operating in Mode 3 (Hot Standby) at 0 percent power, Operations Department personnel were notified that an error was discovered in a calculation used to determine the full-stroke closure time of the "C" Main Steam [SB] Isolation Valve (MSIV) (1-MS-V90). At 1226 on October 16, 2001, 1-MS-V90 was full-stroke exercised to the closed position as part of a surveillance test of the MSIVs to satisfy the requirements of Technical Specifications (TS) 4.0.5 (Inservice Test Program), 4.6.3.3 (Containment Isolation Valves), and 4.7.1.5 (Main Steam Isolation Valves). The closure time for 1-MS-V90 was calculated and recorded as 4.09 seconds when closed utilizing a Train "A" Main Steam Isolation signal. The Repetitive Task Sheet (RTS) used to record the test data was completed by the Control Room Operator (CRO) and subsequently forwarded to the Unit Supervisor (US) for review and approval. The US reviewed the test data to ensure that the surveillance procedure acceptance criteria was met and approved the RTS at 1559 on October 16, 2001. However, there was no independent review of the calculations performed by the CRO. A subsequent review by an Inservice Test (IST) program engineer on October 19, 2001 determined that "A" train stroke time of 1-MS-V90 had been erroneously calculated. The stroke closure time for 1-MS-V90 was determined to be 5.09 seconds instead of 4.09 seconds, which exceeded the Technical Specification limit of 5.0 seconds. Since this condition existed for a period longer than permitted by the TS action statements, this condition is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications. The cause of this event is human error. Immediate corrective actions were implemented and other corrective actions to prevent recurrence have been identified.
4452001001 | Comanche Peak 1, Comanche Peak 2 | 01/04/2001 | 01/31/2001 | ML01037027 | <strong>Emergency Diesel Fuel Oil Technical Specification Surveillance Was Not Met</strong><br /><i>Abstract:&nbsp;</i>On January 04, 2001, during a review of an Industry Operating Experience Report (IOER), Chemistry Personnel (Utility, Non-Licensed) discovered that Technical Specification (TS) Surveillance requirements for fuel testing in accordance with Diesel Fuel Oil Testing Program were not met. Comanche Peak Steam Electric Station (CPSES) TS 3.8.3.3 and 5.5.13 test the fuel by requiring that the new fuel oil has either "a clear and bright appearance with proper color; or water and sediment content within limits." When using the clear and brightness option, TS 3.8.3.3 Bases require verifying the Diesel Fuel Oil has "... proper color when tested in accordance with ASTM D4176-1982." Contrary to the TS and the American Society for Testing and Materials (ASTM) standard, proper color has not been verified or documented during the performance of the clear and bright test for new fuel oil shipments when the clear and brightness option was used. Corrective actions are to revise the applicable procedures to be compatible with the requirements of the Diesel Fuel Oil Testing Program.
4452001002 | Comanche Peak 1, Comanche Peak 2 | 03/07/2001 | 05/07/2001 | ML01135017 | <strong>Primary Plant Ventilation System Negative Pressure Boundary Test Has Been Performed Non-Conservatively With the Ventilation Supply Units' Pneumatic Dampers in the Closed Position</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2001 during a review of the Primary Plant Ventilation System (PPVS) engineering surveillance test procedures, surveillance testing personnel (utility, non-licensed) noted that the PPVS supply fan pneumatic intake dampers were being tested in the "closed" position instead of the "open" position. The dampers are designed to "fail open on loss of instrument air", and have been tested in the closed position since unit start-up. On March 8, 2001, test was conducted with the correct line-up, i.e., dampers in the open position, with acceptable results. The cause of the event was deemed to be less than adequate procedures. Immediate actions were to perform the test with the dampers in the correct position. The applicable procedures will be revised to require the dampers to be in the open position when the test is to be performed.
4452001003 | Comanche Peak 1, Comanche Peak 2 | 03/12/2001 | 05/10/2001 | ML01135019 | <strong>Technical Specification Limiting Conditions for Operation Applicability Not Consistent With Testing Allowed In Turbine Overspeed Protection System Test</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2001, during a review of the turbine overspeed protection system test procedure, a CPSES operator (utility, licensed) noted that the test procedure was in conflict with the Comanche Peak Steam Electric Station (CPSES) Technical Specification. The performance of the test procedure defeats the P-4 (reactor trip) signal. The Technical Specification requires that P-4 be operable in Modes 1, 2, and 3. Operations department reviewed previously performed test documents and verified that the CPSES Technical Specification requirements for the reactor trip P-4 signal being available to initiate a turbine trip was defeated on at least two instances, when the test was performed in Mode 3. The cause of the condition was deemed to be less than adequate test procedures, which was contrary to the Technical Specifications. The applicable procedures have been revised to reflect the Technical Specification requirements.
4452001004 | Comanche Peak 1, Comanche Peak 2 | 04/02/2001 | 04/16/2001 | ML01110023 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2001, with Comanche Peak Steam Electric Station (CPSES) Unit 1 in Mode 6 (Refueling with core offloading), analysis of eddy current plus point testing data on Steam Generators (SG) (EIIS: (AB)(SG)) indicated that greater than 1 percent of the total tubes inspected in SG 1-2, SG 1-3 and SG 1-4 were defective. The majority of the tube defects are attributed to outer diameter stress corrosion cracking at the hot leg top of tubesheet transition. TXU Electric has plugged all defective tubes identified during the current refueling outage. All defective tubes met the criteria of Draft Regulatory Guide 1.121 for structural integrity. TXU Electric maintains a comprehensive program to minimize SG tube degradation. This report also meets the requirements of Special Report as specified in CPSES Technical Specification 5.6.10.a.
4462001001 | Comanche Peak 2, Comanche Peak 1 | 07/18/2001 | 09/17/2001 | ML01261000 | <strong>Reactor Trip Due to Spurious Turbine Trip Signal Originating from AMSAC</strong><br /><i>Abstract:&nbsp;</i>On July 18, 2001, Comanche Peak Steam Electric Station Unit 2 was in Mode 1, Power Operation, operating at 100 percent power. At approximately 7:59 a.m., during performance of a Steam Generator 2-01 Narrow Range Level 519 Channel Operability Test, a test trouble alarm was received on the Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC) panel. During restoration of AMSAC to clear the trouble alarm, a spurious AMSAC signal was generated causing an automatic turbine trip which resulted in an automatic reactor trip from 100 percent power. All control rods fully inserted. Auxiliary Feedwater (AFW) automatically actuated following the reactor trip and the Main Steam Isolation Valves (MSIV's) were manually closed for temperature control. The plant was stabilized in Mode 3 and all systems functioned as designed. TXU Electric believes that the event was caused by a short circuit in a light bulb socket during replacement of an apparently burned out AC power lamp in the AMSAC panel. Corrective actions include replacement of the defective light socket, inspection of other AMSAC light sockets, and modification of the AMSAC power light circuit. All times in this report are approximate and Central Standard Time unless noted otherwise.
4542001001 | Byron 1, Byron 2 | 05/15/2001 | 06/29/2001 | ML01184021 | <strong>Reactor Power Limit Exceeded Due to Improperly Calculated Feedwater Mass Flowrate Utilized in Reactor Power Calorimetric</strong><br /><i>Abstract:&nbsp;</i>During the review of data used to calculate the feedwater (FW) flow calibration constants, two errors were discovered. Specifically, errors were found in the FW density correction and the thermal expansion factor. These errors resulted in a nonconservative calculation of reactor power by 0.12%. Further review determined the errors have been present since May 2000 and the errors were applicable to both Byron Station units. This event was determined to be reportable as violation of an operating license condition based on the average power level over an eight-hour shift exceeding the full steady state licensed power level. An evaluation of the calorimetric instrument uncertainty calculation determined the density correction and thermal expansion coefficient errors did not result in exceeding the 2% Rated Thermal Power (RTP) uncertainty allowance in the safety analysis. Therefore, the assumptions in the safety analysis have remained bounded. The cause of the density correction and thermal expansion coefficient errors was human performance related. A formal engineering calculation process was not utilized due to a lack of clear management expectations and detailed guidance to recognize when a formal calculation is required. Immediately following discovery of the errors, an administrative reactor power limit was established on Unit 1 and a validation of the entire Byron Station process used to calculate the feedwater flow calibration coefficients was performed.
4542001002 | Byron 1, Byron 2 | 09/26/2001 | 11/26/2001 | ML02016015 | <strong>Main Steam Isolation Valves Surveillance Not Performed in Mode 3 as Required by Technical Specification Bases Due to Improper Procedure Revision</strong><br /><i>Abstract:&nbsp;</i>At 1600 hours on September 26, 2001, it was determined that the two Surveillance Requirements (SR) for the Main Steam Isolation Valves (MSIVs) were not tested in Mode 3, as required. The failure to test the valves in Mode 3 resulted in missed Technical Specifications (TS) Surveillance Requirements (SRs) on all 4 MSIVs on each unit, which resulted in both units entering SR 3.0.3. SR 3.0.3 allows up to 24 hours to either perform the missed surveillances or take other remedial measures. In accordance with the TS Bases, these SRs must be performed in Mode 3. Byron Station has been previously testing the MSIVs in Mode 4. The surveillances cannot be performed at power since the SRs require the MSIVs to close. Enforcement Discretion and a subsequent exigent License Amendment Request (LAR) were requested from the NRC to allow continued operations without satisfying the SRs in Mode 3. On September 27, 2001, the NRC granted verbal approval of the Notice of Enforcement Discretion (NOED). The LAR was approved on November 1, 2001. The cause of the missed SR occurred during the Improved Technical Specifications (ITS) implementation project. The procedure revision implementation for the MSIV SRs did not recognize that the more restrictive requirement (i.e., to perform the MSIV SR in Mode 3) was introduced into the TS Bases wording. The root cause of the implementation error was determined to be unknown. Corrective actions include correcting the outage schedule and procedures and reviewing for other potential ITS implementation errors. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(b).
4542001003 | Byron 1 | 09/27/2001 | 01/28/2002 | ML02045041 | <strong>Entry into Technical Specification Limiting Condition for Operation 3.0.3 Due to a Leak on a Safety Injection Valve Weld Caused by a Pre-Existing Condition and Failing to Use Correct Work Scope Revision Process</strong><br /><i>Abstract:&nbsp;</i>Mechanical Maintenance personnel were performing modification work to add vent piping downstream of the Safety Injection (SI) common suction header vent valve 1 S1081. This work was being performed in accordance with a Design Change Package (DCP). In addition to the DCP, although not required, a weld upstream of the 1S1081 valve was selected to be reinforced. Design Engineering did not include the weld buildup as part of the DCP and this was added to the work package by the maintenance work planner after consulting the Site Welding Administrator and the Design Engineer. It is important to note that this weld buildup location was not included in the Clearance Order (CO) Request boundary. While performing the weld buildup on the existing weld upstream of the 1S1081, a pin hole leak developed. This leak was characterized as a small stream about the size of a needle. This section of piping was outside the CO boundary and could not be isolated under normal plant operating conditions. This leak affected the common suction header for both trains of SI. At 1630 hours, it was determined that both trains of SI were inoperable and Technical Specification Limiting Condition for Operations (LCO) 3.0.3 was entered. The operating shift began ramping Unit 1 off line. The leak was repaired at approximately 25% reactor power and LCO 3.0.3 was exited. The root causes of the event were determined to be not using the appropriate process to add work scope to a modification. Corrective actions included stopping the work practice of reinforcing existing welds outside of the DCP process and training the work planners on the requirements of the DCP process. Due to the minor nature of the leak, the SI system, though technically inoperable, was still available to perform its design function. However, the on-line risk of Unit 1 was considered "yellow" when the common SI suction header was drained to facilitate the weld repair.
4552001001 | Byron 2 | 04/02/2001 | 06/01/2001 | ML01156003 | <strong>Multiple Main Steam Safety Valve Relief Tests Exceeded Required Tolerance Due to Disk to Nozzle Metallic Bonding</strong><br /><i>Abstract:&nbsp;</i>During setpoint testing of the Unit 2 Main Steam Safety Valves (MSSVs) on April 2 and 3, 2001, six of 20 MSSVs failed to meet Technical Specification surveillance requirements. Operations entered the applicable Technical Specification Action Condition until each valve was tested satisfactorily. Because the MSSVs were tested sequentially, only one valve was inoperable at any one time. The cause of five of the failures has been determined to be a form of metallic bonding between the disk and the nozzle resulting in an increase in the valve's setpoint. This phenomenon is characterized by MSSVs experiencing a high initial lift setting followed by satisfactory subsequent lift setting, with no intervening adjustments, as occurred in this event. The cause of the out of tolerance setpoint for one MSSV was indeterminate. All out of tolerance MSSVs were refurbished with X-750 Inconel valve disks. This material is less susceptible to this phenomenon. An engineering analysis concluded that the multiple out of tolerance condition was still bounded by design basis analyses. This condition is reportable in accordance with 10 CFR 50.73 (a) (2)(i)(B).
4552001002 | Byron 2 | 06/26/2001 | 08/27/2001 | ML01242035 | <strong>Manual Reactor Trip Due to a Decreasing Steam Generator Level Caused by a Failed Positioner on an Air Operated Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>At 0609 hours on June 26, 2001, the Unit 2 licensed Nuclear Station Operator (NSO) observed the Unit 2 “D" Steam Generator (SG) level begin to decrease. He attempted to further open the Unit 2 Main Feedwater (FW) Regulating Valve (i.e., 2FW540) for the 2D SG. The valve did not respond and the 2D SG level continued to decrease and approached the low level reactor trip setpoint. In anticipation of the automatic trip signal, the NSO initiated a manual reactor trip signal at 0609 hours, prior to reaching the low level setpoint on 2D SG. The reactor trip system responded as expected and shutdown the reactor. The Auxiliary Feedwater (AF) System started as expected to supply auxiliary feedwater to the SGs. During the post reactor trip recovery, an unexpected reactor trip and AF actuation signal was generated when the B SG level was allowed to drop below the actuation setpoint. The 2B AF pump had just been secured and consequently, restarted. The cause of the 2FW540 valve closing was due to a retaining clip in the valve's positioner (i.e., Bailey AV1) not being installed correctly. The cause of the second unexpected actuation signal was due to failure of the licensed Unit Supervisor (US) to verbalize a procedure step concerning SG levels. Corrective actions include revising work instructions to ensure the retaining clip in Bailey AV1 positioners are installed correctly and counseling the US. There were no safety consequences impacting plant or public safety. This event is reportable in accordance with 10 CFR 50.73 (a) (2)(iv).
4552001003 | Byron 2 | 08/17/2001 | 10/17/2001 | ML02004058 | <strong>Improper Technical Specification Action Condition Application for Process Sampling Containment Isolation Valve Due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2001, a human performance error occurred on Unit 2, leading to Technical Specification (TS) 3.6.3, Containment Isolation Valves (CIV) non-compliance. A Unit 2 'A' train CIV for the Hydrogen Monitor System was mistakenly identified and used as the isolation boundary for the 'B' train Hydrogen Monitor. In addition to the wrong train, the valve selected was a "fail open" valve and would not isolate the penetration upon being de-activated. Because of this error, the Station failed to correctly isolate the correct containment penetration for the 2B Hydrogen Monitor. In addition the containment penetration for the `A' Hydrogen Monitor was also rendered inoperable since the `A' train CIV failed open when power was removed and would not have closed upon receipt of a containment isolation signal. Neither penetration was isolated within the required four hours of the occurrence as required by TS. The error was discovered and rectified approximately 22 hours later. The root cause of this event was determined to be a failure of the licensed operators to follow standard operating practices in determining and implementing equipment isolation boundaries as expressed in departmental procedures and policies. The Operations department is currently developing an Operations Gap Analysis and Excellence Plan. This plan will identify areas where personnel performance is not meeting expectations. Following completion of the plan, implementation of actions necessary to achieve performance improvement will be undertaken. There were no safety consequences impacting plant or public safety as a result of this event. The Hydrogen Monitors and their associated CIVs do not impact core damage frequency. This event is reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(i)(b).
4552001004 | Byron 2 | 08/16/2001 | 10/30/2001 | ML02046003 | <strong>Technical Specification Non-Compliance Caused by Improper Component Installation and Post Maintenance Test on an Area Radiation Monitor that Generates an Automatic Containment Ventilation Isolation Signal</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2001, Instrument Maintenance Department (IMD) technicians began maintenance activities on the Unit 2 containment area radiation monitor 2AR11J. During the activity, an IMD technician improperly landed an electrical lead and caused the failure of several printed circuit boards. An emergent repair ensued which involved the improper re-installation of an output relay. This relay provides a containment ventilation isolation signal to the solid state protection system (SSPS). The faulty installation caused a permanent containment ventilation signal to be present. A containment ventilation isolation signal was generated and subsequently reset in the control room with the belief the signal was spurious due to the maintenance restoration activity. The reset activity blocked the signal from reactivation, though it was still present. The post maintenance test to demonstrate operability did not check the function of this relay and consequently, the monitor was restored to operable status with a faulty relay. The error was discovered 15 days later during the execution of an SSPS surveillance. The root causes were determined to be an improper installation of the relay by the IMD technician and a knowledge deficiency by the IMD and operations supervision in determining the post maintenance testing requirements. Corrective actions include counseling the IMD technicians involved and training the IMD and operations personnel to improve system knowledge. Due to redundant actuation trains and diverse isolation signals, there were no safety consequences as a result of this event. This event is reportable to the NRC in accordance with 10CFR 50.73 (a)(2)(i)(b).
4562001001 | Braidwood 1 | 09/19/2001 | 06/07/2002 | ML02171007 | <strong>Three Main Steam Safety Valves Exceeded The Technical Specification Limit by Greater Than 3%</strong><br /><i>Abstract:&nbsp;</i>During testing of the Unit 1 Main Steam Safety Valves (MSSVs) on September 19 and September 20, 2001, three valves lifted in excess of their setpoints by greater than the 3%Technical Specification (TS) tolerance. For each case where the MSSV lifted greater than the 3% tolerance, the appropriate TS Condition was entered. The valves were tested sequentially. Therefore only one valve was known to be inoperable at any time. The valves were adjusted as necessary and retested to place them in the required tolerance range prior to exiting the TS Condition. An evaluation has been performed by Nuclear Fuels Management with the results indicating the limits of the UFSAR accident scenarios impacted by the MSSVs have not been exceeded. The results of an industry survey conducted by Braidwood Station engineers and a failure analysis performed by Altran Corporation indicate that a thicker oxide layer may decrease oxide bonding and minimize the sticking characteristics of the MSSVs. However, Altran Corporation summarized that based on what was observed through laboratory investigation, no specific conclusions could be drawn or root cause identified as to why the X-750 disk from Braidwood exhibited the high lift setpoint phenomenon attributed to oxide bonding. The results of the industry survey suggest that long continuous runs contribute to valve sticking. Prior to the testing on September 19 and 20, 2001, Braidwood Unit 1 had completed a 535 day continuous run. The oxide bond appears to be broken when valves are subjected to a thermal cycle between tests. This event is being reported pursuant to 10CFR50. 73(a)(2)(i)(B).
4572001001 | Braidwood 2 | 05/19/2001 | 07/17/2001 | ML01212025 | <strong>Braidwood Unit 2 Reactor Trip and Subsequent Loss of Non-Safety Related Offsite Power Due to Failure to Perform Concurrent Verification and Improper Command and Control</strong><br /><i>Abstract:&nbsp;</i>At 0406 on 05/19/01, Braidwood Unit 2 tripped due to a loss of loop 2C reactor coolant flow while operating at 100 percent power. The 2C reactor coolant pump tripped when a nonlicensed operator opened the incorrect system auxiliary transformer (SAT) feed potential transformer fuse door on 6.9kV Bus 258 during preparations for a Unit 2 SAT outage. The loss of the 2C reactor coolant pump resulted in an automatic reactor trip due to low flow in the 2C loop. Due to the existing electrical lineup in support of the SAT outage, power to the 6.9kV buses and non-ESF 4kV buses was lost when the turbine/generator tripped offline. This resulted in a loss of all reactor coolant pumps, circulating water pumps, the main feedwater pumps and the condensate/condensate booster pumps. The reactor coolant system was maintained on natural circulation cooling with the secondary heat sink supplied by the steam generator power operated relief valves and auxiliary feedwater supplying the steam generators. The root causes for the event were failure to perform concurrent verification to identify the correct SAT primary potential transformer fuse door and improper command and control to ensure critical tasks were performed correctly. The corrective actions are counseling and discipline of the responsible individuals and development and implementation of a policy to strengthen command and control standards for execution of critical activities in the plant.
4572001002 | Braidwood 2 | 09/26/2001 | 11/26/2001 | ML02016014 | <strong>Main Steam Isolation Valves Not Stroke Timed in Mode 3 as Required</strong><br /><i>Abstract:&nbsp;</i>While reviewing the schedule and testing requirements for the Unit 1 Main Steam Isolation Valves (MSIV) while in refueling outage A1R09, it was identified that Braidwood Station had not been testing the MSIVs as described in the Technical Specification (TS) Bases. At 1600 on September 26, 2001, it was determined that the MSIVs on Braidwood Unit 2 were not tested in Mode 3, as required. This did not affect Braidwood Unit 1 since it was is in refueling outage A1R09, outside of the mode of applicability for the TS Surveillance Requirement (SR). The failure to test the valves in mode 3 resulted in a missed TS SR, which resulted in Braidwood Unit 2 entering SR 3.0.3. SR 3.0.3 allows up to 24 hours to perform the missed surveillance. In accordance with the Bases for TS 3.7.2 "Main Steam Isolation Valves (MSIVs)," SR 3.7.2.1 must be performed in Mode 3 at operating temperature and pressure. The surveillance cannot be performed at power since the SR is stroke timing of the valve in the closed direction. Since the SR could not be performed, Generic Letter 87-009 "Sections 3.0 And 4.0 of Standard Tech Specs on Limiting Conditions For Operation And Surveillance Requirements" was used to allow 24 hours to seek enforcement discretion for Braidwood Unit 2. Braidwood prepared a Notice of Enforcement Discretion (NOED) seeking discretion from compliance with the requirements of SR 3.7.2.1 and 3.7.2.2. The NOED and subsequent exigent License Amendment Request (LAR) sought discretion from performing SRs 3.7.2.1 and 3.7.2.2 until the first start-up after September 27, 2001. On September 27, 2001, the Nuclear Regulatory Commission (NRC) granted verbal approval of the NOED. The LAR was approved on November 2, 2001. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4582001001 | River Bend | 04/21/2001 | 06/20/2001 | ML01177034 | <strong>Unplanned Reactor Scram During Turbine Control Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2001, at approximately 2:54pm, a reactor scram occurred during scheduled testing of the main turbine control valves. The plant was at approximately 58 percent rated power at the time of the scram. The scram was an automatic response to high reactor steam pressure resulting from an unanticipated closure of the main turbine control valves. Plant systems responded normally following the scram. Thirteen reactor safety-relief valves opened following the turbine trip, which is an anticipated response to this transient. Operators implemented the appropriate response procedures, and promptly stabilized the plant systems. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the reactor protection system. Subsequent troubleshooting and testing did not positively identify the root cause for the turbine trip. The most likely cause was determined to be a turbine speed signal error generated by rotor dynamics of the high pressure turbine during the testing of control valve no. 1. This event was of very low significance. A main turbine trip while at power is an analyzed event, and all plant systems responded normally.
4582001002 | River Bend | 10/04/2001 | 11/05/2001 | ML02025041 | <strong>Potential Violation of Maximumn Power Limit Dur to nonconservative Error in Core Thermal Power Calculation Software.</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2001, a review by River Bend engineering of a General Electric (GE) report determined that the station has in the past potentially operated slightly above the maximum core thermal power as authorized in the facility operating license. This event is being reported as required by River Bend's license condition 2.E under the 10CFR50.73 reporting format. In September 2001, GE issued a report titled "Impact of Steam Carryover Fraction on Process Computer Heat Balance Calculations." The GE report details the condition in which a nonconservative error in the process computer software causes the calculation of core thermal power to be slightly low. It is estimated that the station has operated, at times, approximately three megawatts thermal over its licensed maximum limit. The moisture carryover constant in River Bend's process computer was previously defined to be 0.1 percent. As a conservative measure to assure compliance with the operating license, that value has been changed to 0.0. Any process computer heat balance subroutines will now utilize the new constant value of 0.0, pending the disposition of the forthcoming GE Service Information Letter on this subject. As stated in the General Electric report, use of the carryover fraction of 0.1 percent in thermal power calculations, while nonconservative, does not represent a safety issue. Therefore, this condition was of minimal consequence with respect to the health and safety of the public.
4582001003 | River Bend | 09/24/2001 | 11/20/2001 | ML02015030 | <strong>Unplanned Automatic Start of Standby Service Water System During Surveillance testing Due to Inadequate Control of Test Configuration</strong><br /><i>Abstract:&nbsp;</i>On September 24, 2001, at approximately 4:55 p.m. CDT with the plant in a refueling outage, an unplanned automatic actuation of the Division II standby service water system occurred during Division I integrated emergency core cooling systems testing. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of a safety system. The actuation of Division II standby service water occurred as a result of an incorrect alignment of two motor-operated valves in the system. After plant conditions were established to support starting the test, the required service water valve alignment was not properly established prior to commencement of the test. When the test was initiated, a low pressure condition was momentarily induced in the standby service water system. The Division II standby service water system responded as designed to the low pressure condition. After an initial assessment, the system was restored to its standby configuration, and the test proceeded. This event was of minimal significance with respect to the health and safety of the public. The reactor was in cold shutdown at the time of the event, and the Division II standby service water system responded as designed. No loss of safety function occurred.
4582001004 | River Bend | 10/17/2001 | 12/17/2001 | ML02024011 | <strong>Automatic Start of Division II Diesel Generator Due to Loss of Division II 4160 Volt Normal Feeder Breaker</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2001, at approximately 2:48 a.m. CDT, with the plant at 80 percent power, the normal feeder breaker to the Division II safety-related 4160 volt AC switchgear opened unexpectedly. This caused a loss of power to the Division II 4160 volt and 480 volt AC systems, and an automatic start signal to the Division II diesel generator (DG). This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(a) as a valid actuation of a safety system. This event also caused a loss of power to the Division II reactor protection system circuitry, resulting in the invalid actuation of containment isolation valves. The cause of the 4160 volt feeder breaker trip was determined to be a failed optical isolator in the preferred station service primary protection circuitry. The failure was internal to the isolator card, and resulted in a false signal to the 4160 volt feeder breaker's trip coil. This event was of minimal significance with respect to the health and safety of the public. The Division II DG automatically started and restored power to the Division II AC electrical systems as designed. Actuations of containment isolation valves and emergency ventilation systems occurred as expected for a loss of power. Plant operation was not interrupted.
4612001001 | Clinton 1 | 01/16/2001 | 02/13/2001 | ML01052035 | <strong>Enforcement Discretion to Replace Generator Bearings in Division 2 Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>Vibration data obtained during performance of the Technical Specification (TS) required 24-hour endurance test of the Division 2 emergency diesel generator (DG) identified degradation of one of the two generator bearings. The data indicated that the degradation exceeded pre-established vibration acceptance criteria, so a decision was made to replace the bearing as a proactive measure. Vibration measurements taken prior to the recent operation of the DG had indicated the onset of bearing degradation. Since the work required to restore the DG could not be completed within the TS allowed outage time (AOT) due to the extensive maintenance required to replace the bearing, enforcement discretion was requested from the NRC and granted. The cause of the event is an error in a design change in 1993 that installed generator shaft guards. The shaft guards provided an electrical connection to the skid ground that defeated the insulation of the generator bearing causing fluting of both generator bearings. Contributing causes were also identified. Corrective action includes removing the shaft guards, revising a design review standard, changing preventive maintenance practices for vibration monitoring, and revising a procedure to periodically monitor generator shaft currents.
4612001002 | Clinton 1 | 02/04/2001 | 04/04/2001 | ML01101014 | <strong>Failure to Incorporate Recommendation from Technical Information Letter Results in Random Scram During Turbine Valve Testing</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2001, Clinton Power Station (CPS) was in Mode 1 at approximately 96 percent power. During performance of turbine valve surveillance testing of the #3 Combined Intermediate Valve, an emergency trip system (ETS) low fluid pressure transient occurred as sensed by the control fast closure pressure switches resulting in an automatic scram. The cause for the event was determined to be an inadequate process for the review and approval of the CPS response to General Electric Technical Information Letter (TIL) 1212-2. This TIL contains a recommendation that a flow restricting orifice be installed in the P-Port of the fast acting solenoid valves in the turbine electrohydraulic control system for main turbine stop valves, control valves, and combined intermediate valves. Installation of the orifice prevents random reactor scrams on low ETS pressure during valve testing. The review of this TIL did not identify that the recommended orifice was not installed in the P-Port of the FASV for the #3 CIV. The corrective actions for this event include installation of the recommended orifices, revising the Operating Experience program procedure, providing training, and reviewing the responses to other operating experience documents.
4612001003 | Clinton 1 | 07/24/2001 | 09/21/2001 | ML01268021 | <strong>Failure to Follow Procedure Due to Human Error Results in Incorrectly Lifting Leads, Causing Loss of Feedwater Level Signal, and Reactor Scram on High Vessel Water Level</strong><br /><i>Abstract:&nbsp;</i>Instrument Maintenance (IM) technicians were performing a quarterly channel functional test on the B Reactor Feedwater level channel with the A reactor feedwater level channel in service. During the surveillance test, the technicians incorrectly performed a step in the procedure and lifted the Channel B-Device GT leads. Per procedure, the step for lifting the leads is only performed if a high reactor water level condition exists, and no such condition existed. Lifting the leads caused a loss of the reactor vessel level input signal for feedwater control, resulting in an immediate demand by the Master Level Controller. A feedwater transient began that resulted in reactor water level rising above the High Level 8 trip initiating an automatic reactor scram. The cause of this event was human error. The technicians involved did not follow the procedure and performed a step not applicable to current plant conditions. Corrective actions for this event include personnel actions for the technicians involved in the event, revising the surveillance procedure and reviewing other IM procedures, issuing a risk review and screening procedure, training on various topics, and increasing management oversight on backshifts.
4822001001 | Wolf Creek | 11/16/2001 | 01/14/2002 | ML02058054 | <strong>Potential Submergence of Safety-Related Equipment Due to an Inadequate Flooding Calculation</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2001, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel identified an error in an internal flood calculation. The calculation under estimated the input flow rate from a pipe break in two Auxiliary Building rooms and over estimated the drain flow rate from these rooms. As a result of correcting these values in the calculation, the calculation results now predict a flood water level that would submerge safety-related equipment required to switch the suction of the Auxiliary Feedwater (AFW) pumps from the Condensate Storage Tank (CST) to the Essential Service Water (ESW) system. Evaluations of event scenarios indicate that flooding of safety-related AFW equipment could occur and/or the decay heat removal function of AFW would not be accomplished. The isolation valve for this line has been throttled, thus reducing the input flow rate and the resultant flood water level to ensure components required to fulfill the AFW system safety function are not submerged. The cause for including these incorrect assumptions in this calculation is indeterminate due to the historical nature of this condition (the calculation was performed by an Architect/Engineer's staff in 1986). Based on a sampling review of other calculations, this issue is believed to be an isolated case. This condition is considered to be of minimal safety significance.
4832001001 | Callaway | 01/12/2001 | 02/09/2001 | ML01044017 | <strong>Missed step in test procedure results in an invalid Reactor Trip Breaker actuation due to the system being improperly removed from service</strong><br /><i>Abstract:&nbsp;</i>At 09:28 on 01-12-01, with the Plant operating at full power, an unplanned actuation of the "A" Reactor Trip Breaker occurred during testing of "A" Solid State Protection System (SSPS). The "A" Reactor Trip Breaker Bypass Breaker had previously been closed as part of the testing procedure; therefore the "A" Trip Breaker actuation had no effect on Plant operation Due to a missed step in the procedure, the INPUT ERROR INHIBIT switch for the "A" train SSPS had not been placed in the INHIBIT position. Placing the switch in the INHIBIT position generates an Intermediate Range Rodstop Block and blocks the source range detector. Immediately prior to this step is a caution statement that has a requirement to notify the Reactor Operator. The Technician read the statement, notified the Reactor Operator as required, and incorrectly initialed the following step as complete, but failed to reposition the switch. When the Technicians cycled the "A" logic switch, the "A" Reactor Trip Breaker opened and the Control Room received annunciator 56B, RCS < 50 degrees F sub-cool. The Control Room Supervisor suspended testing, notified I&C Supervision, notified Engineering and initiated an immediate review of the events. It was discovered that the INPUT ERROR INHIBIT switch had not been placed in the INHIBIT position. The switch was placed in INHIBIT and the test was completed.
4832001002 | Callaway | 02/14/2001 | 04/11/2001 | ML01107053 | <strong>Foreign object renders 'B' Essential Service Water pump inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0851, on 2114101, with the Plant in Mode 1 at 100 percent Reactor Power, the 'B' Essential Service Water (ESW) pump was started to support performance of a surveillance procedure. Upon starting, the pump experienced low discharge pressure and flow. The pump was secured and declared Inoperable, which also rendered the 'B' Emergency Diesel Generator, 'B' Containment (CTMT) Spray pump and 'B' train CTMT coolers Inoperable. The 'C' CTMT cooler was also Inoperable as part of scheduled 'A' train work. At 0851, with 'A' and 'B' train CTMT coolers plus the 'B' CTMT Spray pump Inoperable, the Plant met Technical Specification (T/S) 3.0.3 conditions. 'C' CTMT Cooler was restored to Operable at 1123 and T/S 3.0.3 was exited. Subsequently, pump inspection revealed a tygon hose in the pump suction. The hose was removed and the pump was declared Operable at 0231, 2/15/01. Further review of the incident determined that the system had been Inoperable since 1415, 2/9/01. A review of work performed from 1415, 2/9/01 to 0231, 2/15/01 revealed that the Plant had unknowingly entered T/S 3.0.3 four additional times. The root cause of the event was loss of pump function due to foreign material. Corrective actions include foreign material program enhancement.
4832001003 | Callaway | 03/09/2001 | 04/27/2001 | ML01137028 | <strong>Reactor Trip Due to Loss of Both Rod Drive Motor Generators</strong><br /><i>Abstract:&nbsp;</i>At 1252, 3/9/01, with the Plant in Mode I at 100 percent Reactor Power, after opening the output breaker for 'B' Rod Drive Motor Generator (RDMG) in preparation for maintenance, the output breaker for 'A' RDMG opened. This deenergized the Rod Control System and caused all rods to insert into the Reactor (Rx) core. As a result of the rod insertion, primary temperature and pressure decreased and caused an OTdeltaT Rx trip to occur which opened both Rx Trip breakers. All systems operated as expected except for rod K-10 which had a faulty indication. The primary was borated an additional 150 ppm. Troubleshooting found a faulty circuit card which when replaced, corrected the K-10 indication problem. Plant startup and return to service was delayed by equipment problems with 'B' Main Feedwater Regulating Valve. After completion of repairs, the Plant returned to service on 3/13/01. The cause of the RDMG output breaker opening has been traced to a 40-volt ripple, which caused an over voltage condition to be sensed. The 40-volt ripple vanished the day after the trip and its source has not been determined.
4832001005 | Callaway | 09/17/2001 | 11/09/2001 | ML02015005 | <strong>Auxiliary Feedwater Actuation Due to Loss of DC Bus, PK01</strong><br /><i>Abstract:&nbsp;</i>At 1207, 9/17/01, with the Plant in Mode 1 at 100 percent Reactor (Rx) Power, non-safety related DC electrical bus PK01 was inadvertently de-energized while cross-tying power sources in preparation for planned battery maintenance. One lube oil pressure switch for each Main Feed Pump was de-energized which generated an Auxiliary Feedwater Actuation Signal. This resulted in both Motor Driven Auxiliary Feedwater Pumps (MDAFP) starting and Steam Generator (S/G) Blowdown isolating. Reactor Coolant System (RCS) Letdown isolated due to power being lost to the operator's solenoids for valves BBLCV459 and BBLCV460. The MDAFPs injected cold water from the Condensate Storage Tank into all four S/G's during the initial phase of this event. This cold water caused RCS pressure to momentarily decrease to 2218 psig, and Rx power to momentarily rise to 101. 18 percent. Rx power and RCS pressure were restored to normal parameters within allowed time limits with no adverse effects. Power was restored to PK01 and plant systems returned to normal operating conditions. The event was caused by inadequate procedural guidance concerning indications of successful electrical bus cross-connection. Corrective actions include procedure revisions to incorporate adequate guidance on electrical equipment manipulations.
4982001001 | South Texas 1 | 09/24/2001 | 11/19/2001 | ML02015022 | <strong>Failure of Essential Cooling Water Pump 1C Following Maintenance</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2001, Unit 1 was in Mode 1 in coastdown operations in preparation for a refueling outage. A Train C Essential Cooling Water system outage was entered at 0200 hours in order to perform scheduled maintenance. On September 21, 2001, the Train C Essential Cooling Water pump was started in order to perform post-maintenance surveillance testing. The pump ran for approximately 10 minutes with what was thought to be adequate cooling and lubrication water flow. At approximately 2106 hours, the pump was manually stopped when output pressure dropped to zero. The pump was observed to come to an abrupt stop. Subsequent investigation identified that significant damage had occurred to the No. 2 pump bearing, and the lower pump shaft exhibited indications of overheating. The root cause of the pump damage was determined to be foreign material, which caused insufficient cooling/lubricating flow by obstructing the bearing flow orifices. Because pump repair time would exceed the 7-day Allowed Outage Time of Technical Specification 3.7.4, enforcement discretion was requested to permit continued operation of the unit while the pump was repaired. Enforcement discretion was granted on September 23 at 1800 hours. Repair work was completed and on September 26, 2001 at 0905 hours the Train C Essential Cooling Water system and the associated systems it supports were restored to operable status. Corrective actions include revising operating procedures to contain additional pump stop criteria based on indicated lube water flow, and revising maintenance procedures to add specific foreign material exclusion/cleaning requirements prior to pump reassembly. This event was reviewed for risk impact and found to be risk insignificant since the conditional core damage probability was approximately 8.24E-7.
4982001002 | South Texas 1 | 10/13/2001 | 12/12/2001 | ML02015013 | <strong>Pressurizer Safety Valve Setpoints Discovered Outside Required Tolerances</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2001 Unit 1 was shutdown in Mode 6 in refueling outage 1RE10. Information was received from an offsite vendor that during pressurizer safety valve "as found" set point testing, valve N1RCPSV3451 had a lift pressure of 2406 psig which is low outside of the Technical Specification required setpoint of 2485 psig +/-2% (2435.3 to 2534.7). Valve N1RCPSV3452 had an "as found" lift pressure of 2411 psig. On October 15, 2001 the vendor reported that safety valve N1 RCPSV3450 had an "as found" lift pressure of 2422 psig. These test results constitute a violation of Technical Specification 3.4.2.2, Reactor Coolant System - Operating. The root causes of the valves failing the "as found" lift tests include: (a) the inherent differences between the "as left' test conditions and the "as found" test conditions, plus nozzle loading effects which are inducing stresses and misalignments in the valves, and (b) the narrow tolerance band of +/- 2% which is too restrictive considering the valve nozzle loading effects and these inherent differences. Corrective actions include installation of replacement valves with "as left' lift settings of 2485 psig +/- 1 %, and requesting a Technical Specification change to optimize setpoint tolerances for the Pressurizer Safety Valves "as found" lift setpoints. The "as found" Pressurizer Safety Valve setpoints did not violate any safety analysis limits and did not adversely impact Reactor Coolant System overpressurization or Departure from Nucleate Boiling Ratio analysis.
4992001001 | South Texas 2 | 02/07/2001 | 04/09/2001 | ML01101001 | <strong>Manual Reactor Trip and Engineered Safety Features Actuation</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2001, at 1828, Unit 2 was operating at 10% power, escalating to 12-14% power, in preparation for closing the Main Generator Breaker when a Reactor Operator performing electrical plant bus transfer operations inadvertently deenergized the 2F Auxiliary and Standby 13.8 kV busses. As a result Reactor Coolant Pump 2A was de-energized, requiring the operating crew to initiate a manual reactor trip in accordance with plant procedures. All control rods fully inserted. All actuated safety equipment operated as required. The root causes identified for this event include time pressure imposed by electrical alarms and interlocks that lead to a deviation from fundamental work practices, and less than adequate procedural direction. Corrective actions include revising procedural guidance for this activity, training Plant Operations personnel on the pitfalls for time pressure driven evolutions, and revisiting the time limit setpoints for parallel operations of 13.8 kV busses. This event was reviewed for risk impact and found to be risk insignificant since the conditional core damage probability is less than 2x10-7.
4992001002 | South Texas 2 | 03/01/2001 | 04/23/2001 | ML01120005 | <strong>Manual Reactor Trip as a Result of Switchyard Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2001, at 0821, Unit 2 was operating at 95% power, activities were underway to remove the 345kV switchyard North Bus for maintenance. Switchyard breaker Y590 was opened. Unknown to the operating crew, the C phase pole of switchyard breaker Y600 which had been previously closed, remained opened. With the C phase pole of breaker Y600 still opened, the Control Room received electrical panel alarms and the three operating Circulating Water Pumps tripped off line, requiring the operating crew to initiate a manual reactor trip in accordance with plant procedures. All control rods fully inserted. All actuated safety equipment operated as required. The root cause identified for this event is failure of the operating linkage of switchyard breaker Y600 C phase pole. The bushing required between the linkage pin and the operating linkage was not installed and most likely left out during fabrication. Corrective actions include repair of the failed breaker, inspection of a similar switchyard breaker, and further review of switchyard breaker inspection procedures. This event was reviewed for risk impact and found to be risk insignificant since the conditional core damage probability is less than 2x10-7.
4992001003 | South Texas 2 | 03/19/2001 | 05/17/2001 | ML01142031 | <strong>Steam Generator 2C Classified as Category C-3 in 2RE08</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2001, during refueling outage 2RE08, the results of steam generator tube inspections in steam generator 2C were classified as category C-3 in accordance with Technical Specification 4.4.5.2.d. in that 48 tubes out of 4,615 (i.e., >1%) had been found defective. All defective steam generator tubes were plugged before the steam generators were returned to service. There were not any adverse safety consequences or implications as a result of this event. This event did not adversely affect the safe operation of the plant or the health and safety of the public. The cause of the imperfections was outside diameter stress corrosion cracking.
4992001004 | South Texas 2 | 05/08/2001 | 07/05/2001 | ML01191017 | <strong>Automatic Reactor Trip due to Low Water Level in Steam Generator 2A</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2001, at 1528, Unit 2 was operating at 100% power. Activities were in progress to monitor the valve positioner on steam generator `2A' Feedwater Regulating Valve (FRV) using a laptop computer and Hart communication adapter connected to the positioner signal leads. After several minutes of monitoring, the troubleshooting team connected the laptop computer to a utility outlet to keep its battery charged. Unknown to the team, the Hart adapter was designed with one of its leads connected to the laptop computer ground. The grounded Hart adapter lead was connected to the positive signal lead of the FRV positioner. The FRV control circuit is designed with the negative signal lead connected to plant ground in the 7300 Process Cabinets. When the laptop AC power cord with ground plug was plugged into the utility outlet, both signal leads for the FRV were connected to ground. This resulted in a loss of positioner control signal, closure of the FRV and rapid decrease in steam generator `2A' water level. The operators observed the loss of feedwater flow and attempted to reopen the FRV in manual control. Operations directed the team to remove test equipment. Operations staff ordered a manual reactor trip; however, steam generator `2A' reached the LO-LO Level setpoint and the reactor tripped automatically. All control rods fully inserted. All actuated safety equipment operated as required. The root causes identified were that personnel did not recognize the ground potential of the laptop and adapter, and the work control process did not provide adequate controls for this activity. Corrective actions include improving the work control process and establishing programmatic controls for the use of test equipment.
5282001001 | Palo Verde 1 | 03/31/2001 | 05/24/2001 | ML01150014 | <strong>RCS Pressure Boundary Leakage Caused by Degraded Alloy 600 Instrument Nozzle</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2001 with Unit-1 operating in Mode 4, Hot Shutdown, and cooling down to Mode 5, Cold Shutdown, for a refueling outage engineering personnel discovered boric acid on a reactor coolant system hot leg instrument nozzle. The cause of the boric acid accumulation was primary water stress corrosion cracking of alloy 600 Inconel material in the instrument nozzle. The amount of boric acid found demonstrates the crack was small and the leakage rate low. The nozzle was visually inspected during the last refueling outage in 1999 with no leakage identified. Visual inspections of other alloy 600 hot leg nozzles did not identify other degraded components. As corrective action the nozzle was modified during the refueling outage and prior to the Unit entering Mode 4. In addition, the current Palo Verde Alloy 600 strategy is to modify all alloy 600 hot leg nozzles during future outages. A similar previous condition was reported in LER 50-528/1999-006-00.
5282001002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 03/29/2001 | 05/24/2001 | ML01150015 | <strong>Technical Specification Violation Due to Deficient Test Procedure for Refueling Purge Valves</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2001, engineering personnel informed plant operations personnel that the local leak rate test (LLRT) methodology may not have conservatively quantified leakage rates for the inboard refueling purge valves. Specifically, engineering personnel had determined the LLRT methodology measured leakage using a reverse flow method that may not be equivalent to the leakage through the inboard valves had they been pressurized in the accident direction. Since the LLRT results may not have conclusively demonstrated the valves' ability to perform their intended safety function, operations personnel in Units 1, 2 and 3 declared the inboard refueling purge valves inoperable and entered the applicable Limiting Condition for Operation. Blind flanges have been installed and tested on refueling purge penetrations 56 and 57 in Units 1, 2, and 3 to ensure penetration integrity. A previous similar event was reported in LER 50-528/2000-004-00.
5282001003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 10/10/2001 | 12/04/2001 | ML02004064 | <strong>Technical Specification Required Shutdown Due to Degraded Control Element Assemblies</strong><br /><i>Abstract:&nbsp;</i>On October 10, 2001, at approximately 0430 MST, Palo Verde Unit 2 was in Mode 1 (POWER OPERATION), operating at approximately 100 percent power when Control Room personnel were advised of a potentially transportable condition affecting the integrity of Control Element Assemblies (CEAs). Preliminary inspection of Unit 3 CEAs during refueling revealed one CEA with cracks. Due to the similar design and operating history of CEAs, similar cracks were assumed to also be present in Unit 2. Based upon the Unit 3 discovery, Unit 2 plant operators initiated a plant shutdown and at approximately 0937 MST, Palo Verde Unit 2 entered Mode 3 (HOT STANDBY). Unit shutdown occurred normally and following the manually inserted reactor trip per the unit shutdown procedure, all CEAs fully inserted into the core. Unit 2 was taken to Mode 6 (REFUELING) to inspect and replace the CEAs. The event did not adversely affect the health and safety of the public. In the past three years, there have been no previous similar events reported pursuant to 10CFR50.73 for CEA degradation at Palo Verde Nuclear Generating Station. This CEA degradation LER reports APS' activities for Units 1, 2, and 3.
5282001004 | Palo Verde 1 | 09/14/2001 | 12/12/2001 | ML02017014 | <strong>TS Violation for Inoperable RCS Leak Detection Instrument Due to Misaligned O-ring</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2001 with Unit 1 operating at approximately 100 percent power in Mode 1 (Power Operation) chemistry personnel determined that the reading on the particulate channel of the reactor coolant system (RCS) leakage detection system was not consistent with containment atmosphere grab sample results. It was subsequently determined that the particulate channel had been degraded since September 14, 2001, when the particulate filter was replaced. Misalignment of an O-ring following the filter replacement resulted in airflow by-passing the particulate filter resulting in inaccurate indication. A second occurrence of a misaligned O-ring was identified on November 6 for the time period of October 17 to November 2, 2001. The cause of the O-ring misalignment was determined to be inadequate guidance and controls related to replacement of the O-ring and a design that made O-ring seating difficult. Corrective actions include properly aligning the O-ring and implementing detailed instructions for proper O-ring replacement. No previous similar events have been reported by Palo Verde Nuclear Generating Station in the last three years.
5282001005 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 12/11/2001 | 02/07/2002 | ML02058019 | <strong>Inadequate Surveillance Test for Time Response Testing of Hi Log Power Trip Function</strong><br /><i>Abstract:&nbsp;</i>On December 11, 2001, plant technicians discovered a procedural inadequacy in the method used for response time testing of the Plant Protection System Log Power Trip. This method did not meet Technical Specification Surveillance Requirements 3.3.1.13, and 3.3.2.5. All three Palo Verde Units were in Mode 1 when the Log Power Trip was declared inoperable. Since the Log Power Trip is not required in Mode 1 operation, no Limiting Condition for Operation Required Action was entered. Cause of the inadequate test method is attributed to inadequate documentation of the system design impact upon the time response testing requirements. Retest using an adequate test procedure was completed on December 21, 2001. The "As Found" response times were all acceptable and the log power channels were returned to operable status. The Surveillance Test Procedure will be updated with a note to reflect the need to conduct log power trip time response testing using the correct signal range. There have been no previous similar licensee event reported in the last three years.
5292001001 | Palo Verde 2 | 03/19/2001 | 05/24/2001 | ML01150013 | <strong>Main Steam Safety Valves As-Found Lift Pressure Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2001, Unit 2 was in MODE 1, operating at approximately 100 percent power when augmented testing revealed that a single main steam safety valve (MSSV) had an as-found lift pressure above the Technical Specification limit of +/- 3 percent of design lift pressure. The single MSSV is believed to have experienced a sticking phenomenon resulting from the valve disc bonding with the nozzle seat. The valve was reset per plant procedures to +/-1 % of the required setpoint. Previous similar events have been reported in LERs 50-529/2000-009, 50-529/1999-002, 50-530/1998-003, 50-528/1998-004, 50-529/1997-001, and 50-530/1997-003.
5292001002 | Palo Verde 2 | 07/13/2001 | 08/31/2001 | ML01255018 | <strong>Reactor Trip Due to Unexpected Closure of Main Steam Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2001, at approximately 0821 Mountain Standard Time, Unit 2 was in Mode 1 (POWER OPERATION), when a logic board and pin connector in the "B" Train Main Steam and Feedwater Isolation System failed causing three of four main steam isolation valves (MSIVS) to close. The reactor tripped from 100% power on Reactor Protective System Low Departure from Nucleate Boiling Ratio (DNBR). This DNBR trip was due to an auxiliary trip generated by all four Core Protection Calculator channels. The auxiliary trip was the asymmetric steam generator transient trip function based on cold leg temperature differences between the two steam generators. All Control Element Assemblies fully inserted. Two SG #2 Main Steam Safety Valves lifted as expected due to the MSIVs fast-closing. The primary plant was stabilized in Mode 3 (HOT STANDBY) with forced circulation with both steam generators being used for heat removal via the atmospheric dump valves. The event did not adversely affect the health and safety of the public. In the past three years there have been no similar events reported where a failed logic board in the Main Steam and Feedwater Isolation System logic cabinet caused the closure of MSIVs and a subsequent reactor trip.
5302001001 | Palo Verde 3 | 05/19/2001 | 07/18/2001 | ML01206004 | <strong>Automatic Reactor Trip Due to Unforeseen Problems Controlling ASI</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2001 at 0306 Mountain Standard Time (MST), Unit 3 was in MODE 1 (Power Operation), at approximately 19 percent rated thermal power when the reactor automatically tripped on an Axial Shape Index (ASI) auxiliary trip signal from the Core Protection Calculator (CPC). Unit 3 was operating at 19 percent power to accommodate corrective maintenance to resolve a high vibration problem on the main turbine. The root cause of the trip was that the downpower game plan did not include CPC ASI predictions, Axial Offset Anomaly (AOA) effects on ASI, or previous downpower differences between predicted ASI and the core operating limit supervisory system (COLSS) ASI. There has been one similar event reported within the last three years in LER 2-2000-007-00.re changes and training.
5302001002 | Palo Verde 3 | 10/29/2001 | 12/28/2001 | ML01150015 | <strong>Unit 3 Mode 3 Entry With An Auxiliary Feed Water Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2001 at 1515 MST and again on November 2, 2001 at 0528 MST Unit 3 control room personnel entered Mode 3 with the steam driven Auxiliary Feed Water (AFW) pump inoperable. Unit 3 was being returned to service following a refueling outage. Maintenance had been performed on both the steam driven AFW pump and the associated steam supply valves during the outage. Control room personnel incorrectly interpreted a provisional note in TSLCO 3.7.5 that allows Mode 3 operation with the steam driven AFW pump inoperable and proceeded with the mode change to Mode 3 on two separate occasions in violation of TSLCO 3.0.4. The steam supply valves were tagged closed and deenergized to comply with containment isolation requirements of Technical Specification Limiting Condition for Operation (TSLCO) 3.6.3 pending in-service valve testing. (The steam supply valves being closed and deenergized rendered the steam driven AFW pump inoperable.) Planned corrective actions to prevent recurrence include procedure changes and training.