## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192002001 | Oyster Creek | 03/26/2002 | 05/23/2002 | ML02158029 | <strong>Plant Operations Outside of the Technical Specifications Due to a Degraded System</strong><br /><i>Abstract:&nbsp;</i>At 7:00 AM on March 23, 2002, a sufficient volume of water had condensed in the Offgas Radiation Monitor sample chamber to cause the monitor to read unacceptably low. This resulted in the monitor being incapable of performing its intended function of isolating the Off Gas Line if Technical Specification release limits were exceeded. The sample chamber heat trace had failed allowing moisture to accumulate in the sample chamber. The system engineer, in response to a maintenance request, developed a troubleshooting plan which included a procedure to remove moisture from the sample chamber. On April 9, 2002, at 5:49 PM, draining was commenced on the sample chamber. Upon the draining of the chamber, indications returned to normal. The system was declared operable at 7:25 PM. The cause of the Technical Specification violation was a failed sample chamber heat trace. The heat trace was restored to an operable condition. The safety significance of this occurrence was minimal. Although the Air Ejector Offgas Radiation Detection System was inoperable, the Stack Radioactive Gaseous Effluent Monitoring System was in operation. No unexpected activity was noted. Weekly samples performed by the chemistry department of air ejector offgas did not show an increase in offgas activity.
2192002002 | Oyster Creek | 10/11/2002 | 12/04/2002 | ML02352006 | <strong>Local Leak Rate Test Results in Excess of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2002, Local Leak Rate Test results indicated that Main Steam Isolation Valve V-1-0007 exceeded the Technical Specification leak rate limit of .05(.75) La at 35 psig (equivalent to 15.98 SCFH). The leak was unable to be quantified and was greater than 50 SCFH at 35 psig. The cause of this occurrence was attributed to component degradation. The safety significance of this occurrence is considered minimal as the total penetration leakage would have been limited by Main Steam Isolation Valve V-1-0009 in the same header. The leakage past V-1-009 was quantified at 2.214 SCFH. V-1-0007 was refurbished and successfully leak rate tested prior to restart from the 1R19 Refueling Outage.
2192002003 | Oyster Creek | 10/10/2002 | 04/02/2004 | ML04105012 | <strong>Insufficient Appendix R Electrical Separation due to Void in Sand</strong><br /><i>Abstract:&nbsp;</i>A void was discovered in an area expected to be filled with sand beneath a portion of the two 480 VAC switchgear rooms. This void created an open area between two 4160 VAC feeder conduits. Because of the void, Appendix R electrical separation criteria were no longer met. Apparently, sand may not have completely filled the area and/or had settled over time creating this void. The safety significance of this discovery is minimal, as there is no combustible material in the void. Both cables are contained in conduit and have sufficient Class 1E electrical separation. Immediately upon discovery, a continuous fire watch was stationed. Additional actions were subsequently taken to open communication between the void and adjacent smoke detectors. This would provide early warning early warning of a degraded condition. Adequate separation will be provided by re-filling the void between the two 4160 VAC feeder conduits to meet Appendix R requirements. The sand fill will be monitored. No similar events have occurred.
2202002001 | Nine Mile Point 1 | 11/01/2002 | 12/27/2002 | ML03007069 | <strong>115 Kilovolt Offsite Power Inoperable Due to Low Voltage on Line 4 and Line 1 Out of Service</strong><br /><i>Abstract:&nbsp;</i>At 1508 hours on November 1, 2002, with 115 kilovolt (kV) Line 1 out of service to support emergency repair activities being performed on Line 2, National Grid Power Control (NGPC) notified the Nine Mile Point Unit 1 (NMP1) control room staff that a low contingency voltage alarm had been received for 115 kV Line 4. When Line 1 was removed from service, NMP1 entered action statement 3.6.3 of the Technical Specifications, requiring restoration of Line 1 within seven days or commence a plant shutdown. Upon notification of the low contingency voltage alarm, NMP1 operatorsdeclared Line 4 Inoperable and proceeded with Action statement 3.6.3 of the Technical Specifications for both 115 kV lines inoperable. With 115 kV offsite power inoperable, both emergency diesel generators were started and aligned to power emergency buses, as required by procedure. At 2310 hours, Line 1 was restored to service and the low contingency voltage alarm cleared. With both 115 kV lines operable, NMP1 exited 3.6.3 action statement of the Technical Specifications. The cause of the event was inadequate validation and verification of the administrative process governing the interface between NMP1 and NGPC for maintaining 115 kV voltage. This led to weaknesses in the process. For example, there was no formal administrative process identified for taking Line 1 out of service. Contributing causes include insufficient training, inadequate administrative controls, and the design of Line 4, which can require actions to boost voltage when Line 1 is out of service. Corrective actions include implementing additional training, procedure modifications, and modifications to provide voltage control when Line 1 is out of service and Line 4 is supporting the 115 kV bus.
2202002002 | Nine Mile Point 1 | 10/17/2002 | 12/27/2002 | ML03007069 | <strong>Loss of One Control Rod Drive Pump Train Due to Circuit Breaker failure</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2002, at approximately 1100 hours, with Nine Mile Point Unit 1 (NMP1) at approximately 100 percent power, the #12 control rod drive (CRD) pump failed to start during performance of the quarterly surveillance. The pump was visually observed to begin rotation and then coast to a stop. Visual inspection of the pump supply circuit breaker found the breaker in the "OPEN” position. A 7-day limiting condition for operation action Statement was entered, as required by Technical Specification 3.1.6b. The redundant #11 pump was verified operable as required by TS 4.1.6c. A spare breaker was identified and installed and the CRD pump successfully started. The #12 train was declared operable and the LCO action exited on October 19, 2002, at approximately 1315 hours. Subsequently, it was determined that the #12 CRD pump bad been inoperable from September 24, 2002, until it was declared operable on October 19, 2002. Thus, the pump was inoperable for 25 days versus 7 days allowed by TS 3.1.6b. The cause of this event was determined to be inadequate post maintenance testing. Contributing causes included a defective circuit breaker over current trip device (EC trip device), and lack of compliance with applicable higher level administrative procedures. Corrective actions included replacement of the defective circuit breaker, a thorough review of similar model circuit breakers in safety-related and non-safety related applications at NMP1, and written guidance to personnel regarding post maintenance testing expectations.
2202002003 | Nine Mile Point 1 | 12/02/2002 | 01/31/2003 | ML03042032 | <strong>Loss of Power to Reactor Protection System (RPS) Bus 12 While RPS Bus 11 Emergency Power Source Was Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 12/2/02, at 1647 hours with power level at approximately 100 percent and Emergency Diesel Generator (EDG) 102 out of service for maintenance, Nine Mile Point Unit 1 (NMP1) experienced a loss of Uninterruptible Power Supply (UPS) 172, which resulted in the loss of Reactor Protection System (RPS) Bus 12. With the loss of UPS 172, emergency power was not available to RPS Bus 12. RPS Bus 11 remained energized but its emergency power source, EDG 102 was out of service. With EDG 102 out of service and RPS Bus 12 de-energized, Technical Specifications (TS) required that the emergency power source be restored to either RPS Bus 11 or RPS Bus 12 within an hour or commence a shutdown and be shutdown within ten hours. RPS Bus 12 was re-energized from non-safety related Bus 130A at 1709 hours on 12/2/02. At 1746 hours on 12/2/02, operators began a normal reactor shutdown. At 1900 hours on 12/2/02, EDG 102 was returned to service and the Action statement requiring a shutdown within ten hours was exited. On 12/03/02, at 1248 hours, RPS Bus 12 was returned to UPS 172. Troubleshooting determined that the UPS 172 trip was the result of an actuation of overvoltage protective relay RLY-(PRC172)59-1. The overvoltage signal was determined to have been invalid and caused by set point drift. The set point drift was the result of degraded electrolytic capacitors in power supply PWRS-(PRC172)PS-1. The apparent cause of this event is design inadequacy, in that a single degraded power supply would trip UPS Bus 172. Contributing to this event were degraded electrolytic capacitors associated with the power supply. A loss of electrolyte had degraded the capacitors. Corrective actions include replacing the failed power supply, conducting a failure analysis on the failed power supply, and developing a modification to preclude loss of a RPS Bus due to a single degraded power supply. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(B) in that neither RPS Bus had its emergency power supply operable.
2372002001 | Dresden 2 | 01/18/2002 | 03/19/2002 | ML02091064 | <strong>Unit 2 Isolation Condenser Time Delay Relay Surveillance Failures Due to Setpoint Tolerances Specified with No Margin</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2002, at 2135 hours, during the performance of quarterly Technical Specification (TS) surveillance procedure, DIS 1300-01, "Sustained High Reactor Pressure Calibration", Revision 12, three of the four Isolation Condenser (IC) [BL] time delay relays were found to exceed their TS Allowable Values (AV). The TS AV is </= 15 seconds. The as-found values of the relays were found to be at 15.6 seconds, 15.4 seconds, 15.4 seconds, 14.8 seconds for relays 2-595-117A, 2-595-117B, 2-595-117C and 2-595-117D, respectively. The root cause was determined to be an inadequate setpoint calculation. This calculation allowed the settings to remain at the Technical Specification limit, which did not allow margin for drift. As a result, the IC automatic initiation circuitry would have been delayed by 0.4 seconds. A review of the General Electric (GE) analysis for IC initiation indicated significant safety margin. Evaluation of the actual pressure setpoints determined that the IC would have automatically initiated and provided its safety function for any time delay relay setting below 24.4 seconds. Safety function would have been delayed, not lost. Therefore, the safety significance of this event is minimal.
2372002002 | Dresden 2, Dresden 3 | 04/10/2002 | 06/10/2002 | ML02171011 | <strong>Smoke Purge Mode Operation Prevents Safety Function of the Control Room Emergency Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2002, at approximately 1835 hours, control room personnel received the "CTRL ROOM HVAC FIRE PANEL TROUBLE" annunciator. Additionally, as a result of the alarmed condition, the control room heating ventilation and air conditioning (HVAC) system automatically realigned from its normal mode of operation to the smoke purge mode. Operations personnel were dispatched to the local alarm panel to determine the cause of the alarm condition. The local panel indicated that smoke had been detected in the control room return air ductwork. A walkdown of potential areas was immediately performed. There was no observed indication of smoke or fire. The smoke purge mode of operation aligns the control room HVAC system to provide 100 percent outside air to remove smoke from the control room area. The initiation was not capable of being immediately reset. The approximate flow rate of air is 20,000 scfm, which would render the control room emergency air filtration unit incapable of mitigating the control room dose expected during an accident. Plant personnel investigated the possible causes of the initiation. At approximately 2144 hours, the smoke purge mode was reset and the control HVAC system was realigned to its normal mode of operation. The root cause was determined to be a knowledge deficiency during the design of the "B" train Control Room Emergency Ventilation System (CREVS) installed in 1982 for control room habitability. A modification will be implemented to change the automatic initiation to a manual initiation. A sampling of plant modifications that were completed during this period will be performed to ensure that generic implications are addressed. This condition did not increase the frequency of an occurrence, which would have required the CREVS to be placed in service. Therefore probability of an occurrence concurrent with the smoke purge operation is low. At no time did this condition compromise the health and safety of the public. This condition has minimal safety significance.
2372002003 | Dresden 2, Dresden 3 | 05/09/2002 | 07/08/2002 | ML02197057 | <strong>Manual Valve Failures Prevent the Cooling Water Flow to Control Room Refrigeration Condensing Unit</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2002, while performing the monthly surveillance requirement for the control room heating, ventilation and air conditioning (HVAC) system, the refrigeration condensing unit (RCU) compressor tripped due to high discharge pressure. A review of the system operating parameters by Operations determined that there was no cooling water flow through the RCU heat exchanger. Troubleshooting of the system determined that the disk from manual valve 2/3-3999-334 (inlet) was separated from the stem and became stuck in the closed position preventing any cooling flow to the Control Room Train B HVAC RCU heat exchanger. Additional investigation determined that manual valve 2/3-3999-332 (outlet) was also found separated from stem but did not block the flowpath. The failed disks of the valves were evaluated and found to be corroded over the entire surfaces. The cause of this event was determined to be a combination of using carbon steel material and frequently exercising the valves in a Service Water environment. Frequent exercising of the valves caused the protective corrosion layer on the ears to be removed, which accelerated the rate of corrosion. The valve internals were removed in accordance with a temporary modification, which allows flow to the heat exchanger. The valves will be replaced with stainless steel valves. The non-safety related Control Room HVAC System "A" Train was available and started during the unavailability of the "B" Train HVAC System RCU. The heat removal capability of the "A" Train System is equivalent to the "B" Train. At no time did this condition compromise the health and safety of the public.
2372002004 | Dresden 2, Dresden 3 | 05/31/2002 | 07/30/2002 | ML02219038 | <strong>Control Room Ventilation Ductwork Breached During Replacement of Temperature Transmitter</strong><br /><i>Abstract:&nbsp;</i>On May 28 2002, instrument maintenance (IM) personnel were performing a calibration of the main control room heating ventilation and air conditioning (HVAC) supply air temperature instrumentation. During the performance of the calibration, it was determined that the temperature transmitter had failed. The transmitter was located in the control room supply air duct. A work order was generated to replace the failed temperature transmitter. On May 31, 2002, maintenance personnel proceeded to replace the failed transmitter. A supply duct access door was opened to replace the transmitter. The opening of this access door resulted in the control room ventilation system being inoperable. The root cause of the event was determined to be ineffective change management during the implementation of the plant barrier control program, which resulted in a knowledge deficiency. The access door was sealed and smoked tested. The model work order was revised to include a caution related to the impairment of the control room boundary. Additionally, a walkdown was performed, to identify additional access doors that may require signs. Signs were placed in the area to make individuals aware of the risk to the control room HVAC system. Maintenance work planners will be trained on the use of the barrier control program procedure. The control room envelope was breached for approximately 20 minutes. During this time there were no movement of irradiated fuel nor was there a potential to drain the vessel. Due to the short period of time that the access door was open, the probability of an occurrence which would have required the initiation of the Control Room Emergency Ventilation system was low. At no time did this condition compromise the health and safety of the public.
2372002005 | Dresden 2 | 06/04/2002 | 08/02/2002 | ML02220045 | <strong>Pressure Switches Found Above Technical Specification Allowable Values</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2002, the Instrument Maintenance Department (IMD) began performance of monthly calibration surveillance for the pressure switches associated with reactor pressure vessel relief valves. During the performance of the surveillance IMD discovered that the pressure switch setpoint for valve 2-203-3A (as found at 1134.6 psig) exceeded the Technical Specification (TS) Allowable Value (AV) of < / = 1133.5 psig. The pressure switch was readjusted to within as left tolerances per station procedure. Following calibration of the pressure switch for valve 2-203-3A, IMD began the calibration for pressure switch associated with valve 2-203-3B and discovered that the pressure switch setpoint (as found at 1110.6 psig) exceeded the TS AV of < / = 1110.5 psig. The pressure switch was readjusted to within as left tolerances per station procedure. The remaining three pressure switches were tested and found to be within the TS required AV. The cause of this event was determined to be deficient procedural instruction. A review was performed on all Technical Specification related instrument maintenance procedures that test Bourdon Tube sensor type pressure switches and the identified instrument maintenance station procedures were revised to maintain operating pressure at the pressure switch during the performance of the surveillance. The as-found condition of the two (2) pressure switches would have resulted in a slight delay in the opening of their associated reactor pressure vessel relief valves. The as-found pressures for valve 2-203-3A and 2-203-3B were 1.1 and 0.1 psig higher than their associated TS AV, respectively. Therefore, no failure of the valves actually occurred. Both valves would have operated to mitigate reactor pressurization events. Additionally, the reactor pressure vessel safety valves were operable at the time of this occurrence to aid in the mitigation of pressure transients. At no time did this condition compromise the health and safety of the public.
2442002001 | Ginna | 02/05/2002 | 03/29/2002 | ML03155036 | <strong>Loss of "A" Condenser Circulating Water Pump Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2002, at approximately 0911 EST, with the plant in Mode 1 at approximately 100% steady state reactor power, the "A" condenser circulating water pump tripped. The Control Room operators entered Abnormal Operating Procedure AP-CW.1 for loss of the circulating water pump. At approximately 0912 EST, following procedural direction, the reactor was manually tripped. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all safety systems operated as designed, and the reactor was stabilized in Mode 3. The tripping of the "A" condenser circulating water pump was caused by the failure of a pump motor field wire. The circulating water pump motors are synchronous motors. When the wire failed, motor field current was lost and the motor was tripped by its power factor relay protection. The field wire failure was preceded by the failure of a constant voltage transformer in the motor excitation circuit.
2442002002 | Ginna | 11/08/2002 | 12/20/2002 | ML03014039 | <strong>Small Breach in Ventilation System Results in Potentially Not Being Able to Mitigate the Consequences of an Accident</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2002, the plant was in Mode 1 at approximately 100% steady state reactor power. At approximately 0905 EST, it was discovered that there was a small breach in a flexible connection at the inlet of the Control Room HVAC system (system VI) Return Air Fan (AKF08). The plant entered Technical Specification Limiting Condition for Operation 3.0.3 for approximately 40 minutes while temporary repairs were made. It was determined that the small breach in the flexible connection could have caused an in-leakage into the Control Room greater than that assumed in the accident analysis. This was reported to the NRC within eight hours of the determination per 10 CFR 50.72(b)(3)(v)(D). The cause of the small breach was a partial failure of a flexible connection. Corrective action to prevent recurrence is listed in Section V.B.
2472002001 | Indian Point 2 | 01/06/2002 | 03/01/2002 | ML02072002 | <strong>While Preparing for Maintenance Activities Personnel Error Results in Two Emergency Diesel Generators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2002, at approximately 1730 hours, while performing an independent verification of tagging operations prior to planned maintenance activities on 23 Emergency Diesel Generator (EDG)[EIIS:EK], an individual performing the verification mistakenly actuated the overspeed trip lever for 21EDG. This condition resulted in the unavailability of both 21 and 23EDGs, and placed the plant in a shutdown action statement per Technical Specification 3.0.1. The individual immediately recognized the error, and initiated corrective actions to restore 21EDG to operable condition. 21EDG was returned to service in less than five minutes, and the action statement of Technical Specification 3.0.1 was subsequently exited. At the time, the plant was at 100 percent power, and normal offsite power feeders were available. No injuries to plant personnel, damage to any equipment, or adverse safety implications to the public occurred as a result of this event. The EDG system is designed such that any two of the three dedicated power trains are capable of supplying the minimum engineered safety features loads, assuming the single failure of one power train or EDG. This report is submitted pursuant to 10 CFR 50.73 (a) (2) (v) as a condition that alone could have prevented the fulfillment of the safety function of a structure or system needed to mitigate the consequences of an accident, and 10 CFR 50.73 (a) (2)(ii) as a condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety.
2472002002 | Indian Point 2 | 06/08/2002 | 08/07/2002 | ML02221036 | <strong>Restoration of Previously Isolated Portion of Weld Channel and Containment Penetration Pressurization System</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2002, at approximately 0530 hours, a previously determined inoperable and retired portion of the Weld Channel and Containment Penetration Pressurization System (WCCPPS)[EIIS:BD], Zone W-11, was determined to be operable following the completion of an engineering investigation. The WCCPPS provides a means for determining the leak tightness of the containment by continuously pressurizing the positive pressure zones incorporated into the containment penetrations, the channels over the welds in the steel liner, and certain containment isolation valves. Indian Point 2 Technical Specification 3.3.D.2.c. states, "With the portion of the WC & PPS inoperable, and it is determined that it is not repairable by any practicable means, then that portion may be disconnected from the system." Contrary to this requirement, it was determined that from March 2000 to June 2002, Zone W-11 was not appropriately retired. This report is submitted pursuant to 10 CFR 50.73 (a) (2)(i) (B) as any operation or condition, which is prohibited by the plant's Technical Specifications. At the time of discovery, the plant was at 100 percent power. No injuries to plant personnel, damage to any equipment, or adverse safety implications to the public occurred as a result of this event.
2472002003 | Indian Point 2 | 07/19/2002 | 10/11/2002 | ML02289008 | <strong>138 KV Ground Protection Trip Results in Auto Start of Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On July 19, 2002, at approximately 1413 hours, a loss of the Indian Point Unit 2 Buchanan 138-kV offsite power source [EIIS:FK] occurred due to the actuation of ground protection controls for the 138/6.9-kV station auxiliary transformer. This 138-kV source is the preferred offsite supply to 6.9-kV Buses 5 and 6. As a result, engineered safety feature (ESF) 480-V Buses 5A and 6A and associated required safeguards equipment became de-energized. Per Technical Specification 3.7.B.3, plant operation may continue for 24 hours if the entire 138-kV source of power is lost provided all three (3) emergency diesel generators (EDG) [EIIS:EK] are operable. As designed, all three EDGs received an automatic start signal. However prior to this, 21 EDG had been declared inoperable in preparation for maintenance activities. At 1429 hours, operations personnel restored 21 EDG to operable status and re-energized Buses 5A and 6A by closing the output breakers from 21 and 23 EDGs. This report is submitted pursuant to 10 CFR 50.73 (a) (2)(iv) (A) as an event or condition that resulted in a manual or automatic actuation of an emergency AC electric power system. At the time of the event, the plant was at 100 percent power. No damage to any equipment, or adverse safety implications to the public occurred as a result of this event. A contract worker fatality occurred as a result of the grounding of a conductor on the 138-kV feeder.
2472002005 | Indian Point 2 | 10/08/2002 | 12/06/2002 | ML02345008 | <strong>Central Control Room Wall Identified as Being in Non-Conformance with Design Drawings</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2002, an operability assessment of the Indian Point Unit 2 Central Control Room (CCR) south wall determined that in the event of a postulated design basis earthquake, the wall would be subjected to excessive differential building motion. The as-found condition of the wall was identified as being in non-conformance with existing design drawings. During a seismic event, this condition could result in cracking of the wall and a potential breach of the CCR envelope, preventing the Control Room Air Filtration System [EIIS:VI] from performing its design function of limiting dose to the operators. This condition was discovered during an ongoing extent of condition review of masonry wall design deficiencies. Indian Point Unit 2 Technical Specification 3.3.H.1 states that, "The control room air filtration system shall be operable at all times when containment integrity is required." Furthermore, Technical Specification 3.3.H.2 states, "From the date that the control room air filtration system becomes and remains inoperable for any reason, operations requiring containment integrity are permissible only during the succeeding 3.5 days." In accordance with Technical Specification 3.3.H.2, on October 8, at approximately 1330 hours, the control room air filtration system was declared inoperable, and the limiting condition of operation was entered in order to implement corrective actions. On October 9, at approximately 1320 hours, upon completion of the necessary actions, the limiting condition of operation was exited. At the time of discovery, the plant was at 100 percent power. No injuries to plant personnel, damage to any equipment, or adverse safety implications to the public occurred as a result of this event.
2472002006 | Indian Point 2 | 10/09/2002 | 12/04/2002 | ML02344002 | <strong>Two of Three Emergency Diesel Generators Inoperable Due to Component Failures; a Condition Prohibited by Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2002, at 1518 hours, a controlled shutdown commenced per Technical Specification (TS) 3.0.1. TS 3.0.1 was entered because Emergency Diesel Generators (EDG) 21 and 23 were declared inoperable. EDG 23 was declared inoperable on October 8, 2002, at 2152 hours, due to a failure of monthly surveillance test PT-1121C. EDG 23 failed the test due to unexpected load swings. Testing of the remaining EDGs per TS identified that EDG 21 had jacket water in a cylinder leak-off line to the fuel oil drip tank. Thermograph inspection confirmed that EDG 21 had a cylinder breach and it was declared inoperable at 1359 hours. TS require three operable EDGs during power operation with a 7 day allowed outage time (ACT) for one inoperable EDG. As a result of two inoperable EDGs, TS 3.0.1 was entered. Reactor power was reduced to approximately 97% when at 1635 hours, EDG 23 was declared operable and TS 3.0.1 was exited. Potential causes of EDG 23 inoperability were identified but no specific cause could be determined. An Operability Determination concluded the 23 EDG was operable. The cause of EDG 21 inoperability was an internal defect to the 3L piston power head. Corrective actions included increased testing of the 23 EDG, and replacement of EDG 21 engine powerhead. The event had no effect on public health and safety.
2492002001 | Dresden 3 | 03/23/2002 | 05/22/2002 | ML02158030 | <strong>HPCI Not in Standby Operation when Required by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2002, at 1603 hours, during reactor startup from a Unit 3 maintenance outage (D3M09), the High Pressure Coolant Injection (HPCI) system was not aligned to standby conditions when reactor steam dome pressure exceeded 150 psig. Technical Specification 3.5.1 requires HPCI to be operable in Modes 1, 2 and 3 when reactor steam dome pressure is >/= 150 psig. Significant maintenance had been performed on the HPCI system during D3M09. This maintenance required the performance of the low pressure HPCI run to validate operability. The operating crew believed HPCI was not operable until the low-pressure run was completed. They also believed there was a 12-hour allowance for HPCI to be inoperable above 150 psig to perform this test. Based on this belief, Operations personnel allocated resources to other activities that were required to be completed prior to reaching the reactor conditions that would support the low-pressure HPCI test, thus the HPCI 3-2301-4 and 3-2301-5 valves (steam supply) were left closed in preparation for the low pressure run. The isolation valves would have opened upon receipt of an initiation signal and HPCI would have started. Additionally, Low Pressure Coolant Injection and Core Spray systems were in standby and would have injected upon receipt of an initiation signal. Therefore, the safety significance of this event is minimal.
2492002002 | Dresden 3 | 07/21/2002 | 09/19/2002 | ML02274048 | <strong>Reactor Scram Due to Main Shaft Oil Pump Failure</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2002, at 2033 hours Dresden Nuclear Power Station received an automatic reactor scram as the result of the main turbine tripping. The turbine trip was due to low discharge pressure from the turbine shaft bearing oil pump. Previous to the scram, on July 15, 2002, the turbine was taken off-line following identification of damage to the Permanent Magnet Generator (PMG). Following inspection of the PMG, the unit was returned to service on July 16, 2002. On July 21, 2002, low discharge pressure from the turbine shaft bearing oil pump caused the Unit 3 turbine to trip and consequently, a reactor scram occurred. The cause was determined to be the degradation of the auxiliary control rotor gear coupling insulation, resulting in current flow through the gear shafts which caused electrolysis and accelerated wear of the bearings. The corrective actions include revising turbine front standard procedures to include dismantling and inspection of the extension tube, inspecting and meggering the insulated coupling splines, and inspecting the front standard insulation kit per General Electric specifications. At no time did this condition compromise the health and safety of the public. The failure of the Main Shaft Oil Pump (MSOP) resulted in low turbine oil pressure, which initiated a turbine trip and reactor scram as designed. All safety systems functioned as designed following the reactor trip.
2492002003 | Dresden 3 | 10/08/2002 | 12/09/2002 | ML02352004 | <strong>Reactor Recirculation Loop A Sensing Line Socket Weld Vibration Fatigue Failure</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2002, at approximately 0421 hours, with power being reduced for refueling outage D3R17, an inspection of the Dresden Nuclear Power Station (DNPS) Unit 3 drywell was performed. The inspection of the drywell was performed due to an increase in unidentified leakage on September 14, 2002. The leakage had increased from 0.2 gpm to approximately 0.65 gpm. During the inspection, the leak was identified on a one inch diameter piping socket weld associated with the Reactor Recirculation (RR) "A" loop low pressure flow venturi differential pressure sensing line. A Unit 3 shutdown was performed as required by Technical Specifications for primary pressure boundary leakage. The root cause was attributed to an inadequate 1-1 axial leg socket weld (i.e. weld leg along the pipe side of the weld equal to the Code-required weld leg dimension) application in a system experiencing flow-induced vibration. The 1-1 axial leg socket weld was installed in 1985 as part of a major reactor recirculation piping replacement project. The weld was consistent with industry standards at the time of installation. Corrective actions include replacement of the Unit 3 RR Loop A high and low pressure venturi sensing line, elbows and piping with a bent pipe configuration with no elbows. In addition, the installation of 2-1 axial leg socket welds (i.e. weld leg along the pipe side of the weld equal to twice the Code-required weld leg dimension) was performed on both the 3A and 3B RR Loop venturi sensing lines.
2492002004 | Dresden 3 | 10/14/2002 | 12/13/2002 | ML02357031 | <strong>Main Steam Safety Valves Failed the Technical Specification As-Found Lift Setpoint</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2002, during Dresden Station Nuclear Power Station's Unit 3 refueling outage (D3R17), two Main Steam Safety Valves (MSSV) failed the Technical Specification lift setpoint Surveillance Requirement (SR) 3.4.3.1. The SR requires the valves to test within plus/minus one percent of the lift setpoint. The valves both lifted at minus 2.6 percent. Following testing, the valves were disassembled and inspected by NWS Technologies. Following disassembly, no discrepancies were found that would account for the low setpoint lifts. A review of industry events and discussions with the manufacturer found this to be attributed to routine drift. Setpoint drift of as much as three percent without any mechanical failures is normal throughout the industry. The root cause of this event has been determined to be setpoint drift. The setpoint drift can be attributed to the inherent characteristics of the valve hardware in conjunction with heating/cooling cycles and the vibration on the valves during service. Corrective action to prevent recurrence is to expand the Technical Specification setpoint tolerance for Main Steam Safety Valves. The event did not affect the safe operation of the plant or the health and safety of the public. The two MSSVs addressed in this report both lifted below the setpoint specified in the Technical Specifications. The MSSVs provide overpressure protection during the most severe pressurization transient. The safety significance of this event is minimal, since the MSSVs lifting below the setpoint would not have prevented the valves from performing their overpressure protection function should they have been required to perform this safety function.
2492002005 | Dresden 3 | 07/05/2001 | 02/14/2003 | ML03059024 | <strong>High Pressure Coolant Injection System Inoperable Due to Water Hammer Event</strong><br /><i>Abstract:&nbsp;</i>On July 19, 2001, Dresden Nuclear Power Station (DNPS) personnel identified a Unit 3 High Pressure Coolant Injection (HPCI) discharge piping support in a degraded condition. An operability determination was performed, which supported continued HPCI operability. Due to perceived low safety significance, the damaged support was not immediately repaired. Corrective actions were to restore the supports during the next scheduled maintenance window. A review of Transient Analysis Display System (TADS) data made it apparent that a hydrodynamic transient/water hammer had occurred on July 5, 2001, during an automatic initiation of the Unit 3 HPCI system. The hydrodynamic transient/water hammer event was the result of a combination of air pockets and steam voids in the discharge piping, which resulted from inadequate venting of the system. The support was repaired and the discharge piping vented on September 30, 2001. On November 16, 2001, the Nuclear Regulatory Commission (NRC) issued an Inspection Report which identified an Unresolved Item associated with the operability of the HPCI system with the degraded support. In January 2002, DNPS provided engineering analysis to the NRC and in June of 2002, the NRC transmitted a Request for Additional Information associated with the analysis. These questions were discussed in a meeting on July 25, 2002, and in subsequent teleconferences between members of Exelon and NRC. In response to these questions, DNPS performed additional evaluations. Subsequently, DNPS has been unable to demonstrate through analysis that the Unit 3 HPCI piping and supports would have met operability evaluation acceptance criteria following an additional automatic initiation. On October 4, 2002, DNPS concluded that the Unit 3 HPCI system was inoperable for the period following the hydrodynamic transient/water hammer on July 5, 2001, until September 30, 2001.
2492002006 | Dresden 3 | 12/07/2002 | 02/05/2003 | ML03043037 | <strong>Reactor Recirculation Loop "A" Sensing Line Socket Weld Failure</strong><br /><i>Abstract:&nbsp;</i>On December 07, 2002, at approximately 0635 hours, with power being reduced to investigate previously detected and monitored elevated drywell unidentified leakage, an inspection of the Dresden Nuclear Power Station (DNPS) Unit 3 drywell was performed. During the inspection, the leak was identified on a one inch diameter piping socket weld associated with the Reactor Recirculation (RR) "A" loop low pressure flow venturi differential pressure sensing line. A Unit 3 shutdown was completed as required by Technical Specifications for primary pressure boundary leakage. The root cause was attributed to mechanically induced residual pipe stresses due to the installation techniques performed on the reactor recirculation sensing line repair during the October 2002, Unit 3 refueling outage (D3R17) coupled with sensing line vibration, caused by resonance frequency with the RR pump speed. Corrective actions include minimizing the welding induced residual stresses by enhanced fit-up process and minimizing the mechanically induced stresses by proper tie-back support alignment in the repaired sensing line. An exclusion zone and action level values were established to minimize reactor recirculation pump speed in the area of the resonance frequency of the piping based upon a vibration monitoring plan implemented to monitor and document the RR Loop A low pressure and RR Loop B high pressure sensing line vibrations. A piping configuration modification will be installed to improve the vibration response characteristics of the Unit 3 RR Loop A and Loop B high and low pressure sensing lines.
2502002001 | Turkey Point 3 | 06/05/2002 | 08/01/2002 | ML02224014 | <strong>Vital Battery Cell Voltage Below Technical Specification Allowable</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2002, with the unit operating at approximately 100% reactor power, a quarterly surveillance performed under Technical Specification 4.8.2. l.b recorded a 3A vital battery individual cell voltage that was below the Technical Specification allowable value. This condition was recognized during a review of the quarterly surveillance test results by an Electrical Maintenance Supervisor at 1340 on June 17, 2002. This was reported immediately to the Nuclear Plant Supervisor and the 3A battery was declared inoperable. Operation of the unit with an inoperable vital battery for more than two hours is prohibited by Technical Specification 3.8.2.1. Since the condition existed for a longer time than permitted by Technical Specification action statement 3.8.2.1.b, the plant entered TS 3.0.3 and completed the required recovery actions within the time allowed by Technical Specification 3.0.3. The spare battery was placed in service on June 17, 2002 at 1423 and Technical Specification 3.0.3 was exited. This event is reported per the requirements of 10CFR50.73(a)(2)(i)(B). The cause of this event was a small internal short circuit, causing a low voltage condition on one vital battery cell. Contributing causes were personnel error and inadequate procedures for identifying the Technical Specification impact of the failed surveillance. Corrective actions include personnel training and revisions to surveillance procedural guidance.
2502002002 | Turkey Point 3 | 08/02/2002 | 10/01/2002 | ML02282038 | <strong>Operation with One Component Cooling Water Pump in Excess of Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On 8/02/02, Turkey Point Unit 3 was operating at 100% power. At 8:28, the 3A Component Cooling Water (CCW) pump [CC:P] was declared out of service to allow Electrical Maintenance to replace its 4.16 kV [EA:52] breaker with a refurbished breaker. Operations entered Technical Specifications (TS) 3.7.2, Action b., which allows operation for 72 hours with one CCW pump operable or two CCW pumps operable but not from independent power supplies. After breaker replacement, Operations started the 3A CCW pump, declared it operable at 12:45 and exited the TS action statement. On 8/04/02, the 3A CCW pump was stopped as part of periodic Inservice testing. On 8/06/02 at 3:25, Operations attempted to start the 3A CCW pump, but the refurbished breaker failed to close due to an improper breaker/cubicle interface setup and the vibrational shock of the first breaker closing action. As such, there was no operable 3A train CCW pump available from 8/02/02 at 8:28 until 8/06/02 at 12:43 (i.e., 100 hours and 15 minutes), when the 3C CCW swing pump was aligned to the 3A train. The Unit 3 CCW system did not comply with TS 3.7.2, Action b., and is reported herein under 10CFR50.73 (a)(2)(i)(B). The cause for this event was lack of specific procedural guidance in breaker/cubicle interface. Corrective actions include revising procedures/work instructions to add detailed checks of the breaker/cubicle interfaces and training Maintenance and Operations personnel.
2542002001 | Quad Cities 1 | 01/09/2002 | 03/11/2002 | ML02085067 | <strong>Reactor Shutdown Due to Failure of Reactor Recirculation Jet Pump</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2002, at 1416 hours, with the reactor at 100% power, Quad Cities Nuclear Power Station Unit 1 jet pump #20 hold-down beam failed, causing a trip of the "B" recirculation pump motor and a high main steamline (MSL) radiation alarm. Per Technical Specifications, the reactor was taken to Mode 3 (shutdown). The preliminary root cause of the failure of the jet pump #20 hold-down beam was intergranular stress corrosion cracking in the transition portion of the beam. The "B" recirculation pump motor tripped due to the introduction into the recirculation pump impeller of a piece of the failed beam. The MSL high radiation alarm was due to the changes in flow dynamics and mixing in the annulus region of the vessel due to the jet pump failure, which caused increased carryover of Nitrogen-16 into the MSLs. The safety significance of this event was minimal. All emergency core cooling systems were operable during this event. The failure of the jet pump was readily detected from diverse plant parameters displayed in the control room, and the reactor was shut down within eight hours of initial indications. Corrective actions included replacing all of the original-style BWR/3 jet pump hold-down beams with BWR/4 beams on Units 1 and 2, replacing the "B" recirculation pump impeller and repairing jet pump #20.
2542002002 | Quad Cities 1 | 11/13/2002 | 01/13/2003 | ML03023047 | <strong>Automatic Initiation and Loading of Emergency Diesel Generator Due to Loss of Voltage to Emergency Bus as a Result of Door to Potential Fuse Drawer Falling Open</strong><br /><i>Abstract:&nbsp;</i>On November 13, 2002, at 0458 hours, with Unit 1 in Refuel Mode, the Unit 1 Division II Emergency Diesel Generator (EDG) started automatically and loaded to the emergency bus (Bus 14-1) in response to a loss of voltage on the bus. This occurred when the door for the Bus 14-1 potential fuse drawer opened, which caused a sensed loss of voltage, the opening of the feed breakers, and the resulting actual loss of voltage to Bus 14-1. It was determined that the door to the potential fuse drawer had not been completely latched. The root cause was a lack of awareness of the vulnerability of the door locking mechanism. Immediate corrective actions included closing the door and verifying other potential fuse drawer doors were latched. One other door at the bus that feeds Bus 14-1 (Bus 14) was identified as being closed but not fully latched. The safety significance was minimal in that both unlatched doors were on Unit 1 Division II. The Division I Emergency Bus and EDG were not affected by this issue. Corrective actions include training, development of a checklist for ensuring the doors are latched, and placement of a warning placard on each door.
2552002001 | Palisades | 11/12/2002 | 12/19/2002 | ML02361018 | <strong>Noncompliance with Technical Specification Requirements for Safety Injection Tank T-82D</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2002, at approximately 1339 hours, with the plant operating at 100% power, operations noted apparent leakage from safety injection tank T-82D via trending of multiple plant parameters. Subsequently, non-isolable leakage from safety injection tank T-82D was observed visually. Safety injection tank T-82D was declared inoperable at 1345 hours on November 11, 2002. Nuclear Management Company, LLC requested enforcement discretion to extend the completion time for Technical Specification 3.5.1, Condition B, by 24 hours, for a total of 48 hours, to allow for restoration of safety injection tank T-82D to operable status. The Nuclear Regulatory Commission verbally exercised discretion at 1332 hours on November 12, 2002. Nuclear Management Company reduced plant power to approximately 60% and performed the required repairs to safety injection tank T-82D, which was subsequently declared operable at 0906 on November 13, 2002. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, since safety injection tank T-82D was not restored to operable status within the 24 hours allowed by Technical Specification 3.5.1, Condition B.
2552002002 | Palisades | 12/01/2002 | 01/21/2003 | ML03030034 | <strong>Automatic Reactor Trip and Safety System Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2002, at approximately 2154 hours, with the plant operating at 100% power, an automatic reactor trip occurred on main generator loss of load. The loss of load occurred when a transmission tower's static line hanger failed, allowing one of two static lines to contact a 345 KV transmission line, tripping the main generator. The static line also contacted the rear bus in the switchyard that supplies the plant non-1E 4160 volt startup transformers. The rear bus tripped on a fault-to-ground causing a loss of non-1E 4160 volt AC buses. Consequently, both main feedwater pumps tripped, and the auxiliary feedwater system started automatically on low steam generator level, as expected. The plant was maintained at or near normal operating pressure and temperature subsequent to the trip, on natural circulation, since startup power for primary coolant pumps was also lost. The plant was returned to service on December 5, 2002. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an automatic reactor trip and automatic actuation of the auxiliary feedwater system.
2552002003 | Palisades | 12/21/2002 | 02/19/2003 | ML03059025 | <strong>Inoperable Containment Hydrogen Monitors</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2002, it was discovered during surveillance testing, that the pipe caps for two test taps on the right channel containment hydrogen monitor instrument lines were not installed. The open test taps rendered the right channel containment hydrogen monitor inoperable. The right channel containment hydrogen monitor is believed to have been in this condition for approximately 20 months, exceeding the 30-day completion time of Technical Specification 3.3.7.A for restoring an inoperable channel of containment hydrogen monitoring to operable status. A review of the status of the left channel containment hydrogen monitor during the 20-month period that the right channel was inoperable revealed one occasion, in November 2002, during which the left channel was inoperable for approximately 9 days, exceeding the 72-hour completion time of Technical Specification 3.3.7.D for restoring one of two channels of containment hydrogen monitoring to operable status. Upon discovery, the test tap pipe caps were reinstalled and the right channel containment hydrogen monitor was declared operable. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2602002001 | Browns Ferry 2 | 05/28/2002 | 07/25/2002 | ML02213056 | <strong>Rod Block Monitoring Calibration Error Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2002, Instrument Maintenance was scheduled to perform a surveillance requirement (SR) to calibrate the Unit 2 Rod Block Monitor (RBM) channel B. A prerequisite step in the procedure required the "applicable Operating Limit Minimum Critical Power Ratio (OLMCPR)" be provided by Reactor Engineering. Test personnel contacted the on-call reactor engineer, stated the RBM calibration procedure was being performed, and the OLMCPR value was needed. The on-call reactor engineer provided the OLMCPR value for the current plant operating conditions rather than the RBM setpoint basis OLMCPR value specified in the Core Operating Limits Report. This value was provided to the test performers and was used to calibrate the RBM Channel B. Two days later a similar error was made while calibrating RBM Channel A. On May 28 Maintenance and Reactor Engineering personnel recognized the errors during post-work in-shop reviews. The RBM channels were declared inoperable and required TS actions taken. The RBM channels were then correctly calibrated. The root cause of this event was procedural inadequacy. Corrective actions included correctly calibrating the RBM channels, revising surveillance procedures, and briefing Instrument Maintenance, Reactor Engineering, and Operations personnel.
2602002002 | Browns Ferry 2 | 07/27/2002 | 09/25/2002 | ML02276006 | <strong>Automatic Scram Resulting from Main Bank Transformer Bushing Fault</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2002, a Unit 2 main generator trip, main turbine trip, and reactor scram occurred from 100% power. All expected system responses were received, including the automatic opening of four safety-relief valves. Actuation of primary containment isolation system groups 2, 3, 6, and 8 occurred due to the expected temporary lowering of reactor water level. This logic isolates shutdown cooling (if in service), isolates the reactor water cleanup system, isolates the normal reactor building ventilation, initiates the standby gas treatment and the control room emergency ventilation systems, and retracts traversing incore probes (if inserted). The normal heat rejection path for the reactor remained in service. Reactor water level was recovered to the normal operating range by the normal reactor water level control system. Neither the high pressure coolant injection nor reactor core isolation cooling systems were used during this event. The generator tripped due to a ground fault on a main bank transformer bushing, which occurred due to thermal degradation of the paper insulation of the bushing’s internal condenser. Corrective actions included replacement of all of the low-side bushings on the transformer and increased monitoring of generator neutral resistor voltage trends. All new bushings will be installed on Unit 2 and Unit 3 main bank transformers. TVA will re-evaluate the criteria used in determining bushing condenser replacement intervals, and the bushing maintenance practices will be revised accordingly.
2602002003 | Browns Ferry 2, Browns Ferry 3 | 11/22/2002 | 01/21/2003 | ML03031023 | <strong>Non-Conservative Oscillation Power Range Monitoring Tmin Specification for Unit 2 and Unit 3</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2002, General Electric (GE) notified TVA of a 10 CFR Part 21 condition potentially affecting Browns Ferry (BFN) related to the use of a non-conservative Tmin value in the Oscillation Power Range Monitor (OPRM) system algorithm. TVA confirmed that the condition was applicable to BFN. At 1630 hours Central Standard Time on November 22, the OPRM upscale trip function was declared inoperable on Unit 2 and Unit 3. Technical Specifications Limiting Condition for Operation 3.3.1.1 Condition I was entered, and Required Action I.1 was taken to initiate within 12 hours an alternate method to detect and suppress thermal-hydraulic instability oscillations. The root cause of this event was a flawed original GE design of the OPRM system algorithm. Interim corrective actions have been implemented to establish manual methods for detection and suppression of instability. BFN will monitor the actions of GE and the Boiling Water Reactor Owners’ Group (BWROG) Detect and Suppress Committee Option III design reviews and recommendations to determine what corrective actions are required to resolve the OPRM problems identified in the November 22, 2002 10 CFR 21 notification.
2612002001 | Robinson 2 | 10/09/2002 | 12/09/2002 | ML02346017 | <strong>Four Main Steam Safety Valves Fail to Meet Acceptance Criteria During Lift Pressure Testing</strong><br /><i>Abstract:&nbsp;</i>During testing of the Main Steam Safety Valves (MSSVs) on October 9 and 10, 2002, it was determined that four of the 12 MSSVs had as-found lift pressures that exceeded the Technical Specifications (TS) tolerance of +/-3%. The four valves' as-found lift pressures were over TS lift pressures by the following amounts: SV1-1A was 3.1% over, SV1-2B was 4.1% over, SV-1C was 3.8% over, and SV1-2C was 6.9% over. A condition report (number 73940) was initiated and the corrective action program significant adverse condition investigation has been completed. The root cause of the high lift pressures was attributed to mechanical component failure/degradation based on slight binding of the spindle on the guide bearing. The corrective actions for this event included maintenance on the MSSVs and post-maintenance testing as required for the maintenance performed. This condition was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B)as a condition prohibited by the plant's TS, based on guidance contained in NUREG-1022,"Event Reporting Guidelines 10 CFR 50.72 and 50.73" Revision 2.
2632002001 | Monticello | 01/21/2002 | 05/03/2002 | ML02161009 | <strong>Mechanical Pressure Regulator Failure Causes Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>While operating at 100% power at 1735 on January 21, 2002, a turbine control valve fast closure (load rejection) signal resulted in a reactor scram. All rods fully inserted and all safety systems functioned as designed. The primary cause of the scram was failure of the main turbine pressure control system. A detailed review of plant computer data revealed that the mechanical pressure regulator (MPR) had been behaving erratically for several days prior to the scram. This erratic behavior eventually caused the MPR to take control from the electric pressure regulator. This initiated rapid cycling of the turbine control and bypass valves which tripped both protection system sub channels on reduced hydraulic oil pressure at the control valve acceleration relay. Investigation determined that failure of the MPR was caused by a damaged rate feedback bellows. Following repair of the MPR, and completion of other unrelated maintenance, the unit was returned to service at 1327 on January 27, 2002.
2632002002 | Monticello | 02/13/2002 | 05/03/2002 | ML02161009 | <strong>Application of Instrument Deviation Acceptance Criteria Allowed As-Found Settings to be Outside Technical Specification Value</strong><br /><i>Abstract:&nbsp;</i>A Licensee Event Report is being submitted because it was identified that in the past, multiple instrument setpoints exceeded plant Technical Specifications (TS) during a given calibration period due to a common cause. The "cause or condition" is that the calibration procedure used the allowable deviation in the TS Bases to allow the as-found condition to exceed a TS trip setting. The condenser low vacuum scram instruments were found to have exceeded TS settings. The instrumentation was able to fulfill its safety related function.
2632002003 | Monticello | 03/22/2002 | 05/20/2002 | ML02161029 | <strong>Primary Containment Group 3 Isolation Signal on High Flow While Repressurizing Reactor Water Cleanup System Piping</strong><br /><i>Abstract:&nbsp;</i>While operating at 100% power at 1727 on March 22, 2002, an automatic Group 3 containment isolation signal was generated after sensing high Reactor Water Cleanup (RWCU) system flow. At the time, operations personnel were in the process of restoring the RWCU system to service following investigation of leakage associated with filter demineralizer isolation valves. The re-performance of the filling and venting portion of the restoration procedure was not performed, because personnel failed to realize that during the investigation process voids had been created within the system. When repressurizing the system, high flow rates resulted in actuation of the protection logic. Following resolution of these issues and completion of maintenance, the RWCU system was pressurized and returned to service at 0310 on March 24, 2002.
2632002004 | Monticello | 04/01/2002 | 05/29/2002 | ML02164077 | <strong>Unplanned Loss of Both Trains of Control Room Ventilation During Auto Start Testing Due to Timing Circuit Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2002 both trains of the Control Room Ventilation (CRV) System were found to be inoperable during annual low flow testing due to a timing circuit relay failure. The inoperability of both trains of CRV occurred when B train was made inoperable by procedure to simulate low system flow and test the auto start feature of A train. The A train failed to auto start in response to simulated low flow. In response, the control room operators manually started the A train of CRV. Within two hours, B train was returned to operable status. The affected train (CRV-A) was repaired in about 24 hours. The safety significance was minimal since one train was manually started when the failure to auto start was identified. No Limiting Conditions of Operation were violated as a result of the failure or subsequent actions.
2632002005 | Monticello | 07/22/2002 | 09/20/2002 | ML02275043 | <strong>Entered Unplanned LCO for Both CRV Trains Inoperable Due to Pressure Switch Drift</strong><br /><i>Abstract:&nbsp;</i>While performing an Emergency Service Water (ESW) Valve and Pump Test with the B-division Control Room Ventilation (CRV) Inoperable as required per procedure, the A-division CRV compressor tripped on low cooling water flow. The A-division CRV was declared inoperable, and the station entered Technical Specification (T.S.) 3.17.A.3, which contained an action statement to restore one CRV train to operable within 24 hours. The B-division CRV was returned to an operable status at 1701. Both divisions of CRV were inoperable for 31 minutes. The cause of the event was excessive drift of the differential pressure switch (DPS), DPS-4029A. When DPS-4029A drifted high, the A-division CRV compressor tripped on low service water flow and could not be restarted. The A-division switch was recalibrated and the A-division CRV was restored to an operable status in approximately 24 hours.
2632002006 | Monticello | 10/08/2002 | 12/06/2002 | ML02354039 | <strong>Surveillance Activity to Isolate Transmitter Prevents Fulfillment of Safety Function</strong><br /><i>Abstract:&nbsp;</i>During the review of Nuclear Instrument surveillances, plant personnel discovered that the current method of isolating the flow transmitter isolation valves for the Average Power Range Monitor (APRM) Recirculation Flow Instrumentation resulted in a condition that could momentarily prevented a flow bias scram signal in the trip system being tested. This event was the result of an incorrect procedure revision performed in 1992.
2632002007 | Monticello | 10/21/2002 | 12/19/2002 | ML02361032 | <strong>Application of Instrumentation Deviation Acceptance Criteria Allowed As-Found Settings for High-Drywell Pressure to be Outside Technical Specification Value</strong><br /><i>Abstract:&nbsp;</i>A During the quarterly surveillance 0003, Drywell High Pressure Scram and Group 2, 3, and Secondary Containment Isolation Test and Calibration Procedure, it was discovered that the as-found value for the B and C channels exceeded the Technical Specification (TS) limit for High Drywell Pressure. The instrumentation was able to fulfill its safety function. The channels were adjusted and verified to have as-left limits within TSs. The common cause or condition for both instrument channels is that the calibration procedure used the allowable deviation in the TS Bases to allow the as-found condition to exceed a TS trip setting.
2652002001 | Quad Cities 2 | 03/04/2002 | 05/22/2002 | ML02158030 | <strong>High Pressure Coolant injection System Uncoupled above 150 psig Due to Misapplication of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2002, at 1255 hours during a reactor startup, Unit 2 reactor pressure was increased above 150 psig with the High Pressure Coolant Injection turbine uncoupled from the pump. This put the unit in Technical Specification (TS) 3.5.1, condition F. This is a violation of TS 3.0.4, which does not allow entry into a specified condition of applicability while a Limiting Condition for operation is not met. HPCI was subsequently recoupled. The root cause of this event was that licensed personnel misapplied TS 3.5.1. As a contributing cause, the reactor startup procedural guidance was inadequate to ensure operable status of TS-required equipment when non-Mode conditions of applicability were entered. Corrective actions include changes to the reactor startup procedure and training concerning application of TS. The safety significance of this event was minimal. Reactor pressure did not get above approximately 160 psig until HPCI was recoupled, and the Reactor Core Isolation Cooling and Automatic Depressurization systems, as well as the low pressure Emergency.
2652002002 | Quad Cities 2 | 04/05/2002 | 06/03/2002 | ML02169017 | <strong>Manual Scram Due to Reactor Level Transient As a Result of a Digital Feedwater Level Control System Design Error</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2002, at 1028 hours, a manual scram was inserted on Unit 2 in response to increasing reactor level. The increase in reactor level was due to a blown fuse in the Digital Feedwater Level Control (DFWLC) system, caused by the inadvertent grounding of test leads during an instrument surveillance. Although the DFWLC logic is intended to be able to respond to a blown fuse without causing a level transient, the indicating fuse holder provided a circuit that inhibited recognition of the blown fuse by the DFWLC logic. The root cause of the Unit 2 reactor scram was a design deficiency involving the installation of indicating fuse holders. The inadvertent grounding of the test leads was a contributing cause. Also, although the operator actions were in accordance with procedure, different actions may have mitigated this event. The safety significance of this event was minimal. Adequate makeup to the vessel was available at all times from the feedwater system, as well as from the ECCS systems. Corrective actions include removal of the indicating fuse holders, actions to minimize the potential for grounding test leads, and review of the default operator actions for a level transient.
2652002003 | Quad Cities 2 | 07/11/2002 | 09/09/2002 | ML02261033 | <strong>Reactor Shutdown Due to Failure of Reactor Steam Dryer From Flow-Induced Vibrations as a Result of Extended Power Uprate</strong><br /><i>Abstract:&nbsp;</i>On July 11, 2002, at 0241 hours, Unit 2 plant personnel conservatively initiated a shutdown using Technical Specification (TS) Section 3.0.3. The reactor entered the shutdown mode (Mode 3) at 1417 hours. An operability assessment had previously been performed in response to indications of a damaged reactor steam dryer (initial indications started on June 7, 2002). TS 3.0.3 was conservatively entered when those indications changed such that, based on the analysis of the changed indications, reasonable assurance of continued operability of connected safety systems could no longer be supported. Following the unit shutdown, an inspection of the Unit 2 Reactor internals on July 13, 2002, revealed that a Steam Dryer cover plate had failed. Fragments were found in a Main Steam line and a Main Turbine stop valve inlet screen. The root cause of the steam dryer failure was determined to be a lack of industry experience and knowledge of flow-induced vibration dryer failures. The dryer failed as a result of fatigue caused by flow-induced vibrations created by higher steam flows due to Extended Power Uprate conditions. The safety significance of this event was minimal. Subsequent reviews determined all of the Unit 2 safety systems would have responded as designed had a design basis event occurred and that the entry into TS 3.0.3 was not a required entry. Therefore, this report is submitted as a voluntary report. Corrective actions include repair to the Unit 2 steam dryer and further evaluation of resonant frequency issues.
2652002004 | Quad Cities 2 | 08/02/2002 | 09/30/2002 | ML02283033 | <strong>Inadequate Separation in Both Trip Systems of the Scram Discharge Instrument Volume Input to the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On August 2, 2002, at 2015 hours, Unit 2 entered Technical Specification (TS) 3.3.1.1, Condition B, which requires one channel in one trip system of the Reactor Protection System (RPS) to be placed in trip within six hours. It had been determined that one channel of the Scram Discharge Instrument Volume (SDIV) RPS trip in each of the RPS trip systems was inoperable. A modification to replace the SDIV high level sensing instrument that had been installed in March of 2002 had also removed a relay that served as a separation point between the safety-related RPS input and the non-safety-related process computer input. Within the six hours, a temporary modification removing the computer input was in place and the unit exited Condition B of TS 3.3.1.1. The cause of the failure to identify the separation issue was a lack of technical rigor during the design process. Because one operable channel remained in each RPS trip system, the safety significance of this event was minimal. Corrective actions include training concerning identification of separation issues and reinstallation of the removed relay.
2652002005 | Quad Cities 2 | 10/07/2002 | 11/29/2002 | ML02344023 | <strong>Failure of Low-Pressure Coolant Injection Logic Test Due to a Detached Wire</strong><br /><i>Abstract:&nbsp;</i>October 7, 2002, at 1044 hours, a detached wire was found in a panel in the auxiliary equipment room as the result of a logic test failure. With the wire detached, one division of the Low Pressure Coolant Injection (LPCI) system would not have automatically started, and the flow from the other division may have been diverted from the reactor vessel. All pumps and valves could have been operated manually from the control room control panels and plant operators would have been able to restore required flow to the vessel. The detached wire was determined to be due to poor installation of the wiring and a lack of formal expectations concerning the inspection of equipment disturbed during work activities. Corrective actions include attaching the wire correctly and establishing and implementing expectations concerning the performance of inspections for electrical components and equipment following work activities.
2662002001 | Point Beach 1 | 08/16/2002 | 10/15/2002 | ML02303019 | <strong>Steam Generator Blowdown Valve Analyzed As Not Able to Close Against Full Differential Pressure</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2002, during the development of the new AOV evaluation and assessment program at Point Beach Nuclear Plant (PBNP), NMC Engineers determined that 1MS-5959, one of two steam generator (SG) blowdown isolation valves on Unit 1, may have been unable to shut with full differential pressure of 1085 psig across the valve. The new AOV evaluation and assessment program is used to determine whether the valve's performance will meet design basis functions under prescribed operating conditions. In this case, we evaluated that 1MS-5959 would not have shut under those conditions. Since this is a new evaluation method, it was not used when the valve was diagnostically tested in 1999. This condition was documented in the PBNP corrective action program as CAP029065. Interim action was taken to place the valve in the required shut position to ensure that minimum feed water flow requirements would be maintained in the event of a loss of normal feed water accident. Following diagnostic testing, adjustment of the spring closing force of this AOV, and successful completion of post maintenance testing, 1MS-5959 was restored to full operability, and Unit 1 "B" SG blowdown was restored. The remaining Unit 1 and 2 SG blowdown isolation valves at PBNP were evaluated and determined to be capable of shutting against the maximum differential pressure assumed within the calculation. This event is reportable as an unanalyzed condition that had the potential to significantly degrade plant safety. The safety assessment concluded that the overall safety significance of this event was low.
2662002002 | Point Beach 1 | 09/25/2002 | 11/22/2002 | ML02338012 | <strong>Unit 1 A-Train Reactor Protection Cable-Routed in B-Train Cable Trays</strong><br /><i>Abstract:&nbsp;</i>While completing a plant modification for rerouting of cables, NMC personnel identified an A-Train engineered safeguards features (ESF) actuation circuit installed in a B-Train cable tray. This circuit provides an A-Train SI actuation signal to the A-Train reactor protection system. The A-Train SI actuation signal is also routed to the B-Train reactor protection through a separate cable. This routing discrepancy has existed since original plant construction. This condition is being reported as a condition prohibited by the Technical Specifications. The other two Unit 1 cables associated with this unique cable scheme were routed correctly. The cable routing for Unit 2 was verified correct during the unit's Spring 2002 refueling outage. This cable routing discrepancy was corrected as part of the ongoing modification and completed during the Unit 1 Fall 2002 refueling and maintenance outage. A safety assessment concluded that this cable separation violation had no impact on the public health and safety and did not involve a safety system functional failure.
2662002003 | Point Beach 1, Point Beach 2 | 10/29/2002 | 10/10/2003 | ML03289011 | <strong>Possible Common Mode Failure of AFW Due to Partial Clogging of Recirculation Orifices</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2002, while conducting post maintenance testing of the P-38A motor driven auxiliary feedwater pump, recirculation flow was slightly reduced. Initial investigations discovered that the flow restricting orifice in the recirculation line from the pump discharge to the condensate storage tanks was partially restricted. Following engineering analyses and evaluations, NMC concluded on October 29, 2002, that the potential existed under specific conditions for a common mode failure mechanism to result in the plugging of the orifices in the recirculation lines for all four AFW pumps. This could result in the loss of safety function if the discharge from the AFW pumps were throttled and inadequate flow existed in the recirculation line to preclude pump failure due to overheating. An ENS notification was made on October 29, and interim compensatory measures consisting of crew briefings and information posting were completed which restored the AFW system to operable status. Additional actions Included temporary procedure changes and training for the operators. Laboratory testing of the orifice design concluded that the installed recirculation orifices were susceptible to clogging. A plant modification was completed that replaced the orifices with an improved design that is not susceptible to clogging. During the interval that these orifices were installed, there was no plant event which resulted in an actual failure of the AFW system.
2692002001 | Oconee 1, Oconee 2, Oconee 3 | 03/07/2002 | 05/06/2002 | ML02135046 | <strong>Pressurizer Heat Loss Exceeds Standby Shutdown Facility Powered Heater Capacity</strong><br /><i>Abstract:&nbsp;</i>On 03/07/2002 Site Engineering concluded that ambient heat losses from the Pressurizer (PZR) on all three Oconee units exceeded the capacity of PZR heaters powered from the Standby Shutdown Facility (SSF). Therefore, the ability to maintain a steam bubble in the PZR for system pressure control during SSF events (Fire, Flood, and Security) might be lost and the existing procedural guidance would not fully address some expected conditions. Normal system operation or other emergency scenarios were not affected because additional PZR heaters are available in those conditions. PZR heaters support operability of the SSF Auxiliary Service Water System (SSF ASW). Per Technical Specification 3.10.1, the SSF ASW was declared inoperable for all three Oconee units. Abnormal Procedures were subsequently revised to provide adequate guidance and all on-coming operators received simulator training on the new guidance prior to accepting shift duties. Additional corrective actions are planned. The apparent cause was a fundamental lack of appreciation for the potential impact of PZR insulation deficiencies. This event is considered to have no significance with respect to the health and safety of the public.
2692002002 | Oconee 1, Oconee 2, Oconee 3 | 03/22/2002 | 06/12/2002 | ML02172051 | <strong>Potential for Fire to Indirectly Damage Mitigation Component</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2002, with all three Oconee units operating in mode 1 at 100% Rated Power, an engineering evaluation identified the potential for an adverse valve actuation during a design basis fire. This valve actuation involves the inadvertent opening of either of two valves in the low pressure injection (LPI) system due to an assumed failure in the valve control circuitry. The opening of either valve would cause the Borated Water Storage Tank (BWST) to empty its contents to the Reactor Building Emergency Sump. The water from the BWST would flood the Reactor Coolant Make-Up (RCMU) Pump resulting in its failure. The RCMU pump supplies reactor coolant pump seal and make-up flow during some design basis fire scenarios. Roving fire watches have been implemented as compensatory measures in the area of the affected cables. These fire watches are required while the unit is in Modes 1, 2, or 3 and will remain in place until modifications are implemented to mitigate this condition. The apparent cause of this condition is a historic design deficiency. An engineering risk assessment concludes that the likelihood of the actual spurious actuation of these valves is extremely low. This event is considered to have minimal safety significance with respect to the health and safety of the public.
2692002003 | Oconee 1 | 04/01/2002 | 05/22/2002 | ML02157001 | <strong>Minor Reactor Pressure Vessel Head Leakage Due to Primary Water Stress Corrosion Cracking of An Alloy 600 Control Rod Drive Nozzle</strong><br /><i>Abstract:&nbsp;</i>Unit 1 entered its scheduled end-of-cycle 20 refueling outage on March 23, 2002. With the reactor vessel head (RVH) still installed on the vessel, a qualified visual inspection of the bare RVH was performed on March 24, 2002. From this visual inspection, two CRDM nozzle penetrations (Nos. 1 and 7) were identified with boron deposits on the CRDM tube. In accordance with Duke's response to NRC Bulletin 2001-01, both nozzles were categorized as masked and required further inspections. To avoid impacting the outage schedule, nozzles 5, 8 and 9 were subsequently added to the inspection list due to uncertainty regarding the ability to perform a full 360 degree visual inspection with the head installed. Results of an ultrasonic test inspection on the five nozzles revealed axial indications on the outside diameter of nozzles 1, 7 and 8. These indications, which centered on the lower nozzle to J-groove interface, did not extend through the tube wall or reveal a leak path by extending above the J-groove weld. Follow-up dye-penetrant exams confirmed that nozzle 7 had leaked and that nozzle 1 repairs were not required. From past nozzle repair data, a conservative decision to repair nozzle 8 was made although a leakage path was not identified. On April 1, 2002, after confirming that the Reactor Coolant System pressure boundary had been degraded during power operations, an 8-hour notification was made at 2123 hours in accordance with 10 CFR 50.72(b)(3)(ii)(A) reporting requirements. The apparent root cause of the nozzle leaks is primary water stress corrosion cracking. The two nozzles were repaired prior to unit restart. This event had minimal safety significance with respect to the health and safety of the public.
2692002005 | Oconee 1 | 11/28/1997 | 09/16/2002 | ML02268048 | <strong>Potential Failure of Manual Atmospheric Dump Valve Due to Pressure Locking</strong><br /><i>Abstract:&nbsp;</i>On 11-28-97, during a Unit 1 refueling outage, 1MS-156, "lB MS Line Atmospheric Vent Block Valve" was replaced with a flexible wedge gate valve design. On 7-8-02, as part of a project to review manual valves for pressure locking (PL) vulnerability, Engineering identified that 1MS-156, was potentially susceptible to PL. Valves in this application on other trains/units are solid wedge design. On 7-10-02 a vent line was installed on the valve bonnet, ending the potential for PL. At 1600 hours on 7-18-02, with Unit 1 operating in mode 1 at 100 per cent, 1MS-156 was determined to have been inoperable from 11-28-97 until 7-10-02 due to the potential for PL to prevent opening during postulated events. At 1843 hours on 7-18-02, an 8-hour Non-Emergency Notification was made to the NRC under 10 CFR 50.72(b)(3)(v). The root cause of this event is deficient design, due to an unanticipated system interaction, which resulted from a lack of awareness of pressure locking as a concern for manual valves. This event is considered to have no significance with respect to the health and safety of the public.
2702002001 | Oconee 2 | 10/03/2002 | 11/26/2002 | ML02135046 | <strong>Tech Spec Valve Manually Inoperable Due to Mechanical Interference</strong><br /><i>Abstract:&nbsp;</i>On 10-3-02, with Unit 2 operating at 100% in Mode 1, Maintenance personnel performing a routine Preventive Maintenance lubrication procedure discovered that 2LP-9 could not be manually operated, as required by Technical Specification 3.5.3, due to interference between a handle on the handwheel and a hanger. Operations and Engineering were contacted. Engineering determined that the handle is not a requirement for operation. The handle was removed from the handwheel, allowing the valve to be manually opened. Investigation found that the interference had existed since a larger operator was installed on the valve in May, 2001.The cause was a design oversight during the development of the modification. Appropriate personnel have been counseled. A contributing factor was that a manual stroke test, part of the Post-Modification Test plan, was performed after the hanger was removed due to emergent work needed to facilitate additional testing. Additional personnel will receive awareness training on this event. This event is considered to have no significance with respect to the health and safety of the public.
2702002002 | Oconee 2 | 10/15/2002 | 12/03/2002 | ML02347002 | <strong>Reactor Pressure Vessel Head Leakage Due to Primary Water Stress Corrosion Cracking of Alloy 600 Control Rod Drive Nozzles</strong><br /><i>Abstract:&nbsp;</i>Unit 2 entered its scheduled end-of-cycle 19 refueling outage on October 12, 2002. On October 15, 2002, a qualified visual inspection of the bare reactor vessel (RV) head was performed per NRC Bulletin 2001-01. Results of the visual inspection revealed several control rod drive mechanism (CRDM) nozzles were either classified as "masked" or leaking. Per Duke's response to NRC Bulletin 2001-01, nondestructive examinations of these and other CRDM nozzles were subsequently performed. Using conservative repair decisions supported by ultrasonic test and liquid dye-penetrant inspection techniques, a total of fifteen CRDM nozzles were categorized as appropriate for repair. All of the flaws identified in the nozzle base material were axial. The apparent root cause of the nozzle leaks is primary water stress corrosion cracking (PWSCC). The 15 nozzles were repaired prior to unit restart. The RV heads for all three units will be replaced as a long-term PWSCC solution. For this event, the overall safety significance of this event was minimal and there was no actual impact on the health and safety of the public.
2702002003 | Oconee 2 | 10/31/2002 | 12/16/2002 | ML02360019 | <strong>Steam Generator Tube Leak During In-Situ Pressure Test</strong><br /><i>Abstract:&nbsp;</i>On 10-31-02, Unit 2 was defueled in No Mode for a Refueling outage. During in-situ pressure testing, Steam Generator (SG) "B" Tube 37-27 began to leak at approximately 3900 psig. This did not meet the "3 times normal operating delta-p pressure" (4250 psig) test criterion. The failure was at an axially oriented indication in a dent with manufacture burnish marks (MBM) superimposed over the dent. The tube was removed from service by plugging. Axial indications have been seen in dents in the past and are anticipated in the ONS SGs. Existing test data was reviewed. Unit 2 had 28 indications of dents and MBM that overlapped and were preventatively plugged. Unit 3 had no similar indications. Unit 1 found 13 such indications but had no indication of cracking. The root cause of this event is human error (i.e. guidance document not followed correctly) due to a difficulty associated with interpreting eddy current test results. During previous inspections, the combination of signals from the overlapping indications resulted in masking the defect. Additional guidance for eddy current analysis will be provided so that this type of complex indication that potentially could mask degradation shall be considered for plugging. This event is considered to have no significance with respect to the health and safety of the public.
2712002001 | Vermont Yankee | 09/05/2002 | 10/24/2002 | ML02303044 | <strong>Core Thermal Power Exceeded Due to Non-Conservative Moisture Carryover Assumption</strong><br /><i>Abstract:&nbsp;</i>On 10/03/01, as a result of information received from General Electric Nuclear Energy (GENE) in September of 2001, it was determined that Vermont Yankee (VY) had potentially been operating slightly above its licensed Maximum Power Level as set forth in License Condition g.3.A. A moisture carryover fraction of 0.1% had been used from previous guidance by GENE. On 10/03/01 this value was changed to 0.0% in VY's calorimetric calculation model, pending the determination of an actual average moisture carryover content value. On 09/05/02, it was determined that the average moisture carryover fraction was approximately 0.029%; therefore core power may have been exceeded by approximately 1 Megawatt-thermal (MWth), which correlates to 0.06% of the Maximum Power Level. Use of the non-conservative moisture carryover fraction of 0.1% does not represent a safety issue. The change in core thermal power is an order of magnitude less than the precision of the MCPR safety limit evaluation process and is enveloped by the allowed uncertainties in the evaluation process and computer core thermal power estimate. The cause of this event is the failure to empirically determine the value of the percentage of moisture carry-over present once the plant became operational, and subsequent use of a design assumption in determining Core Heat Balance.
2712002003 | Vermont Yankee | 11/04/2002 | 12/20/2002 | ML03003046 | <strong>Reactor Building to Torus Vacuum Breakers Exceed Testing Acceptance Criteria Due to a Common Cause</strong><br /><i>Abstract:&nbsp;</i>On 11/04/02 to 11/06/02 with the plant at full power, quarterly In-Service Testing (IST) surveillance of the two Reactor Building to Torus Vacuum Breakers was performed. The seats for these valves were replaced during the October 2002 refuel outage. The vacuum breakers are 20 inch Walworth swing check valves, each capable of separately providing 100% vacuum relief to prevent the primary containment from exceeding the external design pressure. Both valves exceeded the IST program lift force acceptance criteria and one valve was slightly above the Technical Specification limit of 0.5 psid with a lift pressure of 0.52 psid. However, this 0.02 psid increase in lifting force would not have exceeded the Design Basis lift pressure of 2.0 psid required to meet the Torus Design Basis limit. This surveillance was subsequent to pressurization of the valves to 44 psig in the closed direction for primary containment leak rate testing (LLRT), which was performed after seat replacement during the previous refueling outage. The LLRT pressurization caused firm seating of the valves against the elastomeric seats, resulting in a higher breakaway force. The valves operated within Technical Specification requirements when re-tested subsequent to pressurization to 27 psig, a test pressure approximately equal to the postulated peak Torus accident pressure for Vermont Yankee. Subsequent IST of the valves indicated that the force required to move the disks is within the acceptable IST range. During testing, one valve always remained fully functional with respect to the Technical Specification requirements, thereby providing 100% design pressure vacuum relief for the Torus.
2722002001 | Salem 1, Salem 2 | 02/15/2002 | 04/12/2002 | ML02119040 | <strong>Non-Conservative Steam Generator Low-Low Level Setpoint</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2002, PSEG received information from Westinghouse indicating the steam generator low-low level setpoint for reactor trip and initiation of Auxiliary Feedwater was potentially non-conservative. Subsequent evaluation of the plant specific analyses for Salem 1 and 2 determined that a power reduction was required to maintain the plants within their current safety analysis limits, and that design changes were required to raise the steam generator low-low level setpoints. Unit 1 reactor power was lowered to less than 38% and Unit 2 reactor power was lowered to 78% when the condition was found. On February 16, 2002, design changes were implemented for Salem Unit 1 and 2 to raise the Steam Generator low-low level Setpoints to 14% This event was caused by the failure to account for the differential pressure created by steam flow past the mid-deck plate in the moisture separator section of the steam generator. Westinghouse indicated that this differential pressure phenomenon would cause the steam generator narrow-range to read higher than the actual water level. This event is reportable in accordance with 10CFR50.73(a)(2)(ii)(B), "Any event that resulted in the nuclear plant being in an unanalyzed condition that significantly degraded plant safety, "10CFR50.73(a)(2)(v)(A), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition," and 10CFR50.73 (a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident."
2722002002 | Salem 1 | 06/03/2002 | 08/02/2002 | ML02226053 | <strong>Containment Spray Additive Tank Exceeded Technical Specification Limit Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 3, 2002, it was identified that Salem Unit 1 operated with the Containment Spray (CS) system Spray Additive Tank (SAT) Sodium Hydroxide (NaOH) concentration below the TS 3.6.2.2 lower concentration limit of 30% weight/weight (w/w). During the performance of a scheduled Technical Specification (TS) Surveillance of the SAT on June 3, 2002, it was identified that the NaOH concentration was 29.57 % w/w. The SAT concentration was returned to appropriate TS NaOH concentration on June 4, 2002. A follow-up investigation of this event identified that the tank had been below the lower concentration limit for greater than the TS Allowed Outage Time (AOT) of 72 hours. Based on the SAT isolation valve leakrate, the SAT Sodium Hydroxide concentration could have been out of spec for as much as 95 days. The apparent cause of the concentration dilution was a combination of gradual back-leakage through the isolation valves from the RWST and inadequate SAT level trending. Corrective actions to be completed include repair of leaking isolation valve(s) and review of operational trending practices of the SAT parameters. There were no actual safety consequences associated with this event. The identified reduced NaOH concentration (29.57 % w/w) would have had no impact on the radiological consequences of an accident. An analysis performed concluded that with a concentration as low as 28% w/w the system was capable of meeting all required design functions in the event of a Large Break Loss of Cooling Accident (LB LOCA).
2722002003 | Salem 1 | 08/08/2002 | 09/06/2002 | ML02261024 | <strong>Special Report - Waste Gas Oxygen Analyzer Inoperable Greater than 30 Days due to Low Sensor Output</strong><br /><i>Abstract:&nbsp;</i>On July 9, 2002, Salem Unit I waste gas analyzer (WGA) {WE/AE} failed its channel check due to oxygen concentration readings less than the acceptance criteria. The WGA has been removed from service and has been inoperable for greater than 30 days. The oxygen analyzers have repeatedly given lower than acceptable readings, typically within several weeks of being replaced or recalibrated. The low readings are attributed to failure of the oxygen sensors. The apparent cause is being investigated with the sensor manufacturer (Whitaker). Planned corrective actions include sensor repair or replacement upon completion of the apparent cause investigation. There were no safety consequences associated with this event because alternate means of oxygen sampling and analysis remain available during waste gas holdup system operation. This Special Report is being submitted pursuant to Salem Unit 1 Technical Specification 3.3.3.9, for WGA inoperable greater than 30 consecutive days.
2722002004 | Salem 1 | 11/12/2002 | 01/13/2003 | ML03023027 | <strong>Manual Reactor Trip and Automatic Auxiliary Feedwater Actuation on Low Steam Generator Level due to Feedwater Pump Runback</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2002, Salem Unit 1 was manually tripped due to a Steam Generator Feedwater Pump (SGFP) runback resulting from voltage decrease in the control power to its governor. The undervoltage occurred when a technician inadvertently grounded the power circuit for a valve limit switch during troubleshooting. The runback was not annunciated in the control room; a level alarm was received several minutes later. Operators initiated main turbine runback and reduced reactor power. As level continued to decrease to the trip setpoint, operators initiated a manual reactor trip. Auxiliary feedwater (AFW) pumps started automatically as expected, and plant shutdown was achieved without complications. The root causes are silent SGFP runback that requires manual operator action, inadequate error prevention while taking voltage readings, and lack of recognition of the risk of troubleshooting. Corrective actions include design changes to minimize and improve plant response to SGFP runbacks, review of the human performance aspects of the root causes and procedural improvements for managing risk of work activities. Operator actions were in accordance with procedures and the plant responded as designed to the manual reactor trip. There were no safety consequences associated with this event. This event is reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to reactor trip and AFW system actuation.
2722002005 | Salem 1 | 10/10/2002 | 12/09/2002 | ML02352006 | <strong>Unexpected Auto-Start of Turbine Driven Auxiliary Feedwater Pump at Start of Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On October 10, 2002 at 2016 hours, during the scheduled performance of a manual trip of Salem Unit 1 to begin the 1R15 refueling outage, an unexpected auto start of the No. 13 Auxiliary Feed pump occurred. This auto start was a result of Steam Generator levels reaching the Low-Low Level Setpoint. The Steam Generator Low-Low Level Setpoint was revised earlier this year from 9% to 14% narrow range as a result of a Westinghouse identified industry concern. This was the first planned Unit trip since the Low-Low Level setpoints had been revised. There were no actual safety consequences associated with this event. The No. 13 Auxiliary feedwater pump was stopped, and plant cooldown continued in accordance with Technical Specification limits. This event is reportable under 10 CFR 50.73 (a)(2)(iv)(A) as an actuation of the auxiliary feedwater system.
2722002006 | Salem 1 | 10/15/2002 | 12/12/2002 | ML02354024 | <strong>As-Found Values for Main Steam Safety Valve and Pressurizer Safety Valve Lift Setpoints Exceed Technical Specification Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>During 1R15, with Salem Unit 1 in Mode 6 (Refueling) one Main Steam Safety Valve (MSSV) {SB/RV} and one Pressurizer Safety Valve (PSV) {AB/RV} that were tested in accordance with the requirements of the Technical Specifications (TS) and the ASME Operational and Maintenance (OM)-1 Code failed. On October 15, 2002, one of the five MSSVs failed to meet the TS required acceptance criteria, as established in TS Table 3.7-1. The MSSV testing scope was expanded (in accordance with ASME OM-1) to two additional valves. Both MSSVs tested satisfactorily. The apparent cause of the MSSV failing to meet the TS acceptance criteria was attributed to the valve spindle rubbing the spindle guide during lift due to misalignment. Corrective action taken was to repair the valve, retest to ± 1 % as required by the TS, and reinstall. On October 16, 2002, one PSV failed to meet TS 4.4.2 acceptance criteria. The PSV testing scope was expanded (in accordance with ASME OM-1) to two additional valves. Both PSVs tested satisfactorily. The apparent cause of the failure is that this was an original assembly valve and some parts may not have been lapped in place. Corrective action taken was to replace with the spare valve, tested to ± 1 % as required by the TS. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
2722002007 | Salem 1 | 10/16/2002 | 12/13/2002 | ML02360036 | <strong>Core Alterations Performed Without Direct Communications</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2002 at approximately 1200 hours, lifting of the upper internals from the reactor vessel (defined as a CORE ALTERATION in Technical Specifications) was commenced and continued until the upper internals were placed in their stand without incident. Technical Specification 3.9.5 states "Direct communication shall be maintained between the control room and personnel at the refueling station" and is applicable during CORE ALTERATIONS. Although the licensed operator maintained intermittent communication with control room operators, direct communication through the use of dedicated personnel on headsets on the refueling floor and in the control room did not occur. The apparent cause for this event was conflicting procedural definitions of what constitutes a core alteration. A contributing cause includes the lack of procedural guidance clearly defining whose responsibility it is to ensure that communications are established and maintained between the control room and refueling floor. Another contributing cause was a less than adequate pre job brief. Corrective actions include procedure revisions for clarification, initiation of a license change request, and review of the event with affected personnel. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as an operation or condition that is prohibited by the plant's Technical Specification.
2722002009 | Salem 1 | 12/12/2002 | 02/10/2003 | ML03052009 | <strong>Failure to Perform Required Action of Technical Specification 3.1.3.2.1</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2002, at 0821, the individual rod position indication (IRPI) for control rod 1C3 was declared inoperable on Salem Unit 1. Technical Specification action statement (TSAS) 3.1.3.2.1.a was entered which requires that either the position of the non-indicating rod is to be determined by use of the power distribution monitoring system or incore movable detectors once every 8 hours or to reduce thermal power to less than 50% of rated thermal power. The verification of the position of rod 1C3 was performed at 1430 and 2030 hours using the power distribution monitoring system. However, upon subsequent review of the 1430 and 2030 performance, the duty reactor engineer identified that the rod position verification had been performed on Unit 2 instead of Unit 1. The causes of this event are attributed to imprecise communication between the Control Room Supervisor (licensed operator) and Reactor Engineer due to failure to conduct a pre job brief and failure of personnel to utilize human error reduction techniques. A contributing cause to this event was inadequate procedure guidance for the Reactor Engineers. Personnel involved in this event from Operations and Reactor Engineering have been held accountable in accordance with company policies. Additionally this event will be evaluated for inclusion in Licensed Operator Training Program and Engineering Continuing Training Program, lessons learned will be communicated to the engineering organization and Reactor Engineering procedures have been revised. This report is being made in accordance with 10CFR50.73(a)(2)(i)(B), "any operation or condition which was prohibited by the plant's Technical Specification."
2752002001 | Diablo Canyon 1, Diablo Canyon 2 | 02/09/2002 | 04/15/2002 | ML02115047 | <strong>Technical Specification Violation Due to Nonconservative Steam Generator Narrow Range Water Level Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2002, at 1620 PST, with Units 1 and 2 in Mode 1 (Power Operation) at 100 percent power, the steam generator (SG) narrow range (NR) low-low level reactor protection channel setpoints were determined to be nonconservative and therefore inoperable. Plant operators entered the limiting condition for operation (LCO) 3.0.3 shutdown requirements and began shutdown of both Units 1 and 2. A 4-hour, non-emergency report was made at 1730 PST in accordance with 10 CFR 50.72(b)(2)(i) and 50.72(b)(3)(v)(A). The Nuclear Steam Supply System (NSSS) vendor, Westinghouse, investigating SG level response recorded February 9, 2002, determined the SG NR level setpoints were nonconservative for operation greater than 60 percent power. On February 14, 2002, at 2228 PST and 2045 PST, for Units 1 and 2, respectively, plant operators exited LCO 3.0.3 when power was reduced to less than 60 percent. The cause of this event was the NSSS vendor failure to identify to PG&E the mid-deck plate differential pressure effect on reactor trip and engineered safety features setpoints. Corrective actions include revision of the SG NR low-low level setpoint, review of the NSSS vendor's corrective actions for this condition, and a follow-up audit of the of the vendor's corrective actions taken.
2752002002 | Diablo Canyon 1 | 05/19/2002 | 05/22/2002 | ML02156054 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2002, with Unit 1 in Mode 6 (Refueling), analysis of eddy current testing on Steam Generator (SG) 1-2 indicated that greater than one percent of the tubes were defective. On May 19, 2002, at 1759 PDT, PG&E made a nonemergency report to the NRC as required by Technical Specification (TS) Table 5.5.9-2, "Steam Generator (SG) Tube Inspection." On May 20, 2002, PG&E discussed the preliminary results of the eddy current inspection with the NRC during a phone conference. PG&E also notified the NRC that primary water stress corrosion cracking and circumferential indications were detected at tube support plate (TSP) intersections, satisfying TS 5.6.10 paragraphed. The majority of the tube defects were attributed to outside diameter stress corrosion cracking and to primary water stress corrosion cracking at TSP intersections. PG&E has plugged all defective Unit 1 tubes identified during the current refueling outage in accordance with TS 5.5.9. All defective tubes met the criteria of Regulatory Guide 1.121 for structural integrity at the end of Cycle 11. PG&E maintains a comprehensive program to minimize SG tube degradation.
2752002003 | Diablo Canyon 1, Diablo Canyon 2 | 04/30/2002 | 10/29/2002 | ML02310031 | <strong>Unanalyzed Condition Due to Heavy Load Movement Over a Restricted Area</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2002, between 0930 and 0940 PDT, with the unit in Mode 5 (Cold Shutdown), a main turbine low pressure (LP) turbine outer cover was moved over a Unit 1 turbine building heavy loads restricted area above the diesel generators and 4kV vital bus ventilation, contrary to Inter-Departmental Administrative Procedure MA1.ID14, "Plant Crane Operating Restrictions." The 70-ton LP turbine cover was moved from the LP C turbine location (northern most LP section at center line of the turbine/generator), raised approximately 15 feet, transported north over the Operation Support Team offices on the north end of the elevation 140 foot turbine building, then west, and lowered onto a previously evaluated laydown area designated on the laydown drawing. The primary cause of the event was the failure of utility and outage contract turbine maintenance personnel to comply with procedures for movement of loads within a heavy loads restricted area. Corrective actions to prevent recurrence include a review of this event for all crane operator and rigging qualifications, having a person knowledgeable in the heavy loads rigging program present at the pre-job tail boards, and modification of plant procedures requiring engineering to ensure, during their evaluations, that the movement of heavy loads will not violate restrictions for load handling.
2752002004 | Diablo Canyon 1 | 06/03/2002 | 08/02/2002 | ML02227071 | <strong>Automatic Reactor Trip on Low Steam Generator Level Due to Feedwater Flow Control Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On June 3, 2002, at 1302 PDT, while Unit 1 was in Mode 1 (power operation) at 86 percent power, Unit 1 experienced an automatic reactor trip due to low-low steam generator (SG) water level in SG 1-1. Feedwater flow was terminated to SG 1-1 when the feedwater flow control valve, FCV-510, failed closed. The valve failed closed, as designed, on loss of air when a valve-mounted air test connection broke off after contacting structural steel during thermal expansion of the feedwater piping. The test connection was reinstalled in a configuration to prevent contact with structural steel during thermal expansion. Similar installations were visually inspected during the subsequent power ascension to assure there were no other problems resulting from thermal movement of piping. The root cause of the event was a deficiency in the design-change and work-control processes to consider configuration control of trip-sensitive instruments that are mounted on plant piping subject to thermal expansion during power ascension. As corrective action to prevent recurrence, PG&E will identify trip-sensitive components on thermally expanding piping and include provisions in the design change and work-control processes to consider their configuration during modification and maintenance.
2752002005 | Diablo Canyon 1 | 06/10/2002 | 08/09/2002 | ML02233042 | <strong>Technical Specification 3.4.10 Not Met During Pressurizer Safety Valve Surveillance Testing Due to Random Lift Setting Spread</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2002, during a routine, scheduled performance of Surveillance Test Procedure M-77, "Safety and Relief Valve Testing," PG&E identified two of three pressurizer safety valves (PSVs) outside the Technical Specification (TS) 3.4.10, "Pressurizer Safety Valves," tolerance lift setting of greater than 2460 psig and less than 2510 psig. The PSVs were disassembled, inspected, and reset within TS requirements at the offsite test facility. PG&E believes the cause of the PSV lift setting being outside the TS allowance is random lift setting spread. PSV lift setting repeatability has been recognized as an industry-wide problem. PG&E has participated in extensive investigative test programs, both jointly with the nuclear steam supply system vendor, Westinghouse Owners Group, and independently. The results of the industry investigations are documented in WCAP-12910, "Pressurizer Safety Valve Set Pressure." PG&E has previously enhanced the PSV maintenance activities and testing procedures resulting in improved performance. No further corrective actions are required.
2752002006 | Diablo Canyon 1 | 05/06/2002 | 11/26/2002 | ML02339006 | <strong>Technical Specification LCO 3.7.17.2 Not Met During the 1R11 Refueling Outage When Two Fuel Assemblies Were Placed in Adjacent Locations</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2002, at 1025 PDT, during the Unit 1 eleventh refueling outage, fuel assembly J55 was placed adjacent to fuel assembly DD14 resulting in a violation of Technical Specification (TS) LCO 3.7.17.2, "Spent Fuel Assembly Storage-Region 2." On May 11, 2002, at 1534 PDT during the core reload, fuel assembly DD14 was removed from the adjacent location exiting the Technical Specification violation. On September 27, 2002, a utility engineer discovered the nonconforming condition while updating a new fuel-tracking software package. PG&E believes the cause of the violation was a personnel error on the part of the preparer, reviewer and approver of the core offload sequence. Corrective actions include using a checklist outlining the key areas for focus when preparing, reviewing and approving the core offload sequence, and using a new fuel-tracking software program to ensure compliance with TS requirements.
2772002001 | Peach Bottom 2 | 12/21/2002 | 02/07/2003 | ML03052031 | <strong>Circuit Card Failure Results in a Primary Containment Group I Isolation and Plant Scram</strong><br /><i>Abstract:&nbsp;</i>At approximately 2035 on 12/21/02, Unit 2 automatically scrammed as a result of Main Steam Line Isolation Valve closure due to a Group I Primary Containment Isolation System (PCIS) actuation. The Group I PCIS actuation was a result of low main steam line pressure caused by the opening of Main Steam Line Bypass Valves due to an Electro-Hydraulic Control (EHC) circuit malfunction. PCIS Group II/III isolations were received as expected. A secondary containment isolation damper did not initially close due to a sticking solenoid valve. The redundant damper closed as designed. The High Pressure Coolant Injection and Reactor Core Isolation Cooling (RCIC) systems automatically started and injected water into the reactor vessel. RCIC was used to control reactor water level although the flow controller operated erratically which was subsequently determined to have caused RCIC to be inoperable resulting in a condition prohibited by Technical Specifications. Additionally, the reactor cool down rate of 100°F/hr was exceeded at 2205 hours on the reactor bottom head resulting in a Technical Specification Required Action entry. The Required Action entry was exited upon conclusion of a satisfactory thermal cycles analysis. The EHC control circuit malfunction was due to a component failure on a circuit card. Corrective actions include replacing the defective circuit card, replacing the secondary containment isolation damper solenoid valve, readjusting the RCIC flow controller, and reinforcing the monitoring of cool down rates to licensed operators.
2802002001 | Surry 1 | 12/31/2002 | 03/03/2003 | ML03069038 | <strong>Inadvertent Auxiliary Feedwater Pumps Autostarts Due to Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2002 at 09:18 hours with Unit 1 at 100% power, the Train "A" Motor Driven Auxiliary Feedwater Pump (MDAFWP) autostarted. The autostart resulted from an invalid signal due to a relay failure. This autostart is reportable under 10 CFR 50.73(a)(2)(iv). At the time of the event, the Steam Driven Auxiliary Feedwater Pump (SDAFWP) and the redundant Train "B" MDAFWP were operable, flow continued from the two normal Feedwater Pumps, and the cross-connect from the Unit 2 AFW system was operable. The Train "A" MDAFWP was secured, and replacement of the failed relay was initiated. While replacing the failed relay, two inadvertent autostarts of the SDAFWP occurred. In both cases a temporary jumper lost continuity due to intermittent contact by the jumper's alligator clip. The SDAFWP was secured following both inadvertent autostarts. After the second inadvertent autostart of the SDAFWP, the jumper was held in place while the failed relay was replaced, and the Train "A" MDAFWP was declared operable at 20:12 hours. The two autostarts of the SDAFWP are also reportable under 10 CFR 50.73(a)(2)(iv). During both SDAFWP autostarts events, flow continued from the two normal Feedwater Pumps, the function of the SDAFWP starting relay was not lost, the Train "B" MDAFWP was operable, and the cross-connect from the Unit 2 AFW system was operable.
2812002001 | Surry 2 | 04/13/2002 | 06/12/2002 | ML02171018 | <strong>Residual Heat Removal Piping Corrosion Through-Wall Leak</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2002 at 05:05 hours during plant heatup with Unit 2 at cold shutdown, a through-wall leak was discovered on the "B" residual heat removal (RHR) pump suction 3/4-inch diameter balance line. This condition did not meet ASME XI code requirements therefore, the line was declared inoperable. Furthermore, the line was not isolable from either RHR train therefore, both trains of RHR were declared inoperable. This condition is reportable pursuant to 10CFR50.73(a)(2)(vii). The line remained structurally adequate therefore, both trains of RHR were capable of performing their intended function and the system remained in service until repairs were implemented. Because no reactor coolant system (RCS) loops were operable at that time, the Technical Specification requirement that a minimum of two non-isolated loops shall be operable was not met. As such, this condition is also reportable pursuant to 10CFR50.73(a)(2)(i)(B). Plant heatup proceeded, keeping the RHR System in service, until two RCS loops were put into operation, restoring Technical Specification compliance. The RHR System was taken out of service, the 3/4-inch line was replaced, and the RHR System declared operable. The cause of this leak was transgranular stress corrosion cracking initiated from the outer surface of the 3/4-inch line.
2812002002 | Surry 2 | 10/30/2002 | 12/23/2002 | ML02365055 | <strong>Low Head Safety Injection System Inoperable Due to Partially Closed Valve</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2002, with Unit 2 operating at 100% reactor power, an operator taking logs determined the valve for-the Low Head Safety Injection (LHSI) Pump 2-SI-P-1A Seal Cooler Outlet was out of position. Further investigation found the valve was approximately 90% closed when it should have been fully open and LHSI Pump 2-SI-P-1A was declared inoperable. During the time 2-SI-P-1A was inoperable, the #3 Emergency Diesel Generator power supply for the redundant 2-SI-P-1B LHSI Pump was also inoperable due to preplanned maintenance and as a result, 2-SI-P-1B could not be considered operable in accordance with Technical Specification 3.0.2. These conditions could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident and are therefore reportable pursuant to 10CFR50.73(a)(2)(v)(D). Due to Technical Specifications requiring one LHSI Pump operable during reactor operation, a 6-hour limiting condition of operation (LCO) was entered at 1708 hours. This condition is reportable pursuant to 10CFR50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. The valve for LHSI Pump 2-SI-P-1A Seal Cooler Outlet was opened and the LCO was exited at 1723 hours. This event resulted in no safety consequences or significant implications therefore; the health and safety of the public were not affected.
2812002003 | Surry 2 | 11/23/2002 | 01/18/2003 | ML03028064 | <strong>Reactor Trip due to Turbine Electro-Hydraulic Control Circuitry Failure</strong><br /><i>Abstract:&nbsp;</i>On November 23, 2002, at 0332 hours, Unit 2 was at 85% power for the performance of the Turbine Governor Valve Freedom Test. During the performance of the test, while closing # 3 Turbine Governor Valve, the Turbine Valve Limiter failed to zero causing all four governor valves to close. The Control Room received a Low Low Steam Generator Level signal resulting in an automatic reactor trip. This is reportable under 10CFR50.73(a)(2)(iv)(A), as an event that resulted in the manual or automatic actuation of any engineered safety feature, including the reactor protection system.
2812002004 | Surry 2 | 11/23/2002 | 01/18/2003 | ML03028063 | <strong>Turbine Trip Fuses Removed Resulting in Condition Prohibited by Tech Specs</strong><br /><i>Abstract:&nbsp;</i>At 1815 hours on November 23, 2002 with Unit 2 at Hot Shutdown conditions, post-maintenance testing (PMT) was initiated on main steam stop valves #1 and #3 following valve limit switch adjustments. As part of the PMT, turbine trip fuses in the turbine solenoid trip circuit and the backup turbine solenoid trip circuit were removed. With these fuses removed, Trains A and B of the turbine trip logic were defeated. This condition, which is prohibited by Technical Specifications (TSs), is being reported in accordance with 10CFR50.73(a)(2)(i)(B). It has been determined that this condition resulted from a human error. The preparation of a 1997 procedure revision and its supporting safety evaluation considered the requirements of TS Table 3.7-1, but overlooked the requirements of TS Table 3.7-3.
2822002001 | Prairie Island 1, Prairie Island 2 | 07/16/2002 | 09/16/2002 | ML02268015 | <strong>Condition Prohibited by Technical Specifications Due to Potential Auxiliary Building Special Vent Zone Boundary Degradation</strong><br /><i>Abstract:&nbsp;</i>Prairie Island Technical Specification 3.6.E.2 states that; "Openings in the Auxiliary Special Ventilation Zone are permitted provided they are under direct administrative control and can be reduced to less than 10 square feet within 6 minutes following an accident". On July 16, 2002, while both units were operating at 100% power, a potential uncontrolled Auxiliary Building Special Vent Zone (ABSVZ) boundary leakage path was identified. Upon discovery of the potential deficiency, the doors from the "Hot" Chemistry Lab to the ABSVZ were treated as openings in the boundary and were placed under administrative controls as allowed by the Technical Specifications. The cause of the event is attributed to design changes that were performed during plant construction in 1973, which realigned "Hot" Chemistry Lab ventilation supplies and failed to recognize the potential effect on the ABSVZ boundary. Future design changes or continued use of administrative controls are being evaluated as corrective actions to resolve this issue. No equipment failures occurred during this event.
2822002002 | Prairie Island 1 | 11/15/2002 | 01/13/2003 | ML03024003 | <strong>Manual Reactor Trip and Auxiliary Feedwater Pump Start During Planned Shutdown</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2002, Unit I was undergoing an orderly shutdown in preparation for a planned refueling outage. Prior to the shutdown, an existing problem with the steam generator blowdown flash tank vent line bellows to 13A Feedwater Heater had been identified and contingency plans were in place for monitoring the level of the 13A Feedwater Heater during the load decrease. At approximately 2020 during the load decrease, Operators made the decision as planned, to manually trip the reactor when it was determined that a Hi Hi Level in the heater, could not be reduced. Reactor power at the time of the trip was 12%. During performance of reactor trip recovery procedures, 11 Turbine Driven Auxiliary Feedwater Pump auto started at 2055 when the running Main Feedwater Pump was secured. Following investigation and repair to the steam generator blowdown flash tank vent line bellows and completion of all refueling outage activities, the unit was returned to service on December 6, 2002.
2822002003 | Prairie Island 1 | 12/01/2002 | 02/29/2004 | ML04069073 | <strong>Failure to Meet Technical Specification Limiting Condition for RCS Pressure and Temperature Limits</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2002, with Unit 1 in MODE 5, Reactor Coolant System (RCS) temperature dropped below 80 degrees F in response to jogging the Reactor Coolant Pumps (RCP) as part of RCS fill and vent. Tech. Spec. (TS) Limiting Condition for Operation (LCO) 3.4.3 requires that the RCS temperature be maintained within the limits of the Pressure and Temperature Limits Report (PTLR) at all times. PTLR section 3.0 requires that the RCS temperature when not vented, remain above 86 degrees F. Required Action C.2 for TSLCO 3.4.3 specifies evaluating the RCS acceptability for continued operation before entering MODE 4. At that time the condition for entry into the TS was not recognized and the required action was not completed prior to entering MODE 4. This issue was discovered during a subsequent evaluation and identified as a reportable event (any operation or condition which was prohibited by TS) on December 31, 2003. The cause of the low temperature condition was attributed to insufficient procedural guidance during the RCS fill and vent to preclude a temperature transient during a RCP start. The cause of the TS violation was a PTLR implementation weakness. The organization had deficient knowledge of the basis for the PTLR limits. Subsequent evaluations determined that the RCS remained operable and that the event had no actual consequences with respect to the reactor vessel integrity.
2852002001 | Fort Calhoun | 12/17/2001 | 01/16/2002 | ML02063064 | <strong>Contraband Found in a Vehicle During Entrance Search to the Site Protected Area</strong><br /><i>Abstract:&nbsp;</i>On December 17, 2001, a handgun was found when a vehicle was searched during processing into the protected area. A shipment had arrived that day at the Fort Calhoun Station (FCS) access control point to the owner controlled area. The driver and shipment were verified, and the driver was asked about declaring prohibited items. The driver was informed of FCS's prior knowledge of his declaration of a handgun at another plant. The driver stated that he had nothing to declare. The driver was escorted with the load to the protected area access point. Prior to entering the protected area, the driver was again asked about declaring prohibited items. Security officers named specific items (including handguns) listed on the access checklist. The driver stated that he had nothing to declare and gave consent to search the tractor-trailer. A security officer searched the cab of the tractor and discovered a handgun between a closet panel and the cab wall of the tractor. The handgun was confiscated. The driver, the tractor, and the handgun never entered the protected area. The cause of this incident was a lack of understanding on the part of the driver of the truck of the seriousness of carrying prohibited items into the protected area at FCS. The driver of the truck was not allowed to enter the protected area. The driver was escorted off the owner controlled area, and the handgun was returned to the driver at that time.
2852002002 | Fort Calhoun | 04/03/2002 | 06/03/2002 | ML02164010 | <strong>Inappropriate Use of Manual Operator Action Renders Multiple Safety Systems Inoperable</strong><br /><i>Abstract:&nbsp;</i>An inspection found that the quarterly full flow tests on the Auxiliary Feedwater (AFW) system pumps inappropriately took credit for manual operator action to isolate the full flow test line in the event that AFW flow was needed for an accident. Eliminating this unapproved credit rendered both trains of the AFW system inoperable for the length of the test. This test had been performed in this manner since about 1993. A review found that other procedures credited using manual operator actions for automatic actions. During part of a test of the Emergency Core Cooling System (ECCS), the pump recirculation line was isolated for a short period of time. During this time, had an accident signal started the ECCS pumps with plant greater than injection pressure the pumps would have run at shutoff head until the operator took action to restore the minimum flow path. The Fort Calhoun Station (FCS) review of NRC Information Notice (IN) 97-78 incorrectly assumed that the NRC had approved crediting manual operator actions to maintain the pump operable when a violation on a related AFW issue was closed in an NRC Inspection Report. FCS reviewers assumed that IN 97-78 requirements were being met by administrative control of manual operator actions. This resulted in a less than adequate review. Plant procedures have been corrected to implement the appropriate guidance and appropriate personnel have been trained.
2852002003 | Fort Calhoun | 11/01/2002 | 12/20/2002 | ML02365050 | <strong>Inadequate Cable Separation Resulting in Noncompliance with 10CFR50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>During a self assessment Fort Calhoun Station completed a review of cable separation for components in Fire Area 30 (Containment), an issue was identified with the configuration of the pressurizer level transmitter signal cables. After an exhaustive review of documentation, a containment entry was made to confirm actual cable configuration. During the containment entry, pressurizer level transmitter cable separation was determined not to comply with Appendix R separation requirements. The root cause of this condition is a failure to recognize and fully apply the separation requirements for cables in conduits as required by 10 CFR 50 Appendix R. The problem of cable separation will be corrected by a modification in accordance with Appendix R as directed by the corrective action system.
2852002004 | Fort Calhoun | 12/19/2002 | 02/13/2003 | ML03052023 | <strong>Inadequate Procedural Guidance Resulting in Noncompliance with 10 CFR 50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>During a self assessment Fort Calhoun Station completed a review of cable separation for components in Fire Area 30 (Containment), an issue was identified with the configuration of the pressurizer level transmitter signal cables. After an exhaustive review of documentation, a containment entry was made to confirm actual cable configuration. During the containment entry, pressurizer level transmitter cable separation was determined not to comply with Appendix R separation requirements. The root cause of this condition is a failure to recognize and fully apply the separation requirements for cables in conduits as required by 10 CFR 50 Appendix R. The problem of cable separation will be corrected by a modification in accordance with Appendix R as directed by the corrective action system.
2862002001 | Indian Point 3 | 06/07/2002 | 07/05/2002 | ML02200015 | <strong>Operation in a Condition Prohibited by Technical Specifications Due to an Inoperable Service Water Pipe Caused by a Leak That Exceeded the AOT</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2002, during routine rounds, operations identified a leak in a 18 inch diameter service water (SW) supply header pipe in the Primary Auxiliary Building (PAB). Engineering inspected the leaking pipe and initiated non-destructive examinations to characterize the extent of the degradation. Additional testing was performed on June 6, and on June 7 further testing and an evaluation of collected data was performed. A plan of action was developed and the NRC notified. On June 7, at 2035 hours, Engineering concluded the pipe was inoperable. Operations entered SW Technical Specification 3.7.9.E.1 Action Statement (AS) with a 12 hour completion time and closed valves to isolate the leaking pipe. Code repair of the pipe was initiated and because the repair time would exceed the SW TS AOT, a notice of enforcement discretion (NOED) was prepared and a request for an additional 60 hours was submitted to the NRC. The NOED was authorized prior to exceeding the TS AOT, pipe repairs completed and the SWS returned to operable on June 9, 2002, after approximately 44.5 hours. The cause of the pipe leak was corrosion of the carbon steel weld metal at the butt weld of the 18 inch diameter pipe. Corrective actions were a code repair of the pipe and an assessment of the existing program for Generic Letter 89-13 with adjustments that include radiographic testing of four additional weld locations of similar pipe size and flow characteristics prior to refueling outage 12 scheduled in March 2003. The event had no effect on public health and safety.
2862002002 | Indian Point 3 | 05/17/2001 | 07/29/2002 | ML02217018 | <strong>Inoperable Isolation Valve Seal Water System Due to a Mispositioned Valve is Outside Technical Specifications and a Safety System Functional Failure</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2002, a Nuclear Plant Operator discovered that a manually operated vent valve (IV-1428) on the Isolation Valve Seal Water System (IVSWS) header was mispositioned in the open position making the IVSWS system inoperable. The open vent valve could have prevented pressurization of the IVSWS headers and the seal water in the IVSWS Tank would have drained in less than 2 hours. IVSWS is designed to provide a containment isolation valve water seal after a postulated loss of coolant accident to mitigate containment isolation valve leakage. The inoperability of the system since May 17, 2001 violated Technical Specifications and was a safety system functional failure. The cause of the mispositioning of the valve was human error in the failure to perform all system restoration steps during performance of a surveillance test. Upon discovery, the operator closed the vent valve and restored the IVSWS to operability. Corrective actions for past mispositioning events address the cause and extent of condition. A review of 3PT-R025A and other procedures written in similar format will be conducted to determine necessary changes. The inoperable IVSWS had no significant effect on public health and safety since the containment isolation valves remained operable and would have minimized plant leakage after a postulated loss of coolant accident.
2862002003 | Indian Point 3 | 11/15/2002 | 01/14/2003 | ML03017019 | <strong>Automatic Reactor Trip Due to the Failure of a 345 KV Main Output Breaker</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2002, during full power operation, an automatic reactor trip (RT) occurred. The RT occurred due to the actuation of the reactor protection system (RPS), which was caused by a main turbine trip that was the result of actuation of the main generator primary and backup lockout relays. The main generator trip actuation was caused by the actuation of the electrical protective relaying direct trip circuitry from the 345 KV main output breakers. The 345 KV main output breaker No. 3 faulted open resulting in a trip signal to breakers Nos. 1, 3, and 6 which opened. Breaker 5 had opened prior to the event for unknown reasons. The protection associated with the breakers actuated the lockout relays. Station offsite power was maintained throughout the event. There was no automatic start of the Emergency Diesel Generators. The Auxiliary Feed Water pumps automatically started. The cause of the event was a RT actuation due to a failure of 345 KV main output breaker No. 3. The breaker No. 3 failure was due to high contact resistance caused by misalignment from poor vendor workmanship. Corrective actions include assessment of the output breakers, maintenance and testing of output breaker No. 1, verification that breaker No. 1 is capable of supporting 100% power, and implementation of a monitoring plan for breaker No. 1. Output breaker 3 was inspected, repaired and returned to service. The procedure for breaker maintenance will be revised. The event had no effect on public health and safety.
2872002001 | Oconee 3 | 11/14/2002 | 01/13/2003 | ML02135046 | <strong>Moisture Separator Reheater Level Results in Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2002, Oconee Unit 3 was operating in Mode 1 at 100% power. At approximately 0419 hours, Unit 3 experienced a high level in a Moisture Separator Reheater (MSRH). The turbine tripped as a protective feature to prevent water from backing up into the turbine. This caused an anticipatory reactor trip. The high level was caused by three separate equipment failures which resulted in discharge flow paths from the 3A Moisture Separator Drain Tank (MSDT) becoming isolated and water backing up into the MSDT and MSRH. In this event, the plant systems and operators responded as expected. Automatic system responses and operator actions in accordance with procedures were adequate to safely control the reactor following this trip. The corrective action was to repair the three Unit 3 A MSDT level control equipment problems. The health and safety of the public was not compromised by this event.
2892002001 | Three Mile Island 1 | 12/01/2001 | 03/15/2002 | ML02087035 | <strong>Vital Power Supply Failure Due to Blown Fuse</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2001, one of the four 120 volt vital power busses lost power due to a blown fuse in the 1B vital power buss inverter during surveillance testing. The plant was completing a refueling outage, the reactor was not critical, the turbine was not on-line, and the decay heat load from the core was very low. The loss of one of the four 120 volt vital power busses did not result in any adverse plant condition, but the condition that caused that loss was determined to potentially be applicable to the other three vital power busses. The condition allowing the potential loss of the vital power busses originated earlier during the refueling outage, on November 24, 2002, when modifications were implemented related to installation of new auxiliary transformers. The condition was corrected on December 3, 2001, prior to the reactor being made critical. This event was determined to be reportable on January 15, 2002, as a condition that could have prevented the fulfillment of the safety function of systems that are needed to remove residual decay heat. A risk evaluation of this condition determined it to be a significance level of Green. The root causes are that the original design of the power supplies to the vital power buses did not meet certain design specifications, and the design documents did not accurately reflect voltage limits to the inverters. Corrective actions address the design discrepancy and the less than adequate design documents. There were no adverse safety consequences from this event, and the event did not affect the health and safety of the public.
2892002002 | Three Mile Island 1 | 05/29/2002 | 07/26/2002 | ML02212042 | <strong>Pressurizer Code Safety Valve Setpoint Outside Tolerance During Plant Operation Due to Mechnical Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2002 TM1-1 was operating at 100 percent power. NWS Technologies informed AmerGen of unsatisfactory test results for one of the two code pressurizer safety valves (PCSV), removed during the cycle 14 refueling outage. NWS Technologies was contracted to perform the offsite pressurizer safety valve testing and the testing was conducted within the required time constraints. Technical Specification 3.1.1.3.a Bases requires the PCSVs to lift at 2500 psig plus or minus 3 percent during the "as-found" testing. One of the two PCSVs tested 3.8 percent high, which is outside the required 3 percent tolerance limit. The most probable root cause for this setpoint drift is a lack of contact area between the upper spring washer and spring, which allowed for relative movement due to an external force. There was no affect on the health and safety of the public during the past operating cycle because reanalysis shows that Reactor Coolant System pressure would not have exceeded the safety limit if the most limiting pressure transient had occurred.
2932002001 | Pilgrim | 07/07/2002 | 09/04/2002 | ML02255043 | <strong>High Pressure Coolant Injection System Inoperable Due to Fuse Failure</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2002, the High Pressure Coolant Injection (HPCI) system was declared inoperable for 30 minutes. The cause was a failed fuse that is part of the control power circuitry for the circuit breaker of a normally closed motor-operated valve in the HPCI system injection piping. Inspection of the failed fuse identified a separation that had occurred at an internal solder connection between the fuse end cap and the fusible link. The fusible link was intact. The fuse was replaced and the system was returned to operable status on July 7, 2002. The event occurred at 100 percent reactor power with the reactor mode selector switch in the RUN position. The reactor vessel pressure was approximately 1035 psig with the water temperature at the saturation temperature for that pressure. This event posed no threat to public health and safety.
2932002002 | Pilgrim | 09/12/2002 | 11/12/2002 | ML02324022 | <strong>Control Room High Efficiency Air Filtration System Inoperable Due to Inadequate Post Modification Testing</strong><br /><i>Abstract:&nbsp;</i>On September 12, 2002, both trains of the control room high efficiency air filtration system (CRHEAFS) were inoperable for approximately 4.25 hours. The root cause of this event was a human performance error by a utility licensed operator with respect to the inappropriate decision to declare the "B" CRHEAFS train operable without all procedural requirements satisfied following the humidity switch replacement. Contributing to this unintentional human performance error were procedural weaknesses that made it more difficult to determine the correct operability testing requirements. In addition, the design change, under which the humidity switch was replaced, incorrectly wired the switch such that the switch would not energize the heater when relative humidity exceeded 70%. Procedural controls are being strengthened and training is being developed for the operations staff to ensure necessary Technical Specification testing is performed prior to declaring a system operable. This condition posed no threat to public health and safety.
2932002003 | Pilgrim | 10/03/2002 | 12/02/2002 | ML02337056 | <strong>Loss of Automatic Scram Safety Function Due to Age-Related Failure of Recirculation Flow Converter</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2002, at 0150 hours, reactor protection system (RPS) trip channel `A' and one of the two rod block channels were manually tripped. These actions were taken because the related average power range monitors (APRMs) were declared inoperable due to non-conservative drift from the recirculation loop 'A' flow converter. The converter provides flow-bias input to the APRMs that are part of the respective RPS trip channel. The APRMs are equipped with the Enhanced Option I-A flow control trip reference feature. Consequently, an automatic scram would not have occurred when entering the Exclusion Region as a result of a runback of both recirculation pumps to the minimum speed as assumed in the Enhanced Option I-A stability solution while RPS trip channel `A' was not tripped. The direct cause was the age-related failure of the recirculation system loop `A' flow converter. The root cause was a lack of a preventive maintenance activity to replace the recirculation flow converters. The flow converter was replaced and calibrated with satisfactory results. Corrective actions planned include creating preventive maintenance activities to periodically replace the flow controllers. The condition posed no threat to public health and safety.
2962002001 | Browns Ferry 3 | 01/09/2002 | 03/08/2002 | ML02085071 | <strong>Failure to Meet Technical Specification Requirements for Inoperable Primary Containment Isolation Instrumentation Due to Removal of Incorrect Temperature Switches</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2002, at 0849 hours, four Reactor Core Isolation Cooling (RCIC) steam line space temperature switches were replaced with temperature switches intended for replacement of the High Pressure Coolant Injection (HPCI) steam line space temperature switches. This resulted in the Primary Containment Isolation Instrumentation being inoperable. At 1425 hours, the Control Room was notified of the error and technical specification actions were initiated to isolate the affected penetration flow path. Since the Primary Containment Isolation instrumentation was made inoperable without the knowledge of Operations, TVA did not take the required technical specification actions within one hour of the instrumentation becoming inoperable. In accordance with 10 CFR 50.73 (a) (2) (i) (B), this report is being submitted as any operation or condition prohibited by the plant's technical specifications The root cause for this event was personnel error. Maintenance personnel failed to properly execute the verification process required by site procedures. The individuals focused only on the address portion of the component identifier rather than on the complete component identifier. Actions to prevent recurrence included appropriate personnel corrective actions for involved personnel and stand-down briefings and refresher training for Instrument and Controls (I&C) maintenance personnel.
2962002002 | Browns Ferry 3 | 03/26/2002 | 05/23/2002 | ML02161017 | <strong>An unplanned auto-start of two emergency diesel generators due to personnel error During an equipment clearance process.</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2002, at 1752 hours, while installing safety grounds to the 3B 4KV Unit Board during the Unit 3 Cycle 10 refueling outage, an electrician inadvertently caused an electric arc flashover when a safety ground connecting rod was positioned too close to an energized breaker high-side stab. The electric arc flashover resulted in de-energizing the Unit Board. Consequently, this de-energized two 4KV shutdown boards causing two emergency diesel generators to auto-start. The root cause of the event was personnel error due to inattention to detail and failure to adequately self-check. Corrective actions include: (1) Training was given to Electrical Maintenance personnel on the proper methodology to apply safety grounds, (2) A TVA policy/procedure will be developed for safety ground installations, (3) Training will be developed and conducted on installation of safety grounds of medium voltage compartments, and (4) As appropriate, test carts will be used to reduce the potential for inadvertent electric arc flashover. This condition is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of a system listed in 10 CFR 50.73(a)(2)(iv)(B).
2962002003 | Browns Ferry 3 | 04/06/2002 | 06/04/2002 | ML02165034 | <strong>Actuation of RPS While Shutdown Due to Inadvertent Depressurization of Scram Pilot Air Header</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2002, Unit 3 was in day 12 of its cycle 10 refueling outage. Electrical Maintenance personnel were performing preventive maintenance work on the reactor protection system (RPS) manual scram contactors. At approximately 1314 hours CST, a full reactor scram was received due to low pressure in the RPS scram pilot air header. A loose plunger arm screw on an RPS scram contactor was discovered. This loose plunger arm prevented proper operation of the associated auxiliary contacts. These contacts are designed to open when the main contactor is energized. With the plunger arm in a loose condition, these contacts were remaining closed when the main contactor was energized. Faulty auxiliary contact operation on this RPS contactor caused the RPS 3A portion of the energization circuitry for one backup scram valve to be partially completed when it should not have been. During subsequent work on the RPS 3B contactors, the backup scram valve energization circuit was unknowingly completed, resulting in the valve's actuation. The purpose of the backup scram valve is to vent and depressurize the scram pilot air header upon a full scram condition; the inadvertent operation of this valve directly caused the actual scram pilot air header low pressure and the resulting full actuation of the RPS logic. As corrective actions the loose plunger arm screw was tightened, the screws on the remaining Unit 3 and Unit 2 contactors were inspected and tightened as necessary, and Electrical Maintenance instructions are being revised to ensure the scram contactor auxiliary contacts are inspected during preventive or corrective maintenance activities.
2962002004 | Browns Ferry 3, Browns Ferry 2 | 10/22/2002 | 12/20/2002 | ML03006040 | <strong>Loss of High Pressure Coolant Injection (HPCI) Flow Controller Power Supply</strong><br /><i>Abstract:&nbsp;</i>On 10/22/02, Electrical Maintenance personnel were engaged in a maintenance activity on 250 VDC Battery Charger 4. To aid in the repair of out-of-service Battery Charger 4, a supporting work activity was being performed to obtain comparison waveform data from in-service Battery Charger 3. While connecting an oscilloscope to the Battery Charger 3 circuitry as part of this supporting work, a malfunction was inadvertently induced which resulted in the charger output going to its maximum value. This abnormally high output voltage was briefly applied to Battery Board 3 and its associated loads before the charger was automatically tripped by electrical protective devices. As a result of the application of this abnormally high voltage, fuses of two Emergency Core Cooling System Analog Trip Unit (ECCS ATU) Inverters cleared. One of these ECCS ATU inverters supplied Unit 2 loads. With Unit 2 shutdown in a mid-cycle outage, the loss of this inverter had no operational impact. The other inverter supplied Unit 3 loads. These loads included the flow controller for the high pressure coolant injection (HPCI) system. The capability to control HPCI flow was lost as a consequence. The root causes of this event were: 1) the failures of personnel to identify all possible failure modes of the charger, 2) the work authorization process did not require a reassessment of the work activity following a change in the original work scope to include additional equipment. Operations, Maintenance, and Engineering personnel will be trained on the possibilities of introducing grounds into circuits via M&TE use. The work authorization process will be revised.
2982002001 | Cooper Station | 09/18/2002 | 01/29/2003 | ML03035061 | <strong>Loss of High Pressure Coolant Injection Safety Function Due to Gland Seal Condenser High Level Annunciation</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2002, at 1425 Central Daylight Time (CDT), with Cooper Nuclear Station (CNS) in Mode 1, Power Operation, at approximately 100 percent power (steady state), the Control Room received annunciator, "High Pressure Coolant Injection (HPCI) Gland Seal Condenser Hotwell High Level." In accordance with the alarm response procedure, the HPCI Auxiliary Oil Pump switch was placed in the Pull-to-Lock (PTL) position at 1428 CDT. The HPCI system was declared inoperable per Technical Specification. This event was initiated by the failure of a non-essential Gland Seal Condenser level switch. Upon completion of replacement of the level switch and post work testing of the system, HPCI was restored to operable status at 1339 CDT on September 20, 2002. The cause of the event is attributed to the procedure change process in place during 1993, which lacked the necessary rigor to ensure the design function of the Gland Seal Condenser was understood before adding the step to inhibit HPCI. The extent of condition was confined to this procedure. Process improvements since 1993 have corrected this deficiency. The alarm response procedure was revised to remove the step to inhibit HPCI which caused this event. The procedure revision was effective on December 27, 2002.
3012002001 | Point Beach 2 | 02/22/2002 | 04/18/2002 | ML02121043 | <strong>Completion of Nuclear Plant Shutdown Required by LCO 3.5.2 Required Action B.1</strong><br /><i>Abstract:&nbsp;</i>On 2/20/2002, at approximately 0100 (all times CST), the PBNP Unit 2 "B" train safety injection pump (2P-1 5B) was damaged while performing a monthly preventive maintenance procedure to ensure bearing lubrication. When the pump was started, motor current increased as normal, but then decayed to less than 10 amps. Based on this response, the control room operators secured the pump. In the field, an auxiliary operator monitoring the evolution heard a loud bang near the end of the pump coast down. He also observed excessive pump seal leakage following the test. The pump was declared out of service and LCO 3.5.2 was declared not met. TS Action Condition A.1 was entered which requires an inoperable ECCS train to be restored to an operable status within 72 hours. Subsequent inspection of the pump following disassembly of the casing revealed damage to the rotating element, the coupling and shaft keys between the pump and the motor, the pump internal wear rings, and other components. The apparent cause of the pump damage was gas binding of the pump as a result of back leakage of nitrogen-saturated fluid from the "A" SI accumulator through the pump discharge. Repair of the pump was initiated with the expectation that the pump could be returned to service within the 72 hours allowed. At 1400 on 2/22/2002, it was determined that we were unlikely to return the pump to service in the time remaining. Accordingly, at 1448 a shutdown of Unit 2 was initiated and the unit was in Mode 3 at 1926. The 2P-15B safety injection pump was subsequently returned to service on 2/24, and Unit 2 returned to service on 2/25/2002. Corrective actions to prevent recurrence include periodic venting of the SI pumps and discharge piping.
3012002002 | Point Beach 2 | 04/30/2002 | 10/28/2002 | ML02221016 | <strong>Pressurizer Safety Valve Failed to Lift at Test Pressure</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2002, a vendor conducting off-site testing of the Point Beach Nuclear Plant (PBNP) Unit 2 RCS pressurizer safety valves reported that safety valve 2RC-435 failed to lift at a test pressures up to 2660 psig. The lift pressure specification for this valve is from 2440 to 2551 psig. This valve had been last tested in November 2000 by the same vendor and, at that time, had been reported to be within specification. In accordance with the vendor's normal practice, following the set point test the valve is tested for seat leakage. If leakage is identified, the disc and nozzle are lapped to insure that the valve is leak tight with undamaged seats. In 2000 during the reassembly of the valve following this process, the valve was unknowingly rendered incapable of lifting within the specified pressure range. Following discovery of this failure in April, the other Unit 2 in-service safety valve was tested and found to lift within the specified range. The first valve assembly was corrected and the set point retested with satisfactory results. However, NMC concluded that Unit 2 operated for the entire cycle with only one operable pressurizer safety valve. The required design capacity for the RCS pressurizer safety valves assumes the use of 2 valves based on RCS pressure not exceeding the maximum code allowable 110% of design pressure for the maximum calculated in surge of reactor coolant into the pressurizer. This event is reportable both as a condition prohibited by the Technical Specification (LCO 3.4.10) and as an unanalyzed condition that had the potential to significantly degrade plant safety. Our safety assessment concluded that, for the FSAR Chapter 14 Loss of Load accident, although this safety valve was inoperable, the actual availability of the pressurizer power operated relief valves would have compensated for the pressure relief capacity of that safety valve, and the RCS pressure would not exceed the Tech Spec safety limit.
3022002001 | Crystal River 3 | 06/17/2002 | 08/14/2002 | ML02234054 | <strong>Automatic Start of an Emergency Diesel Generator Due to Loss of the Offsite Power Transformer</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2002, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER (RTP). An electrical storm was in progress. At 10:48, CR-3 experienced a loss of "A" Train off site power due to loss of the Offsite Power Transformer (OPT). The cause for loss of the OPT was a short during a lightning storm that resulted in relay actuation. During the lightning storm, the ground potential was raised to a point where pre-existing damage allowed a short to the ground conductor. Repairs were made and the OPT was returned to service. On July 20, 2002, FPC's CR-3 was in MODE 1 at 100 percent RTP. No electrical storm was in progress. At 16:45, CR-3 experienced a loss of "A" Train offsite power due to loss of the OPT. The cause for loss of the OPT was latent damage to the cable insulation from the lightning strike that caused loss of the OPT on June 17, 2002. Repairs were made and the OPT was returned to service. In both events, Emergency Diesel Generator EGDG-1 A automatically started and re-energized 4160v Engineered Safeguards (ES) Bus "A." Automatic actuation of EGDG-1A is reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. Corrective actions include an evaluation of cable replacement. No previous similar occurrences have been reported to the NRC.
3022002002 | Crystal River 3 | 11/07/2002 | 12/10/2002 | ML02352016 | <strong>Reactor Trip Due to Substation Generator Output Breaker Relay Mis-operation</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2002, Florida Power Corporation's (FPC's) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER (RTP). One of two 500 kilovolt (KV) substation generator output breakers (breaker 1662) was closed. The other 500KV substation generator output breaker (breaker 1661) was out of service for scheduled maintenance. At 14:39, a main turbine trip and subsequent anticipatory reactor trip occurred when breaker 1662 opened. The cause for opening of breaker 1662 was mis-operation of an Agastat 7024AC time delay relay contact used to remove power from phase-to-phase fault relay 39E and phase-to-ground fault relay 39F. Upon removal of the supply power to the Agastat relay, the relay contact created a voltage spike of the 39E relay power supply. Reactor Protection System actuation is reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. The Agastat relay has been replaced by a multi-function programmable relay to block the trip signal from the 39E and 39F relays when applying or removing control power and prior to de-energizing the relays. No previous similar occurrences have been reported to the NRC by CR-3.
3052002001 | Kewaunee | 01/10/2002 | 03/11/2002 | ML02079050 | <strong>Unanalyzed Condition: Strong Pump - Weak Pump Interaction Between Component Cooling Water Pumps</strong><br /><i>Abstract:&nbsp;</i>On 1/10/02, Nuclear Management Company (NMC) personnel determined that under certain operating conditions, the 'A' Component Cooling Water (CCW) pump discharge capacity overpowered the 'B' CCW pump. Consequently, with both pumps operating in parallel, the 'B' CCW pump was "dead-headed" against the unopened discharge check valve. At 1601 CST, on 1/10/02, NMC conservatively reported this condition to the Nuclear Regulatory Commission (NRC) in accordance with 10CFR50.72(b)(3)(ii)(B) as a condition that results in the plant being in an unanalyzed condition that significantly degrades plant safety. The design of the CCW system has been in place since original plant construction. It is apparent that the original designers failed to realize the potential design interaction from both pumps automatically starting on a Safety Injection signal or loss of offsite power condition. Additionally, NRC Bulletin 88-04 provided industry notice of the potential of this pump design interaction under minimum flow conditions. However, plant engineering staff failed to recognize the vulnerability of parallel pump operation under moderate system flow requirements. This condition was assessed with an incremental core damage frequency of 8.5E-7, which corresponds to a very low risk significance. NMC plans to implement a design change to prevent this pump-to-pump interaction. Kewaunee's root cause evaluation continues. Further cause determination efforts may reveal the need for additional administrative corrective actions.
3052002002 | Kewaunee | 05/05/2002 | 07/05/2002 | ML02192046 | <strong>Technical Specifications Required Shutdown: CCW System Leak Could Not Be Repaired Within LCO</strong><br /><i>Abstract:&nbsp;</i>On 5/5/02, Nuclear Management Company, LLC (NMC) determined that repairs to correct leaking tubes in the Component Cooling Water (CCW) system heat exchangers (Hxs) could not be completed within the Technical Specifications (TS) allowed outage time. Consequently, a conservative decision was made to shutdown the plant to repair the Hxs. A plant shutdown was completed at 1906 on 5/5/02 in accordance with guidance provided by TS. Leakage from the CCW system was discovered to exist through the 'A' CCW Hx to the service water (SW) system. SW is the engineered safety features (ESF) system, ultimate heat sink providing CCW cooling. Visual inspection of the Hx tubesheet area revealed a number of tubes with through-wall leaks near the tube ends. Further inspection revealed significant circumferential cracking in the tube to tubesheet hard roll transition region. Laboratory analysis of two sample tubes removed from the Hx determined the cracking was caused by stress corrosion cracking in the hard roll transition area. An extent of condition inspection of the 'B' CCW heat exchanger revealed similar cracking with no in-service detectable leakage. The Hxs were repaired by sleeving all the in-service Hx tubes. Further review of the need to replace the Hxs completely or in part is in progress. The CCW Hx leakage did not make the CCW system inoperable. Both heat exchangers remained available to perform their safety function in all probabilistic event scenarios. Except when removed from service for testing and maintenance, the Hxs remained available to provide their design function to remove heat from supported components. Since there was no failure to remove heat, there was no increase in risk as a result of this condition. The leakage of CCW water to the environment also posed no public health or safety risk. There was no radiological release consequence, and CCW release was consistent with approved release paths and flows.
3052002003 | Kewaunee | 12/05/2002 | 02/03/2003 | ML03042053 | <strong>Technical Specifications Action Requirements Not Followed - Inadequate Tech Spec Basis</strong><br /><i>Abstract:&nbsp;</i>On 12/5/2002 and 12/16/02, with the plant operating at 100% power, Nuclear Management Company (NMC) personnel determined that, in the past, Technical Specification (TS) 3.1.a.5, PORVs and PORV Block Valves, action requirements had not been implemented. This condition was discovered when questions were raised regarding the operability of the reactor coolant system (RCS) pressurizer (PRZR) power operated relief valves (PORVs) during surveillance testing. TS 3.1.5.a.5.A.2 requires "With one PORV inoperable due to causes other than excessive seat leakage, within 1 hour either restore the PORV = to OPERABLE status or close its associated block valve and remove power from the block valve." A review of surveillance testing and operating events determined that contrary to this requirement, controllers for the PORVs were placed in manual for greater than one hour without performing the action requirements to close and remove power from the associated block valve. The apparent cause for this event was an inadequate understanding of the bases for the PORV TS. Contributing causes included conflicting requirements for the TS and a failure to perform a thorough review of the TS change documentation. Corrective actions included initiating procedure changes to accurately reflect the TS requirements, reviewing other plant documents for changes that may be required, and initiating a TS change to remove the automatic operation requirement for the PORVs. An assessment was performed that determined the risk to Public Health and Safety as a result of this condition was insignificant. This report does not describe a safety system functional failure.
3112002001 | Salem 2 | 01/11/2002 | 03/11/2002 | ML02079050 | <strong>Technical Specification Shutdown Due to 2A Diesel Generator Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0303 on January 11, a plant shutdown in accordance with Technical Specifications was commenced. Limited Condition for Operation (LCO) action 3.8.1.1.b states, "...with one diesel generator ... inoperable,... restore the inoperable diesel generator to OPERABLE status within 72 hours or be in at least HOT STANDBY within the next 6 hours and in COLD SHUTDOWN within the following 30 hours." The 2A emergency diesel generator (EDG) had been taken out of service on January 8, 2002 at 0303 hours for a scheduled maintenance window to last 44 hours. On January 9, the 2A EDG experienced erratic speed and voltage control during post-maintenance testing and could not be repaired prior to exceeding the 72 hour LCO. At 0836 on January 11, Salem Unit 2 entered Mode 3. On January 12 at 1242 hours, the 2A EDG was returned to operable status and the cool down to Mode 5 was halted. The cause of the shutdown of Salem Unit 2 was attributed to a failure to diagnose and repair the cause of the EDG oscillations within the remaining LCO time following planned maintenance. Corrective actions associated with this event include replacement of the voltage regulator, procedure changes, preventive maintenance reviews and lesson learned discussions. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(A), "The completion of any nuclear plant shutdown required by the plant's Technical Specifications...".
3112002002 | Salem 2 | 04/20/2002 | 06/19/2002 | ML02177036 | <strong>Containment Internal Pressure Not Maintained Within Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>Salem Unit 2 operated in a condition prohibited by Technical Specification (TS) 3.6.1.4, "Internal Pressure," for periods from May 1999 until April 2002 due to inaccurate containment pressure indication. On April 20, 2002, PSEG Nuclear discovered that the instrument loop for the containment differential pressure indicator contained additional 250 ohm resistors. The effect of the additional resistors was to cause the indicated differential pressure to be one half of the actual differential pressure. The indicator is used by plant operators in controlling containment pressure within the limits specified in TS 3.6.1.4. This event resulted from the installation of an incorrect part as an equivalent replacement for an obsolete differential pressure alarm module. There were no safety consequences associated with this event. The containment differential pressure indicator is separate from the protective and engineered safety feature instrumentation systems, and the OPERABILITY of these systems was unaffected. Resistors were removed and all loop components were verified to operate properly.
3112002003 | Salem 2 | 05/21/2002 | 08/01/2002 | ML02226061 | <strong>Failure to Maintain Elements of the Salem Fire Protection Program</strong><br /><i>Abstract:&nbsp;</i>At approximately 1730 hours on May 20, 2002, preliminary test results were obtained for tracer gas tests being performed for the Unit 1 Elevation 78 Lower Electrical Penetration Area and the Unit 1 Elevation 64' 4160 Volt Switchgear Room. Results from these tests identified room leakage sufficient to prevent the carbon dioxide system in these areas from maintaining the required concentration of 50% for a hold time of 20 minutes as required by NFPA-12. At the time the results were presented, a review of data from tests being performed in the Unit 2 Elevation 78' Lower Electrical Penetration Area indicated that similar results would be expected for this area as well. An extent of condition review was performed considering that the primary leakage was through the CO2 isolation dampers and it was determined that the Unit 2 4160 Volt Switchgear Room, and the Unit 1 & 2 460 Volt Switchgear Rooms may also be affected such that these rooms may not be capable of maintaining the carbon dioxide concentration of 50% for the hold time of 20 minutes. As a result the carbon dioxide systems for these six fire areas were impaired and fire watches were established in accordance with the Fire Protection Program. The cause of the excessive leakage from these fires areas is a misapplication of the carbon dioxide isolation damper design (original design specification) for continued operation of the Switchgear and Penetration Area Ventilation (SPAY) system supply fans during a carbon dioxide discharge. Appropriate compensatory measures have been established in accordance with the fire protection program until design or configuration changes can be implemented to correct the excessive leakage.. This report is being made in accordance with Unit 2 License Condition 2.i, which requires reporting any violation of the Fire Protection Program (License Condition 2.C.10).
3132002001 | Arkansas 1 | 09/25/2002 | 11/18/2002 | ML02325020 | <strong>Main Steam Safety Valve As-Found Lift Settings Were Not Within Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>Prior to a scheduled refueling outage, testing revealed that the lift settings of eight of the sixteen Main Steam Safety Valves (MSSVs) were outside the plus or minus three percent Technical Specifications requirement. MSSVs that were not within one percent of their setpoint were adjusted and retested until repeatable lifts were within tolerance. Since lift values were both high and low, no single root cause for the condition could be determined. Potential failure modes were spring relaxation, seat bonding, excessive spindle run out, a change to a different type of test device and steam header pressure oscillations during the testing. An evaluation determined that the MSSVs would have performed their required safety functions with the as-found lift points, and safety analysis results would not have been invalidated. Additional testing and inspection of the MSSVs is planned in order to identify actions to improve performance.
3132002002 | Arkansas 1 | 10/04/2002 | 12/03/2002 | ML02344017 | <strong>Main Turbine trip Due to Binding of the Mechanical Trip Spool Valve resulted in an Automatic Actuation of the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>While performing the Main Turbine Overspeed Trip Test with reactor power approximately 42 percent, an automatic actuation of the Reactor Protection System (RPS) occurred. Upon completion of the Overspeed Trip Test, the trip/latch lever failed to fully reset and latch, thereby preventing restoration of the Auto Stop Oil System pressure. When the test lever was released, the turbine tripped resulting in a reactor trip. Plant response to the trip was normal and uncomplicated. The plant was stabilized in hot standby conditions. The direct cause for the Auto Stop Oil System pressure failing to be restored was determined to be binding of the mechanical trip spool valve in a partially tripped condition due to the buildup of corrosion particles and oil-based residue on the spool valve surfaces. The Auto Stop Oil System and the mechanical trip spool valve and associated components were inspected and cleaned or repaired as necessary. Preventive maintenance tasks will be developed requiring routine inspections and flushing of the Auto Stop Oil System. The event was determined to have had minimal safety significance.
3132002003 | Arkansas 1 | 10/07/2002 | 12/04/2002 | ML02340054 | <strong>Reactor Coolant System Pressure Boundary Leakage from a Crack in a Control Rod Drive Mechanism Nozzle Reactor Vessel Head Penetration Weld Due to Previous Weld Repair Method</strong><br /><i>Abstract:&nbsp;</i>Indication of boric acid was noted in the area of one Control Rod Drive Mechanism (CRDM) nozzle on the Reactor Vessel (RV) head during visual inspection at the start of a scheduled refueling outage. Other nozzles did not exhibit indications of leakage. Non-destructive examination (NDE) found indications of cracking in the nozzle that had resulted in Reactor Coolant System (RCS) pressure boundary leakage. NDE of all nozzles revealed indications in six others (not through-wall) and a likely porosity weld defect in another. Other than the porosity, all indications were from primary water stress corrosion cracking (PWSCC). The leaking nozzle had been repaired during the previous refueling outage. The root cause of the leakage was attributed to the design of the previous repair method that did not isolate all PWSCC susceptible material from the Reactor Coolant System. All nozzles with indications were repaired with improved design methods. The leakage did not result in wastage of the RV head. A new RV head fabricated with nozzle material and welds that are significantly more resistant to PWSCC has been purchased for installation in a future outage.
3132002004 | Arkansas 1 | 10/05/2002 | 12/04/2002 | ML02340048 | <strong>Reactor Coolant System Pressure Boundary Leakage from a Fatigue Stress Crack of a Weld Connecting a Drain Line to a High Pressure Injection Line</strong><br /><i>Abstract:&nbsp;</i>During inspections in the Reactor Building at the start of a scheduled refueling outage, a leak was discovered from a weld on a drain connection to a High Pressure Injection (HPI) line. The weld was removed and sent to an off-site laboratory. This evaluation determined that the cracked weld was from high cycle, low stress fatigue. Weld defects were present and were a major contributor to crack initiation. The weld had been in service for 12 years. The weld was replaced with an enhanced configuration to provide greater vibration resistance. Inspections of similar welds in the HPI lines revealed no other leakage indications. Vibration measurements during shutdown conditions, including HPI Pump full flow testing, indicated acceptable levels. Additional vibration measurements are planned. An evaluation concluded that the HPI System would have been able to provide adequate flow to the Reactor Vessel for potential accident scenarios even if the weld had failed completely.
3152002001 | Cook 1 | 01/25/2002 | 03/15/2002 | ML02091045 | <strong>Failure to Perform Ice Condenser Door Testing in Accordance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2001, as a result of questions from the NRC resident inspection team, it was determined that the surveillance requirements verifying the opening, closing, and frictional torque of the ice condenser inlet doors within the specified limits required by Unit 1 Technical Specifications 4.6.5.3.1.b.3, 4.6.5.3.1.b.4, and 4.6.5.3.1.b.5were not met. All of the ice condenser doors were refurbished during the extended outage and recent re-testing of the Unit 2 ice condenser doors adequately demonstrated that the ice condenser lower inlet doors are operable. The recent refurbishment of all ice condenser inlet doors for both units when coupled with the successful re-testing of the Unit 2 ice condenser inlet doors provided reasonable assurance that although not re-tested that the Unit 1 ice condenser doors would perform their safety function. Therefore, it has been determined that the failure to correctly test the ice condenser inlet doors for both units had minimal safety significance. The cause of the inadequate testing has been determined to be inadequate testing methodology and inadequate training of testing personnel. Corrective actions included re-testing of the Unit 2 ice condenser doors, revision of the applicable testing procedures, and enhanced training of testing personnel. Additionally, an Emergency License Amendment was issued providing a one time exception to the testing requirements specified in Unit 1 Technical Specifications 4.6.5.3.1.b.3, 4.6.5.3.1.b.4, and 4.6.5.3.1.b.5.
3152002002 | Cook 1 | 02/19/2002 | 04/19/2002 | ML02128049 | <strong>Pressurizer Power Operated Relief Valves Inoperable Due to Control Switch Position</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2002, stroke testing of the Unit 1 pressurizer power operated relief valve (PORV) block valves 1-NMO-152 and 153 was being performed in accordance with surveillance test procedure 01-IHP-4030-STP-053, "Pressurizer Power Operated Relief Valve Functional Test." During the test, a reactor operator noticed that the control switches for pressurizer PORVs 1-NRV-152 and 153 were positioned slightly to the left of the AUTO position. Subsequent investigation identified that the control switches had been out of position from February 6, 2002, to February 19, 2002. As such, the pressurizer PORVs were declared inoperable due to the loss of automatic function to control reactor coolant system pressure below the setting of the pressurizer code safety valves. This condition is reportable in accordance with 10 CFR 50.72(a)(2)(i)(B), for a condition prohibited by plant technical specifications. The cause of this event was the lack of awareness by the reactor operators to the potential for mis-positioning the pressurizer PORVs when placing the control switch in the AUTO position. This event has minimal safety significance since the Donald C. Cook Plant Nuclear Plant accident analyses do not take credit for the automatic actuation of the pressurizer PORVs for overpressure protection of the reactor coolant system. In addition, the valves would still be capable of operating in manual to mitigate a steam generator tube rupture accident. The Unit 1 pressurizer PORV control switches were restored to the AUTO position and the PORVs were declared operable. A lessons learned memo was issued to all plant operators regarding proper pressurizer PORV control switch manipulation. The appropriate procedures will be revised to re-order the restoration steps such that the pressurizer PORVs are placed in the AUTO position before the associated block valves are opened.
3152002003 | Cook 1 | 05/03/2002 | 06/28/2002 | ML02184001 | <strong>Main Steam Safety Valves Exceed Allowable Lift Setpoints</strong><br /><i>Abstract:&nbsp;</i>On May 2-3, 2002, with the unit at approximately 52% power, seven of twenty Main Steam Safety Valves (MSSVs) (EIIS:SB,RV) failed to meet Technical Specifications (TS) required lift settings specified in TS 4.7.1.1, Table 4.7-1. TS 4.7.1.1 allows a +/- 3% tolerance on the as-found lift setting and requires all tested valves to be set to a +/- 1 % as-left tolerance. Operations personnel entered the applicable TS Action Statement until each valve was adjusted and tested satisfactorily. In accordance with 10 CFR 50.73(a)(2)(i)(B), this condition is being reported as a condition prohibited by TS. The cause of the test failures was attributed to metallic bonding between the valve disc and the nozzle. Adjustments were made and all of the "as-left" lift settings were within the +/- 1 % acceptable range. No component was left outside of its acceptable range. The MSSVs ensure that the secondary system pressure will be limited to within 110% of 1085 psig during the most severe anticipated system operational transient. The as-found test results of the seven valves discussed in this LER were still well below the 110% design pressure value. Thus, there is reasonable assurance that the valves were capable of performing their primary safety function as well as maintaining an adequate heat sink for the primary side. Therefore, this event is not considered safety significant since the valves in question would have performed their function.
3152002004 | Cook 1 | 05/11/2002 | 06/28/2002 | ML02184003 | <strong>Unit 1 Ice Condenser Lower Inlet Door Test Failure</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2002, during the conduct of routine surveillance testing of the Unit 1 Ice Condenser, conducted in accordance with Technical Specification (TS), 4.6.5.3.1.b.3, the Donald C. Cook Nuclear Plant identified ice condenser door 15R failed its 40 degree opening force portion of the test. The failure of ice condenser door 15R was due to incorrectly adjusted tension springs. The springs were adjusted and ice condenser door 15R was successfully restested in accordance with TS 4.6.5.3.1.b.3. All remaining ice condenser doors were successfully tested and remained OPERABLE. Analysis has demonstrated that the failure of one door did not render the ice condenser INOPERABLE. Therefore, it has been determined that the failure of ice condenser door 15R had minimal safety significance.
3152002005 | Cook 1 | 06/14/2002 | 08/13/2002 | ML02226085 | <strong>Unit 1 Manual Trip Due to Trip of East Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>At 1443 hrs on June 14, 2002, Unit 1 was manually tripped following the trip of the East main feedwater (FW) pump (MFP). The East MFP tripped due to a loss of main feed pump turbine condenser vacuum caused by an influx of debris following the start of the #13 circulating water (CW) pump. On June 14, 2002, at 1751 hours, in accordance with 10 CFR 50.72 (b)(2)(iv)(B), a four-hour ENS notification (Event No. 38993) was made to the NRC for a condition that resulted in an actuation of the reactor protection system when the reactor is critical. The cause of this event was the transport of debris (primarily zebra mussel shells and sand) into the East MFP turbine condenser upon the start of the #13 CW pump. A contributing factor was the closure of 12-WMO-30 (the center lake water intake valve) a few days prior to the start of the #13 CW pump. The safety significance of this event was minimal since plant procedures and operator training provided sufficient direction for control room personnel to shutdown the plant and maintain it in a safe shutdown condition. In addition, this event had no impact on the ability of the main FW system to perform its feedwater isolation accident mitigation function. The Unit 1 East and West MFP turbine condenser tubes and waterboxes were cleaned on June 14, 2002. CNP will take actions to mitigate the effects of debris on CW pump startups with the unit on line. Specifically, precautions will be added to the CW system operating procedure to identify the potential vulnerability for debris intrusion associated with starting CW pumps with the unit on-line. The procedures will also include guidance for use of MFP turbine condenser waterbox lancing when starting a CW pump with a unit on-line.
3152002006 | Cook 1, Cook 2 | 06/12/2002 | 08/02/2002 | ML02220045 | <strong>Switchyard Fire Results in Violation of Technical Specification 3.0.5</strong><br /><i>Abstract:&nbsp;</i>On June 12, 2002, at 1345 hours, the "BC" 34.5 kilovolt (kV) circuit breaker opened and a trouble alarm for the TR101 CD reserve auxiliary transformer was received in the control room. This was caused by an explosion in the 345 kV switchyard and oil fire in the "L" switchyard output feeder breaker. This resulted in the loss of the preferred offsite power source to the Unit 1 East Essential Service Water (ESW) pump. Since the Unit 2 East ESW pump was out of service for planned maintenance to replace the pump, Unit 1 entered the 2-hour action requirement of Technical Specification (TS) 3.0.5 at 1345 hours. Subsequent protective switching by the system load dispatcher resulted in the loss of the preferred offsite power source to the Unit 2 West ESW pump and Unit 2 also entered the 2-hour action requirement of TS 3.0.5 at 1359 hours. Donald C. Cook Nuclear Plant (CNP) requested and received enforcement discretion from the NRC to extend the 2-hour allowed action time by 10 hours to allow sufficient time to restore the Unit 2 East ESW pump to an operable status and exit TS 3.0.5. This Licensee Event Report (LER) is being submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(i)(B) for operation or condition prohibited by the TS. CNP determined that compliance with TS 3.0.5 to place both Unit 1 and Unit 2 in Mode 3 within the time required by the action statement could initiate an undesirable transient. In addition, due to the degraded material condition of the switchyard at the time of the event, the risk associated with maintaining both units on line for an additional 10 hours was less than the risk associated with taking both Unit 1 and Unit 2 off line. Therefore, there was no net increase in risk associated with operating the plant for approximately 10 additional hours. CNP completed replacement and testing of the Unit 2 East ESW pump and exited TS 3.0.5.
3152002007 | Cook 1 | 06/23/2002 | 08/22/2002 | ML02241005 | <strong>Technical Specification 3.3.3.1 Required Special Report for Inoperable Radiation Monitors</strong><br /><i>Abstract:&nbsp;</i>This special report is being issued in accordance with the special reporting requirements specified in the Donald C. Cook Nuclear Plant (CNP), Technical Specification (TS), 3.3.3.1, Actions 22A and 22B. Specifically, radiation monitor 1-VRA-1310, "upper containment high range radiation monitor," was inoperable for a period of 11 days and radiation monitor 1-MRA-1702, "steam generator No. 3 power operated relief valve 1-MRV-233 outlet radiation detector and interface box," for a period of 79 days. Both radiation monitors were immediately returned to operable status. Corrective actions will revision of applicable procedure and training of technicians. In both cases TS 3.3.3.1 Actions 22A and 22B require a special report within 14 days of the monitors becoming inoperable as required by TS 3.3.3.1, Actions 22A and 22B. CNP's failure to issue the required special reports within the required 14 day time limit is being evaluated in accordance with CNP's corrective action program.
3152002008 | Cook 1 | 04/25/2002 | 08/01/2003 | ML03220025 | <strong>Failure to Complete Unit Shutdown as Required by Technical Specification 3.6.5.1</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2003, with Unit 1 in MODE 1, during an extent of condition review for LER 50-316/2003-004-00, "Weight of Ice Basket Below Minimum Allowed in Technical Specification (TS) 3.6.5.1," Donald C. Cook Nuclear Plant (CNP) discovered that on April 27, 2002, Unit 1 was not placed into shutdown action as required by TS 3.6.5.1. On April 25, 2002, Unit 1 was operating in MODE 1, with ice basket weighing in progress. Ice Basket 24-1-7 was weighed and discovered to be weighing 1099 pounds (lbs.), which is below the minimum acceptable weight of 1144 lbs. as specified in TS 3.6.5.1.d. CNP failed to recognize that this condition constituted a failure to meet the Limiting Condition for Operation (LCO) for TS 3.6.5.1 and did not enter the associated 48 hour LCO action for an inoperable ice bed. Accordingly, on April 27, 2002, Unit 1 was not shut down in accordance with TS 3.6.5.1. The cause for the failure to comply with the TS was human error. Procedure 12-EHP-4030-010- 262, "Ice Condenser Surveillance and Operability Evaluation," will be revised to include instructions that a low ice basket weight results in an entry into the action statement of TS 3.6.5.1. Training specific to TS 3.6.5.1 will be provided to the Operators. This condition is being reported in accordance with the reporting criteria specified in 10 CFR 50.73(a)(2)(i)(B) as a failure to meet the requirements of TS 3.6.5.1.
3162002001 | Cook 2 | 01/26/2002 | 03/28/2002 | ML02091021 | <strong>Containment Isolation Valve Alignment Error During Local Leak Rate Testing</strong><br /><i>Abstract:&nbsp;</i>On January 26,2002,during refueling outage 13,10 CFR 50 Appendix J, Type B and C leak rate testing was being performed in accordance with procedure 02-EHP-4030-234-203,"Unit 2 B &C Leak Rate. "This procedure requires root shutoff valve 2-GPX-301-V1 [EIIS:LK:SHV ] from the nitrogen supply manifold to be in the closed position for testing. When core alterations commenced, valve 2-GPX-301-V1 was thought to be tagged "Do Not Operate" in the closed position as required by procedure 02-OHP-4030-STP-041,"Refueling Integrity". Upon successful completion of the leak rate testing, an auxiliary equipment operator (AEO) found the root shutoff valve 2-GPX-301-V1 in the open position during the valve lineup restoration. This resulted in refueling integrity being lost while fuel movement was in progress. The control room was notified and core alterations were suspended. Based on investigation of this incident, the valve was mispositioned for approximately 10 hours. This breach of refueling integrity is prohibited by Technical Specification (TS) and is therefore reportable in accordance with 50.73(a)(2)(i)(B). The cause of this event was failure to follow procedures. The AEO performing the initial valve lineup for testing opened valve 2-GPX-301-V1 and inappropriately pulled the "Do Not Operate" tag from the valve contrary to the requirements of plant procedures 02-EHP-4030-234-203 and 02-OHP-4030.STP.041. Operations restored valve 2-GPX-301-V1 to the closed position, thereby re-establishing refueling integrity. A review of the completed B &C test lineups impacting refueling integrity was conducted and verified that no other loss of containment integrity had occurred during core alteration. A lessons learned memo was published and distributed to the auxiliary equipment operators. The human performance and personal accountability aspects of this issue have been appropriately addressed.
3162002002 | Cook 2, Cook 1 | 02/12/2002 | 04/12/2002 | ML02106014 | <strong>Technical Specification 3.9.4.c was Violated During Core Alteration</strong><br /><i>Abstract:&nbsp;</i>On February 12, 2002, Technical Specification (TS) 3.9.4.c was violated when the 100 PSI Control Air to Containment Control Air Header #2 Train 'B' Containment Isolation Valve, 2-XCR-101 [EIIS:LK:SHV], was stroked open during core alterations with open test connections on both sides of the valve, one inside containment and one outside. This configuration provided direct access from the containment atmosphere to the outside atmosphere. The apparent cause was determined to be ineffective procedural control (02-OHP-4030.STP.041). The preferred method for establishing refueling integrity for 2-CPN-74 in the procedure does not consider the possibility that the control air ring headers may be cross-tied. A contributing cause was that the installation of containment control air header cross-tie jumpers was not documented in the Proceduralized Temporary Modification Log on January 20, 2002. Upon discovery that the preferred method used to maintain refueling integrity for 2-CPN-74 was ineffective, an alternate method was established and valve 2-XCR-101 was visually confirmed to be intact and closed. The Temporary Modification Log Index was reviewed to verify that other Temporary Modifications were logged. The containment control air cross-tie jumpers were documented in the log at that time. The refueling integrity procedures will be revised to ensure that the methods used to establish refueling integrity for Penetrations CPN-74 and CPN-29 recognize that the Containment Control Air headers may be cross-tied. Unit 1 and Unit 2 Type B and C Leak Rate Testing procedures will be revised to ensure that steps are added for documenting the placement of the containment control air header cross tie jumpers in the Proceduralized Temporary Modification Log.
3162002003 | Cook 2 | 04/03/2002 | 05/29/2002 | ML02154019 | <strong>2AB 250-Volt D.C. Battery Inoperable for Longer Than Allowed by Plant's Technical Specification</strong><br /><i>Abstract:&nbsp;</i>During the weekly battery surveillance on April 3, 2002, a maintenance electrician identified cracks in the top cover between the post seals and the sample tubes of battery cells 27 and 102 of the 2AB 250-volt D.C. battery bank. The cracks were above the electrolyte with no indications of electrolyte leakage observed. The time of identification was 1200 on April 3, 2002. An action request was generated at 1530 on April 3, 2002, to document the deficiency. Shift manager notification was not made by the initiator or supervisor performing the approval as required by procedure. Operations became aware of the equipment deficiency at 1700 on April 4, 2002, when a deficiency tag was processed for the 2AB battery. The Shift Manager visually confirmed the cracking on cells 27 and 102, and identified, during an extent of condition inspection, that cell 35 exhibited the same cracking phenomenon. The 2AB battery was declared INOPERABLE at 1812 and Unit 2 entered technical specification (TS) action statement 3.8.2.3.b. A TS required shutdown commenced at 2114 on April 4, 2002, when the battery was not returned to an operable status. A four-hour ENS notification, event number 38832, was made at 2330 on April 4, 2002, in accordance with 10 CFR 50.72(b)(2)(i) for an initiation of a reactor shutdown required by the plant's TS. The TS required shutdown was terminated at 0145 on April 5, 2002, when a Notice of Enforcement Discretion (NOED) was granted by the Nuclear Regulatory Commission (NRC). In granting the NOED, the NRC would not enforce the allowed outage time in TS action 3.8.2.3.b for 13 hours, thereby providing an additional 11 hours for restoration of the 2AB battery to an OPERABLE status. The three cracked battery cells were replaced and 2AB battery was declared OPERABLE at 0755 on April 5, 2002. Unit 2 subsequently returned to full power.
3162002004 | Cook 2 | 01/19/2002 | 12/13/2002 | ML02352005 | <strong>Unanticipated Start of the Turbine Drive Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>At 00:01 hours on 01/19/02, in preparation for a Unit 2 refueling outage, Operations shift personnel initiated a planned manual reactor trip of Unit 2 from 22% power per Procedure 02-OHP-4021-001-003, Revision 15, "Power Reduction." Shortly thereafter, an automatic start of the turbine driven auxiliary feedwater pump (TDAFP) occurred as a result of a valid low-low level indication in the steam generators. The automatic start of the TDAFP was determined to be an "unanticipated" engineered safety feature (ESF) actuation. Steam generator levels rapidly recovered. Operators secured the TDAFP and throttled the flows from the motor driven auxiliary-feedwater pumps in accordance with plant procedures for reactor trip response and recovery. Reactor coolant system cooldown and depressurization proceeded normally. During the trip, pressurizer level shrank lower that procedurally anticipated, resulting in a reactor coolant system' letdown isolation. At 07:56 on 01/19/02, the Shift Manager made an eight hour, non-emergency notification to the NRC (EN# 38640) per 10 CFR 50.72(b)(3)(iv)(A) for an unanticipated ESF actuation. The cause of this event was inadequate procedural guidance. Corrective actions included revision of the applicable procedures to include a reduction in the planned power level trip point to reduce the potential for automatic start of the TDAFP.
3162002005 | Cook 2 | 05/12/2002 | 01/12/2004 | ML04029057 | <strong>Unit 2 Trip due to Instrument Rack 24-Volt DC Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>At 2301 hrs on May 12, 2002, Unit 2 tripped due to an instrument rack power supply failure. Specifically, the second of two redundant 24-volt direct current (VDC) power supplies to reactor control instrumentation control group cabinet 2-PS-CGC-16 failed. The failure of both power supplies caused steam generator (SG) feedwater regulating valve 2-FRV-210 to close. Unit 2 subsequently tripped on low water level in SG-21 coincident with low feedwater flow. In accordance with 10 CFR 50.72 (b)(2)(iv)(B), a four-hour ENS notification (Event #38915) was made to the NRC on May 13, 2002, at 0255 hours for an event or condition that resulted in an actuation of the reactor protection system (RPS) when the reactor is critical. As such, this LER is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(iv)(A) for a condition or event that resulted in an automatic actuation of the RPS system. The preliminary cause of this event was age-related failure of components within the power supplies. A contributing factor was that no provisions existed for periodic monitoring of the power supplies. This event had minimal safety significance since plant procedures and operator training provided sufficient direction for control room personnel to shutdown the plant and maintain it in a safe shutdown condition. The failed 24-VDC power supplies were replaced. The remaining 24-VDC control group power supplies in Unit 2 were inspected and one power supply was replaced. Routine tasks have been established to verify the availability of the 24-VDC power supplies for both Unit 1 and Unit 2.
3162002006 | Cook 2 | 07/22/2002 | 09/06/2002 | ML02255039 | <strong>Unit 2 Reactor Trip Due to Low Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>At 0045 hours on July 22, 2002, Unit 2 tripped due to low condenser vacuum. At the time of the trip, operators were performing a flush of the main condensers in preparation for the upcoming biocide treatment of the circulating water system. In accordance with 10 CFR 50.72 (b)(2)(iv)(B), a four-hour ENS notification (Event # 39081) was made to the NRC on July 22, 2002, at 0233 hours for an event or condition that resulted in an actuation of the reactor protection system (RPS) when the reactor is critical. As such, this LER is being submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(iv)(A) for a condition or event that resulted in an automatic actuation of the RPS system. The apparent cause of the event is a previously unrecognized steam side heat transfer anomaly in "C" main condenser that has resulted in "C" North water box removing significantly more heat than in "C" South water box. Corrective actions to prevent recurrence of this event will be determined by an equipment root cause investigation to be performed after the steam side of the "C" main condenser has been inspected during the next Unit 2 outage of sufficient duration. Additional corrective actions, including preventive actions, may be developed based on the results of the investigation. If significant changes are identified as a result of completion of the root cause investigation, an update to this LER will be submitted. As a compensatory action, the main condenser water box flushing and isolation procedure has been revised to provide improved guidance for performing these activities to minimize the possibility of a unit trip. The safety significance of this event was minimal. Plant systems responded per design with no significant anomalies noted. Plant procedures and operator training provided sufficient direction for control room personnel to shutdown the plant and maintain it in a safe shutdown condition. There was no impact on the health and safety of the public as a result of this event.
3162002007 | Cook 2 | 11/05/2002 | 12/13/2002 | ML02352003 | <strong>Unit 2 Technical Specification 3.8.1.1 Allowed Outage Time Exceeded</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2002, at 0827 hours, the Unit 2 CD Emergency Diesel Generator (EDG), was declared inoperable and Technical Specification (TS) 3.8.1.1, Action "b", was entered in preparation for routine surveillance testing in accordance with TS 4.8.1.1.2.a.5. Within approximately 10 minutes after reaching full load of 3500 kilowatts (kW) during the surveillance test, the CD EDG load began oscillating approximately 150 kW. The amount of time required to correct this condition exceeded the 72-hour allowed outage time requirements of TS 3.8.1.1, Action "b". Donald C. Cook Nuclear Plant (CNP) requested and received enforcement discretion from the Nuclear Regulatory Commission (NRC), to extend the 72-hour allowed outage time by an additional 72 hours. The purpose of this extension was to allow sufficient time to restore the Unit 2 CD EDG to operable status and exit TS 3.8.1.1, Action "b". CNP evaluated the described condition and determined that the risk of operating an additional 72 hours with the Unit 2 CD EDG unavailable was less than the risk associated with a plant shutdown. The apparent cause of the load oscillations was a failure of the electronic governing module in the EDG speed governing system. Corrective actions include replacement of the governor. A formal root cause analysis is in progress to ensure adequate corrective actions to prevent recurrence are identified and implemented.
3172002001 | Calvert Cliffs 1 | 03/08/2002 | 04/19/2002 | ML02115012 | <strong>Vital Bus Circuit Breaker Inoperable Due to Seismic Positioner Mounting</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2002, it was determined the 14B 480 Volt AC Vital Bus Supply Circuit Breaker (52-1413) was not operable since initial licensing of Unit 1 until breaker replacement occurred during maintenance on March 5, 2002. The 14B 480 Volt AC Vital Bus Supply Circuit Breaker (52-1413) was installed in the plant with the seismic positioner oriented upside down relative to the position in which the breaker was originally qualified for a Safe Shutdown Earthquake. This condition probably originated during field installation of the breaker during construction. Unit 1 was defueled when this condition was discovered. Unit 2 was operating at 100 percent power. Event investigation concluded the seismic positioner was installed incorrectly since initial construction and the breaker was inoperable but functional in all conditions except during and after a Safe Shutdown Earthquake. All safety-related 480 Volt AC circuit breakers have been inspected. No other seismic positioners were found out of position.
3172002002 | Calvert Cliffs 1, Calvert Cliffs 2 | 02/21/2002 | 04/18/2002 | ML02115010 | <strong>Potential High Pressure Safety Injection Pump Run-out Failure</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2002, a potential high pressure safety injection (HPSI) pump run-out failure mode was determined to exist if a large break loss-of-coolant-accident (LOCA) occurred during reverse flow testing of HPSI pump discharge check valves. The test resulted in a plant configuration where the non-tested HPSI pump was aligned to both HPSI headers. If a large break LOCA had occurred during the test, the remaining operable HPSI pump would have supplied coolant to both headers. High pressure safety injection pump flow-rate would have increased and probably caused the pump to fail due to run-out. High pressure safety injection pumps have been verified to operate satisfactorily at flow-rates up to 771 gpm. However, the increased flow-rate when injecting into two headers pushes the predicted flow above this value. It is not known at what flow-rate run-out failure of a HPSI pump would occur. This potential HPSI failure is caused by a procedural deficiency that has been present since startup. The test procedure has been changed to ensure that the operable HPSI pump is only aligned to it's own header during this test.
3172002003 | Calvert Cliffs 1 | 07/24/2002 | 09/17/2002 | ML02263011 | <strong>Reactor Trip Due to Loss of Reactor Coolant Pump Motor Oil</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2002, at approximately 1338 hours, Unit 1 received a low level alarm on 11A Reactor Coolant Pump (RCP) motor upper bearing oil reservoir. At approximately 1620 hours, Unit 1 Control Room Supervisor ordered a rapid downpower of Unit 1 in response to indications of increasing RCP motor thrust bearing temperatures. At 1628 hours, the Unit 1 Control Room Supervisor ordered a manual trip of Unit 1 when 11A RCP motor thrust bearing temperature reached 195 degrees Fahrenheit, in accordance with plant operating instructions. Unit 1 was manually tripped and all systems responded satisfactorily, with the exception of a turbine bypass valve, which closed slowly, causing Unit 1 Steam Generator pressures to approach the point of operator action to shut the main steam isolation valves. This event was caused by the failure of a butt weld on an RCP motor oil cooler line. The weld failure resulted in a through-wall crack that allowed lubricating oil to drain from the reservoir. This loss of oil resulted in oil starvation of the thrust bearing and subsequent overheating of the RCP motor thrust bearing.
3172002004 | Calvert Cliffs 1, Calvert Cliffs 2 | 08/27/2002 | 03/31/2005 | ML05096008 | <strong>Post-Accident Monitoring Instrumentation Not Seismically Connected</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2002, a condition was discovered that could have prevented the Unit 1 and Unit 2Post-Accident Monitoring System from fulfilling its safety function. Loose cable connectors for could have caused the Containment Area Radiation High Range Indicators 1(2)-RI5317A(B) connectors was the loss of channels to fail during a seismic event. The cause of the loose cable The pin retention springs are pin retention springs in the connectors due to time and normal use. required for the operability of each channel. Corrective maintenance performed on each channel indicated that retention springs were missing from all four channels. The affected channels remained in service, but would not have been operable from the time of discovery until completion of the post maintenance testing after the corrective maintenance. This condition was first identified on April 14, 2000 and ended on Febraruary 16, 2002 (Uint 1)and April 11, 2002 (unit 2). Analysis indicated that during this period the channels should have been declared out-of-service and a Technical Specification Limiting Condition for Operation should have been entered, but was not. The connectors were promptly replaced up onto prevent determination of cause. Maintenance procedure revisions will add measures recurrence of this condition.
3182002001 | Calvert Cliffs 2 | 01/24/2002 | 03/20/2002 | ML02081003 | <strong>Pump Flexible Drive Gear Wear Causes Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2002 during a routine inspection of Calvert Cliffs 2A Emergency Diesel Generator (EDG), it was discovered that the pump flexible drive gear that drives auxiliary pumps necessary for diesel operation, was pitted. The EDG was required to remain out-of-service for a time period greater than allowed under the plant's Technical Specifications. Enforcement discretion was requested and granted by Nuclear Regulatory Commission to allow the Unit to continue operation until February 2, 2002 while the pump flexible drive gear was replaced. The gear was replaced and 2A EDG was returned to service at 2:35 pm on January 31, 2002. The cause of the event was misalignment of the pump flexible drive gear. This caused abnormal pitting to occur on the pump flexible drive gear. The other similar EDGs at Calvert Cliffs were inspected for similar problems and none were found. A root cause analysis is in progress and additional actions will be implemented based on the results.
3212002001 | Hatch 1 | 02/08/2002 | 03/26/2002 | ML02093007 | <strong>Manual Reactor Scram Inserted Because of High Hydrogen Content in the Off-Gas System</strong><br /><i>Abstract:&nbsp;</i>On 02/08/2002, at 2252 EST, Unit 1 was in the Run mode at 27% rated thermal power (746 CMWt). At that time, the Reactor Protection System (RPS) was manually actuated to facilitate placing the Main Condenser mechanical vacuum pump in service. Prior to the reactor shutdown, on 02/08/2002, at approximately 2100 EST, degraded operation of the Main Condenser Off Gas Recombiner System had resulted in high hydrogen in the Off Gas. Procedure 34AB-N62-001-1S (FAILURE OF RECOMBINER AND CONTROL OF SUSTAINED COMBUSTION IN THE OFF GAS SYSTEM) was entered at about 2100 EST and licensed personnel proceeded to reduce reactor power from 100 percent rated thermal power beginning at about 2105 EST. Per the procedure, the in-service Steam Jet Air Ejector was removed from service at about 2200 EST due to Off Gas Hydrogen concentration reaching approximately 4%. Unit 1 was scrammed to facilitate placing the mechanical vacuum pump in service for maintaining the Main Condenser as the heat sink. The lowest Reactor Water Level during the scram was approximately 165 inches above the top of the active fuel (7 inches above instrument zero) this was above any ESF actuation settings. Therefore, no automatic ESF actuations were received and none were required. There was no Reactor Pressure increases during the scram. Reactor pressure following the reactor shutdown did not exceed the pre-event level of 1035 psig. The cause of the event was component failures that resulted in blocked drain lines in the off gas system. The blocked drain lines caused the recombining action to degrade resulting in high hydrogen in the off gas system. Corrective actions included restoring the off gas system drain lines.
3212002002 | Hatch 1 | 04/19/2002 | 06/13/2002 | ML02170023 | <strong>Technical Specification Required Plant Shutdown Because of High Unidentified Reactor Coolant System Leakage</strong><br /><i>Abstract:&nbsp;</i>On 4/19/02 at 1650 EST, Unit 1 was in the Run mode at a power level of approximately 525 CMWT (19 percent rated thermal power). Power was reduced in order to identify and repair the source(s) of leakage into the drywell floor drain sump. Limiting Condition for Operation (LCO) 3.4.4 establishes limits for both the increase in rate within a 24-hour period and the overall rate of unidentified leakage in the drywell. The leakage exceeded the allowable limits of Technical Specifications LCO 3.4.4. Therefore, at approximately 2100 EST a manual scram was inserted using the normal shutdown procedure, shutting down the unit as required by LCO 3.4.4, Required Action C. 1. A drywell entry was made, and on 4/20/02 at approximately 0036 EST it was determined that the source of drywell leakage originated from a leaking Safety Relief Valve (SRV) 1B21F013J. The tailpipe vacuum breaker (1B21F037J) associated with this SRV had failed in the stuck open position allowing steam to vent directly into the drywell. By 0146 EST, the drywell unidentified leakage rate was within the Technical Specification limits. The cause of SRV 1B21FO13J leaking was component failure. The valve's main disc was stuck in the partially open position. The actuator piston had become cocked on the main disc's stem causing it to bind in the valve body. The cause of the vacuum breaker (1B21F037J) failing was determined to be the result of leakage past the main seat of SRV 1B21FO13J. This leakage caused the vacuum breaker to rapidly cycle open and closed which caused the bolts holding the disc to the swing arm to break. The safety relief valve and the vacuum breaker were replaced and functionally tested.
3212002003 | Hatch 1, Hatch 2 | 08/08/2002 | 11/22/2002 | ML02331055 | <strong>Main Steam Line High Flow Setpoint Not Within Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On 8/8/2002, at 1400 EDT, with Unit 1 and 2 in the Run mode at a power level of 2763 CMWt, the plant Architect Engineer notified Southern Nuclear that the setpoints for the main steam line high flow Group I isolation had previously been non-conservative, due to the use of an incorrect discharge coefficient for the main steam line flow nozzles. The error was discovered by General Electric during an independent review of Technical Specifications allowable values and analytical limits for a thermal power optimization program. Previous investigations into the potential problem had resulted in a conservative resetting of the actual in-plant main steam line high flow setpoints on 8/6/2002. At the time of the notification, therefore, the actual plant setpoints were set correctly. The cause of this event could not be conclusively determined. It is believed to be personnel error that involved a transposition of numbers. Corrective actions included a pre-emptive reset of the setpoints and continuing a review of Instrument and Controls calculation.
3212002004 | Hatch 1 | 08/14/2002 | 09/12/2003 | ML03259073 | <strong>Turbine Overspeed Control Valve of the High Pressure Coolant Injection System Fails</strong><br /><i>Abstract:&nbsp;</i>On 8/14/02 at 1419 EDT, Unit 1 was in the Run mode at a power level of approximately 2763 CMWT (100 percent rated thermal power). Prior to this time on 8/14/02 at 0125 EDT, the High Pressure Coolant Injection (HPCI, EIIS Code BJ) system weekly auxiliary oil pump run was performed in accordance with procedure 34SV-SUV-019-0. During a system walk down at 1419 EDT on 8/14/02, oil was discovered on the floor beside the Unit 1 HPCI skid. The oil reservoir level was found below the low level mark. During a subsequent troubleshooting run of the auxiliary oil pump, hydraulic control fluid sprayed out of the hydraulic actuator of the turbine overspeed trip control valve, lE41-F3082. The HPCI System was declared inoperable following the discovery of the leaking 1E41-F3082 valve actuator. The turbine overspeed trip control valve was repaired. Subsequently, the auxiliary oil pump was started and the system checked for leakage and for proper system pressures with no anomalies identified. The HPCI system was then declared operable on 8/15/02, at 0900 EDT. The cause of the event was a failed hydraulic actuator diaphragm. Corrective actions for this event included the replacement of the failed diaphragm, and the establishment of a requirement to periodically replace these diaphragms. SNC has installed a newer style diaphragm on Unit 2, and scheduled the installation of this newer style diaphragm on Unit 1 during the next system outage.
3212002005 | Hatch 1 | 10/10/2002 | 12/06/2002 | ML02344023 | <strong>Water Level Transient Following Manual Reactor Scram Causes Group 2 PCIS Isolation</strong><br /><i>Abstract:&nbsp;</i>On 10/10/2002 at 2220 EST, Unit 1 was in the Run mode at an approximate power level of 1341 CMWT (48.5 percent rated thermal power). At that time, Operations personnel manually scrammed the reactor per procedure 34GO-OPS-013-1S, "Normal Plant Shutdown," for a planned Unit outage for the replacement of three Safety Relief Valve (SRV) main bodies. Following the manual scram, water level decreased due to void collapse from the rapid reduction in power, reaching a minimum of approximately minus 10 inches (about 148 inches above the top of the active fuel). The decrease in water level resulted in receipt of a Group 2 Primary Containment Isolation System (PCIS) isolation signal and closure of the Group 2 Primary Containment Isolation Valves per design. The operating Reactor Feedwater Pump restored level to its desired value. Personnel reset the Group 2 isolation signal and restored the isolation valves to normal per procedure 34AB-C71-001-1S, "Scram Procedure." This event was the result of the expected water level decrease from void collapse and proceduralized operator action following a reactor scram. Operations personnel increased water level to approximately 45.5 inches, about eight to ten inches above the normal operating level, in anticipation of the level decrease. Nevertheless, water level decreased to a point below the Group 2 PCIS isolation setpoint. Personnel actions were in accordance with approved procedures. These procedural instructions will be evaluated for revision, if needed, to improve the methodology used for reactor vessel level control during planned shutdowns.
3232002001 | Diablo Canyon 2, Diablo Canyon 1 | 08/31/2001 | 01/15/2002 | ML02043005 | <strong>Fasteners Failed Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2001, with Unit 2 in Mode 1 (Power Operation) at 100 percent power, a PG&E employee investigating a steam leak discovered a broken stud on a valve bonnet for a steam generator 10 percent atmospheric steam dump valve. Investigations found the remaining seven bonnet fasteners had cracks in either the studs or nuts. On October 3, 2001, based on results from multiple Charpy impact tests of fasteners in similar service, PG&E concluded the material had become embrittled. The fasteners failed due to Stress Corrosion Cracking (SCC). PG&E has determined that the SCC was caused by a combination of unanticipated high temperature embrittlement and elevated stress in the presence of corrodants. Ten years of operation at temperatures of as low as 470 degrees F embrittled the ASME SA 564, Type 630, Condition H1100 (17-4 PH) stainless steel material, causing increased susceptibility to SCC. Higher than expected stress was presumably caused by inadequate administrative controls over the maintenance torquing practices. Corrective actions include replacing embrittled material in plant locations where it is highly susceptible to SCC, and/or exposed to significant impact loads at low temperature. Also, maintenance practices are being revised to enhance torquing practices.
3232002002 | Diablo Canyon 2 | 02/09/2002 | 07/10/2002 | ML02205011 | <strong>Unit 2 Manual Reactor Trip Due To Loss of Main Feedwater to a Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2002, at 0337 PST with Unit 2 in Mode 1 (Power Operation) at 100 percent power, plant operators initiated a manual reactor trip due to failure of main feedwater regulating valve (MFRV) FW-2-FCV-540 that isolated feedwater to steam generator 2-4. A 4-hour, non-emergency report was made to the NRC on February 9, 2002, at 0709 PST in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 50.72(b)(3)(iv)(A).Safety systems responded as required, except for an expected automatic reactor trip based on steam generator low level, which is evaluated in LER 1-2002-001, dated April 15, 2002, as referenced in sections II.B. and IV of this LER. The immediate cause of the failure was excess current in the coil of Asco solenoid valve (SV) SV-540B, which caused failure of a power fuse and forced the FCV-540 to close. The excess current in the SV was caused by failure of the insulation due to thermal aging degradation. Immediate corrective actions included replacing a failed fuse and the SV. Corrective actions to prevent recurrence include: 1) revising the environmental qualification (EQ)calculation and re-evaluating the replacement period for Asco SVs; 2) replacing Asco SVs or their coils for the MFRVs and bypass valves during the next refueling outage for each unit; 3) reviewing the adequacy of other EQ calculations prepared by the same individuals; and 4) reevaluating preventive maintenance frequencies for all continuously energized EQ solenoid valves. An additional prudent action was completed to prep area case study to communicate lessons learned from the inadequate EQ calculation.
3232002003 | Diablo Canyon 2 | 08/22/2002 | 12/16/2005 | ML05364008 | <strong>Technical Specification 3.7.7 Not Met due to Cable Fault</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2002, at 0332 PDT with Unit 2 in Mode 1 (Power Operation) at 100 percent power, Required Action A.1 for Technical Specification 3.7.7, Vital Component Cooling Water (CCW) System, was not met when the completion time was exceeded due to a cable fault. On August 19, 2002, after receiving brief CCW Pump 2-3 ground alarms, operators started CCW Pump 2-1, shut down Pump 2-3, and declared CCW Pump 2-3 inoperable until the cause could be determined. On August 21, 2002, in response to a request for enforcement discretion, the NRC granted verbal enforcement discretion for 72 hours until the motor feeder cable replacement and post-maintenance testing could be completed. On August 23, 2002, at 1342 PDT, repairs and testing were completed, and CCW Pump 2-3 was declared operable. The immediate cause of the event was a ground fault in the "C" phase power cable to CCW Pump 2-3, resulting in pump inoperability. Immediate corrective actions included replacing all three phases of the CCW Pump 2-3 cables. The root cause of the event was a manufacturing defect based on the presence of isolated contaminant particles in the insulation. Corrective actions to prevent recurrence include replacing 4kV cables in both units.
3232002004 | Diablo Canyon 2 | 11/08/2002 | 12/23/2002 | ML03003046 | <strong>Manual Start of Unit 2 AFW Pumps Due to Ocean Debris and High Swells</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2002, at 0633 PST, with Unit 2 in Mode I (Power Operation) at 20 percent reactor power, operators manually tripped the turbine due to indications of high differential pressure on the traveling screens at the intake structure. Operators also manually tripped both circulating water pumps resulting in a loss of condenser. In accordance with the abnormal operating procedure for loss of normal heat sink, operators manually shut down the reactor and started the motor driven auxiliary feed water pumps. PG&E has developed extensive models to help predict the impact of Pacific Ocean storms, and to give adequate time to prepare for such events. PG&E anticipated the potential adverse affects from high swells and ocean debris, and had reduced power to 20 percent to facilitate a plant shutdown if necessary, without a reactor trip. PG&E cannot entirely eliminate the potential need to manually shut down the reactor when high seas and dislodged plant life from the ocean floor result in heavy debris loading on the traveling screens. Therefore, there are no corrective actions to prevent recurrence.
3242002001 | Brunswick 2 | 11/01/2002 | 12/23/2002 | ML02360043 | <strong>Instrumentation Malfunction Results in Loss of Safety Function for the High Pressure Coolant Injection System</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2002, at approximately 1641 hours, a Unit 2 High Pressure Coolant Injection (HPCI) Steam Line Flow-High analog trip unit (Rosemount Model 510DU7A010) malfunction resulted in a HPCI Steam Supply Outboard Isolation valve closure and HPCI system inoperability. The plant responded as designed to the event. Plant operators entered the appropriate Technical Specification Limiting Conditions for Operation and the trip unit was replaced. By November 2, 2002, at 0542 hours, the HPCI system was returned to service and declared operable. The safety significance of this occurrence is considered minimal. The cause of the HPCI system isolation and inoperability is attributed to the spurious actuation of the analog trip unit due to the malfunction of the output transistor. Further testing and evaluation is in progress to better understand the failure mode and establish appropriate action thresholds. The special process procedure for monitoring analog trip unit output voltages will be revised to incorporate the updated thresholds. The scope of analog trip unit and/or output transistor replacement activities will then be determined and corrective actions initiated as appropriate.
3242002002 | Brunswick 2 | 12/19/2002 | 02/14/2003 | ML03056064 | <strong>Remote Shutdown Panel Power Supply Inverter Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>During a review of the impact of electrical faults on the systems required to safely shutdown the facility in the event of a control room fire, it was determined that an existing inverter design is incompatible with the center tap design of the ungrounded DC electrical system. Specifically, a postulated fire that results in an electrical short of the Unit 2 Division 2 125/250 VDC distribution system to ground can potentially result in the loss of automatic or manual control of the Reactor Core Isolation Cooling (RCIC) turbine at the Remote Shutdown Panel (RSDP). The current fire safe shutdown analysis credits the RCIC system for post-fire inventory control during a worst-case main control room fire. The postulated loss of the RSDP RCIC control capability is considered an unanalyzed condition. The cause of the condition is attributed to the failure to recognize and incorporate critical design characteristics into the design specification. The affected inverter has been modified to eliminate the potential for inverter failure as a result of hard grounds on the 125/250 VDC distribution system. Other installed inverters with susceptible surge suppression will be modified in accordance with the work management process. Additional corrective actions include training and communication of the issue with appropriate individuals and applicable procedure and process enhancements. The actual and potential safety significance of this condition is considered minimal.
3252002001 | Brunswick 1 | 11/22/2002 | 01/20/2003 | ML03028065 | <strong>Oscillation Power Range Monitor (OPRM) Inoperability Due to Non-Conservative Setpoint</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2002, GE Nuclear Energy (GE) identified a reportable condition in accordance with 10 CFR 21.21(d) (i.e., SC02-21, "Stability Option III: OPRM Train Specification"). SC02-21 states that the Stability Option III period based detection algorithm (PBDA) range for minimum period of detection (i.e., Tmin) values specified in Licensing Topical Report NEDO-31960-A, "BWR Owner's Group Long-Term Stability Solutions Licensing Methodology (Supplement 1)," was non-conservative and recommended that the Oscillation Power Range Monitor (OPRM) be considered inoperable if the Tmin value is set greater than 1.2 seconds. Stability Option III is installed on Unit 1 and the Tmin value was set at 1.4 seconds. Therefore, at 1328 Eastern Standard Time (EST) on November 22, 2002, all OPRM channels were declared inoperable in accordance with Technical Specification (TS) 3.3.1.1, "Reactor Protection System (RPS) Instrumentation," and an alternate method to detect and suppress thermal hydraulic instability oscillations was placed into effect as directed by Condition I of TS 3.3.1.1. Subsequently, the Tmin value was changed to 1.2 seconds and all OPRM channels were declared operable at 0917 EST on November 27, 2002. The safety significance of this occurrence is considered minimal. The apparent cause of the event is an incomplete analysis, performed by GE, when establishing oscillation period ranges to be used for the PBDA.
3272002001 | Sequoyah 1, Sequoyah 2 | 02/15/2002 | 04/12/2002 | ML02106049 | <strong>Westinghouse Electrical Corporation Error Results in Nonconservative Steam Generator Level Setpoint</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2002, Sequoyah performed an assessment of the narrow range steam generator level measurement instrument channels, based on a Nuclear Safety Advisory Letter from Westinghouse Electric Corporation. This assessment determined that the demonstrated accuracy calculation for low-low level trip setpoint narrow range span did not account for the measurement bias associated with the differential pressure (dP) created by the steam flow past the mid-deck plate in the moisture separator section of the steam generators. This dP phenomena could cause the steam generator narrow range level channels to read higher than actual water level at high steam flows. This could cause the low steam generator level trip setpoint to be nonconservative. The cause of the condition was the failure of Westinghouse personnel to account for the measurement bias, when establishing the low-low steam generator level setpoint calculation. TVA will modify the steam generator setpoints, as applicable, to account for the identified condition.
3272002004 | Sequoyah 1, Sequoyah 2 | 07/12/2002 | 09/10/2002 | ML02254049 | <strong>Automatic Reactor Trip Resulting from a Failure of a Breaker Causing an Undervoltage Condition on Two Reactor Coolant Pumps and Failure to Perform a Technical Specification Required Action</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2002, at 2223 Eastern Daylight Time, an automatic reactor trip occurred on Unit 2 as a result of an undervoltage condition on two reactor coolant pumps. The undervoltage resulted from the loss of power to Start Bus 2B, when the alternate feeder breaker attempted to close while being racked into the connect position. This closure attempt caused the normal feeder breaker to trip open, resulting in a loss of bus voltage initiating the reactor trip. When Start Bus 2B deenergized one offsite power source became inoperable. Operations personnel did not verify the availability of the remaining offsite power sources. The main control room operators took appropriate actions to stabilize the reactor in hot standby. The cause of the reactor trip was the failure of the alternate feeder breaker for Start Bus 2B to function properly when being returned to its normal configuration. The cause of failing to verify the availability of the remaining offsite power sources was supervisor duties were improperly focused, as priorities were placed on restoring off-site power and the diesel generators to normal alignment. A diagnostic of the breaker is being performed. The breaker will be repaired or replaced as necessary.
3282002002 | Sequoyah 2 | 05/19/2002 | 06/19/2002 | ML02176010 | <strong>Manual Reactor Trip Resulting from the Failure of Control Rods to Respond</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2002, at 0447 Eastern Daylight Time the Unit 2 reactor was manually tripped as a result of a Rod Control System Urgent Failure Alarm on Shutdown Bank B and Control Bank D. During performance of low power physics testing, Operations personnel attempted to insert shutdown rod bank B, when the rod control urgent alarm actuated. After actuation of the alarm, operators identified that group two of shutdown rod bank B would not move. With shutdown rod bank B not able to be inserted, a slight positive reactivity existed. Operations personnel decided to insert Control Bank D to insert negative reactivity. The Group 2 control bank rods would not move. As previously discussed, the reactor was manually tripped based on not being able to insert group two rods in control bank D and shutdown bank B with a slight increasing reactivity trend. The main control room operators took appropriate actions to stabilize the reactor in hot standby (Mode 3). The most likely cause of the condition appears to be an intermittent failure of the multiplexing relay in the rod control system. The multiplexing relay was replaced.
3282002003 | Sequoyah 2 | 05/31/2002 | 07/29/2002 | ML02217073 | <strong>Automatic Reactor Trip Resulting from a Generator Stator Cooling Water High Temperature Caused by a Raw Cooling Water Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2002, at 0116 Eastern Daylight Time the Unit 2 turbine tripped followed by a reactor trip as a result of an actuation of the main generator stator cooling water failure circuit. Prior to the trip, Operations personnel observed increased temperature on the generator stator cooling water system. Indications show that the generator stator cooling water temperature reached the setpoint then actuated as required. The main control room operators took appropriate actions to stabilize the reactor in hot standby (Mode 3). The generator stator cooling water high temperature was the result of a raw cooling water isolation valve failure causing low flow to the stator cooling water system heat exchanger. The raw cooling water valve was replaced.
3282002004 | Sequoyah 2 | 12/26/2002 | 02/04/2003 | ML03042048 | <strong>Reactor Trip Resulting From the Loss of a Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>On December 26, 2002, at 1620 Eastern Standard Time, the No. 3 reactor coolant pump (RCP) tripped because a neutral over-current condition on the No. 3 RCP motor. The loss of the No. 3 RCP resulted in a reactor coolant system low flow and subsequent automatic reactor trip. A feedwater isolation and auxiliary feedwater start occurred, as designed. Control room operators responded to the event in accordance with plant procedures. They promptly diagnosed the plant condition, took the actions necessary to stabilize the unit, and maintained the unit in hot standby, Mode 3. The cause of the event was a neutral over-current condition on the No. 3 RCP motor. The motor was replaced and the unit was returned to service.
3312002001 | Duane Arnold | 03/08/2002 | 04/25/2002 | ML02130034 | <strong>Unplanned Mode Change While Re-Aligning the RHR System from Shutdown Cooling (SDC) Mode to Low Pressure Coolant Injection (LPCI) Standby Readiness During Reactor Startup</strong><br /><i>Abstract:&nbsp;</i>In preparing to transition from Mode 4 to Mode 3, the Control Room Operators had secured Shutdown Cooling (SDC). The running recirculation pump and decay heat were raising Reactor Coolant System (RCS) temperature as expected. During the realignment of Low Pressure Coolant Injection (LPCI), Residual Heat Removal (RHR) Crosstie Valve, V19-0048, could not be opened. The inability to open this valve prevented the restoration of LPCI to standby readiness. The inability to place LPCI in standby readiness meant that the transition to Mode 3 would result in a violation of Technical Specification 3.0.4 and a failure to meet Technical Specification Surveillance Requirement 3.5.1.2. Operators were unable to restore SDC in time to prevent the transition to Mode 3 as RCS temperature momentarily exceeded 212 degrees Fahrenheit. The cause of this event is the failure of a setscrew in the manual operator of the RHR Crosstie Valve V19-0048. The setscrew did not hold the yoke sleeve nut in place. The yoke sleeve nut had backed off its threads and fallen onto the valve stem preventing normal operation of the valve. Recommended corrective actions include inspection of V19-0048 and similar manual valves to ensure that the setscrews are secure. There were no actual safety consequences associated with this event.
3312002002 | Duane Arnold | 08/05/2002 | 10/03/2002 | ML02288004 | <strong>Technical Specification Required Shutdown Due to Residual Heat Removal Service Water (RHRSW) Strainer Plugging Caused by Algae Intrusion from the Cedar River</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2002, with one loop of Residual Heat Removal Service Water (RHRSW) already inoperable, the other (redundant) loop was declared inoperable for the same reason. As a result, a plant shutdown was initiated and completed in accordance with the plant's Technical Specifications (TS). The cause of the event was the introduction of large amounts of algae into the RHRSW system strainers. Strainers in the pump discharge paths became clogged with the algae during routine testing, resulting in high differential pressures across the strainers. Per plant procedures, operators considered the strainers inoperable, which led to both RHRSW loops being declared inoperable, even though TS required cooling water flow rates could still be achieved. Corrective actions included cleaning the strainers, chemical treatment of the incoming river water that supplies the RHRSW system, and inspections and cleaning of service water pits where algae is likely to grow or settle. There were no actual safety consequences associated with this event. Potential consequences were minimal due to the ability to achieve TS required flow rates and procedural steps in place to bypass the strainers had the need arisen. The plant commenced startup on August 11, 2002.
3312002003 | Duane Arnold | 09/02/2002 | 10/31/2002 | ML02311010 | <strong>Technical Specification Required Shutdown Due to Reactor Core Isolation Cooling Inoperability Caused by Air Entrainment in the RCIC Oil System</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2002, Technical Specification (TS) LCO 3.5.3 Condition A, Reactor Core Isolation Cooling (RCIC) System Inoperable, was entered for two days of planned maintenance. Following completion of maintenance, RCIC system operability testing failed on August 21, 2002 due to air entrainment in the oil system. Troubleshooting activities continued for the next twelve days. On September 2, 2002, TS LCO 3.5.3 Condition B, was entered following failure of RCIC post startup operability testing due to oil system flooding and a plant shutdown was initiated. RCIC oil system modifications were made on September 5 and 6, 2002. RCIC testing was performed satisfactorily and TS LCO 3.5.3 Condition B was exited on September 9, 2002. The introduction and entrainment of air in the RCIC oil system was the cause of the repeated RCIC test failures. DAEC site personnel were unable to resolve the air entrainment issues within a 14 day period. This resulted in a plant shutdown per TS LCO 3.5.3 Condition B. RCIC oil system modifications were made to reduce and release entrained air. Procedural and programmatic changes have been initiated to improve the site's response to plant events. There was no impact on public health and safety associated with this event.
3332002001 | FitzPatrick | 07/22/2002 | 07/31/2003 | ML03226065 | <strong>Both Trains of Core Spray and One RHR Pump inoperable Due to Out of Tolerance Pump Start Time Delay Relays</strong><br /><i>Abstract:&nbsp;</i>On July 22, 2002, with the reactor at 100 percent power, during the performance of the Core Spray (CS) Initiation Logic System Functional Test 3J (ST-3J), it was determined that the time delay for both “A” and “B” division CS pump start time delay relays exceeded the values required by Technical Specifications (TS). As part of the extent of condition evaluation on August 24, 2002, with the reactor at 100 percent power, the "C” and “D” Residual Heat Removal (RHR) Pump Start Timer Temporary Surveillance Test 120 (TST-120) was performed on the associated pump start time delay relays. During this test, it was determined that the time delay for the "D” RHR pump start time delay relay exceeded the value required by TS by 0.03 seconds. The equipment related root cause of the out of tolerance condition was a lack of relay "exercising” due to the extended test interval of the relays. The human performance related root cause was failure to assume the relay drift was time dependent, as required by procedure. A contributing cause was identified as inadequate guidance in a calculation verification checklist that allowed operating experience considerations to be neglected. Interim corrective actions included recalibrating the CS and RHR relays and increasing their test frequency. Long-term corrective actions include replacement of the subject relays with a more suitable device and revising the associated calculation verification process.
3342002001 | Beaver Valley 1, Beaver Valley 2 | 09/25/2002 | 11/15/2002 | ML02323031 | <strong>Silt Levels in Main Intake Structure Exceed Allowable Values</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2002, it was determined that previously measured silt levels in three bays of the Beaver Valley Power Station (BVPS) Main Intake Structure had exceeded acceptable limits to assure adequate inflow from the Ohio River into the Intake Structure bays in order to provide sufficient ultimate heat sink cooling needs during the design basis/licensing basis bounding extreme low river water event. This was identified during follow-up evaluations of issues raised during a Latent Issues design review of the BVPS Service Water System. Even though the Ohio River has never approached the design basis/licensing basis extreme low water level, the BVPS Unit 1 safety related River Water System and the BVPS Unit 2 safety related Service Water System must have adequate ultimate heat sink capability to adequately support the bounding low probability low river water level design basis/licensing basis postulated scenario. Current BVPS design analyses show that adequate inflow to the suction of the River/Service Water System pumps may not be assured with greater than 22 inches of solid blockage in an Intake Structure bay. Previously identified as-found silt levels in Intake Structure bays have exceeded 22 inches. This represents a potential unanalyzed condition that could significantly degrade plant safety. Therefore, this is being reported pursuant to 10 CFR 50.73 (a)(2)(ii)(B). The cause of this event was inadequate/incomplete design aspects. The accumulation of silt in the Intake Structure is only a potential concern during an extreme low river water level condition. The probability of an extreme low river water level is small. The silt is considered to form a completely solid dam as a conservative assumption. However, the silt is not qualitatively expected to be capable of forming a solid dam if an extreme low river water level condition were to occur. The safety significance of prior conditions where the Intake Structure silt levels exceeded 22 inches in the past was low.
3342002002 | Beaver Valley 1 | 11/11/2002 | 01/08/2003 | ML03014013 | <strong>Manual Reactor Trip During Planned Shutdown Due to Turbine Motoring Alarm</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2002, Beaver Valley Power Station (BVPS) Unit 1 was performing a planned power reduction from full power at a rate of approximately 12 percent per hour for a scheduled maintenance outage. At approximately 1946 hours, the plant was at 53 percent power and the Turbine Motoring Condition alarm was received. An automatic turbine trip will occur if this alarm is received for more than 30 seconds. An automatic reactor trip will also occur following a turbine trip signal, if the plant power level is above 49 percent power. After approximately 20 seconds from the time of the alarm, the Control Room Unit Supervisor directed a manual reactor trip. Control room personnel implemented Emergency Operating Procedure E-0 for a reactor trip. The Auxiliary Feed Water System actuated as expected and all other systems functioned as required. An investigation into the event determined that the turbine motoring condition alarm was caused by a failure of the turbine differential pressure instrument that measures the differential pressure between the turbine impulse pressure and the turbine exhaust. The failure was due to a misapplication of the instrument to the service conditions. The failed instrument was replaced with a new instrument more suited for the application. The manual initiation of a reactor trip via the Reactor Protection System by the BVPS Unit 1 control room operator on November 11, 2002, was a valid manual reactor trip signal and was not part of a pre-planned sequence during testing or reactor operation. Therefore this event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). The safety significance of the manual reactor trip on November 11, 2002 was small.
3352002001 | St. Lucie 1 | 09/28/2002 | 11/06/2002 | ML02329038 | <strong>As-Found Cycle 17 Main Steam Safety Valve Setpoints Outside technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2002, St. Lucie Unit 1 was in Mode 1 and holding at approximately 6 8 percent reactor power for Technical Specification testing of the main steam safety valves setpoints. Two main steam safety valves lifted outside the Technical Specification limits of +1 percent to -3 percent. Main steam safety valves V8203 and V8214 failed low by small deviations. The cause of the low as-found setting was setpoint drift. V8203 and V8214 were overhauled and reinstalled during the refueling outage. Operation of the facility with the as-found setting was within analytical bounds. Therefore, this event had no impact on the health and safety of the public.
3352002002 | St. Lucie 1 | 10/24/2002 | 12/23/2002 | ML02360045 | <strong>Manual Reactor Trip on Low Steam Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2002, St. Lucie Unit 1 was in Mode 1 at approximately 6 percent reactor power during power ascension at the end of refueling outage SL1-18. Attempts to "latch" the turbine were unsuccessful, and the resultant turbine trip signal drove the 15 percent main feedwater bypass valves to the post-trip position. Steam generator levels rose and the operating main feedwater pump tripped on high steam generator -water level. The operators tripped the reactor when the steam generator water levels dropped below the procedural trip requirements during the efforts to restore feedwater. The cause of this event was the failure of the turbine valves to latch and latent procedural weaknesses in that the adverse consequences of a "partial latch" condition were not addressed. The failed turbine latch initiated the chain of events that ultimately led to the manual reactor trip. Corrective actions include the completed repair of the turbine front standard latch function, procedure enhancements, continuing training, and potential plant modifications to the 15 percent main feedwater bypass valve controller.
3362002001 | Millstone 2 | 02/19/2002 | 04/16/2002 | ML02121050 | <strong>Two Reactor Coolant System Pressure Boundary Leakage Events</strong><br /><i>Abstract:&nbsp;</i>This LER reports two events related to Reactor Coolant System (RCS) pressure boundary leakage. On February 19, 2002, with the plant in Mode 5 (Cold Shutdown), a visual inspection of Millstone Unit No. 2 pressurizer heater penetrations and pressurizer instrument nozzle penetrations was being performed. Two heater sleeve penetrations were found to show indications of minor leakage as evidenced by boron precipitation build up on the outside of the penetrations. The cause of this event was a through wall crack in two of the pressurizer heater sleeves. This allowed primary coolant into the annulus between the pressurizer lower head and the heater sleeve and therefore was a breach of the reactor coolant pressure boundary. The leaking heater sleeves have been repaired by the use of Mechanical Nozzle Seal Assembly (MNSA) clamps. Additionally, On February 22, 2002, with the plant in Mode 6 (Refueling), helium leak tests were performed on the "A" and "C" Reactor Coolant Pump (RCP) seal coolers and thermal barrier heat exchangers in an effort to identify the source(s) of the leakage from the RCS into the Reactor Building Closed Cooling Water (RBCCW) system. This testing confirmed leakage on the "C" RCP. The RCP seal cooler is part of the RCS pressure boundary. It is likely that the leak is in the drilled hole heat exchanger. The cause of the leak is uncertain. The leaking "C" RCP cover and rotating element (which contains the RCP seal cooler) was replaced with a rebuilt spare. Subsequent to Millstone Unit No. 2's return to power operation, there has been no detectable evidence of reactor coolant ingress to the RBCCW system. The system is continuously monitored for radioactivity via an in-line detector, and water samples are analyzed weekly for long term trending of radioactive contamination in accordance with IE Bulletin 80-10.
3362002002 | Millstone 2 | 04/19/2002 | 06/18/2002 | ML02179003 | <strong>Reactor Trip Due to Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2002, with the plant operating at approximately 99.5 percent power, a turbine trip resulted in an automatic reactor trip when a temperature switch in the Stator Water Cooling System tripped on a high value. The temperature switch in the Stator Water Cooling System was found with a trip setpoint value approximately 14°C lower than the acceptance criteria found in the calibration procedure. Following the reactor trip, main steam reheat valves, 2-MS-2A and 2-MS-2B, did not close as expected and had to be manually closed, resulting in an unexpected RCS cooldown. Auxiliary Feedwater automatically initiated to compensate for a low level in the Steam Generators caused by shrinkage. Required safety equipment functioned as expected and this event is considered to be of low safety significance. The cause of this event is indeterminate. The presumptive causes are either an equipment failure or insufficient oversight and controls that led to calibration errors. Following the reactor trip, the temperature switch was tested and re-calibrated to the proper setpoints prior to plant restart. To prevent recurrence the stator coolant temperature switch from both Millstone Unit Nos. 2 and 3 will be replaced. The Unit No. 2 device will then be sent to the vendor for a failure analysis. In addition, separate procedures will be developed for secondary plant instruments that are trip sensitive at Unit Nos. 2 and 3.
3362002003 | Millstone 2 | 05/22/2002 | 07/18/2002 | ML02212025 | <strong>Failure to Comply with Technical Specification Action Statement for One Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2002, with the Unit in Mode 1 at 100% power and one emergency diesel generator (EDG) inoperable due to planned EDG testing, Operations personnel failed to perform verification of offsite power sources within one hour as required by Technical Specification (TS) 3.8.1.1, action b.1. The action to verify offsite power sources is met by completion of surveillance requirement 4.8.1.1.1 which calls for verification of correct breaker alignment and indicated power available for each required offsite circuit. This human error was caused by an inadequate procedure design. Although the surveillance procedure requires the user to determine the applicability of TS 3.8.1.1, there is no specific step or sign-off to ensure that the action statement is met. The corrective action to prevent recurrence is to revise the monthly EDG surveillance procedures to provide an action step to complete the one hour offsite circuit TS action statement before proceeding further with the procedure. Personnel involved in the event were counseled. Upon discovery of this condition, approximately three and three quarter hours into the diesel testing, appropriate action was taken to complete the missed verification activity required by TS 3.8.1.1, action b.1, and the required offsite power sources were determined to be available. Off-site power sources remained available at all times during the EDG testing.
3362002004 | Millstone 2 | 08/03/2002 | 10/02/2002 | ML02284018 | <strong>Reactor Shutdown Due to Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2002 at 1213, a controlled shutdown was commenced due to an entry into Technical Specification (TS) 3.0.3. The entry into TS 3.0.3 was due to two leaks at socket welded tee and elbow fittings in the charging header. The cracking of the welds is an industry known susceptibility associated with the use of socket welds in the charging system. The cause of the weld failures was high cycle fatigue resulting from high vibration levels induced by the positive displacement charging pumps. The release due to the leak did not exceed limits as specified by the offsite dose calculation manual, and therefore, had negligible impact on the dose to the public. The flow rate through the charging header remained at the design flow rate while borating the Reactor Coolant System to the required plant condition and associated shutdown margin. The system demonstrated its functionality by meeting the system requirement of injecting boric acid at a flow rate greater than what is required for operability. Therefore, this event did not constitute a safety system functional failure and was not safety significant. The two failed welds were replaced and the two downstream elbows and their welds were also replaced. All repaired welds were replaced with reinforced leg socket welds to reduce the likelihood of recurrence of cracking at these specific locations. As an interim corrective action to prevent recurrence, an anti-vibration clamp was installed on the header piping.
3362002005 | Millstone 2 | 08/07/2002 | 10/03/2002 | ML02290044 | <strong>Automatic Reactor Trip Due to Low Steam Generator Level During Power Ascension</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2002, with the plant operating in Mode 1 and in power ascension at approximately 55 percent power, an automatic reactor trip occurred due to low steam generator level. Post trip procedures were followed and the plant responded normally without any engineered safety feature actuation. Prior to the event, feedwater was being supplied to the steam generators by the "A" steam generator feedwater pump (SGFP).The event took place during the startup sequence of the "B"SGFP. The discharge flow from the SGFPs is fed into a common header which in turn is sent through the No.1 feedwater heaters and then to the steam generators. The SGFPs are each protected from reverse flow by a check valve,2-FW-1A and B. Downstream of the check valves are motor operated isolation valves,2-FW-38A and B.As part of the startup sequence for placing the "B"SGFP in service, the operators opened the motor operated isolation valve, 2-FW-38B. Almost immediately, steam generator level deviation alarms were received. The operators commenced closing 2-FW-38B, but the time for the motor operated valve closure was not sufficient to recover steam generator levels prior to the reactor trip. The cause of the loss of feedwater flow to the steam generators was the failure of the "B"SGFP discharge check valve (2-FW-1 B) due to an inadequate anti-rotation weld. The root cause is that the organization failed to install adequate anti-rotation welds in the SGFP discharge check valves in 1990. The SGFP discharge check valves were inspected and repaired with improved anti-rotation welds.
3382002001 | North Anna 1, North Anna 2 | 06/25/2002 | 08/06/2002 | ML02233052 | <strong>Incorrect Waste Gas Decay Tank Oxygen Analyzer Setpoint Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2002, at 1330 hours, with Units 1 and 2 in Mode 1 operating at 100% power, it was identified that the alarm setpoint for the Waste Gas Decay Tank (WGDT) Oxygen Analyzer may allow the tank oxygen to exceed the limit of Technical Specification (TS) 3.11.2.5. TS 3.3.3.11 requires the oxygen monitor to be operable with the alarm setpoint set to ensure the limits of TS 3.11.2.5 are not exceeded. TS 3.11.2.5 requires that the concentration of oxygen in the WGDTs be limited to less than or equal to 2% by volume whenever the hydrogen concentration could exceed 4% by volume. Calibration and functional test procedures specify a voltage with an acceptable range of +/- 0.5% for ensuring the oxygen analyzer is set to meet TS requirements. However, use of the upper end of the acceptable range may cause the TS limit of less than or equal to 2% oxygen to be exceeded. This event is being reported as a condition prohibited by TS in accordance with 10CFR50.73(a)(2)(i)(B). The cause of the event is attributed to personnel error that resulted in the establishment of inadequate procedures that did not satisfy TS requirements. The action statement of TS 3.3.3.11 was entered and the alarm setpoint was subsequently adjusted to within the TS limit. No significant safety consequences resulted from this event because the WGDT oxygen concentration remained below TS limits. The health and safety of the public were not affected at any time during this event.
3382002002 | North Anna 1, North Anna 2 | 08/16/2002 | 10/11/2002 | ML02296042 | <strong>Incorrect Low Temperature Overpressure Protection Setpoints Due to Inadequate Procedures</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2002, at 1000 hours, with Units 1 and 2 in Mode 1 operating at 100% power, it was identified that the Low Temperature Overpressure Protection System (LTOPS) setpoints for the Pressurizer Power Operated Relief Valves (PORV) may have exceeded the Technical Specification (TS) limits. On August 30, 2002, a review of completed Unit 1 and 2 calibration procedures from the previous three years identified six occasions where the temperature enable or pressure lift settings for the PORVs were outside of the TS limits by a very small margin. This event is being reported as a condition prohibited by TS in accordance with 10CFR50.73(a)(2)(i)(B). The cause of the event is attributed to personnel error that resulted in the establishment of procedures where non-conservative application of allowed tolerance to the setpoint resulted in not satisfying TS requirements. No significant safety consequences resulted from this event because the PORVs would have lifted within the limits established by the Safety Analysis Limits for the system. The health and safety of the public were not affected at any time during this event.
3392002001 | North Anna 2 | 09/14/2002 | 11/06/2002 | ML02318048 | <strong>Reactor Vessel Head Leakage Due to Hot Short Cracking and Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On September 8, 2002, North Anna Unit 2 was shutdown for a scheduled refueling outage. A qualified, visual barehead inspection of the reactor vessel head and penetrations was performed to identify evidence of leakage as required by NRC Bulletin 2001-01. On September 14, 2002, with Unit 2 in Mode 6, the qualified, visual barehead inspection on penetrations 21 and 31 identified through-wall leakage based on the presence of boric acid deposited on the reactor head at these penetrations. A non emergency 8-hour notification was made to the NRC, at 2214 hours, on September 14, 2002, in accordance with 10CFR50.72(b)(3)(ii)(A). The event is also reportable in accordance with 10CFR50.73(a)(2)(i)(B). The apparent cause of the event was hot-short cracking, which occurred during original fabrication of the reactor vessel head, that was accelerated by primary water stress corrosion cracking. Corrective action is to replace the reactor head. No significant safety consequences resulted from this event since RCS unidentified leakage was well below Technical Specification limits. No safety concerns exist since cracking that is contained entirely in the weld metal would not lead to nozzle ejection. The health and safety of the public were not affected at any time during this event.
3412002001 | Fermi 2 | 03/08/2002 | 05/07/2002 | ML02135023 | <strong>HPCI and RCIC Room Area Temperature Switches Beyond TS Allowable Value</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2002, at approximately 1430 hours, technicians (utility, non-licensed) performing a Channel Functional Test on Division I High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) Room Area High Temperature switches (E41N602A and E51N602A) found the temperature switch setpoint to be set above the Technical Specification (TS) allowable value. The cause of the temperature switches being set beyond TS allowable values was found to be a loose battery connection in a test instrument. HPCI and RCIC room area temperature isolation is provided to detect a small leak from the associated HPCI or RCIC system steam piping. The isolation is diverse from the steam line high flow instrumentation. The Division I HPCI and RCIC room area temperature isolation channels would have functioned at a slightly higher setpoint. During the time the Division I temperature switch setpoints were incorrect the Division II HPCI and RCIC room area temperature isolation channels were available, except during their Channel Functional Test. There was no condition that would have prevented an isolation from occurring. The room area high temperature isolation functions are not assumed in any UFSAR transient or accident analysis. Division II temperature switch setpoints were verified to be correct and Division I temperature switches were immediately adjusted to within their required setpoints. Corrective actions being considered are to add verification steps to procedures and include lessons learned into the Maintenance Initial and Continuing Training Program.
3412002002 | Fermi 2 | 02/19/2002 | 06/26/2002 | ML02190039 | <strong>Fire Protection Dedicated Shutdown Valve Accessibility Impacted by Field Modification</strong><br /><i>Abstract:&nbsp;</i>As a result of a fire protection program self assessment, on May 2, 2002, Detroit Edison Company determined that a field modification performed on February 19, 2002 invalidated an inherent assumption in the procedure for controlling the plant from the dedicated shutdown panel. Specifically, the motor operator for motor operated valve (MOV) N2000F636, Condenser Hotwell Emergency Makeup Bypass Valve, was rotated 180 degrees to help alleviate an oil leakage problem. Rotating the MOV relocated the motor operator handwheel away from the first floor of the Turbine Building such that operators could not reasonably close the valve without the use of a ladder. Procedure 20.000.18, "Control of the Plant from the Dedicated Shutdown Panel," directs operators to de-energize and manually close N2000F636 to prevent losing Condensate Storage Tank (CST) water inventory to the Hotwell, in case a hot short caused the valve to open. Losing CST inventory threatens the ability to achieve safe shutdown conditions in the event of a fire. Therefore, this condition is reportable under Section 2.F of the Fermi 2 Operating License as a violation of License Condition 2.C.(9). Based on the short delay associated with obtaining a ladder and closing the valve, this condition did not result in any adverse effect on the health and safety of the public. A dedicated ladder has been staged near the valve. Other corrective actions involve the identification of Appendix R components in the plant CECO database, additional training and guidance on dealing with Appendix R components, and periodic verification of the steps in procedure 20.000.18.
3412002003 | Fermi 2 | 06/28/2002 | 08/26/2002 | ML02248027 | <strong>Breaching of Control Room Emergency Filtration (CREF) System Ductwork Integrity</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2002, Division 1 Control Room Emergency Filtration (CREF) system was started to support a Post Maintenance Test. Following the system start, a Nuclear Operator reported unusual noise from the Division 1 Control Center Heating, Ventilation and Air Conditioning (CCHVAC) Return Air Fan. Vibration analysis concluded that the most probable cause was a failing fan outboard bearing. The fan was shutdown and Division 1 CREF system was declared inoperable. A work request was initiated which identified the need to open an access panel in the fan ductwork. The access panel had to be unlocked and opened to allow access to the fan outboard bearing. The work request was reviewed and authorized by Operations. At 2152 hours, control room pressure increased and control room pressure alarms were received. A Nuclear Operator was dispatched to evaluate the Division 1 CREF system maintenance activities and noted that the access panel was open. Evaluation of the pressure response of the Division 2 CREF system identified that opening the access panel on the Division 1 Return Air Fan duct work resulted in unfiltered, bypass leakage into the Division 2 CREF system. Technical Specification 3.0.3 was entered due to both divisions of CREF system being inoperable. Immediate actions were taken to close the access panel and reestablish CREF system ducting integrity. Analysis of the event identified deficient knowledge of CREF system divisional interrelationship and inadequate implementation of the work control process as the causes.
3412002004 | Fermi 2 | 10/02/2002 | 05/07/2003 | ML03134057 | <strong>Reactor Scram Due to Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2002, at 1453 hours, the reactor scrammed from 100 percent power. Condenser pressure increased when Circulating Water Pump (CWP) 2, one of four running CWPs, failed. Condenser pressure exceeded the main turbine trip setpoint. The main turbine tripped, resulting in a reactor scram. Prior to the scram at 1452 hours the Circulating Water Header Low Pressure annunciator was received. The Condenser Pressure High annunciator was received and control room operators (licensed, utility) entered the Abnormal Operating Procedure for Loss of Condenser Vacuum. The main turbine automatically tripped causing a reactor scram on main turbine control valve fast closure. All safety systems responded as expected. All rods fully inserted into the core. Reactor level decreased below Level 3, resulting in expected isolation signals. After the reactor scram, condenser vacuum recovered. Reactor level was recovered with the Feedwater/Condensate System. No Emergency Core Cooling Systems initiated and no Safety Relief Valves lifted. The cause of the event was a failure of CWP 2. This event is being reported in accordance with 10 CFR 50.73 (a)(2)(iv)(A), as an event that resulted in manual or automatic actuation of any systems listed in paragraph (a)(2)(iv)(B), i.e., actuation of the Reactor Protection System including reactor scram or reactor trip. The cause of the CWP failure was fatigue failure of the diffuser casing to column bolts due to insufficient or loss of pre-load.
3412002005 | Fermi 2 | 11/21/2002 | 01/16/2003 | ML03023065 | <strong>Non-Conservative Setpoint for Stability Option III (OPRM) Period Based Algorithm - T(min)</strong><br /><i>Abstract:&nbsp;</i>The General Electric Company submitted a 10 CFR Part 21 notification identifying that they had determined that the stability Option III period based detection algorithm (PBDA) range for minimum period of detection (Tmin) values that they had specified may be non-conservative, and recommended that the Average Power Range Monitor (APRM) Oscillation Power Range Monitor (OPRM) Upscale trip (Technical Specification Limiting Condition for Operation (LCO) 3.3.1.1, function 2.f) be considered inoperable for plants with Tmin set at greater than 1.2 seconds. In response, all OPRM channels we're declared inoperable on November 21, 2002 because the Fermi 2 OPRM Tmin value was set at 1.4 seconds. Alternate methods to detect and suppress thermal hydraulic instability oscillations were placed into effect in accordance with Technical Specification 3.3.1.1, Action J. The apparent deficiency identified in the Tmin value was discovered during recent calculations performed by General Electric in support of extended power uprate analyses for other plants. The newly identified shorter period oscillations have decay ratios of less than 0.8; and therefore, are not of concern. Additionally, the operators have been trained to recognize instabilities and to take appropriate actions should an instability occur. Therefore, this event had no safety significance. Tmin was changed to 1.2 seconds, and all OPRM channels were declared operable on December 19, 2002.
3412002006 | Fermi 2 | 12/29/2002 | 02/21/2003 | ML03059025 | <strong>Manual Reactor Scram During Reactor Shutdown to Repair Modular Power Unit 3</strong><br /><i>Abstract:&nbsp;</i>On December 28, 2002, at 0440 hours, a low voltage condition was discovered on Modular Power Unit. Investigation into this condition concluded that the 120 VAC voltage (MPU) 3, Distribution Cabinet 2. Investigation into this condition concluded that the 120 VAC voltage regulator associated with MPU 3 had degraded such that the output voltage was93 VAC. MPU 3 is a non-Class 1E 120 VAC Instrumentation and Control Power (ICP) System that provides related Balance of Plant (BOP) instrumentation and control loads including several control circuits, indicators and. It was concluded that a loss of the feedwater pumps and the circulating recorders in the control roomwater pumps could occur if operation were allowed to continue, or if on line repair was attempted. Reactor power was reduced to approximately 73 percent using recirculation flow. Further power reduction using control rods was then attempted when it was found that control rods could not be moved using the Reactor Manual Control System (RMCS). The inability to manually move rods during the power reduction was attributed to the degraded voltage on MPU 3. The normal power reduction was stopped and the reactor was manually scrammed on December 29, 2002, at 0010 hours. All other systems responded as expected. Following shutdown, the voltage regulator in MPU 3 was bypassed under a temporary modification to allow an upstream voltage regulator associated with its normal power supply, Bus 72 F, to control the MPU 3 voltage.
3462002001 | Davis-Besse | 02/14/2002 | 04/11/2002 | ML02107024 | <strong>Main Steam Safety Valve Setpoints Greater Than Allowable Values</strong><br /><i>Abstract:&nbsp;</i>On February 14 and 15, 2002, with the unit in Mode 1 at approximately 95 percent power, setpoint testing determined four of the Main Steam Safety Valves (MSSVs) had a setpoint more than three percent above the desired setpoint. These setpoints exceeded the ASME Code allowable value, rendering the valves inoperable in accordance with the Technical Specifications. The setpoint of each MSSV was adjusted to within one percent of the desired setpoint upon discovery, as necessary. Based on the as-found lift setting pressures, the Main Steam System pressure would not have exceeded previously evaluated values during any anticipated overpressure transients. The three MSSVs with the highest initial setpoint appeared to have experienced oxide bonding between the stainless steel valve disk and nozzle seat. These three MSSVs were removed and replaced with valves that have inconel valve seats, which are less susceptible to oxide bonding. The valve disks of the remaining MSSVs will be replaced during the next two refueling outages with the inconel valve disks. The fourth MSSV that lifted high was due to inherent test methodology inaccuracies during previous tests. More accurate test equipment will be used in the future. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3462002002 | Davis-Besse | 02/27/2002 | 04/29/2002 | ML02122008 | <strong>Reactor Coolant System Pressure Boundary Leakage Due to Primary Water Stress Corrosion Cracking of Control Rod Drive Mechanism Nozzles and Reactor Pressure Vessel Head Degradation</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2002, at 1330 hours, ultrasonic (UT) examination of the Control Rod Drive Mechanism (CRDM) nozzles revealed axial indications in the J-groove weld and Alloy 600 nozzle resulting in pressure boundary leakage for CRDM nozzle #3. This was reported within 8 hours, at 1542 hours, as a non-emergency condition in accordance with 10CFR50.72(b)(3)(ii)(A). On March 5, 2002, a follow-up notification was made to report completion of the UT examinations and through pressure boundary axial indications in the Alloy 600 nozzles at CRDM nozzles #1 and #2. On March 8, 2002, a further notification was made in accordance with 10CFR50.72(b)(3)(ii)(A) to report degradation of the Reactor Pressure Vessel (RPV) head. These events are being reported in accordance with 10CFR50.73(a)(2)(ii)(A) as a condition that resulted in the nuclear power plant, including its principal safety barriers, being seriously degraded and 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The apparent cause of the axial flaws resulting in pressure boundary leakage was determined to be Primary Water Stress Corrosion Cracking (PWSCC). The root cause of the RPV head condition is boric acid corrosion resulting from moisture introduced due to PWSCC cracking of CRDM nozzle #3. The CRDM nozzles and the RPV head will be repaired prior to returning the DBNPS to service from the current refueling outage. Industry and NRC assessments have previously concluded that axial flaws do not present an immediate safety concern. Therefore, the discovery of these flaws alone has minimal safety significance. The as-found condition of the RPV head was assessed and would have functioned to maintain the RPV head structural integrity during anticipated operational occurrences and postulated accidents.
3462002003 | Davis-Besse | 03/11/2002 | 05/09/2002 | ML02135013 | <strong>Fuel Movement in Spent Fuel Pool Without Required Door Attendant</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2002, with the unit in Mode 6 it was identified that a designated individual was not available immediately outside the personnel air lock to close the door as required by the Technical Specifications. Upon discovery, a designated individual was immediately dispatched. Technical Specifications require two independent Emergency Ventilation Systems (EVS) servicing the spent fuel pool area to be operable; otherwise movement of fuel in the spent fuel pool area is prohibited. The EVS can be considered operable with the containment equipment hatch open and both doors of the containment personnel air lock open, provided that a designated individual is available immediately outside the personnel air lock to close the door. Closure of the airlock door ensures that the EVS can establish a negative pressure boundary in a timely manner following a fuel handling accident. The EVS remained capable of exhausting and filtering air from the fuel handling area during this event; therefore this event had low safety significance. This condition, which is a result of human error, is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
3462002004 | Davis-Besse | 05/23/2002 | 07/22/2002 | ML02205034 | <strong>Containment Isolation Closure Requirements for RCP Seal Injection Valves MU66A-D</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2002, with the reactor in Mode 6, it was determined that the pressure regulating valve setpoint for the Reactor Coolant Pump (RCP) Seal Injection Valves (MU66A-D) was inadequate to ensure closure of the valves upon receipt of a containment isolation signal. This condition represents a potential common-mode failure. As the result of this condition, during postulated accident conditions, a potential pathway for uncontrolled radioactive leakage outside containment could be created. This condition has apparently existed since original plant construction. This condition is a violation of Technical Specification 3.6.3.1 for Modes 1-4. In addition, the valves were determined to be installed inconsistent with design assumptions. The causes of these conditions are less than adequate design interface communication and design control. Design basis requirements for Category 1 and 2 Air Operated Valves (AOVs) and their associated components will be established in accordance with the AOV Reliability Program Manual. MU66A-D, MU38, and all other Category 1 and 2 AOVs will be verified to conform to their design basis requirements or component modifications will be made to restore conformance with design basis requirements.
3462002005 | Davis-Besse | 09/04/2002 | 05/21/2003 | ML03147007 | <strong>Potential Clogging of the Emergency Sump Due to Debris in Containment</strong><br /><i>Abstract:&nbsp;</i>On September 4, 2002, with the reactor defueled, investigations determined that a gap in the sump screen larger than allowed by design basis (greater than 1/4-inch openings) existed. Also, the existing amount of unqualified coatings and other debris inside containment could have potentially blocked the emergency sump intake screen, rendering the sump inoperable, following a loss of coolant accident. With the emergency sump inoperable, both independent Emergency Core Cooling Systems (ECCS) and both Containment Spray (CS) systems are inoperable, due to both requiring suction from the emergency sump during the recirculation phase of operation. This could prevent both trains of ECCS from removing residual heat from the reactor and could prevent CS from removing heat and fission product iodine from the containment atmosphere. This condition is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, in accordance with 10 CFR 50.73(a)(2)(v)(B) and (D) as a condition that could have prevented fulfillment of a safety function and in accordance with 10 CFR 50.73(a)(2)(vii) where a single cause or condition caused two independent trains or channels to become inoperable in a single system. Actions to address debris issues are being undertaken and construction of a new strainer system to restore operability and add margin is in progress.
3462002006 | Davis-Besse | 08/11/2002 | 03/26/2004 | ML04090033 | <strong>Emergency Diesel Generator Exhaust Piping Not Adequately Protected From Potential Tornado-Generated Missiles</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2002, with the plant defueled, a deficiency was identified where the last six feet of the Emergency Diesel Generators (EDG) exhaust piping is not protected from tornado-generated missiles. Additionally, an exterior door to a Main Steam Line Room was identified as not adequately protecting the Main Steam Safety Valves (MSSVs) from tornado-generated missiles. While the probability of a missile striking this equipment and damaging it to the point that it can no longer perform its designated safety function is remote, the licensing basis at the time of discovery was that systems vital to safe shutdown in the event of a tornado are enclosed in structures designed to withstand such missiles. The affected equipment was declared inoperable. Since these design deficiencies for the protection of the safety equipment existed since initial plant operation, the operation of the plant in this condition was prohibited by the Technical Specifications, and therefore these events were reported in accordance with 10CFR50.73(a)(2)(i)(B). A probabilistic methodology for tornado missile risk analysis of unprotected plant features was incorporated into the plant's licensing basis; no other facility modifications were determined to be necessary.
3462002007 | Davis-Besse | 04/24/2002 | 11/14/2003 | ML03322032 | <strong>Potential Leakage of Incore Monitoring Instrumentation Nozzles at Bottom of Reactor Vessel</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2002, with the reactor defueled, visual inspections of the underside of the reactor vessel revealed corrosion deposits. The heaviest concentration of corrosion deposits was noted around the center and lowest reactor incore monitoring instrumentation guide tube. Two sets of deposit samples were taken and analyzed in an attempt to determine if the deposits were caused by one or more leaking incore nozzles, or as a result of runoff from cleaning of the reactor vessel closure head. However, no definitive conclusions could be reached with respect to the source of the deposits. An inspection was conducted in September 2003 to confirm that no leakage of the incore nozzles existed by raising the Reactor Coolant System to normal operating pressure, holding these conditions for approximately seven days, and then reducing conditions to perform a bare metal visual inspection for evidence of leakage. Based on the results of the Reactor Coolant System Pressure test, there was no identified leakage of the reactor vessel incore nozzles. Therefore, this issue had no safety significance. Since no incore nozzle leakage was identified, this condition was reported voluntarily.
3462002008 | Davis-Besse | 03/08/2002 | 05/06/2003 | ML03133019 | <strong>Containment Air Coolers Collective Significance of Degraded Conditions</strong><br /><i>Abstract:&nbsp;</i>Following unit shutdown for refueling on February 16, 2002, various degraded conditions were identified associated with the Containment Air Coolers (CACs). A review was performed of the collective significance of these degraded conditions adverse to quality. An engineering evaluation of structural integrity issues has been performed which concluded that corrosion and pitting that resulted from boric acid deposition was not sufficient to render the CACs structurally inoperable during or following a safe shutdown earthquake. An engineering evaluation has been performed of non-conservatisms utilized in piping stress analysis for the Service Water (SW) System that feeds the CACs. This evaluation concluded that the SW piping and CAC cooling coils would remain functional following postulated accidents. Notifications made to the licensee under Part 21 did not render the CACs inoperable. Fouling conditions have been identified for both air and water sides of the cooling coils. An engineering evaluation of thermal performance issues concluded that with the containment emergency sump available, the CACs, in conjunction with Containment Spray (CS), would perform their intended function. Conditions that may render the sump unavailable and consequences on operation of the CS are discussed in LER 2002-005-01. This information is being provided to the NRC on a voluntary basis.
3462002009 | Davis-Besse | 11/29/2002 | 05/17/2006 | ML06142015 | <strong>Degradation of the High Pressure Injection Thermal Sleeves</strong><br /><i>Abstract:&nbsp;</i>On November 29, 2002, with the reactor defueled, during a bore scope examination a crack was discovered on the 2-2 High Pressure Injection (HPI)/Makeup thermal sleeve. Inspection of the 2-1 HP thermal sleeve on December 3, 2002 also revealed a cracked thermal sleeve. After discovery of the two cracks, the degraded thermal sleeves were replaced. The crack in either thermal sleeve did not affect the ability of the HPI system to perform its designed function nor did either crack provide a source of Reactor Coolant System pressure boundary leakage. The cause of the cracks appears to be high cyclic thermal fatigue. This event was determined to not meet the requirements of a reportable condition under 10 CFR 50.73. However, due to the industry interest in HPI thermal sleeve failure, this event is being reported voluntarily as a Licensee Event Report in accordance with the guidance provided in Section 2.7 of NUREG-1022, Revision 2, Event Reporting Guidelines.
3482002001 | Farley 1 | 05/03/2002 | 06/20/2002 | ML02175012 | <strong>Reactor Trip Due to Inadvertent Electrical Contact During Recorder Maintenance</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2002, with the reactor at 100% power, Unit 1 experienced an automatic reactor trip due to an indicated reactor coolant pump bus undervoltage on 2 of 3 busses. Undervoltage relays associated with "A" Reactor Coolant Pump (RCP) bus were in a tripped condition due to surveillance testing in progress. While reconnecting power leads to the neutron flux recorder following recorder repair, the tape on an energized power lead was inadvertently breached and the lead was shorted to ground. The short caused an undervoltage condition on the B vital instrument bus. The B vital instrument bus is the power supply for the recorder as well as the B RCP undervoltage relays. As a result of the "A" RCP bus undervoltage relays tripped for testing and drop out of the "B" RCP bus undervoltage relays due to the shorted power lead, the coincidence necessary to generate a RCP bus undervoltage reactor trip was met. A second trip signal was generated in another 2 milliseconds due to a 1 of 3 RCP breaker position open signal resulting from the "B" vital instrument bus undervoltage condition alone. All safeguards equipment functioned as designed following the trip. All RCPs continued to operate throughout the event. The event was caused by an inadequate work order planning and scheduling process which did not consider potential consequences of energized work. A second cause was inadequate management expectations with respect to taping of electrical leads. Procedural guidance has been developed to require work planning to, specifically identify work activities associated with energized conductors and the affected power source. Procedural guidance has been developed to evaluate work activities involving energized conductors during work scheduling. Procedural guidance has been developed and personnel working on energized conductors have been trained on enhanced taping/insulating techniques for energized leads.
3482002002 | Farley 1 | 10/15/2002 | 12/05/2002 | ML02344000 | <strong>Manual Reactor Trip Due to Partially Dropped Control Rod</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2002 at 2356, with the reactor at 100% power, Unit 1 was manually tripped due to a partially dropped control rod. Rods had been stepped in from 227 to 222 steps over the past three hours for routine xenon oscillation suppression. Upon inserting Bank D rods from 222 to 221 steps, rod F-06 dropped 24 steps to 198. A rod deviation alarm and a single channel high negative neutron flux rate trip alarm annunciated. Operators manually tripped the reactor in accordance with Abnormal Operating Procedures. All safeguards equipment functioned as designed following the trip. The dropped rod was due to an open failure of the movable gripper coil blocking diode. When the diode failed open and rod motion was attempted, the control rod was in an unlatched condition for up to 300 milliseconds while power was removed from the stationary gripper during the normal rod motion cycle. This resulted in a free fall of rod F-06 until the rod control logic re-energized the stationary gripper. A design change was implemented to remove the blocking diodes from all stationary and movable gripper coil circuits. Testing was performed to verify that this change had no significant effect on the gripper unlatch times and therefore no effect on rod drop times. Testing verified that the rod control system continued to operate per design. The reactor was returned to critical at 0542 on October 17, 2002. The corresponding design change was implemented on Unit 2.
3482002003 | Farley 1 | 11/06/2002 | 12/31/2002 | ML03006007 | <strong>Technical Specification Violation Due to Section of Condensate Storage Tank Missile Barrier Not in Place</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2002 at 0950, it was discovered that a section of the required missile bamer was not in place for the Unit 1 Auxiliary Feed Water (AFW) suction piping from the Condensate Storage Tank (CST). It was determined that this event represents a Technical Specification violation since the CST is required to be operable during severe weather events which can generate missiles. The required missile barrier section was replaced within time limits of CST Technical Specification 3.7.6 Action A from the time of discovery. A walkdown of other missile barriers on both units was conducted to identify any other possible missing barriers. None were identified. The CST outlet isolation valves are enclosed in a concrete valve box enclosure for protection from tornado generated missiles, with a 4-section cover plate above the enclosure to protect the valves and piping from dropped objects that may occur during tornado events. Investigation revealed that one section of this plate had been removed on March 19, 2002 for work on the freeze protection system, and not replaced. This event was due to lack of policy and administrative controls for removal of missile barriers when accessing equipment behind the missile barriers. Contributing causes were training and work practices in that plant personnel failed to recognize that all sections of the missile barrier were required to be in place to provide adequate missile protection Permanent labels have been placed on the CST concrete valve box enclosure cover plates to require Shift Supervisor notification prior to removal, and the gratings have been tack welded in place for positive control until corrective actions are complete. Shift crews will be informed of this event prior to taking shift. Appropriate plant personnel will be informed of this event and missile barrier requirements by January 15, 2003, and FNP will establish and communicate policy and administrative controls for missile barriers by January 15, 2003. Appropriate procedures and preventative maintenance tasks will be revised by January 15, 2003 to require shift supervisor notification if missile barriers are to be removed during work activities.
3482002004 | Farley 1 | 12/10/2002 | 02/03/2003 | ML03042057 | <strong>Manual Reactor Trip on Loss of Both Steam Generator Feed Pumps</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2002 at 0824, with the reactor at 100% power, Unit 1 was manually tripped due to loss of both Steam Generator Feed Pumps (SGFP's). Facilities personnel were removing a catch bag near the area of the lA SGFP and the 120/208 Volt Miscellaneous Bus. An individual was applying force to break a tie-wrap which had been used to support the catch bag. When the tie-wrap broke, the individual momentarily lost his balance, reached out to steady himself, and inadvertently depressed a pushbutton on the local control panel for the 120/208 Volt Miscellaneous Bus. This resulted in deenergization of the Miscellaneous Bus and loss of control power to both SGFP's. The SGFP control valves closed resulting in loss of main feedwater to the Steam Generators. Operators manually tripped the reactor in accordance with Abnormal Operating Procedures. All safeguards equipment functioned as designed following the trip. This event was caused by personnel error-a lack of awareness of the sensitivity of surrounding equipment and the consequences of inadvertent contact with such equipment. Contributing causes were failure to consider the consequences of actions prior to the event and failure to use the proper tool to safely remove the tie wrap. A protective barrier has been installed over the Unit 1 Miscellaneous Bus control panel pushbuttons to prevent inadvertent contact. Access to the Unit 2 panel has been barricaded until plant conditions permit barrier installation. The individuals directly and indirectly involved have been coached on specific human performance aspects of this event. A stand down meeting of facilities personnel was held to reinforce station expectations for human performance aspects of this event, including proper tool use, situational awareness of sensitive plant equipment, communications with Operations prior to performing activities near sensitive equipment, and prejob briefings.
3522002001 | Limerick 1, Limerick 2 | 02/28/2002 | 04/01/2002 | ML02156053 | <strong>Unauthorized Access to the Protected Area</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2002 at 18:05 hours, it was discovered that a contractor had been allowed access into the protected area based on inadequate pre-employment screening and inadequate administrative control. On February 25, 2002 a contractor requesting access to the site for refueling outage 1R09 provided a urine sample that gave indication of being adulterated (soap like odor). Per procedure, a second witnessed sample was provided. Both samples were sent to an offsite testing facility. Both sample numbers were entered into the computer tracking system in the "pending" status. When the results of the second (witnessed) sample returned as negative, the Fitness for Duty analyst updated the computer tracking system to indicate an acceptable result. The acceptable test result information was unknowingly carried forward to indicate "acceptable" on the badging screen. A badge was subsequently issued, and on February 28 the contractor entered the protected area for approximately 4 hours along with 4 other contractors who were appropriately badged. There were no adverse consequences. The security access history for the contractor was reviewed. Corporate Security personnel interviewed all the individuals involved. Additional administrative controls were put in place until the computer tracking system logic was corrected.
3522002002 | Limerick 1 | 02/04/2000 | 05/23/2002 | ML02157002 | <strong>Inoperable Core Spray Internal Line Break Alarm Due to Instrument Zero Offset Change</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2000, the "Core Spray Line Internal Break" alarm was determined to be inoperable due to a change in the as-found zero offset value of the monitored parameter. The condition is most likely caused by an accumulation of steam voiding in the vertical leg of the Core Spray header. Technical Specification 3.5.1, ECCS - Operating, requires this alarm to detect differential pressure in excess of 4.4 psid between the "A" and "B" Core Spray headers. The alarm was inoperable since it was not capable of detecting all Core Spray line breaks internal to the reactor pressure vessel. The setpoints have since been modified to account for the expected variations in the zero offset values of the monitored parameter.
3522002003 | Limerick 1 | 05/19/2002 | 07/18/2002 | ML02205004 | <strong>Scram Due to Actuation of Main Thrust Bearing Wear Detector</strong><br /><i>Abstract:&nbsp;</i>An actuation of the Unit 1 main turbine thrust bearing wear detector (TBWD) occurred during scheduled testing of the main turbine combined intermediate valves (CIV). Excessive clearances within the thrust bearing assembly allowed 31 mils of axial displacement on the main turbine shaft during closure of CIV-2. This was detected by the TBWD and caused an actuation. Detailed inspections of the detector and partial disassembly of the housing were performed. The TBWD trip will be bypassed during CIV testing.
3522002004 | Limerick 1 | 08/23/2002 | 10/22/2002 | ML02303028 | <strong>Reactor Enclosure Recirculation System (RERS) Train Potentially Inoperable for a Period Exceeding the TS AOT</strong><br /><i>Abstract:&nbsp;</i>The 1A train of the Reactor Enclosure Recirculation System (RERS) tripped due to a low flow condition during monthly surveillance testing. The investigation identified that three issues when taken in combination, contributed to the train failure. The train flow element output was less than expected due to previous damage. The flow controller time-response was affected by the derivative (rate) setting, and high Ambient temperature effects contributed to lower system flow. This condition existed for a period that potentially exceeded the TS AOT.
3532002001 | Limerick 2 | 07/23/2002 | 09/18/2002 | ML02268002 | <strong>Manual Scram Due to Failure of Main Condenser Air Removal System</strong><br /><i>Abstract:&nbsp;</i>Limerick Unit 2 was manually scrammed due to degraded main condenser vacuum. The condenser air removal system failed due to temperature in the steam jet air ejector (SJAE) condenser exceeding the design limit. The design limitations of the steam jet air ejector system were not properly addressed during the turbine retrofit project resulting in plant operating procedures allowing these limitations to be exceeded. Operating procedures for both units were revised to require a power reduction prior to condensate temperature or condenser backpressure exceeding established limits that maintain sufficient margin to ensure proper operation of the air removal system.
3532002002 | Limerick 2 | 07/24/2002 | 09/23/2002 | ML02275035 | <strong>Manual Scram Due to Failure of Main Condenser Air Removal System</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2002 at 00:26 hours during unit shutdown, all three Unit 2 Main Condenser Offgas Hydrogen Analyzers were placed in purge mode, with the steam jet air ejectors in service, without compensatory sampling in place. This condition represented a violation of Technical Specifications 3.3.7. The cause of this event was that shift management allowed all three H2 analyzers to be purged without compensatory sampling in place, based on incorrect assumptions of future plant conditions. Corrective actions included restoring an analyzer to operable status, making appropriate revisions to the affected procedures, and reviewing the event with Operations and Instrument and Controls (I&C) departments.
3542002001 | Hope Creek | 03/20/2002 | 05/15/2002 | ML02165034 | <strong>"B" Residual Heat Removal Inoperability Due to Mispositioned Minimum Flow Manual Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2002, the "B" Residual Heat Removal (RHR) minimum flow manual maintenance isolation valve was discovered in the closed position. The valve was discovered closed by two non licensed operators who were preparing to close and tag the valve in preparation for a planned system outage. The cause of the inoperability of "B" RHR was a mispositioned valve. The cause of the mispositioning could not be identified. The "B" RHR pump has been evaluated for its response to a large break Loss of Coolant Accident (LOCA) and a small break LOCA, and for its ability to provide long-term post event cooling. An engineering evaluation based on industry operating experience determined that the pump would be available for at least 18 minutes without minimum flow protection. This exceeds the amount of time that the "B" RHR pump is required to respond to a LOCA. Based on the above, there was no impact to the health and safety of the public. Corrective actions included position verification of all accessible manual isolation valves, "lessons learned" discussions, and a review of the use of valve line-ups. There are no commitments associated with this LER.
3542002002 | Hope Creek | 04/05/2002 | 06/27/2002 | ML02190002 | <strong>Secondary Containment Breach Due to Open 1 Inch Vent Line</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2002 Hope Creek operators discovered a Secondary Containment breach of 1 inch piping on a Service Water Emergency Makeup line. The breach was caused by the simultaneous open condition of a tagged open Service Water header vent valve in the Auxiliary Building and the opening of Service Water piping in the Reactor Building for planned repair. This simultaneous open condition provided a pathway for air to travel from the Auxiliary Building (atmospheric pressure) to the Reactor Building. The Reactor Building is maintained at a slight negative pressure. This condition existed from April 5 until discovery on April 30. The apparent cause of this event is the failure to identify the impact of proposed maintenance on the Secondary Containment boundary and failure to identify Technical Specifications associated with planned work. Corrective actions include: a. Restoration of Secondary Containment integrity upon discovery. b. Improvements to guidance on corrective maintenance work order review, tagging, and Technical Specification review for applicability. There is no safety significance to this event. Margins demonstrated during surveillance testing of Reactor Building integrity show Secondary Containment remained capable of performing its safety function.
3542002003 | Hope Creek | 05/13/2002 | 06/12/2002 | ML02172040 | <strong>License Condition Violation — Reactor Power and Minimum Feedwater Temperature Limits</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2002, at 0025 hours the Hope Creek Generating Station experienced a major electrical transient, coincident with a lightning strike on the 5024 New Freedom Line. The apparent cause of the transient as experienced in the plant was the clearing and rapid, automatic re-powering of the 5024 Line, which ties to the Salem switchyard. The electrical transient resulted in a false signal and subsequent auto-isolation of all three (6A/B/C) high-pressure feedwater heaters, as well as other equipment malfunctions. Power peaked at. Abnormal Operating Procedures were entered for 105.23% due to the reduced feedwater temperature Reactor Power, Feedwater Heating, Turbine Hydraulic Pressure and Drywell Pressure. The plant was stabilized at approximately 80% power, and all equipment was returned to normal service. On May 13, 2002, at 1459 hours, a twenty-four hour notification was made to report potential operation outside of License Condition 2.C (1), which authorizes PSEG Nuclear LLC to operate the facility at reactor core power levels not in excess of 3339 megawatts thermal (100 percent rated power) and 2.C (11), which prohibits after the first operating cycle, operation with a feedwater heating capacity that would result in a rated power feedwater temperature less than 400 degrees F unless analyses supporting such operation are submitted by the licensee and approved by the staff. This event is being reported as a Special Report in accordance with the requirements of License Condition 2.F. There was no safety consequences associated with this event since significant margins were available to all power distribution thermal limits.
3542002004 | Hope Creek | 06/22/2002 | 08/19/2002 | ML02240008 | <strong>Engineered Safety Feature Actuation - Reactor Scram Caused by Turbine Trip from Moisture Separator High Level Following Intermediate Runback of Reactor Recirculation Pumps</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2002 at approximately 1417, Hope Creek Generating Station experienced an automatic reactor scram as a result of a turbine trip due to high moisture separator (MS) level. The high MS level resulted from failure of the level controls to adequately respond to the transient, due in part to two phase flow in the drain path. The initiating event that ultimately resulted in the scram was failure of a logic card that caused a secondary condensate pump (SCP) to trip. The automatic reactor scram was successful, but anomalous control rod position indications immediately after the scram prompted operators to initiate alternate rod insertion in accordance with procedures. Condensate flow to feedwater heaters 1 and 2 isolated due to high heater feedwater level; operators manually established bypass flow. Cooldown was in accordance with Technical Specification limits and there were no safety consequences as a result of this event. Corrective actions include replacement of the SCP logic card, corrective maintenance of the normal MS drain control loop and adjustments to the MS dump valve controls to improve response time. This event is reportable under 10 CFR 50.73 (a)(2)(iv)(A) as an actuation of the reactor protection system.
3542002005 | Hope Creek | 06/28/2002 | 07/25/2002 | ML02213042 | <strong>Potential to Exceed Licensed Power Level Due to Malfunction of The Crossflow Correction Factor Instrumenation</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2002, at 1343 hours, a notification was made to the NRC to report a potential operation outside of License Condition 2.C (1), which authorizes PSEG Nuclear LLC to operate the facility at reactor core power levels not in excess of 3339 megawatts thermal (100 percent rated power). On 5/26/02, operators identified that the feedwater cross-flow correction factor was lower after returning to normal operations from a down power evolution. Balance of plant indications led operators to suspect the indicated reactor power with the correction factor applied might be non-conservative. If the plant were operating with a non-conservative correction factor, the calculation of core thermal power was lower than. Detailed actual power and resulted in the plant being operated above the license thermal power limit analyses have confirmed that a malfunction of the crossflow instrumentation correction factor caused the plant to operate by as much as 0.47% overpower. The apparent cause of the event is attributed to a malfunction of the crossflow correction factor instrumentation as a result of cracked insulation be coming lodged between the crossflow meter's clamp and the pipe. Immediate corrective actions included removing crossflow from service and reducing power to the pre 1.4% uprate value. Additional corrective actions included the installation of new crossflow transducers and validation of current crossflow performance. The mounting configuration was changed to prevent similar occurrences. This Special Report is being submitted in accordance with the requirements of License Condition 2.F. There were no safety consequences associated with this event since significant margins were available to all power distribution thermal limits.
3542002006 | Hope Creek | 06/27/2002 | 08/21/2002 | ML02248025 | <strong>Operation with Offgas Rad Monitors Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 1 at approximately 0200 hours, operators declared offgas pretreatment rad-monitors inoperable due to the identification of anomalous readings when compared to the pre-shutdown levels. The plant was starting up and had only recently reached 100%power when the operators noted that the Rad Monitors were reading about one decade lower than immediately prior to the shutdown. Other available plant instrumentation indicated that the system was functioning properly. Further investigation by control room, radiation protection, and chemistry staff revealed that the readings were inconsistent with samples of the process gas stream. Upon further investigation by a chemistry supervisor and technician, it was determined that a 1/8"system purge valve was off of its normal, fully closed position, resulting in a dilution of the sample flow. The cause of the valve being in an off-normal position cannot be determined, however, it is suspected that water may have caused the displacement of the valve. This condition is being reported in accordance with the requirements of 10CFR50.73(a)(2)(i)(B) as "Any operation or condition which was prohibited by the plant's Technical Specifications."
3542002007 | Hope Creek | 09/30/2002 | 11/27/2002 | ML02345009 | <strong>Core Spray Discharge Line Alarms Inoperable</strong><br /><i>Abstract:&nbsp;</i>Hope Creek operated in a condition prohibited by Technical Specifications (TSs) 3.5.1 and 3.4.3.2 due to a closed instrument root valve for the B core spray loop pressure transmitter. Based on a review of plant records, PSEG Nuclear concluded the pressure transmitter was isolated from September 6 through September 30, 2002. The apparent cause for this event was less than adequate instructions for restoration and system lineup verification contained in the procedure for core spray pump inservice testing. There were no safety consequences associated with this event. The isolated transmitter provides an alarm only function, not assumed in any event for dependence on operator action. The closed valve was reopened and the B core spray loop was restored to OPERABLE status. Lessons learned from this event will be communicated to control technicians. The procedure for core spray pump inservice testing will be revised. Similar procedures will be reviewed and revised as necessary.
3612002001 | San Onofre 2, San Onofre 3 | 09/11/2001 | 01/29/2002 | ML02033004 | <strong>Aging Phenomenon Affects Certain Potter and Brumfield Relays</strong><br /><i>Abstract:&nbsp;</i>On 9/11/01, while performing a subgroup relay test on Emergency Feedwater Actuation Signal (EFAS) 1 Train B, Steam Generator (SG) E-089 Auxiliary Feedwater (AFW) Isolation Valve 2HV4715 failed to close. AFW pump 2P140 started and AFW control valve 2HV4706 to SG E-089 closed as expected. 2HV4715 did not close as expected and was verified locally to be open. Plant operators manually closed 2HV4715 from the control room. Upon investigation, SCE discovered that the P&B relay (2L035K402) used for 2HV4715 had failed. SCE determined the return springs of 2L035K402 would not fully rotate the relay shaft to its zero-degrees stop position when de-energized. A self-lubricating nylon hub in deck 1 of the form "Y" contacts (i.e., closest to the relay coils and the heat they generate) had deteriorated such that reinforcing glass fibers in the nylon were creating an abrasive interface. SCE replaced the relay and returned the EFAS train to operable status within the time allowed by the Tech Specs. SCE also determined that there is no need to utilize the form "Y", high current contacts. A proactive approach will be implemented to replace the P&B MDR-7032 relays with P&B MDR-7033 or P&B MDR-7034 relays, which do not contain form "Y" contact blocks. Because the failed relay is not in the EFAS or MSIS actuation logic for 2HV4715, there was no safety significance to this event.
3612002002 | San Onofre 2, San Onofre 3 | 02/08/2002 | 05/09/2002 | ML02134027 | <strong>Boric Acid, AFW Boundary Valve, and CCW Backup Nitrogen Valves Omitted from TS Surveillances</strong><br /><i>Abstract:&nbsp;</i>On 3/1212002, SCE recognized that the Emergency Boric Acid Flow Path surveillance procedure did not include Volume Control Tank (VCT) isolation valves as part of the 31 day surveillance (SR) required by SR 3.1.9.3 and SR 3.1.10.4. Subsequently, SCE recognized that the procedures for performing 31-day flow path surveillances for the CCW and Aux Feedwater Systems (SRS 3.7.7.2 and 3.7.5.1 respectively) also omitted several valves. In each case, the affected valves are located in branch or support system lines and are not in the direct system flow paths. Because the omitted valves should have been included in the SR procedures, SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). Due to the passage of time, SCE did not determine the cause of this occurrence. SCE will revise the appropriate procedures for the Boric Acid, Component Cooling Water and Auxiliary Feedwater systems to include the omitted valves. SCE will review similar surveillance procedures for other systems to ensure the associated surveillance procedures included all TS required components for each flow path. The position of all of the affected valves is controlled by plant procedures. None of the affected valves were mispositioned. There was no safety significance to this event.
3612002003 | San Onofre 2, San Onofre 3 | 06/30/2002 | 08/28/2002 | ML02246035 | <strong>Inadequate Procedure Results in Incorrect Adjustment of the Steam Bypass Control System Causing a Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2002, plant operators were performing startup testing at the end of the Unit 2 Cycle 12 Refueling Outage. At that time, the reactor was at about 18 percent thermal power. In response to a small steam imbalance, the Steam Bypass Control System (SBCS) "quick opened" all four SBCS valves. This caused steam pressure to decrease to the low steam generator pressure trip setpoint, which in turn caused reactor protection system (RPS) and main steam isolation system (MSIS) actuations. The Unit 2 RPS and MSIS actuations occurred because the SBCS Dynamic Response Module (DRM) had been improperly adjusted during the Unit 2 Cycle 12 refueling outage. This adjustment error was caused by an inadequate procedure. On July 5, 2002, the Unit 2 SBCS DRM was adjusted to its correct values; On August 10, 2002, the Unit 3 SBCS DRM was adjusted to its correct values. SCE concludes that this event was of very low to no safety significance. The SBCS is not credited in the accident analysis and safety systems functioned correctly.
3612002004 | San Onofre 2, San Onofre 3 | 07/03/2002 | 08/30/2002 | ML02248001 | <strong>Defective Procedure Results in TS Violation When Reactor Thermal Power Was Increased Above 20 Percent Prior to Completing All Required Surveillance</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) Surveillance Requirement (SR) 3.0.4 prohibits entry into a mode or other specified condition in the Applicability of a Limiting Condition for Operation (LCO) unless the TS LCO's SRs have been met. On July 3, 2002, operators raised reactor power above 20 percent Reactor Thermal Power (RTP) prior to completing some TS SRs for the Core Operating Limits Supervisory System (COLSS) and the COLSS Backup Computer System (CBCS) alarm functions. This operation prohibited by TS SR 3.0.4 is being reported in accordance with 10CFR50.73(a)(2)(i)(B). The cause of this event was a defective procedure. SCE will revise the TS SR procedure to reduce the probability of similar events. Two similar events with the same apparent cause were discovered during the investigation of the July 3 event. SCE concludes there was very little to no safety significance to these events. In each case, the subsequent surveillances provided reasonable assurance that COLSS and CBCS alarms were operable at the time 20 percent RTP was exceeded.
3612002005 | San Onofre 2, San Onofre 3 | 01/15/2002 | 12/02/2002 | ML02339015 | <strong>Missed TS SR for Salt Water Cooling System Check Valves</strong><br /><i>Abstract:&nbsp;</i>On 1/15/2002, Southern California Edison (SCE) failed to properly perform a Technical Specification (TS) Surveillance (SR) for the Salt Water Cooling System check valve that isolates the system from the non-safety related Service Water System. The missed TS SR was not discovered until 10/3/2002. The apparent cause for the delay in resolving this issue was that it was given a relatively low work priority and the issue was not identified as a potentially missed TS SR. TS SR testing completed successfully 10/11/2002 using a temporary procedure, bringing both units into compliance with the TS. The surveillance procedure was revised on 11/15/2002. SCE is evaluating human performance and work processes to determine if additional corrective actions are required to reduce the probability of occurrence of similar events. There was minimal safety significance for this event.
3612002006 | San Onofre 2 | 11/02/2002 | 12/31/2002 | ML03006007 | <strong>Main Feedwater Controller Fault Causes Loss of Main Feedwater and Reactor trip on Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On 11/2/2002 at 0316 PST, with the Unit 2 reactor at 100% power, the Reactor Protection System (RPS) tripped the Unit A main Feedwater (FW) controller failed; the FW regulating valve (2FV1111) began to close; and the water level in steam generator 89 decreased to the low-level trip set point. SCE made a 4 hour telephone notification to the NRC in accordance with 10CFR50.72(b) and is providing this follow-up report in accordance with 10CFR50.73(a)(2)(iv)(A). SCE's cause evaluation is ongoing. However, preliminary investigations Indicate that the 2FC1111 main FW controller card had a shorted low limit operational amplifier (Motorola, MLM301AG, date code 7432). This may be an age-related failure. This LER will be supplemented if this conclusion changes significantly. SCE replaced both Unit 2 main FW controller cards (2FC1111 and 2FC1121) with new cards (even though 2FC1121 tested satisfactorily). As a precautionary measure, the corresponding cards in Unit 3 have been scheduled for replacement. UFSAR Section 15 2.2 5 and 15.10.2 2.5 evaluate the Loss of Normal Feedwater Flow with the plant at full power. The UFSAR analysis shows that all of the event acceptance criteria (DNBR, offsite doses, peak linear heat rate, peak RCS pressure, and peak secondary pressure) are met. Therefore, there was little to no safety significance to this event.
3612002007 | San Onofre 2 | 11/04/2002 | 12/31/2002 | ML03006007 | <strong>Pressurizer Spray Valve Malfunction Results in a Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2002, at about 1625 PST, one of the two-pressurizer spray valves began operating erratically, and ultimately stopped moving at 47 percent open and caused pressurizer pressure to decrease. Attempts to close the spray valve were unsuccessful. At 1638 PST, plant operators manually tripped the reactor. At 2215 PST, SCE made a 4-hour telephone notification to the NRC in accordance with 10 CFR 50 72(b)(2)(iv)(B). SCE is providing this follow-up report in accordance with 10 CFR 50.73(a)(2)(iv)(A). The cause of pressurizer spray valve's behavior has not yet been determined. Testing and observation suggest internal binding. This valve will be disassembled during the next refueling outage. On November 4, 2002, spray valve PV-0100A was isolated when the inlet and outlet manual block valves were closed. The second pressurizer spray valve will be used for the remainder of the operating cycle. A causal evaluation and applicable corrective actions will be performed following the valve disassembly as part of the corrective actions program. The pressurizer spray valves are not safety related, are not included within the Technical Specifications and are not required for accident mitigation purposes. SCE concludes that this event was of low to no safety significance.
3622002001 | San Onofre 3 | 02/27/2002 | 04/24/2002 | ML02120000 | <strong>Loss of Offsite Power With Consequential RPS/ESF Actuations Due to Maintenance Error</strong><br /><i>Abstract:&nbsp;</i>On 2/27/02 at 1043 PST, a technician was performing maintenance and testing in the San Diego Gas & Electric (SDG&E) portion of the San Onofre switchyard. As planned for the work, the South West bus was de-energized. All the transmission lines from SDG&E territory, Unit 3 reserve auxiliary transformer (RAT), and Unit 3 main transformer (main generator) were aligned to "South East" bus. The technician's approved work scope was to test the Breaker Failure Local Backup (BFLBU) scheme on the South West bus breakers. The technician exceeded the authorized work scope and chose also to test the cross bus BFLBU trip from a breaker on the South East bus. While doing so, the technician also failed to isolate a trip signal between the South West bus and the South East bus and the resulting signal tripped all the breakers connected to the South East bus, including the Unit 3 main transformer breaker and Unit 3 RAT breakers. Consequently, the Unit 3 main turbine/generator tripped, the reactor tripped, both emergency diesel generators started and Auxiliary Feedwater started. Operators manually started the Emergency Containment Coolers. The loss of offsite power and associated Reactor Protection System and Engineered Safety Features actuations were reported to the NRC in accordance with 10CFR50.72(b)(2)(iv)(B) and 10CFR50.72(b)(3)(iv)(A). This written report is provided in accordance with 10CFR50.73(a)(2)(iv)(A). Offsite power was restored in about 32 minutes. Future switchyard detailed work plans will be reviewed and approved by SONGS Operations prior to the commencement of work. The event had minimal safety significance.
3622002002 | San Onofre 3, San Onofre 2 | 09/09/2002 | 11/19/2002 | ML02325021 | <strong>Breaker Failure to Close Renders Containment Emergency Fan Inoperable for Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2002, the Unit 3 Containment Emergency Fan Unit 3ME402 failed to start. This failure was traced to the breaker installed in position 3B0611 (that powers 3ME402) and testing verified that the breaker would not close when given a close signal On September 24, 2002 (discovery date), SCE concluded that the breaker had failed immediately after its last close operation on August 24, 2002. A similar period of inoperability of this breaker may have existed from June 1, 2002 to June 29, 2002. This event was caused by an inability of the closing springs for this breaker to fully charge through the end of the charge cycle. Asea Brown Boveri (ABB) addressed this failure mode in a 10CFR21 report sent to the Nuclear Regulatory Commission (NRC) on May 6, 2002. SCE replaced the operating mechanism for the failed breaker with a mechanism that is not susceptible to the failure mode discussed in the Part 21 notification. There are 23 breakers of this type installed in safety-related applications in Units 2 and 3 SCE has replaced 5 of these breakers and the remaining breakers are planned for either replacement of the operating mechanism or change out with a breaker not susceptible to this failure mode. This event was of low safety significance.
3622002003 | San Onofre 3 | 10/16/2002 | 12/11/2002 | ML02350003 | <strong>Main Feedwater Pump Turbine Trip Results in Manual Actuation of Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2002, Unit 3 plant operators were conducting Main Feedwater Pump Turbine (MFWPT) lube oil supply auto-start testing. Immediately after restoring the MFWPT lube oil supply to normal operation, MFWPT 3K006 tripped. Plant operators manually started the Auxiliary Feedwater (AFW) system and initiated a power reduction to approximately 75% power. The AFW system functioned correctly. This manual actuation of AFW is being reported in accordance with 10CFR50.73(a)(2)(iv)(A). SCE's investigation is ongoing. To complete the cause evaluation, the MFWPT lube oil system and associated control systems will require disassembly. SCE will complete the cause evaluation following the next scheduled refueling outage and implement appropriate corrective actions at that time. SCE concludes that this event was of very low to no safety significance; all safety systems functioned correctly.
3622002004 | San Onofre 3 | 05/07/2002 | 12/17/2002 | ML02354035 | <strong>Emergency Room Cooler for Component Cooling Water Pump Conservatively Considered Inoperable for Longer Than Allowed by TS</strong><br /><i>Abstract:&nbsp;</i>On 5/7/02, during a surveillance run of an ECWS train, plant personnel noticed that emergency room cooler 3ME455 sounded noisy and conservatively declared it inoperable. After collecting bearing vibration data, the bearings were replaced and on 5/20/02, 3ME455 was returned to service, within the 14 days allowed by TS 3.7.10. At that time, it was SCE's engineering judgment that ME455 was capable of performing its safety function at the time it was removed from service. The noise from 3ME455 is attributed to normal bearing wear. The bearings for 3ME455 were replaced and the unit declared operable on May 20, 2002. Later, SCE re-evaluated this occurrence and on 1023102, concluded that it could not be determined with certainty (1) how long 3ME455 would have operated in its as-found condition and (2) when 3ME455 bearing degradation began. Because the bearing degradation may have existed for more than 14 days prior to discovery, SCE conservatively considers that 3ME455 may have been inoperable for longer than allowed by TS 3.7.10 without implementing the actions required by TS 3.7.7. SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). There is little or no safety significance to this event because the normal and emergency room coolers are not essential for CCW pump operability.
3662002001 | Hatch 2 | 03/28/2002 | 05/07/2002 | ML02133029 | <strong>Component Failure in a Limit Switch Leads to Inoperability of HPCI System</strong><br /><i>Abstract:&nbsp;</i>On 03/28/2002 at 0300 EST, Unit 2 was in the Run mode at a power level of 2763 CMWT (100 percent rated thermal power). At that time, the High Pressure Coolant Injection (HPCI) system was rendered inoperable when personnel closed turbine exhaust line vacuum breaker isolation valve 2E41-F111. Personnel closed valve 2E41-F111, a primary containment isolation valve, per the requirements of Unit 2 Technical Specifications Condition 3.6.1.3.A following unsatisfactory operation of turbine exhaust line vacuum breaker isolation valve 2E41-F 104 during a routine surveillance. Because valve 2E41-F104 is a primary containment isolation valve, its unsatisfactory operation required that Unit 2 Technical Specifications Condition 3.6.1.3.A be entered. Entry into Condition 3.6.1.3.A required that valve 2E41-F111 be closed to isolate the affected penetration, effectively isolating the turbine exhaust line vacuum breakers and preventing them from performing their intended function. As a result, the HPCI system was rendered inoperable. This event was caused by component failure. The spring tension in the forger base sub-assembly of a limit switch had weakened, preventing proper electrical contact and causing the open position indication to malfunction. Because the valve's actual position was uncertain, it was declared inoperable. This required valve 2E41-Fill to be closed and the HPCI system to be rendered inoperable. Personnel adjusted the spring tension, completed successfully the valve test, and declared valve 2EI I-F104 operable. After re-opening valve 2E41-Fl 11 and completing scheduled maintenance work and the proper functional tests, the HPCI system was declared operable at 1322 EST on 03/28/2002.
3682002001 | Arkansas 2 | 04/15/2002 | 06/12/2002 | ML02168004 | <strong>Reactor Coolant System Pressure Boundary Leakage Due to Primary Water Stress Corrosion Cracking of Pressurizer Heater Sleeves</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2002, with the plant in cold shutdown for refueling, five Pressurizer heater sleeves were found to be leaking. Leakage was identified by small amounts of boron discovered at the sleeve penetration interfaces. A sixth leaking heater sleeve was identified on April 30, 2002, during heatup from the outage. The root cause evaluation concluded that the failure mechanism for all six leaking heater sleeves was Primary Water Stress Corrosion Cracking (PWSCC) of Alloy 600 material. Inspection of the Pressurizer base metal area surrounding each sleeve indicated that no boric acid wastage had occurred. The leaks were repaired using ASME Code-qualified Mechanical Nozzle Seal Assemblies. All Pressurizer and hot leg nozzles were re-inspected following repair and heatup. No additional leakage was identified. Routine visual inspections were determined to be adequate to detect future similar leakage.
3682002002 | Arkansas 2 | 12/19/2002 | 02/10/2003 | ML03043026 | <strong>Automatic Actuation of the Reactor Protection System Caused by a Main Turbine Trip Due to Failure of the Main Generator Reverse Power Relay Resulted in a Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>A trip of the Main Turbine while operating at 100 percent power resulted in automatic actuation of the Reactor Protection System and a reactor trip. Plant response was uncomplicated and the plant was promptly stabilized in hot standby conditions. The trip resulted from a failure of the Main Generator reverse power relay. The relay had been in service since initial plant construction in the late 1970s. Periodic testing and calibration of the relay had last been performed in 2000. Inspections and testing verified that the relay failure did not result from external conditions. Evidence obtained following the failure did not allow conclusive determination of the root cause, and the relay was sent to the manufacturer for further evaluation. The relay was replaced and the replacement was monitored during the plant startup. There have been no previous similar events at Arkansas Nuclear One.
3692002001 | McGuire 1 | 03/04/2002 | 04/29/2002 | ML02135024 | <strong>Manual Reactor Trip in Response to Loss of Feedwater Valve Control Power</strong><br /><i>Abstract:&nbsp;</i>Event Description: On March 4, 2002, the 1A Steam Generator experienced decreasing level when its main feedwater supply valves failed closed. In response to the decreasing lA Steam Generator level, the Unit 1 reactor was manually tripped. After the trip, the 1A Steam Generator experienced a Lo-Lo level condition which automatically started the 1A and 1B Auxiliary Feedwater Pumps. There were no malfunctions of equipment needed to respond to the event. Event Cause: An electrical short in a capacitor located within the cabinet containing the lA Steam Generator main feedwater supply valves control circuitry caused a loss of electrical power to the control circuitry for these valves. Corrective Action: Failed components were replaced. McGuire will evaluate possible design changes to prevent a capacitor failure from causing a reactor trip due to a loss of electrical power to process control cabinet circuitry.
3692002002 | McGuire 1 | 10/01/2002 | 11/25/2002 | ML02338012 | <strong>Automatic Actuation of Diesel Generator 1B Due to Cutler-Hammer Model E30 Control Switch Failure</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in Mode 6 (Refueling) and Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: On October 1, 2002, while conducting Engineered Safety Features (ESF) testing on DG 1B, the DG output breaker unexpectedly tripped open, causing a blackout on the 4kV Essential 1ETB bus. The load sequencer and DG 1B responded accordingly to re-energize the bus and connect the blackout loads to the bus. The redundant 4kV Essential 1ETA bus remained operable during the event. Event Cause: The root cause of the blackout event was failure of the Cutler-Hammer (C-H) pushbutton control switch for the DG output breaker due to its contact block plunger stuck in the depressed position. Corrective Action: The failed switch was replaced. Other Category "A" (high safety significant and/or critical to production) C-H Model E30 control switches that are constructed with dual-circuit contact blocks with at least one normally-closed contact will be replaced with contact blocks manufactured after 1979.
3702002001 | McGuire 2 | 04/05/2002 | 05/31/2002 | ML02164032 | <strong>Residual Heat Removal System Inoperable Due to Stuck Open Check Valve</strong><br /><i>Abstract:&nbsp;</i>During a Residual Heat Removal (ND) system flushing evolution, the 2A ND Pump discharge check valve (2ND-23) became stuck open. During an event requiring residual heat removal, this condition could have diverted sufficient 2B ND Pump flow from the reactor core to prevent the 2B ND train from performing its safety function. There were no immediate indications to plant operators that 2ND-23 was stuck open. Procedurally directed actions to render the 2A ND train inoperable were implemented later during the ND system flushing evolution. The combination of these conditions resulted in both trains of the Unit 2 ND System being inoperable. Upon identifying this condition, plant operators responded quickly to restore operability of the 2B ND train. The total time that both ND trains were simultaneously inoperable was approximately 1 hour and 54 minutes. A probabilistic risk assessment determined this event to be of no significance to the health and safety of the public. Event Cause: Design deficiency-previous redesign of 2ND-23 in 1999, to preclude the valve from sticking open, was inadequate. Corrective Action: 2ND-23 was modified to preclude sticking open. A review determined that other applications of this valve model at McGuire are not susceptible to sticking open.
3702002002 | McGuire 2 | 08/22/2002 | 10/14/2002 | ML02296033 | <strong>McGuire Unit 2 Manual Reactor Trip Due to Rapid Loss of Generator Hydrogen and Subsequent Fire</strong><br /><i>Abstract:&nbsp;</i>Event Description: On August 22, 2002, a pipe plug located on the bottom side of an oil vapor extractor canister housing on the generator hydrogen system dual tower gas dryer skid failed, resulting in a rapid loss of hydrogen and a fire. In response, operators manually tripped the Unit 2 reactor and dispatched the fire brigade. The fire brigade isolated the hydrogen source and extinguished the fire. Following the reactor and turbine trip, steam generator water levels continued to increase as a result of the 2B main feedwater pump turbine not going to the rollback hold position. Once the steam generator water levels reached their high-high setpoint, the main feedwater pumps automatically tripped due to a feedwater isolation signal. The loss of the main feedwater pumps resulted in an automatic start of the 2A and 2B motor driven auxiliary feedwater pumps. Event Cause: Inadequate maintenance work practices and a lack of proper coordination of a functional verification were the causes for this event. Corrective Action: Inspected the fire affected area and performed appropriate repairs. Removed the Unit 2 dryer from service. Revised the dryer operating procedures to ensure proper functional verifications following maintenance. Other similar procedures and maintenance work practices will be reviewed and revised as appropriate.
3742002001 | LaSalle 2, LaSalle 1 | 03/16/2002 | 05/13/2002 | ML02148049 | <strong>Transient Increases in Unit 2 Unidentified Leakage Due to Clogged Drywell Floor Drain Sump Cover</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2002, the calculated unidentified leakage on Unit 2 reached 3.0 gpm, which exceeded the value calculated the previous day by more than 2.0 gpm. Technical Specification (TS) 3.4.5.d limits the increase in unidentified leakage within the previous 24 hour period to less than or equal to 2.0 gpm. The increase in unidentified leakage was transient, and returned to normal values. Troubleshooting indicated that debris collected on the drywell floor from previous maintenance activities had clogged the drywell floor drain. This debris restricted flow through the floor drain, which created a hold up of water on the drywell floor. This rendered the leakage detection system incapable of identifying increases in unidentified leakage of 2.0 gpm within 24 hours. Agitation of the debris from normal equipment shifts allowed the water to drain into the sump at an increased rate. The cause was determined to be inadequate post-outage cleaning of the drywell floor. The drain covers and the drywell floor were cleaned. Periodic maintenance activities will be created to clean and inspect the drywell floor following refueling outages. The safety significance of the event was minor, since the unidentified leakage was less than TS limits, and redundant means to detect reactor coolant leakage were available.
3742002002 | LaSalle 2, LaSalle 1 | 05/30/2002 | 07/19/2002 | ML02207048 | <strong>Loss of voltage control on the 2B emergency diesel generator due to failure of the voltage regulator range potentiometer R3</strong><br /><i>Abstract:&nbsp;</i>On 05/30/02, at 1551, the 2B Diesel Generator (DG) was started and brought to full load for post-maintenance testing. The DG operated normally for approximately 15-20 minutes, then reactive load (VAR) began to vary erratically. The operator attempted to control VAR manually using the voltage regulator motor-operated potentiometer without success, and the 2B DG was unloaded and shutdown. The cause was a failure of the voltage regulator range potentiometer R3. The root cause was determined to be inadequate design, since the potentiometer used is inherently noisy. Corrective actions were to replace the R3 potentiometer, and to establish a periodic testing program to ensure that R3 performance does not degrade. The Station is pursuing an alternative potentiometer for this application. The safety significance of the event was minimal. The 2B DG was out-of-service for maintenance when the failure occurred, and was restored to operable status within the Technical Specification allowed outage time. The 2B DG provides emergency power to High Pressure Core Spray (HP). Normal AC power was available to HP at all times, and all other ECCS systems and Reactor Core Isolation Cooling were operable during the event.
3822002001 | Waterford 3 | 01/30/2002 | 03/29/2002 | ML02092011 | <strong>Shield Building and Controlled Ventilation Area Systems Inoperable Due to Maintenance Activities</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2002, with the plant operating in Mode 1 at 100% reactor power, it was discovered that the methods for testing and performing maintenance for both the Shield Building Ventilation System and the Controlled Ventilation Area System resulted in both trains of each system becoming inoperable. The testing and maintenance methods required opening the train doors of each unit, such that they would be opened to atmosphere. The door opening creates a path to the operable train suction during accident conditions when both train inlet valves open upon a Safety Injection Actuation Signal. Because of this path, neither system would have been able to achieve required vacuum conditions during accident conditions. To preclude the effect of the door opening in the future, the inlet valves for the trains being tested or maintained will be tagged closed allowing the opposite train to achieve required vacuum conditions. This condition is being reported pursuant to 10CFR 50.73(a)(2)(i)(B), 10CFR 50.73(a)(2)(v) and 10CFR 50.73(a)(2)(vii). There was no actual event that required the operation of these systems to preclude the release of radioactive material. Therefore, the condition did not compromise the health and safety of the general public. This event is considered a Safety System Functional Failure.
3822002002 | Waterford 3 | 02/04/2002 | 03/29/2002 | ML02092011 | <strong>Reactor Trip Circuit Breakers Rendered Inoperable During Response Time Testing</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2002, with the plant operating in Mode 1 at 100% reactor power, four channels of reactor trip circuit breakers were rendered technically inoperable without a corresponding entry into Technical Specifications (TS). Reactor trip circuit breaker response time testing was being performed in accordance with an approved maintenance procedure. The procedure required the installation of jumpers that bypass the actuation signals for the undervoltage trip function for the eight breakers simultaneously. A reactor trip circuit breaker is considered inoperable when either the undervoltage or shunt trip devices are not functional. The Control Room Supervisor discovered the condition. The Control Room staff stopped the testing and restored the plant to a normal configuration. The root cause was identified as a latent organizational weakness in the initial procedure development, review and approval process in 1982. This procedure weakness was not recognized during subsequent procedure revisions. This condition is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, since the channels were inoperable beyond the allowed outage time of one hour (TS 3.0.3). The procedure has been revised to require bypassing trip devices on only one channel at a time. The reactor trip circuit breakers would have still performed their function via the shunt trip device if called upon by a valid signal.
3822002003 | Waterford 3 | 02/15/2002 | 04/01/2002 | ML02105022 | <strong>Inoperable Auxiliary Component Cooling Water Pump Due to Lack of Lubrication</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2002, with the plant operating in Mode 1 at 100% reactor power, it was determined that the Auxiliary Component Cooling Water Pump B had been inoperable for a period exceeding the 72 hour allowed outage time of Technical Specification 3.7.3. The inoperability of the pump was caused by the failure of the pump's outboard bearing, which resulted from the failure to exclude foreign material from the lubricant during maintenance or oil addition. This resulted in a lack of lubrication to the bearing. The bearing failure was identified on December 30, 2001. The bearing oil was drained from the ACCW Pump B, all pump accessible areas were cleaned and the outboard was replaced. A failure analysis was performed on the bearing. This analysis determined that the initial failure had likely occurred on December 23, 2002. This condition is being reported pursuant to 10CFR 50.73(a)(2)(i)(B), as operation or condition prohibited by Technical Specifications. Although Auxiliary Component Cooling Water Pump B was inoperable, the opposite train pump was available to perform all necessary safety functions. Therefore, this condition did not compromise the health and safety of the general public.
3822002005 | Waterford 3 | 03/23/2002 | 05/22/2002 | ML02144012 | <strong>Temporary Inability to Achieve Cold Shutdown With Both Trains of Shutdown Cooling Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2002, at approximately 1005, the plant was in Mode 4 and Operations was attempting to lineup shutdown cooling for the Refuel 11 outage, when the emergency plan was entered (Alert declared), due to the inability to achieve cold shutdown. The condition occurred when two Shutdown Cooling System suction isolation valves (SI-405A(B)) failed to open when attempted from the Control Room. This rendered both trains of shutdown cooling inoperable. Following several attempts, valve SI 405A opened at 1137 and the other valve, SI-405B, opened at 1143 when the temperature differential across the valves decreased. Therefore, the valves failed to open over a period of approximately one and a half hours. It was later determined that the root cause of the event was thermal binding. Modifications have been made to increase the open stroke thrust for the subject valves. The safety significance of this event was negligible. This event did not compromise the health and safety of the general public. This event is considered a Safety System Functional Failure.
3822002006 | Waterford 3 | 05/09/2002 | 06/10/2002 | ML02172050 | <strong>Possible Operation in Excess of 100% Licensed Power Limit Due to Instrumentation Biases</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2002 the plant was in mode 1 at approximately 99.9% power. A preliminary investigation to evaluate an identified discrepancy between three available reactor core calorimetric thermal power indications was completed. The preliminary investigation concluded that an approximate 1.9% non-conservative deviation existed between the Main Steam venturi flow meter power indication (MSBSCAL) and the more accurate power measurement from the newly installed Leading Edge Flow meter (LEFM) CheckPlus ultrasonic flow meter (USBSCAL). The deviation is likely the aggregate of several biases factored into the MSBSCAL indication and secondary side component degradation during the period from February 1995 through 1998. Thus, Waterford 3 may have operated at steady state power levels in excess of the 100% licensed power limit from approximately February 1995 to plant shutdown for Refueling Outage 11 on March 22, 2002. The investigation to determine the actual root cause of this condition is ongoing. Actions have been taken to assure current plant operations do not exceed the licensed power limit. This report is being made pursuant to Waterford 3 License Condition 2.F for potential violation of License Condition 2.C.1, "Maximum Power Level." Since the analyzed power of 102% was not exceeded on a steady state basis and transients were bounded by the existing Chapter 15 safety analyses, this condition was of minimal safety consequences and the health and safety of the general public was not compromised.
3872002001 | Susquehanna 1, Susquehanna 2 | 02/22/2002 | 04/23/2002 | ML02123033 | <strong>Temporary Loss of Control Structure Chillers</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2002 with Unit 1 at 81 % power and Unit 2 at 100% power, the 'B' Control Structure (CS) Chiller (EIIS: KM) tripped when an operator placed the chiller's handswitch from 'Auto' to 'Start' following an automatic start of the equipment. The 'B' chiller automatically started when the 'A' chiller tripped during post-maintenance testing. The cause of the 'B' CS Chiller trip was lack of specific procedural guidance for the operating condition. In the absence of procedural guidance for a chiller after automatically starting, operators typically place the handswitch from 'Auto' to 'Start' to bring the equipment alignment within generic operating guidance. The handswitch "break-before-make" design imposes an additional start event on the equipment for this action, and the resulting electrical transient tripped the electrical supply breaker for the associated equipment fan. The appropriate operating procedure for the CS Chillers will be revised to provide guidance following an automatic start of the equipment to avoid similar operator-induced trips. This event is reportable as an event or condition that could have prevented fulfillment of a safety function per 10CFR50.73(a)(2)(v). Based upon the simplicity of resetting the electrical supply breaker and the short amount of time that no chillers were available, this event resulted in very low safety significance.
3872002002 | Susquehanna 1, Susquehanna 2 | 03/03/2002 | 05/01/2002 | ML02133001 | <strong>Main Steam Isolation Valve Total Leakage Exceeded Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2002 with Unit 1 in its twelfth refueling and inspection outage (Mode 4, Cold Shutdown; 0% Power), an evaluation of the data from the scheduled Main Steam Line (MSL) Local Leak Rate Testing determined that the as-found minimum pathway leakage for the Main Steam Isolation Valves (MSIV) exceeded the Technical Specification limit of 300 Standard Cubic Feet per Hour (SCFH). The total as found MSL minimum pathway leakage, including subsequent test results from other valves in the MSL minimum pathway category, was 1065 SCFH. The cause of the MSIV leak rate test failures was a valve design that did not properly align seating surfaces during valve closure. Misalignment of the poppet to valve body seating surfaces allowed unacceptable leakage. Each MSIV has been modified with improved design features that will improve the MSIV alignment and sealing performance. This event is reportable as a degraded principal safety barrier per 10CFR50.73(a)(2)(ii)(A). Considering the results of extrapolation of design basis accident analysis, the projected dose results using realistic dose analysis, and the conservative nature of the test results, this event had very low safety significance. There were no actual consequences to the health and safety of the public as a result of this event.
3872002003 | Susquehanna 1 | 03/04/2002 | 05/03/2002 | ML02134047 | <strong>Operations Prohibited by Technical Specifications Due to Inoperable ATWS Recirc Pump Trip Breaker</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2002 at 01:20 with Unit 1 in Mode 4 at 0% power, an Instrumentation and Control Technician performing a 24 month logic system functional test observed that an Anticipated Transient Without Scram (ATWS) Recirculation Pump Trip (RPT) 4.16 kV breaker did not trip as required. The Truck Operated Cell (TOC) switch contact in the rear of the associated 4.16 kV switchgear cubicle had failed to make-up properly. The TOC had excessive drive shaft and gear rotary motion, which allowed the TOC to over-travel when the breaker was "racked-in". The breaker was "racked-out" and returned to the "racked-in" position. The contact was checked for proper continuity and the logic system functional test was then completed successfully. The TOC was subsequently replaced with a design that is less susceptible to over-travel. An investigation showed that the contacts are not visible (i.e. "blind') when the breaker is in the "racked-in" position and there is no specific written guidance on how to verify that the contact is properly made-up. All other ATWS-RPT breakers were checked for proper contact make-up and found satisfactory. All other 4.16 kV breaker cubicles that have "blind" TOC contacts will be identified and it will be determined where verification of contact alignment is necessary. Written guidance and training for monitoring the necessary "blind" TOC contact make-up after a breaker is "racked-in" will be established. The condition may have existed since the last time the breaker had been racked-in during the previous Unit 1 refueling and inspection outage in the Spring of 2000. This event is reportable as a condition prohibited by Technical Specification 3.3.4.2 per 10CFR50.73(a)(2)(i)(B). There was not a loss of safety function associated with the event. There were no actual adverse consequences to the health and safety of the public as a result of this event.
3872002004 | Susquehanna 1 | 04/22/2002 | 06/21/2002 | ML02184053 | <strong>Manual Scram After 'B' Recirculation Pump Tripped</strong><br /><i>Abstract:&nbsp;</i>At 01:15 on April 22, 2002 with Unit 1 in Mode 1 (Power Operation) at 17% power, plant operators initiated a manual reactor scram in response to anomalous core flow indications observed following a recirculation pump trip that had occurred at 00:16. Following the pump trip, power and flow values plotted on the Unit's power to flow map were found to be in a position left of the natural circulation line. This was unexpected because a second recirculation pump continued to provide forced circulation. While no power flux oscillations were observed, Operations Management elected to scram the reactor because operators were uncertain about core flow indications and plant procedures did not provide a clear response to the observed conditions. Investigation revealed that past industry and internal experience provided insight into the flow instrumentation logic that resulted in a plotted position left of the natural circulation line. Susquehanna's previous response to this information did not adequately educate operators on, or initiate procedural changes to address, this anticipated instrument behavior. To preclude recurrence of this event, procedures now direct operators to utilize a core plate differential pressure correlation in lieu of core flow instrumentation during low flow, single-loop operation. Should an operator plot a point to the left of the natural circulation line despite this tool, procedures have been modified to provide clear direction for reactor scram. Operators have been trained on these changes. This event is reportable for Unit 1 as an unplanned actuation of systems that mitigate the consequences of significant events per 10CFR50.73(a)(2)(iv)(A). There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
3872002005 | Susquehanna 1, Susquehanna 2 | 07/26/2002 | 08/26/2002 | ML02255046 | <strong>Dry Fuel Storage Canister Filled With Incorrect Gas Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2002 at 19:30 with both Unit 1 and Unit 2 in Mode 1 at 100% power, a Maintenance Mechanic observed that argon gas had been used to backfill a NUHOMS® 52-B Dry Shielded Canister (DSC) instead of helium gas. The condition was discovered after the DSC vent and siphon port covers and the outer top cover were installed and welded into place, but prior to transporting the DSC from the reactor building to the Independent Spent Fuel Storage Installation. All dry fuel storage activities on the refueling floor were suspended. A procedure was developed to breach the outer top cover, remove the argon gas from the DSC, confirm and verify it was backfilled with helium gas and weld repair the outer top cover. Repair of the DSC was completed on August 11, 2002. The event occurred when maintenance mechanics erroneously connected the DSC backfill skid to argon compressed gas cylinders, rather than helium compressed gas cylinders. Management review identified that latent organizational weaknesses contributed to this human error event. In response to this event, dry fuel storage work crews received non-routine training to emphasize the need to read labeling when selecting gas cylinders. Routine procedures will be revised to require verification of the correct backfill gas prior to loading other DSCs. Maintenance shift turnover practices will be improved and pre job checklists will emphasize important tasks. The identified latent organizational weaknesses have been entered into the corrective action process and will be further evaluated. This event is reportable under 10CFR72.75(d)(2), as a significant reduction in the effectiveness of the storage confinement system. However, since there was margin available in the other design parameters, there were no nuclear safety consequences as a result of the event. An analysis of the condition determined that the cladding temperature of the fuel stored in the DSC would not exceed the design basis fuel cladding temperature for the NUHOMS® design. It was also determined with a high degree of confidence that the DSCs already stored in the horizontal storage modules were backfilled with the correct helium gas. Therefore, there were no actual adverse consequences to the health and safety of the public as a result of this event.
3872002006 | Susquehanna 1, Susquehanna 2 | 10/03/2002 | 02/20/2004 | ML04062045 | <strong>Supplemental LER on Failure of Startup Transformer ST-20</strong><br /><i>Abstract:&nbsp;</i>At approximately 0230 hours on October 3, 2002, a fire occurred on Startup Transformer (ST) No. 20.The transformer fire was extinguished by the transformer's automatic deluge system. Unit 1 was in MODE 1 - Power Operation operating at 100% power and Unit 2 was in MODE 2 -Startup. Unit 2 was manually scrammed due to a loss of both Reactor Recirculation pumps. Unit I continued operation at 100% power. The fire was extinguished quickly and caused no significant impact to adjacent systems or structures. An Emergency Plan Unusual Event was declared at 0315 when it was determined that two explosions also occurred. The Unusual Event was terminated at 0552 on October 3, 2002.ST No. 20 was replaced and declared operable on October 10, 2002. This event was reported in LER 50-387/2002-006-00, PLA-5534 dated October 15, 2002. This supplement to that LER provides the final conclusions of PPL's investigation of the transformer failure. The conclusion of this investigation was that the root cause was an undetectable internal fault. This internal fault could have originated from several possible sources. It was also determined that the primary and backup lockout relays did not actuate as expected during the event. The lockout relays provide electrical protection for the ST-20 Startup Transformer and function automatically to protect the transformer. The failure of the primary and backup lockout relays to actuate did not cause the event. Corrective actions have been developed and implemented with sufficient breadth to address the possible causes of both the transformer and the protective relay failures. No safety barriers were affected by this event. There were no consequences to the health and safety of the public as a result of this event.
3872002007 | Susquehanna 1 | 09/03/2002 | 11/04/2002 | ML02318004 | <strong>Operations Prohibited by Technical Specifications Due to Inoperable High Pressure Coolant Injection Check Valve</strong><br /><i>Abstract:&nbsp;</i>On September 3, 2002 with Unit 1 in Mode 1 (Power Operation) at 100% power, the Unit 1 High Pressure Coolant Injection (HPCI) exhaust check valve (155F049) was declared inoperable following Local Leak Rate Testing (LLRT). A review of the system operating history concluded that the valve had likely been inoperable for 135 days prior to the time of discovery. This period exceeds Technical Specification required action completion times developed for Primary Containment Isolation Valves (PCIV). Disassembly revealed that vibration induced degradation of the valve's internal components compromised the valve's ability to check flow. The HPCI system's ability to inject flow to the reactor vessel, however, had not been affected. Additionally, inboard isolation gate valve (HV155F066 ) remained operable and capable of performing the penetration isolation function. The exhaust check valve has been reworked and satisfactorily tested. The corresponding Unit 2 HPCI exhaust check valve has also been tested and inspected. While the Unit 2 components were found to be in good condition , the valve's resilient seal was replaced as a preventative measure. Exhaust check valves in each Unit' s Reactor Core Isolation Cooling system, which comprise all additional valves at the station of similar design and function, were inspected. These inspections did not reveal similar problems. Routine inspection tasks have been developed for all the aforementioned check valves to preclude recurrence of this situation. This event is reportable for Unit 1 as a condition prohibited by Technical Specification 3.6.1.3 per 10CFR50.73(a)(2)(i)(B). There were no actual adverse consequences to other plant equipment or to the health and safety of the public as a result of this event.
3882002001 | Susquehanna 2 | 03/11/2002 | 05/10/2002 | ML02155045 | <strong>Operation Prohibited by Technical Specifications Due to Mispositioned 125 VDC Transfer Switches</strong><br /><i>Abstract:&nbsp;</i>At 01:15 on March 12, 2002, with Unit 2 in Mode 1 (Power Operation) at 100% power, an operator performing rounds discovered that some transfer switches for 125 VDC power sources supplying common loads (i.e., loads that support operation of both units) were in the incorrect position. The Unit 1 Division 2 125 VDC power sources had been declared inoperable on March 11 for refueling outage work on Unit 1. in this condition, the Unit 2 Technical Specifications require transfer of associated Unit 1 and common loads to the corresponding Unit 2 125 VDC power source within 2 hours. Upon discovery that the switches were mispositioned, Operations personnel declared the applicable common loads inoperable at 02:00. At 03:00 all the transfer switches for associated common loads were properly aligned and the common loads were restored to operable status. The mispositioned transfer switches were due to inadequate control of an attachment in the transfer switch alignment procedure OP-102-002. Page 1 of 2 for Attachment J had been inadvertently omitted while copying the procedure for implementation. The causes of the event were 1) Operations personnel had less than adequate knowledge of procedure attachment page control and 2) self-checking and peer checking techniques are not normally used for performance of administrative tasks such as copying procedures. A bulletin was issued to Operations personnel to describe attachment page control, and those requirements will be included in routine training. An Operations stand-down was conducted for standards of error and event prevention to include the use of self-checking and peer checking for administrative tasks, and those standards will be included in a procedure. A method to more clearly delineate the beginning and end of Operations procedure attachments will be established. This event is reportable as a condition prohibited by the Technical Specifications per 10CFR50.73(a)(2)(i)(B). There was not a loss of safety function associated with the event. There was no unmet demand for 125 VDC loads while the transfer switches were mispositioned, and therefore, there were no actual adverse consequences to the health and safety of the public as a result of this event.
3882002002 | Susquehanna 2 | 03/16/2002 | 05/15/2002 | ML02157013 | <strong>Loss of Control Structure Chiller Safety Function When 4.16 kV Breakers Found "Racked-Out"</strong><br /><i>Abstract:&nbsp;</i>At 02:40 on March 16, 2002 with Unit 2 in Mode 1 (Power Operation) at 100% power, an in-plant operator restoring equipment line-ups for personnel protection discovered that two Unit 14.16 kV breakers were in the "racked-out" position instead of "removed" from their corresponding 4.16 kV emergency switchgear bus cubicles. As a result, the buses were not seismically qualified and should have been declared inoperable from the time the breakers were "racked out" on March 8. With the two busses inoperable, both Control Structure Chillers were also inoperable. After being notified, control room operators initiated an inspection of the remaining 4.16 kV emergency switchgear bus breakers in Unit 1. None were found mispositioned. At 03:10, the breakers were "racked in" and the corresponding buses were returned to operable status. The mispositioned breakers were attributed to inadequate preparation and review of an equipment release form and clearance order by Work Management and Operations personnel. Personnel that prepared and reviewed those documents did not utilize a procedure that describes bus operability requirements for "racked out" breakers. Those involved had a larger number of tasks than usual to complete and relied on memory rather than reviewing the procedure. Operations personnel that processed the clearance order and placed breakers in the "racked out' position did not recognize that the action made the buses inoperable. All other similar equipment release forms were checked for problems. None were found. Placards were installed on all 4.16 kV emergency switchgear bus breakers stating acceptable positions. An informational bulletin on the event was issued to Operations personnel. Work management personnel will receive a tailboard on the event and use of a software flag for incorrect equipment position designations will be evaluated. This event is reportable as an Event or Condition That Alone Could Prevent Fulfillment of a Safety Function per 10CFR50.73(a)(2)(v)(D) and a Condition Prohibited by the Technical Specifications per 10CFR50.73(a)(2)(i)(B) for Unit 2. Unit 1 was not affected by the event. A risk analysis of the event showed there was a negligible increase in risk to Unit 2 while the breakers were "racked out". A seismic event did not occur while the breakers were in the "racked out" position, no actual loss of power, and no actual adverse consequences to the health and safety of the public as a result of this event.
3882002003 | Susquehanna 2 | 03/29/2002 | 05/24/2002 | ML02156041 | <strong>Low Service Water Flow Causes Temporary Loss of Control Structure Chillers</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2002, with Unit 1 in a refueling outage (Mode 5, 0% Power) and Unit 2 operating at reduced power (Mode 1, 24% Power) to support Unit 1 and Unit 2 cooling tower valve replacement activities, the operating Unit 1 Service Water (EIIS Code: KG) pump cavitated. The low Service flow condition caused the in-service 'A' Control Structure (CS) chiller to trip at 23:44 and inhibited standby 'B' chiller from automatically starting. Actions were taken to restore selected systems using Emergency Service Water (ESW) in accordance with the off-normal procedure for loss of Service By 00:12 on 3/30/02, the `B' CS chiller was capable of fulfilling its required safety functions for all conditions. The loss of Unit 1 Service Water was caused by low water level in the Unit 1 Cooling basin and high Unit 1 Cooling Tower screen differential pressure. The inability to promptly restore CS chiller to service following a low cooling water flow trip was caused by a design limitation within chiller control logic and less than adequate procedures to restore the chillers. The operating procedures for the Service Water system and for CS Chillers will be revised to prevent recurrence of this event. The control logic for the CS chillers will be modified so that a loss of Service Water will not prevent manual automatic starting with ESW. Based upon the short amount of time that neither chiller was fully available, and the fact that the chillers would have provided the required safety function in most accident situations, this event resulted in very low safety significance. There were no actual consequences to the health and safety of the public as a result of this event.
3882002004 | Susquehanna 2 | 09/30/2002 | 11/27/2002 | ML02344024 | <strong>Unplanned RPS Actuation - Loss of Condenser Vacuum and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On September 30, 2002 with Unit 2 in Mode 1 (Power Operation) at 100% power, electricians working at an Uninterruptable Power Supply (UPS) inappropriately configured panel breakers in a manner that energized a large set of capacitors. A Reactor Recirculation pump runback caused by the resulting momentary electrical transient reduced power to 72%. The electrical transient also resulted in an Off gas system shutdown and a slow degradation of condenser vacuum. At 72% power, an automatic reactor scram occurred, in accordance with plant design, when the Main Turbine tripped on low condenser vacuum. The automatic Main Turbine trip occurred sooner than proceduralized setpoint information indicated it should have, thus precluding a manual intervention that was planned upon attainment of a predetermined condenser pressure. Poorly worded work instructions associated with the UPS panel work were responsible for the inappropriate breaker alignment. Additionally, a malfunctioning UPS panel breaker permitted establishment of the erroneous configuration despite breaker closure logic that should have prevented the alignment. ECCS was not challenged during this event. No abnormal operator actions were required to place the plant in a stable condition. The malfunctioning UPS panel breaker will be replaced. The plant procedure that governs work instruction development will be modified to improve the content and format of future work plans. Preventative maintenance tasks will be developed to ensure proper operation of the malfunctioning UPS panel breaker and other similar UPS breakers. Finally, turbine trip setpoint information contained in Operating procedures has been revised to reflect actual trip settings. This event is reportable for Unit 2 as an Unplanned RPS Actuation per 10 CFR 50.73(a)(2)(iv)(A). There were no actual adverse consequences to plant equipment or to the health and safety of the public as a result of this event.
3882002005 | Susquehanna 2 | 10/07/2002 | 11/27/2002 | ML02344024 | <strong>Operations Prohibited by Technical Specifications Due to Inoperable Main Steam Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2002 with Unit 2 in Mode 4 (Cold Shutdown) at 0% power, the '2B' Inboard Main Steam Isolation Valve (MSIV: HV241F022B) was declared inoperable when the valve stroked greater than a second faster than allowed by Technical Specifications (1.92 sec. Actual vs. 3-5 sec. Target). A review of test history concluded that the valve may have been inoperable for as many as 360 days prior to the time of discovery. This period exceeds Technical Specification required completion times developed for Primary Containment Isolation Valves (PCIV). Calculations were performed following this event, using more restrictive closure stroke times than those actually experienced, to determine reactor pressures following a postulated Main Steam isolation. These calculations confirm that the peak reactor vessel pressure would not have exceeded established limits. Primary containment entry and inspection revealed that an oil leak on the oil dashpot hydraulic piping was responsible for the failed stroke test. The leak was repaired on October 7, 2002 and the MSIV is now fully operable. Maintenance procedures, preventative maintenance activities, modification solutions and industry best practices will all be explored for changes to enhance MSIV oil piping leak performance. At no time was the valve's ability to provide containment isolation adversely affected by the fast closure time. This event is reportable for Unit 2 as a condition prohibited by Technical Specification 3.6.1.3 per 10 CFR 50.73(a)(2)(i)(B). There were no actual adverse consequences to plant equipment or to the health and safety of the public as a result of this event.
3882002006 | Susquehanna 2 | 10/30/2002 | 12/23/2002 | ML03003072 | <strong>Operations Prohibited by Technical Specifications Due to Inoperable Reactor Core Isolation Cooling Check Valve</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2002 with Unit 2 in Mode 1 (Power Operation) at 100% power, the Unit 2 Reactor Core Isolation Cooling (RCIC) exhaust check valve (249F040) was declared inoperable following Local Leak Rate Testing (LLRT). A review of the system operating history concluded that the valve had likely been inoperable for 18 days prior to the time of discovery. This period exceeds Technical Specification required action completion times developed for Primary Containment Isolation Valves (PCIV). Disassembly revealed that the valve had not fully seated following the last RCIC turbine operation. During the investigation, the minimal force generated by the weight of a maintenance tool was sufficient to return the disk assembly to a fully seated position. The RCIC system's ability to inject flow to the reactor vessel was not affected by this event. Additionally, the inboard isolation gate valve (HV249F059) in this penetration remained operable and capable of performing the containment isolation function. Potential cause contributors to the exhaust check valve failure have been addressed through cleaning the valve internals and chamfering sharp edges that had been present on the valve's guide ribs. A Local Leak Rate Test was satisfactorily performed following the valve maintenance effort. Upon refilling the test volume following turbine operation under low steam flow, visual observation at an upstream drain did not detect leakage past the valve thus providing additional assurance that the valve would fully seat under these conditions. This event is reportable for Unit 2 as a condition prohibited by Technical Specification 3.6.1.3 per 10 CFR 50.73(a)(2)(i)(B). There were no actual adverse consequences to other plant equipment or to the health and safety of the public as a result of this event.
3892002001 | St. Lucie 2 | 05/13/2002 | 07/03/2002 | ML02190009 | <strong>Control Room Envelope DegradedDuring Door Seal Maintenance Activities</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2002, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power. St. Lucie started repair activities on control room door RA-114, an external door of a two-door vestibule. On May 16, 2002, the control room failed a Technical Specification pressurization surveillance test, and St. Lucie determined that the tee failure was due to the inability of RA-108, the vestibule inner door counterpart to RA-114, to maintain the control room boundary during RA-114 maintenance activities. Although this condition existed for longer than 24 hours, the Technical Specification allowed outage time for an inoperable control room ventilation system, the effect of the door seal maintenance on the control room envelope was not realized prior to the test failure. This event was caused by personnel error because degraded door seal conditions were not adequately evaluated. Although a pre-maintenance check was performed, the contra room ventilation system was in its normal, not emergency, system lineup and the check was therefore unable to correctly determine the status of the control room boundary. Door seals were installed on RA-108, and the control room passed its pressurization surveillance test on May 16, 2002. This event is being considered for inclusion in the continuing training program.
3892002002 | St. Lucie 2 | 08/19/2002 | 10/14/2002 | ML02289009 | <strong>As-Found Cycle 12 Pressurizer Safety Valve Setpoints Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2002, St. Lucie Unit 2 was in Mode 1 at approximately 100 percent reactor power. Wyle Labs informed FPL of unsatisfactory test results for two of the three code pressurizer safety valves removed during the Cycle 13 refueling outage. Wyle Labs was contracted to perform the offsite pressurizer safety valve testing and the testing was conducted within the required time restraints. Technical Specification 3.4.2.2 requires the as-found setpoints of the pressurizer safety valves to be = 2435.3 psig and = 2535.3 psig. The as-found settings of two St. Lucie Unit 2 pressurizer safety valves were 2.37 and 3.66 percent high, outside the Technical Specification tolerance limit of +/- 2 percent. The cause of the failed pressurizer safety valve tests was due to valve spring performance issues and mechanical setpoint drift over the operating cycle. There is no past or present operability concern as the subject pressurizer safety valves were removed and replaced with pre-tested valves during the St. Lucie Unit 2 Cycle 13 refueling outage. There was no affect on the health and safety of the public during past St. Lucie Unit 2 Cycle 12 power operations because the limiting overpressure analyses remain bounding for the as-found condition.
3902002001 | Watts Bar 1 | 03/01/2002 | 04/29/2002 | ML02126053 | <strong>Loss of RHR Flow Path in Mode 6 with Reduced RCS Level</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2002 at approximately 0258 hours, with Watts Bar Unit 1 in Mode 6 (Refueling) and RCS temperature at 100 degrees F, while attempting to realign the RHR system from RWST supply to RCS loop operation, operators isolated the common suction to the Residual Heat Removal (RHR) pumps on two occasions over a three minute span. At the time of the event, operators were performing full flow testing of ECCS lines in conjunction with reactor cavity fill. The crew had not been briefed during shift turnover of other work activities which removed power from a rack which provided a permissive pressure switch signal to two valves which required manipulation during the realignment. The root cause of this event was inadequate work review and scheduling coupled with less than expected transfer of information, pre-job brief, and response to an emergent operating condition. Corrective actions to include: Counsel/coach individuals/groups involved, include this event in training, refine the scheduling and planning process by which work activities are tied to specific plant conditions or milestones and impacts are evaluated based on plant conditions and scheduled activities. (Voluntary Report)
3902002002 | Watts Bar 1 | 03/07/2002 | 09/09/2002 | ML02254033 | <strong>Missing Auxiliary Feedwater Guard Pipe Inspection Covers - Voluntary LER</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2002, while the plant was in Mode 6,an on-shift senior reactor operator discovered two inspection covers missing from the guard pipe which encapsulates the Unit 1 four inch Auxiliary Feedwater Pump Turbine (AFWPT) steam supply line where this line passes through the Unit I Auxiliary Building elevation 692.0 penetration room and enters into the AFWPT room. The guard pipe is used as a barrier to isolate a steam leak in case of a steam supply line rupture and vent steam into the AFWPT room where redundant temperature sensors will initiate isolation by closure of redundant valves located in the south main steam valve vault room. This guard pipe was installed primarily to prevent unacceptable damage to essential equipment located in the auxiliary building. The encapsulation serves to restrain the pipe thus preventing pipe whip and confines the steam jet. Upon initial evaluation, it was postulated that a circumferential rupture at the 90° elbow (near the area where these inspection covers were found missing), could have resulted in potentially unacceptable impact on environmental qualification of safety related equipment needed to mitigate the event. In addition to the missing covers, a penetration seal was found to be inappropriately installed in the mechanical sleeve which connects the guard pipe to the AFWPT room which may have delayed automatic isolation of the postulated rupture of the steam supply line. However, since that time, TVA has performed an extensive evaluation and determined that equipment required to mitigate the event would perform required functions. This LER is being provided as a voluntary report. The cause of the condition has not been identified. The condition appears to have existed since prior to initial fuel load in November of 1995.Corrective actions included fabrication and replacement of the pipe covers, removal of the penetration seal, and a confirmation review of similar configurations in the plant.
3902002003 | Watts Bar 1 | 07/13/2002 | 09/11/2002 | ML02259006 | <strong>Automatic Turbine/Reactor Trip Due to Main Transformer Protection Circuit Ground Due to Inadequate Cable Splice</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2002, at approximately 1622 EDT, while the plant was in Mode 1, at 100% power, Watts Bar Unit 1 experienced an automatic turbine/reactor trip when a C-Phase Main Transformer differential relay actuated This occurred because a bolted cable splice associated with a C-phase current transformer (CT) came into contact with the CT junction box; thereby shorting the differential relay protection circuit to ground. The apparent factors contributing to this short circuit condition include temperature, cable splice material, vibration, and configuration of the splice inside the junction box. All control rods inserted properly in response to the reactor trip. The Auxiliary Feedwater (AFW) System actuated in response to the trip, as designed. Plant response was in accordance with design with no complications. Operations shift personnel performance was in accordance with applicable procedures. Subject to confirmatory laboratory testing, the root cause of this event was determined to be inadequate work instructions that allowed lower temperature rated tape to be used on a cable replacement and/or inadequate application of splice material. Corrective actions include revision and training on TVA's engineering and maintenance procedures for high temperature jacketing material, laboratory analysis of damaged splices, and reinspection and taping of similar vulnerable cable splices.
3902002004 | Watts Bar 1 | 09/21/2002 | 11/08/2002 | ML02319008 | <strong>Partial Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>While operating at 100% power on September 21, 2002, Watts Bar Unit 1 experienced a momentary loss of the 161 kV offsite power feed to Common Station Service Transformer (CSST) D. WBN's two offsite power supplies are fed from a remote switchyard located at the Watts Bar hydroelectric plant. The affected offsite power source through CSST D is the primary power source for 6900V Shutdown Boards 1B-B and 2B-B. The partial loss of offsite power was caused by the inadvertent manual operation of a breaker at the hydroelectric plant switchyard. The opening of the breaker occurred at 11:00:20 (EDT) and the breaker was reset to provide offsite power at 11:00:34 (EDT). Due to this event, and the loss of the primary feed to the shutdown boards, a valid engineered safety function (ESF) actuation occurred which started all four of the standby diesel generators (DGS), along with, as designed, the 1B-B Motor Driven Auxiliary Feedwater (AFW) Pump and the Turbine Driven AFW Pump. The DGS provided power to the affected Shutdown Boards and other required blackout loads during the event.
3902002005 | Watts Bar 1 | 09/27/2002 | 11/26/2002 | ML02333046 | <strong>Loss of Offsite Power Due to a Fire at the Watts Bar Hydroelectric Generating Plant (WBH)</strong><br /><i>Abstract:&nbsp;</i>At 0824 EDT on September 27, 2002, Watts Bar Nuclear Plant (WBN) Unit 1 was operating at 100% power when 6.9 kV shutdown logic board panel 1A-A load stripping relay actuated. At 0842 EDT, the 6.9 kV shutdown logic board panel 1B-B load stripping relay actuated. These actuations occurred due to a loss of both offsite power lines which resulted in an automatic start and loading of both trains of Emergency Diesel Generators. At 0852 EDT, WBN declared a notification of unusual event (NOUE) due to the loss of both offsite power sources which resulted from a fire at the Watts Bar Hydroelectric Generating Plant (WBH). The WBN fire brigade was dispatched to fight the fire and remained there until the fire was extinguished. Since the brigade remained at the fire location and callout of additional brigade staffing took greater than two hours, 10 CFR 50.54(x) was invoked to address this departure from the minimum fire brigade staffing requirement of the WBN Fire Protection Report. WBN remained at 100% power with all four emergency diesel generators operating throughout the event. Offsite power was restored using an interim offsite configuration from Sequoyah and Rockwood lines. TVA evaluated and determined this configuration to be a Generic Letter (GL) 91-18 non-conforming condition that supports functionality and operability of both 161 kV preferred power sources per GDC 17. Condition D of LCO 3.8.1 was exited at 0125 EDT on September 28, 2002, when the first qualified offsite source was returned to service. WBN remained in Condition A of LCO 3.8.1 until the second qualified offsite source was returned to service at 0300 EDT. The NOUE was exited at 0308 EDT on September 28, 2002.
3952002001 | Summer 1 | 02/04/2002 | 04/04/2002 | ML02098018 | <strong>Missed Analyses on Diesel Fuel Oil Sample</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2002, diesel fuel was delivered onsite for the emergency diesels. Technical Specification surveillance requirement 4.8.1.1.2.d.2 for fuel analysis is implemented by Surveillance Test Procedure, STP 606.001. This procedure directs that a sample be obtained from each truck delivering diesel fuel oil and selected analyses be performed prior to unloading into the storage tanks. As required, a sample was collected from the diesel fuel oil truck and the appropriate analyses were performed with acceptable results before the truck was unloaded. Seven additional analyses are required to be completed within 30 days of sampling the truck, however the sample collected from the diesel fuel oil truck was mistakenly discarded before the remaining seven analyses were completed. The cause was determined to be human error. The supervisor had told the individual that it was okay to discard all lube oil samples located on the sample cart. The individual discarded all the old samples on the cart including the diesel fuel oil sample. The immediate corrective action was to perform all analyses on the contents of both storage tanks. The tanks were determined to be within specification. The emergency diesel generators were operable at all times.
3952002002 | Summer 1 | 04/18/2002 | 06/13/2002 | ML02177003 | <strong>Incorrect Value in Fuel Handling Accident Analysis</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2002, while performing an evaluation on control room habitability after a Fuel Handling Accident (FHA) for a NRC request for information related to the Spent Fuel Pool Expansion Project, it was discovered that a prior evaluation used a non-conservative input in the calculation. The prior evaluation concluded the resulting activity release from a postulated FHA could be rapidly detected and contained within the reactor containment via rapid closure of the purge supply and exhaust isolation valves. This conclusion was based, in part, on the minimum transit time within the exhaust ventilation ducting from the reactor cavity to the purge isolation valves. The transit time has now been determined to be less than the credited time to close the isolation valves, thus creating the potential for an environmental release. The cause was determined to be an assumption that the FHA occurred in the vicinity of the reactor cavity whereas the new calculation considered more limiting locations within the refueling canal. Corrective actions were taken to establish administrative controls to restrict operation of the reactor cavity and refueling canal surface ventilation system during periods of core alterations and fuel movement inside containment. This action is expected to have little or no impact on ALARA since plant operating experience has indicated that airborne contamination being emitted from the cavity/canal water surface is not significant.
3952002003 | Summer 1 | 06/01/2002 | 01/28/2003 | ML03042001 | <strong>Automatic Reactor Trip Due to Spurious Noise on a Nuclear Instrumentation Channel</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2002, at 1840, the reactor tripped automatically due to a spike on Nuclear Instrumentation (NI ) Intermediate Range channel N-36. The reactor was being held steady at approximately 2% power and no significant plant evolutions were ongoing at the same time. The indicator for channel N-36 spiked to a value greater than the trip setpoint and the reactor protection system automatically tripped the plant. After the trip, spiking was still occurring on this channel. No other NI channel indicated any power increase during this event. The cause was preliminarily determined to be noise resulting from a failed or degraded circuit card. Multiple circuit cards were replaced and the spiking problem did not reappear. The actual cause of the noise problem has not been determined. The vendor has indicated the power supply vintage has the potential to fail high and cause additional damage to circuit cards, although there is no evidence that a power supply failure occurred. The power supply was not replaced at this time. One circuit card (A-8) has the visual appearance of overheating. The card A8 will be sent off to the vendor for failure analysis. A root cause investigation determined that a high voltage power supply problem was the cause. The power supplies have been replaced. The circuit cards and power supplies are being placed into the preventative maintenance program for routine replacement.
3952002004 | Summer 1 | 06/17/2002 | 08/16/2002 | ML02232034 | <strong>Automatic Reactor Trip on Lo-Lo Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2002, the plant was operating at 100% power when a fuse blew in the digital speed control system for the "C" main feedwater pump. Per procedure, the operating crew began reducing load at the rate of 1% per minute, and the remaining 2 main feedwater pumps began increasing speed and flow to compensate for the loss of the third pump. As the discharge flows for the operating feedwater pumps increased, the flows over-ranged the flow transmitters and the newly installed digital speed control system interpreted the signal as a "bad quality" flow value and the pumps' recirculation valves went full open. With a significant portion of feedwater flow now being diverted to the deaerator instead of the steam generators, steam generator levels began to decrease. Operators were unable to take manual control of the recirculation valves and increased the load reduction rate to 3% per minute, but steam generator levels continued to decrease. "A" steam generator reached its lo-lo level of 30% narrow range first and initiated the reactor trip signal and subsequent reactor trip. The transient response of the plant was appropriate for a reactor trip caused by reduced feedwater flows and resulting decreased steam generator levels. Reactor coolant system average temperature (Tave), pressurizer pressure and level, and steam generator levels returned to normal no-load values within minutes of the initial trip transient. No safety injection set points were challenged, and both the turbine driven and the 2 motor driven emergency feedwater pumps started as designed and supplied sufficient feedwater to effect recovery. The cause of the reactor trip has been determined to be a design deficiency in the implementation of the digital speed control system for the main feedwater pumps.
3972002001 | Columbia | 02/14/2002 | 04/10/2002 | ML02113047 | <strong>Completion of Technical Specification Required Shutdown to Comply with Technical Specification LCO 3.8.1 Required Actions of Condition F</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2002 at 0314 with Columbia Generating Station (Columbia) operating at 100% power, planned online maintenance commenced on Emergency Diesel Generator (EDG) 2. Maintenance was completed as scheduled. Surveillance testing to demonstrate operability of the EDG-2, and exit from the Limiting Condition of Operation (LCO), was started on February 13. Immediately after the EDG-2 output breaker was closed, the control room received an annunciator alarm. Investigation and evaluation revealed that the circuit breaker had closed but the Mechanism Operated Cell (MOC) switch assembly had failed to change state as expected. Columbia was at 100% power, when it was decided to shutdown the plant within the 72 hour completion time of TS 3.8.1 Required Action B.4. On February 14, 2002 at 1257 the plant entered Mode 3 as required by TS 3.8.1.F.1. The failure of the MOC switches to not fully actuate was due to lack of preventive maintenance and a breaker replacement that produced less drive force to actuate the MOC assembly. The root cause was the failure to recognize the importance of MOC assembly maintenance. The corrective actions are to establish maintenance on all 4160 volt and 6900 volt cubicle switchgears, and to enhance an existing Circuit Breaker Program to provide guidance on breaker and cell maintenance.
3972002003 | Columbia | 05/03/2002 | 08/07/2002 | ML02227027 | <strong>Water Leakage Paths Through Fire Rated Floor Assemblies</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2002, at 1540 hours approximately 15 to 20 gallons of water spilled onto the floor of the Radwaste Building Cable Spreading Room (CSR). A small amount of water leaked down into the Remote Shutdown Room below the CSR floor. The pathway for leakage through the floor of the CSR was through cracks in the concrete that allowed a penetration flood seal to be bypassed, and through shrinkage and flexural cracks in the reinforced concrete floor slab. The shrinkage and flexural cracks in the CSR floor were also the source of a small amount of leakage from the spilled water into the Division II switchgear room. Operability of safety-related equipment in the Remote Shutdown Room and Division II switchgear room was not affected. The root cause of this event is unsealed cracks that allowed leakage through floors. Contributing cause codes are associated with inadequate attention to emerging problems, as well as inadequate decision making, improper mindset, and tunnel vision. Immediate corrective action was to post compensatory one-hour fire/flood tours, and to seal the cracks that leaked. This Licensee Event Report is being submitted voluntarily because it might be of generic interest to other licensees.
3972002005 | Columbia | 12/28/2002 | 02/25/2003 | ML03065091 | <strong>Main Steam Leakage Control Fan Potentially Inoperable During a Design Basis Accident Due to Undersized Thermal Overloads</strong><br /><i>Abstract:&nbsp;</i>On December 23, 2002, with the plant in Mode 1 at 100% power, the Main Steam Isolation Valve Leakage Control Fan 1 (MSLC-FN-1) tripped off during its monthly surveillance after approximately 45 minutes of operation. Operators reset the thermal overload (TOL) relays and the fan re-started. The fan tripped a second time after approximately 50 minutes of operation. Upon investigation, it was determined that the TOL relays for the fan motor were undersized for the application. On December 29, 2002, new properly sized TOLs were installed and the system was returned to an operable status. The root cause for the undersized TOL relays was a lack of programmatic instructions to ensure communication between organizations. A new motor was installed in 1991 and the nameplate load on the new motor was higher than the original motor. There was no direction to verify or update the governing electrical drawing E528. A contributing cause appears to be a wrong assumption that the difference in the full load amps between the new and original motor required no further actions. The corrective action for this event is already in place. Current plant procedures establish a limitation on use for motors, and direct the E528 drawing to be revised when new motor attributes are different from the motor being replaced. Additional recommendations have been made to improve the motor limitation on use and to perform a partial review of electrical drawing E528 to ensure drawing fidelity.
4002002001 | Harris | 01/02/2002 | 03/04/2002 | ML02074053 | <strong>Reactor Trip Due to Main Feedwater Regulating Valve Bypass Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On January 2, 2002 at 0305, the Harris Nuclear Plant (HNP) was manually tripped, during a plant startup following RFO-10, due to a failure of a Main Feedwater Regulating Valve Bypass Valve. The plant trip was initiated at approximately 7% reactor power when Steam Generator (SG) divergent level swings were observed on all three SGs. SG level was being controlled in automatic by the Main Feedwater Regulating Valve Bypass Valves (MFRVBV) and the valves were traveling full open to full shut in response to the level swings. Following a full shut swing, "C" MFRVBV (1FW-198) failed to respond to an automatic open demand signal from the associated controller located on the Main Control Board. The Balance of Plant operator attempted to open 1FW-198 by taking the controller to manual with a 100% demand, however, indication of actual valve position showed the valve to be shut. With "C" SG level at 30% narrow range level indication, the Unit Senior Control Operator (USCO) directed a manual reactor trip. The manual reactor trip was successful. Cause: Component Failure: Component degradation. The I/P converter for "C" MFRVBV (1FW 198) experienced a failure attributed to an internal blockage of air. Corrective actions: Replaced the I/P on "C" MFRVBV with a Masoneilan Model 7000 I/P.
4002002002 | Harris | 07/13/2002 | 09/11/2002 | ML02259023 | <strong>Manual Reactor Trip Due to Turbine Digital Electro-Hydraulic Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>At about 1:10 am on July 13, 2002, with the plant reducing load to perform a turbine valve test, a manual reactor trip was performed due to a Main Turbine Digital Electro-Hydraulic (DEH) control system malfunction. While reducing load to 900 MWe; governor valve 4 indicated shut with demand still indicating 8.4%. The DEH "HOLD" button was pressed but the other three governor valves continued closing. A manual reactor trip was inserted due to the uncontrolled turbine load decrease. An automatic start of the Auxiliary Feedwater Pumps occurred due to low steam generator level during the transient. Cause: A component failure led to conditions requiring the manual reactor trip. Component failure and failure to incorporate industry operating experience into the preventative maintenance program, operating procedures, and training are the root causes identified for this event. Corrective Actions: The failed component was replaced. Ownership of the DEH computer controls system has been transferred from the Nuclear Information Technology Unit to Harris Engineering. Operations procedures are being revised to provide guidance for operator control of turbine DEH system. Training will be provided to operators when MANUAL control of DEH is appropriate.
4002002003 | Harris | 08/15/2002 | 10/09/2002 | ML02290033 | <strong>Reactor Trip Due to Momentary Grid Undervoltage</strong><br /><i>Abstract:&nbsp;</i>At 21:26 on 8/15/02 the Harris Plant tripped from Mode 1 and approximately 100% power due to Reactor Coolant Pump (RCP) momentary undervoltage (UV) on two out of three RCPs. The under voltage relays associated with the "B" and "C" RCPs actuated simultaneously making up the required reactor protection logic to initiate a reactor trip as designed. An Auxiliary Feedwater System automatic start also occurred during this event due to low steam generator level resulting from the plant transient. The offsite power supply to Harris Plant and the onsite power distribution systems remained energized throughout the event. Cause: The cause of the reactor trip was the momentary grid undervoltage condition. The cause of the undervoltage condition was a grid transient generated when a faulted transformer was loaded onto a 230 KV transmission line in Raleigh, NC, approximately 20 miles from the Harris Plant. Corrective Actions: The Carolina Power & Light Transmission Department evaluated the event and developed an action plan to decrease the probability of a similar grid event. The Harris Plant will monitor actions by the Transmission Department. No specific actions will be taken for the Harris Plant itself based on equipment and personnel performing in accordance with expectations.
4002002004 | Harris | 08/30/2005 | 10/28/2005 | ML05307055 | <strong>Unanalyzed Condition due to Inadequate Separation of Associated Circuits</strong><br /><i>Abstract:&nbsp;</i>On December 20, 2002, inspection of the Harris Nuclear Plant (HNP) Safe Shutdown Analysis (SSA) identified that postulated fires could cause spurious actuation of certain valves. Valve actuation in the flowpath for the protected Charging/Safety Injection Pump (CSIP) could result in loss of the pump. Similarly, simultaneous spurious closure of multiple valves in the flowpaths to the Reactor Coolant Pump (RCP) seals could result in the loss of RCP seal cooling. HNP implemented interim compensatory actions upon discovery. During review and validation, HNP identified other postulated fires could cause spurious actuation of certain valves or components that could also result in the conditions described above and other similar conditions. These additional conditions were discovered on January 29 and July 23, 2003; February 13, August 13, September 14 & 15, October 4, 20, 26 & 29, 2004; and January 18, July 22, August 4 & 30, 2005. The cause of these conditions is inadequate original Safe Shutdown Analysis of certain conductor-to-conductor interactions or certain operator manual actions. Design changes or other methods approved by the NRC will be used to restore compliance.
4102002001 | Nine Mile Point 2 | 03/21/2002 | 05/20/2002 | ML02155046 | <strong>Automatic Scram Signal During Refueling Outage due to Inadequate Instrument Air Isolation Procedure</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2002, with Nine Mile Point Nuclear Station (NMPNS) Unit 2 shut down for refueling outage 8 (RFO 8), and in mode 5, a full scram signal was received at approximately 0315 hours. The reactor had been shut down prior to receipt of the scram signal. No control rod motion occurred as a result of the scram. High level in the Scram Discharge Volume (SDV) generated the scram signal. The high level in the SDV occurred when air from the Service Air System (SAS) supplying the Scram Air Header (SAH) was lost and the scram valves failed open allowing water to enter the SDV. Service Air, which is supplied by the Instrument Air System (IAS), was inadvertently lost during the planned isolation of the IAS. The isolation of IAS was being done in accordance with a new procedure N2-PM-@075, Instrument Air Outage - RFO8. Service Air was lost when the IAS was isolated without ensuring that an alternate air supply to the SAS was in service. The cause of the scram was the failure of the procedure's author and reviewers to ensure that the procedure for isolating the IAS includes steps for maintaining air supply to the SAS. Contributing causes include evolving changes in the work scope leading to late involvement of the reviewers, and insufficient time allotted for procedure validation and review. Corrective actions include changes to procedure N2-PM-@075, review of the scram event summary by Operations technical reviewers and procedure authors, and enhancements to verification and validation checklists that are used for reviewing new or revised procedures.
4102002002 | Nine Mile Point 2 | 03/16/2002 | 09/12/2002 | ML02263049 | <strong>Reactor Water Cleanup System Differential Flow Isolation Signal Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2002 at approximately 0030, Reactor Water Cleanup System (RWCU) Division I and Division II differential flow instruments were declared inoperable. The plant was shutting down for Refueling Outage 8 with thermal power approximately 18 percent. Flow from the RWCU was being directed to the condenser to control reactor vessel water level. As operators increased flow to the condenser, the differential flow indication also increased, which was unexpected. The purpose of the differential flow instrumentation is to identify breaks in the RWCU and automatically isolate RWCU from the Reactor Coolant System when the differential flow value reaches a predetermined setpoint and remains there for a specified period of time. Operations investigated the unexpected response and concluded that there was no leak or break in the RWCU system and that the differential flow instrumentation was malfunctioning. Operations then declared the differential flow instrumentation inoperable and entered the Action Statements for Technical Specification (TS) 3.3.6.1. The actions were to isolate the penetration within one hour, or be in hot shutdown within 12 hours and cold shutdown within the following 24 hours. Operations continued with the planned shutdown. Although the differential flow instrumentation was inoperable, the isolation valves would still close on reactor vessel low water level, and high ambient temperature in sections of the reactor building where the "hot leg" portion of RWCU is located. Unit 2 reached cold shutdown at approximately 0840 on March 16, 2002 and exited the TS action statement. The event was initially evaluated by Operations as not reportable at the time the instrumentation was declared inoperable. Further evaluation by the Licensing and Engineering Departments concluded that the event was reportable. The cause of the unexpected response of the RWCU differential flow instrumentation was incomplete filling and venting of the RWCU piping post maintenance. The cause of the incorrect reportability assessment was the incorrect understanding that the reactor vessel low level and high ambient temperature isolation signals were redundant to the differential flow isolation signal. Corrective actions include a procedure change to address venting of RWCU differential flow instrumentation lines post maintenance and a procedure change to address the reportability of inoperable RWCU differential flow instrumentation.
4102002003 | Nine Mile Point 2 | 09/29/2002 | 11/23/2002 | ML02338028 | <strong>Open Door Between the Control Building and the Auxiliary Building Results in Breach of the Control Room Envelope</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2002, at approximately 2015 hours, an Operator, while on Control Building rounds, found Control Room Envelope Door C288-1 open. This resulted in an inoperable Control Room Envelope boundary and the need to consider both Control Room Envelope Filtration (CREF) Systems inoperable. The plant entered Action Statement B of Technical Specification 3.7.2, Control Room Envelope Filtration (CREF) System, which requires restoration of the Control Room Envelope boundary within 24 hours. The door was immediately closed and the Action Statement exited. The door is designed to close automatically but in this instance the door remained open due to interference between the door seal and the floor, after a member of the Security Force passed through the door. Investigation by Security concluded that the door had been open for less than one hour. The event is reportable in accordance with 10 CFR 50.73(a)(2)(v) as "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident." The cause of the event was the failure by a member of the Security Force to properly implement self-checking to ensure that the door was closed and secured after passing through. A contributing cause was interference between the door and the floor. Corrective actions include correcting the condition that caused the door to remain open, briefing Security Force personnel on the event, labeling doors, disseminating information about the event and the importance of door position, modifying General Employee Training, activating alarms on key carded doors and modifying procedures.
4102002004 | Nine Mile Point 2 | 11/11/2002 | 01/07/2003 | ML03023040 | <strong>Reactor Trip Due to Main Steam Isolation Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2002, at approximately 0515 hours, with Nine Mile Point Unit 2 (NMP2) at 100 percent power, an outboard main steam isolation valve (MSIV) disc separated from its stem allowing the disc/piston assembly to drop into the valve seat. This led to the rapid loss of flow in the "B" Main Steam Line resulting in a steam pressure transient. As result of increasing reactor pressure, the reactor scrammed due to a "Reactor Pressure High" trip signal. After the reactor scram, all MSIVS received closure signals and closed. The cause of the closure signals to the MSIVs was a "Main Steam Line High Flow" MSIV auto-isolation signal. The high main steam line flow was caused by the increased reactor pressure and flow being restricted to three of the four main steam lines. The reactor scram and MSIV closure are reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A). This report also constitutes a Part 21 Notification. The cause was a deficient MSIV design that did not ensure the proper stem-to-disc thread loading. Contributors to the failure were marginal thread dimensions and inadequate torque specifications during assembly. Five of eight MSIVs had been modified incorporating an improved design. The failed MSIV had not been modified. The corrective action was the incorporation of a modified stem-to-disc connection on the three remaining unmodified valves.
4102002006 | Nine Mile Point 2 | 12/16/2002 | 02/14/2003 | ML03058051 | <strong>Reactor Scram Due to Loss of Generator Stator Cooling</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2002, at 1545 hours, with Nine Mile Point Unit 2 (NMP2) operating at 100 percent power, an automatic turbine generator runback was experienced as a result of high temperature in the Generator Stator Cooling Water System. As a result of increasing reactor pressure, the reactor automatically scrammed at 1548 hours due to a "High Reactor Pressure" trip signal. At the time of the scram, reactor power was approximately 71 percent of rated power. This event is reportable in accordance with 10 CFR 50 73(a)(2)(iv)(A) as an automatic actuation of the Reactor Protection System that resulted in a reactor scram The cause of the high temperature in the Generator Stator Cooling Water System was failure of a mechanical linkage connection within stator water temperature controller 2GMC-TIC101. The cause for this failure was installation of the controller in a manner that exposed it to high vibration, which, over time, caused the linkage to fail. Recognition of past industry operating experience (OE) could have prevented occurrence of the NMP2 event. The corrective actions include replacement of temperature controller 2GMC-TIC101, inspection of other pneumatic controllers, initiation of engineering activities to increase the long-term reliability of 2GMC-TIC101, and changes to the industry OE review program.
4122002001 | Beaver Valley 2 | 01/11/2002 | 03/08/2002 | ML02071057 | <strong>Service Water Conditions for the Recirculation Spray System Leak to Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>During a surveillance test on January 11, 2002, service water flow rate through the Bravo train of the Recirculation Spray System (RSS) was found to provide insufficient flow as required by Beaver Valley Power Station Unit No. 2 Technical Specification (TS) 4.6.2.2.e.3. Upon discovery, the Bravo RSS train was declared inoperable and TS 3.6.2.2 action statement was entered. The cause of the low flow was blockage of the tubesheet by corrosion products formed in the inlet to the B RSS HX due to the presence of a prior air leak on the inlet endbell. The air leak on the endbell existed because approximately 4 adjacent mechanical fasteners of the 36 on the inlet endbell were loose. The loose fasteners were caused by improper maintenance techniques when the inlet endbell was reassembled during the prior refueling outage. On January 15, 2002, while planning for the service water flow surveillance test through the Alpha RSS train, it was discovered that both trains of RSS had been inadvertently rendered inoperable during the draining of the B/D RSS heat exchangers on three separate occasions. During the draining of the RSS heat exchangers, a common service water discharge isolation valve was closed per procedure on three separate occasions. Closing this valve placed the service water system in a configuration where the service water flow through the Alpha train of RSS has not been demonstrated to meet the minimum service water flow rate required by TS 4.6.2.2.e.3 of greater than 11,000 gpm for one train of RSS. Thus, during the three periods when the common isolation valve was closed (making the Alpha train of RSS inoperable) while the Bravo train of RSS was inoperable due to corrective maintenance, both trains of RSS were inoperable. This event is a condition prohibited by the plant’s TS and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The Bravo train RSS during its flow blockage and the Alpha train during the common valve closure remained capable of performing their safety function. Thus, the safety significance of this event was small.
4122002002 | Beaver Valley 2 | 02/14/2002 | 04/12/2002 | ML02106052 | <strong>Tagout Reduces Ability of Emergency Diesel Generator to Respond to Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2002, during a refueling outage at Beaver Valley Power Station Unit 2, clearance tags were being hung to remove the 2-2 emergency diesel generator (EDG) from service to support its scheduled refueling outage maintenance activities. This clearance for the 2-2 EDG had been modified approximately five days prior to its posting, to include additional electrical isolation. During the clearance revision, a typographical error resulted in one set of potential transformer (PT) fuses for the 2-1 EDG being added to the clearance instead of for the 2-2 EDG. This error was not discovered during the review process. The PT fuses were removed from the 2-1 EDG at 1400 hours (hrs) on February 14 by the clearance work order. This action disabled the 2-1 EDG output breaker, making the EDG inoperable because the EDG would not automatically load after starting. Subsequently, during the restoration of the 2-2 EDG to operation, it was discovered at 1815 hrs on February 18, that the 2-1 EDG PT fuses had been previously removed. The 2-1 EDG was immediately declared inoperable. The PT fuses were re-installed in the 2-1 EDG and the 2-1 EDG was declared operable at 1830 hrs. BVPS Unit 2 Technical Specification 3.8.1.2.b requires one EDG be operable in Modes 5 and 6. During the time that the PT fuses were removed from the 2-1 EDG, no EDGs were operable. This was a condition prohibited by the plant’s Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). This event occurred due to three causes: 1) shutdown safety process weakness, 2) outage clearance process weakness, and 3) expectations for clearance review/approval were not clearly understood nor consistently reinforced. The Core Damage Probability for this event was determined to be significantly less than 1E-06. The safety significance of this event was determined to be small.
4122002003 | Beaver Valley 2, Beaver Valley 1 | 02/22/2002 | 09/19/2002 | ML02269007 | <strong>Calibration Discrepancies in Delta Temperature Tau Time Constant Values Used in the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>During a review of the historical data for Overtemperature Delta Temperature (OTDT) reactor trip function used in the Reactor Protection System (RPS) at Beaver Valley Power Station (BVPS) Unit No. 2, it was identified that the procedure methodology for lead/lag testing did not provide correct data for time constant measurements. The incorrect OTDT lead and lag times caused the OTDT time constant Tau 4 (lead time) for all three Reactor Coolant System loops to not comply with the BVPS Unit 2 Technical Specification 3.3.1.1 Reactor Trip System Instrumentation setpoints, which requires a Tau 4 value of greater than or equal to 30 seconds. Therefore, the previously implemented Tau 4 time constant was not in compliance with BVPS Unit 2 Technical Specification requirements. During an extent of condition review, it was identified that surveillance calibration procedures utilized to calibrate the Overpower Delta Temperature (OPDT) rate/lag modules at BVPS Unit No. 1 contained incorrect scaling values and calibration instructions. This caused the OPDT time constant Tau 3 (lead time) for all three Reactor Coolant System loops to not comply with the BVPS Unit 1 Technical Specification 3.3.1.1 Reactor Trip System Instrumentation setpoints, which requires a Tau 3 value of greater than or equal to 10 seconds. Therefore, the previously implemented Tau 3 time constant was not in compliance with BVPS Unit 1 Technical Specification requirements. Continuing extent of condition review identified that the Tau 7 and K5 constants used in the OPDT reactor protection system channels at BVPS Unit 2 were incorrectly set. Therefore, the previously implemented Tau 7 and K5 constants were not in compliance with BVPS Unit 2 Technical Specification requirements. The BVPS Unit 1 and Unit 2 discrepancies are reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). These events were combined due to being identified via the same review activity. The cause for the Tau 4 and Tau 7/K5 discrepancies at BVPS Unit 2 was determined to be less than adequate method of presentation of written communication in 2001. The cause for the Tau 3 discrepancy at BVPS Unit 1 occurred due to non-existent/inadequate process to translate, verify and review that design requirements are correctly implemented in calibration procedures. The safety significance of these conditions was low.
4132002001 | Catawba 1, Catawba 2 | 02/24/2002 | 05/30/2002 | ML02164028 | <strong>Both Trains of Control Room Area Chilled Water System Were Inoperable Simultaneously as a Result of Inadequate Troubleshooting Follow-Up</strong><br /><i>Abstract:&nbsp;</i>From February 24, 2002 at 1735 hours until February 27, 2002 at 2255 hours, both trains of the Control Room Area Chilled Water System (CRACWS) were inoperable simultaneously, resulting in Units 1 and 2 being unknowingly in Technical Specification (TS) 3.0.3. At the time, CRACWS Train B was out of service for preventive maintenance. It was retroactively determined that during the early morning hours of February 21, 2002, the CRACWS Train A chiller had become inoperable due to relay leads that had loosened over time and had made intermittent contact. The leads eventually disconnected. The problem with the leads was not identified prior to taking CRACWS Train B out of service as a result of inadequate troubleshooting follow-up. This event resulted in a violation of TS 3.0.3, as well as a violation of TS 3.7.11 for the CRACWS. Corrective actions taken in response to this event include communicating the troubleshooting aspects of this event to appropriate station personnel so that suspected problem causes are validated prior to considering equipment operable.
4132002002 | Catawba 1 | 04/30/2002 | 06/24/2002 | ML02178001 | <strong>Condition Prohibited by Technical Specifications - Failure to Comply with the Required Actions of TS 3.9.2 with One Train of the Boron Dilution Mitigation System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2002, at approximately 0100 with Unit 1 in Mode 6, vital AC instrument panel board 1ERPD was removed from service for scheduled maintenance. Removing 1ERPD from service rendered train B of the Boron Dilution Mitigation System (BDMS) inoperable and it also disabled the Source Range Nuclear Instrument N-32 High Flux at Shutdown alarm function. Operations did not recognize that these functions were inoperable until approximately 0530. Technical Specification (TS) 3.9.2 requires two trains of BDMS operable in Mode 6. If one train becomes inoperable, there are several required actions that have to be completed. Therefore, since the required actions of TS 3.9.2 were not completed within the time allowed, this is a condition prohibited by TS and reportable to the NRC as an LER. The root cause was less than adequate use of available information to properly identify the effects of isolating 1ERPD. Corrective actions include discussing this event with the personnel involved, development of Operations Management guidance, and reviewing this event in Licensed Operator Training. This event is considered to be of no significance with respect to the health and safety of the public.
4132002003 | Catawba 1 | 05/26/2002 | 07/22/2002 | ML02207001 | <strong>Emergency Personnel Hatch Unlatched</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2002 at 0835 hours, the Unit 1 Emergency Personnel Hatch between upper and lower containment was discovered unlatched. Approximately 10 minutes after discovery of this condition, the hatch was latched, sealed, and returned to operable status. Technical Specification (TS) 3.6.14 requires the hatch to be operable and closed in Modes 1-4. The Limiting Condition for Operation requires the inoperable hatch to be restored to operable status and closed within one hour. The exact time the hatch became unlatched could not be determined but the condition most likely existed longer than the one hour allowed by the Limiting Condition for Operation. This event is being reported as a condition prohibited by Technical Specifications 10CFR50.73(a)(2)(i)(B). The root cause for the hatch becoming unlatched could not be conclusively determined. The most likely cause for the event is attributed to a hatch design that is prone to inadvertent unlatching due to passing traffic.
4132002004 | Catawba 1, Catawba 2 | 03/04/2002 | 07/25/2002 | ML02219031 | <strong>Pipe Spray Interaction Affecting Safety Related Equipment</strong><br /><i>Abstract:&nbsp;</i>During review of a plant modification it was noted that 600 volt motor control centers (MCCs) 1EMXG and 2EMXH may not have been adequately protected from potential moderate energy spray interactions in the chilled water (YC) chiller rooms. A section of fire protection system piping and demineralized water (YM) piping in both A and B train chiller rooms were identified as potential sources for moderate energy spray onto the MCC. Engineering evaluated this condition and determined that MCCs 1EMXG and 2EMXH had not been adequately protected from the effects of a moderate energy pipe break associated with the YM or fire protection systems inside the Train A and B YC chiller rooms as required by the UFSAR. Temporary spray deflectors were installed to correct the issue. Follow up reviews by engineering determined that 4160 volt bus 2ETA was determined to be a water spray target from fire protection piping to the hose rack cabinet in the area. Operations was notified and declared 2ETA inoperable and applied Technical Specification 3.8.9. A spray deflector was installed and 2ETA was declared operable. This event did not affect the health and safety of the public.
4132002005 | Catawba 1, Catawba 2 | 06/25/2002 | 07/25/2002 | ML02212041 | <strong>An Americium-241 Source Was Lost During Procedure Verification Activities</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2002, with both Catawba Units operating in mode 1 at 100% power it was determined that an Americium (Am-241) alpha source was missing. It was determined that the loss occurred on April 18, 2002 during a walkthrough associated with development of a procedure for calibration of a PCM-2 whole body monitor. An investigation determined that the cause of this event was an inadequate program for handling this sealed alpha source. Corrective actions include training for radiation protection personnel on precautions for handling sealed sources and fabrication of an alpha source holder for use in PCM-2 calibrations. This event had no effect on the safe operation of the plant. This source would present no danger to the health and safety of the public unless it were inhaled or ingested. Inhalation or ingestion of the source is considered unlikely due to the probable disposition and physical characteristics of the source.
4132002006 | Catawba 1 | 06/24/2002 | 09/25/2003 | ML03281027 | <strong>Technical Specification Noncompliance - Inoperable Diesel Generator Caused by Inadequate Wire Lug Crimping at Closing Spring Motor Disconnect Switch</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2002, at approximately 1100 hours, with the unit operating at 100 percent power, during performance of a periodic test, it was discovered that diesel generator 1B output breaker 1ETB-18 would not close. During troubleshooting, the ring lug wiring connection to the motor disconnect switch in breaker 1ETB-18's spring charging circuit was found to be disconnected. The springs in a breaker of this type are charged immediately after the breaker closes. All evidence indicates when the breaker was closed during the previous diesel generator test at approximately 2000 hours on June 24, 2002, the degraded connection finally opened and the springs did not completely recharge. If the charging springs are not fully charged the breaker mechanism is not latched and cannot be closed automatically. Diesel generator 1B was inoperable between June 24, 2002 at 2000 hours until the problem was corrected on June 29, 2002, at approximately 0125 hours, which exceeds the Technical Specification Allowed Outage Time. The root cause of this event is inadequate crimping of the wire in the ring lug connection. Corrective actions include breaker preventive maintenance program enhancements. This event did not adversely affect the health and safety of the public.
4162002001 | Grand Gulf 1 | 03/29/2002 | 05/28/2002 | ML02150038 | <strong>Follow-up to Division 2 DG Notice of Enforcement Discretion</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER to provide a follow-up to the Notice of Enforcement Discretion (NOED) received by Grand Gulf Nuclear Station on March 29, 2002. The NOED extended the limiting condition for operation (LCO) time by 72 hours to allow for repair and testing of the diesel generator (DG)[EK] as a result of the jacket water temperature switch failures. The NOED was invoked at 0402 on March 2gth to avoid commencing a Technical Specification (TS) required shutdown. Although the NOED was used to avoid the commencement of a plant shutdown, the Division 2 DG was restored to operable status in time to preclude a reportable condition. The Division 2 DG was declared inoperable on March 26, 2002 at 0402 for planned maintenance. During the planned maintenance, various problems occurred such as infant mortality failure of some of the process sensors that caused the DG to remain inoperable. Along with the infant mortality switch failure, the equipment tagging and re-tagging issues and the limited contingency planning resulted in a planned outage time of 46 hours extending into excess of the 72-hour allowed LCO. A root cause determination was performed with the resultant root cause identified as job performance standards not adequately defined. Condition Report, CR-GGN-2002-00555 was written to address exceeding the 72-hour LCO and will address the corrective actions to prevent recurrence of this type event.
4162002002 | Grand Gulf 1 | 04/29/2002 | 06/27/2002 | ML02200042 | <strong>RHR System Pressure Higher Than Normal Rendering Primary Containment Isolation Valve (PCIV) Inoperable for About 11 Days</strong><br /><i>Abstract:&nbsp;</i>During the performance of Residual heat Removal/Low Pressure Coolant Injection System RHR/LPCI-"A” [BO] quarterly functional test in accordance with procedure 06-OP-1El2-Q-0023 it was noted that RHR-A System pressure was higher than normal (approximately 80 psig total pressure). Investigation of this abnormality revealed that this pressure had existed since the system was last "filled and vented" on April 18, 2002 following maintenance on the system. The pressure source was determined to be P11 (Condensate & Refueling Water Storage and Transfer System) which is used during the "fill and vent" procedure. E12F044A (See “A” in the attached RHR Figure) was found not fully seated which admitted P11 to the system. This valve is an inboard Primary Containment Isolation Valve (PCIV) for penetration 20. The valve was immediately torqued closed upon discovery (April 29, 2002). Technical Specification Limiting Condition of Operation (LCO) 3.6.1.3 states, "Each PCIV shall be OPERABLE". The term Operable/Operability is defined as, "A system, subsystem, division, component, or device shall be OPERABLE or have OPERABILITY when it is capable of performing its specified safety functions(s)". Based on review of this event, E12F044A was considered inoperable for about 11 days. Therefore, this event is reportable and a 60-day LER is required.
4162002003 | Grand Gulf 1 | 06/22/2002 | 08/20/2002 | ML02233070 | <strong>Reactor Scram Due to Loss of Service Transformer 21</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2002 at approximately 2217, while operating at steady state conditions of 100 percent rated thermal power and 88.7 percent total core flow, a reactor scram occurred on Turbine Control Valve fast closure. It was the result of a ground fault on the secondary (i.e. 34.5 kV side) of Service Transformer 21 Engineered Safety Feature busses 16 and 17 were de-energized. Division 2 and 3 diesel generators started and energized busses 16 and 17, respectively. No Emergency Core Cooling System initiated. A partial loss of plant non-safety power busses occurred. Those powered by Service Transformer 21 were lost, while those powered by Service Transformer 11 remained energized. Important loads lost were both Reactor Recirculation Pumps, and the running Electro-hydraulic Control (EHC) pumps. A third EHC pump auto started on low fluid pressure. Condensate Pumps B and C, and Condensate Booster Pump C tripped due to loss of buss 14AE. Numerous Division 2 isolations occurred due to loss of 16AB. The lowest reactor level noted during the transient was minus 7 inches, approximately 18 inches below the low level automatic scram setpoint of 11 inches. Auxiliary site power loop was also de-energized. Important loads lost were the Emergency Operations Facility and a partial loss of security lighting. Both Reactor Feed Pumps (RFPs) tripped on low suction pressure about 8 minutes after the scram. One RFP was immediately restored. Safety related control room air conditioner “B” failed to sequence back on after the diesel re-energized buss 16. The air conditioner was started manually.
4232002001 | Millstone 3 | 01/25/2002 | 03/14/2002 | ML02087029 | <strong>Control Room Emergency Ventilation System Surveillance Failure</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2002, with reactor power at 100 percent, it was identified that the ventilation system flow measurements obtained to satisfy the monthly Technical Specification surveillance requirement for the Control Room Emergency Ventilation System (CREVS) had been corrected twice for the density effects of local pressure. The current surveillance data for both trains, adjusted to remove the extra pressure correction, was verified to be within the required range. However, a review of historical surveillance data identified several cases where the recorded Train A surveillance data, adjusted to remove the extra pressure correction, resulted in recorded system flows outside the required range. As a result, Train A of the CREVS was left in an inoperable, but available condition after completion of the historical surveillance tests. The time Train A was in this condition exceeded the 7 day allowed outage time. This issue is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications. During the time period that Train A of the CREVS was inoperable, no work was done that would have affected system flow rate. Train A was only inoperable due to the ventilation flow calculation error. Train A would have been capable of performing its accident mitigation function, as demonstrated by subsequent monthly testing which produced acceptable flow rates. This event did not result in the loss of any safety function, and is of low safety significance. The procedure used to perform the surveillance tests was not correctly revised in 1992 when new test equipment was purchased. The cause of this condition is attributed to weak interdisciplinary review requirements for procedure changes during that time period. Procedure changes have been completed to remove the pressure correction factor when this test instrument is used.
4232002002 | Millstone 3 | 12/26/2001 | 04/11/2002 | ML02168044 | <strong>Breaker Mechanism Failure Results in Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2002, Dominion Nuclear Connecticut, Inc. (DNC) determined that circumstances involving an event which occurred on December 26, 2001, were reportable as a condition prohibited by Technical Specifications (TS). On December 26, 2001, with the unit in Mode 1 at 100 percent power, the "B" Emergency Diesel Generator (EDG) was inoperable due to the EDG output breaker closing springs failure to charge. TS 3.8.1.1 requires a verification of offsite sources within 1 hour and at eight hour intervals, and completion of a common cause investigation within 24 hours. The condition existed for approximately 29 hours before identification, during which time the requirements of TS 3.8.1.1 were not met. This is considered operation prohibited by the plant's TS, and is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). The apparent cause for the breaker mechanism failure could not be determined. The delay in detecting that the "B" EDG was inoperable has been attributed to both work practice and the omission of relevant information in procedures. The item is documented in a recent NRC inspection report (NCV 50-423/01-14-01). This condition had low safety significance, and there was no loss of safety function. "A" train vital equipment was operable and no plant work was done to compromise the unit's risk configuration during the time that the "B" EDG was inoperable. The "B" EDG breaker was replaced on December 28, 2001, and the "B" EDG was returned to an operable status.
4232002003 | Millstone 3 | 08/22/2002 | 10/21/2002 | ML02302016 | <strong>Inadequate Validation of Fire Safe Shutdown Analysis Assumptions</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2002, with the Unit in Mode 1 at 100% power, it was determined that emergency operating procedure (EOP) directed actions did not provide adequate assurance that power operated relief valve (PORV) function would be disabled within a timeframe that would prevent a fire-induced spurious PORV actuation from depressurizing the reactor coolant system (RCS). During subsequent review, on August 22, 2002, it was determined that the assumed timeframe for mitigation of spurious opening of an atmospheric dump valve (ADV) bypass valve would not maintain pressurizer within acceptable levels as required by fire safe shutdown design basis. A plant response to spurious operation of a PORV is similar to a small break loss of coolant accident and spurious operation of the ADV bypass valve is similar to an excess steam demand event. The ability to effectively diagnose and manage events like these coincident with a design basis fire was not consistent with the fire safe shutdown design basis. These circumstances represent an unanalyzed condition that could significantly degrade plant safety and is being reported pursuant to 10CFR50.73(a)(2)(ii)(B). This condition is historical in nature dating to the original development of the assumptions used to support the fire safe shutdown analysis. Consequently a root cause evaluation was not performed. The apparent cause is attributed to a failure to properly validate fire safe shutdown analysis assumptions. Upon discovery, compensatory actions were implemented to minimize risk of fire in the areas of concern. These actions included increased surveillances to verify operability of detection and suppression systems, and to confirm control of transient combustibles and ignition sources in the affected areas.
4242002001 | Vogtle 1 | 03/12/2002 | 05/07/2002 | ML02144021 | <strong>Improperly Wired Interlock Affects ECCS Recirculation Valve</strong><br /><i>Abstract:&nbsp;</i>During the 1R10 refueling outage, two wiring errors were discovered that would have prevented the opening of 1HV-8804B during a loss of power to Train A. 1HV-8804B provides a path from the discharge of the Train B Residual Heat Removal Pump to the suction of the high head Centifugal Charging Pumps and the intermediate head Safety Injection Pumps. Although post-LOCA flow requirements continued to be met for design bases accidents, this condition represents operation of the unit in a condition prohibited by the Technical Specifications for post-LOCA ECCS recirculation operations. A review of work orders has found that these mis-wirings likely occurred during maintenance performed in 1991 and/or 1996. However, because of the time lapses involved, the root cause of these human performance errors cannot be conclusively determined. The appropriate procedure will be revised to require electricians to utilize the elementary drawing and wiring diagrams to verify wiring terminations prior to lifting leads on safety-related motor operated valves scheduled for maintenance.
4242002002 | Vogtle 1 | 04/05/2002 | 05/29/2002 | ML02154014 | <strong>Containment Isolation Valve Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2002, personnel were performing thermal overload bypass testing. A thermal overload bypass jumper was found disconnected in motor control center (MCC) cubicle 1BBE-07. The affiliated load for this circuit is the Reactor Coolant System Hot Leg Sample Valve, 1HV-3548, which is also a containment isolation valve (CIV). The jumper was promptly re-connected. Without the jumper in place, an overcurrent condition may have tripped the valve's (1HV-3548) thermal overload, rendering it incapable of performing its containment isolation function of closing. Technical Requirements Manual, Section 13.8.2, requires that a motor-operated valve with an inoperable thermal overload bypass jumper be declared inoperable and the appropriate Technical Specification (TS) condition be entered. Because 1HV-3548 is a CIV, TS 3 .6.3, "Containment Isolation Valves," is applicable. Since steps had not been taken to comply with action statement requirements, the unit operated in a condition prohibited by the TS. The cause of this event was the failure to properly install and verify the bypass jumper installation during the previous refueling outage. Personnel involved with this event will be counseled regarding the need for diligence when installing and verifying safety-related wiring. In addition, this event will be added to operating experience training for electricians.
4242002003 | Vogtle 1 | 04/20/2002 | 06/13/2002 | ML02172049 | <strong>Loss of Main Feedwater Leads to Unplanned ESF Actuation and Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2002, power ascension was in progress following a refueling outage. At 0500 EDT, a control room alarm was received due to the water level decreasing in steam generator (SG) #4. The reactor operator (RO) increased the speed of the A main feedwater pump (MFP). Almost simultaneously, the balance-of-plant operator recognized that the A MFP mini-flow valve was open and an operator in the turbine building was directed to shut it. Water levels in all four SGs began to rise rapidly, and operators lowered the MFP speed and throttled the main feedwater regulating valves. However, at 0509 EDT, SG #4 reached its high level setpoint which led to a turbine trip, a main feedwater isolation, and an auxiliary feedwater system actuation. The shift superintendent ordered a manual reactor trip, which occurred at 0510 EDT. The causes of this event are: the failure to increase MFP speed in normal increments to correspond with increased water demand as reactor power was rising, and an inadequate response to the SG water levels when it was recognized that levels had dropped too low. The operating crew involved has been counseled on the expectations of managing evolutions and performed just-in-time training prior to assuming the next shift.
4252002001 | Vogtle 2, Vogtle 1 | 10/22/2002 | 12/05/2003 | ML03343028 | <strong>Inadequately Staked Capscrews Render Residual Heat Removal Pumps Inoperable</strong><br /><i>Abstract:&nbsp;</i>At Unit 2 on October 22, 2002, while defueled, residual heat removal (RHR) pump A was started for dynamic fill and vent of the RHR system. Moments later, the pump tripped. An investigation determined that a back casing ring capscrew had come loose and lodged between the impeller and the back casing ring. It was found that the pump was last operated on October 11, 2002, when the unit was in Mode 6 (Refueling). It is believed that the capscrew came loose and lodged between the impeller and the back casing ring as the pump was being placed into standby status on October 11th. Because two pumps are required to be operable at certain times in Mode 6, this represented operation in a condition prohibited by the Technical Specifications. Because the other RHR pump was also found to have inadequately staked capscrews, this represented a condition that could have prevented the fulfillment of the safety function of a system needed to remove residual heat. This condition is also reportable per 10 CFR 21.21 because similar back casing rings with inadequately staked capscrews were found in the warehouse. Inadequately staked capscrews were also found in the Unit 1 Train B RHR pump during the fall 2003 refueling outage. The root cause of this event was determined to be the failure of the manufacturer to properly stake the back casing ring capscrews. The capscrews on the back casing rings for the affected RHR pumps were properly staked prior to the pumps being returned to service and the Units returning to Mode 6.
4252002002 | Vogtle 2 | 11/13/2002 | 01/08/2003 | ML03017060 | <strong>Steam Generator Level Control Problems Lead to Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 13, 2002, power ascension was in progress following a refueling outage. At approximately 0354 EST, the licensed operator designated as the steam generator water level control operator (SGWLCO) began to transfer steam generator feedwater control from the bypass feedwater regulating valves (BFRVs) to the main feedwater system regulating valves (MFRVs). A series of water level transients commenced in each of the four steam generators (SGs) that culminated in the SG #3 water level increasing to its Hi-Hi level setpoint at 0405 EST. The main feedwater system isolated, the main feedwater pump tripped, and the auxiliary feedwater system actuated, as designed. As SG water levels decreased to their low level setpoints, a manual reactor trip was initiated at 0405 EST, and SG water levels were stabilized in Mode 3 (hot standby). The root cause of this event was the failure of the SGWLCO to follow procedure by having all BFRVs and MFRVs open simultaneously. A secondary cause of this event was less than adequate supervisory oversight by the Unit Shift Supervisor in verifying procedure compliance during feedwater control operations. The policy for implementing unit operating procedures is being reviewed to determine if the level of flexibility and/or interpretation is appropriate. Expectations of command and control issues are also being evaluated.
4402002001 | Perry | 09/22/2002 | 01/31/2003 | ML03043003 | <strong>Unplanned Automatic SCRAM During Main Turbine Mechanical Trip Weekly Testing</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2002, at 0146 hours, when the Perry Nuclear Power Plant was operating in Mode 1 at 90 percent reactor power, a turbine trip occurred which resulted in a turbine control valve fast closure reactor scram Investigation determined that the turbine trip occurred due to the failure of the turbine trip latch assembly to properly reset following weekly testing. While attempting to reset the scram following the event, it was identified that a Scram Discharge Volume (SDV) drain valve stem coupling had failed. The valve repositioned to its required closed position during the scram, however, it would not reopen when the scram was reset. Additionally, increased seal leakage from Reactor Recirculation Pump A was noted. The turbine trip was caused by a malfunction of the turbine trip latch assembly which failed to reset following testing of the mechanical trip device. The failure to relatch was determined to be caused by latch travel limitations as a result of two missing setscrews. The missing set screws were replaced, the linkage was adjusted and the assembly was retested. The SDV drain valve failure to open was due to failure of the stem coupling. All four SDV vent and drain valve stem couplings were replaced with a coupling of an improved design The reactor recirculation pump seal leakage was due to a dislodged guide bushing in the seal assembly. The seal was replaced with a rebuilt spare seal. This event was reviewed and determined to be within design evaluation limits, and therefore was determined to be not safety significant. This event was reported via the Emergency Notification System in accordance with 10CFR50 72(b)(2)(iv)(B), as an event that resulted in an actuation of the Reactor Protection System when the reactor is critical. This report is being submitted in accordance with 10CFR50.73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of the system specified in 10CFR50.73(a)(2)(iv)(B)(1), which is the Reactor Protection System.
4402002002 | Perry | 10/23/2002 | 10/24/2002 | ML03304034 | <strong>Failure of the High Pressure Core Spray Pump to Start</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2002, at-1113 hours, the High Pressure Core Spray (HPCS) pump failed to manually start during routine testing of the HPCS room cooler at the Perry Nuclear Power Plant. At the time of the failure, the HPCS system was inoperable for the conduct of the testing and required Technical Specification actions had already been completed. The HPCS pump breaker did not close because the circuit breaker cell switch was out of adjustment. The root cause of the event was determined to be procedural inadequacy. The maintenance instruction for adjusting the cell switch did not provide adequate criteria for the inspection of the circuit breaker cubicle cell switch when performing maintenance. Following adjustment of the cell switch linkage and verification of proper operation, HPCS was returned to operable status at 1529 hours on October 24, 2002. Redundant Emergency Core Cooling Systems remained available during the unavailability of HPCS, but HPCS is significant from a risk perspective. Therefore, this event is considered to have a low to moderate safety significance, This event was reported to the NRC via the Emergency Notification System (ENF #39311) on October 23, 2002, at 1216 hours, in accordance with 10CFR5O.72(b)(3)(v)(D) as a condition that could have prevented the fulfillment of a safety function needed to mitigate the consequences of an accident. This LER is submitted in accordance with 10CFR50.73(a)(2)(v)(O) as an event or condition that could have prevented the fulfillment of a safety function of systems, structures or components needed to mitigate the consequences of an accident.
4402002003 | Perry | 11/14/2002 | 01/13/2003 | ML03023047 | <strong>Inadequate Emergency Closed Cooling Water Surveillance Instruction Results in the Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2002, with the Perry Nuclear Power Plant operating in Mode 1 at 100 percent power, a review of the Emergency Closed Cooling Water (ECCW) Pump and Valve Operability Test instruction steps revealed that the system's two independent loops were temporarily interconnected through non-safety related chemical addition system piping to facilitate performance of reverse flow testing of the ECCW system pump discharge check valves. Interconnecting the two safety related, divisionally separated loops of ECCW through the non-safety related piping, created a configuration whereby a design basis accident, which includes a seismic event, could have resulted in loss of ECCW system inventory. The loss of system inventory could have resulted m the loss of ECCW cooling capability. Consequently, the safety systems supported by ECCW would have been unable to perform their residual heat removal and accident mitigating safety functions during the time the loops were interconnected. The cause of this event was determined to be inadequate preparation, review and approval of the quarterly "ECC Pump and Valve Operability Test," Revision 7, made effective on November 18, 1998. The procedure has since been revised to eliminate reverse flow testing since it was determined that the ECCW system pump discharge check valves have no safety function to close in a design basis accident. Since the loops were cross-connected for only short periods of time for testing, this condition was considered to have low safety significance. The interconnection of the two independent ECCW subsystems is considered a condition that could have prevented the fulfillment of a safety function of a system needed to remove residual heat in accordance with 10CFR50.73(a)(2)(v)(B) and mitigate the consequences of an accident in accordance with 10CFR50.73(a)(2)(v)(D). This condition is also considered an event whereby a single condition caused two independent trains to become inoperable in a single system designed to remove residual heat in accordance with 10CFR50.73(a)(2)(vii)(B) and mitigate the consequences of an event in accordance with 10CFR50.73(a)(2)(vii)(D).
4432002001 | Seabrook | 05/28/2002 | 07/26/2002 | ML02219035 | <strong>Reactor Trip Due To A Digital Rod Position Indication Card Failure</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2002, at 2:31 AM, with the plant in Mode 4, the Control Room Operator initiated a manual reactor trip due to the loss of indication for control rod L5 during control rod surveillance testing. At the time of the event, control bank A was at 72 steps withdrawn; the other shutdown and control banks were fully inserted into the core. During the withdrawal of control bank A, a Digital Rod Position Indication (DRPI) urgent alarm was received indicating that the rod position indication for Control Bank A was invalid. Pursuant to Technical Specification 3.1.3.3, the reactor trip breakers were manually opened using the reactor trip switch. All rods fully inserted. All systems functioned as required. At the time of the event, reactor coolant temperature was approximately 276 degrees Fahrenheit and reactor coolant pressure was approximately 552 psig. An eight-hour event notification to the Nuclear Regulatory Commission (NRC) was made pursuant to the requirements of 10CFR50.72(b)(3)(iv)(A). The event notification was 38947. It was determined that DRPI rod L5 position indication card had failed in service. The failed card was replaced and the surveillance was completed satisfactorily. This License Event Report is being submitted pursuant to the requirements of 10CFR50.73(a)(2)(iv)(A).
4432002002 | Seabrook | 07/31/2002 | 09/27/2002 | ML02282019 | <strong>Non-Compliance with the Requirements of Technical Specification 3.8.1.1 Action b</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2002, with the plant operating at 100 % power, a surveillance test was performed on emergency diesel generator [EK] DG-1 B (DG-1 B). After approximately three hours of fully loaded operation of DG-1 B, plant operators noted that the kilovolt amperage reactive (kVAR) indication was fluctuating. As a result of the fluctuation, plant operators subsequently shutdown the engine and declared DG-1 B inoperable at 2302 on July 24, 2002. Technical Specification (TS) 3.8.1.1 Action statement b. requires that when one diesel generator is inoperable, the operability of the remaining diesel must be demonstrated operable within 24 hours. TS 3.8.1.1 Action b. also identifies that the operability of the remaining diesel generator need not be verified if it has been successfully operated within the last 24 hours, or if currently operating, or if the diesel generator became inoperable due to 1.) Preplanned preventive maintenance or testing; 2.) An inoperable support system with no potential common mode failure for the remaining diesel generator, or 3.) An independently testable component with no potential common mode failure for the remaining diesel generator. Subsequent analysis of the event determined that the decision not to test DG-1A within 24 hours was not consistent with guidance provided in TS Bases section 3/4.8.1. The failure to meet the requirements of TS 3.8.1.1 action b. is a condition prohibited by the Technical Specifications and is reportable pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B). Subsequent testing of DG-1A was satisfactorily completed at 0247on July 31, 2002. Additional corrective actions to prevent recurrence have been identified. There were no adverse safety consequences as a result of this event.
4452002001 | Comanche Peak 1, Comanche Peak 2 | 09/20/2002 | 11/15/2002 | ML02325036 | <strong>Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2002, at 12:00 p.m., it was identified that an Emergency Diesel Generator (EDG) should be declared inoperable while paralleled to an offsite source because the single failure criterion of IEEE Standard 379-1972 would not be satisfied when an EDG is operated in parallel with offsite power in Modes 1-4. The Comanche Peak Steam Electric Station (CPSES) Unit 1 and 2 EDGs were operated in parallel with offsite power on some occasions in the past for a time period greater than the time allowed to complete the Required Actions of the applicable Technical Specification. TXU Generation Company LP (TXU Energy) has determined that the cause of this event was that the uniqueness of the design and the operating restrictions of the CPSES electrical system were not clearly apparent. Upon determining that the EDGs were inoperable while paralleled to an offsite source, the EDG surveillance test procedures were changed to ensure that an EDG that is paralleled to an offsite source is declared inoperable. All times in this report are approximate and Central Daylight Savings Time unless noted otherwise.
4452002002 | Comanche Peak 1 | 10/06/2002 | 04/25/2003 | ML03121048 | <strong>Technical Specification Report for Steam Generators Meeting C-3 Category</strong><br /><i>Abstract:&nbsp;</i>Comanche Peak Steam Electric Station (CPSES) Unit 1 was taken off line on September 28, 2002 for the ninth refueling outage (1RF09). As part of the scheduled surveillance requirements of CPSES Technical Specification (TS) 5.5.9, analysis of eddy current plus point testing data on the Steam Generators (SGs) indicated that greater than 1 percent of the total tubes inspected in 3 of 4 SGs were defective. The majority of the tube defects are attributed to circumferential outside diameter stress corrosion cracking (ODSCC) at the hot leg top of tubesheet (TTS) transition. TXU Generation Company LP (TXU Energy) has plugged and/or sleeved the defective tubes identified during the current refueling outage. With the exception of one tube (which is discussed in the Safety Consequences and Implications below), all defective tubes met the criteria of NUREG 1022, Revision 2, for structural integrity. TXU Energy maintains a comprehensive program to identify SG tube degradation. All times in this report are approximate and Central Daylight Savings Time unless noted otherwise.
4452002003 | Comanche Peak 1 | 10/07/2002 | 01/16/2003 | ML03023045 | <strong>Auto Start of the CPSES Unit 1Train B Emergency Diesel Operator</strong><br /><i>Abstract:&nbsp;</i>On October 07, 2002, at 0936, during 345 KV switchyard east bus relay testing, an unexpected pickup of a relay contact occurred which generated a signal that caused the Unit 1 6.9 KV safeguards busses to transfer to the alternate power source. During the bus transfer to the alternate power supply, the Unit 1 train B emergency diesel generator (1-02) unexpectedly auto started. At the time, Unit 1 was in Mode 6 with the reactor cavity water level > 23 feet above the vessel flange and core off-load in progress. Refueling communications were lost as a result of the power interuption, core off load was suspended, and all switchyard work was halted. Non-safeguards plant power was restored at 1112 and core off-load resumed at 1319. Unit 2 remained at full power during this event and was unaffected. All times in this report are approximate and Central Daylight Time unless noted otherwise.
4452002004 | Comanche Peak 1 | 10/30/2002 | 12/30/2002 | ML03003072 | <strong>Two Pressurizer Safety Valves Found with Unsatisfactory Lift Setpoints</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2002, the Pressurizer Safety Valves (PSVs) were removed from the system and shipped off site to NWS Technologies for surveillance testing in support of the ninth refueling outage on Comanche Peak Unit 1. Testing was performed by the vendor using a procedure designed to comply with ASME/ANSI OM-1987 Part 1 and Westinghouse Owner's Group guidance, using saturated steam as the test medium. Two of the three PSVs failed their as-found lift tests with lift pressures below the Technical Specification (T/S) 3.4.10.1 setpoint of 2485 psig (plus or minus 1 % range). These failures resulted in the determination that two independent trains were inoperable in a single safety related system designed to mitigate the consequences of an accident. TXU Energy believes that this event was a result of setpoint drift of a magnitude within the design requirements of the valves. The valves were returned to operable status using normal rework for these components with no further actions planned.
4462002001 | Comanche Peak 2 | 06/06/2002 | 08/05/2002 | ML02226088 | <strong>Reactor Trip Due to Primary Water Pump Vibration High Signal</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2002, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, operating at 100 percent power. At 1924 hours, while Maintenance personnel were investigating a "Generator Electronic Protection Failure" alarm, a "Turbine Generator Channel 1 Primary Water Pump Vibration High" signal was received. This resulted in a Main Generator trip which caused a trip of the Unit 2 Main Turbine. The Unit 2 reactor automatically tripped on a "Turbine Trip >50% Power" signal. All control rods fully inserted, and all Auxiliary Feedwater pumps automatically started on Lo-Lo Steam Generator level as expected. TXU Generation Company LP (TXU Energy) believes that the event was caused by a Primary Water Pump Vibration Expansion Measuring cabinet circuit breaker failing open which caused a spurious "Turbine Generator Channel 1 Primary Water Pump Vibration High" signal. Corrective actions include replacement of the failed breaker, failure analysis on the failed breaker, and evaluation of potential circuit design changes or modifications. All times in this report are approximate and Central Daylight Standard Time unless noted otherwise.
4462002002 | Comanche Peak 2 | 06/19/2002 | 08/19/2002 | ML02240005 | <strong>Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2002, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1, Power Operation, operating at 99.5 percent power. At 1130 hours, during an investigation into a previously failed circuit card in the Engineered Safety Feature Actuation System, Engineering personnel discovered that a component on the card was not covered by an approved surveillance procedure. This constituted a missed Technical Specification surveillance. This condition applies to twelve Unit 2 Steam Generator Level Channel Operational Test procedures. TXU Generation Company LP (TXU Energy) believes that the cause of the event was less than adequate attention to detail on the part of the preparer and technical reviewer during revision of the Unit 2 Steam Generator level Channel Operational Test procedures following a design change to the circuitry. Corrective actions include procedure revisions, satisfactory performance of the Technical Specification surveillance tests, drawing reviews, and issuance of a Lessons Learned. All times in this report are approximate and reflect Central Daylight Standard Time unless noted otherwise.
4542002001 | Byron 1 | 03/08/2002 | 12/09/2005 | ML05349024 | <strong>Multiple Main Steam Safety Valve Relief Tests Exceeded Required Tolerance due to Disk to Nozzle Metallic Bonding and Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>During setpoint testing of the Unit 1 Main Steam Safety Valves (MSSVs) on March 7 and 8, 2002, three of the 20 MSSVs (i.e., 1MS014D, 1MS015C, and 1MS014C) failed to meet Technical Specification (TS) required lift setpoint tolerances. Operations personnel entered the applicable TS Action Condition until each valve was tested satisfactorily. Because the MSSVs were tested sequentially, only one valve was known to be inoperable at any one time. The cause of the 1MS014C and 1MS015C test failures is attributed to metallic bonding between the disk and the nozzle. This phenomenon is characterized by MSSVs experiencing a high initial lift setting followed by a significant drop in the lift setpoint, with no intervening adjustments. The 1MS015C had the new Inconel X-750 disk material, which is believed to be less susceptible to metallic bonding. The evaluation for this valve failure continues and a supplemental report will be issued. The cause of the third valve's test failure is attributed to setpoint drift. Corrective actions include replacing the 1MS014C and 1MS014D valves' disks with the X-750 Inconel material. An engineering analysis concluded that the design basis analyses bounded the out-of-tolerance MSSV condition. The condition of multiple MSSVs being outside of their required lift setting tolerance band is reportable in accordance with 10 CFR 50.73(a)(2)(i)(b),"Any operation or condition prohibited by the plants Technical Specifications." "Byron Station will continue to monitor the performance of the MSSVs through the 2004 and 2005 refuel outages and issue a supplemental report in late 2005.
4542002002 | Byron 1 | 03/18/2002 | 05/16/2002 | ML02141017 | <strong>Two of Three Pressurizer Safety Valve Relief Tests Exceeded Required Tolerance Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) 3.4.10, "Pressurizer Safety Valves," require three pressurizer safety valves to be operable with lift settings greater than or equal to 2460 psig and less than or equal to 2510 psig. TS Surveillance Requirement 3.4.10.1 requires each pressurizer safety valve to be lift-tested in accordance with the Inservice Testing (1ST) program. The TS acceptance criteria of the IST lift test is plus or minus 1% tolerance. Two pressurizer safety valves (i.e., 1 RY8010A and I RY8010B) were removed and tested during the recent Unit 1 refuel outage. The 1 RY8010B valve's "as-found" lift setting was +1.1%, and the 1 RY8010A valve was +2.0%. The valve Vendor reported this information to the Station's Inservice Testing Engineer who entered this condition into the station corrective action program. The cause for this concern is that the current TS requirement (SR 3.4.10.1) is too restrictive for the normal design performance of these valves and the lack of Station Management responsiveness in reconciling this discrepancy. Operable replacement valves were installed. Corrective action will be to pursue a relaxation of the 1% TS tolerance for the pressurizer safety valves lift setpoint. An engineering analysis on the effects of these valves lifting at the as-found setpoints concluded that all acceptance criteria in the Updated Final Safety Analysis Report Chapter 15 analyses are still met. This condition of multiple pressurizer safety valves being outside of their required lift setting tolerance band is reportable in accordance with 10 CFR 50.73 (a)(2)(i)(b), "Any operation or condition prohibited by the plant's Technical Specifications."
4542002003 | Byron 1 | 10/15/2002 | 12/13/2002 | ML02360029 | <strong>Two Automatic Reactor Trips Due to Reactor Coolant Overtemperature Conditions Caused by Digital Electrohydraulic Control System Circuit Card Failure Causing the Turbine Governor Valves to Close</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2002, at approximately 1217 hours, the Unit 1 reactor automatically tripped due to a Reactor Coolant (RC) over temperature condition. The immediate cause of the RC over temperature condition was the turbine governor valves closing causing a loss of turbine load. A malfunction in the Digital Electrohydraulic Control (DEHC) System was apparent, however thorough diagnostic testing could not 'identify any problems with the DEHC system. Four circuit cards with a high probability of causing this type of malfunction were replaced and the unit was restarted with additional monitoring equipment. On November 7, 2002 at approximately 1247 hours, the Unit 1 reactor again automatically tripped due to a RC over temperature condition. The investigation revealed a very similar scenario between the previous trip, and this trip. However, immediate indications and subsequent diagnostic testing of the DEHC system this time revealed a failure of the Bit Logic (BL3) circuit board in the DEHC computer. The cause of both reactor trips is attributed to this malfunctioning Bit Logic '(BL3) circuit board in the DEHC computer. The circuit board malfunction was intermittent in nature and could not be diagnosed for the first reactor trip. The failure of the board was due to a single chip, type SN74H60. The cause of the failure of the chip is not determined at this time. The DEHC system computer's BL3 card was replaced. Further analysis will be conducted on the failed chip to determine the cause of the failure. There were no safety consequences impacting plant or public safety as a result of these events. The unit is designed to cope with a loss of turbine load event. In both trips, the reactor trip system functioned as designed and shut down the reactor without incident. These events are reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(iv).
4562002001 | Braidwood 1 | 04/08/2002 | 06/07/2002 | ML02171007 | <strong>Setpoint Drift Causes Two of Three Pressurizer Safety Valve Lift Tests to Exceed Technical Specification Tolerance</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2002, Braidwood Station discovered that two of three pressurizer safety valves (PSVs) removed during refueling outage A1R09 and subsequently tested at an offsite facility, did not meet the Technical Specification (TS) acceptance criteria. TS 3.4.10, "Pressurizer Safety Valves," requires three pressurizer safety valves to be operable with lift settings greater than or equal to 2460 psig and less than or equal to 2510 psig. The surveillance requirement requires each valve to be operable in accordance with the Inservice Testing (IST) Program and that following testing the lift setting shall be within +/- 1 percent of the TS setpoint. One valve had a lift setpoint 1.1 percent high, the other was 1.4 percent low. There are no material condition issues with the PSVs that are contributing to the test failures. The PSVs are performing within their design capabilities. The test failures are mainly due to the close tolerance required by the current plant safety analysis and reflected in TSs and the inability of the valves to perform within that tolerance. Contributing to the valve test failures is lack of management responsiveness to reconcile continued PSV test failures. The corrective action is to investigate revising the safety analysis to support a relaxation of the 1 percent TS requirement for the PSV lift setpoint tolerance. An engineering analysis on the effects of the PSVs lifting outside of the TS tolerance concluded that all acceptance criteria in the Updated Final Safety Analysis Report Chapter 15, "Accident Analyses," were still met. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4562002002 | Braidwood 1 | 04/16/2002 | 09/27/2002 | ML02277057 | <strong>Failure of Pressurizer PORV Instrument Air Accumulator Check Valves to Isolate Caused by Improper Maintenance Procedures</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2002, Braidwood Station discovered that both trains of Unit 1 pressurizer power operated relief valves (PORV) instrument air accumulator check valves were likely incapable of isolating the instrument air (IA) accumulators from the IA supply header for operating cycle 9. The failure of the check valves to isolate IA would result in the PORVs being inoperable in the event of a loss of IA to the containment building. The root cause of the check valve failures was an incorrect link bushing gap that resulted in valve disc o-ring interference with the valve seat. This interference resulted in o-ring displacement from the disc o-ring grove, preventing proper closure of the check valve. The incorrect bushing gap was caused by not using the correct maintenance procedures in the past. Corrective actions to prevent recurrence are to (1) revise the work orders for the pressurizer PORV IA accumulator check valves to ensure the correct maintenance procedure is used for all maintenance on the check valves, (2) ensure the correct post maintenance testing is performed following maintenance activities on the check valves, and (3) revise the PORV testing surveillance to ensure that testing is performed only after all maintenance activities are complete. The simultaneous failure of both Unit 1 pressurizer PORVs caused by a loss of IA has been determined to be risk significant in accordance with the Significance Determination Process. \ This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4562002003 | Braidwood 1, Braidwood 2 | 09/11/2002 | 11/26/2003 | ML03336058 | <strong>Isolated Loop Reactor Coolant System Boron Sample Outside of Technical Specification Frequency Requirement Due to Misapplication of the Implementing Procedure</strong><br /><i>Abstract:&nbsp;</i>Braidwood Station Technical Specification (TS) Surveillance Requirement (SR) 3.4.18.2 requires the isolated loop Reactor Coolant System (RCS) boron concentration to be verified to be greater than or equal to the required shutdown margin (SDM) boron concentration of the unisolated portion of the RCS within 4 hours prior to unisolating the loop. Braidwood has not always been in literal compliance with the SR time requirement. During refueling outages, isolated loop boron concentration is determined from samples of the water used to fill the RCS loop. However, these samples were often collected and analyzed greater than 4 hours before the loop isolation valves were opened. The root cause of the TS SR noncompliance was a misapplication of a note that was added to the procedure that directs RCS loop restoration (BwOP RC-8). This procedure was relied upon as the implementing procedure to ensure the requirements of SR 3.4.18.2 were met. The SR was interpreted, in the context of the note, as being met when the RCS loop fill boron concentration was compared to the required SDM boron concentration within the SR time requirements before unisolating the isolated loop. The note was not properly reviewed in accordance with 10 CFR 50.59 to ensure literal compliance with the TS SR. This event is applicable to both Braidwood Units. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4572002001 | Braidwood 2 | 04/08/2002 | 06/07/2002 | ML02171022 | <strong>Multiple Test Failures ot Pressurizer Safety Valves and Failure to Report Those Failures Due to Management Weakness in Applying Reportability Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2002, Braidwood Station discovered that the failure of multiple pressurizer safety valves (PSVs) removed during Unit 2 refueling outages A2R07 and A2R08 and subsequently tested at an offsite facility, was not reported as required. In each of the outages, two of three PSVs failed to lift within the required Technical Specification (TS) setpoint when tested at an offsite test facility. TS 3.4.10, "Pressurizer Safety Valves," requires three pressurizer safety valves to be operable with lift settings greater than or equal to 2460 psig and less than or equal to 2510 psig. The surveillance requirement requires each valve to be operable in accordance with the Inservice Testing (IST) Program and that following testing the lift setting shall be within +/- 1 percent of the TS setpoint. There are no material condition issues with the PSVs that are contributing to the test failures. The PSVs are performing within their design capabilities. The test failures are mainly due to the close tolerance required by the current plant safety analysis and reflected in TSs and the inability of the valves to perform within that tolerance. The corrective action to prevent further test failures is to investigate relaxing the 1 percent TS requirement for the PSV lift setpoint tolerance. Identification and training of all personnel involved in the decision process for determining reportability is the corrective action to prevent future errors in reportability evaluation. An engineering analysis on the effects of the PSVs lifting outside of the TS tolerance concluded that all acceptance criteria in the Updated Final Safety Analysis Report Chapter 15, "Accident Analyses," were still met. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4582002001 | River Bend | 09/18/2002 | 11/18/2002 | ML02323033 | <strong>Automatic Reactor Scram Due to Main Turbine Electro-hydraulic-Control Malfunction</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2002, at 8:25 p.m., an automatic reactor scram occurred while the plant was operating at 100 percent power. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the reactor protection system and a manual actuation of the reactor core isolation cooling system. The sequence of events leading to the scram began with a voltage transient in the main turbine electro-hydraulic control system. This resulted in a "close" signal to the main turbine control valves, which caused reactor steam pressure to rise. The scram was initiated by a high neutron flux signal in the average power range monitors resulting from the rise in reactor steam pressure. Following the scram, a valve in the main condensate pump discharge header closed unexpectedly, shutting off flow to the reactor feedwater pumps. All three reactor feedwater pumps tripped in sequence due to low suction pressure, as designed. Operators initiated the reactor core isolation cooling system to provide makeup water to the reactor. This event is bounded by the analyses contained in the River Bend Updated Safety Analysis Report, and thus was of minimal significance with respect to the health and safety of the public.
4612002001 | Clinton 1 | 04/25/2002 | 06/23/2002 | ML02184002 | <strong>Lack of Barriers to Limit Impact of Grid Disturbance During Reverse Feed of New Main Power Transformers Results in Trip of Static VAR Compensators, Auto-start of Emergency Diesel Generator and Shutdown Service Water System Pump</strong><br /><i>Abstract:&nbsp;</i>A reverse feed was initiated through new Main Power Transformers (MPTs) to support removing the Reserve Auxiliary Transformer (RAT) power source for maintenance. A few seconds after closing the switchyard breaker, protective relaying for the Static VAR Compensators (SVC) actuated due to inrush harmonic currents that originated from the MPTs as a result of MPT energization. This tripped the RAT and Emergency Reserve Auxiliary Transformer (ERAT) SVCs to off. Without the SVC support, the ERAT output voltage dropped below the second level undervoltage setpoint, causing the Division 3 bus to transfer to the on-site source, resulting in an auto-start of the Division 3 Emergency Diesel Generator (DG). After the Division 3 DG re-energized the bus, the Div 3 essential Shutdown Service Water pump auto-started in response to a low system pressure signal. Operators entered the Off-Normal Procedure for Loss of AC Power, and suspended core alterations and movement of irradiated fuel assemblies. The causes of this event were the absence of barriers to limit the impact of the grid disturbance and the design review for the new MPTs did not identify the potential for grid disturbance impacts. The procedures for the reverse feed activity and the electrical review standard will be revised to prevent recurrence.
4612002002 | Clinton 1 | 05/13/2002 | 07/11/2002 | ML02205004 | <strong>Inadequate Preventive Maintenance Program for the Feedwater System Results in Lockup of a Turbine-Driven Reactor Feed Pump and Scram on High Reactor Pressure Vessel Water Level During Extended Power Uprate Testing</strong><br /><i>Abstract:&nbsp;</i>Extended Power Uprate testing was in progress with the 'A' Turbine-Driven Reactor Feed Pump (TDRFP) in manual on its flow controller and the 'B' TDRFP in automatic on the Startup Level Controller (SLC). When a planned reactor pressure vessel (RPV) water level increase from 32 to 38 inches was performed for startup testing using the SLC, water level increased but the Feedwater Level Control System (FLCS) did not adjust to stabilize water level. The operator took manual control of the SLC and lowered the demand signal to the 'B' TDRFP, but level continued to rise and an automatic reactor scram occurred on high RPV water level before insertion of a manual scram. The 'B' TDRFP did not respond to the lowered demand signal due to a lock-up of the TDRFP from mechanical binding. The cause of this event is an inadequate preventive maintenance program for the Feedwater System that did not identify the TDRFP limit switch guide as a critical component and establish appropriate preventive maintenance to prevent its failure. Corrective action includes developing a preventive maintenance task to inspect, clean and lubricate the limit switch guide mechanism periodically; replacing the 'B' TDRFP horizontal linkage rod, and reviewing the preventive maintenance program for the Feedwater System to assure critical components have adequate preventive maintenance tasks assigned.
4612002003 | Clinton 1 | 07/04/2002 | 08/28/2002 | ML02248034 | <strong>Manufacturing Process Deficiency in Main Power Transformer Sudden Pressure Relay Causes False Actuation of Relay Resulting in Generator and Turbine Trip and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On July 4 the sudden pressure alarm for the `B' Main Power Transformer (MPT) actuated in the Main Control Room and at the same time the reactor automatically scrammed from 95 percent reactor power. The sudden pressure alarm was initiated by a malfunction of the sudden pressure relay (SPR). The SPR initiated a Generator trip and lockout. The Generator trip caused a Main Turbine trip and Turbine Control Valve fast closure, resulting in the reactor scram. The SPR trip also initiated the `B' MPT deluge system, and the fire pumps automatically started as expected. Operators entered Emergency Operating Procedures due to an expected low reactor water level transient. The root cause for the reactor scram was a latent defect in the bimetal of the SPR control orifice that likely occurred during the manufacturing process and resulted in a false actuation of the SPR. Corrective action for this event includes replacing the deficient `B' MPT relay, testing the MPT SPRs for proper operation, and implementing a design change to modify the SPR trip logic.
4822002001 | Wolf Creek | 01/04/2002 | 03/25/2002 | ML02099012 | <strong>Voluntary Report of Emergency Diesel Generator Heat Exchanger Tube Degradation</strong><br /><i>Abstract:&nbsp;</i>This information is reported voluntarily appropriate to the guidance provided in NUREG 1022, "Event Reporting Guidelines 10 CFR 50.72 and 50.73," revision 2, section 2.7 "Voluntary Reporting." Heat exchanger tube degradation was identified on both of Wolf Creeks Generating Station's (WCGS) Emergency Diesel Generators (EDGs). WCGS initiated an investigation team to examine this issue. Although the team concluded the EDGs were operable at the time of discovery, heat exchangers on both EDGs were found to be in a degraded condition. Suspect tubes were plugged. The team determined that the Preventive Maintenance (PM) program in place during the mid1990s did not implement eddy current testing (ECT) to monitor structural integrity of EDG heat exchanger tubing. This condition monitoring is in addition to the thermal performance monitoring performed in response to NRC Generic Letter 89-13, "Service Water System Problems Affecting Safety-Related Equipment." Specific information is included with respect to ECT programs, including the identification and disposition of test data containing absolute drift indication (ADI), suspected dealloying (SDA), and tube pitting indications in admiralty brass heat exchanger tubes. Wolf Creek Nuclear Operating Corporation (WCNOC) believes this information may be of generic interest to the nuclear industry.
4822002002 | Wolf Creek | 04/25/2002 | 06/17/2002 | ML02177001 | <strong>Mode Change with RCS Unidentified Leakage Greater than Technical Specificaion 3.4.13</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2002, while in Mode 4, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel completed surveillance procedure STS BB-004, "RCS Water Inventory Balance." A calculational (rounding) error resulted in the conclusion that the Reactor Coolant System (RCS) (EIIS system code AB) unidentified leakage was within the Technical Specification (TS) limit of 1.0 gpm. The unidentified leakage was actually 1.091 gpm, or.091 gpm above the TS limit. On April 25, 2002, Wolf Creek Generating Station (WCGS) entered Mode 3 from Mode 4 contrary to TS Limiting Condition of Operation (LCO) 3.0.4. This specifies that the plant cannot change modes when an LCO is not met. The calculational error made in STS BB-004 was not recognized until after the mode change. When the error was recognized, TS 3.4.13, "RCS Operational LEAKAGE," Condition A, was entered. The source of the leakage was identified and corrected. On April 26, 2002, the leak rate was 0.31 gpm, and Condition B of TS 3.4.13 was exited. This event is reportable per 10 CFR 50.73(a)(2)(i)(B) as a violation of the plant's Technical Specifications. The root cause of this event was inadequate procedural guidance for performing RCS leakage calculations. No impact on personal, nuclear, or radiological safety resulted from this event.
4822002003 | Wolf Creek | 05/08/2002 | 06/28/2002 | ML02219041 | <strong>Reactor Protection System Actuation and Reactor Trip Due to Feedwater Regulating Valve Control Card Failure</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2002, at 5:07 p.m., Wolf Creek experienced an automatic actuation of the Reactor Protection System (RPS) including an automatic reactor trip due to low water level in the "D" steam generator (SG). This actuation occurred following the closure of the "D" SG main feedwater regulating valve (FRV) during surveillance testing. When the FRV closed, "D" SG level decreased below the reactor trip setpoint of 23.5 percent, initiating a reactor trip. The unit received a feedwater isolation and auxiliary feedwater actuation (both motor and turbine driven) because of the low-low SG levels. All control rods fully inserted, and the RPS and the Engineered Safety Features (ESF) Systems performed as expected. The cause of the FRV closure was the failure of a Westinghouse 7300-series manual controller card for the "D" SG FRV. The failed controller card was replaced. The safety significance of this event is low. This event is bounded by the current licensing basis analyses as reported in Wolf Creek Generating Station (WCGS) Updated Safety Analysis Report (USAR) section 15.2.7 "Loss of Normal Feedwater Flow." All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
4822002004 | Wolf Creek | 06/07/2002 | 10/17/2002 | ML02298003 | <strong>Cable Separation Issue That Could Potentially Affect Post-Fire Safe Shutdown Equipment Availability</strong><br /><i>Abstract:&nbsp;</i>At 0815 on June 7, 2002, the Wolf Creek Generating Station (WCGS) Shift Manager was notified of a postulated fire event that could cause a cable-to-cable hot short. If cable-to-cable hot shorts are assumed to occur, this event has the potential to cause water in the refueling water storage tank (RWST) to drain to the containment recirculation sump. It was discovered that the control cables for two redundant motor operated valves are routed in the same electrical raceway. The two valves are in the same electrical separation group, but are redundant in their function of conserving water inventory in the RWST. Further investigation determined that the control cables for motor operated valves in the opposite electrical separation group have the same configuration. The cause of this condition is that cable-to-cable interactions were not considered in the initial design of the plant. At 0945 on July 19, 2002, the Shift Manager was notified of conditions where a postulated fire event could lead to the loss of motor control centers that power post-fire safe shutdown equipment in both trains due to inadequate horizontal separation in conjunction with improper breaker coordination. At 1030 on August 20, 2002, conditions were discovered where a postulated fire could cause the loss of both centrifugal charging pump's (CCP) capability to successfully inject borated water into the reactor. The safety significance of these events is low.
4822002005 | Wolf Creek | 09/09/2002 | 10/24/2002 | ML02305007 | <strong>Engineered Safety Features Actuation Including Emergency Diesel Generator Start</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2002, at 3:58 p.m. Central Daylight Time (CDT), Wolf Creek Generating Station (WCGS) experienced a Degraded Voltage signal on Emergency Power Bus NB01 causing an automatic actuation of the "A" Emergency Diesel Generator ("A" EDG) and the associated Load Shedder and Emergency Load Sequencer (LSELS). The cause of the degraded voltage signal was determined to be due to a hardware failure in an electronic relay driver card in the LSELS degraded voltage circuitry. An actual degraded emergency bus voltage situation did not exist. The safety significance of this event is low. All safety related equipment responded to the actuation signal as expected. There were no adverse effects on the health and safety of the public.
4832002001 | Callaway | 12/03/2001 | 03/01/2002 | ML02072044 | <strong>Manual Auxiliary Feedwater Actuation and Subsequent Gas Binding of the "A" Motor Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On 12/3/01, a normal plant shutdown was being conducted to facilitate repairs to the Main Generator. After electrically unloading the Main Generator, high vibration occurred on the main turbine requiring breaking condenser vacuum to expedite stopping the main turbine. Both Motor Driven Auxiliary Feedwater (MDAFW) pumps were started prior to breaking vacuum. "B" MDAFW pump operated normally, but "A" MDAFW pump failed to develop sufficient pressure and flow. The Turbine Driven Auxiliary Feedwater (TDAFW) pump was placed in service to supply all Steam Generators. "A" and "B" MDAFW pumps were secured, and an investigation was begun to determine the problem with "A" MDAFW pump. The gas binding of "A" MDAFW pump was caused by a piece of foam from a floating cover inside the Condensate Storage Tank (CST), momentarily blocking the pump suction and creating a partial gas binding situation. On 1/31/02, Callaway Plant shutdown to facilitate removal of the CST floating cover. After the floating cover was removed, the CST was cleaned, inspected, and returned to service. All three AFW pumps, plus suction and discharge piping, were inspected. The high turbine vibration was due to a rapid cooldown of the main turbine, which affected internal component clearances. Procedures have been revised to provide additional guidance to maintain acceptable cooldown rates for the Main Turbine.
4832002002 | Callaway | 01/16/2002 | 03/15/2002 | ML02085060 | <strong>"A" Motor Driven Auxiliary Feedwater Pump Inoperable Due to Auxiliary Feedwater Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On 2/6/02, Callaway Engineering personnel completed final evaluation of a design calculation error associated with the Auxiliary Feedwater (AFW) system which impacted surveillance testing acceptance criteria. The design calculation error was made by Bechtel in 1984. This error resulted in a reduced operating margin between normal AFW Pump performance and Design Basis allowable acceptance criteria. A review of past pump performance data was conducted as part of a Past Operability review. The results of the review determined that the "A" Motor Driven Auxiliary Feedwater (MDAFW) pump did not meet the revised acceptance criteria five times within the last three years. Corrective actions include a review of other applicable design calculations provided by Bechtel and evaluation of methods to regain margin for the AFW pumps which include procedure revisions, revised valve positions, and possible rotating element replacement.
4832002003 | Callaway | 02/07/2002 | 04/02/2002 | ML02105034 | <strong>Auxiliary Feedwater Valve Inoperable Due to Faulty Electronic Circuit</strong><br /><i>Abstract:&nbsp;</i>On 2/6/02, with Callaway Plant in Mode 4, 0 percent reactor power, a Modification package was completed that reduced the flow control setpoints for Auxiliary Feedwater (AFW) flow control valves. This modification was implemented to reduce full flow on the Motor Driven Auxiliary Feedwater (MDAFW) pumps to prevent reaching run-out conditions. On 2/7/02, at approximately 0950, during the performance of a retest procedure to verify proper valve operation, AFW flow control valve, ALHV0011, failed to reduce and control flow at setpoint. Troubleshooting revealed a faulty electronic circuit card in the flow control circuit. After this card was replaced on 2/8/02, ALHV0011 performed satisfactorily. A review of past test data revealed that this problem first occurred on 5/15/01 during a retest on a different AFW flow control valve. ALHV0011 was not directly associated with the 5/15/01 retest document and the unsatisfactory data was not detected. This past unsatisfactory data indicated that ALHV0011, and thus "A" train of Auxiliary Feedwater, was inoperable from 5/15/01 until 2/1/02 when Callaway Plant entered Mode 4 and Auxiliary Feedwater was no longer required per Technical Specification 3.7.5.
4832002004 | Callaway | 02/13/2002 | 04/12/2002 | ML02114058 | <strong>Reactor Protection System Actuation While Performing Main Turbine Shell Warming in Mode 4</strong><br /><i>Abstract:&nbsp;</i>On 2/13/02, Callaway Plant was in Mode 4 with Reactor Coolant System (RCS) temperature at 300 degrees F and RCS pressure at approximately 395 psig. The Reactor Trip Breakers were closed, Main Turbine Shell warming was in progress, and Auxiliary Feedwater system testing was being conducted. At 0434, a Reactor Protection System (RPS) signal was generated that tripped open the Reactor Trip Breakers. Subsequent investigation revealed the trip was due to pressure in the Main Turbine increasing above an interlock setpoint of 56 psig (P-13), which is equivalent to 10 percent power. When this interlock was satisfied, it in turn enabled a Low Pressurizer Pressure Reactor Trip permissive (P-7) with a setpoint of RCS pressure less than 1885 psig. Since RCS pressure was approximately 395 psig, an RPS signal was generated to open the Reactor Trip Breakers. The cause of the event was operating procedures not clearly identifying plant conditions required to perform Main Turbine Shell Warming. Corrective actions taken were to revise plant procedures to reflect appropriate cautions and restrictions for performing Main Turbine Shell warming.
4832002005 | Callaway | 02/28/2002 | 04/12/2002 | ML02114057 | <strong>Inaccurate Steam Generator Low-Low Level Setpoints Due to Westinghouse Design Calculation Error</strong><br /><i>Abstract:&nbsp;</i>On 2/18/02, Callaway Plant received Westinghouse Letter SCP-02-14, which transmitted Nuclear Safety Advisory Letter (NSAL) 02-03. This NSAL addressed an error in the Westinghouse Steam Generator (S/G) water level setpoint analysis in which the pressure drop across a mid-deck plate internal to the S/G separator assembly was not accounted for in analysis calculations. This pressure drop adversely affected S/G low-low setpoint uncertainty calculations. On 2/28/02, Callaway staff engineers determined that this situation was applicable to Callaway with the S/G low-low setpoints being nonconservative and that the S/G Low-Low Trip function might not provide protection against a Main Feed Line Break (MFLB) inside Containment. A decision was made to reduce reactor power to approximately 30 percent and adjust the S/G Low-Low Trip setpoints to 21.6 percent narrow range level for normal containment environment and 27 percent narrow range level for adverse containment environment, which would satisfy the safety analysis requirements. Additional corrective actions included revision of plant procedures utilizing the S/G Low-Low Trip values.
4832002006 | Callaway | 06/07/2002 | 06/25/2004 | ML04183023 | <strong>Hot short issue reveals potential for draining RWST to Containment Sump</strong><br /><i>Abstract:&nbsp;</i>On 6/7/2002, Wolf Creek Nuclear Operating Corporation (WCNOC) contacted the Callaway Plant Fire Protection Engineer and informed the engineer of a potential hot short issue involving EJHV8811A, BNHV8812A, EJHV8811B, and BNHV8812B where it would be possible to drain the Refueling Water Storage Tank (RWST) to containment sumps if a fire were to occur in a location where the control circuit cables for these valves are run in the same electrical raceway. Callaway Engineering conducted extensive investigations and concluded that this was a credible threat. A GL 91-18 Operability Determination was performed, the on-shift Control Room Shift Supervisor was appraised of the situation, and hourly fire watches were instituted for the affected rooms. Long term corrective actions are under evaluation pending NRC endorsement of NEI guidance. Revision 1: Thus far, the NRC has not endorsed the NEI guidance for fire induced circuit failure issues. The NRC did issue RIS 2004-04 on March 2, 2004. This revision of the LER is in response to the NRC guidance documented in the RIS.
4832002007 | Callaway | 04/27/2002 | 05/23/2002 | ML02164012 | <strong>Violation of Site Security Plan due to Inclement Weather</strong><br /><i>Abstract:&nbsp;</i>On 04/27/02 at 2023 hours, the Shift Security Supervisor with the approval of the Operations Shift Supervisor directed Security Force Members to seek cover due to a tornado sighting/warning in Callaway County. Outside patrols and Operations Gate officers were directed to seek cover in alternate facilities. Security vehicles were arranged to prevent site access prior to leaving posts. Protected Area posts and controls were moved into safe buildings with their contingency gear. The fall back defensive strategy was maintained. No required compensatory posts were closed as a result of this event. At 2037, the danger was no longer present and operations were returned to normal. An Event Notification telephone call was made to the NRC Operations Center at 2105, 04/27/02 (EN# 38882).
4832002008 | Callaway | 04/18/2002 | 06/07/2002 | ML02170010 | <strong>Non-conservative Technical Specification Allowable Value for Main Steam Line Pressure Negative Rate</strong><br /><i>Abstract:&nbsp;</i>On 4/18/2002, during an extent of condition review concerning the neutron flux positive rate trip function, a concern was identified where Technical Specification (T/S) Table 3.3.2-1, Allowable Value for the Steam Line Pressure Negative Rate - High (HNPR), is less restrictive than the Safety Analyses Limit (SAL) credited in the Callaway Mode 3 Main Steam Line Break (MSLB) analysis. T/S lists the allowable value for the HNPR function as less than or equal to 124 psi. T/S Bases lists the Nominal Trip Setpoint (NTS) for the HNPR function as less than or equal to 100 psi. The Safety Analysis Limit (SAL) for the HNPR function is 100 psi. Consequently, the current T/S allows the HNPR function to be set at a value less conservative than the value assumed in the safety analysis. Corrective actions being evaluated include either decreasing the T/S Allowable Value from less than or equal to 124 psi to less than or equal to 100 psi, or revising the Callaway Mode 3 MSLB analysis to credit a HNPR SAL greater than or equal to 124 psi. Because the plant was operating in Mode 1, there were no immediate operability concerns. A Generic Letter 91-18 Operability Determination was completed which included the required compensatory actions for T/S compliance if the plant is taken to Mode 3 with reactor coolant system pressure below the P-11 setpoint of 1970 psig.
4832002010 | Callaway | 07/02/2002 | 08/30/2002 | ML02254024 | <strong>Potential for fire-induced common cause failure</strong><br /><i>Abstract:&nbsp;</i>On 6/25/02, with Callaway Plant in Mode 1 at 100 percent power, testing was being conducted involving "A" Train Ultimate Heat Sink (UHS) sump heater, SEF02A. When energized, the motor control center (MCC) feeder breaker, NG0705, tripped. Investigation revealed that SEF02A was grounded and that its feeder breaker protection was not properly coordinated with the MCC feeder breaker. The next closest breaker with ground fault protection was NG0705. An extent of condition review was completed that revealed a potential for safety related components and load centers to experience a common cause failure if a single fire were to occur in Auxiliary Building Fire Area A-1. MCC's NG01 A and NG02A could experience a fire induced ground fault condition due to cable damage on downstream loads, which could cause the loss of either, or both, NGO1A and NG02A. In addition, cables in Fire Area A-1 for "A" and "B" Residual Heat Removal pump room coolers have less than the required 20 feet of horizontal separation per FSAR Table 9.5E-1. Compensatory actions taken include establishment of hourly fire watches in affected areas, isolation of circuit breakers for UHS sump heaters pending completion of an electrical design change, issuing an Operations Night Order detailing actions to be taken to restore NG01A and/or NG02A in the event of a fire, and evaluating revisions to Fire Area Pre-plans.
4832002011 | Callaway | 11/05/2002 | 11/19/2002 | ML02331022 | <strong>"A" Steam Generator Tube Inspection Results Classified as C-3</strong><br /><i>Abstract:&nbsp;</i>At 1419 CST, 11/5/02, in Event Notification # 39345, Callaway reported the following: "During refueling outage RF12, interim results of "A" Steam Generator tube inspections indicate 62 tubes out of 5431 tubes (i.e., > 1%) have been found to be defective. This steam generator tube inspection result for the "A" Steam Generator is classified as category C-3 in accordance with Technical Specification 5.5.9, Table 5.5.9-2. All defective tubes will be plugged before the steam generator is returned to service. There were no adverse safety consequences or implications as a result of this event. This event did not adversely affect the safe operation of the plant or the health and safety of the public. " This initial notification was reported under 10CFR50.72(b)(3)(ii)(A) as a Degraded Condition, however, under NUREG 1022, section 3.2.4, discussion (A) 3, the present C-3 classification of the "A" Steam Generator (S/G) tubes does not meet the listed criteria for serious S/G tube degradation. The initial notification was amended to reflect that the report was made per requirements of Technical Specification (T/S) 5.5.9, Table 5.5.9-2 only. The C-3 condition does not meet the criteria for serious S/G tube degradation and is not a degraded or unanalyzed condition. This LER is submitted in compliance with T/S requirements, not due to an actual serious S/G tube degradation.
4832002013 | Callaway | 11/21/2002 | 01/17/2003 | ML03023072 | <strong>RPS actuation in Mode 4 while performing TADOT testing</strong><br /><i>Abstract:&nbsp;</i>At 2156, 11/21/02, with Callaway Plant in Mode 4 at zero percent power, an unplanned actuation of "B" Reactor (Rx) Trip Breaker occurred while performing plant procedure OSP-SB-0002B, Reactor Trip Breaker `B' TADOT (Trip Actuating Device Operational Test) - Shutdown. At step 6.4.9.2, the Solid State Protection System (SSPS) logic testing switch "A" was inadvertently mispositioned, which activated permissive P-10. This in turn activated permissive P-7, which enabled the Low Pressurizer Pressure Reactor Trip set at 1885 psig. With the Reactor Coolant System (RCS) at approximately 970 psig, a low pressure was sensed, processed by SSPS, and a trip signal sent which opened the "B" Rx Trip Breaker. Since the plant was already shutdown, no adverse consequences resulted. An Event Review Team (ERT) was convened to review the event. It was determined that the event was due to human error caused by over-rotating the SSPS logic switch. Proposed corrective actions include a procedure enhancement on test switch alignment and manipulations.
4832002014 | Callaway | 12/14/2002 | 02/12/2003 | ML03052005 | <strong>Reactor Trip While Removing "C" Condensate Pump from Service</strong><br /><i>Abstract:&nbsp;</i>At 0421, 12/14/2002, Callaway plant experienced an automatic reactor trip on Overtemperature delta T (OTDT). The trip occurred while reducing power from 100 percent power to approximately 80 percent at 1 percent per minute to secure "C" Condensate pump due to an oil leak. While reducing power, OTDT penalty, points accumulated due to: a) control rod insertion which caused Axial Flux Deviation to go further negative, b) an existing Axial Offset Deviation and c) a pre-existing conservative gain adjustment in the electronic circuitry for the OTDT trip function. Control rods were placed in automatic at the beginning of the down power evolution in accordance with plant procedures. The accumulation of penalty points culminated in a rod stop and turbine runback. Subsequently at approximately 83 percent power, the reactor tripped on OTDT. Initial plant response, including Auxiliary Feedwater actuation, was per design. The Turbine Driven Auxiliary Feedwater Pump (TDAFP) was secured but later received a start signal when two steam generator (S/G) levels decreased below the actuation setpoint, and experienced an overspeed condition. SIG levels were restored to normal using the motor driven auxiliary feed pumps. The plant was stabilized in Mode 3 at normal operating temperature and pressure. Emergency Notification System notifications were completed at 0811.
4982002001 | South Texas 1 | 02/26/2002 | 04/25/2002 | ML02122035 | <strong>Control Room Envelope Ventilation System Failed to Maintain a Positive Pressure in the Control Room</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2002 Unit 1 was operating in Mode 1 at 100% power. Unit 1 was in a "B" train extended allowed outage (EAOT) maintenance state. Instrument & Control maintenance personnel were performing a preventive maintenance task to replace backup power supply batteries in two plant fire detection panels for the Electrical Auxiliary Building (EAB). During the maintenance, at approximately 1030, a return air fire damper failed closed. This condition changed the air balance relationship between the EAB and the Control Room Envelope (CRE) ventilation systems. The CRE ventilation subsystem was unable to maintain the required positive differential pressure of at least 0.125 inches water gauge. Plant Operations personnel became aware of the change in differential pressure and initiated troubleshooting efforts to determine the cause. At approximately 1405 on February 26, engineering personnel informed the control room that the fire damper was tripped closed. Operations personnel did not believe that CRE ventilation system operability was affected. On February 27 a differential pressure test was performed on the CRE which identified the inability to meet the positive differential pressure of Technical Specification (TS) Surveillance requirements 4.7.7.e.3. The Shift Supervisor declared all three trains of CRE ventilation inoperable at 1035 and entered TS action 3.7.7.c. Following repairs to the fire damper, Control Room ventilation systems were declared operable at 2045 on February 27, 2002.
4982002002 | South Texas 1, South Texas 2 | 11/14/2002 | 01/10/2003 | ML03016017 | <strong>A Condition That Could Have Prevented the Fulfillment of a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2002, Unit 1 was operating at 100% reactor power and Unit 2 was defueled. Troubleshooting was in progress for a condition where the Unit 2 Electrical Auxiliary Building (EAB) supply fan 21C had tripped. It was determined that the fan motor breaker's Amptector longtime overload trip setting may have been set too low and could result in tripping of the fan motor during an off site degraded voltage condition. A subsequent investigation determined that the EAB HVAC supply fans in each unit would not have fulfilled their design safety function under specific analyzed conditions. The EAB Heating, Ventilation and Air Conditioning (HVAC) system's design safety function is to maintain ambient temperature conditions to provide operator comfort and to satisfy environmental requirements of safety equipment under normal operating, transient and postulated accident conditions. Each South Texas Project unit has three trains of EAB HVAC. The root cause of this event was setting the Amptector long time overcurrent setting at an amperage that did not allow sufficient margin for preventing inadvertent trips under all design voltage conditions. Corrective actions consisted of resetting the overcurrent setpoint to a higher value to meet fan motor design criteria under all analyzed conditions and verifying this condition was not generic to other breakers in the units.
4982002003 | South Texas 1 | 11/16/2002 | 01/15/2003 | ML11298A19 | <strong>Manual reactor trip due to apparent loss of Open Loop Coollng Water System Pressure</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2002 Unit 1 was operating at 100% power, at approximately 2036 the Unit 1 control room personnel received unexpected electrical system trouble alarms in the control room. Within several minutes Open Loop Cooling Water pump 12 tripped. The control room staff attempted to start Open Loop pump 13. Open Loop pump 13 did not start. The Reactor Operator (RO) noted that the Open Loop header pressure was approximately 30 to 40 psig and relatively stable. The yard watch operator that had been dispatched to the Circulating Water Intake Structure (CWIS) reported to the control room that the pump bay was filling with water and that it was believed to be coming from the Open Loop system header. While the off-normal procedure actions were being implemented for loss of Open Loop auxiliary cooling water, Open Loop header pressure indication in the control room dropped to zero psig. The Unit Supervisor directed the Unit 1 reactor be tripped manually and that Open Loop pump 11 be secured. Water level in the CWIS was observed to still be rising even after the last Open Loop pump was secured. Investigation revealed that the water was issuing from a large hole in the side of Circulating Water (CW) pump 11 casing. Circulating Water pump 11 was then secured. An Auxiliary Feedwater (AFW) actuation occurred approximately 25 seconds following the manual reactor trip due to Lo-Lo water level in the 2C Steam Generator. The AFW system operated and maintained water level in all four Steam Generators. All actuated safety related equipment operated as required.
4982002004 | South Texas 1 | 11/20/2002 | 01/27/2003 | ML03035000 | <strong>Steam Generator Power Operated Relief Valve Failed to Close on Demand</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2002, Unit 1 was in Mode 3 at 0% power. Unit 1 was being maintained in Mode 3 due to equipment failure in the Circulating Water system which required the main condenser to be taken out of service. The Steam Generator (SG) Power Operated Relief Valves (PORV) were being used to control decay heat removal from the primary plant. Plant operators attempted to close PORV 1B in manual control and the valve failed to close. Investigation revealed that the thermal overload on the breaker supplying power to the actuator hydraulic pump for the PORV 1B had tripped. The thermal overload was reset and PORV 1B fully closed. Due to obsolescence of various Class 1E Motor Control Center (MCC) sub-components, the Class 1E MCC buckets are being replaced with new buckets and sub-components. The MCC components for the PORV 1B were replaced in 2000 under the plant modification process. The replacement bucket for the PORV 1B contained a heater element rated at 114% of the motor's maximum operating current. The STP design requirement for this heater in this application is a rating between 125% and 140% of motor maximum operating current. Two PORV's in Unit 2 also had replacement buckets with heater elements undersized for this application. The breakers with under sized heater elements have been replaced. Additional training will be provided for engineering personnel on procurement practices.
4992002001 | South Texas 2 | 01/17/2001 | 04/10/2002 | ML02108036 | <strong>Gaseous Waste Processing System Oxygen Monitor Automatic Trip Inoperable</strong><br /><i>Abstract:&nbsp;</i>During a review of narrative logs maintained by Gaseous Waste Processing System (GWPS) operators, an incident was identified in Unit 2 where, on January 17, 2001, the GWPS Inlet Header Valve and Discharge Flow Valve control handswitches were left in the "OPEN" position for longer than four hours. This configuration made the automatic trip feature of the oxygen monitor for the GWPS inoperable. Technical Specification 314.3.3.11 states, "The explosive gas monitoring system instrumentation channels shown in Table 3.3-13 shall be OPERABLE with their Alarm/Trip Setpoints set to ensure that the limits of Specification 3.11.2.5 are not exceeded." Specification 3.11.2.5 limits the concentration of oxygen in the GWPS inlet to less than or equal to 3% by volume. The explosive gas monitoring instrumentation must be capable of performing Its function automatically to be considered operable. When the control handswitches for the inlet and discharge valves are in "OPEN'", the automatic trip function of the oxygen monitor is bypassed and the instrumentation should be declared inoperable. Four hour grab samples must be taken and the samples analyzed within the following four hours or the GWPS must shut down. No documentation could be found to show that the samples were taken or analyzed. The handswitches for the inlet and outlet control valves in this event were in the "OPEN" position for approximately 12 hours before being placed in the "NORMAL" position which restored the automatic trip function.
4992002002 | South Texas 2 | 06/14/2002 | 08/13/2002 | ML02232072 | <strong>Unit 2 Manual Reactor Trip Due to Unexpected Closure of Feedwater Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 14, 2002 Unit 2 was operating in Mode 1 at 100% power. At approximately 0435 Unit 2 lost feedwater flow to steam generator 2C during the performance of Feedwater Valve Operability Test. This test performs a partial stroke of the feedwater isolation valve from 100 percent open to 90 percent open. During the test the valve failed closed. After verifying there was no indication of feedwater flow to the 2C steam generator, the Unit Supervisor directed the Reactor Operator to manually trip the reactor. The reactor was in the tripped condition approximately 15 seconds following closure of the feedwater isolation valve (FWIV). The unexpected closure of the 2C feedwater isolation valve resulted from a blown fuse in the class-1E control circuit for the B-train safety solenoid for the 2C isolation valve. The blown fuse was the result of a shorted rectifier assembly used for surge suppression on the B-train safety solenoid for the 2C FWIV. This event resulted in no personnel injuries, offsite radiological releases or damage to important safety related equipment. Following the reactor trip, auxiliary feedwater automatically actuated as expected. There were no human performance issues or challenges to plant safety and the plant responded as expected.
4992002003 | South Texas 2 | 07/07/2002 | 08/01/2004 | ML04216001 | <strong>Automatic Reactor trip due to Main Turbine Trip caused by High Water Level in 2B Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2002 Unit 2 was operating in Mode 1 at 100% power. The Unit 2 main turbine generator tripped automatically due to a High-High level in the 2B steam generator (SG). The reactor tripped automatically as a result of the main turbine trip. The trips occurred shortly after the Channel II inverter and distribution panel de-energized. The loss of the distribution panel and inverter resulted in the loss of power to the instrumentation channels selected to control narrow range steam generator water level. This failure resulted in loss of SG level signal to all four SG Main Feedwater Regulating Valve (MFRV) control circuits because they were all selected to the same channel. This caused the MFRVs to go fully open. With the MFRVs fully open, water level increased in all four steam generators. Steam generator 2B reached its high-high level set point resulting in the main turbine trip and the feedwater isolation signal. The cause of the inverter failure and distribution panel loss of power was a change in breaker E2D11/3A characteristics. As the breaker has aged, the time differential between opening of the breaker contacts has increased. As a result, the contact opening has become more sequential and less simultaneous. The second cause of the reactor trip was having all four steam generator level control switches aligned to a single control channel coupled with the loss of power to instruments on that channel. Corrective actions include splitting the SG level channels to two separate control channels, revising a procedure to deselect the channel affected by the battery charger swap at the SG level controls and inverter replacement. Additionally, the installation and testing of suppression diodes to Class 1E battery charger relays was included. This event resulted in no personnel injuries, offsite radiological releases or damage to safety related equipment. There were no challenges to plant safety and the plant responded as expected.
4992002004 | South Texas 2 | 12/15/2002 | 07/01/2003 | ML03190005 | <strong>Turbine Blade Failure</strong><br /><i>Abstract:&nbsp;</i>At 1808 hours on December 15, 2002, Unit 2 was at 100% power when it was manually tripped due to excessive vibration in Low Pressure Turbine 22. Subsequent investigation identified that a blade had cracked and broken off and was ejected from the low pressure turbine into the condenser. Additional cracked blades were found in Low Pressure Turbines 22 and 23. The cause of the blade cracking was a design flaw with the rotor train (natural frequency modes near 120 Hz) and a faulty new generator rotor (differences between old and new rotor cause increased rotor train response). These flaws were not recognized by the vendor, Siemens-Westinghouse, due to errors in their modeling of the Turbine-Generator rotor system. Corrective actions include repairing the Unit 2 rotor system and damaged blades, installing vibration monitoring equipment, and evaluating the data taken during and after the Unit 2 restart. Subsequent studies confirmed that the corrective actions were effective in reducing torsional vibrations and the plant has operated continuously since March 2003. This event resulted in no personnel injuries, offsite radiological releases or damage to safety related equipment. There were no challenges to plant safety and the plant responded as expected.
5282002001 | Palo Verde 1 | 11/10/2002 | 01/07/2003 | ML03014038 | <strong>Reactor Trip due to Core Protection Calculators Generating a CEA Deviation Trip Signal</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2002 at approximately 2250 MST, Palo Verde Unit 1 was in Mode 1 (POWER OPERATION), operating at approximately 64 percent power when an automatic reactor trip occurred on low Departure from Nucleate Boiling Ratio (DNBR). The four Core Protection Calculators (CPC) generated a reactor trip on low DNBR due to the misalignment of a Control Element Assembly (CEA) from its subgroup. The misalignment occurred due to a failed optical isolation card in the control system for the CEA. The reactor was stabilized in Mode 3 (HOT STANDBY), and the Shift Manager classified the event as an uncomplicated reactor trip. No engineered safety feature actuations occurred during the event and none were required. The cause of the reactor trip was a hardware failure that caused a CEA position deviation. Based on the CEA deviation, a large penalty factor was generated in both control element assembly calculators (CEAC1 and CEAC2), that resulted in an automatic reactor trip to occur on low DNBR. In the past three years, there have been no previous similar events reported pursuant to 10CFR50.73.
5292002001 | Palo Verde 2 | 03/05/2002 | 05/01/2002 | ML02135023 | <strong>Main Steam Safety Valve As-Found Lift Pressures Outside of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2002, Unit 2 was in MODE 1, operating at approximately 100 percent power when augmented testing revealed that two main steam safety valves (MSSV) had an as-found lift pressure above the Technical Specification limit of +/- 3 percent of design lift pressure. These MSSVs are believed to have experienced setpoint drift. The valves were reset to +/- 3% of setpoint to maintain plant operability for the duration of the surveillance test clock. No attempt was made to reset the valves to +/-1 % of the required setpoint since both valves were scheduled for replacement. Previous similar events were reported in LER 50-529/2000-002.
5292002002 | Palo Verde 2 | 04/18/2002 | 06/17/2002 | ML02177035 | <strong>Post-test Constants Entered into Core Protection Calculator System</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2002 at 17:49 Mountain Standard Time, with Unit 2 in Mode 1, Reactor Engineering personnel detected that the unit was operated prior to test completion, with post-test instead of pre-test values for the Core Protection Calculator (CPC) DNBR and LPD uncertainty multipliers during post-outage power ascension testing. The error was caused by engineering personnel applying data elements from an incorrect location in a table. Post-testing values were applied instead of pre-testing values. Corrective action was taken immediately to correct the CPC constants. In addition, Units 1 and 3 were verified to have the correct constants installed. A previous similar event was reported in LER 50-530/2002-001.
5302002001 | Palo Verde 3 | 01/16/2002 | 03/13/2002 | ML02087048 | <strong>TS Violation Due to Incorrect Constant Entered in Core Operating Limit Supervisory System</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2002 at 1316 Mountain Standard Time, with Unit 3 operating in Mode 1, Power Operations, at approximately 99 percent power, reactor engineering personnel notified control room personnel that the core operating limit supervisory system (COLSS) had constants installed that were non-conservative. This error resulted in the COLSS power-operating limit for the departure from nucleate boiling ratio (DNBR) being non-conservative. The error was caused by engineering personnel applying an incorrect adjustment when performing a manual calculation to support cycle 10 operation following the unit's 9th refueling outage that was completed on November 5, 2001. Corrective action was taken to restore the COLSS constants. In addition, Units 1 and 2 were verified to have the correct constants installed. No previous similar events have been reported in the last three years.