## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192004001 | Oyster Creek | 05/17/2004 | 07/13/2004 | ML04202033 | <strong># 1 EDG Inoperable Caused by Cooling Fan Bearing Bolts Not Torqued Properly Following Preventative Maintenance</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2004 at 04:40, at the end of the bi-weekly #1 Emergency Diesel Generator (EDG) (EK - DG) load test an operator reported that the EDG was making an unusual noise and the cooling fan belts and pulleys were observed to be loose. It was also observed that the pillow-block bearing supporting the cooling fan drive shaft and sheave assembly had one bolt missing and one bolt loose. A 7-day Technical Specification LCO was entered at 05:00. The previous maintenance on the pillow block bearing support occurred about 17 days earlier during the two year overhaul completed in late April 2004. A review of the procedures and documentation that were used to perform the cooling fan maintenance and interviews with the individuals that performed the fan work during the overhaul were conducted. The investigation determined that the pillow block bearing hold down bolts had not been torqued as required by the vendor manual. All repairs were completed on May 17, 2004 at 17:12. Immediately following the repairs, #1 EDG Load Test was again performed as the cooling fan post-maintenance test and to validate operability. The diesel was declared operable at 20:25. No previous similar events of improper maintenance activities on the diesel generators leading to loose and missing bolts and fasteners due to improper torquing were identified.
2192004002 | Oyster Creek | 05/14/2004 | 12/12/2007 | ML07353113 | <strong>Change in the Methodology Used by General Electric and Global Nuclear Fuel to Demonstrate Compliance with Emergency Core Cooling System Performance Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2004, at approximately 0813 hours with the plant operating in the RUN Mode at 100% power, General Electric (GE) informed Oyster Creek Generating Station (OCGS) of a change in the calculation of Peak Cladding Temperature (PCT) and maximum local cladding oxidation. A new heat source has been postulated during the Loss of Coolant Accident (LOCA) event that involves the recombination of hydrogen and oxygen within the fuel bundles during core heatup. This event was initially reported to the NRC on May 14, 2004 in a voluntary notification as a result of the 10 CFR 50.46(a)(3)(ii) requirement to report this issue in accordance with 10 CFR50.72 and 10 CFR50.73. The cause of this event is that the potential oxygen source and subsequent heating effects of the hydrogen-oxygen recombination phenomenon were not properly considered during the original development of the LOCA evaluation methodology. An evaluation performed by GE based on a corrective action from Revision 0 of this LER has determined that there is sufficient conservatism in the Appendix K analysis such that it bounds the nominal Upper Bound PCT and maximum oxidation values (including the hydrogen-oxygen recombination phenomenon) at all exposures. Therefore, the original SAFER/CORCL application methodology for conformance of the Appendix K analysis 10 CFR50.46 limits remains applicable. The hydrogen-oxygen recombination phenomenon does not need to be considered in the Appendix K analysis. This evaluation applies to the normal inerted containment condition. As an Interim Corrective Action, an 8% Peak Linear Heat Generation Rate (PLHGR) reduction is applied when the containment is allowed to be deinerted above 25% power. This constraint is currently being maintained, however, based on the above GE analysis, this reduction may be reduced or, if further evaluations relative to the basis for deinerted operation allow, may be eliminated.
2192004003 | Oyster Creek | 05/27/2004 | 02/16/2005 | ML05061071 | <strong>Actuation of Reactor Protection System due to Spurious Hi-Hi Trip Signals on Intermediate Range Monitors Caused by Electromagnetic Interference</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2004, at 00:31 hours, with the Reactor Mode switch in the Startup position, a reactor scram from approximately 2% power was caused by a spurious actuation of Nuclear Instrumentation (NI) Intermediate Range Monitor (IRM) (EIIS-IG) channels 13, 14, and 18. The spurious actuation was caused by electromagnetic interference (EMI). The reactor shut down as designed. The safety significance of this event is considered minimal. The plant responded as designed for this type of event. Technical Specification limits were maintained. There was no radioactive release. All safety systems were fully operable. Off-site power was available. Operator performance was satisfactory. A Root Cause Analysis has been completed identifying the root cause of the EMI induced spiking of the IRM channels. IRM-13 & 14 were found to have loose cable connections at the drawer and nicks in the outer surface of the cable. This has been traced as the entry point of the noise intrusion and the reason the channels spiked. A coated surface on the circuit preamplifier box, on IRM-1 8, caused a poor connection to a common ground point and provided another entry point for noise intrusion. Connections were tightened, damaged cabling was repaired, and one IRM pre-amplifier was replaced.
2192004004 | Oyster Creek | 09/01/2004 | 10/01/2004 | ML04282023 | <strong>Operation in Excess of the Thermal Power Limit Due to Plant Computer Isolator Power Supply Degradation Affecting Input Values to the Heat Balance Calculation</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2004, at 13:50 (EDT), upon installation of a replacement Plant Computer System (PCS) (EIIS-ID) Isolator Power Supply (EIIS-RJX), the PCS Heat Balance indicated 1936 MWth, which exceeded the licensed maximum power limit of 1930 MWth. Initial results of the prompt investigation indicated that the power supply began to degrade on August 29, 2004. This degradation resulted in a slow lowering of indicated Control Rod Drive (CAD) (EIIS-AA) Flow, which provides input to the PCS Heat Balance calculation. Based on evaluations of the impact of the degradation, the 1930 MWth limit was exceeded on August 30, 2004 at 18:41. Power peaked at 1937 MWth, approximately 100.4%, on September 1, 2004. As a result, the thermal power limit was exceeded for greater than eight hours prior to recognition and actions taken to restore power below the license limit. The cause of this event was the slow degradation of the PCS isolator power supply, which resulted in a non-conservative heat balance calculation. All safety systems were fully operable and the safety significance of this event is considered minimal based on the small amount of deviation from the thermal power limit. There were no previous similar events of slowly degrading heat balance input parameters causing calculated core thermal power to lower resulting in operator actions to raise reactivity and consequently thermal power in advertently above the license limit.
2192004005 | Oyster Creek | 09/11/2004 | 11/10/2004 | ML04322008 | <strong>Main Steam Isolation Valve Failed to Close During Partial Valve Closure Surveillance Due to Mechanical Binding</strong><br /><i>Abstract:&nbsp;</i>On Saturday, September.11, 2004, with the plant in the Run Mode 100% power; the outboard Main Steam Isolation Valve (MSIV) NSO4 failed the 10% MSIV closure test. A 24 hour TSLCO was entered at 0930. To verify operability of the valve, plant power was reduced to 40% power and the MSIV full closure test was performed at 1747. This test also failed. At 1823 the inboard MSIV NSO3A was isolated and electronically locked in place due to the NSO4A being inoperable. With power maintained at approximately 40%, a complex troubleshooting plan was performed that concluded the valve was stuck open due to an internal problem. A plant shutdown was performed on September 14, 2004 to repair the MSIV. Internal inspection of the valve determined the failure of the poppet to close was caused by excessive rib and poppet guide wear resulting from poppet vibration induced by steam flow. All safety systems were fully operable and the safety significance of this event is considered minimal based on the demonstrated capability of the inboard MSIV NSO3A to fully close. No other MSIV failures caused by rib wear were identified. LER 88-013, occurred on July 9, 1988 when inboard MSIV IV (NS03A) failed the then quarterly full closure test due to stem failure caused by poppet vibration.
2192004006 | Oyster Creek | 11/05/2004 | 01/04/2005 | ML05012011 | <strong>Local Leak Rate Test Results in Excess of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On Friday, November 5, 2004, with the plant in Cold Shutdown for refueling outage 1R20, the as-found Leak Rate Test (LLRT) of Main Steam Isolation Valve (MSIV) NS04A failed to meet the acceptance criteria of Technical Specification 4.5.D.2. The acceptance criteria was revised just prior to 1R20 and is now less than or equal to 11.9 SCFH and the actual measured leakage was 24.3 SCFH at 20.6 psig. The valve was last refurbished during forced outage 1FO7 in September 2004 and found to be acceptable after maintenance that replaced the valve poppet. The valve was successfully repaired in 1R20 and subsequently passed the as-left LLRT. The apparent cause of the as-found LLRT failure in 1R20 was irregularity of the mating surfaces between the poppet seating surface and the valve body seating surfaces. Previous similar events of LLRT failures have occurred in each of the last two refueling outages: LER 2000-010, Local Leak Rate Test Results in Excess of Technical Specifications, NS04B LER 2002-002, Local Leak Rate Test Results in Excess of Technical Specifications, NS03A
2192004007 | Oyster Creek | 11/22/2004 | 01/21/2005 | ML05027051 | <strong>Automatic Containment Isolation Bypassed During Reactor Startup Due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2004 at 10:41 a.m. during startup operations following 1 R20 Refueling Outage, a reactor operator (RO) bypassed the automatic Containment Ventilation and Purge Isolation (EIIS-JM) function due to an incorrect step in the plant start-up procedure. The incorrect step had the wrong nomenclature and directed the RO to a key-locked bypass control switch (CFI-HS) only intended to be used in implementing Emergency Operating Procedure (EOP) actions. The procedure guidance was reviewed and determined to be incorrect and the bypass switch realigned to normal after 1 Hour 41Minutes. During the time that the switch was placed in bypass, the automatic isolation function of both V-27-1 and V-27-2 was bypassed and consequently the safety system function of these Primary Containment Isolation Valves to close and isolate in response to a LOCA signal was prevented. This condition is, by definition, a Safety System Functional Failure (SSFF) in accordance with NEI 99-02. The apparent cause of this event was an incorrectly worded step in the plant startup procedure. All other safety systems were fully operable and there were no circumstances that would have required automatic containment isolation while the function was bypassed. There were no previous similar events involving inadvertent bypassing of the containment isolation function due to inadequate procedures.
2202004001 | Nine Mile Point 1 | 05/02/2004 | 07/01/2004 | ML04195018 | <strong>Manual Reactor Scram and Cooldown Rate Exceeding Technical Specification Limits Due to Electromatic Relief Valve Failure to Close</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2004, at approximately 0209 hours, while conducting post-maintenance testing following plant startup, Electromatic Relief Valve (ERV) 123 would not reclose following remote manual actuation. Efforts to close the ERV failed and at 0217 hours the plant was manually scrammed. High Pressure Coolant Injection initiated on low Reactor Water Level due to the level transient associated with the scram as expected. Reactor cooldown rate exceeded Technical Specification limits for the first hour following the scram. An engineering evaluation concluded that 10 CFR 50 Appendix G requirements were not violated and that structural integrity of the Reactor Pressure Vessel (RPV) was not compromised. The root cause for the ERV failure to close was "inadequate use of procedures." The failure resulted from improper assembly of the pilot valve following maintenance. An extra gasket erroneously installed in the pilot valve assembly allowed bypass leakage around the pilot valve causing the main valve to remain open after the pilot valve was closed. The excessive cooldown rate resulted from the stuck open ERV, which limited the ability to control the rate of RPV depressurization and cooldown. The ERV was disassembled and reassembled correctly. Subsequent testing demonstrated satisfactory valve performance.
2202004002 | Nine Mile Point 1 | 05/14/2004 | 07/12/2004 | ML06214044 | <strong>Changes and Errors in the Methodology Used by General Electric and Global Nuclear Fuel to Demonstrate Compliance with Emergency Core Cooling System Performance Requirements</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2004, at approximately 0917 hours with the plant operating at 100% power, General Electric (GE) informed Nine Mile Point Nuclear Station, LLC, (NMPNS) of a change in the calculation of Peak Cladding Temperature (PCT) and maximum local cladding oxidation. A new heat source has been postulated during the Loss of Coolant Accident (LOCA) event which involves the recombination of hydrogen and oxygen within the fuel bundles during core heatup. Based on 10 CFR 50, Appendix K, inputs and assumptions, the additional heat generated resulted in an estimated 25 degree F increase in PCT and a 1.73% increase in maximum local oxidation. Consequently, the previous LOCA analysis was potentially non-conservative relative to PCT and maximum local cladding oxidation, and a conservative estimate of the calculated increase in local cladding oxidation exceeded the 17% limit of 10 CFR 50.46(b)(2) by 1.23%. This event was initially reported to the NRC on May 14, 2004 in an 8-hour non-emergency report in accordance with 10 CFR 50.46(a)(3)(ii) and 10 CFR 50.72(b)(3)(ii)(B). The cause of this event is that the heating effects of the hydrogen-oxygen recombination phenomenon were not properly considered during the original development of the LOCA evaluation methodology. Corrective actions include a 2% Maximum Average Planar Linear Heat Generation Rate (MAPLHGR) reduction, an 8% Peak Linear Heat Generation Rate (PLHGR) reduction when the containment is allowed to be deinerted above 25% power, and additional analyses to further evaluate the hydrogen-oxygen recombination phenomenon using more appropriate best-estimate/upper bound LOCA evaluation methodology. NMPNS will provide a supplement to this LER following completion of the evaluation if the results substantially alter the conclusions and/or corrective actions.
2202004003 | Nine Mile Point 1 | 02/25/2003 | 09/13/2004 | ML04268033 | <strong>Inadequate Environmental Qualification Barrier Considerations Resulting in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>This report identifies an historic condition which, upon later evaluation, was determined to constitute an event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. On February 25, 2003, with the plant operating at 100 percent power, several doors to the Nine Mile Point Unit 1(NMP1) Control Room and Auxiliary Control Room were breached (opened) for ventilation purposes while the Control Room Ventilation System was out of service for maintenance. Subsequently, questions were raised concerning the Environmental Qualification (EQ) implication of the open doors. Two of the doors (D107 and D109) are part of the boundary between EQ mild environment zones in the Control Room/Auxiliary Control Room and harsh environment zones in the Turbine Building during a postulated High Energy Line Break (HELB). Under certain HELB conditions, a mild environment could not be assured in the Control Room, placing the plant in an unanalyzed condition. The immediate cause of the event was procedural inadequacy in that NMP1 procedures did not include EQ implications in breach evaluations. Corrective actions included restoration of the EQ boundary and plant procedure revision to include EQ considerations in NMP1 breach permit evaluations.
2202004004 | Nine Mile Point 1 | 08/30/2004 | 10/29/2004 | ML04335013 | <strong>Manual Reactor Scram Due to Failure of #13 Feedwater Flow Control Valve Positioner</strong><br /><i>Abstract:&nbsp;</i>On August 30, 2004, at approximately 0825 hours, with the mode switch in "RUN" and reactor thermal power at approximately 100%, Nine Mile Point Unit 1 experienced feedwater flow oscillations. Efforts to manually stabilize feedwater flow were unsuccessful. At approximately 0833 hours, a manual scram was initiated to shutdown the plant. The feedwater flow oscillations were caused by degradation of the #13 feedwater flow control valve positioner due to a ruptured diaphragm in the output pilot valve. The root cause was determined to be the original design did not adequately establish a service life that took into account operating the positioner at the maximum recommended air supply pressure, thereby decreasing the service life below the established preventive maintenance frequency. The positioner, including the failed pneumatic module, for the #13 feedwater flow control valve was replaced. Subsequent testing demonstrated satisfactory flow control capabilities. To prevent recurrence, the positioner will be replaced every two years.
2372004001 | Dresden 2 | 04/12/2004 | 06/11/2004 | ML04173041 | <strong>Unit 2 High Pressure Coolant Injection System Inoperability Due To Lifted Leads</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2004, at 1810 hours (CDT), with Unit 2 at 100 percent power in Mode 1, Instrument Maintenance Technicians reported to plant operations personnel that High Pressure Coolant Injection System instrumentation leads were found lifted and taped. The disconnected instrumentation leads would have prevented the automatic realignment of the High Pressure Coolant Injection System pump suction from its non-safety related water source, the Condensate Storage Tanks, to its safety related water source, the Suppression Pool. The High Pressure Coolant Injection System was declared inoperable. The instrumentation leads were reconnected and the High Pressure Coolant Injection System was declared operable at 1853 hours (CDT) on April 12, 2004. The root cause of the High Pressure Coolant Injection System lifted and taped instrumentation leads was the failure of an Instrument Maintenance Supervisor to verify restoration of the leads when the surveillance was stopped. The corrective actions to prevent reoccurrence of the human performance error is to conduct four consecutive monthly reinforcements of management expectations with regards to procedures MA-AA-1000, "Conduct of Maintenance," Section 7, "Documentation of Work," and MA-DR-AD-6-00001, "Maintenance Shift Turnover Guidelines."
2372004002 | Dresden 2 | 04/24/2004 | 06/23/2004 | ML04182019 | <strong>Unit 2 SCRAM Due To Main Steam Isolation Valve Closure and Subsequent Inoperability Of The Isolation Condenser</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2004, at 0603 hours (CDT), with Unit 2 at approximately 20 percent power in Mode 1 and the Main Turbine Generator off-line in preparation for a scheduled maintenance outage, an automatic scram occurred due to closure of the Main Steam Isolation Valves. During the event, Main Steam Isolation Valve 2-203-2B closed slower than allowed by Technical Specifications. There were no Electromatic or Safety Relief valve actuations and no Emergency Core Cooling System initiations. Primary Containment Isolation System Group 2 and 3 isolations occurred as expected. All other systems responded to the automatic scram as expected. The Isolation Condenser System was used for primary system pressure control and operated as expected for approximately 5 hours. On April 24, 2004, at 1050 hours (CDT), with Unit 2 at zero percent power in Mode 3, the Isolation Condenser System was declared inoperable when valve 2-1301-3 could not be fully opened. The Reactor Water Cleanup System and Gland Seal System were subsequently used for pressure control. The root cause of the Main Steam Isolation Valve closure and resulting scram was attributed to inadequate drainage of the Main Steam Lead Drain System. The corrective action to prevent reoccurrence is to inspect for foreign material in the Main Steam Lead Drain System and clean as necessary. The root cause of the failure of Isolation Condenser valve 2-1301-3 to open was attributed to procedural inadequacy associated with setting the valve's Open Torque Switch Bypass. The corrective action to prevent reoccurrence was to revise the procedure for setting the valve's Open Torque Switch Bypass.
2372004003 | Dresden 2, Dresden 3 | 04/28/2004 | 06/28/2004 | ML04190038 | <strong>Units 2 and 3 Control Room Emergency Ventilation System Inoperable Due To Damper Failure To Close</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2004, with Unit 2 at 52 percent power in Mode 1, it was discovered during routine realignment of the Units 2 and 3 Control Room Heating, Ventilation and Air Conditioning System from Train A to Train B, that damper 2/3-5741-053B failed to close. The Control Room Emergency Ventilation System utilizes this Control Room Heating, Ventilation and Air Conditioning System damper and requires this damper to be capable of closure during a postulated Design Basis Accident. The Control Room Emergency Ventilation System was declared inoperable at 1209 hours (CDT). The root cause of the damper 2/3-5741-053B failure to close was determined to be inadequate instructions in procedure DOA 5750-01, "Ventilation System Failure," and no signoff for the pipe plugs in the Work Order. The corrective actions to prevent reoccurrence are to revise procedures DOA 5750-01 and MA-AA-716-010, "Maintenance Planning."
2372004004 | Dresden 2 | 04/28/2004 | 08/27/2004 | ML04247039 | <strong>Unit 2 Manual Scram Due To The Trip Of A Reactor Recirculation Pump</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2004, at 1536 hours (CDT), with Unit 2 at approximately 66 percent power in Mode 1, a manual scram was inserted by operations personnel due to the plant being in a region of the reactor's power to flow map that required an immediate scram. The power to flow condition was caused by the unexpected trip of the 2A Reactor Recirculation Pump and the manual scram was in accordance with immediate operator actions specified in procedure DOA 202.01,"Recirculation (RECIRC) Pump Trip - One Or Both Pumps." There were no Electromatic or Safety Relief valve actuations and no Emergency Core Cooling System initiations. Primary Containment Isolation System Group 2 and 3 isolations occurred as expected due to normal reactor water level decrease following the scram. All control rods fully inserted and all other systems responded to the manual scram as expected. The root cause of the trip of the 2A Reactor Recirculation pump and the manual scram was attributed to a lack of detailed rewinding and acceptance test requirements in the Exelon large motor standard that governed the rewind of the 2A Reactor Recirculation pump motor. The corrective action to prevent recurrence is to revise the Exelon Nuclear Engineering Standard NES-EIC-40.01, "Large Motor (>2 kv) Repair Requirements," to address the B-Stage rewind process to incorporate detailed B-Stage rewinding and acceptance-testing requirements similar to the requirements of the Vacuum Pressurization Impregnation Process used during the manufacturing of the original motor.
2372004005 | Dresden 2, Dresden 3 | 05/16/2004 | 08/30/2004 | ML04253009 | <strong>Units 2 and 3 Inoperable Turbine Condenser Vacuum - Low Switches</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2004, with Unit 2 at approximately 100 percent power in Mode 1, the 2A Turbine Condenser Vacuum - Low switch for the Reactor Protection System became inoperable due to the collection of water in its vacuum sensing line. The inoperable switch was not immediately detected and the condition existed for a period of time that exceeded the Completion Times associated with Required Actions of Technical Specification 3.3.1.1, "Reactor Protection System (RPS) Instrumentation." The root cause of the event was that previous efforts to correct the vacuum sensing line errors were too narrowly focused and did not inspect/repair all internal and external sensing lines to all turbine hoods. Temporary vent valves have been installed on Turbine Condenser Vacuum - Low switches 2A, 2C, 3A and 3C to continuously purge and clear condensation from the line. The corrective action to prevent recurrence is to perform internal and external condenser walk downs to determine Turbine Condenser Vacuum - Low switch sensing line slope and repair or modify as necessary.
2442004001 | Ginna | 07/22/2004 | 09/20/2004 | ML04272022 | <strong>Gaps in the Control Room Emergency Zone Boundary</strong><br /><i>Abstract:&nbsp;</i>During a control room emergency zone boundary inspection several gaps (totaling approximately 117.7 square inches) were discovered between the armor plate east wall and the control room floor. This exceeded the 5.25 square inch limit specified in Technical Specification (TS) 3.7.9 Bases, requiring Potassium Iodide (KI) to be credited as a compensatory measure until the gaps were sealed. Corrective action to prevent recurrence is outlined in Section V.B.
2442004002 | Ginna | 12/13/2004 | 02/03/2005 | ML05041029 | <strong>Consolidated Rod Storage Canister Placed in Incorrect Storage Location</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2004, at approximately 0900 EST, the plant was in Mode 1 at approximately 100% steady state reactor power. While preparing a core offload plan for the 2005 refueling outage, three consolidated rod storage canisters (C02, C07, and IC4) were found to have been classified according to Improved Technical Specifications (ITS) LCO 3.7.13 as category "A1" when they should have been classified as higher reactivity category "A2". One of the three canisters (IC4) was located face adjacent to two higher category "B" fuel assemblies (F44 and Z26). This condition is contrary to ITS section 4.3.1.1 (d) and ITS LCO 3.7.13. Actions were immediately initiated to return the storage of the fuel to an acceptable configuration. R.E. Ginna Nuclear Power Plant, LLC (Ginna LLC) believes that the cause of the event was related to the use of canister data in the computer database when contained assembly data should have been used.Corrective action to prevent recurrence is outlined in Section V.B.
2472004001 | Indian Point 2 | 09/01/2004 | 10/25/2004 | ML04308031 | <strong>Manual Reactor Trip Due to Oscillating Feedwater Flow and Steam Generator Level with Flow Perturbations Caused by a Degraded Feed Water Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2004, at approximately 0005 hours, Operations manually tripped the reactor as a result of oscillating Feedwater (FW) flow and 22 Steam Generator (SG) level with flow perturbations and FW pipe movement in the Auxiliary FW Pump Building. All control rods fully inserted and all primary systems functioned properly. The 22 FW flow control valve (FCV)-427 failed to fully close. Operators initiated 22 FW isolation by closing the 22 FW isolation valves. At 0021 hours, a 22 SG High-High level trip was actuated at 73% SG level initiating closure of the Main FW pump discharge valves and Main FW and Low Flow FW regulating and isolation valves. The plant was stabilized in hot standby with decay heat being removed by the main condenser. Off site power remained available and therefore the emergency diesel generators did not start. The Auxiliary FW (AFW) system automatically started as a result of a SG low level normally experienced on trips from full power. The cause of the event was a disengaged valve cage in FCV-427 from the valve body web. The cause of the valve cage loosening was improper installation in 1997 due to inadequate guidance in the maintenance procedure used to verify that the cage was fully seated and properly torqued into the valve body web. Significant corrective actions were inspection and repair of FCV-427 with revised guidance and revision of the valve maintenance procedure (AOV-B-012-A) to incorporate steps to verify that the cage is fully engaged and torqued into the valve body. The event had no effect on public health and safety.
2472004002 | Indian Point 2 | 09/24/2004 | 11/24/2004 | ML04335040 | <strong>Regulating Valve Closure Due to a De-energized Solenoid Operated Valve from Wiring Failure</strong><br /><i>Abstract:&nbsp;</i>On September 24, 2004, at approximately 11:55 hours, Operations manually tripped the reactor as a result of decreasing 23 Steam Generator (SG) level. Prior to the event Control Room(CR) operators observed decreasing 23 SG level and received an alarm for 23 SG level control deviation. CR operators attempted manual control of 23 FW regulating valve(FRV) FCV-437 without success in restoring SG level. The 23 SG level continued to decrease and as directed, the CR operator tripped the reactor at 15 percent SG level. All control rods fully inserted and all primary systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. Offsite power remained available therefore the emergency diesel generators did not start. The Auxiliary FW system automatically started as a result of a SG low level due to shrink effect. The cause of the event was de-energization of Solenoid Operated Valve (SOV)FCV-SOV-437-E due to disconnection of wiring to the SOV coil causing the SOV to fail open resulting in closure of 23 FW FCV-437. The failed connection was caused by the in correct orientation of the SOV due to a modification that lacked sufficient information due to a failure to follow the Planning and Engineering procedure for the modification and lack of a questioning attitude. Significant corrective actions were replacement of the FCV-437-SOV-E solenoid, inspection of remaining SOV connections and coaching on maintaining a questioning attitude. Planning and Engineering procedures are to be reviewed and revised as necessary. The event had no effect on public health and safety
2472004003 | Indian Point 2 | 10/20/2004 | 12/17/2004 | ML04358023 | <strong>Plant in a Condition Prohibited by Technical Specifications due to Error Making Gaseous Radiation Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2004, at approximately 1920 hours, Chemistry determined that the set point of vapor containment noble gas gaseous radiation monitor 42 (R-42) was not in compliance with the Technical Specification (TS) 3.3.6 allowable value (AV) of </= three (3) times background. The R-42 set point was not changed when implementing TS amendment 238 (conversion to TS based on NUREG 1431 and implementation of NRC Generic Letter 89-01, removing effluent regulation to the ODCM) on December 19, 2003. The R42 set point that was not changed was based on a calculation of the set point required to assure effluents were limited to less than 10 CFR 20 limits and has been consistently above the background by more than a factor of three. The event, the Project Team revising the TS and the TS section reviewer(s) not identifying the basis for the existing set point or that the operator aid containing the set point required a change to reflect the revised TS AV, was apparently caused by a process control inadequacy. Corrective action was taken to reset the R-42 set point to meet the TS AV with the term "background" synonymous with the monitor reading during periods of minimal or no primary leakage and to revise the set point in Operator Aid 2-OA-04-004. Additional corrective action will be taken to review radiation monitor requirements in TS, Technical Requirements Manual and Operational Dose Control Manual to verify that the proper set points / allowable values are incorporated. Action is also underway to formalize and improve the process for controlling radiation monitor set points. The event had no significant effect on public health and safety since the existing set point adequately isolated the required penetrations.
2472004004 | Indian Point 2 | 11/09/2004 | 01/06/2005 | ML05012013 | <strong>Emergency Diesel Generator Actuation from 480 VAC Safety Bus Undervoltage/Blackout Signal Due to Missing Tie Breaker Contact Fingers</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2004, two of three emergency diesel generators (EDG) actuated during are fueling outage planned evolution to tie 480 VAC safety bus 3A to 480 VAC safety Bus 6A. When the normal supply breaker to bus 6A was opened, an unexpected loss of power to 480 VAC safety bus 6A occurred. The de-energized bus 6A caused an undervoltage/blackout signal to be generated that automatically actuated 2 of 3 EDGs which started and powered their assigned safety buses (2A/3A, 5A). The EDG for bus 6A was out of service for planned maintenance and therefore remained de-energized. The 22 Residual Heat Removal (RHR) pump and 22 Spent Fuel Pool (SFP) pump were in service on bus 6A and were de-energized by the event. RHR cooling was restored in approximately 5 minutes and SFP cooling restored in approximately 39 minutes. All fuel assemblies were installed in the core but the reactor vessel head and upper internals were removed. Offsite power remained available. The cause of the event was missing primary disconnect contacts due to a failure to install them on bus tie breaker 52/3AT6A during preventive maintenance in March 2003 as a result of human performance (HP) error/inadequate work practices. Significant corrective actions included breaker removal, repair, reinstallation and testing; conducted a meeting with maintenance staff to review the event, discuss lessons learned and reinforce management's expectations on use of HP tools (i.e., self-checking, verification, questioning attitude, place keeping). Applicable procedures will be revised. The event had no effect on public health and safety.
2472004005 | Indian Point 2 | 11/26/2004 | 01/24/2005 | ML05033035 | <strong>Automatic Reactor Trip Due to Turbine Generator Trip Caused by Low Stator Cooling Water Pressure</strong><br /><i>Abstract:&nbsp;</i>An automatic Reactor Trip occurred on November 26, 2004, at 1322 hours, due to a Main Generator/Turbine trip as a result of low stator cooling water pressure from an erroneous low inlet pressure trip on the Main Generator Stator Cooling Water System (SCWS). All control rods fully inserted and all primary systems functioned properly. The Auxiliary Feed Water (AFW) system automatically started as a result of a Steam Generator low level due to shrink effect. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. Offside power remained available therefore the emergency diesel generators did not start. The cause of the event was an incorrect pressure washstand for the SCWS due to inadequate integrated system and post-work testing and setup of the system, inadequate operational procedure guidance for start-up/fill and venting of SCWS and inappropriately attempting to adjust SCWS control valve Y-63. Significant corrective actions included performance of a setup process of the SCWS in accordance with engineering's evaluation and recommendations including setting of the SCWS flow control valve Y-63 hot at 465 gpm (range 454-477) before plant re-start. An integrated SCWS post work test procedure will be prepared including complete development of I&C PM's for the post work test procedure, and improvements in operational procedure guidance. The event had no effect on public health and safety.
2492004001 | Dresden 3 | 01/24/2004 | 03/24/2004 | ML04096010 | <strong>Unit 3 Automatic Scram During Testing of the Main Turbine Master Trip Solenoid Valves</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2004, at 0037 hours (CST), with Unit 3 at 96 percent power in Mode 1, an automatic scram occurred while performing the weekly surveillance of the Main Turbine Master Trip Solenoid Valves. The surveillance testing was performed in accordance with procedure DOS 5600-02, "Periodic Main Turbine, EHC and Generator Tests." The event was caused by a malfunction of the Main Turbine Master Trip Solenoid Valves, which resulted in the depressurization of the Emergency Trip Supply hydraulic header and the resulting momentary closure of the Main Turbine Stop Valves below 90 percent full open. The Reactor Protection System actuated as a result of the Main Turbine Stop Valve position and, as designed, automatically scrammed the reactor. The plant responded as expected to the automatic scram. The root cause of the malfunction of the Main Turbine Master Trip Solenoid Valves was attributed to an improperly designed position switch rod and its associated housing by the Original Equipment Manufacturer, General Electric. The corrective actions to prevent reoccurrence are to replace the Main Turbine Master Trip Solenoid Valves with valves of a different design. The safety significance of this event was minimal. All control rods fully inserted and all systems responded as expected to the automatic scram. There were no subsequent major equipment malfunctions
2492004002 | Dresden 3, Dresden 2 | 01/30/2004 | 03/30/2004 | ML04097045 | <strong>Unit 3 Automatic Scram Due To Main Turbine Low Oil Pressure Trip and Subsequent Discovery of Inoperability of the Units 2 and 3 High Pressure Coolant Injection Systems</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2004, at 1155 hours (CST), with Unit 3 at 97 percent power in Mode 1, an automatic scram occurred due to a Main Turbine trip from low lube oil pressure. The event occurred during a swapping of lube oil coolers. After the scram, reactor water level increased above the Reactor Feed Pump High Level trip set point. Reactor water level was subsequently restored to normal and the Reactor Feed Pumps were restarted. On February 1, 2004, at 0400 hours (CST), subsequent investigations into the January 30, 2004, event determined that the High Pressure Coolant Injection Systems for Dresden Units 2 and 3 were inoperable. The inoperability was due to evaluations that determined that the Feedwater Level Control System would not maintain the post scram reactor water level below that which would prevent water from entering the High Pressure Coolant Injection System's turbine steam line. The root cause of the automatic scram was inadequate procedural guidance for the swapping of Main Turbine lube oil coolers. The root cause of the High Pressure Coolant Injection System inoperability was low margin in the Feedwater Level Control System to accommodate changes to the post-scram vessel level response. The corrective action to prevent reoccurrence of the scram is to modify procedure DOP 5100-04, "Turbine Oil Cooler Operation? The corrective action to prevent reoccurrence of the High Pressure Coolant Injection Systems inoperability is to modify the post-scram response of the Feedwater Level Control System.
2492004003 | Dresden 3, Dresden 2 | 05/05/2004 | 10/29/2004 | ML04314026 | <strong>Unit 3 Scram Due to Loss of Offsite Power and Subsequent Inoperability of the Standby Gas Treatment System for Units 2 and 3</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2004, at 1327 hours (CDT), with Unit 3 at 100 percent power in Mode 1, an automatic scram occurred due to a Main Generator Load Reject when a loss of offsite power occurred. The Emergency Diesel Generators automatically started and powered their respective electrical busses. All control rods fully inserted and Group I, II and III isolations occurred as expected. Operations personnel manually initiated the Isolation Condenser System for reactor pressure control, the High Pressure Coolant Injection System for reactor water level control, and the Low Pressure Coolant Injection System for Torus cooling. All systems initially responded to the scram as expected except the Standby Gas Treatment System was unable to maintain the Secondary Containment at the Technical Specification Surveillance Requirement limit of greater than or equal to 0.25 inches of vacuum water gauge. An Unusual Event for the loss of offsite power was declared at 1342 hours (CDT) and terminated at 1601 hours (CDT) on May 5, 2004. Additionally, during restoration of offsite electrical power to Bus 33, the Emergency Diesel Generator 2/3 output electrical breaker tripped. The root causes associated with the load reject and loss of offsite power and the low Secondary Containment vacuum were respectively, equipment failure in the "C" phase of the 345 kilovolt circuit breaker 8-15 and a degraded Secondary Containment boundary not detected due to an inadequate leak rate test procedure. The investigation into the apparent cause of the Emergency Diesel Generator output breaker trip was indeterminate.
2492004004 | Dresden 3 | 05/08/2004 | 07/07/2004 | ML04203031 | <strong>Unit 3 Shutdown Due To Inoperable Source Range Monitor</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2004, at 0450 hours (CDT), with Unit 3 subcritical during startup in Mode 2, Source Range Monitor (SRM) 24 was declared inoperable due to erratic indications. SRM 22 was already inoperable due to an inability to obtain "full in" indication of the detector in the reactor core region. This resulted in the plant being unable to meet the Technical Specification (TS) 3.3.1.2,"SRM (SRM) Instrumentation," requirement of 3 operable SRMs in Mode 2. All control rods were fully inserted in accordance with TS action requirements and the plant entered Mode 3. All systems responded as expected to the manual shutdown.
2492004005 | Dresden 3 | 09/29/2004 | 11/29/2004 | ML04253009 | <strong>Unit 3 Isolation Condenser Time Delay Relays Exceed Technical Specification Allowable Value</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2004, at 1235 hours (CDT), with Unit 3 at approximately 100 percent power in Mode 1, it was discovered that 3 of the 4 Unit 3 Isolation Condenser Time Delay Relays exceeded their Allowed Value specified in Technical Specification 3.3.5.2, "Isolation Condenser (IC) System Instrumentation." The event was discovered while performing Surveillance Procedure DIS 1300-08, "Sustained High Reactor Pressure Time Delay Relay Calibration." This event identified that two independent channels of the time delay portion of the Unit 3 Isolation Condenser Initiation Logic were inoperable and is being reported under 10 CFR 50.73(a)(2)(vii), "), "Any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system." Additionally, this event is being reported under 10 CFR 50.73(a)(2)(i)(B), "Operation or condition prohibited by Technical Specifications." The Isolation Condenser Time Delay Relays were previously calibrated on June 16, 2002 by using a stopwatch. The root cause of the event was due to an ineffective extent of condition review for a corrective action associated with a 1996 event in which stopwatches were determined to not be sensitive enough for calibration checks on components with limited margin. The corrective action to prevent recurrence was to use a strip chart recorder for calibrating the Isolation Condenser Time Delay Relays.
2492004006 | Dresden 3, Dresden 2 | 10/31/2004 | 01/19/2005 | ML05033047 | <strong>Units 2 and 3 Main Turbine Generator Rotor Cracks</strong><br /><i>Abstract:&nbsp;</i>Dresden Nuclear Power Station, Units 2 and 3, had been experiencing increasing trends in vibration levels on both Main Turbine Generators, bearings 9 and 10 since May 2004. Numerous efforts and reviews during the summer and fall of 2004 were not successful in resolving the vibration. Dresden Unit 3 entered a refueling outage in October 2004 and as part of the outage scope, the Main Turbine Generator was inspected. On October 31, 2004, the inspection identified that the Unit 3 Main Turbine Generator Rotor had a crack in the shaft near the rotor coupling. This finding resulted in the decision to remove Unit 2 from service and conduct an inspection of its rotor shaft. On November 1, 2004, a crack was identified on the Unit 2 rotor shaft. The Unit 2 crack was in the same general location and similar configuration as the Unit 3 crack. These events are being reported as a Voluntary Licensee Event Report in accordance with the guidance contained in NUREG 1022, Revision 2, "Event Reporting Guidelines 10 CFR 50.72 and 50.73." The root cause of these events was determined to be intermittent oscillating torsional loading on the generator rotor, which produced a torsional fatigue failure mode. The cause of the intermittent oscillating torsional loading is indeterminate. The cause and source of the intermittent oscillating torsional loading will be investigated through analytic modeling and data acquisition during plant operation.
2502004001 | Turkey Point 3, Turkey Point 4 | 01/26/2004 | 10/18/2004 | ML05083034 | <strong>EDGs Inoperable by Use of GTDs in Startup Transformer Breakers</strong><br /><i>Abstract:&nbsp;</i>Ground test devices (GTD), installed in the Unit 3 startup transformer breaker cubicles during startup transformer maintenance, would cause the Unit 3 emergency diesel generators (EDG) to respond to a loss of offsite power (LOOP) in droop mode instead of isochronous mode. In droop mode, EDG steady state output frequency would be less than that required by Technical Specification (TS) Surveillance Requirement (SR) 4.8.1.1.2; and, therefore, both Unit 3 EDGs are considered inoperable during startup transformer maintenance. It was also determined that, with a GTD installed in the A or B Intake Cooling Water (ICW) pump or the Component Cooling Water (CCW) pump switchgear cubicle, no ICW or CCW pump would be automatically loaded during sequencer loading onto the associated EDG under LOOP conditions. Therefore, the A or B ICW or CCW pump, with the GTD device installed in its associated cubicle, and the ICW or CCW pump on the swing D Bus switchgear, would both be considered inoperable.The cause of this event was due to a misunderstanding of the effect of the GTD used in the 4 kV cubicles on associated EDG and 4 kV switchgear control circuits, and a procedural deficiency that did not include this precaution. Procedures have been revised to install appropriate jumpers, when GTDs are installed in associated 4 kV cubicles, prior to the next maintenance or test.
2502004002 | Turkey Point 3 | 09/25/2004 | 11/19/2004 | ML04342021 | <strong>As-Found Cycle 20 Main Steam Safety Valve Setpoint Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2004, Turkey Point Unit 3 was in Mode 1 and holding at approximately 50 percent reactor power while performing Technical Specification surveillance testing of the Main Steam Safety Valves setpoints, just prior to the Unit 3 Cycle 21 Refueling Outage. The Unit 3 "B" Steam Generator (SG) MSSV, RV-3-1405, as-found lift pressure was 1136.1 psig, which was greater than the TS allowable setpoint pressure of ±3% of 1085 psig (1052.5 psig -1117.5 psig). RV-3-1405 was declared inoperable and the plant entered TS action statement 3.7.1.1.b. Reactor power was at 50%, which was below the 53% reactor power required per TS 3.7.1.1.b. The valve was subsequently adjusted and retested twice to within +/-1% of its required setpoint. The cause of the event was a slow build-up of corrosion between the ground ends of the spring and the spring washers. During the planned Unit 3 refueling shutdown which commenced on September 27, 2004, the valve was disassembled, and repaired. Operation of the facility with the Main Steam Safety Valves as-found settings was within analytical bounds; therefore, this event had no impact on the health and safety of the public.
2502004003 | Turkey Point 3, Turkey Point 4 | 10/08/2004 | 12/07/2004 | ML04350031 | <strong>Single Failure Vulnerability in Dousing Function Can Cause Emergency Containment Filters to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>During a Unit 3 clearance review, a single failure vulnerability was identified in the dousing function of the Emergency Containment Filters (ECF). The loss of power to certain power panel breakers could inadvertently douse all three ECFs for Unit 3. A similar condition applies to Unit 4. Three ECFs are provided in each reactor containment building to remove radioactive iodine so that offsite radiation dose is maintained within regulatory guideline values during a maximum hypothetical accident. The ECF system is required to perform its safety-related function of radioiodine removal, assuming a single active failure. The impact of the reduced capability of the doused ECF charcoal adsorbers to remove methyl iodide is an increase in offsite and control room dose to the thyroid. The increase in control room dose is greater than the increase in offsite dose; however, a realistic dose evaluation shows that the regulatory guideline value would not be exceeded in either case. The cause of the design deficiency is human error both in the original redesign of the dousing initiation system and in subsequent reviews of the single failure vulnerability. A modification to correct the design deficiency has been performed for both Units 3 and 4. Since no actual event occurred which relied on the ECFs to perform their safety function nor would the degraded performance of the ECFs result in doses above regulatory limits, it was concluded that the health and safety of the public were not affected by the ECF design deficiency.
2502004004 | Turkey Point 3 | 11/29/2004 | 01/27/2005 | ML05083034 | <strong>Plant Shutdowns Due to Drop of Shutdown Bank Rod E-11 During Low Power Physics Testing</strong><br /><i>Abstract:&nbsp;</i>At Turkey Point Unit 3, on November 29, 2004 at approximately 0009 hours, the reactor was manually tripped as a result of Shutdown Bank B rod E-11 dropping into the core during low power physics testing. After troubleshooting and recommencing low power physics testing, Shutdown Bank B rod E-11 again dropped into the core on November 30, 2004. The reactor was manually tripped at 0920 hours for this occurrence. In each event the dropped rod condition placed the unit in Technical Specification 3.0.3 requiring a shutdown. For each event the unit was subcritical in Mode 2 as a result of the dropped rod prior to the reactor trip. The apparent cause is attributed to an intermittent contact in a pin in the CRDM coil stack connector associated with rod E-11. A displaced pin in the connector caused the intermittent contact. The displaced pin was due to an inadequate vendor procedure that did not specify pin inspection prior to mating the connector halves, and cable routing that did not consider connector alignment, which complicated the mating process. The E-11 coil stack connector pushed pin was reseated, a bent pin aligned and the connector was properly mated. Vendor and plant procedures, used to mate the cable to the CRDM coil stack connectors (as well as the rod position indicator coil stack connectors), will be revised to help ensure proper connector mating. The dropped rod events did not compromise the health or safety of plant personnel or the general public and there was no increase in risk.
2502004005 | Turkey Point 3 | 12/03/2004 | 02/01/2005 | ML05046021 | <strong>Heat-Damaged Cables Cause Potential Inoperability of 2 of 3 Pressurizer Water Level Monitoring Channels</strong><br /><i>Abstract:&nbsp;</i>In response to a failed power operated relief valve pressure transmitter cable found during the Unit 3 Cycle 21 refueling outage, investigation revealed other degraded cables contained in conduits located above the reactor coolant system (RCS) hot legs. The degradation of cables associated with level transmitters LT-3-460 and LT-3-461, pressurizer level channels 2 and 3, respectively, would not have assured their ability to function after an accident. The cause of cable degradation is conduits/cables routed in close proximity to RCS hot leg piping with limited heat dissipation capability. This resulted in localized hot spots that subjected the cables to prolonged temperatures above the cable insulation design rating. Contributing factors include: gaps in RCS piping insulation; uninsulated RCS pipe stubs; the enclosed area (i.e., low ceiling) and a Normal Containment Cooling (NCC) ventilation register that was closed due to a broken linkage. Corrective action included 1) All degraded cables were removed and replaced with new cables. 2) Gaps and other deficiencies in piping insulation were repaired. 3) All NCC ventilation registers in the vicinity of the RCS hot and cold legs we reverified open prior to Unit 3's return to operation. 4) Temperature monitoring equipment was installed on conduits in close proximity above the RCS hot legs to record temperatures during the current operating cycle to establish the qualified life for the new cables. 5) The potential for cable degradation in the operating Unit 4 was evaluated to determine the impact on system and component operability. It was concluded that the health and safety of the public were not affected by the degraded cable condition.
2502004006 | Turkey Point 3 | 12/14/2004 | 02/10/2005 | ML05055005 | <strong>Manual Reactor Trip Due to Fire in the High Pressure Turbine Area</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2004, at 11:40 with Units 3 and 4 operating in Mode 1 at 100 percent power, a fire was reported at the North end of the Unit 3 High Pressure Turbine, beneath the turbine deck. At 11:45 Unit 3 was manually tripped due to the fire in the High Pressure Turbine area. The fire brigade responded and the fire was extinguished at 11:49. No damage to equipment or personal injury occurred and no Engineering Safety Feature Actuation was required as a result of the manual reactor trip. The fire was caused by the ignition of oil vapors generated by oil leaking from the number 2 bearing seal onto the High Pressure Turbine lower shell insulation. The cause of the seal oil leak was a result of poor workmanship performed during the spring 2003 refueling outage turbine seal overhaul. Specifically, the leaking oil was caused by improper bolting of the seal, inadequate gasket, inadequate sealing compound and shims introduced during the seal overhaul performed during the spring 2003 Unit 3 refueling outage. The Unit 3 turbine shaft seals were rebuilt, oil soaked insulation was removed, metal lagging added where necessary, and insulation replaced. The turbine fire did not affect any of the Unit 3 safety systems. All safety systems responded as designed; therefore, the health and safety of the public were not affected by the turbine fire and manual reactor trip.
2502004007 | Turkey Point 3 | 12/28/2004 | 06/30/2005 | ML05189006 | <strong>Manual Reactor Trip due to Main Generator Exciter Turbine Cooling Water Leak</strong><br /><i>Abstract:&nbsp;</i>On December 28, 2004 at 22:46 Turkey Point Unit 3 reactor was manually tripped from 70% power following a fast load reduction from 100%. The load reduction was initiated when it was recognized that the Turbine Plant Cooling Water (TPCW) leakage exceeded the makeup capability to the TPCW surge tank. The reactor trip was initiated following the discovery of water in the Turkey Point Unit 3 Main Generator exciter housing. The apparent cause of the exciter TPCW air cooler leak was found to be a failed gasket at the joint between the cooler channel head and the air cooler assembly. The root cause of the cooler failure is determined to be poor workmanship on the part of the refurbishment vendor along with inadequate technical guidance to the supplier for the repairs. Immediate corrective actions included the identification and repair of the TPCW leak source and drying of electrical components. Although parts of the 3B 4160 Volt safety related switchgear enclosure at the lower elevation were wetted due to water intrusion through the conduit penetrations in the overhead, the bus remained energized throughout the event. All plant parameters remained within the design envelope for this type of transient. All plant safety systems functioned as designed and there were no adverse effects on the operating crew's ability to safely shutdown the reactor and stabilize the plant. The health and safety of the public was not challenged nor adversely affected by this event.
2512004001 | Turkey Point 4 | 03/18/2004 | 05/14/2004 | ML04141006 | <strong>Inadequate Calibration Renders Radiation Process Effluent Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2004, an evaluation to address an NRC unresolved issue concluded that the method used to calibrate the plant vent gaseous effluent monitor [IL], R-14 was not in accordance with the Technical Specification (TS) and Offsite Dose Calculation Manual (ODCM) calibration requirements. Since the calibration is a condition of operability, R-14, was declared inoperable. The inoperability dates back to 1984 when the calibration requirements were revised via a License Amendment. Compensatory measures required by Technical Specifications and the ODCM were implemented. TS Table 3.3-4, item 2b, requires that either R-14 or the Plant Vent System Level Particulate, Iodine, and Noble Gas (SPING) Monitor [DET] be operable. TS Table 3.3-4 Action 28 requires that if neither R-14 or plant vent SPING are operable, then suspend operations in the Unit 4 Spent Fuel Pool (SFP) [ND] area involving spent fuel manipulations. On March 18, 2004, it was discovered that two irradiated fuel assemblies were moved on 10/21/03 from the Turkey Point Unit 4 SFP to the Reactor with the Plant Vent SPING out of service. Since R-14 was inoperable due to incorrect calibration and the Plant Vent SPING was inoperable due to obtaining a Tritium grab sample with spent fuel manipulations in progress, Action 28 of TS Table 3.3-4 was not met. Accordingly, this event is reportable per 10CFR50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." The cause of the event is not properly translating the TS calibration requirements into plant procedures. Corrective actions include instrument calibration, revision of calibration procedures, and enhancing TS License Amendment implementation process. The health and safety of the public was not affected by this event.
2512004002 | Turkey Point 4 | 05/14/2004 | 07/13/2004 | ML04202039 | <strong>Automatic Reactor Trip Due to Low Steam Generator Level and Steam/Feedwater Flow Mismatch</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2004, at about 1729 hours, an automatic reactor trip occurred from 100% reactor power after the 4A Steam Generator (S/G) Feedwater Flow Control Valve FCV-4-478 closed unexpectedly. This resulted in an automatic reactor trip actuated by steam flow/feedwater flow mismatch coincident with 4A S/G low-level. The Reactor Operator (RO) identified the condition causing the "S/G A Level Deviation" annunciation and placed FCV-4-478 In manual control. The RO then attempted to manually trip the reactor; however, the reactor automatic trip Initiated first. All three turbine driven auxiliary feedwater (AFW) pumps started as expected, supplying the S/Gs. The spurious closure of FCV-4-478 was caused by the failure of a capacitor in the Hagan feedwater flow controller, which caused the controller output to drive to zero closing the feedwater regulating valve. This caused the steam flow/feedwater flow mismatch coincident with the 4A steam generator low level. An Engineering Evaluation of the failed component determined that the capacitor failure mode was a short circuit and the capacitor was being utilized in a circuit for which it was exposed to an operating voltage above its ratings. The root cause of the event was inadequate implementation of a plant design change to eliminate an originally supplied undersized capacitor design. Immediate corrective actions included replacement of the Hagan Flow Controller FC-4-478 and the associated Hand/Auto Station FC-4-478F, followed by automatic transfer testing and Post Maintenance Testing. Controller power loss manual/auto fail-over tests were also successfully performed on FC-4-488 andFC-4-498 (in the other two control loops). Equipment operated as expected during the event and all parameters were within the envelope of the Updated Final Safety Analysis Report (UFSAR) analysis for Loss of Normal Feedwater. As a result, the event did not compromise the health and safety of the public.
2512004003 | Turkey Point 4 | 08/03/2004 | 10/15/2004 | ML04301023 | <strong>Oil Leak Causes High Head Safety Injection Pump to be Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>The outboard bearing oiler for high head safety injection (HHSI) pump 4B was found empty on August 3, 2004. Subsequent investigation determined that the previously identified minor outboard bearing oil leak experienced a step change in leak rate rendering the pump inoperable on or about June 6, 2004. Therefore, the 4B HHSI pump was unavailable for 60 days due to the oil leak, which exceeds the Technical Specification allowed outage time of 30 days. Any one of the three remaining HHSI pumps was capable of performing the intended HHSI safety function. The cause of the oil leak was due to human performance deficiencies during the last pump overhaul assembly of the bearing housing. A contributing cause was insufficient guidance in the maintenance procedure for bearing housing work. Plant procedures have been revised to provide additional guidance in performing HHSI pump bearing maintenance. All other plant safety-related pumps have been inspected to ensure that no other similar oil leakage conditions exist. Oil addition program enhancements and trend plan development guidance for oil leak monitoring have been developed under the corrective action program to address generic implications. It was concluded that the health and safety of the public were not affected by this event.
2512004004 | Turkey Point 4 | 12/25/2004 | 10/21/2005 | ML05318016 | <strong>Manual Reactor Trip due to Lowering Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On December 25, 2004, at 07:36 EST with Unit 4 operating in Mode 1 at 100 percent power, Turkey Point Unit 4 experienced a declining vacuum in the main condenser. When condenser vacuum reached less than 22 inches Hg, reactor trip criteria was met and the plant was manually shut down. Decay heat was removed via theAtmospheric Steam Dumps. The Auxiliary Feedwater System automatically started as expected. All rods inserted correctly and all systems functioned as designed. The apparent cause of the lowering condenser vacuum was failure of a turbine slop drain line inside the condenser. Corrective action was taken to temporarily plug the inlet and outlet ends of the leaking slop drain until the condenser could be accessed and permanent repairs completed during the 2005 Spring Refueling Outage. The apparent cause of the failed slop drain line was determined to be a poor bi-metallic weld coupled with a weak joint design and inadequate supports. Lab analysis of the failed bi-metallic weld indicated it failed in high cycle fatigue. Failure of both of the piping U-bolt supports allowed vibration to cycle the bi-metallic weld to the point of failure. The health and safety of the public were not affected by this event. Unit 3 is susceptible to the same failure; therefore, the slop drains have been plugged. They will have similar repairs in the next refueling outage.
2542004001 | Quad Cities 1 | 07/13/2004 | 09/10/2004 | ML04266012 | <strong>Technical Specifications Allowable Value Exceeded for Main Steam Flow Switches due to Inadequate Drift Allowance</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2004, during performance of the Unit 1 Main Steam Line (MSL) High Flow Switch Calibration and Functional Test, two main steam [SB] flow instruments [FS] were determined to have as-found setpoints that exceeded the Technical Specifications (TS) Allowable Value. The instruments were re-calibrated to be within the TS allowable range. A total of 16 switches, four per steam line, are installed on the Unit 1 main steam lines. The switches feed into the Primary Containment Isolation System [JM], with a “one out of two twice” logic. The root cause of this event is that inadequate drift allowance was used in the engineering setpoint calculations for the MSL flow switches in this application. The safety significance of this event was minimal. The instruments would have provided the trip signal within the analytical values assumed in the accident analysis. Corrective actions will include a revised drift analysis including a review of the current Allowable Value, Setpoint, Setting Tolerance, Expanded Tolerance and calibration frequencies as appropriate to improve margin to the Technical Specifications Allowable Value. Additionally, a previous event (LER 2-04-005) indicated our plans to replace the MSL instruments with an improved design.
2542004002 | Quad Cities 1 | 07/30/2004 | 09/28/2004 | ML04279048 | <strong>Technical Specification Allowable Value Exceeded for Low Pressure Coolant Injection Loop Select Reactor Low Pressure Switches 5 . EVENT DATE 6.on/x-</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2004, during performance of the Residual Heat Removal (RHR)/ Low Pressure Coolant Injection (LPCI) reactor low pressure calibration and functional test on the Unit 1 A loop, two switches were found outside of the technical specification allowable values. Each switch was adjusted to within the appropriate setting tolerances at the time of discovery. The root cause of this event was determined to be an unapproved/undocumented historic modification to remove one of the two internal micro-switches in each pressure switch some time prior to 1996. The safety significance of this event was minimal. Although the switches had drifted outside of the technical specification allowable value, they retained the capability of performing the safety function. The switches were recalibrated. Corrective actions include increased calibration frequency, replacement of the switches, and briefing of personnel concerning configuration control.
2542004003 | Quad Cities 1, Quad Cities 2 | 10/08/2004 | 12/06/2004 | ML04351017 | <strong>Control Room Emergency Ventilation Test Failure due to Deficient Modification to Hatch Covers</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2004, at 0300 hours, it was determined that the Control Room Emergency Ventilation System (CREVS) Test had not been performed correctly during the last performance, and TS Surveillance Requirement (SR) 3.0.3 was entered for a missed surveillance. At 2120 hours, the surveillance was performed and the pressure differential was determined to be less than required. The CREVS was declared inoperable, TS SR 3.0.3 was exited and TS Action 3.7.4.A was entered. At 2158 hours, an Emergency Notification System call was made in accordance with 10CFR50.72(b)(3)(v)(D) for loss of safety function of a single train system. The seals for two hatch covers were enhanced and the test was re-performed successfully. On October 9, 2004, at 0400 hours CREVS was declared operable. This event was caused by an inadequate review of a procedure change in 1998, and a deficient modification to the hatch covers in 1999. Corrective actions include enhancements to the seals and a procedure change to add flow criteria to the test procedure. The safety significance was minimal because CREVS does not impact reactor safety and the Control Room Emergency zone differential pressure was positive at all times.
2552004001 | Palisades | 08/31/2004 | 10/13/2004 | ML04301019 | <strong>Reactor Protection System and Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2004, at 0715 hours, the plant was operating at approximately 100% power. A rapid plant down power was commenced following report of a fire in the vicinity of the P-2B condensate pump lower motor bearing. At 0718 hours, the reactor was manually tripped from approximately 95% power, in conjunction with securing the P-2B condensate pump, and the imminent loss of main feedwater. Following the reactor trip, the auxiliary feedwater system started automatically to maintain steam generator water level. The plant was stabilized in Mode 3. Overheating, and ultimately fire, at the condensate pump lower motor bearing were caused by pump and motor misalignment following maintenance in July 2004. The pump and motor misalignment occurred as a result of inadequate maintenance instructions. Proper alignment criteria were established and incorporated into the work instruction when the repaired motor was reinstalled in September 2004. The safety significance of this event was minimal. All safety systems functioned as expected during the plant trip. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the reactor protection system and automatic actuation of the auxiliary feedwater system.
2552004003 | Palisades | 10/23/2004 | 04/19/2005 | ML05116023 | <strong>Main Steam Safety Valves Exceeded Lift Setpoint Acceptance Band</strong><br /><i>Abstract:&nbsp;</i>Testing of main steam safety valves revealed a total of 11 out of 24 unsatisfactory as-found lift pressure tests. All of the unsatisfactory as-found lift pressures were above the acceptance band. Technical Specification Limiting Condition For Operation (LCO) 3.7.1 requires a minimum of 23 out of 24 main steam safety valves to be operable in modes 1, 2 and 3. Since the cause of the multiple unsatisfactory as-found lift pressures may have arisen over a period of time, there is a likelihood that all of the required main steam safety valves were not operable during past plant operation. Therefore, this occurrence is considered reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The cause of the occurrence has been identified as a combination of disc/seat sticking and binding/bonding at the valve spindle guide bearing. Final lift pressures were established in accordance with requirements. A maintenance and testing plan has been developed to test the valves on a more frequent basis.
2602004001 | Browns Ferry 2 | 07/08/2004 | 09/07/2004 | ML04252021 | <strong>Reactor Scram from Sensed Power Load Unbalance Condition</strong><br /><i>Abstract:&nbsp;</i>While in steady state operation at 100% power, a Unit 2 main turbine trip/reactor scram occurred. All expected system responses were received, including the automatic opening of seven safety-relief valves. Electrical switching was in progress at the time of the scram, and during this switching activity the Unit 2 Unit Preferred System (UPS) 120 VAC Bus was inadvertently de-energized briefly. The reactor scram occurred at this time due to a turbine control valve fast closure/turbine trip condition. The loss of the UPS power would not by itself be expected to result in a turbine trip/reactor scram because of the fault-tolerant design of the main turbine electro-hydraulic control (EHC) system logic. However, it was determined that one of two main generator output current signal channels in the EHC logic had been automatically bypassed previously by the system software during a separate power supply transient on a different plant distribution bus. The subsequent temporary interruption of the UPS bus caused the loss of the second main generator output current signal channel, and the system logic indicated that a power-load unbalance (i.e., main generator load reject) condition existed. The event root cause was the procedure controlling the transfer of the UPS bus contained detail inadequate to prevent interaction between the alternate and normal supplies’ voltage control circuits. A contributing factor was an EHC system software configuration which gave the system an unrecognized single point scram vulnerability. Corrective actions include procedure revisions and improvement in the EHC logic alarm capability.
2602004002 | Browns Ferry 2 | 07/10/2004 | 09/07/2004 | ML04253008 | <strong>Automatic Reactor Scram During Startup Due To Spurious Upscale Trip On The Intermediate Range Monitors</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2004, at 2235 hours Central Daylight Time (CDT) Unit 2 received an automatic reactor scram from approximately one percent power due to an upscale trip on Intermediate Range Monitor (IRM) E (Reactor Protection System (RPS) channel A), IRMs F and H (RPS channel B). At the time of the reactor scram, the Reactor Mode Switch was in Startup and the IRMs were on ranges 6 and 7. IRM C was bypassed and was being withdrawn from the core in support of a maintenance activity to verify the correlation between ranges 6 and 7. After placing IRM C in the bypass mode the operator commenced withdrawing the detector with a series of bumps (starts and stops of the drive mechanism). The goal was to obtain a 60 percent scale reading on IRM C. The full reactor scram occurred on the third bump of the drive mechanism. All systems responded as designed and all control rods fully inserted. No Emergency Core Cooling System or Primary Containment Isolation System set-points were reached; therefore, no other system actuations took place. Immediately following the reactor scram the Mode Switch was placed in, Shutdown. The root cause of the upscale IRM trip was electrical noise generated by the movement of IRM C. This electrical noise caused voltage spikes on IRM E (RPS Channel A) and IRM F and H (RPS Channel B) that led to the subsequent reactor scram. Corrective actions include evaluation of the IRMs for possible upgrades to enhance noise isolation.
2602004003 | Browns Ferry 2 | 07/12/2004 | 01/24/2005 | ML05025003 | <strong>Inoperability of Turbine Control Valve Fast Closure Pressure Switches Beyond TS Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On Monday, July 12, 2004, Unit 2 was in power ascension following start-up from a scram which had occurred on July 8, 2004. The scram had occurred when the power-load unbalance (PLU) circuit of the main turbine electro-hydraulic control (EHC) system unexpectedly actuated during in-plant electrical switching. Engineering and 10 CFR 50.59 evaluations were completed to determine if reactor operation was acceptable with the PLU function disabled. The initial evaluations determined such operation was acceptable, and prior to reactor start-up the EHC PLU function was disabled via temporary modification. This modification was performed to eliminate the scram potential from the PLU circuit. Subsequently, the conclusions of the initial evaluations were found to be in error. After further consideration and discussions with General Electric, it was determined the temporary modification would be removed. On August 10, 2004, the temporary modification was removed to restore the EHC PLU function. The period of approximately 30 days between the Unit 2 reactor exceeding 30% power and the removal of the temporary modification exceeded the 4-hour out-of-service time allowed by the TS Table 3.3.1.1-1 for the turbine control valve fast closure pressure switch function. The root cause was that the BFN FSAR failed to include a description of the PLU function or its relationship to the transient analyses. The FSAR has been revised and personnel involved in 50.59 evaluations briefed.
2612004001 | Robinson 2 | 03/28/2004 | 05/26/2004 | ML04153008 | <strong>Both Trains of High Pressure Safety Injection Inoperable for Approximately 25 Minutes</strong><br /><i>Abstract:&nbsp;</i>At approximately 1343 hours on March 27, 2004, during a routine hand-rotation check of the "C" high pressure safety injection (HPSI) pump, it was discovered that the pump shaft was exhibiting some binding. At the time, the "C" HPSI pump was in service as the "B" Train HPSI pump. The "C" HPSI pump was declared inoperable and Condition A of Technical Specifications Limiting Condition for Operation (LCO) 3.5.2 was entered. This LCO Condition requires restoration of the inoperable HPSI train within 72 hours. At that time, the "B" HPSI pump was in service as the Train "A" HPSI pump. The "A" HPSI pump was out-of-service due to a previously discovered condition of minor flange leakage near two of the casing bolts. It was determined that the "A" pump could be restored to operable status and placed back in service to restore two trains of HPSI. In order to do so, the "B" HPSI pump was removed from service as the Train "A" pump and placed in service as the Train "B" pump. Therefore, at 1026 hours on March 28, 2004, for approximately 25 minutes, during the process of placing the "B" HPSI pump in service on Train "B," which was necessary to allow the "A" HPSI pump to be returned to service, there was no HPSI pump automatically available to provide HPSI to the Reactor Coolant System. The cause of the event was the sequence of mechanical equipment failures that necessitated the transfer of the "B" HPSI pump from Train "A" to Train "B." This condition is being reported in accordance with 50.73(a)(2)(ii)(B) and 50.73(a)(2)(v)(D).
2612004002 | Robinson 2 | 05/23/2004 | 07/21/2004 | ML04205020 | <strong>Entry into MODE 3 with the Steam Driven Auxiliary Feedwater Pump Flowpath Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1555 hours on May 23, 2004, during operations being conducted for restart of H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, the reactor operating MODE was changed from MODE 4 to MODE 3 with the Steam Driven Auxiliary Feedwater (AFW) pump flowpath not correctly aligned for operation, as required by Section 3.7.4 of the HBRSEP, Unit No. 2, Technical Specifications. Specifically, the suction valve (AFW-4) to the Steam Driven AFW pump was closed with a caution tag that stated the valve was to be maintained in the "closed" position. At 2139 hours, the caution tag was removed and the suction valve was opened. Opening the suction valve restored compliance with the Technical Specifications requirement in Section 3.7.4. as delineated in Surveillance Requirement 3.7.4.1, which requires each AFW valve in each water flowpath to be in the correct position. It was determined that the root cause of this situation was conflicting requirements. Corrective actions to revise the appropriate procedures are planned that will improve the procedural guidance and prevent recurrence of this situation. The health and safety of the public and plant personnel were not impacted by this event. The required safety functions were maintained, and the operating parameters of the plant were maintained within required safety limits. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's Technical Specifications.
2632004001 | Monticello | 07/21/2004 | 09/20/2004 | ML04264052 | <strong>Both Control Room Ventilation Trains Inoperable due to Failure of Seal on the In-Service Ventilation Train Compressor</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2004 while the "B" train of Control Room Ventilation was out-of-service for maintenance, the "A" train tripped due to a compressor seal failure. This rendered both trains of Control Room Ventilation inoperable. The 'B" train of Control Room Ventilation was restored to service within an hour. The "A" Train compressor seal was replaced on July 23, 2004 restoring both trains to operable status. The cause of the "A" Train seal failure was that the seal face cracked when the compressor started. In accordance with 10 CFR 50.72 (b)(3)(v)(D), "Event or Condition that could have Prevented Fulfillment of a Safety Function," an 8-hour event notification was made to the USNRC due to the loss of both trains of CRV, which are required to mitigate the consequences of an accident.
2632004002 | Monticello | 09/01/2004 | 11/01/2004 | ML04307013 | <strong>Cable Separation Issue Discovered During Appendix R Re-analysis</strong><br /><i>Abstract:&nbsp;</i>While operating at 100% power on September 1, 2004, during a reconstitution review of the Monticello10 CFR 50, Appendix R Safe Shutdown Analysis (SSDA) program, personnel discovered a non-conformance with 10 CFR 50, Appendix R, III.G.2 divisional separation criteria. Personnel determined the 4KV motor power cables for the Division I Residual Heat Removal (RHR) and Core Spray (CS) pumps pass through a Division II area without an adequate barrier. The Division I cables are physically located in a cable pull junction box (J113) in the Reactor Core Isolation Cooling (RCIC) room, which is designated as a Division II Fire Zone per the SSDA. As a result, an hourly fire watch was established in the RCIC Room, and an NRC notification was made in accordance with 10CFR50.72(b)(3)(ii)(B). The root cause of this failure to provide required cable separation was a failure by personnel to recognize the 10 CFR 50, Appendix R non-compliance during the original Safe Shutdown Analysis. Due to the age of the non-conformance (1983) and the unavailability of personnel involved in the original SSDA development to interview, the station was unable to obtain any additional factual insights regarding the cause of the non-conformance. NMC has initiated a modification to restore compliance with 10 CFR 50, Appendix R, Section III.G.2. This modification will provide a 3-hour fire rated barrier for the Division I RHR and CS cables located within pull box J113.
2632004003 | Monticello | 12/15/2004 | 02/14/2005 | ML05045046 | <strong>High Pressure Coolant Injection System Declared Inoperable due to Loose Oil Plug</strong><br /><i>Abstract:&nbsp;</i>On 12/14/2004, the lube oil plug on the High Pressure Coolant Injection (HPCI) Turbine Booster Pump had been removed to take an oil sample and replaced. The turbine was then operated to perform vibration analysis. Later on 12/14/2004, a Monticello Nuclear Generating Plant operator found a small amount of oil under the oil plug on the High Pressure Coolant Injection (HPCI) Turbine Booster Pump and the oil plug was identified as being loose. The plug was immediately tightened and oil level verified. At 1300 on 12/15/2004, based on the evaluation by Operations that the HPCI plug could have backed further out during extended operation, and caused the HPCI system to be unable to fulfill its safety function, an Event Notification was made to the NRC for the event. The root cause of the loose drain plug is the lack of programmatic controls to ensure the minimum required tightness is applied during reinstallation of the drain plugs after sampling or changing oil. The current practice was to allow oil drain plugs to be installed as a skill of the craft activity by Operations personnel. Operations personnel had not been sufficiently trained on this skill area. The small tool used, and the height of the plug (71 inches) also contributed to the event. NMC has initiated corrective actions to ensure that oil drain plugs are sufficiently tightened following oil-sampling activities.
2652004001 | Quad Cities 2, Quad Cities 1 | 01/18/2004 | 03/29/2004 | ML04097046 | <strong>Drywell High Radiation Monitor Failure due to Unsoldered Wiring Connection</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2004, it was determined during troubleshooting that a wire on the selector switch for the Unit 2 "A" drywell (DW) radiation monitor was crimped back on itself at a connection point but was not soldered. This instrument provides post-accident indication as well as an isolation of Primary Containment (Group II isolation) in response to high radiation levels in the drywell. The troubleshooting was being performed in response to a drop in the indicated value on January 18, 2004, from 3R/hr to 1R/hr. It was determined that the chassis was manufactured with an unsoldered switch connection, and that this connection made intermittent contact. In the event of a gross failure of the fuel cladding, the discontinuity may have prevented a containment isolation initiation during a DW high radiation condition. However, high DW pressure and low reactor water level instrumentation would have initiated a Group II isolation in the event of a break in the reactor coolant pressure boundary inside containment. The DW radiation monitors on Unit 1 and Unit 2 were checked and no additional loose or unsoldered connections were identified.
2652004002 | Quad Cities 2 | 03/09/2004 | 05/10/2004 | ML04139052 | <strong>Axial Flaws Detected in Recirculation Piping During Inservice Inspection</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2004, during a refueling outage on Unit 2, axial flaws were detected during a scheduled Inservice Inspection (ISI) of a recirculation system weld (02B-S7). Although the axial indications could not be fully characterized using qualified Performance Demonstration Initiative inspection techniques, the flaw sizes were estimated to be approximately 0.35 and 0.25 inches long and approximately 0.39 inches deep (not through-wall).The axially oriented intergranular stress corrosion cracking (IGSCC) flaws were most likely detected as a result of the decontamination process increasing there flectivity of the pre-existing flaws. IGSCC mitigation efforts such as hydrogen water chemistry, noble metals chemical addition and mechanical stress improvement process had previously been applied to this weld, and the probability that cracking occurred following these mitigation efforts is low. It is most likely that the flaws were present but not previously detected. An overlay was applied to weld 02B-S7 in accordance with industry guidance, and the other four Unit 2 Category D welds were inspected with no additional flaws identified.
2652004003 | Quad Cities 2 | 03/30/2004 | 05/28/2004 | ML04162034 | <strong>Unit Trip from Turbine Trip During Thrust Bearing Wear Detector Testing</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2004, at 0740 hours, during testing of the Thrust Bearing Wear Detector (TBWD), the main turbine tripped and a Reactor Protection System trip signal was received from the closure of the main turbine stop valves. All control rods fully inserted, and the unit was taken to shutdown. The cause of this event was the inappropriate use of a surveillance procedure with a known single-point vulnerability, in lieu of a calibration procedure. This was caused by an implementation practice that did not require performance of all three TBWD calibration procedures following turbine maintenance. The safety significance of this event was minimal. All plant systems operated as designed to shut the unit down. Corrective actions include the revision of the operations turbine test of the TBWD to provide a positive means of inhibiting a turbine trip during TBWD testing, a review of the implementation of Instrument Maintenance procedures for other situations in which the procedures are used interactively with procedures from another department, and the revision of the work frequency codes that determine when the local adjustment procedures are performed such that the procedures are appropriately performed at the end of an outage.
2652004004 | Quad Cities 2 | 04/19/2005 | 07/25/2005 | ML05214041 | <strong>Main Steam Safety/Relief Valve As-Found Setpoint Outside of Technical Specification Allowed Value Due to Pressure Adjusting Spring Tolerances, Pressure Cap Material and Vibration</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2004, during as-found testing of the Unit 2 Main Steam Safety Relief Valve (S/RV), it was identified that the S/RV had an as-found pressure setpoint 6.8% above nameplate, which exceeded the Technical Specification allowed value (nameplate+/- 1%) and the ASME Code requirements (nameplate +/- 3%). During disassembly of the pilot stages of the valve, a 0.008" groove in the bellows cap assembly was identified. The root cause of the S/RV degraded condition is insufficient pressure adjusting spring tolerance specifications in combination with the use of a bellows cap material that did not have sufficient hardness. Original corrective actions included further vibration testing. As a result of the vibration testing, the S/RVs were replaced with S/RVs with improved subcomponents. The Appendix R event, Anticipated Transient Without Scram (ATWS), ASME overpressure and fuel thermal analyses applicable to Unit 2 Cycle 17 were re-evaluated as satisfactory using as-found safety valve data.
2662004001 | Point Beach 1 | 05/06/2004 | 06/25/2004 | ML05087017 | <strong>Reactor Vessel Upper Head CRDM Penetration 26 Flaw Indication</strong><br /><i>Abstract:&nbsp;</i>During the performance of non-destructive examinations (NDE) of the Point Beach Nuclear Plant (PBNP) Unit 1 reactor pressure vessel head as required by the First Revised NRC Order (EA-03-009), possible flaw indications were observed using ultrasonic testing (UT) techniques in the "J" groove weld area for CRDM head penetration 26. To further characterize these indications, multiple dye penetrant (PT) examinations of the penetration 26 J groove weld area were performed, including PT testing following minor excavation of the weld surface. The results of these examinations confirmed the existence of flaws in the "J" groove weld. On May 6, 2004, based upon preliminary analyses, NMC determined that these indications would probably not be found acceptable under ASME Code standards. Therefore, this condition was reported under 10 CFR 50.72(b)(3)(ii)(A) as a significant degradation of a principal safety barrier. Research on the observed UT indications concluded that the indications were likely the result of weld repairs during fabrication and were not related to primary water stress corrosion cracking. A weld repair of the penetration 26 CRDM nozzle was completed on May 22, 2004, in accordance with an approved plant modification. The safety significance of this condition was minimal. PBNP Unit 1 was returned to service following the U1R28 refueling outage on June 8, 2004.
2692004001 | Oconee 1 | 01/08/2004 | 03/08/2004 | ML04076083 | <strong>Unit Shutdown due to Reactor Coolant Leak Above Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On 1/8/2004 Oconee Unit 1 was at approximately 26% RTP, with an increasing leak rate trend from an unidentified location in the Reactor Coolant System (RCS). At 1312 hours a power reduction was initiated to reduce dose inside containment to facilitate a search for the leak source. At 1502 hours, Operations personnel conservatively estimated the leakage to be approximately one gpm. Technical Specification (TS) 3.4.13 Condition A was entered. At 1902 hours Operations personnel declared Unit 1 in TS 3.4.13 Condition B, which required that the unit be placed in Mode 3 within 12 hours. At 1912 hours an ENS notification was made per 10CFR 50.72 (b)(2) for initiation of a TS required shutdown. The NRC assigned event number 40433. At 1925 hours Operators completed the shutdown by entering Mode 3. The leak was subsequently identified as a crack in 3/8 inch diameter tubing at a fitting on a Reactor Vessel Level Instrument line. The cracked section was cut out and a new fitting installed. A cause evaluation concluded that the crack was vibration induced and had propagated over time. This event is considered to have no significance with respect to the health and safety of the public.
2692004002 | Oconee 1, Oconee 2, Oconee 3 | 05/04/2004 | 09/09/2004 | ML04265038 | <strong>Main Steam Line Break Mitigation Design/Analysis Deficiency</strong><br /><i>Abstract:&nbsp;</i>The Automatic Feedwater Isolation System (AFIS) Circuitry actuates various components including the main and startup feedwater control valves (FCVs) in order to mitigate a Main Steam Line Break (MSLB) with or without a Loss of Offsite Power (LOOP). Tech Spec 3.7.3 requires the FCVs to be operable. The FCVs fail-as-is and require Instrument Air (IA) to close. On April 29, 2004, Units 1 and 3 were operating in Mode 1 at 100% power; Unit 2 was in No Mode during a refueling outage. During discussion between Site Engineering (SE) and General Office-based Safety Analysis (SA) personnel, it was recognized that, for smaller breaks, actuation signals/alarms may be delayed such that the IA header may depressurize before AFIS and/or operator actions initiate FCV closure. For breaks inside containment, this could lead to pressurization of the Reactor Building (RB) above the RB design pressure (but below RB failure pressure, 144 psig). Immediate action was taken to maintain a diesel air compressor operating at all times pending a more permanent resolution. On May 4, 2004 the event was determined to be reportable. The FCVs are considered to have been inoperable longer than allowed by TS. The root causes are deficient analysis and documentation. This event is considered to have no significance with respect to the health and safety of the public.
2692004003 | Oconee 1 | 09/12/2004 | 11/11/2004 | ML04328060 | <strong>Loss of Containment Spray due to Test When Redundant Train Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 9-12-04, Oconee Unit 1 was operating at 100% in Mode 1 with Channel 7 of the Engineered Safeguards Actuation System out of service. As a result, the1A train of the Reactor Building Spray (RBS) System had been declared out of service (OOS). At 15:55 the 1B RBS Train was declared out of service to stroke test 1LP-22, a pump suction valve. At 15:58 the stroke test was complete and the 1B RBS Train was returned to service. When logging the Technical Specification (TS) condition entry, an operator recognized that both trains had been OOS simultaneously, which placed Unit 1 in TS 3.0.3 for three minutes. At 19:14 on 9-12-04 an ENS notification per 10CFR 50.72 (b)(3)(v)(D) was completed (Event Number 41037). The root causes of the event were a procedure adherence error (a Senior Reactor Operator forgot to perform a required log review for OOS components) and a work process error (a scheduling code indicated the train as available during the test activity). Corrective actions include counseling and revising the test activity code. This event is considered to have no significance with respect to the health and safety of the public.
2692004004 | Oconee 1, Oconee 2 | 11/17/2004 | 09/29/2005 | ML05278039 | <strong>Improper Overloads Installed on Control Room Ventilation Filter Train</strong><br /><i>Abstract:&nbsp;</i>On 11-17-04, with Oconee Units 1 and 2 in Mode 1 at 100% Full Rated Power,the Control Room Ventilation System Train B Outside Air Booster Fan tripped unexpectedly at 1638 hours during a post maintenance test. This train supplies the shared Unit 1 and 2 control room with filtered air to reduce the impact on control room personnel due to any release of airborne contamination following a postulated accident. Investigation determined that the installed motor starter relay overload heater elements were improperly sized such that the train might trip following an accident. A modification was performed to install the proper size overload heaters, and the fan was declared operable on 11-19-04 at 1809 hours. The fan tripped again on 4-10-05.The A train on Unit 1 and 2 and both trains on Unit 3 were verified to have proper overloads installed. The apparent cause of the initial trip was that the B train was not included in the scope of a 1987 modification which revised the overload heaters on the A train. The cause of the 4-10-05 trip was improper installation of the new overload heaters during replacement on11-18-04. This event is considered to have no significance with respect to the health and safety of the public.
2712004001 | Vermont Yankee | 04/05/2004 | 05/26/2004 | ML04156035 | <strong>Main Steam Isolation Valve Leakage Exceeds a Technical Specification Leakage Rate Limit</strong><br /><i>Abstract:&nbsp;</i>On 04/05/04, with the plant shutdown for refueling, the "B" inboard main steam line isolation valve exceeded its allowable leakage rate limit during local leakage rate testing. Technical Specification (TS) 3.7.A.4 states that whenever primary containment is required, the leakage from any one main steam isolation valve (MSIV) shall not exceed 31 standard cubic feet per hour (scfh) at 44 psig. The leakage rate test result on the "B" main steam line outboard MSIV was completed satisfactorily. Additionally, the total combined leakage rate from all Primary Containment penetrations was less than the maximum allowable leakage rate limit of 0.8% air weight per day as specified in TS 6.7.C, thereby remaining within the design bases of the plant. The cause of the leakage rate test failure was due to a binding of the stem and packing follower from scoring and galling that was compounded by each subsequent cycling of the valve during scheduled surveillance activities. This mechanical degradation occurred as a result of maintenance instructions provided during prior maintenance activities that lacked specificity regarding tolerances. The MSIV was disassembled, repaired, modified, cleaned, tested satisfactorily and returned to service. This condition was bounded by the primary containment design basis analysis and therefore, did not significantly degrade plant safety. There was no increased risk to the health and safety of the public as a result of this event.
2712004002 | Vermont Yankee | 04/20/2002 | 09/29/2004 | ML04281022 | <strong>Special Nuclear Material Inventory Location Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On 04/20/04, with the reactor shutdown for a refuel outage, an inventory of Special Nuclear Material (SNM) in the Spent Fuel Pool (SFP) revealed that two fuel rod pieces were not in the designated storage location. This condition was reported to the NRC on 04/21/04 pursuant to 10 CFR 50.72 (b)(2)(xi) as NRC Event Number 40694 for a news release, amended on 05/19/04 to address additional reporting regulations. The two fuel rod pieces were the product of a fuel reconstitution performed in 1979 due to Crud Induced Localized Corrosion (CILC) fuel rod failures identified at Vermont Yankee and elsewhere within the nuclear industry. An investigation team was formed to complete a root cause analysis of the event and to search for the fuel rod pieces. The investigation was accomplished primarily by completing an inspection of the SFP, document reviews, interviews with VY employees (past and present) and interviews with contractors that had been associated with SFP activities and radioactive waste operations at Vermont Yankee. On 07/13/04 the two fuel rod pieces were located in the SFP on top of the channel rack in a cylindrical liner specifically designed by General Electric for storing fuel rod pieces. On 07/13/04, the NRC was notified of this development in the investigation, and was documented as NRC Event Number 40867.
2712004003 | Vermont Yankee | 06/18/2004 | 06/14/2005 | ML05172046 | <strong>Automatic Reactor Scram due to a Main Generator Trip as a Result of an Iso-Phase Bus Duct Two-Phase Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>On 06/18/04 at 0640, with the plant at full power, a turbine load reject scram occurred due to a two phase electrical fault to ground on the 22 kV iso-phase bus. All safety systems responded as designed and the reactor was shutdown without incident. Off-site power transmission lines and station emergency power sources were available throughout the event. Arcing and heat generated during the fault damaged an area around the iso-phase bus ducts and Main Transformer low voltage bushings. The electrical faults disrupted an oil line flange between the Main Transformer oil conservator (expansion tank) and the "C" phase low voltage bushing box, and the leaking oil ignited. Fire suppression systems activated automatically. An Unusual Event was declared at 0650 for a fire lasting greater than 10 minutes. The VY Fire brigade and local community fire departments declared the fire under control at 0717. At 1245, the Unusual Event was terminated. The electrical grounds that initiated the event were caused by loose material in the "B" iso-phase bus duct as a result of the failure of a flexible connector. The grounds raised the voltage on the "A" and "C" iso-phase busses contributing to the failure of the "A" phase surge arrester. The root causes of the event were determined to be the result of a flexible connector fabrication deficiency and preventative maintenance not being performed on the surge arresters located in the Main Generator Potential Transformer (PT) Cabinet. There was no release of radioactivity, breach of secondary containment or personnel injury during this event.
2722004001 | Salem 1 | 04/09/2004 | 10/12/2004 | ML04301025 | <strong>As Found Value for Main Steam Safety Valve Lift Setpoint Exceeds Technical Specification Allowable Limit</strong><br /><i>Abstract:&nbsp;</i>During the Salem Unit 1 sixteenth refueling outage (IR16), ten of the Main Steam Safety Valves were initially lift setpoint tested in accordance with the Inservice Test (IST) Program. On April 9, 2004, PSEG discovered that one of the Main Steam Safety Valves tested failed its as-found lift setpoint test. The as-found actuation pressure for Main Steam Safety Valve 13MS13 was below the lower limit of minus 3% of the nameplate setpoint as stated in the Salem Technical Specification (TS) Table 3.7-1. The TS value is 1110 psig +/- 3%. The apparent cause of this event has been attributed to the unsatisfactory condition of the spring and mating spring caps. Because the actual lift setpoint of the 13MS13 was not within the required acceptance criterion of +1- 3%, two additional Main Steam Safety Valves were tested. The two additional Main Steam Safety Valves (11MS13 and11 MS 14) tested satisfactory and no further testing was required. The failed valve was replaced with a pre-tested and certified spare. This event is reportable per the requirements of 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
2722004002 | Salem 1, Salem 2 | 09/03/2002 | 05/20/2004 | ML04154044 | <strong>Non Conservative Technical Specifications - Containment Fan Coil Units</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2004, a review of the control room operator's logs was completed as a result of a discrepancy identified on February 24 between the Salem Units 1 and 2 Technical Specifications (TS) 3.6.3.2 and the current licensing basis analyses assumptions. Specifically, PSEG identified that TS 3.6.3.2 Action b (for both Salem Units) was non-conservative. TS 3.6.3.2 Action b contains an allowable outage time of 72 hours whenever three or more Containment Fan Coil Units {BK}(CFCU) are inoperable provided that two Containment Spray {BE}(CS) pumps are operable. Current design analyses do not support the plant configuration allowed by TS 3.6.3.2 Action b. The control room operator's log review identified at least two occasions (September 3, 2002 and July 3, 2003 for Salem Units 1 and 2 respectively) where T.S. 3.6.3.2 Action b had been entered. The cause of this event was determined to be the existence of the non-conservative Technical Specification. The reason for failing to identify the condition earlier was determined to be an inadequate review for an Updated Final Safety Analysis Report (UFSAR) change related to NSAL 00-010 “Containment Safeguards Heat Removal Capability.” Corrective actions taken were: (1) In accordance with Administrative Letter 98-10, Salem Operations established guidance to enter Technical Specification 3.0.3 when more than two Containment Fan Coil Units are inoperable regardless of the number of operable Containment Spray pumps until the Technical Specifications are revised, (2) A license change request to correct the Technical Specification was submitted on April 15, 2004, (3) Other similar generic technical correspondence will be reviewed for proper closure and the event will be shared with engineering personnel. This is being reported under the requirement of 10CFR50.73(a)(2)(v)(C) and (D), as a condition that could have prevented the fulfillment of a safety function of a system needed to remove heat, or control the release of radioactive material, or mitigate the consequences of an accident.
2722004003 | Salem 1 | 06/02/2004 | 09/03/2004 | ML04260041 | <strong>Completion of Plant Shutdown to Comply With Technical Specifications - 3.6.1.1 "Containment Integrity."</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2004 at approximately 1230 hours, the 1SW26 valve (service water to the turbine building isolation valve) was declared inoperable as a result of investigation into an abnormal condition with Service Water in the turbine building. A plant shutdown was initiated in accordance with Technical Specification 3.6.1.1 "Primary CONTAINMENT INTEGRITY". On June 2, 2004, non-licensed operations personnel identified an abnormal condition in the control of the turbine building service water pressure. During a routine tour of the turbine building while returning Unit 1 from its sixteenth refueling outage, the operator noticed that the temperature in the number 11 main turbine lube oil heat exchanger was approximately 110 degrees F. Further investigation revealed that the service water to the turbine building regulating valve (1STI) was full open with only 72 psig in the service water turbine header downstream of 1ST1. These conditions, low pressure and high temperatures, were not normal for the plant conditions at the time. Further troubleshooting indicated that the service water to the turbine building isolation valve (1SW26) had been improperly installed and its motor operator improperly set up. The root cause of the event is attributed to failure to follow the process of match marking to assure that the actuator was properly installed with respect to the valve position. Corrective actions taken were: the valve actuator was removed, the valve disc was rotated 180 degrees, And re-tested satisfactorily. Additional corrective actions will include revising the applicable installation procedures, including lessons learned for similar activities in upcoming outages and evaluating the event for inclusion in the continuing training program. This event is being reported under the requirement of 10CFR50.73(a)(2)(i)(A), incompletion of a plant shutdown to comply with Technical Specifications.
2722004004 | Salem 1 | 07/21/2004 | 09/20/2004 | ML04272033 | <strong>Non-essential Loads Not Isolated With One Chiller Inoperable as Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2004 at 0414 hours Salem Unit 1 No. 11 Chiller was removed from service for a scheduled work activity. With a single chiller inoperable, Technical Specifications (TS) require that the appropriate non-essential heat loads be isolated within 4 hours. This required closing of valves 1CH30 and 1CH151.These valves were closed and white caution tag stickers hung next to the panel control switches. During July 21, 2004 dayshift, operations personnel were performing surveillance testing on Train 'A' of the Solid State Protection system. The procedure directs the 1CH30 and 1CH151 valves to be opened following completion of test. During restoration the Nuclear Control Operator performing the test noted the No. 11 Chiller out of service, but failed to notice the white caution stickers for the valves. At 1205, valves, 1CH30 and 1CH151 were reopened. At approximately 1858 hours, the oncoming nightshift noted valves were open and entered TS 3.0.3. The valves were immediated reclosed, non-essential load isolation was reinstated, and TS 3.0.3 was exited. The cause of this event was human error attributed to a lack of attention to detail and the lack of QV&V prior to taking action. Corrective actions taken include incorporation of this event into current licensed operator requalification training segment emphasizing and re-enforcing the use of human error reduction techniques. Additionally, procedure(s) will be revised to require closing associated manual isolation valves when isolating non-essential loads. This event is reportable per the requirements of 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
2722004005 | Salem 1 | 12/05/2004 | 10/06/2005 | ML05292007 | <strong>ECCS Leakage Outside Containment Exceeds Dose Analysis Limits (11 RHR Heat Exchanger)</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2004, the 11 Residual Heat Removal (RHR) loop was placed in service in accordance with plant operating procedures to support forced outage activities. Following the start of the 11 RHR pump, an equipment operator (non licensed operator) performed a walk down of the system and verified that the 11 RHR train was operating properly with no leakage observed. Approximately one (1) hour after the initial verification, a health physics technician (non licensed personnel) reported that the 11 RHR heat exchanger (HX) had developed a leak. Maintenance and Operations personnel performed a walk down of the system and identified the leakage to be 0.50gpm at the top of the RHR HX (top flange). The leakage was limited to a small area on the top of the heat exchanger flange. The cause of this event was determined to be personal error. During the last Unit 1 refueling outage while preparing the work package to replace the heat exchanger gasket, the design engineer preparer and reviewer performed an Equivalent Change Package (ECP) instead of utilizing the required Design Change Package (DCP) process. Because the identified leakage rate exceeded the assumptions made in the dose analysis calculation for emergency core cooling system (ECCS) leakage outside the containment, this event is reportable in accordance with10CFR50.73(a)(2)(v), "any event or condition that could have prevented the fulfillment of the safety function of structures or system that are needed to.....(C) control the release of radioactive material."
2722004006 | Salem 1 | 09/15/2004 | 11/15/2004 | ML04328052 | <strong>Operation in a Condition Prohibited by Technical Specification - Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2004, a review of actions associated with the performance an In Service Test (IST) determined that the actions taken on September 15 were inappropriate and the Plant was not in compliance with Technical Specifications. On September 15, 2004, during performance of the quarterly In Service Test in accordance with approved plant surveillance test procedures, the Service Water inlet valve to the 11 Containment Fan Coil Unit (11SW58) failed to indicate closed on the control console upon stroking the valve, thus exceeding its Required Action stroke time. Technical Specification 3.6.3.1 was entered at 21:17 on September 15, 2004. Following non-intrusive troubleshooting, additional strokes, and consultation with IST personnel, the Technical Specification was exited at 22:41 on September 15. A review of the actions taken on September 15 by the IST Program Manager concluded that Technical Specification 3.6.3.1 should not have been exited. According to the requirements of the IST program, the first stroke is the IST stroke time. The IST program does not include provisions for multiple strokes to determine operability of a valve that has exceeded its Required Action stroketime without the performance of maintenance or a rigorous engineering evaluation. The cause of this event was determined to be personnel error. An immediate corrective action taken was to repair and retest the 11SW58valve. This report is being made in accordance with 10CFR50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications..."
2722004007 | Salem 1 | 12/08/2004 | 02/07/2005 | ML05053010 | <strong>Operation in a Condition Prohibited by Technical Specification - Technical Specification 3.3.2.1</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2004, during a reactor power increase the nuclear control operator (NCO) (Licensed operator) noticed that the 11 Steam Generator steam line flow Channel 1 was reading approximately 10% while channel 2 and all the other loop channels were reading approximately 26%. Initial troubleshooting into this event revealed a leak on the low pressure side of the transmitter and identified that the transmitter equalizing valve was open slightly. The transmitter equalizing valve must remain closed for the transmitter to function properly. Further investigation revealed that this transmitter was last worked on December 8, 2004 to perform a sensor calibration. Therefore, it is assumed that the transmitter was inoperable as of December 8, 2004, and therefore Technical Specification 3.3.2.1 Action Statement 19 was not complied with. Specifically, that the inoperable channel be placed in the tripped condition within 6 hours. The apparent cause of this event is attributed to failure of personnel to utilize self-check techniques and to comply with written procedures. The transmitter equalizing valve was closed and the leak was repaired. This event is reportable in accordance with 10CFR50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications..."
2752004001 | Diablo Canyon 1 | 04/08/2004 | 05/10/2004 | ML04140003 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2004, with Unit 1 in no Mode (Defueled), analysis of eddy current testing on Steam Generator (SG) 1-4 indicated that greater than one percent of the tubes were defective. PG&E made a nonemergency report to the NRC as required by Technical Specification (TS) Table 5.5 .9-2, "Steam Generator (SG) Tube Inspection," at 1402 PDT. On April 14, 2004, PG&E discussed the preliminary results of the SG eddy current inspection during a phone conference with the NRC. PG&E notified the NRC that primary water stress corrosion cracking (PWSCC) and circumferential indications were detected at tube support plate intersections, per TS 5.6.10 paragraph d. On April 20, 2004, analysis of eddy current testing on SG 1-1 also indicated that greater than one percent of the tubes were defective. PG&E made a nonemergency report requred by TS Table 5.5.9-2, at 2026 PDT. The majority of the tube defects in SG 1-4 were attributed to circumferential PWSCC in the U-bend region. The majority of the tube defects in SG 1-1 were attributed to axial outside diameter stress corrosion cracking at tube support plate intersections. PG&E has plugged all defective Unit 1 tubes identified during the current refueling outage in accordance with TS 5.5.9. All defective tubes met condition-monitoring requirements at the end of Cycle 12. PG&E maintains a comprehensive program to minimize SG tube degradation.
2752004002 | Diablo Canyon 1 | 07/21/2004 | 09/20/2004 | ML04279044 | <strong>TS 3.0.3Required Shutdown Due to TS 3.7.7,"Vital CCW System," Limiting Condition for Operation Not Met</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2004, with Unit 1 in Mode 1 (Power Operation) at approximately 100 percent power, a nonvital component cooling water (CCW) leak was identified. PG&E licensed plant operators conservatively concluded that the leak could potentially disable both vital CCW loops, thus the limiting condition for operation (LCO) for Technical Specification (TS) 3.7.7, “Vital CCW System," was not met. Plant operators entered TS 3.0.3 at 1900 PDT, and a Unit 1 forced shutdown was commenced at 2020 PDT. At 2157 PDT plant operators made a nonemergency event notification (EN #40890) in accordance with 10 CFR 50.72(b)(2)(i). On July 22, 2004, at 0033 PDT, following reactor coolant pump (RCP) 1-3 upper bearing Tube oil cooler isolation, TS 3.0.3 was exited. On July 23, 2004, at 1432 PDT, following RCP 1-3 upper bearing Tube oil cooler channel head replacement, TS 3.7.7 was exited. The cause of this event was high cycle fatigue cracking of the CCW supply pipe nozzle at the RCP 1-3 upper bearing lube oil cooler channel head. Contributory causes include the cooler channel head was in operation at or near the piping resonant frequency. Corrective action to prevent recurrence includes moving the natural frequency off-resonance (away from 20 Hz).
2772004001 | Peach Bottom 2 | 02/22/2004 | 04/16/2004 | ML04118056 | <strong>Manual Scram Resulting from Low Condenser Vacuum due to a Failed Feedwater Turbine Expansion Joint</strong><br /><i>Abstract:&nbsp;</i>Peach Bottom Unit 2 was manually scrammed at approximately 1510 hours on 2/22/04 as a result of decreasing Main Condenser vacuum. Prior to the event, at 1424 hours, an increase in the air in-leakage into the condenser occurred. This prompted entry into the Operational Transient (OT) procedure for low condenser vacuum. Condenser vacuum was 27.1" Hg at the time the OT procedure was entered. A power reduction was performed to approximately 43% power with a resultant condenser vacuum of approximately 25.5" Hg. A briefing was conducted and the reactor was manually scrammed in accordance with the OT procedural direction since Condenser vacuum was not restored to above the procedurally required 26.2" Hg value for the current plant condition. As a result of the manual scram, reactor water level decreased, as expected, to below the reactor water level-three (lo-level) set point resulting in Primary Containment Isolation System Group II and III isolations. The cause of the event was due to a leaking Reactor Feed pump Turbine Exhaust expansion joint. The expansion joint was repaired. There were no safety consequences as a result of this event.
2772004002 | Peach Bottom 2 | 09/07/2004 | 11/19/2004 | ML04335001 | <strong>Technical Specification Non-Compliance due to Inoperable Primary Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On 9/23/04, during planned refueling outage maintenance activities, maintenance technicians discovered foreign material (i.e. a bolt) in the valve body of the High Pressure Coolant Injection (HPCI) Turbine Exhaust Drain Line Inboard Isolation Air-Operated Valve (AO-137). It was subsequently determined that this foreign material was the cause of a previously identified failure of this valve to close that was discovered on 9/8/04 at approximately 1700 hours during the performance of routine surveillance testing. Further investigation determined that the foreign material in the system piping was originally identified as being lost during previous refueling outage maintenance activities performed in September 2002. The evaluation performed for the lost material did not result in the expectation that the material would travel to the AO-137. However, the bolt migrated to the AO-137 valve body during a HPCI system run. The previous HPCI system run prior to the discovery of the valve seating concern was on 9/7/04 at approximately 1400 hours. Therefore, this is considered the time that the foreign material entered the valve seat area and therefore the AO-137 is considered to have become inoperable at that time. Because the Technical Specification 4-hour Required Action to isolate the penetration was not performed until 9/08/04 by 2100 hours, this event was determined to be a condition prohibited by the Technical Specifications. The bolt was removed and the other areas of the HPCI turbine piping system were thoroughly inspected for additional foreign material. There were no previous similar LERs. There were no actual safety consequences associated with this event.
2772004003 | Peach Bottom 2 | 12/22/2004 | 01/20/2005 | ML05033012 | <strong>Automatic Scram due to an Electro-Hydraulic Control System Malfunction</strong><br /><i>Abstract:&nbsp;</i>On 12/22/04 at approximately 0455 hours, a Unit 2 Reactor scram occurred as a result of a Primary Containment Isolation System (PCIS) Group I isolation. The Group I PCIS isolation was a result of low main steam line pressure caused by the opening of Main Turbine Bypass Valves due to an Electro-Hydraulic Control (EHC) circuit malfunction. The PCIS Group I isolation resulted in the closure of the Main Steam Isolation Valves (MSIVs). As would be expected for a PCIS Group I isolation, Reactor water level decreased to the Level 2 set point resulting in the actuation of the High Pressure Coolant Injection (HPCI), Reactor Core Isolation Cooling (RCIC) and the Alternate Rod Injection (ARI) / Recirculation Pump Trip systems. PCIS Group II and IlI isolations also occurred as Reactor water level passed through the Level 3 set point. The cause of the EHC system malfunction was due to a failed 'A' Pressure Regulator circuit card. The card was found to have a manufacturing defect involving excess solder. The defective card was replaced and the EHC system tested to verify proper operation. The EHC system was placed in service and has been appropriately controlling Reactor pressure since this event. Similar installed circuit cards on Unit 2 were inspected and no similar solder deficiencies were observed. Additional evaluations and corrective actions are being performed in accordance with the corrective action program. This event was not considered to be risk significant.
2782004001 | Peach Bottom 3 | 03/17/2004 | 04/30/2004 | ML04125003 | <strong>Loss of High Pressure Coolant Injection System Function as a Result of Inoperable Flow Controller</strong><br /><i>Abstract:&nbsp;</i>On 3/17/04, at approximately 1235 hours, during the performance of a routine surveillance test for the High Pressure Coolant Injection (HPCI) system, Operations personnel discovered that HPCI was inoperable. During performance of the surveillance test, the HPCI turbine could not achieve a speed above 1000 rpm and no significant discharge pressure was observed. Within two minutes of the initial turbine start, HPCI was tripped and the steam supply isolation valve was closed. The cause of the event is due to an inoperability of the HPCI system flow controller. The HPCI controller was discovered to not respond properly. The flow controller was replaced. HPCI was satisfactorily tested and returned to an operable status on 3/19/04 by 0145 hours. Other flow related components on the HPCI system were evaluated and found to be in an acceptable condition. Other similar flow controllers (HPCI and RCIC) on Units 2 and 3 were evaluated for extent of condition concerns and determined to be operable. There were no actual safety consequences associated with this event.
2782004002 | Peach Bottom 3 | 08/03/2004 | 11/05/2004 | ML04322033 | <strong>Loss of High Pressure Coolant Injection System Automatic High Level Trip as a Result of Lifted Lead</strong><br /><i>Abstract:&nbsp;</i>On 9/14/04, at approximately 0400 hours, during the performance of a routine surveillance functional test of the 'D' channel of Emergency Core Cooling system (ECCS) compensated trip system, Instrument and Controls (I&C) Technicians experienced an unexpected test result and immediately halted the testing. It was promptly recognized that an electrical lead in the circuitry for the High Pressure Coolant Injection (HPCI) system had been previously lifted and had not been properly restored. The location of the lifted lead in the circuitry resulted in the inability to automatically trip the HPCI turbine on high water level (i.e. Level 8). This automatic function is required by plant Technical Specification 3.3.5.1, ECCS Instrumentation. The failure to restore the electrical lead occurred during the testing of the 'C' channel of the ECCS compensated trip system on 8/3/04. The cause of this event was due to inadequate human performance during the I&C testing performed on 8/3/04 and an inadequate procedure step to independently verify the connection was properly restored. The electrical lead was re-connected on 9/14/04 by 1200 at which time the automatic trip of the HPCI turbine on high water level was restored to service.
2782004003 | Peach Bottom 3 | 10/09/2004 | 11/30/2004 | ML04335002 | <strong>Technical Specification Non-Compliance due to Loose Wire on a HPCI Suction Valve Logic Relay</strong><br /><i>Abstract:&nbsp;</i>On 10/9/04, at approximately 0500 hours, during the performance of a routine surveillance test for the High Pressure Coolant Injection (HPCI) system, Operations personnel discovered that the Condensate Storage Tank (CST) suction source Motor Operated (MO) Valve (MO-17) did not automatically close when the Suppression Pool Suction source valves (MO-57 & MO-58) were opened during the surveillance test. It was subsequently determined that a condition prohibited by Technical Specifications existed as a result of the Technical Specification 3.3.5.1 function of transferring the HPCI suction from the CST to Suppression Pool being inoperable for a time period longer than allowed in Technical Specification 3.3.5.1. Trouble shooting determined that the automatic closure of the MO-17 did not initially occur due to a loose wire on a logic relay associated with the auto close function of the MO-17. The connection was retightened. The HPCI CST-Suppression Pool transfer logic was returned to an operable condition on 10/10/04. There were no previous similar LERs. There were no actual safety consequences associated with this event.
2802004001 | Surry 1 | 12/04/2004 | 02/02/2005 | ML05045038 | <strong>Emergency Service Water Pump Found Inoperable After Entry into a Mode</strong><br /><i>Abstract:&nbsp;</i>On December 4, 2004, Unit 1 was operating at 40% reactor power and Unit 2 was at 100%. While conducting a periodic test of the diesel-driven Emergency Service Water (ESW) Pump 1C, the pump failed to start. The pump was declared inoperable and a 7-day Technical Specification (TS) action statement was entered. The cause is attributed to partial implementation of a design change that failed to remove unused wiring which energized a circuit, and resulted in damage to the diesel starter motor during post-modification testing. Following the start failure, the unused wiring was removed. The starter solenoid and starter motor were replaced. The pump was successfully tested and returned to service on December 7, 2004. The pump was inoperable when the Unit 1 reactor coolant system temperature exceeded 350 degrees Fahrenheit and pressure exceeded 450 pounds per square inch on December 1, 2004. Since TS has no specific section 3.0 limitation on entry into a Mode when a LCO is not met, a voluntary LER is being submitted. This event resulted in no safety consequences or significant implications and the health and safety of the public were not affected. The design change for ESW Pumps 1 A and 1B will be revised, and circuitry evaluated after implementation. Engineering training will address related items. Maintenance implementation of design changes will be strengthened.
2812004001 | Surry 2 | 05/21/2004 | 11/13/2004 | ML04328041 | <strong>Switchyard Device Failure Results in a Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2004, at 2108 hours with Units 1 and 2 at 100% power, the Unit 2 main generator leads "A" phase Coupling Capacitor Voltage Transformer (CCVT) in the switchyard failed. The generator protective relays actuated, tripping the main generator, and resulting in trips of the turbine and reactor. Emergency systems functioned as required, including the Reactor Protection System (RPS) and Auxiliary Feedwater (AFW) System. A Notification of Unusual Event was declared related to the switchyard CCVT failure. Unit 2 was stabilized at hot shutdown. The cause of the CCVT failure was age-related degradation. The failed CCVT was replaced. On May 22, 2004, following refill of the Emergency Condensate Storage Tank, an unisolable leak in a buried Unit 2 AFW recirculation line was discovered. The AFW system was declared inoperable. Further evaluations determined that the AFW system was capable of performing its intended function. The cause of the AFW piping leak was external galvanic corrosion of the buried carbon steel piping due to the failed corrosion protection. The recirculation line was rerouted. There were no significant safety consequences associated with this event. The automatic actuations of the RPS and the AFW are reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). The AFW leak is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(vii).
2852004001 | Fort Calhoun | 07/29/2004 | 09/24/2004 | ML04268047 | <strong>Failure To Perform A Leakage Test Due To Lack Of Understanding of Penetration Design</strong><br /><i>Abstract:&nbsp;</i>While investigating the requirements for the Type B Local Leak Rate Test (LLRT) for the fuel transfer tube, it was discovered that the sleeve for the transfer tube, M-100, had not been tested as required by 10 CFR 50 Appendix J and Technical Specification 3.5 (3) (iv). Records cannot be found to determine if the test has been performed as required since initial construction. The lack of understanding of the design features of penetration M-100, coupled with the reasonable conclusion that M-100 is similar to the equipment hatch, led to a comfort level with the testing program and, consequently, lack of a proper test had never been questioned. The M-100 sleeve was subsequently tested satisfactorily. Similar penetrations were reviewed to ensure that this problem had not occurred at any other plant locations. No similar situations occurred.
2852004002 | Fort Calhoun | 10/19/2004 | 12/17/2004 | ML05006008 | <strong>Inoperable Diesel Generator for 28 Days Due to Blown Fuse During Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2004, while reviewing detailed plant computer data related to the operation of Emergency Diesel Generator Number 2 (DG-2), it was discovered that DG-2 had become inoperable for 28 days beginning on July 21, 2004. The inoperability was the result of a failed fuse affecting DG-2 voltage output. Data obtained from the plants computer system confirmed that the condition occurred as the operators were performing engine unloading and shutdown during completion of the monthly surveillance test on July 21, 2004. Based upon the analysis of available physical evidence and troubleshooting activities, the root cause for the open fuse condition was determined to be the result of premature aging. It appears that the failed fuse had experienced premature aging due to cyclic loading. A lack of formality or rigor in validating computer alarms which occur during the performance of routine evolutions (such as surveillance testing) is the root cause for the delay unrecognizing the initial inoperability condition of DG-2. The failed fuse was replaced and DG-2 was tested satisfactorily. Plant procedures have been revised to require reactor operators to acknowledge all computer annunciators during normal operation and have been revised to have computer alarm response match annunciator tile alarm response. Procedures have been changed so that fuses are replaced as "sets" where applicable.
2872004001 | Oconee 3 | 02/26/2004 | 04/26/2004 | ML04126015 | <strong>Unit 3 Trip Due to Foreign Material in Turbine Electro-Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>At 11:50:56 on 02-26-2004 Oconee Unit 3 reactor tripped on high Reactor Coolant System pressure approximately three minutes after an Electro-Hydraulic Control (EHC) pump was returned to service following routine maintenance. Post-trip response was normal. Investigation found that a small piece of foreign material, specifically a piece of clear plastic packaging material, inadvertently entered the system during replacement of a discharge filter. The material clogged the hydraulic fluid entry port of a turbine stop valve, causing all four stop valves to close. The root cause was determined to be in attention to detail by two Maintenance technicians performing the task. The material was found and removed. This event is considered to have no significance with respect to the health and safety of the public.
2872004004 | Oconee 3 | 12/13/2004 | 02/10/2005 | ML05053023 | <strong>Open Containment Penetration During Refueling Activities</strong><br /><i>Abstract:&nbsp;</i>On 12-13-04, at 1245 with Unit 3 in Mode 6 after core reload was complete, Operations personnel (OPS) discovered a deviation from Technical Specification 3.9.6 on containment closure (CC) during fuel movement. The NRC was notified at 1701 on 12/13/2004 (ENS 41256). CC was verified prior to fuel movement. On 12/7/04, during fuel movement, OPS ran a valve checklist which opened five steam drain valves in the turbine building. The valves are part of the outside containment boundary for a Main Steam penetration and were required to be closed for CC. At 2145 hours on 12/12/04, a CC surveillance found the open valves and closed them. Fuel handling was completed at 0358 on 12/13/2004. OPS checked the actual status of the inside boundary, which was uncontrolled this outage. OPS determined at 1245 on 12/13/04 that at least one valve on this penetration had been open inside containment during this event, making a reportable open flow path. The event root cause was that standards and expectations for the use of the "Containment Isolation Component" tags were not clearly defined or understood. There was no actual release due to the event. This event is considered to have no significance with respect to the health and safety of the public.
2892004001 | Three Mile Island 1 | 02/05/2003 | 12/17/2004 | ML04363040 | <strong>High Pressure Injection Pump Seismic Qualification Impacted due to an Oversight in the Design Process When Power Supplies for the Auxiliary Oil Pumps Were Relocated</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2004, it was discovered that a condition which existed for approximately 4.5 hours during February 2003 should have been reported under the following criteria: 1) a condition prohibited by Technical Specifications (10CFR50.73 (a)(2)(i)(B)), and 2) a condition that could have prevented fulfillment of a safety function (10CFR50.73 (a)(2)(v)). This condition involved a Make-up Pump (MU-P-1B), which was assumed operable during surveillance testing of the emergency diesel generator in the redundant train. However, unknown at the time, MU-P-1B was not operable due to seismic qualification concerns associated with its auxiliary oil pumps. An oversight during a modification in February 1990 did not specify a spacer be installed when relocating both auxiliary oil pump breakers for MU-P-1B to different Motor Control Centers (MCC). Without the spacer, the breaker engagement with the MCC bus bars was not adequate to assure seismic qualification, thus affecting the operability of MU-P-1B. This inadequate breaker engagement condition was identified on January 22, 2004, while troubleshooting a problem with one of the MU-P-1B auxiliary oil pumps. On January 23, 2004, the spacer plates were installed on the breakers for both oil pumps, restoring MU-P-1B operability. The root causes of the event were less than adequate (LTA) human performance during the design of the modification and LTA vendor documentation. The designer incorrectly assumed that the breaker units were interchangeable. Key corrective actions include: 1) revised the appropriate maintenance procedure to verify installation of spacer in this type of application, 2) revise the drawings for the MCCs to note when spacers are needed for proper breaker engagement, and 3) revise the appropriate Corporate Configuration Control procedures to invoke the requirements of Exelon procedures for technical human performance and technical rigor.
2932004001 | Pilgrim | 01/16/2004 | 03/11/2004 | ML04078057 | <strong>Target Rock Relief Valves' Test Pressures Exceed Technical Specification Tolerance Limit</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2004, Wyle Laboratories notified Pilgrim Station of test results indicating that three Target Rock relief valve pilot assemblies exceeded the Technical Specification (TS) tolerance limit of 1115 psig ±11 psi (±1%) during routine testing at the test facility. The cause for the as-found relief pressures exceeding the TS tolerance limit is believed to be setpoint drift resulting from corrosion bonding of the pilot valve assembly disk and seat. The corrosion bonding most likely occurred while the pilot valve assemblies were in storage awaiting testing. These three pilot valve assemblies were removed during the May 2003 refueling outage, stored at Pilgrim Station for approximately seven months, then shipped to Wyle for refurbishment and ASME Code Testing. Certified replacement relief valve pilot assemblies were installed in the plant at the time the test was performed. The condition posed no threat to public health and safety.
2932004002 | Pilgrim | 02/26/2004 | 04/26/2004 | ML04125041 | <strong>High Pressure Coolant Injection System Fuse Failure While System Inoperable for Planned Maintenance and Testing</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2004, the High Pressure Coolant Injection (HPCI) system turbine gland seal condenser (GSC) condensate pump motor became de-energized during post work testing while the HPCI system was inoperable for planned maintenance and testing. An approved analysis has not been conducted to determine the ability of the HPCI turbine to operate for the duration of the system's mission time with the GSC pump inoperable. The root cause was separation of the fuse element from the fuse end cap (ferrule) that was most likely due to manufacturing defect(s) introduced when the fuse was manufactured (pre-1994). The defect(s) resulted in a weak solder connection between the fuse end cap and fuse element. Inspection of the fuse identified the fusible link to be intact. The fuse was a Bussman Limitron, Class RK1, KWN-R-10 type fuse. The fuse was replaced and the pump was post work tested with satisfactory results. Corrective actions planned include the following. The scope of fuses to be replaced is being determined, new fuses are being procured, and selected fuses will be replaced with new fuses. This condition posed no threat to public health and safety.
2932004003 | Pilgrim | 05/06/2004 | 07/06/2004 | ML04197023 | <strong>Target Rock Relief Valves' Test Pressures Exceeding Technical Specification Tolerance Limit</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2004, Pilgrim Station was notified of test results for the pilot valves of two main steam relief valves that had exceeded the Technical Specification limit of 1115 +/-11 psig during testing at the Wyle Laboratories test facility. Certified replacement relief valve pilot assemblies were installed in the plant at the time of the notification. The root cause evaluation identified the most probable cause of initial high as-found popping pressures exceeding the tolerance limit was corrosion bonding of the pilot valve disc and seat. The corrosion bonding most likely developed while the pilot valves were in service. The root cause evaluation identified poor fitting insulation as a contributing cause. Corrective action taken and planned includes replacing the pilot valves with certification tested pilot valves, reworking the insulation, overhauling the pilot valves, and purchasing new insulation. The condition posed no threat to public health and safety.
2932004004 | Pilgrim | 07/30/2004 | 09/28/2004 | ML05011011 | <strong>RCIC System Declared Inoperable During Surveillance Testing due to Flow Controller Potentiometer Oxidation</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2004, the reactor core isolation cooling (RCIC) system was declared inoperable. This action was taken because the RCIC system turbine-pump did not achieve the acceptance criteria of flow rate, discharge pressure, and speed during the performance of a surveillance test of the RCIC system pump. The cause was the potentiometer (i.e. rheostat) in the RCIC flow controller, a GEMAC type 540 manufactured by General Electric Company. The function of the potentiometer is to clamp the high limit output of the controller. The potentiometer was found to have a bad spot (i.e. "dead spot") and prevented the turbine-pump from being adjusted to achieve the acceptance criteria. Infrequent exercising of the potentiometer was identified as a contributing cause. Corrective action taken included the replacement of the potentiometer. Corrective action planned includes the revision of procedures and the replacement of the RCIC system flow controller. The event posed no threat to public health and safety.
2932004005 | Pilgrim | 08/10/2004 | 09/29/2004 | ML04281011 | <strong>Standby Gas Treatment System Inoperable due to Pneumatic Accumulator Leakage Rate</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2004, it was determined that both trains of the Standby Gas Treatment System (SGTS) had been inoperable on August 10, 2004. This was based on train 'A' being made inoperable on August 10, 2004 for planned maintenance, and identification on August 12, 2004 of an SGTS accumulator bank leakage rate greater than design resulting in train 'B' also being inoperable. The direct cause was leakage through the closed exhaust port of a solenoid-operated valve that provides air to an SGTS train 'A' air-operated damper. Corrective action taken included replacement of the solenoid-operated valve and post work testing with satisfactory results. Corrective actions planned include development of a methodology to monitor and trend SGTS instrument air system leakage. The condition was identified while operating at 100 percent reactor power, and posed no threat to public health and safety.
2962004001 | Browns Ferry 3, Browns Ferry 1, Browns Ferry 2 | 02/16/2004 | 04/23/2004 | ML04126050 | <strong>Inoperability of Diesel Generator 3D Beyond TS Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2004, Diesel Generator (DG) 3D was declared inoperable and taken out of service for planned maintenance. On February 9, 2004, following successful completion of post-maintenance testing, the DG was returned to service and declared operable. On February 25, 2004, during performance of surveillance testing, the common accident portion of the DG output breaker control circuitry was found to be incapable of accomplishing its design function of tripping the breaker. Investigation determined that the problem with this circuit had been created during reinstallation of the breaker into its shutdown board compartment on February 9, 2004; therefore, the DG had been inoperable dating back to February 2, 2004. This period of approximately 23 days exceeded the 14 days out-of service time allowed by the Technical Specifications (TS). In summary, a violation of the TS requirements commenced on February 16, 2004, when the allowable 14 day interval elapsed, and this condition was discovered on February 25, 2004. The breaker was found misaligned in its compartment due to interference by a grounding device. The grounding devices will be inspected and those showing damage will be replaced with a more rugged design.
2962004002 | Browns Ferry 3, Browns Ferry 2 | 11/23/2004 | 01/24/2005 | ML05024019 | <strong>Reactor Scram from Main Turbine Trip from Loss of All Speed Feedback</strong><br /><i>Abstract:&nbsp;</i>On November 23, 2004, while Unit 3 was in steady state operation at 100% power, a main turbine trip and subsequent reactor scram occurred. All expected system responses occurred. A lightning strike occurred on the TVA 500-kV system approximately 40 miles distant from Browns Ferry. This strike resulted in a phase-to-ground fault on all three phases of the transmission line, and the electrical power transient caused speed perturbations on both the Unit 2 and Unit 3 main turbines. The rate of speed change seen on Unit 3 was slightly greater than the maximum rate anticipated by the turbine control system logic, and therefore the turbine speed feedback signals, while valid, were designated as invalid by the logic. With all turbine speed feedback signals designated as invalid, a main turbine trip on loss of speed feedback occurred in accordance with the system design, and a reactor scram occurred due to the turbine trip. The event cause was that actual turbine speed changes exceeded those anticipated as possible by the turbine control logic, causing valid speed signals to be designated as invalid. Corrective actions included the adjustment of the affected logic settings, evaluation of the turbine speed response, and consideration of modifying the speed control and turbine trip logic.
2962004003 | Browns Ferry 3 | 06/17/2004 | 02/15/2007 | ML07057022 | <strong>Main Steam Relief Valve Inoperability LCO Exceeded During Operating Cycles 10 and 11 due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Testing of main steam relief valves (MSRV) removed from Unit 3 following the operating cycles 10 and 11 respectively, revealed that in each set of valves tested, multiple valves mechanically actuated at pressures greater than 3% above their nominal setpoint. The Unit 3 Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.3 requires that 12 MSRVs be operable in reactor Mode 1 (power operation), Mode 2 (startup), and Mode 3 (hot shutdown). If less than 12 MSRVs are operable, the unit is to be placed into Mode 3 within 12 hours and Mode 4 (cold shutdown) within 36 hours. Since each BFN unit has 13 installed MSRVs, any concurrent MSRV inoperability would require the above actions to be taken. While the setpoint-drift condition was not identified until after the valves' removal from the plant, MSRV pilot valve disc-seat corrosion bonding in boiling water reactor applications is a known phenomenon, and the condition is deemed to have developed and existed while the valves were in service during operation in cycles 10 and 11. Similar MSRV performance prior to calendar year 2001 was reported by TVA to NRC via LER. However, TVA did not report the failure to meet TS following the Unit 3 operating cycles 10 and 11 in 2002 and 2004. The failure to report the occurrences have been addressed by the TVA Corrective Action Program. LER 296/2006-01 was submitted for Unit 3 Cycle 12 operation. This LER, 296/2004-003-00, addresses the past conditions (i.e., 2002 and 2004) which had not been previously reported. The root cause of this condition was MSRV pilot valve disc-seat corrosion bonding which can develop during normal reactor operations. The affected valves were refurbished and their lift-setpoints re-established prior to their re-installation in the plant. There was no actual safety consequences associated with this condition.
2982004001 | Cooper Station | 02/11/2004 | 04/08/2004 | ML04104076 | <strong>Process Weakness Results in Technical Specification Prohibited Operation</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2004, during validation of a valve line-up on the Service Water (SW) Gland Water system, Cooper Nuclear Station discovered that the gland water piping was cross-connected with SW subsystem "A" safety related pump discharge supplying gland water to both SW subsystems. This resulted in SW subsystem "B" being declared inoperable and required entry into a 30 day Limiting Condition for Operation (LCO). Diesel Generator (DG) 2, which is cooled by SW subsystem "B", and the Control Room Emergency Filter System (CREFS), which was aligned to the DG 2 emergency bus, were declared inoperable and required entry into 7-day Shutdown LCOs. The LCOs were entered at 0310 hours. The gland water line-up was returned to the required configuration and the LCOs were exited at 0340 hours. Further investigation determined that the cross-connected configuration had existed since restoration of the system from planned maintenance performed 21 days earlier. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as "Any operation or condition which was prohibited by the plant's Technical Specifications [(TS)]," due to the length of time DG 2 and CREFS were inoperable, which exceeded the TS 7 day shutdown LCO. The cause of this event was determined to be a process weakness in the Clearance Order program. Additional instructions for development of clearance orders were issued on February 13, 2004 and are vision to the station procedure for development of clearance orders was completed on April 8, 2004.
2982004002 | Cooper Station | 03/28/2004 | 05/27/2004 | ML04154037 | <strong>Failure to Follow Procedure Results in Both Diesel Generators being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2004 diesel generator Division 1 was declared inoperable as a result of day tank float valve strainer fouling. As an interim compensatory measure to support Division 2 operability the diesel fuel oil storage tank cross-tie line valves were opened. On March 28, 2004, at 1303 CST while performing a routine surveillance to check availability of fuel oil for the diesel generators it was discovered that the storage tank levels were not equalized. During the subsequent investigation it was discovered that DGDO-V-23 had not been correctly verified to be in the open position and was, in fact, in the closed position. This resulted in both divisions of diesel generators being declared inoperable. The condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as, "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident". The cause of the condition was a failure to follow procedural methods in checking valve position. Contributing causes included an inconsistent labeling of valve position and a lack of independent verification of valve position when the valve position was checked. The closed valve was opened and diesel generator Division 2 was declared operable. Long-term corrective action is to correct the condition of the transfer valves to ensure that an obvious visible indication of valve position is available that allows ease of interpretation.
2982004003 | Cooper Station | 06/01/2004 | 07/27/2004 | ML04216001 | <strong>High Pressure Coolant Injection Pump Inoperability Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>At 1915 Central Daylight Time (CDT) on June 1, 2004, the control room received an alarm from the High Pressure Coolant Injection (HPCI) exhaust drain pot high-level sensor. This alarm had been occurring hourly or less because the turbine steam supply valve had been leaking. The alarm procedure directs that the exhaust drain pot be drained. This time, however, the alarm did not clear when other indicators revealed that the pot had drained. As precautionary measure, the HPCI system auxiliary oil pump was placed in pull to lock. This in turn resulted in the HPCI Pump becoming inoperable. HPCI remained available at all times. HPCI was returned to service at 1536 CDT on June 2, 2004. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." The cause of the event was poor maintenance of the HPCI steam supply valve resulting in it leaking excessively. This, in turn, caused frequent cycling of the HPCI exhaust line drain pot level switch which became misaligned and failed to operate. The level switch was re-aligned and HPCI was declared operable on June 2, 2004 at 1536 CDT. The HPCI steam supply valve will be refurbished during the next refueling. Preventive maintenance will be established to prevent excessive seat leakage in this valve.
2982004004 | Cooper Station | 08/30/2004 | 10/21/2004 | ML04301012 | <strong>Loss of Safety Function Due to Past Inoperabilities of High Pressure Coolant Injection System</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2003 and November 28, 2003 Cooper Nuclear Station experienced reactor scrams. On both occasions, the reactor vessel water level lowered to the set point causing an automatic start of the High Pressure Coolant Injection (HPCI) system. During reactor water level recovery and stabilization, the HPCI auxiliary oil pump was taken to pull-to-lock, disabling the automatic start function of HPCI. HPCI remained available at all times during these two events. The disabling of a single train safety system is reportable but was overlooked and not included in the respective licensee event reports for the reactor scrams. Two root causes were attributed to these conditions. 1) There was no hard card available for stopping HPCI injection following automatic initiation. 2) The method used for stopping HPCI injection including preventing injection, was performed from memory and had been practiced in the simulator. Corrective action will be to revise HPCI system Operating Procedures to provide hard card guidance for stopping HPCI injection. The revised hard card shall only direct placing the auxiliary tube oil pump control switch in pull-to-lock if the initiation signal cannot be reset, or as otherwise described in the Updated Safety Analysis Report. It must also stop injection as soon as possible by pressing the trip button. Conduct appropriate training to reinforce the new procedural guidance.
3012004001 | Point Beach 2 | 03/30/2004 | 05/21/2004 | ML04154038 | <strong>Safety Injection System Accumulator Operated With Fluid Level Out Of Specification High</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2004, at 11:27 AM, plant operators determined that the borated water level in the Point Beach Nuclear Plant (PBNP) Unit 2 Safety Injection system "A" accumulator (2T-34A) was greater than the level band allowed by Technical Specification (TS) 3.5.1, "Accumulators." This condition was discovered while conducting troubleshooting activities to resolve a discrepancy between the readings of the two "A" accumulator level detectors, 2LT-939 and 2LT- 938. An ultrasonic measurement indicated that the actual level in 2T-34A was above the top of the indicating range. With 2T-34A level greater than 100% (i.e. greater than 1136 ft3), TS LCO 3.5.1 was not met. TS 3.5.1, Action C.1 requires that an inoperable accumulator be restored to operable status within one hour. If that action cannot be completed, the action statement requires the unit to be placed in Mode 3 within an additional six hours. Since 2T-34A could not be recovered within the hour, a reactor load reduction was initiated at 12:15 PM. 2T-34A was recovered at 14:03 and the power reduction secured at 14:05. A RCE investigation determined that PBNP Unit 2 had operated since November 17, 2003, with 2T-34A overfilled, a condition prohibited by Technical Specifications. That condition was created due to an improper vent and fill of the level transmitters following a calibration of the level transmitter while the accumulator was drained for valve maintenance. In addition to restoring the 2T-34A level and pressure to within TS limits, corrective actions have or will include procedure revisions, reviews for extent of condition and staff training to improve understanding of the instrument loop. Based on the PBNP specific PRA modeling and an evaluation of the capability of the 2T-34A accumulator to complete its safety function in the as found condition, this event was identified as having a very low risk significance.
3012004002 | Point Beach 2 | 05/15/2004 | 07/12/2004 | ML04202037 | <strong>Concerns with Diver Safety Results In Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2004, a manual trip of the Point Beach Nuclear Plant (PBNP) Unit 2 was initiated when the control room was notified that a diver had become entangled in the intake structure for the circulating water (CW) system. While inspecting the intake structure for winter damage, the diver's tether, air and communication line became snagged. The diver's line tender, together with the assistance of a rescue diver, were unable to clear the lines. When communications with the diver were lost, the NMC diving liaison on the boat requested that the Unit 2 CW pumps be secured in order to facilitate removing the diver from the water. Securing the CW pumps requires that the reactor first be tripped. After the reactor trip and securing the CW pumps, both divers exited the water uninjured. Plant systems functioned as expected during the reactor trip transient, including the reactor protection and auxiliary feedwater systems. Since the circulating water system was secured, the main condensers were unavailable for decay heat removal. The steam generator atmospheric steam dump valves were used to remove decay heat. An incident investigation and root cause evaluation were conducted. The primary causes of this event were determined to be unclear and inconsistent communications and inadequate supervisory oversight. Process and procedural corrective actions are being completed. PBNP Unit 2 was returned to full load operations on May 20, 2004.
3012004003 | Point Beach 2 | 11/19/2004 | 01/14/2005 | ML04202037 | <strong>Reactor Shutdown Required by Containment Penetration TSAC 3.6.3.C</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2004, a pinhole steam leak was discovered inside containment on the body of valve 2MS-465D, the first-off low side root isolation valve for the Point Beach Nuclear Plant Unit 2 "A" steam generator steam line flow transmitter. The leak location could not be isolated from the main steam line. The affected portion of the main steam line is credited as a closed system boundary for containment penetration P-1, the"A" main steam line penetration. Accordingly, Technical Specification (TS) Condition 3.6.3.C, which is applicable to penetration flow paths with only one containment isolation valve and a closed system, was entered and Required Action C.1 was initiated. The required action for this condition is to isolate the affected penetration flow path with a completion time of 72 hours. The repair of the leak would require a shutdown and cooldown of Unit 2 and could not be accomplished within that 72 hour time frame; therefore, a reactor shutdown and cooldown was promptly initiated. This was considered to be a TS required shutdown and was reported in accordance with 10 CFR 50.72.(b)(2)(i). Unit 2 entered Mode 5 on November 21, 2004, and the valve body leak was repaired. Unit 2 returned to full power operation on November 25, 2004. The cause of the leak was determined to be either a material defect in the valve body or an improper welding process, which provided a stress riser that failed due to cyclic loading. An assessment of the safety significance of this event concluded that the impact of this event on the health and safety of the public was not significant.
3022004001 | Crystal River 3 | 03/24/2004 | 05/18/2004 | ML04147029 | <strong>Reactor Trip Caused By Failed Circuit Board In The Main Feedwater Integrated Control System</strong><br /><i>Abstract:&nbsp;</i>At 03:31, on March 24, 2004, Progress Energy Florida, Inc., (PEF) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. While in steady state operation, a large decrease in the reactor demand and Main Feedwater flow demand signals occurred within the Integrated Control System (ICS). The Main Feedwater pumps ran back until discharge pressure was less than steam generator pressure, at which time the Main Feedwater flow reduced to zero. Upon sensing less than 17 percent Main Feedwater flow, the Anticipated Transient Without Scram (ATWS) Mitigation System Actuation Circuitry (AMSAC) initiated a turbine trip and actuated the Emergency Feedwater System (EFW). The Reactor Protection System (RPS) sensed the turbine trip above 45 percent reactor power and initiated an anticipatory reactor trip. The cause for this event was age-related failure of the zener diodes in the +15 volt regulator circuit for a Bailey 820 Control Module in the Main Feedwater Integrated Control System. The circuit board was replaced. RPS and EFW valid actuations are reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported to the NRC by CR-3.
3022004002 | Crystal River 3 | 04/23/2004 | 06/21/2004 | ML04181050 | <strong>Emergency Diesel Generator Inoperable Due To Fuel Oil Header Outlet Check Valve Leaking Past Seat</strong><br /><i>Abstract:&nbsp;</i>At 12:37, on April 23, 2004, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. During performance of surveillance procedure SP-354A, "Monthly Functional Test of the Emergency Diesel Generator EGDG-1A," EGDG-1A did not start and achieve steady state voltage and frequency in less than or equal to 10 seconds from standby conditions upon receipt of a simulated Engineered Safeguards signal as required by Technical Specifications. The cause for this event was fuel oil header outlet check valve DFV-61 leaking by its seat due to foreign material lodged between the valve disk and seat. This condition allowed fuel oil to gradually drain back through the header outlet to the fuel oil tank, partially depleting the fuel header prime. The check valve was replaced. Based on engineering judgment, EGDG-1A was inoperable for a period of time longer than allowed by Technical Specifications. This condition is being reported under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported to the NRC by CR-3.
3022004003 | Crystal River 3 | 09/06/2004 | 10/29/2004 | ML04310053 | <strong>Reactor Trip And Emergency Feedwater Actuation Caused By 230 Kilovolt Switchyard/Transmission Faults</strong><br /><i>Abstract:&nbsp;</i>At 11:51, on September 6, 2004, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE 1 (POWER OPERATION) at 97 percent RATED THERMAL POWER. During Tropical Storm Frances, phase-to-ground faults occurred concurrently on a 230 kilovolt transmission line and a 230 kilovolt switchyard south bus breaker. Loss of power to the Startup transformer resulted in opening the reactor trip breakers, tripping of the reactor coolant pumps and main feedwater pumps, and loss of power to the Main Turbine Lube Oil System. A main turbine trip and subsequent actuation of the Reactor Protection System occurred. The Emergency Feedwater Initiation and Control System actuated to feed the Once Through Steam Generators. The transmission line fault was caused by mechanical failure of a carbon steel pin in a vertical string of insulators due to high wind conditions. The breaker fault was caused by flash over due to contamination from wind and salt spray. The insulator string was replaced. The breaker was tested, inspected, washed down and returned to service. Actuation of the Reactor Protection System and Emergency Feedwater System are reportable to the NRC. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported.
3022004004 | Crystal River 3 | 09/24/2004 | 11/22/2004 | ML04334022 | <strong>NUREG-1022 Clarification Required Reporting of Previous Steam Generator Tube Inspection Results</strong><br /><i>Abstract:&nbsp;</i>At 14:00, on September 24, 2004, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. The NRC published a Notice of Clarification to Steam Generator Tube Integrity Event Reporting Guidelines in NUREG-1022, "Event Reporting Guidelines 10 CFR 50.72 and 10 CFR 50.73." The Notice of Clarification revised the guidelines used to determine reporting of steam generator inspection results. The NRC directed licensees to consider the results of the previous steam generator tube inspections, including the structural integrity criteria and leakage criteria, against the new reporting guidelines. Crystal River Unit 3 determined that the as-found steam generator projected leakage value for Steam Line Break (SLB), which exceeded the leak rate limit for Refueling Outage 13(13R), is reportable per the revised NUREG-1022 guidance, under 10 CFR 50.73(a)(2)(ii)(A), as a condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. The cause for exceeding the leakage criterion was finding new indications not accounted for in the previous cycle Operational Assessment, and human error in the leakage calculation. Repairs performed during 13R reduced the SLB projected leakage to well below the limit prior to plant startup. This condition does not represent a reduction in the public health and safety. No similar occurrences have been previously reported.
3052004001 | Kewaunee | 01/16/2004 | 09/14/2004 | ML04266012 | <strong>Blocked Lube Oil Coolers to Safety Injection Pumps Force Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2004, with the plant operating at 100% power, the discovery of significant biofouling (blockage by biological matter) of both trains of Safety Injection (SI) Pump lube oil coolers resulted in initiating a Technical Specifications (TS) forced shutdown of the Kewaunee Nuclear Power Plant (KNPP). KNPP was taken offline at approximately 0600 on Friday January 16, 2004. During maintenance and inspection activities on SI pump A on January 15, 2004, the lube oil cooler was found to be biofouled. After the cooler was cleaned similar conditions were found in SI pump B. Visible flow was occurring in only 3 of the 20 tubes in the B cooler inlet pass. Even though the coolers were cleaned and operational, the decision was made to shut down the plant, based on an inability to predict how long it would take for fouling to occur. Service water (SW) continuously flowed into the coolers through a 3/4-inch pipe into the top half of the inlet / outlet chamber. The small tube size, coupled with the size of the tubesheet surface between tubes, resulted in lake weed accumulating against the tubesheet. The biofouling phenomenon existed on the top half of the inlet/outlet tubesheet and the bottom half of the return end tubesheet. Historical experience with the coolers demonstrates that the condition was not new. The root cause of the lube oil cooler becoming plugged was an inadequate cooler design for the conditions and foreign materials that Lake Michigan could introduce into the system. The original design of the SI lube oil cooler was not sufficient given the SW flow velocity, tube size and system configuration. The lube oil coolers have been replaced with a different design. Subsequent extensive calculations and analyses were performed relative to past operability of the SI pumps. It was concluded that the lake weed degradation of the tube oil coolers would not have prevented the ability of the SI pumps to perform all required safety functions. This event is not considered a safety system functional failure.
3052004002 | Kewaunee | 07/21/2004 | 09/20/2004 | ML04272036 | <strong>Missed Technical Specification Surveillance for Leak Testing In-Core Detectors Prior to Use or Transfer, Due t o Inadequate Procedural Guidance EVENT DATE (5) LER NUMBER (6) REPORT DATE</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2004, while the plant was operating at full power, Nuclear Management Company (NMC) personnel determined that the Kewaunee Nuclear Power Plant had missed a surveillance required by Technical Specifications (TS). Specifically, the requirements of TS, Sections 4.13.b and e, were not met. Section 4.13, "Radioactive Materials Sources," in part, requires sources be leak tested in accordance with TS, and sources in storage, not being used and exempt from periodic leak testing shall have a current leak test prior to use or transfer to another licensee . Contrary to TS and based on review of plant records from 1973 through 2004, leak tests were not performed on 13 new in-Core detector sources prior to being put into use, or shipped to another licensed facility. The cause for the missed surveillance was inadequate procedural guidance providing instructions to have required leak tests performed on in-core detectors. Procedure changes to the applicable procedures have been initiated to ensure required leak tests are performed in the future. NMC personnel will also contact licensees that received any in-core detectors that had not been leak tested to determine the scope of any additional corrective action needed to ensure regulatory requirement compliance. The safety significance of failing to complete leak tests required by TS is minimal. Historical radiological survey data, which includes the areas where the detectors may have been stored, or placed for processing, show no evidence of byproduct material expected from a leaking in-core detector.
3052004003 | Kewaunee | 08/12/2004 | 02/22/2005 | ML05063025 | <strong>Control Room Boundary Door Found Ajar - Accident Analysis Assumptions Impacted - Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On 8/12/2004, while the plant was operating at full power, Kewaunee Nuclear Power Plant (KNPP) on-shift personnel discovered a control room emergency zone (CREZ) barrier door not fully closed. The position of the door had an adverse affect on the control room post-accident habitability analysis assumption for air in-leakage to the control room envelope. This, in-turn, was judged to have an adverse affect on the Technical Specifications (TS) operability requirements for the Control Room Post-Accident Recirculation (CRPAR) system. Consequently, with the door less than fully closed, the CRPAR system was considered not capable of fulfilling its post-accident mitigation function to ensure a habitable control room under post-accident conditions. The as-found condition was immediately corrected, the control room envelope was fully restored, and the CRPAR system was returned to operable status within the TS time limitations. The direct cause of the door not being closed was the failure of plant personnel to ensure the door was closed following maintenance that required moving material through the open doorway. The underlying causes of the failure are deficiencies in the KNPP overall barrier control program. Program control guidance is limited to a single barrier control procedure, and for barrier control and identification purposes, labels and warnings are not sufficient to ensure barriers are easily recognizable for all their intended functions. The lack of programmatic controls contributed to plant personnel lack of awareness in understanding barrier control functions and their importance. This event is an example of a safety system functional failure. The safety significance of this event is minimal. The primary contributor to the control room habitability analysis and control room personnel exposure is leakage of radiological contaminants from the containment building. The most recent leak test data shows the containment leakage being only a fraction of the values assumed in the analysis.
3052004004 | Kewaunee | 11/18/2004 | 01/17/2005 | ML05025021 | <strong>Procedural Deficiency Results in Automatic Containment Ventilation Isolation Being Disabled Contrary to Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 18, 2004 at approximately 1630 hours during Kewaunee Nuclear Power Plant (KNPP) refueling shutdown (KR27), control room personnel were performing a refueling checklist and discovered that R-12 (Containment Radiation Monitor) would not automatically isolate Reactor Building Ventilation. Further investigation revealed that performance of Surveillance Procedure SP-55-155C, "Engineered Safeguards Features Prestartup Logic Test," had been initiated at 0750 hours. SP-55-155C placed the Safeguards Train A into test mode at 0803 hours and Safeguards Train B into test mode at 0804 hours, thereby defeating Safeguards Train A and Train B automatic signals to containment ventilation isolation. Technical Specifications TS 3.8.a.8 requires that automatic containment ventilation isolation be operable during refueling operations. When this event was discovered, no reactivity manipulations were occurring and further manipulations were restricted until automatic containment ventilation isolation capability could be restored. The cause of the event was attributed to a lack of adequate guidance in SP-55-155C. In the Operational Consideration section of this procedure, affected Technical Specification TS 3.8.a.8 was not listed. Additionally, the Initial Conditions section of the procedure did not delineate that this procedure could not be performed when refueling containment integrity was required. Procedure changes have been initiated to revise SP-55-155C. In addition, a corrective action has been initiated to ensure that performance of SP-55-155C is properly coordinated with Refueling Containment Integrity requirements. The safety significance of this event was minimal. Radiation Monitors R-12 and R-21 continued to provide indication of radiation levels in the containment atmosphere. Both Radiation Monitors would have alarmed in the control room had an event occurred which required an automatic containment ventilation isolation. Manual isolation of containment ventilation remained available at all times. This event is not a safety system functional failure.
3052004005 | Kewaunee | 11/26/2004 | 01/25/2005 | ML05033039 | <strong>Safety Injection Accumulator Isolation Valve Position During Heatup Violates Technical Specifications-Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>On November 26, 2004, during plant heatup and pressurization, the Reactor Coolant System was pressurized to greater than 1000 psig with the Safety Injection Accumulator Isolation Valves (Sl-20A and Sl-20B) closed, and their actuator power supply breakers tagged off contrary to Technical Specifications. Upon discovery, prompt actions were initiated to open the isolation valves and lock their breakers in the "off" position. An investigation found that an error trap existed in a critical step of Operating Procedure N-0-01, "Plant Startup from Cold Shutdown to Hot Shutdown Conditions". The step stated to realign the safety injection system "at 1000 psig." No precaution or limitation was provided in the procedure to warn the operator against exceeding 1000 psig. This event was determined to have low safety significance. The isolation valves were in the incorrect position for approximately 20 minutes. Due to the reduced reactor coolant system pressure at the time, the primary event of concern, a large break loss of coolant accident was unlikely to occur. In addition, the event took place 48 days after reactor shutdown for the preceding refueling outage, resulting in low decay heat levels at the time. Corrective actions have been taken to prevent reoccurrence by revising operating procedure N-0-01 prestartup checklist procedure N-SI-33-CL. This event is reportable as a Safety System Functional Failure.
3062004001 | Prairie Island 2 | 11/17/2004 | 03/21/2005 | ML05089031 | <strong>Unit 2 Shutdown Required by Technical Specifications Due to Two Trains of Containment Cooling Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2004, Prairie Island Nuclear Generating Plant (PINGP) Staff entered Unit 2 containment to investigate suspected leakage of the 23 containment fan coil unit (CFCU). The 23 CFCU was suspected to be leaking based on control room indication of condensate pot level and Sump A run times. The investigation identified two leaks on the 23 CFCU and also identified one leak on the 22 CFCU. The leaking CFCUs were isolated. Since the leaks affected one of two CFCUs in each of the two trains of containment cooling, and those CFCUs were isolated, both trains of containment cooling were declared inoperable and PINGP Technical Specification Limiting Condition of Operability (LCO) 3.0.3 was entered. The leaks could not be repaired in time to exit LCO 3.0.3 before a plant shutdown was required and a plant shutdown was initiated and completed. Repair of the leaks on the 22 and 23 CFCUs was completed on November 18, 2004 and Unit 2 returned to power operation on November 19, 2004.
3112004001 | Salem 2 | 02/12/2004 | 04/07/2004 | ML04111092 | <strong>Failure to Take Proper Compensatory Containment Air Samples</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2004, the Containment Air Particulate Detector (APD) was declared inoperable and Technical Specification (TS) Action Statements 3.3.3.1 Action 24 and 3.4.7.1 were entered. TS 3.4.7.1 requires grab samples of the containment atmosphere at least once per 24 hours with the gaseous and/or particulate radioactivity monitoring system inoperable. On February 13, 2004, when the required compensatory samples were being collected at approximately 2155 hours, it was identified that containment isolation valve 2VC12 had been tagged closed. Valve 2VC12 was tagged closed at approximately 1130 on February 12, 2004. With this valve closed, representative samples of the containment atmosphere could not be obtained. Samples had been collected with the valve closed on February 12, 2004 at 2120 hours and February 13, 2004 at 0925 hours. The last sample collected with valve 2VC12 open was on February 12, 2004 at 0945 hours. Therefore, a period of approximately 36 hours elapsed between representative samples of the containment atmosphere being obtained contrary to TS requirements. The cause of this event is attributed to personnel error by the Chemistry Technicians that performed the sampling activities on February 12 and 13, 2004. Chemistry personnel involved with this event have been held accountable in accordance with PSEG policies and procedural compliance was reinforced with Salem Chemistry personnel. This report is being made in accordance with 10CFR50.73(a)(2)(i)(B).
3112004002 | Salem 2 | 03/16/2004 | 05/17/2004 | ML04147029 | <strong>Failure To Comply With Technical Specifications During Reactor Protection Instrument Calibration</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2004, at 0830 hours, Loop 21 of OTDT (Over-Temperature Delta-Temperature) Tavg (T-average) calibration was completed. On March 17, 2004, while performing the channel calibration for Loop 22 OTDT, it was discovered that Loop 21 OTDT Pressurizer Pressure channel calibration had not been performed in conjunction with the OTDT channel calibration. Based on this, the OTDT 21 loop setpoint was non-conservative and the Loop 21 OTDT channel was inoperable. OTDT channel 22 calibration was completed satisfactorily on March 17, 2004, and returned to service. The 21 OTDT channel was then correctly calibrated and returned to service. During the period of time between the start of the channel calibration for Loop 21 OTDT and its satisfactory completion, Loop 21 was inoperable. Technical Specification 3.3.1.1, table 3.3-1, item 7, Action 6, requires the inoperable channel to be placed in the tripped condition within six hours. This action was not complied with. When Loop 22 became inoperable, with Loop 21 still inoperable, Technical Specification 3.0.3 should have been entered. This was not complied with because it was not recognized that Loop 21 was inoperable. Both of these issues are Technical Specification prohibited conditions and are reportable under 10 CFR 50.73(a)(2)(i)(B). The cause of this event was attributed to lack of adequate process controls for calibration. Procedure changes will be made to correct the process weakness.
3112004003 | Salem 2, Salem 1 | 04/12/2004 | 06/11/2004 | ML04174071 | <strong>Salem Unit 2 Control Room Emergency Air Conditioning System Unable to Mitigate The Consequences of an Accident</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2004, at approximately 10:33, the Control Room Emergency Air Conditioning System was placed in a condition where it did not comply with its design basis for post LOCA mitigation. During maintenance of the Salem Unit 1 Solid State Protection System, a safety injection signal was generated. As a result of the invalid safety injection signal on Unit 1, the Control Room Emergency Air Conditioning System actuated to its accident pressurized mode alignment, in which the Salem Unit 1 emergency intake air dampers were isolated and the Salem Unit 2 dampers opened. In this configuration, Salem Unit 2 was in a condition where it did not comply with its design basis for post LOCA mitigation. The Salem dose analysis performed to meet the requirements of the General Design Criterion (GDC) 19 states that with only one train of the Control Room Emergency Air Conditioning System available at the start of a design basis LOCA, the make up air supply to pressurize the control room envelope must be supplied by the non-accident Unit's emergency outside air intake. The apparent cause of this event was a defective universal logic card in the Solid State Protection System (SSPS). When this card was moved from one position to another in the SSPS cabinet, a safety injection signal from Unit 1 Train 'B' occurred. Corrective actions taken were: (1) The defective card was replaced, and (2) A full functional test procedure on Train B was performed satisfactory. This condition is reportable under 10 CFR 50.73(a)(2)(v)(D).
3112004004 | Salem 2 | 05/21/2004 | 07/20/2004 | ML04210039 | <strong>Technical Specification Required Plant Shutdown Following Loss of 2B 230-Volt Bus</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2004, at 1147, a fault on a Salem Unit 2 4160/230V transformer caused a 4kV load breaker to trip open on instantaneous over-current, resulting in the loss of the 2B 460V and 230V Vital buses. A Service Water isolation valve supplying the Turbine Generator lost the ability to isolate the Turbine loads. This resulted in the entry into Salem Unit 2 Technical Specification (TS) 3.6.1.1, 'Primary Containment Integrity', Limiting Condition for Operation (LCO) to restore in 1 hour or be in Hot Shutdown in 6 hours. Operators were unable to restore the valve to operable within one hour and therefore commenced a controlled shutdown. All plant systems responded as expected to the conditions. A failure analysis of the event indicates that the root cause of the transformer fault originated in the 2nd phase of the 3-phase transformer due to high voltage winding insulation breakdown caused during initial fabrication of the transformer. Corrective actions included replacing the 2B 4160/230 Volt transformer. This event is reportable per the requirements of 10 CFR 50.73(a)(2)(i)(A), Plant Shutdown Required by Technical Specifications.
3112004005 | Salem 2 | 05/27/2004 | 07/26/2004 | ML04216029 | <strong>Auto Safety Injection Signal Not Unblocked Prior to Mode Change From 5 to 4</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2004, the Automatic Safety Injection (Auto SI) Block for Salem Unit 2 was not removed prior to entering Mode 4. The Auto SI logic trains are directed by procedure and Technical Specification (TS) 3.3.2.1 to be operable (unblocked) prior to transitioning from the Cold Shutdown (Mode 5) to Hot Shutdown (Mode 4). Mode 4 was entered at approximately 0140 hours on May 27, 2004. At approximately 0630, Operations personnel observed that the Automatic Safety Injection (Auto SI) blue light was illuminated on Reactor Protection Logic Panel, indicating that Automatic Safety Injection (SI) was blocked. TS 3.0.3 was entered since both trains of SI were not operable. Actions were immediately taken to reinstate (unblock) Auto SI. TS 3.0.3 was exited at 0635 after the Auto SI interlock had been re-established. The cause of the occurrence was the lack of formal independent verification to ensure TS requirements are met prior to changing plant modes. A contributing cause was the CRS who signed off the step of the IOP misread the step and initialed for Automatic SI Block being ACTIVE, contrary to procedure requirements. An Operations department stand-down (i.e., an interactive discussion between Operation's management team and the shift operators) was conducted to discuss this event. This event is reportable per the requirements of 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
3112004006 | Salem 2 | 07/13/2004 | 03/14/2005 | ML05081042 | <strong>Salem Unit 2 Reactor Trip Due to a Malfunction of a Main Feedwater Regulating Valve (21BF19)</strong><br /><i>Abstract:&nbsp;</i>On Tuesday July 13, Salem Unit 2 tripped due to a malfunction of the 21BF19 valve, while Maintenance/l&C personnel were in the process of testing the Digital Feedwater System. Specifically, the Steam Generator Feed Pump differential pressure input to the feedwater system (PT508) was being tested in accordance with plant procedures. Initially, all the feedwater regulating valves (21-24BF19s) responded as expected. At approximately 1300 hours, the 21BF19 valve stopped responding. The Licensed Nuclear Control Operator placed the controller for the 21BF19 valve in manual and attempted to open the valve. The valve did not respond and the reactor automatically tripped on low steam generator level within approximately 45 seconds of the valve going to 31% open. The failure of the 21BF19 valve positioner (Bailey model number AV2320200) was due to the failure of the I/P that resulted in a sudden drop from 60% to 30% valve position. Some of the corrective actions taken were: (1) The 21BF19 positioner was replaced, (2) The digital feed QAM card was replaced, (3) The bezel control for the 21BF19 was removed and the contacts cleaned, and (4) An air operated valve diagnostic test was satisfactorily performed. This report is being made in accordance with10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
3112004007 | Salem 2 | 07/15/2004 | 03/14/2005 | ML05081042 | <strong>Salem Unit 2 Manual Reactor Trip Due to a Malfunction of a Main Feedwater Regulating Valve (23BF19)</strong><br /><i>Abstract:&nbsp;</i>On Thursday July 15, 2004, Salem Unit 2 was manually tripped while returning to power following the July 13, 2004 automatic reactor trip (LER 311/2004-006, dated September 13, 2004). During start-up, at approximately 8% power, feedwater flow was automatically transitioning from the feedwater bypass valve (BF40) to the main feedwater regulating valves (BF19). As the demand for the main feedwater regulating valves increased the demand for the BF40s decreased, as designed. However, the actual position of the number 23 loop main feedwater regulating valve (23BF19) did not move in response to the increasing demand. As the level in 23 Steam Generator continued to decrease due to the lack of response from 23BF19, the control room operator manually initiated a reactor trip with 23 Steam Generator level at approximately 16%. The failure of the valve was determined to be a positioner failure (Bailey model number AV2320200) due to sticking of the positioner pilot stem because of poor/ineffective vendor quality control allowing uneven surface finishing and dimensions that cause sticking of the positioner pilot stem. Some of the corrective actions taken were: (1) The 23BF19 positioner, as well as all Unit 2 feedwater regulating valves (21, 22, and 24BF19s), were replaced and calibrated under direction of the manufacturer, (2) The overshoot condition for the Unit 2 BF19s positioners was corrected prior to Unit restart, (3) A rollout was performed with appropriate PSEG personnel with specific recommendations to test each positioner pilot spool. Some longer term corrective actions being considered include: (1) Replacing the positioners with a different design and (2) Installing in line air filters (in parallel) at the redundant air panels for the BF19s. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
3112004008 | Salem 2 | 09/09/2004 | 11/08/2004 | ML04322038 | <strong>Unplanned Reactor Trip Due to Main Generator Exciter Brush Failure</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2004 at 0106 hours Salem Unit 2 automatically tripped off line as a result of a Main Turbine Trip which initiated a Reactor Trip. The turbine tripped on Generator Differential and Loss of Field. All control rods fully inserted and all safety related systems were available and functioned as designed. The direct cause of this event was exciter brush/collector flash over. The root causes of this event were that the Generator/Exciter vendors recommended inspections were not implemented and the lessons learned from a 1993 Hope Creek brush failure were not applied to Salem Unit 2. (Salem Unit 1 is a different Generator/Exciter). Corrective actions taken include replacing the Salem Unit 2 exciter brushes, repair to the collector ring damaged in the brush failure event, incorporation of vend or recommended inspections and guidance into plant procedures. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B), specifically (B)(1)reactor trip.
3112004009 | Salem 2 | 10/13/2004 | 12/13/2004 | ML04357045 | <strong>ECCS Leakage Outside Containment Exceeds Dose Analysis Limits (23 Charging Pump)</strong><br /><i>Abstract:&nbsp;</i>This event is reportable in accordance with 10CFR50.73(a)(2)(v), “any event or condition that could have prevented the fulfillment of the safety function of structures or system that are needed to:....(C) control the release of radioactive material; or (D) mitigate the consequences of an accident." On October 13, 2004, at approximately 14:06 the 23 Positive Displacement Charging Pump (PDP) was removed from service to perform scheduled maintenance. The maintenance involved the removal of the suction stabilizer and placing a flange on the suction side piping where the suction stabilizer was removed. Following the tagging evolution, operations personnel noted a 0.55 gpm (125,000 cc/hr) leak back through the suction flange for the PDP. The leakage exceeded the administrative limit (2200 cc/hr) and 3800 cc/hr limit stated in the Final Safety Analysis Report (FSAR) Section 6.3.2.11 for emergency core cooling system (ECCS) leakage outside the containment. Because this leakage could not have been isolated from the recirculation flow path during the recirculation phase of the design basis LOCA, the assumptions made in the dose analysis calculations were violated. The apparent cause for the excessive leakage has been determined to be the failure of the 2CV64 to provide full isolation of the pump. Immediate actions were taken to restore system integrity by removing the blind flange and re-installing the suction stabilizer, thus containing any leakage within the system pressure boundary. Additionally, a corrective action work order has been initiated to repair the discharge valve (2CV64) during the next outage.
3132004001 | Arkansas 1 | 04/29/2004 | 08/16/2004 | ML04238035 | <strong>Operation Prohibited by Technical Specifications due to an Undetected Inoperable Channel of Required Source Range Nuclear Instrumentation During Core Alterations Caused by a Signal Processing Unit Circuit Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>At 2251 CDT on April 29, 2004, with Arkansas Nuclear One, Unit 1 (ANO-1) in Mode 6 for refueling outage 1R18, operators discovered that one of two redundant trains of source range neutron flux monitoring instrumentation was inoperable. ANO-1 technical specifications (TS) require one source range monitor to be operable in Mode 6 and one additional monitor to be operable during core alterations. A review of plant computer historical data determined that the indication for the green train source range nuclear instrument failed at 1052 on April 29, 2004, but was not immediately detected because the count rates indicated on both channels were at the extreme low end of the scale. At the time of the failure, core off-load activities were in progress and continued until all fuel assemblies were removed from the reactor core at 2159. Therefore, for approximately11 hours the unit was in a condition prohibited by TS due to the undetected in operability of one of the two required source range channels. The redundant source range channel remained operable and unaffected by this condition. The cause of this event was determined to be an undetected failure of the signal processor drawer circuit breaker Following replacement of the failed components and post maintenance testing, the source range channel was declared operable.
3132004002 | Arkansas 1 | 04/30/2004 | 06/29/2004 | ML04183036 | <strong>Operation Prohibited by Technical Specifications due to Degradation of a Principal Safety Barrier Caused by Primary Water Stress Corrosion Cracking of a Control Rod Drive Mechanism Nozzle</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2004, following shutdown for a scheduled refueling outage, inspections of the reactor vessel head and associated penetration nozzles revealed two axial indications on the- outside diameter of Control Rod Drive Mechanism Nozzle 61. The cause of the cracks was determined to have been primary water stress corrosion cracking. The penetration was repaired before the unit was returned to service. No evidence of a leak path was identified. A safety assessment concluded that the cracks did not pose any risk for catastrophic failure of the nozzle.
3152004001 | Cook 1, Cook 2 | 07/19/2003 | 06/28/2004 | ML04189037 | <strong>Failure To Comply With Technical Specification 3.7.5.1, Control Room Emergency Ventilation System</strong><br /><i>Abstract:&nbsp;</i>This Licensee Event Report reports an historical failure to comply with Unit 1 and 2 Technical Specification (TS) 3.7.5.1, Control Room Emergency Ventilation System. The noncompliance was identified in 2004 during the conduct of investigation into the cause of a very slow decrease in volume from the Unit 2 refueling water storage tank (RWST). On May 4, 2004, Indiana Michigan Power Company determined that the combined leakage from valve 2-SI-206, south safety injection (SI) pump discharge valve manual isolation pressure seal ring, and seat leakage past the drain valves for the Unit 2 south SI pump casing was greater than that assumed in the safety analysis for Unit 1 and 2 TS 3.7.5.1. This condition existed for 66 hours and 43 minutes during the period from 1337 hours on July 18, 2003, through 0820 hours on July 21, 2003. Corrective actions included the repair of the leaking components, the conduct of an extent of condition review, and the verification that the component repairs did stop the loss of volume from the RWST.
3162004001 | Cook 2 | 03/29/2004 | 05/26/2004 | ML04156034 | <strong>Automatic Reactor Trip Due to RPS Actuation, While Manipulating Reactor Trip Bypass Breaker</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2004, at 1404 hours, Unit 2 received an automatic actuation of the Reactor Protection System (RPS). The RPS actuation occurred while an operator was attempting to rack out the train A Reactor Trip Bypass Breaker (RTBB) during restoration from Solid State Protection System (SSPS ) testing. The direct cause of the event was human error. The operator who performed the breaker manipulation incorrectly inserted the breaker racking bar, causing a momentary ground of one phase of the rod control motor-generator set 260 VAC output. This de-energized the stationary gripper coils for multiple control rods, causing them to drop into the core, resulting in a Power Range Nuclear Instrument Hi-Negative rate RPS actuation. The Auxiliary Feedwater (AFW) System automatically started and functioned as designed. The reactor shutdown and automatic start of the AFW System was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) respectively (EN #40622). Corrective actions included inspection and repair of the RTBB and associated indicator circuits, and verification of operator proficiency with breaker operation prior to manipulation of an RTBB in the plant.
3162004002 | Cook 2 | 04/08/2004 | 06/07/2004 | ML04167053 | <strong>Unplanned Automatic Reactor Protection System Actuation Due to Feedwater Transient During a Power Reduction</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2004 at approximately 2215 Eastern Standard Time, Unit 2 reactor experienced an unplanned automatic reactor protection system (RPS) actuation, resulting in a plant trip from 48 percent power. Prior to the trip, Unit 2 was in the process of lowering power from 82 percent to 8 percent power level. The operating main feedwater pump was being controlled manually via the differential pressure (DP) controller. Failure to manually control DP within the prescribed values, caused all four feedwater regulating valves (FRVs) to begin modulating excessively. All four FRVs were placed in manual control to mitigate the feedwater flow oscillations. However, rising water level in number 24 Steam Generator reached the high level trip setpoint causing an automatic turbine trip which caused the automatic RPS actuation. Plant equipment responded as expected, including the start of the auxiliary feedwater system, except the main generator output breakers failing to open and a condensate leak developing in the main turbine condenser hotwell area. The main generator output breakers were manually opened in accordance with the reactor trip response procedure and the condensate leak was stopped by securing pumps in accordance with plant procedures. The root causes of the event were determined to be inadequate manual main feedwater DP control and inadequate communications between the control room operators and other shift personnel. Corrective actions include redefining and reinforcing standards for the conduct of operations and personnel action taken in accordance with appropriate performance management policies for the control room personnel involved. This event was reported in accordance with 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.72 (b)(3)(iv)(A).
3162004003 | Cook 2, Cook 1 | 10/09/2004 | 12/08/2004 | ML04345030 | <strong>Failure To Comply With Containment Ventilation Operability Requirements Specified In Technical Specifications 3.0.4, 3.9.4, and 3.9.9</strong><br /><i>Abstract:&nbsp;</i>At 1330 hours, on October 9, 2004, Indiana Michigan Power Company (I&M) established an equipment clearance in Unit 2 to facilitate calibration of time delay relays. As part of the clearance, breakers supplying power to both trains of the solid state protection system (SSPS) outputs were opened. This disabled the automatic actuation of both trains of the containment ventilation isolation (CVI) and manual phase "A" containment isolation. At 1441 hours, on October 9, 2004, movement of fuel from the reactor vessel to the spent fuel pool commenced. At this point, the requirements of Technical Specifications (TS) 3.9.9, 3.9.4, and 3.0.4 were not met. Late in the day on October 10, 2004, the clearance was lifted and CVI returned to operable status and compliance with TS 3.9.9, 3.9.4, and 3.0.4 was restored. The causes of this event were the failure to identify and establish appropriate logic sequence/ties for the outage schedule and the failure of the clearance review to identify the adverse impact of the clearance on the plant. Corrective actions included the establishment of enhanced controls for operations shift management activities and clearance order controls. I&M review identified two similar historical events for Unit 1. The similar historical Unit 1 events occurred on: May 11, 2002, through May 13, 2002, and October 26, 2003, through October 30, 2003.
3162004004 | Cook 2 | 11/06/2004 | 01/13/2005 | ML05018026 | <strong>Failure to Comply with Containment Integrity Requirements Specified in Technical Specifications 3.0.4, 3.6.1.1, 3.6.1.2 and 3.6.3.1</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2004, two small drain valves required to be closed for containment integrity were found open at Indiana Michigan Power Company, Donald C. Cook Nuclear Plant, Unit 2. The valves are configured between the redundant containment isolation valves in the non-essential service water (NESW) supply and NESW return lines supporting the containment instrument room east ventilation unit. These valves are required to be closed during Modes 1-4 to meet containment integrity and automatic containment isolation requirements. Subsequent investigation identified that the drain valves were open between the time Unit 2 entered MODE 4 on November 6, 2004, and the time the valves were closed on November 14, 2004. Following entry into MODE 4, the limiting condition for operation requirements of Technical Specifications (TS) 3.6.1.1, 3.6.1.2, and 3.6.3.1 were not met. With plant conditions not consistent with the requirements of TS 3.6.1.1, 3.6.1.2, and 3.6.3.1, specification 3.0.4 was also not met when the applicability conditions for those specifications were entered (i.e., MODE change) without satisfying the provisions in TS 3.0.4.a, 3.0.4.b, or 3.0.4.c. The inboard containment isolation valves and drain valves were closed following identification of the condition, restoring compliance with TS 3.6.1.1, 3.6.1.2 and 3.6.3.1. There were no equipment failures contributing directly to this event. The root cause is failure to have a comprehensive process to provide positive control of containment integrity or containment closure through all MODEs of operation, and inadequate reviews of active clearances prior to MODE change. The corrective actions include procedure changes to assure continuity of configuration control and tracking in all MODEs and adding additional direction in procedures for performing the MODE change clearance reviews.
3172004001 | Calvert Cliffs 1 | 03/20/2004 | 05/18/2004 | ML04145050 | <strong>Reactor Trip During Scheduled Maintenance</strong><br /><i>Abstract:&nbsp;</i>At 13:40 on March 20, 2004, Calvert Cliffs Unit 1 tripped from 100 percent power after Bus 1Y09 was grounded during scheduled maintenance. While replacing a chart recorder in a Control Room cabinet, a power lead feeding the recorder became pinched between the recorder and its case. The insulation on one of the power leads was cut, exposing the live power lead, and a short to case was experienced. This resulted in a loss of 11 Digital Feedwater Automatic Bus Transfer bus which in turn resulted in the deenergization of the 11 Main and 12 Backup Central Processing Units for the digital feedwater system. Mechanical binding of the 11 Feedwater Regulating Valve positioner selector solenoid valve resulted in a loss of signal to the 11 Feedwater Regulating Valve, which immediately began closing. The 11 Steam Generator water level lowered quickly, resulting in an automatic plant trip. The root cause of the trip lies in Human Performance in the area of work practices and design control. Corrective actions include procedure changes to improve risk management of maintenance, on-line testing of components, and monitoring plans for trip sensitive components. Unit I was restarted and paralleled to the grid on March 22, 2004 at 01:03.
3172004002 | Calvert Cliffs 1 | 01/22/2004 | 11/29/2004 | ML04338001 | <strong>Vital Bus Inoperable Due to Scaffold Installation</strong><br /><i>Abstract:&nbsp;</i>On January 14, 2004, with Unit 1 operating at 100 percent power, contrary to Calvert Cliffs Nuclear Power Plant administrative procedure for scaffold control, an unbraced scaffold was installed within 12 inches of safety-related equipment (14A 480V AC load center). The scaffold was not sufficiently braced to preclude impact with the 14A 480V AC load center cooling fins during a Safe Shutdown Earthquake. The scaffold's close proximity to 14A 480V AC load center went undetected for nine days thus causing the load center to be inoperable while the scaffold was in place. This nine day duration exceeded the Limiting Condition for Operation required Completion Time of two hours for Technical Specification 3.8.9.B, "One or more AC vital subsystem(s) inoperable." The initial assessment (March 16, 2004), concluded the event did not meet reporting criteria. On September 28, 2004, the reportability determination was reviewed and determined that the event was reportable. The root cause of this event is attributed to human error. Subsequent corrective actions included immediate communication of the event with scaffold building teams involved.
3182004001 | Calvert Cliffs 2 | 01/23/2004 | 03/23/2004 | ML04086043 | <strong>Reactor Trip Due to Low Steam Generator Water Level After Feed Pump Trip</strong><br /><i>Abstract:&nbsp;</i>At 15:26 on January 23, 2004, Calvert Cliffs Unit 2 tripped from 100 percent power, initiated by the Reactor Protective System due to low steam generator water level caused by an erroneous over speed trip signal on the steam generator feed pump. The erroneous trip signal occurred because of a degraded digital speed monitor supply voltage caused by corrosion of an inline fuse and the fuse holder. The turbine bypass valves and atmospheric dump valves opened as designed, but the quick-open signal did not clear due to the failure of a relay in the reactor regulating circuit. The open valves resulted in over-cooling of the Reactor Coolant System, a Steam Generator Isolation Signal, and a Safety Injection Actuation Signal causing a loss of normal heat removal. During the recovery, a large insurge of subcooled water cooled the pressurizer, lowering reactor coolant pressure to produce a second Safety Injection Actuation Signal. The corroded fuse, fuse holder, and failed relay were replaced. Operations staff was briefed on the effect of a large insurge of water on reactor coolant pressure, and Unit 2 was restarted and paralleled to the grid on January 25, 2004 at 21:53.
3212004001 | Hatch 1 | 02/03/2004 | 03/30/2004 | ML04092012 | <strong>Residual Heat Removal Service Water Pump 1C Inoperable For Failure To Meet NPSH Requirements</strong><br /><i>Abstract:&nbsp;</i>On 2/03/2004 at 1400 ET, Unit 1 was in the Run mode at a power level of approximately 2511 CMWT (91 percent rated thermal power). At that time, an evaluation revealed that the Net Positive Suction Head requirements (NPSHr) for the 1C Residual Heat Removal Service Water (RHRSW) pump that had been in service from 12/20/2002 until 11/17/2003 were not met from 9/14/2003 until Operations removed the 1C RHRSW pump for maintenance on 11/17/2003 at 0325 ET. This evaluation concluded that the 1C RHRSW pump could not meet its NPSHr with the river level below approximately 65.9 feet. River level was below 65.9 ft. from 9/14/2003 to 11/17/2003. The 1C RHRSW pump was replaced and the operability test completed on 12/09/2003. The duration of this condition exceeded the 30 days allowed by the plant's Technical Specifications 3.7.1 Condition A for a single RHRSW pump to be inoperable. The Residual Heat Removal Service Water pumps are used in the long-term containment heat removal mode. This event was caused by inadequate vendor testing to certify that a pump modification would continue to meet the purchase specifications requirements for NPSHr. On 12/09/2003 the 1C RHRSW pump was replaced with a "composite pump" and successfully tested. Additional plant testing has determined that all of the other installed RHRSW pumps on both Unit 1 and Unit 2 are acceptable for river levels down to 61.8 feet. Operating guidance has been established to perform additional RHRSW pump testing for all RHRSW pumps based on specific river levels.
3212004002 | Hatch 1 | 02/24/2004 | 04/23/2004 | ML04118027 | <strong>Air Actuator for Vacuum Breaker failed LLRT because of an inadequate design</strong><br /><i>Abstract:&nbsp;</i>On 2/24/2004 at 1730 ET, Unit 1 was in the Refueling mode. At that time, an investigation of the As Found Local Leak Rate Test (LLRT) failures on five of the twelve suppression chamber to dry well vacuum breakers' air actuators (replaced during the spring 2002 refueling outage) determined that the internal seal arrangement had been changed. This change resulted in the deletion of the inboard primary containment isolation barriers for this primary containment penetration. This resulted in a condition that was prohibited by the plant's Technical Specifications in that the actions required by TS LCO 3.6.1.3 for a failed PCIV were not taken. The cause of the event was that design records for the actuators did not contain sufficient detail to describe the required seal arrangement necessary to maintain containment integrity, in that the requirement for the dual/directional seals was not clear on the design drawings. As a result, the vendor was not aware of this requirement. Corrective actions included rebuilding all twelve suppression chamber to drywell vacuum breaker air actuators to restore the inboard primary containment isolation barrier, issuing a design drawing which clearly depicts the correct configuration of the actuator seals, and revising a statement for future procurement documents.
3212004003 | Hatch 1 | 03/03/2004 | 04/28/2004 | ML04124027 | <strong>4160V Normal Supply Breaker Shutter FailureTrips MOC Switch Causing DG Start on Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2004 at 1345 EST, Unit 1 was in the refueling mode. At that time the ‘swing' (1B) emergency diesel generator (DG) started unexpectedly during the planned removal of the normal supply breaker for the 1F 4160 VAC emergency bus (1R22-S006, Frame 11). A problem with the shutter in this breaker cubicle caused it to become hung up on the breaker when it was being removed from the cubicle. This caused the shutter linkage to depress the Mechanism Operated Cell (MOC) switch which in turn caused an under voltage signal to be generated, starting the ‘swing' DG. The shutter problem was caused by procedure omissions. The 4160 VAC switchgear Preventive Maintenance procedure did not require checks to ensure the shutter assembly travels freely and the C-channel is not deformed. Additionally, the procedure did not contain guidance for the installation of an L-bracket or mounting bolt that could interfere with the shutter linkage arm when the breaker is being put into the cubicle and subsequently racked in. The maintenance procedure will be revised to provide additional guidance by June 30, 2004.
3212004004 | Hatch 1, Hatch 2 | 03/09/2004 | 05/05/2004 | ML04131031 | <strong>Momentary False Low Reactor Water Level Signal Results in Actuations of Safety Systems</strong><br /><i>Abstract:&nbsp;</i>On 03/09/2004 at 0340 EST, Unit 1 was in the Cold Shutdown mode with reactor coolant temperature at approximately189 degrees Fahrenheit to perform the vessel leakage test. Personnel had reduced vessel pressure from 869 psig to 129 psig in order to place the shutdown cooling mode of the Residual Heat Removal (RHR) system into service to facilitate repairs to a reactor vessel head vent line flange discovered leaking during the test. At 0340 EST, as Operations personnel were opening shutdown cooling suction valve 1E11F009, several water level transmitters generated a false low level signal resulting in the actuations of multiple safety systems, including Emergency Diesel Generators, Core Spray pumps, RHR pumps, the Main Control Room Environmental Control System, and all four trains of the Standby Gas Treatment systems. Operators determined that the indications of low level were false and terminated injection by the 1A Core Spray pump within 36 seconds and the 1B Core Spray pump within 12 seconds. Personnel reset the actuation signals and returned the affected systems and components to normal by 0453 EST. This event was caused by personnel error and procedure omissions. Personnel had incorrectly assembled the head vent line flange. The location of the resulting leak was such that the vessel became water-solid during the leakage test. Opening valve 1E11F009 with the vessel water-solid caused a pressure transient that led to a false indication of low water level. The leakage test procedure did not contain instructions for lowering pressure and placing shutdown cooling into service with the vessel water-solid. The head vent line was assembled correctly and the leakage test was completed satisfactorily. The Unit 1 and Unit 2 leakage test procedures will be revised to provide information to help personnel determine whether the vessel is or may be water-solid and to include instructions to recover from such a condition.
3212004005 | Hatch 1 | 04/15/2004 | 06/09/2004 | ML04167040 | <strong>Degraded Reactor Protection System (RPS) Motor Generator (MG) Results In 1B RPS Bus Trip</strong><br /><i>Abstract:&nbsp;</i>On 4/15/2004 at 0700 ET, Unit 1 was in the Run mode at a power level of 2762 CMWT (100 percent rated thermal power). At that time, the "B" Reactor Protection System (RPS) Motor Generator Set (1C71S001B) tripped. The RPS is designed to "fail-safe" so that during a loss of power or control signal the systems powered by the RPS change to their emergency configuration state. Thus, the trip of the bus caused Group 2, Group 5, and outboard small-bore Group 1 Primary Containment Isolation System valves to receive an automatic isolation signal. The Main Control Room Environmental Control System entered the pressurization mode; both units' Standby Gas Treatment Systems initiated; the Primary Containment Hydrogen and Oxygen Analyzers isolated. Also, the Reactor Water Cleanup system, the Fission Product Monitoring system, and the operating Steam Packing Exhauster all tripped. Licensed personnel verified the proper plant response to the initiating signal per procedure 34AB-C71-002-1S, "Loss of RPS." By 0715 ET, licensed personnel energized the RPS bus from its alternate supply and the affected systems were subsequently returned to their normal lineups. The most likely cause of the RPS MG Set trip was determined to be a degraded RPS MG Set motor. The degraded motor was removed and replaced with a new motor.
3232004001 | Diablo Canyon 2 | 11/02/2004 | 12/23/2004 | ML04364019 | <strong>Unplanned Valid Emergency Diesel Generator Auto-start During Phase Sequence Check Due to Personnel Error in Configuring Test Equipment Setup.</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2004, at 11:05 PST, with Unit 2 in Mode 6 (Refueling), vital bus G received an unplanned valid undervoltage signal during the performance of an as-found phase sequence check on the emergency diesel generator (EDG) 2-1 circuit. This undervoltage signal caused an auto-start of EDG 2-1 and autotransfer of vital bus G to EDG 2-1. At 17:08 PST, plant operators transferred vital bus G back to auxiliary power and shut down EDG 2-1. At 17:22 PST, plant operators made a non-emergency event notification (EN #41168) in accordance with 10 CFR 50.72(b)(3)(iv)(A). The cause of this unplanned system actuation was personnel errors by the performer and the independent verifier when setting up test equipment. Corrective action to prevent recurrence includes revising plant administrative procedures to require supplemental (non-site permanent) personnel to have a pre-job brief in human performance error reduction techniques prior to work on sensitive plant equipment.
3242004001 | Brunswick 2 | 06/22/2004 | 08/19/2004 | ML04239046 | <strong>Inoperability of High Pressure Coolant Injection During Maintenance Activity</strong><br /><i>Abstract:&nbsp;</i>On June 21, 2004, Unit 2 was operating at 96 percent of rated thermal power with all Emergency Core Cooling Systems (ECCS) and the Reactor Core Isolation Cooling (RCIC) System operable. The High Pressure Coolant Injection (HPCI) System surveillance test 2MST-HOPIS, "HPCI Reactor High Water Level Channel Calibration and Functional Test," was being performed as a planned maintenance test. During performance of the test, an instrument channel was found out of calibration. Maintenance activities to restore the instrument channel were not completed when the 24 hour limit was reached in the Technical Specifications Required Action, requiring the HPCI system to be declared inoperable on June 22, 2004, at 0900 hours. The instrument channel was subsequently restored and HPCI was returned to operable status on June 22, 2004, at 1455 hours. The safety significance of this condition is considered to be minimal because HPCI was available for injection with operator action, and adequate core cooling was ensured by the operability of the redundant and diverse low pressure ECCS injection/spray subsystems in conjunction with the Automatic Depressurization System. Also, the RCIC system would automatically provide makeup water at high reactor operating pressures. The cause of the maintenance activity exceeding the 24 hour TS required action was failure to establish an effective maintenance plan.
3242004002 | Brunswick 2 | 07/29/2004 | 09/27/2004 | ML04279047 | <strong>Reactor Shutdown Required by Technical Specifications Due to Containment Vacuum Breaker Not Closed</strong><br /><i>Abstract:&nbsp;</i>On July 29, 2004, at 0357 hours, with the plant operating at approximately 88 percent of rated thermal power (RTP), one suppression chamber-to-drywell vacuum breaker, opened for testing, would not close. At 1517 hours, operators inserted a manual Reactor Protection System (RPS) trip from 23 percent of RTP. The RPS trip was part of a controlled shutdown required by Technical Specification Limiting Condition for Operation 3.6.1.6 due to the open suppression chamber-to-drywell vacuum breaker. The vacuum breaker was stuck in the open position due to mechanical interference between a portion of the hinge assembly and a limit switch fit-up bushing on vacuum breaker 2-CAC-X18D. A contributing cause was the sticking of the test actuator in the "open" position. The binding/interference condition was introduced by maintenance activities during the previous refueling outage. The fit-up bushing was adjusted to eliminate the interference with the hinge assembly and the test actuator was replaced. The remaining nine suppression chamber-to-drywell vacuum breakers on Unit 2, as well as the other ten on Unit 1, were inspected to ensure the same conditions did not exist. The suppression chamber-to-drywell vacuum breaker maintenance procedure is being revised to prevent recurrence. The safety significance of this occurrence is considered to be minimal. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) and 10 CFR 50.73 (a)(2)(v)(C) and (D).
3242004003 | Brunswick 2 | 10/29/2004 | 12/21/2004 | ML04363037 | <strong>Unanalyzed Condition due to Missing One-Hour Rated Fire Barrier -480 Volt Switchgear Room</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2004, it was determined that two conduits, located in a BSEP Unit 2 480 volt switchgear room, were not properly protected as required by 10 CFR 50 Appendix R, Section III.G 2. The conduits in question contained Division II circuits and were located closer than 20 feet from the Division I switchgear. The cause of this event is attributed to the use of an inadequate plant drawing during the effort to determine plant changes needed to comply with 10 CFR 50 Appendix R requirements. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly affected plant safety. Corrective actions include implementation of compensatory measures which remained in place until a one-hour rated fire barrier was installed on the conduits, review of other 480 volt switchgear rooms cable separation configurations, and a verification of the fire area designations for all conduits credited for safe shutdown.
3252004001 | Brunswick 1, Brunswick 2 | 01/04/2004 | 03/04/2004 | ML04078027 | <strong>Emergency Diesel Generator No. 3 Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2004, while performing the Emergency Diesel Generator (EDG) No. 3 monthly load test, a jacket water system piping leak of sufficient quantity to render EDG No. 3 inoperable was identified. As part of the investigation into this condition a past operability review was performed. The results of this review indicate that (1) a jacket water system pipe coupling was improperly installed during a coupling gasket replacement activity performed on February 3, 2003, and (2) tightening of the improperly installed coupling on December 8, 2003, resulted in excessive further misalignment of the coupling which impacted EDG operability until the misalignment was identified on January 4, 2004. The cause of the condition is attributed to missing pipe supports which resulted in an inadequate pipe coupling alignment. Failure to perform a functional verification following coupling maintenance on December 8, 2003, is considered a contributing cause. This condition is reportable in accordance with the 10 CFR 50.73 (a)(2)(i)(B), as operation prohibited by the plant's Technical Specifications (TS), in that the EDG was inoperable for a period of time greater than that allowed by the TS. By January 7, 2004, the EDG No. 3 jacket water piping configuration was restored to the as-designed condition, satisfactorily tested, and the EDG returned to service. Additional corrective actions include inspection of the other EDGs for similar jacket water configuration concerns and reinforcement of minor maintenance functional verification requirements with maintenance personnel. Previous reportable occurrences involving either the inoperability of the EDGs or degraded conditions resulting from maintenance activities within the last two years were not identified.
3252004002 | Brunswick 1, Brunswick 2 | 08/14/2004 | 10/13/2004 | ML04294050 | <strong>Manual Reactor Shutdown During Loss of Offsite Power Event</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2004, while experiencing severe weather due to Hurricane Charley, a fault occurred on the Weather spoon 230 kV transmission line (i.e., one of four lines connecting Unit 1 to the grid). Subsequent failure of a power circuit breaker (PCB) associated with the 230 kV 1B bus resulted in a 230 kV 1B bus lockout, and ultimately, a loss of power to the reactor recirculation pumps. By procedure, the loss of these pumps necessitated a manual reactor protection system actuation. As designed, the four emergency diesel generators auto-started and the required emergency buses re-energized. All primary containment isolation actuations occurred as designed. The high pressure injection and reactor core isolation cooling systems were manually started to maintain reactor water level and pressure within acceptable limits. Following restoration of the required systems and completion of the event reviews necessary to support startup, reactor startup was commenced on August 17, 2004. The cause of the event is attributed to a combination of conditions involving the failure of PCB 24B and the switchyard breaker scheme in affect at the time of the event. Corrective actions include replacement of degraded PCB components, leak checks of site PCBs, revision to the PCB maintenance process to adequately address moisture intrusion, and revisions to operating procedures controlling the switchyard breaker scheme.
3252004003 | Brunswick 1, Brunswick 2 | 08/15/2004 | 10/13/2004 | ML04294050 | <strong>Operation Prohibited by Technical Specifications due to Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2004, emergency diesel generator (EDG) No. 1 was declared inoperable, after it was determined that a mispositioned cover on relay 1-E1-AE7-CL-B would prevent proper load shedding of emergency bus E1 prior to EDG No. 1 tying to the bus. The most credible opportunity for the CL-B relay cover to have been mispositioned was during emergency bus E1 preventive maintenance activities performed on March 29, 2004.The root cause of this event is (1) the relay was inadvertently struck or pushed causing the relay to become held in the operated state, combined with (2) the relay cover sides were modified by cutting them back to a maximum extent which made the cover more susceptible to being mispositioned if struck. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plants' Technical Specifications. Corrective actions include removal of the covers from relays 1-E1-AE7-CL-A and 1-E1-AE7-CL-B, inspections of emergency buses E1, E2, E3, and E4, as well as other Unit 1 and Unit 2 systems for similar conditions, and planned training for appropriate maintenance personnel. This condition was discovered during a post-trip review of a manual reactor scram and loss of offsite power which are reported in LER 1-2004-002.
3272004001 | Sequoyah 1 | 03/15/2004 | 05/13/2004 | ML04134038 | <strong>Automatic Reactor Trip with main feedwater isolation and auxiliary feedwater start as a result of a main generator trip from inadvertent protective relay operation on a main transformer.</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2004, at approximately 1517 Eastern standard time, automatic turbine and reactor trips occurred. The trips were the result of a main generator trip. The generator trip occurred because of inadvertent protection relay actuation. Relay actuation occurred as a result of a ground loop (a positive side and negative side ground) on the non-safety related 250 Volt direct current (Vdc) Battery Board 2 system. Following the reactor trip, reactor coolant system (RCS) temperature decreased below 550 degrees Fahrenheit (F). Based on this RCS temperature coincident with a reactor trip, a main feedwater isolation occurred as expected. As designed, auxiliary feedwater was automatically initiated on steam generator low-low level following the reactor trip. The immediate cause of the event was inadvertent actuation of the Unit 1 generator main bank transformer protective relay. The root cause of the event was that a negative ground was created by an improperly abandoned cable. Contrary to the design change, only one end of the cable was lifted and insulated during design change implementation in 1999 by TVA’s Transmission Group. Since completion of the design change in 1999, TVA has taken steps to improve work standards in its Transmission Group by documenting management observations of work activities and implementation of the Substation and Switchyard Construction Standards Manual.
3272004002 | Sequoyah 1 | 10/28/2004 | 12/27/2004 | ML04364020 | <strong>Failure to Comply</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2004, it was determined that there was a failure to comply with Technical Specification (TS) 3.9.1. TS 3.9.1 requires immediately initiating boration of the RCS after it is determined that the reactor coolant system (RCS) boron concentration is below TS limits. TVA personnel reviewed Operations logs and determined that compliance with TS had not been performed as required. On October 28, 2004, at approximately 0418 Eastern daylight time (EDT), Chemistry personnel notified Operations personnel that the Unit 1 RCS boron concentration had been at 1999 parts per million (ppm) as early as 0010. Operations personnel entered TS Limiting Condition for Operation (LCO) 3.9.1 action because the RCS boron concentration was below the TS limit of 2000 ppm. Operations personnel immediately initiated boration of Unit 1 RCS. This event is being reported as an operation prohibited by TS since the TS requires immediately suspending all operations involving core alterations or positive reactivity changes and initiate and continue boration at greater than or equal to 35 gallons per minute (gpm). Operations did not initiate boration of the RCS earlier because Chemistry personnel did not inform Operations of the out-of-limits condition. Chemistry personnel were unaware that Unit 1 had entered Mode 6 at 2357 on October 27, thus requiring a minimum RCS boron concentration of 2000 ppm . The cause of the event was failure to establish adequate margin to the RCS boron concentration limit prior to entering Mode 6. The personnel involved in the transition to Mode 6 were counseled on establishing adequate margins, anticipating changes in plant conditions and adequately communicating within and between departments; and appropriate procedures are being revised to provide provisions for requiring a margin to the 2000 ppm limit.
3282004001 | Sequoyah 2 | 10/01/2004 | 11/29/2004 | ML04335041 | <strong>Failure of a Loop Calculation Processor (LCP) within the reactor protection system.</strong><br /><i>Abstract:&nbsp;</i>On October 01, 2004, at a NRC inspection exit, the inspector stated that a non-cited violation will be issued for failure to comply with Technical Specification (TS) 3.3.1. The violation was issued because following LCP failure, operator action was not taken to place the inoperable channel bistables, for functions served by the LCP, in Protection Set 4, Rack 13, in a tripped condition. The violation was documented in an inspection report issued on October 25, 2004. On July 1, 2004, at 0109 EDT, the reactor Protection Set 4, Rack 13, LCP failed. Processor reset was attempted and found to be unsuccessful. The protection channel remained in the electronic trip condition until Maintenance was prepared to remove the LCP card for replacement. Before card replacement, the Rack was placed in the manual trip condition. The cause of the TS violation was the failure to understand NRC interpretation of the TS requirements. The appropriate procedure was revised to ensure the system is placed in manual trip upon any future failure of the LCP.
3332004001 | FitzPatrick | 10/07/2004 | 01/19/2005 | ML05027017 | <strong>Inadvertent Actuation of ECCS and EDGs While in Refueling Mode</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2004 at 20:55, James A. Fitzpatrick was in a refueling outage with the reactor cavity flooded and the spent fuel pool gates removed. l&C Technicians performed a scheduled calibration of a reactor vessel pressure indicator. During restoration of the indicator, a pressure perturbation was introduced in the sensing line, causing reactor vessel level transmitters that share this line to sense an invalid low reactor water level condition, resulting in an invalid actuation of the Emergency Diesel Generator (EDG) and Emergency Core Cooling Systems (ECCS) initiation logic. The initiation logic functioned as designed, all EDGs started, but did not power the emergency buses (since there was no loss of offsite power) and all low pressure ECCS pumps started and injected into the reactor vessel. Operations personnel verified plant conditions, secured ECCS injection and secured the EDGs. All systems that actuated operated per design. As a result of the injection, water overflowed from the reactor internals storage pit and into the reactor building (RB) floor drain system, resulting in contamination of limited portions of the RB. RB access was restricted and thorough surveys were conducted to identify and post contaminated areas. Once the extent of contamination was identified, a recovery plan was implemented. This LER is being submitted as a voluntary LER.
3342004001 | Beaver Valley 1 | 08/14/2004 | 10/12/2004 | ML04292007 | <strong>Control Rod Shutdown Bank Anomaly Causes Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On 8/14/2004 at 0740 hours during performance of the normally scheduled Control Rod Assembly Partial Movement Surveillance Test at Beaver Valley Power Station (BVPS) Unit 1, the operator performing the test observed an unexpected condition during the insertion of control rod Shutdown Bank "A" which showed Group II rods at 223 steps withdrawn, two steps higher than expected. When the expected response to the rod motion was not received, the surveillance test was stopped. The BVPS Unit 1 Technical Specification (TS) 3.1.3.5 requires shutdown bank control rods to be withdrawn at least 225 steps except during surveillance testing. There are no applicable action requirements for a whole bank not being withdrawn. At 0810 hours, TS 3.1.3.5 and 3.0.3 were entered. At 11:07 hours, the Shutdown Bank "A" rods were withdrawn to 226 steps on the Group II demand counter using the normal rod withdrawal process, exiting TS 3.0.3 and TS 3.1.3.5. The initiation of preparation for shutdown was completed within one hour of entering TS 3.0.3. Thus, BV1 initiated actions to shutdown the Unit, even though actual power level was not decreased. Therefore, this event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications as per NUREG-1022, Rev. 2, page 36. The cause of the Group II Shutdown Bank "A" control rods to fail to move as demanded was a degraded Slave Cycler Logic card inside the Rod Control Logic cabinet. The safety significance of this event was low. All control rods, including the Shutdown Banks, remained trippable throughout the event.
3352004001 | St. Lucie 1 | 04/15/2004 | 06/04/2004 | ML04161022 | <strong>PSB-1 Analysis Non-Conservatisms Led To Past Operation Prohibited by TSs</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2004, as part of an ongoing station-wide electrical calculation upgrade, FPL determined that non-conservatisms in the original electrical distribution analysis led to past operation in a condition prohibited by Technical Specifications. NRC Branch Technical Position PSB-1, "Adequacy of Station Electric Distribution System Voltages," and GDC 17, "Electric Power Systems," require that degraded voltage relays not actuate on expected switchyard voltage and load transients following a unit trip, loss of coolant accident, startup, or shutdown. Contrary to this requirement, prior to the modifications completed during the spring 2004 SL1-19 refueling outage, St. Lucie Unit 1 operated for significant periods of time where a SIAS signal would have resulted in degraded voltage relay actuation for at least one train. The apparent cause of this condition was human error during the original electrical distribution PSB-1 design work in the 1980s and 1990s. All necessary corrective actions to comply with PSB-1 requirements were implemented by the end of the St. Lucie Unit 1 spring 2004 refueling outage.
3352004002 | St. Lucie 1 | 05/17/2004 | 07/16/2004 | ML04208018 | <strong>B Train Emergency Core Cooling System Room Ventilation System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2004, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. A failed emergency core cooling system equipment room ventilation surveillance test led to the discovery of a long-standing breach in the area ventilation boundary that rendered the "B" train of the ventilation system inoperable. The HVE-9B exhaust fan was unable to draw sufficient negative differential pressure with respect to the surrounding reactor auxiliary building spaces. The ventilation boundary breach was caused by an open hatch that was evaluated only for its effect on the fire protection boundary, and not for any postulated effect on the ECCS equipment room pressure boundary. Corrective actions included closing the hatch, performing a successful surveillance, placing information placards, and procedure changes to ensure that fire breach permits consider potential effects on ventilation systems.
3352004004 | St. Lucie 1, St. Lucie 2 | 09/25/2004 | 11/24/2004 | ML04335040 | <strong>Dual Unit Loss Of Offsite Power During Hurricance Jeanne</strong><br /><i>Abstract:&nbsp;</i>At 2356 hours on September 25, 2004, a dual-unit LOOP occurred at the St. Lucie site. Earlier that day both units commenced an orderly shutdown to prepare for the arrival of Hurricane Jeanne. At the time of the LOOP, the site was experiencing hurricane force winds with both units in Mode 4. The emergency diesel generators started and safe shutdown loads (with the exception of the 1B intake cooling water pump) were sequenced as designed. Offsite power was restored to both units by 1103 hours on September 26, 2004. The LOOP was caused by two independent electrical faults associated with the wind-driven salt contamination in the westward eye wall of Hurricane Jeanne. However, with both units shutdown, the switchyard design protection scheme for the main generators effectively reduces electrical power redundancy to the startup transformers. Site damage assessment and recovery efforts continued and both units were returned to service by October 4, 2004. The control switch and load-sequencing relay for the 1B ICW pump were replaced. FPL is evaluating long-term options to restore the switch yard redundancy to the startup transformers when a unit is taken off-line.
3362004001 | Millstone 2 | 03/06/2004 | 04/26/2004 | ML04125038 | <strong>Manual Reactor Trip on Low Steam Generator Level Resulting From a Feedwater Pump Spurious Relay Operation</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2004, at approximately 0050 with the unit in Mode 1 at 100 percent power, and with steam generator (SG) level approaching about 55 percent, operators initiated a manual reactor trip in anticipation of the low SG water level auto trip setpoint. The decreasing SG water level was due to a reduction in feedwater from the loss of the 'B' steam generator feedwater (SGFW) pump. The 'B' SGFW pump had tripped unexpectedly causing lowering SG water levels. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of any of the systems listed in 50.73(a)(2)(iv)(B). This includes Reactor Protection System actuation (RPS) and Auxiliary Feedwater System initiation (AFW). The apparent cause of the trip was agitation of a relay in the feedwater pump control system. This perturbed the relay's signal to the digital control system (MicroNet) sufficiently for it to sense a low pressure condition and initiate a trip of the feedwater pump, even though a low pressure condition did not exist. As a result of the Event Investigation Team (EIT) findings in response to the immediate issue of relay contact sensitivity, a relay's operation in the speed control circuit for the SGFW pumps was changed from an energized closed to an energized open configuration with the associated software changes. This reduces the HGA relay sensitivity to agitation and will avert additional SGFW pump trips.
3362004002 | Millstone 2 | 03/15/2004 | 05/11/2004 | ML04146045 | <strong>Automatic Reactor Trip on Low Steam Generator Level Resulted From a Feedwater Pump Trip During Test</strong><br /><i>Abstract:&nbsp;</i>At approximately 2020 hours on March 15, 2004, with the unit in Mode 1 at 100 percent power, the reactor experienced an automatic reactor trip on low steam generator (SG) water level. The decreasing SG water level was due to a trip of the 'B' steam generator main feedwater (SGFW) pump that had occurred at approximately 2018 hours. The SGFW pump tripped in the course of performing the quarterly overspeed lockout test. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as any event that resulted in manual or automatic actuation of any of the systems listed in 50.73(a)(2)(iv)(B). This includes Reactor Protection System actuation (RPS) and Auxiliary Feedwater System initiation (AFW). It is believed that the use of the lockout control switch for the quarterly performance of a SGFW pump emergency governor and trip lockout exerciser test is problematic and resulted in a momentary opening of switch contacts. This caused a rapid depressurization of the hydraulic overspeed protection system and a trip of the 'B' SGFW pump. To prevent recurrence, the performance of applicable sections of the emergency governor and trip lockout exerciser test procedure at power levels that could challenge a reactor trip from a SGFW pump trip has been suspended until such time as an appropriate final resolution to this condition is specified.
3392004001 | North Anna 2 | 05/09/2004 | 06/29/2004 | ML04189040 | <strong>Inoperable Emergency Diesel Generators Due to Shims for Exhaust Support Missing or Not Secured</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2004, at 2105 hours, with North Anna Unit 2 in Mode 6 (Refueling), both emergency diesel generators (EDG) were declared inoperable. The Unit 2 "H" EDG was out of service for scheduled maintenance. An inspection identified missing shims on the engine exhaust stack seismic support and some loose anchor bolt nuts. A Unit 2 "J" EDG inspection also identified missing shims and loose anchor bolt nuts. The Unit 2 "J" EDG was conservatively declared inoperable because operability of the as found condition could not be immediately determined. With two inoperable EDGs, the capability to maintain the reactor in a safe shutdown condition, remove residual heat, and mitigate the consequences of an accident would have been impaired in the event of a loss of offsite power. This event is reportable pursuant to 10CFR50.73(a)(2)(v). The cause of the event was determined to be unanticipated interaction between the redesigned vertical engine exhaust piping and the old exhaust capped piping with the silencer removed. Actions were implemented to restore the Unit 2 "J" EDG to operable. No significant safety implications existed. An engineering calculation determined the as found condition of the exhaust stack seismic support did not render the Unit 2 "J" EDG inoperable.
3392004002 | North Anna 2 | 05/29/2004 | 07/19/2004 | ML04210013 | <strong>Manual Reactor Trip Due to Control Bank "D" Group Step Counter Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2004, at 0210 hours, a manual reactor trip was initiated as a result of having Control Bank "D" Group demand position indicators inoperable. A mismatch of the Control Bank "D" Group 1 and 2 demand position indicators greater than two steps occurred. This was the result of the Control Bank "D" Group 2 demand position indicator cover not being in its proper position (i.e., snapped down) such that the counter mechanical cams were not engaged. At 0955 hours, an 8-hour Non-Emergency Report was made to the NRC in accordance with 10CFR50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10CFR50.73 (a)(2)(iv)(A) for a condition that resulted in an manual actuation of the reactor protection system. This event posed no significant safety implications because the reactor was subcritical when the reactor trip breakers were opened. Therefore, the health and safety of the public were not affected by this event.
3392004003 | North Anna 2 | 06/06/2004 | 08/04/2004 | ML04266039 | <strong>Inoperable Containment Personnel Lock Resulting in Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2004, at 1605 hours, the outer containment personnel air lock was declared in operable due to leakage discovered during testing. Further review determined that the outer containment personnel air lock was inoperable since the last containment entry prior to the June 6, 2004 test. The last entry occurred on June 4, 2004 at 1348 hours. As a result, the Technical Specification actions were missed to verify within one hour the operable door is closed and lock the operable door closed within twenty four hours. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(B) for a condition that is prohibited by the Technical Specifications. This event posed no significant safety implications since the inner containment personnel air lock was sealed, the containment was operating under vacuum and no leakage escaped to the atmosphere. Therefore, the health and safety of the public were not affected by this event.
3392004004 | North Anna 2 | 06/10/2004 | 08/04/2004 | ML04223026 | <strong>Reactor Trip Due to Incorrect Cell Switch Contact Configuration on Bypass Reactor Trip Breaker</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2004, at 1313 hours, with North Anna Unit 2 operating at 100 percent power (Mode 1), an automatic reactor trip occurred during performance of 2-PT-36.1A (Train A Reactor Protection and ESF Logic Actuation Logic Test). An incorrect contact configuration in the cell switch for "A" Bypass Reactor Trip Breaker caused the event. The incorrect contact configuration created a Turbine Trip Signal which, in turn, resulted in a Reactor Trip Signal. At 1611 hours, a 4-hour Non-Emergency Report was made to the NRC in accordance with 10CFR50.72(b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made in accordance with 10CFR50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System. This event is reportable pursuant to 10CFR50.73(a)(2)(iv) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. The cell switch contact configurations for the Unit 2 Bypass Reactor Trip Breakers were corrected. No significant safety implications existed because the Solid State Protection System was fully capable of tripping the reactor if required.
3412004001 | Fermi 2 | 08/09/2004 | 10/04/2004 | ML04288029 | <strong>Technical Specification Required Shutdown Due to Emergency Diesel Generator Failure</strong><br /><i>Abstract:&nbsp;</i>Emergency Diesel Generator (EDG)-12 was removed from service at 0200 hours on August 2, 2004 to perform routine maintenance, including the eighteen-month inspection, and preventive and corrective maintenance tasks. On August 6, 2004 at 1042 hours, EDG-12 was started as part of surveillance test 24.307.46, Emergency Diesel Generator 12 - Fast Start Followed by Load Reject. Following successful completion of the load reject, the EDG was being cooled down for restoration to operable status. Approximately 2.5 minutes into the cool down run, personnel in the area noted abnormal engine noise. The local operator tripped the EDG promptly at 1311 hours. Subsequent inspection determined that the scavenging air blower had failed and that the EDG could not be repaired within the remainder of the 7 day allowed out of service time. The plant was manually shutdown on August 8, 2004 at 2201 hours in accordance with Technical Specification 3.8.1, Condition C. Plant equipment performed as expected during this reactor shutdown. EDG-12 was surveillance tested after repair and returned to service. The plant was restarted on August 16, 2004.
3412004002 | Fermi 2 | 09/03/2004 | 10/27/2004 | ML04307060 | <strong>Automatic Reactor Shutdown Due To Automatic Voltage Regulator Failure</strong><br /><i>Abstract:&nbsp;</i>On September 3, 2004, at 2345 hours EDT, the reactor scrammed from 100% power as a result of the actuation of an Automatic Voltage Regulator (AVR) trip relay. The AVR experienced an interruption of the communications link between the digital AVR and the power converter thyristors of the generator exciter. The AVR trip resulted in a main generator trip with subsequent main turbine trip and reactor scram. The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of 137 inches above top of active fuel and recovered to normal automatically without operator intervention. Subsequent to the event, the main steam isolation valves (MSIVs) remained open and reactor water level was maintained in the normal band of 173 to 214 inches. Reactor water was supplied by the condensate and reactor feedwater systems, and the resultant reactor steam was sent to the condenser via the turbine bypass lines. Pressure control was maintained by the turbine bypass valves. Reactor dome pressure peaked at about 1090 psig. With reactor pressure maintained below the Safety Relief Valve (SRV) setpoints, none of the SRVs lifted. Reactor water Level 3 isolations occurred as expected. These included isolation Group 4 (Residual Heat Removal Shutdown Cooling and Head Spray), Group 13 (Drywell Sumps), and Group 15 (Traversing In-core Probe System) isolations. Failed AVR components were repaired or replaced, and the plant was restarted on September 5, 2004.
3412004003 | Fermi 2 | 11/02/2004 | 12/21/2004 | ML04363037 | <strong>Standby Liquid Control Pump Inoperable Due to Inadequate Lubrication</strong><br /><i>Abstract:&nbsp;</i>The Standby Liquid Control (SLC) Pump B gear reducer was inspected on November 2, 2004 as a result of high vibration and abnormal oil analysis results from a previous run on October 24, 2004. Only about ten ounces of oil were drained from the reservoir at the time of disassembly versus the approximately 80 ounces expected. The gear reducer was disassembled, and the gears were inspected, but there were no signs of gear damage or significant wear. An operability evaluation was performed and determined that due to the low oil level, SLC Pump B would not have been capable of performing its intended function over a period between July 24 and November 2, 2004 which is longer than allowed by Technical Specification 3.1.7. It was determined that the low oil level was caused by not replacing quarterly gear reducer sample volumes over time. Poor SLC gear reducer level indication and unclear plant procedures also contributed. Procedural, level measurement, and operator training improvements are being evaluated under the corrective action program. The pump was reassembled, lubricated, and tested on November 2, 2004. Vibration returned to normal levels during this test, and the pump was declared operable.
3412004004 | Fermi 2 | 12/04/2004 | 01/25/2005 | ML05033038 | <strong>Automatic Reactor Shutdown Due To Automatic Voltage Regulator Failure</strong><br /><i>Abstract:&nbsp;</i>On December 4, 2004, at 0417 hours EST, during startup from the tenth refueling outage, the reactor scrammed from 60% power as a result of the actuation of an Automatic Voltage Regulator (AVR) trip relay. The AVR experienced an interruption of the communications link between the digital AVR and the power converter thyristors of the generator exciter. The AVR trip resulted in a main generator trip with subsequent main turbine trip and reactor scram. The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of 136 inches above top of active fuel and recovered to normal automatically without operator intervention. Subsequent to the event, the main steam isolation valves (MSIVs) remained open and reactor water level was maintained in the normal band of 173 to 214 inches. Reactor water was supplied by the condensate and reactor feed water systems, and the resultant reactor steam was sent to the condenser via the turbine bypass lines. Pressure control was maintained by the turbine bypass valves. Reactor dome pressure peaked at about 1010 psig. With reactor pressure maintained below the Safety Relief Valve (SRV) setpoints, none of the SRVs lifted. Reactor water Level 3 isolations occurred as expected. These included isolation Group 4 (Residual Heat Removal Shutdown Cooling and Head Spray), Group 13 (Drywell Sumps), and Group 15 (Traversing In-core Probe System) isolations. The plant was restarted on December 5, 2004. Required circuit board replacements, the addition of noise suppression devices, AVR software changes, and associated testing were completed, and the unit was synchronized on December 8, 2004.
3462004001 | Davis-Besse | 01/06/2004 | 03/03/2004 | ML04065052 | <strong>Violation of Steam and Feedwater Rupture Control System Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2004, with the plant in Mode 3, at approximately 1850 hours the Operations shift became aware that a Technical Specification (TS) Action was missed. Feedwater/Steam Generator 2 Differential Pressure High Instrument Actuation Channel 2, PDS-2685B, was removed from service for a channel functional test and calibration. TS 3.3.2.2 Action 16 was entered at 1621, January 6, 2004, which required that PDS-2685B be returned to operable status, or the channel be placed in a tripped condition within one hour. Due to less than adequate work practices and managerial methods, it was not identified until the channel was returned to service approximately two-and-a-half hours later that actions to place the required channel in the tripped position did not occur within the one hour action statement. Actions are being addressed through continual involvement of Station management's monitoring, coaching, feedback, and correction. This event is being reported as an operation or condition prohibited by the Technical Specifications in accordance with 10 CFR 50.73 (a)(2)(i)(B).
3462004002 | Davis-Besse | 08/04/2004 | 10/04/2004 | ML04280025 | <strong>Reactor Trip During Reactor Trip Breaker Testing Due To Fuse Failure</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2004, at 1023 hours with the plant at approximately 100 percent power, surveillance testing was in progress on the Reactor Trip Breakers. When Reactor Trip Breaker "B" was opened in accordance with the test procedure, a reactor trip occurred unexpectedly due to the simultaneous opening of the Reactor Trip Breaker "A." Reactor Trip Breaker "A" opened due to a fuse that had failed prior to the test in a circuit designed to open the breaker when an undervoltage condition is detected. When Reactor Trip Breaker "B" was opened in accordance with the test procedure, both inputs to the Source Interruption Device indicated an undervoltage condition, initiating a trip of Reactor Trip Breaker "A" and a subsequent trip of the reactor. No procedural check existed to check the status of the existing failed fuse indicator lights prior to simulating a trip of the Reactor Trip breakers. The fuse was determined to have failed due to age and fatigue. The failed fuse along with the other three similar fuses in the Reactor Trip Breaker circuitry were replaced, and the four Reactor Trip Breaker Surveillance Tests were revised to require verification of fuse indication prior to performing the test. This event is being reported in accordance with the 10CFR50.73(a)(2)(iv)(A) as an event that resulted in actuation of the Reactor Protection System.
3482004001 | Farley 1 | 03/01/2004 | 04/29/2004 | ML04124020 | <strong>Reactor Trip Due to Steam Generator Feedwater Pump Speed Control Failure</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2004 at 0522, with the reactor at 100% power, Unit 1 automatically tripped due to Steam Generator 1C level reaching its high level setpoint. At approximately 0521, the lead-lag card in the Steam Generator Feedwater Pump (SGFP) master speed control circuit failed, causing a ramp increase in the speed of both SGFPs. The speed increase caused an increase in feedwater flow to all three steam generators. As a result of the increase in SGFP speed, a low SGFP suction pressure condition occurred. Operators responded to the low suction pressure condition and the increasing feedwater flow by starting a stand-by condensate pump and manually closing the Main Feedwater Regulating Valves (MFRVs). The MFRVs responded to the transient, but the integrated reactor operator and system response was not rapid enough to prevent steam generator level reaching the high level setpoint. Per design, the main turbine, both SGFPs, and the reactor tripped. All safety systems functioned as designed. This event was caused by failure of the Lead-Lag (NLL) card in the master SGFP speed control circuit, resulting in a ramp increase in SGFP speed. The unexpected SGFP low suction pressure alarm delayed the operators' diagnosis of the failure, thus delaying operator action which might have prevented the trip. The failed lead-lag (NLL) card has been replaced. Annunciator response procedures have been revised to provide additional guidance for malfunctions of the feedwater control system.
3482004002 | Farley 1 | 11/05/2004 | 12/29/2004 | ML05004021 | <strong>B Train LOSP During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2004, at 0911, with the reactor in Mode 6, Unit 1 experienced a B Train Loss of Site Power (LOSP) due to inadvertent actuation of B Train bus undervoltage relays during surveillance testing. Establishment of initial conditions for performance of the B Train LOSP, Load Shedding, and Station Black Out (SOB) Diesel Generator (DG) Start Test was in progress, with jumpers installed that allowed load shed and 1B DG start relays to energize with the sequencer in test mode. A separate monthly undervoltage relay functional test, normally performed at power and which does not normally actuate Engineered Safety Feature (ESF) Equipment, was being performed at the same time. When the monthly relay test was initiated, an undervoltage condition was detected by the sequencer which initiated the load shed and 1B DG start sequence. The LOSP caused a loss of 1B Residual Heat Removal (RHR) pump. The operating crew immediately restored shutdown cooling by starting the 1A RHR pump in accordance with Abnormal Operating Procedures. This event was caused by inadequate work scheduling and procedures. Additionally, the incompatibility between these tests was not realized by Operations Shift Supervision. The Unit 1 and Unit 2, A Train and B Train LOSP, Load Shedding, and DG Start Test procedures (4 procedures) have been revised to caution tag the sequencer test switch when jumpers are installed, and to add amplifying information to clarify the function of the jumpers. A Training Notice will be sent to licensed personnel explaining the event sequence, root causes and actions to prevent recurrence by January 30, 2005. Outage management procedure changes and additional training reviews will be completed by May 31, 2005.
3522004001 | Limerick 1, Limerick 2 | 04/20/2004 | 06/21/2004 | ML04181058 | <strong>Unplanned Inoperability Of RCIC and HPCI Due To Air In Suction Lines</strong><br /><i>Abstract:&nbsp;</i>Air was discovered in the pump suction lines of Unit 1 and Unit 2 reactor core isolation cooling (RCIC) and high pressure coolant injection (HPCI) systems. The condition was identified during an investigation of an actuation of the Unit 1 RCIC pump low suction pressure turbine trip that occurred with RCIC in the standby mode during performance of the ECCS - Condensate Storage Tank Level Functional Test. The air was present due to a combination of design deficiencies and procedural deficiencies. The RCIC pump suction piping design, associated with the abandoned RHR steam-condensing mode, was deficient in that a vent valve was not provided. The procedures for filling and venting of the HPCI pump suction lines following maintenance did not include venting between the suppression pool suction check valve and the pump. The air has been vented from the Unit 1 and Unit 2 RCIC pump suction lines and the HPCI pump suppression pool suction lines. Also procedures have been revised to include venting of the affected suction line sections.
3522004002 | Limerick 1 | 05/23/2004 | 10/15/2004 | ML04289026 | <strong>Operation Exceeding License Maximum Power Level</strong><br /><i>Abstract:&nbsp;</i>The unit was discovered to be operating in violation of the Facility Operating License at approximately 100.3 percent of rated thermal power following identification of increasing trends in several balance-of-plant parameters. The trends started on May 23, 2004. Calculated thermal power decreased as the output of the transmitter decreased, which resulted in operators increasing power to maintain indicated power at 100 percent. The degraded transmitter was replaced to provide an accurate feedwater flow measurement input to the thermal power calculation.
3532004001 | Limerick 2 | 06/22/2004 | 08/23/2004 | ML04244069 | <strong>Automatic Scram Due to 500 kV Switchyard Faults</strong><br /><i>Abstract:&nbsp;</i>A valid automatic actuation of the reactor protection system occurred when the reactor was critical. This actuation was caused by a main turbine trip due to a power/load unbalance condition. An internal fault occurred on a 500 kV circuit breaker during opening resulting in actuation of the#1 bus differential relay. A concurrent failure on the secondary wiring of the current transformer associated with a different 500 kV circuit breaker combined with the ground fault current from the initial fault to cause an actuation of #3 bus differential relay. Both main generator output circuit breakers tripped due to the actuations of the associated bus differential relays. The 500 kV circuit breaker was repaired and returned to service. The current transformer was replaced and returned to service.
3542004001 | Hope Creek | 01/12/2004 | 03/11/2004 | ML04079036 | <strong>Manual Reactor Scram following Isolation of Primary Containment Instrument Gas (PCIG)</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2004, at 1015 hours during the performance of 18-month Technical Specification calibration of the 'C' channel Reactor Building Exhaust (RBE) radiation monitor, the 'A' channel RBE radiation monitor actuated resulting in an actuation of the Primary Containment Isolation System (PCIS). The actuation of PCIS caused the isolation of the Primary Containment Instrument Gas (PCIG) supply to the in board Main Steam Isolation Valves (MSIVs). Prior to restoration of the PCIG system, the 'D' and 'B' inboard MSIVs began to drift closed. Anticipating the receipt of an automatic scram, the Reactor Operator (RO) manually scrammed the reactor by placing the mode switch to the shutdown position at 1048 hours. Shortly after the scram, the 'A' and 'C' MSIVs began to drift closed. At 1051, PCIG was restored and the inboard MSIVs returned to the open position. The inboard MSIVs never went fully closed which ensured that the main condenser remained available throughout the event for reactor heat removal. Following the manual scram, a low reactor water level scram signal was received (Level 3, +12.5 inches) as expected. At 2123 hours, a second invalid actuation of the PCIS occurred due to equipment related problems. The cause of the PCIS actuation that led to the manual scram is attributed to a loose LEMO connector on the 'A' channel RBE radiation monitor that allowed intermittent contact when a nearby conduit was used as a hand hold to gain access to the 'C' channel RBE radiation monitor for surveillance testing. The apparent cause of the second invalid PCIS actuation is attributed to faulty Bailey cards associated with the RBE high radiation input to PCIS. The corrective actions associated with this event consist of procedure enhancements, emphasizing standards with maintenance personnel, re-evaluation of the scheduling of surveillance testing, and the repair/replacement of equipment. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A).
3542004002 | Hope Creek | 09/19/2003 | 03/18/2004 | ML04090034 | <strong>Control Room Emergency Filtration System Train Inoperable For Greater Than 7 Days</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2004, while reviewing corrective action and maintenance records, it was determined that a violation of Technical Specification (TS) 3.7.2, Control Room Emergency Filtration system (CREF) {VI} had occurred. The discovery was based on conclusions reached regarding past maintenance activities and performance documentation. TS 3.7.2, requires that two independent CREF subsystems to be operable. With one subsystem inoperable the inoperable unit must be made operable within 7 days. On September 10 and 11, 2003 maintenance was performed on the BK400 chiller due to erratic behavior of the chiller. The unit was placed back in service and continued to operate until September 19, 2003 at which time it was placed in standby due to system realignment. On October 2, the BK400 was required to start. Shortly following the call to start, the chiller tripped on low evaporator refrigerant pressure. Corrective maintenance performed on October 3, 2003 found that the float arm had become disengaged. The chiller was repaired and returned to service. Operability screening conducted at that time did not identify the chiller as potentially inoperative for more than 7 days. There were no safety consequences associated with this event because one CREF subsystem was operable at all times. Also, during the period of assumed inoperability of the subsystem there were no radiological releases which would have required operation of the standby CREF to protect personnel in the control room envelope. This event is being reported in accordance with 10CFR50.73 (a)(2)(i)(B).
3542004003 | Hope Creek | 02/23/2004 | 06/24/2004 | ML04189038 | <strong>Both Trains of Control Room Emergency Filtration (CREF) Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2004, at 0152 hours, a high delta pressure alarm was received for the 'A' and 'B' Station Service Water (SSW) strainers. The appropriate abnormal operating procedures were entered in response to the alarms. The high delta pressure condition was cleared on the 'B' SSW strainer ensuring the 'B' SSW loop remained operable. The 'A' SSW strainer high delta pressure condition remained. At 0212 hours, the 'A' SSW loop was declared inoperable, along with the 'A' Safety Auxiliary Cooling System (SACS) loop and the 'A' Control Room Emergency Filtration (CREF) train. The 'B' CREF train was inoperable for planned maintenance on the associated chiller. Technical Specification 3.0.3 was entered since both the 'A' and 'B' CREF trains were inoperable. A shutdown brief was conducted and the operating procedure for shutdown from rated power to cold shutdown was entered at 0305 hours. At 0407, shutdown of the unit commenced. At 0424, the unit shutdown was halted at 94.5% Reactor power when the 'A' CREF train was returned to operable status and TS 3.0.3 was exited. The cause of this event is attributed to an undetected degrading condition of the 'A' SSW strainer that resulted in the trip of the motor overload protection when an influx of river grass created a high delta pressure across the strainer. The failure of the 'A' SSW strainer was due to the restraining nut that holds the main shaft backed off, which caused the strainer internals to lower and come in contact with the rim of the strainer body. Entry into Technical Specification 3.0.3 was necessitated as a result of emergent work in the work schedule in conjunction with planned maintenance. Corrective actions include a change to a maintenance procedure, changes to equipment operator logs and the development of an operational decision strategy for Operations personnel. This event is being report in accordance with 10CFR50.73(a)(2)(v)(D), any event that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
3542004004 | Hope Creek | 04/05/2004 | 06/03/2004 | ML04173044 | <strong>Non-Conservative 4160 Volt Class 1E Bus Operating Limits</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2004, a review of electrical design calculations identified that Operations procedures contained non-conservative values for minimum voltage on the Class 1E 4160 volt buses. The design calculations demonstrate that if voltage on the Class 1E 4160 volt buses are maintained above the minimum analyzed bus voltage level in the calculations, the 4160 volt buses would provide sufficient voltage to start and maintain the running loads without separating from the offsite power source. These calculations were performed to demonstrate compliance with 10CFR50 Appendix A General Design Criteria 17, "Electric Power Systems," and Branch Technical Position PSB-1, Adequacy of Station Electric Distribution System Voltages." Operating logs and procedures used to monitor the 4160 volt Class 1E buses would have allowed the buses to operate below the minimum voltage analyzed in the calculations. In addition to the non-conservative minimum bus voltage in the operating logs, the review of the calculations also identified that the automatic load tap changer (LTC) was set to maintain voltage at a "nominal 4200 volts minimum". At a setpoint of 4200 volts, the LTC was not capable of maintaining the minimum bus voltage assumed in the calculations when setpoint inaccuracies are taken into account. The cause of this event is attributed to inadequate program detail that resulted in an inadequate program to program interface between design calculations and implementing procedures. An Operability Determination was generated to establish the required minimum bus voltage, including instrument inaccuracies, and to operate the load tap changers manually to maintain the buses above the new limit. Additionally, Operating procedures were revised to reflect the new voltage limits and administrative procedures will be revised to address the interface between design calculations and implementing procedures. This event is being reported in accordance with 10CFR50.73(a)(2)(v)(D), any event that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
3542004005 | Hope Creek | 05/17/2004 | 07/16/2004 | ML04210013 | <strong>Control Room Emergency Filtration System Train Inoperable For Greater Than 7 days</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2004, a Technical Specification Action Statement (TSAS) was entered due to degraded performance of the BK400 chiller, a component of the Control Room Emergency Filtration system (CREF). The TSAS was exited later the same day following repair of the chiller. Prior to May 20, 2004, the BK400 chiller had been out of service between May 9 and May 15 for maintenance. A portion of the maintenance activity was the replacement of the guide vane pivot arm. While trouble shooting the problem on May 20, 2004, it was discovered that the chiller guide vane pivot arm was slipping on the drive shaft. Based on this information, the BK400 chiller was determined to not have been capable of performing its design function when it was returned to service on May 15, 2004. Therefore, the BK400 chiller was inoperable from May 9 to May 20 which exceeds the 7 day allowed outage time of TS 3.7.2 Action a. The cause of the slippage was determined to be setscrews that were not fully engaged. The immediate corrective action was to "dimple" the shaft and tighten the setscrews. This event is being reported in accordance with 10CFR50.73 (a) (2)(i) (B).
3542004006 | Hope Creek | 07/16/2004 | 09/13/2004 | ML04266011 | <strong>High Pressure Coolant Injection Design System Requirements Not Demonstrated</strong><br /><i>Abstract:&nbsp;</i>On July 16, 2004 the Hope Creek High Pressure Coolant Injection System (HPCI) was declared inoperable due to the inability to demonstrate via calculation or test data that the system could perform at the level assumed in the design basis accident analysis. Upon discovery, the station entered Technical Specification (TS) 3.5.1.c, a 14 day Limiting Condition of Operation (LCO) for HPCI inoperability. At this time the D Emergency Diesel Generator (EDG) was considered inoperable due to surveillance testing being conducted. As a result, the plant entered TS 3.0.3 and initiated a plant shutdown. This event was reported to the NRC (Event Report 40876). Subsequent engineering review determined that the diesel was not inoperable, therefore the notification made to report the Plant Shut down required by technical specifications 50.72(b)(2)(i) is hereby retracted. An original design document that recommended that the 2 HPCI injection line restrictor orifices be rebored to a larger size had not been acted upon. The actual HPCI flow rate was determined by calculation and surveillance test results to be less than the design requirements of 5600 gpm at 1156 psia. This is a long-standing design issue. Corrective actions include: reboring the orifices, performing testing to document adequate flow, revising design calculations, performing design document reviews of other systems and initiating an analysis to determine if HPCI was capable of meeting functional requirements in the as-found conditions. This event is being reported in accordance with 10CFR50.73 (a) (2) (v) (D), Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
3542004007 | Hope Creek | 08/19/2004 | 10/18/2004 | ML04301006 | <strong>Technical Specification Noncompliance - Radiation Effluent Monitor On North Plant Vent</strong><br /><i>Abstract:&nbsp;</i>On August 24, 2004 at 1310 while completing a weekly sample collection activity on the North Plant Vent (NPV) radiation monitor skid, a test connection valve was found open. With the valve in the open position, air being monitored by the NPV radiation monitoring system was drawn locally from the room diluting process flow from the NPV. This configuration issue appears to have occurred sometime on August 19, 2004 following corrective maintenance on the NPV monitor skid. With the effluent monitoring system in this condition, required sampling for radioiodine, radioactive particulates and noble gases would have been affected. Inability of proper sampling and monitoring of the NPV radiation monitor is a non-compliance with Technical Specification (TS) 3.3.7.5, Accident Monitoring, and Offsite Dose Calculation Manual (ODCM) 3.3.7.11. During the period from August 19 to August 24, 2004 neither required sampling nor the preplanned alternate monitoring was implemented. The preplanned alternate monitoring was not implemented because the position of the test connection valve which caused this condition was not apparent. There were no safety consequences associated with this event because the system is not safety related or required for shutdown of the unit. Corrective actions included realignment of the valves to the correct position and capping the test connection and performing a vacuum test to ensure sampling system integrity. This event is being reported in accordance with 10CFR50.73 (a) (2) (i) (B), Any operation or condition which was prohibited by the plant's Technical Specifications.
3542004008 | Hope Creek | 08/29/2004 | 10/27/2004 | ML04309053 | <strong>Potential For Uncontrolled Radiological Release - Reactor Water Clean-up Isolation</strong><br /><i>Abstract:&nbsp;</i>On 08/29/04 at 1928 hours, an alarm was received in the control room indicating the Reactor Water Cleanup (RWCU) high differential flow isolation channel for the outboard RWCU supply isolation valve was inoperable. The alarm was the result of the Leak Detection System (LDS) initiating a system failure signal. At the time, the functional test for the inboard RWCU high differential flow isolation channel was being performed. During the channel functional test, power to the inboard isolation valve was removed to permit continued RWCU system operation while the isolation function was tested. With the outboard isolation actuation channel inoperable and the inboard isolation valve deenergized in the open position, the required isolation function may not have been completed in the event of a break in the RWCU system. The condition was caused by the coincidental failure of a Nuclear Measurement and Control (NUMAC) analog card and the channel functional test being performed on the other isolation valve. The cause of the NUMAC analog card failure was due to a random component failure. Immediate corrective actions were taken to isolate the RWCU system and restore power to the inboard isolation valve. The NUMAC analog card was replaced. The LDS was successfully tested and declared operable. This event is being reported in accordance with 10CFR50.73 (a) (2) (v) (C), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
3542004009 | Hope Creek | 11/19/2004 | 01/17/2005 | ML05027016 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specification Allowable</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2004, PSEG determined that the setpoint value for several safety relief valves (SRV) exceeded Technical Specification (TS) allowable tolerance specified in TS 3.4.2.1. This specification requires SRV setpoint limits to be within +/- 3% of the specified value. The valves failing to meet limits were Target Rock Model 7567F SRVs. The testing followed Hope Creek fuel cycle 12. In all, a total of five of fourteen SRVs experienced setpoint drift outside of the Technical Specification 3.4.2.1 limit. The apparent cause for three of the SRV setpoint failures is corrosion bonding/sticking of the pilot disc. The apparent cause for the remaining two valves is under investigation. Immediate corrective action was to replace all five valves with tested and certified spare pilot assemblies. These five valves will be disassembled and inspected to document the cause of the failure. Since the number of SRVs outside of the setpoint tolerance limit (five) was greater than the number of SRVs (one) allowed to be inoperable by Technical Specification 3.4.2.1, this condition was determined to be reportable under 10CFR50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant Technical Specifications.
3542004010 | Hope Creek | 10/10/2004 | 12/09/2004 | ML04356017 | <strong>Manual Reactor Scram Due to Moisture Separator Dump Line Failure</strong><br /><i>Abstract:&nbsp;</i>On October 10, 2004, at 1814 hours, the reactor recirculation pumps were taken to minimum speed and the reactor was scramed due to a steam leak (pipe failure) in the turbine building. Immediately following the scram, a reactor water Level 3 (+12.5") scram signal was received as expected due to water level shrink in the reactor vessel. As a result of the pipe failure, condenser vacuum degraded. Operators began to depressurize the reactor to transition water level control to the condensate system. Prior to establishing condensate feed control, a Level 2 (-38") reactor water level actuation was reached on the A and B channels. High Pressure Coolant Injection (HPCI) automatically started and Channel A and B isolations and actuations occurred. The main steam isolation valves (MSIVs) were manually closed by the operators prior to automatic closure due to degrading condenser vacuum. Another Level 3 scram signal occurred during plant stabilization while HPCI and Reactor Core Isolation Cooling (RCIC) were being used to control reactor pressure and level. During the cooldown of the plant using the safety relief valves (SRV), an additional Level 3 scram signal occurred due to level shrink when the SRV was closed. Hope Creek achieved cold shutdown on October 12 at 0509 hours. The cause of the manual reactor scram was the failure of a moisture separator dump line to the condenser. Corrective actions, in part, include repair of the failed piping, procedure changes, development of an Operational and Technical Decision Making process, and Licensed Operator training concerning this event. The above events are being reported in accordance with 10CFR50.73(a)(2)(iv)(A).
3542004011 | Hope Creek | 10/21/2004 | 12/20/2004 | ML04363037 | <strong>Control Room Emergency Filtration Inoperable Longer Than Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2004, the 'A' control room emergency filtration (CREF) train tripped on low flow after receiving a start signal from the Loss of Coolant Accident (LOCA) sequencer during the performance of Loss of Offsite Power (LOP)/LOCA surveillance testing of the 'C' emergency diesel generator (EDG). As a result, the 'A' CREF train was declared inoperable. The CREF train is required to run following a LOCA or a LOCA in conjunction with a LOP (LOP/LOCA). It was determined that the 'A' CREF fan flow controller response upon restoration from a loss of power was extremely slow, which resulted in the demand signal from the controller not driving the flow control damper open fast enough to allow system flow to exceed the low flow setpoint. A review of the 'B' CREF train fan flow controller was performed. Based upon this review, the 'B' CREF train was conservatively declared inoperable. The cause of the CREF fans not being able to restart after a LOP/LOCA signal is still under investigation. A supplemental LER will be submitted by February 28, 2005, to include the results of the completed cause investigation and associated corrective actions. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B), as "a condition which was prohibited by technical specifications."
3612004001 | San Onofre 2 | 03/06/2004 | 04/29/2004 | ML04125003 | <strong>Personnel Error Results in Technical Specification Violation During Movement of Irradiated Fuel</strong><br /><i>Abstract:&nbsp;</i>On 3/6/04, Unit 2 was in a refueling outage and operators were preparing to reload the core. Prior to moving irradiated fuel in the Fuel Handling Building, operators placed PACU Train "A" in operation in accordance with LCO 3.7.14, Action B.1, because Train "B" was inoperable. The Train "A" PACU was placed in operation in parallel mode, in which the normal HVAC system remained in service. Parallel operation is allowed by the Bases to LCO 3.7.14, Action B.1, if two channels of Fuel Handling Isolation Signal (FHIS) are operable. Fuel movement started at 1355 PST on 3/6/04. At 2230 PST on 3/6/04, Train "B" FHIS Radiation Monitor 2RT-7823 was removed from service for a scheduled electrical bus outage. At that time, Operators did not recognize that, with one FHIS channel inoperable, the normal HVAC should have been stopped and PACU Train "A" placed in isolate mode. At 0650 PST, on 3/7/04, Operators discovered this error, suspended movement of irradiated fuel, and placed PACU Train "A" in isolate mode. SCE is reporting this event in accordance with 10CFR50.73(a)(2)(i)(B). This event was caused by personnel error. Operators failed to review the procedural requirements for the movement of irradiated fuel prior to removing 2RT-7823 from service. Appropriate communications and personnel action have been taken. SCE plans to enhance applicable procedures.
3612004002 | San Onofre 2 | 04/10/2004 | 06/04/2004 | ML04160012 | <strong>Manual Reactor Trip and Initiation of Auxiliary Feedwater in Response to Loss of Main Feedwater</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2004, at 1147 PDT, Unit 2 was operating at about 97 percent power when both feedwater pump turbines tripped on high discharge pressure. Plant operators manually tripped the reactor and the auxiliary feedwater system automatically started. SCE reported this event to the NRC in accordance with 10CFR50.72(b)(2)(iv) and 10CFR50.72(b)(3)(iv). This follow-up report is provided in accordance with 10CFR50.73 (a) (2) (iv). The main feedwater pump turbines automatically tripped on high discharge pressure caused by a main feedwater regulating valve and its associated bypass valve closing. SCE concluded the valves began closing due to two concurrent electrical grounds in the feedwater control system (FWCS). The first ground (Ground 1) was caused by a pinched interconnect wire on one of the two feedwater regulating control systems (FWCS); SCE replaced this wire. SCE was unable to locate the second ground but concluded it was an intermittent ground located in the DC power supply of the FWCS. SCE verified that the valves would begin closing (absent a close signal) when two grounds were present. SCE determined that the conditional core damage probability (CCDP) and the conditional large early release probability (CLERP) for this event were 2.8E-6 and 1E-7, respectively.
3612004003 | San Onofre 2, San Onofre 3 | 06/14/2004 | 07/16/2004 | ML04202040 | <strong>Momentary Loss of Operability of the Offsite Power Grid due to a 230 kV Transmission Line Fault in Arizona</strong><br /><i>Abstract:&nbsp;</i>On 06/14/2004 at 0741 PDT, with both units near full power, the offsite power grid [FK] connected to San Onofre experienced a system disturbance. Alarms [ALM] alerted control room Operators (utility, licensed) that grid frequency dipped below 59.7 Hz. The lowest frequency was a momentary dip to about 59.5Hz. The grid returned to normal frequency bands within three minutes, remaining stable thereafter. Units 2 and 3 were otherwise unaffected by the grid disturbance. Southern California Edison (SCE) declared offsite power inoperable per its operating procedures. NUREG1022, Revision 2 indicates offsite power unavailability is reportable regardless of whether other electrical power systems are available. SCE reported this event to the NRC Operations Center (Log No. 40818) in accordance with 10 CFR 50.72(b)(3)(v)(D). This report is provided in accordance with 10 CFR50.73(a)(2)(v)(D). The grid disturbance was initiated by a failed insulator [INS] on a 230 kV transmission line outside Phoenix, AZ. The failed insulator caused a 230 kV transmission line to fall into a transmission tower and short circuit. No corrective actions are required. As the diesel generators [DG] for both units were operable during this event, there was little safety significance to this event. SONGS Units 2 and 3 have not previously experienced loss of offsite power due to offsite grid disturbances.
3612004004 | San Onofre 2 | 11/19/2004 | 12/20/2004 | ML04357022 | <strong>Automatic Reactor Trip Due to Electrical Ground on Main Generator Isophase Bus</strong><br /><i>Abstract:&nbsp;</i>On 11/19/2004 at about 800 PST, Unit 2 was at about 100 percent power when the main generator [EL] and turbine [TA] tripped, and the reactor [R] automatically tripped. The Auxiliary Feedwater System [BA] actuated as designed. SCE reported this event to the NRC (Log No. 41209) at 0925 PST as required by 10CFR50.72(b)(2)(iv)(B). This follow-up report satisfies 10CFR50.73(a)(2)(iv)(A). The main generator isophase bus includes two de-ionizing filters [FLT], between phases, to reduce the likelihood of a phase-to-phase short circuit. This event resulted when several vanes of the filters failed (metal fatigue) and shorted the “A” phase to ground; protective circuits tripped the generator. During the 4/2004 refueling outage, SCE replaced the generator terminal box, and replaced these filters during that work. SCE determined the replacement filters failed due to use of a lower strength aluminum alloy and a vane/frame connection that caused stress risers. Prior to restarting the Unit, SCE installed new de-ionizing filters that have thicker vanes, use a stronger aluminum alloy, and eliminate vane/frame connection stress risers. Plant protective equipment functioned as designed. There was no safety significance to this event because it is bounded by the existing plant safety analysis (UFSAR 15). In the past 3 years SCE has not reported any events caused by failed de-ionizing filters.
3622004001 | San Onofre 3 | 06/04/2004 | 07/02/2004 | ML04190007 | <strong>Manual Reactor Trip Due to Sea Grass at Intake Structure</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2004, at 0445 PDT, plant operators manually tripped the Unit 3 reactor due to degraded circulating water pump suction caused by heavy influx of sea grass across the traveling screens during very low tide conditions. At the time of the reactor trip, Unit 3 was at approximately 80 percent power. Safety systems responded as expected. Southern California Edison (SCE) reported this event to the NRC Operations Center (Log No. 40791) at 0821 EDT in accordance with 10 CFR 50.72(b)(2)(iv)(B) for actuation of the Reactor Protection System (RPS) [JC]. This follow-up Licensee Event Report is provided in accordance with 10 CFR50.73(a)(2)(iv)(A). A traveling screen panel was repaired and broken shear pins replaced. The traveling screen system was tested and returned to service. Circulating water pumps are not essential for safe shutdown of the plant and do not provide a safety function. The SONGS 2/3 UFSAR Sections 15.2.1.3 and 15.10.2.1.3 credit the Auxiliary Feedwater System and ADVs for maintaining an adequate heatsink during a transient in which an instantaneous and complete loss of condenser vacuum occurs. Therefore the event reported here in is bounded by the UFSAR safety analysis identified above.
3622004002 | San Onofre 3 | 06/06/2004 | 05/08/2006 | ML06131018 | <strong>Incomplete Post-maintenance Calibration of Logarithmic Power Level-High Channel A Results in Technical Specification Violations</strong><br /><i>Abstract:&nbsp;</i>During a recent plant outage, SCE repaired Channel "A" of Log Power by replacing a discriminator card and calibrating the channel. Channel "A" was placed in-service for the plant startup that was completed on 6/6/2004. On 6/8/2004, plant personnel were reviewing calibration records and noticed that one portion of the calibration procedure had not been completed. Completing a startup without a valid calibration for Log Power Channel "A" violated TS 3.3.1, TS 3.3.2, and TS 3.0.4. This event resulted from a miscommunication between Maintenance personnel during a shift turnover. SCE has counseled/coached the individuals as appropriate. The expectation to use formal communication during turnovers was reinforced by a communication to site personnel on September 15, 2004. Other related corrective actions that were taken include training and proceduralizing the use of communications as an event defense. This event had no safety significance because Log Power Channels "B", "C", and "D" were unaffected by this occurrence and were fully Operable.
3622004003 | San Onofre 3 | 12/02/2004 | 01/13/2005 | ML05021005 | <strong>Invalid Actuation of Emergency Diesel Generator due to an Invalid Signal</strong><br /><i>Abstract:&nbsp;</i>On 12/2/2004 at about 0247 PST, with Unit 3 defueled, Emergency Diesel Generator (EDG) (EK) 3G002 actuated. This report is being made under 50.73(a)(2)(iv)(A) for an invalid actuation of an EDG due to an invalid signal. A Test Technician performing planned work in an Engineered Safety Features (ESF) Actuation System (JE) relay cabinet attempted to "jumper out" sections of the ESF actuation circuits to prevent actuation of certain ESF components. Instead, the jumper caused a momentary transient on the circuit power supplies and the resulting voltage dip was sufficient to actuate the EDG from the SIAS relay. The EDG functioned as designed. This event was caused by personnel error. As an immediate corrective action, SCE now requires the use of jumpers to be preplanned. SCE is completing a review of maintenance work processes to determine if alternate or additional program enhancements are needed. Since actual plant conditions did not require actuation of the EDG, this is an invalid actuation resulting from an invalid signal. At the time of this event, Unit 2 was operating at about 100 percent power and Unit 3 was in a refueling outage. There was no safety significance to this event. In the past 3 years, SCE has not reported any events of invalid EDG actuations due to an invalid signal.
3642004001 | Farley 2 | 03/30/2004 | 05/28/2004 | ML04154035 | <strong>Technical Specification 3.7.8 Violation due to Operation with One Train of Service Water Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2004, with the unit defueled, it was determined that Unit 2 had been operated in violation of Technical Specification 3.7.8 in that the 2E Service Water Pump failed to start on a Safety Injection Signal during routine surveillance testing. Investigation determined that a splice in the wire carrying the auto start signal had corroded and failed. This failure occurred some time after the last satisfactory surveillance test performed during the fall 2002 refueling outage. There is no firm evidence of when the failure occurred. However, due to the slow degradation rate assumed for the failed conductor, it is likely that the length of time the failure existed exceeded the 72 hour allowed outage time for the B Train of Service Water. The manual start function of the pump was unaffected by this failure. This event was due to the incorrect assembly of splice insulation in a cable pull box during initial construction. Lack of proper sealing of the insulation sleeves over the spliced conductor allowed water intrusion to corrode the conductor. The splice in the affected cable was repaired and the autostart function of the 2E Service Water pump was tested satisfactorily. The preventive maintenance task for pull box inspection and water removal has been revised to include a visual inspection of insulation sleeves on cable splices in the pull boxes. This type of degradation is along term phenomenon; therefore, a sample of cable splices in pull boxes on both units will be disassembled and inspected to identify the onset of degradation prior to failure. If degradation is identified in the sample, appropriate preventive maintenance tasks will be developed and implemented. This action will be completed by the end of the next refueling outage on each unit.
3642004002 | Farley 2 | 04/09/2004 | 06/01/2004 | ML04155030 | <strong>Plant Entered Mode 3 with One Train of Component Cooling Water Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2004, at 2200, with Unit 2 in Mode 4, it was determined that Unit 2 was operated contrary to Technical Specification 3.0.4 in that the unit had entered Mode 4 on April 8, 2004 at 1729, with one train of Component Cooling Water (CCW) inoperable. On the previous day, April 7, 2004, with Unit 2 in Mode 5, HV3096A, CCW from Evaporator Packages and H2 Recombiners, would not open from the Main Control Board and was opened using its manual operator. The fail safe position of this valve is closed to isolate the non-seismic portion of the CCW system from the safety related portion. A caution tag was placed on the valve documenting the abnormal position, and a work order was written for failure of the valve to open. Personnel reviewing readiness for Mode 4 entry failed to recognize the significance of this off normal condition. On April 8, 2004, at2200, during review of readiness for Mode 3 entry, this condition was identified. The valve was taken off the manual actuator and closed. This event was due to cognitive personnel error. Personnel who authorized placing the valve on the manual operator did not recognize that the condition made the on service train of CCW inoperable, and therefore did not generate an LCO tracking sheet for the upcoming Mode 4 entry. Personnel reviewing tagging order status for Mode 4 entry erroneously determined that the valve status given on the tagging order would not constitute an LCO when Mode 4 was entered. Personnel involved have been coached. A Training Advisory Notice has been sent to Operations personnel informing them of the details of this event. The Operations staff will be counseled concerning this event during the next training cycle by August 31, 2004. More specific guidance will be provided for reviewing tagging orders prior to Mode changes. This action will be completed by July 31, 2004.
3642004003 | Farley 2 | 04/09/2004 | 06/04/2004 | ML04160017 | <strong>Technical Specification 3.0.4 Violation Due to Turbine Driven Auxiliary Feedwater Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>From April 9, 2004 at1548 until April 10, 2004 at 0604 Farley Nuclear Plant (FNP) Unit 2 was operated contrary to Technical Specification 3.0.4 in that the unit entered Mode 3 without the operability requirements of Technical Specification 3.7.5 satisfied. Technical Specification 3.7.5 requires three operable trains of Auxiliary Feed Water (AFW) in Modes 1, 2, and 3. Corrective maintenance completed on April 8, 2004 at 0700 (while in Mode 4) caused the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) to be inoperable due to the TDAFWP speed control circuit wiring being inadvertently reversed from the required operable configuration. On April 9, 2004 at 1548, Unit 2 entered Mode 3. On April 10, 2004 at 0603, the TDAFWP turbine tripped on overspeed upon being started for normal surveillance testing. Investigation determined that the TDAFWP was made inoperable due to the wiring errors introduced during corrective maintenance on April 8, 2004. The cause of this event was poor work practices in that trouble shooting procedures were not followed when maintenance personnel disconnected the speed control wiring without documenting the wires lifted or the locations from which each was disconnected. A contributing cause was inadequate configuration control in that the design drawing configuration did not match the as-found TDAFWP speed control wiring configuration. Involved personnel have been counseled on adhering to the requirements of the trouble shooting program. A Training Advisory Notice has been sent to Maintenance personnel informing them of the details of this event. This event and the consequences of not following trouble shooting procedures will be discussed during the regularly scheduled maintenance continuing training program by September 30, 2004.The wiring for the TDAFWP speed control was returned to the required configuration and surveillance testing was performed which verified the operability of the TDAFWP. The wiring configuration for this circuit will be reconciled between field wiring and plant drawings for both FNP units and applicable drawing change requests will be submitted by August 15, 2004.
3642004004 | Farley 2 | 04/11/2004 | 06/04/2004 | ML04160017 | <strong>Reactor Trips Due to Unblocking of Source Range Permissive Interlock</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2004, at 1105, with Unit 2 at zero power critical conditions, the reactor tripped due to a logic failure unblocking the B Train Source Range High Flux Trip (P-6 interlock) which allowed a Source range high flux reactor trip signal to be generated from the B Train source range detector. Solid State Protection System (SSPS) power supply cards were verified to be acceptable through testing. However, based on symptoms identified during trouble shooting efforts and SSPS testing, three suspect cards were identified. As a result of bench testing, two cards (A408and A411) were replaced. B Train SSPS surveillance was conducted satisfactorily. The Unit 2 reactor subsequently achieved criticality at 0315 on April 12, 2004. Thirty minutes after the P-6 interlock was initiated, the reactor tripped again at 0347. Extensive investigation identified an intermittently failing universal logic card (A406). Both reactor trip events were due to an intermittent failure of universal logic card (A406) in the B Train Solid State Protection System (SSPS). The card failure was due to an increased sensitivity to heat believed to be the result of aging. The card was found to be overly sensitive to ambient temperature changes after energization of the Source Range Trip Block (P-6 interlock). The failed card (A406) was replaced as well as other applicable cards (A408 and A411 were replaced again as a conservative measure) in the P-6 interlock circuit. The equipment reliability plan associated with the 7300 system will be revised by November 30, 2004 to incorporate SSPS card failure and aging issues identified during this event.
3662004001 | Hatch 2 | 02/18/2004 | 04/13/2004 | ML04107024 | <strong>Water Intrusion into Relay Panel 2H21-P232 Results in the Start of the"2C"Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On 2/18/2004 at 1547 ET, Unit 2 was in the Run mode at a power level of approximately 2772 CMWT (98.8% rated thermal power). At that time, an 8 inch Plant Service Water (PSW) pipe was being cut in support of implementation of a planned design change. Despite precautions taken some water drained onto the Unit 2 ‘2C' Emergency Diesel Generator (DG) relay panel 2H21-P232 which caused the ‘2C' DG to start from an apparent invalid signal. The DG did not tie to the bus, and the bus remained energized throughout the event. Licensed Operations personnel shut down the DG by 1604 ET on 2/18/2004, and the DG's mode switch was left in the test position until the completion of trouble shooting activities. This event resulted from personnel failing to anticipate the volume of water that could be released from the pipe cut due to the combination of the pipe configuration and sediment build-up in the pipe. A contributing cause was failure to protect relay panel 2H21-P232 from any potential water damage. Troubleshooting and repair activities were completed; and the Operability Surveillance (34SV-R43-006-2S, DIESEL GENERATOR 2C SEMI-ANNUAL TEST) was completed on 2/20/2004 at 0505 ET. Procedural guidance is being incorporated into the appropriate plant procedures to ensure that electrical equipment is protected when breaching nearby systems.
3662004002 | Hatch 2 | 09/25/2004 | 11/23/2004 | ML04334025 | <strong>Unplanned Group 2 PCIS Isolation From a Water Level Transient Following Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 9/25/2004 at 0106 EST, Unit 2 was in the Run mode at an approximate power level of 981 CMWT (35 percent rated thermal power). At that time, Operations personnel manually scrammed the reactor per procedure 34GO-OPS-013-2, "Normal Plant Shutdown," for a planned Unit outage for the repair of the "L" Safety Relief Valve (SRV). Following the manual scram, water level decreased due to void collapse from the rapid reduction in power, reaching a minimum of approximately minus 6 inches above instrument zero (about 152 inches above the top of the active fuel). The decrease in water level resulted in receipt of a Group 2 Primary Containment Isolation System (PCIS) isolation signal and closure of the Group 2 Primary Containment Isolation Valves per design. The operating Reactor Feedwater Pumps restored level to its desired value. Personnel reset the Group 2 isolation signal and restored the isolation valves to normal per procedure 34AB-C71-001-2, "Scram Procedure." The receipt of the unplanned Group 2 PCIS isolation was the result of a vessel water level decrease due to void collapse from the rapid reduction in power following the planned insertion of a manual scram. Procedure 34GO-OPS-013-2, "Normal Plant Shutdown," failed to inform the operators that the receipt of a Group 2 signal was expected. Upon inserting the scram water level decreased to a point approximately equal to the Group 2 PCIS isolation setpoint. The Normal Plant Shutdown procedure will be revised to provide guidance to preclude reaching the Group 2 Isolation setpoint as well as provide guidance to state when the Group 2 isolation is expected.
3662004003 | Hatch 2 | 10/03/2004 | 12/01/2004 | ML04341006 | <strong>Failure to Restore Caution Tag on Service Air System Resulted in Primary Containment Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 10/03/2004 at 0530 ET, Unit 2 was in the Run Mode at an approximate power level of 561 CMWT (20 percent rated thermal power). At that time, Primary Containment was declared inoperable upon realizing that both manually operated Primary Containment Isolation Valves (PCIVs) 2P51 -F651 and 2P5 1-F513 were open for penetration 21. Technical Specification 3.6.1.3 Condition B was entered because both manually operated PCIVs for one penetration were open in Mode 1. Required Action Statement (RAS) 2-04-197 was initiated at 0530 on 10/03/2004 which required closing at least one PCIV within 1 hour. With Maintenance support, the shift was able to close PCIV 2P51-F513 at 0655 on 10/03/2004. RAS 2-04-197 continues to remain active because 2P51 -F651 located inside the drywell is open. Valve 2P5I-F513 is confirmed closed once every 31 days. Clearance process controls were inadequately addressed by the procedures associated with startup and drywell closeout. The procedures for startup and drywell closeout will be revised to strengthen the controls established for the clearance process. Procedure 34GO-OPS-003-2, "START-UP SYSTEM STATUS CHECKLIST" and procedure 34GO-OPS-028-2, "DRYWELL CLOSEOUT" will be revised to ensure that the tagouts related to the clearance process database are checked prior to startup.
3682004001 | Arkansas 2 | 03/16/2004 | 05/17/2004 | ML04141005 | <strong>Operation Prohibited by Technical Specifications due to an Inoperable Channel of Wide-Range Containment Water Level Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2004, with Arkansas Nuclear One, Unit 2 (ANO-2) operating in Mode 1 at 100 percent power, a waste control operator found the power switch for Wide-Range Containment Water Level Transmitter 2LT-5645-1 [IP] in the off position. This condition rendered one of the two technical specification (TS) required channels of wide-range containment water level indication inoperable. The level transmitter power switch was immediately returned to the correct position, restoring operability of the level indication instrumentation. A review of plant data indicated that the power switch had been turned off on October 9, 2003, during the latter part of the previous refueling outage and remained undetected until March 16, 2004. An investigation of this condition did not reveal any activity that would explain why the power switch for level transmitter 2LT-5645-1 was turned off. Since there was no physical barrier to protect against accidental repositioning of the power switch, it is likely that the switch was accidentally bumped into the off position by personnel exiting the containment building. A protective cover will be installed over the level transmitter power switch to minimize the likelihood of inadvertent movement. In addition, a requirement has been added to operator logs to verify the position of the power switch when performing associated indication channel checks.
3682004003 | Arkansas 2 | 09/29/2004 | 11/29/2004 | ML04336017 | <strong>Entry into an Operational Mode Prohibited by Technical Specification due to Inoperable Pressurizer Proportional Heaters</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2004, with Arkansas Nuclear One, Unit 2 (ANO-2) in mode 4, two AC circuit breakers that supply pressurizer proportional heaters were found in a tripped condition. This condition was discovered during a containment building inspection that was performed in preparation for a plant startup following a forced outage. The tripped circuit breakers rendered one of two proportional heater banks inoperable. The circuit breakers were reset and monitored with no further abnormalities observed. After the monitoring period, the breakers were considered operable and the ANO-2 startup proceeded. ANO-2 entered operational mode 3 at 0513 on September 30, 2004. Once in mode 3, technical specifications require both pressurizer proportional heater groups to be operable. Subsequently, during the performance of a proportional heater surveillance test, the same two breakers were again discovered in a tripped condition. Based on this second failure, it was determined that these breakers would not have been capable of performing their intended function and should not have been considered operable when ANO- 2 entered mode 3 from mode 4. Consequently, the mode change was in violation of technical specification 3.0.4 which prohibits entry into an operational mode when the conditions of the limiting conditions for operation are not met. The apparent cause for this condition is degradation of the breaker to bus bar connection. Loose connections resulted in increased line side heating causing the breaker thermal element to trip at a current value less than the breaker rating. Repairs were made to problem circuits in both proportional heater breaker panels. Testing was completed verifying that heater capacity for both groups satisfied technical specification requirements. Thermography testing verified there were no overheating connections after repairs.
3692004001 | McGuire 1, McGuire 2 | 10/16/2001 | 09/16/2004 | ML04272034 | <strong>Auxiliary Feedwater System in prohibited condition due to inadequate procedure.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 and Unit 2 were in Mode(Power Operation) at 100 percent power. Event Description: In October 2001, procedure actions were implemented to close and remove motive electrical power from valve CA86A, "A" train assured water supply to the Turbine Driven Auxiliary Feedwater Pump. This condition rendered each Unit's Turbine Driven Auxiliary Feedwater Pump inoperable for approximately eight days. The failure to recognize this condition resulted in a failure to satisfy Auxiliary Feedwater System Technical Specification requirements. This condition is reportable as per 10 CFR 50.73 (a)(2)(i)(B). This event was not significant with respect to the health and safety of the public. Event Cause: Inadequate procedure revision resulted in inoperable Turbine Driven Auxiliary Feedwater Pumps. Corrective Action: Applicable procedures were revised to adequately address operability. Performed a review of other station procedures that close and remove motive electrical power from CA86A and revised any procedures with similar discrepancies or placed them on hold. Evaluation will be performed to verify that procedure revisions were adequately justified.
3692004002 | McGuire 1 | 10/07/2002 | 01/12/2006 | ML06024022 | <strong>Main Steam Isolation Valve Inoperable</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the start of the event, Unit 1 was in MODE 3 (Hot Standby) Event Description: In 2002, during maintenance, 1SM-3 ("C" Steam Generator Main Steam Isolation Valve) was re-assembled incorrectly which rendered it incapable of closing to isolate a steam line break from the other Unit 1 Steam Generators when required. In consequence, 1SM-3 was inoperable for periods in excess of Technical Specification requirements. In addition, there was a period when 1SM-3 and 1SM-1 ("D" Steam Generator Main Steam Isolation Valve) were simultaneously inoperable. This constituted a safety system functional failure. This event was not significant to the health and safety of the public. Event Cause: 1SM-3 was assembled incorrectly and accepted due to deficiencies in the procedure used to maintain, re-assemble, and test Main Steam Isolation Valves. Corrective Action: The cause analysis determined that the 1SM-3 failure mode was not transportable to any other Unit 1 and Unit 2 Main Steam Isolation Valves. The procedure used to maintain, re-assemble, and test Main Steam Isolation Valves has been revised. 1SM-3 was repaired.
3732004001 | LaSalle 1 | 08/02/2004 | 09/30/2004 | ML04281012 | <strong>Invalid Containment Isolation Valve Local Leak Rate Test Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On 08/02/04, during the development of operator Local Leak Rate Test (LLRT) training, the LLRT Program Owner determined that an inaccurate procedural method for determining static head pressure correction factors was used in the test for the Reactor Core Isolation Cooling (RCIC) Barometric Condenser Vacuum Pump Discharge Containment Isolation check valves 1(2) E51-F028. These valves were declared inoperable and the RCIC Vacuum Pump Discharge Isolation valves 1(2) E51-F069 were closed. The procedural deficiency was corrected, and on 09/09/04, the Unit 1 valve (1E51-F028) was retested and failed its LLRT. On 09/17/04, the valve was disassembled, the valve internals were cleaned, and the disc and spring were replaced. The valve passed its post-maintenance LLRT and was declared operable. The cause of this event was a procedure error that has existed since 1986. Corrective actions included revising the affected procedure to correct the correction factor method, and to revise all LLRT procedures requiring head correction to require a signature for the person calculating the correction factor and for the person verifying the calculation.
3732004002 | LaSalle 1, LaSalle 2 | 09/29/2004 | 11/24/2004 | ML04337012 | <strong>'B' Control Room Area Filtration Subsystem Inoperable Due to Unsecured Inspection Port Cover</strong><br /><i>Abstract:&nbsp;</i>On 9/29/04, during the performance of a surveillance, it was discovered that the 'B’ control room area filtration (CRAF) subsystem was unable to maintain a positive pressure in the Auxiliary Electric Equipment Room of greater than or equal to 0.125inches water gauge relative to adjacent areas during the pressurization mode of operation at a flow of less than or equal to 4000 CFM, as required by Technical Specification Surveillance Requirement 3.7.4.5. Troubleshooting identified an unsecured inspection port cover in the suction ductwork associated with fire damper OVE39Y.The cover was reinstalled and the surveillance was completed acceptably. A root cause investigation was unable to determine the reason for the unsecured cover. Corrective actions included taping the associated inspection port cover latches, and procedural changes to ensure configuration management and material condition of the inspection access port doors.
3742004001 | LaSalle 2 | 02/01/2004 | 03/26/2004 | ML04097045 | <strong>Reactor Protection Bus ‘B’ Trip and Inoperable Automatic Depressurization Valves Due to Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>At 2334 hours on2/1/04, the 2B Reactor Protection System (RPS) Motor-Generator (MG) Set output breaker (EPMA D) tripped, resulting in a loss of the `B' RPS bus. The loss of the `B' RPS bus resulted in a half-scram and `B' side Group 1 (except Main Steam Isolation Valves), 2, 3, 4, 5, 6, 7 and 10 containment isolations. The Group 10 isolation isolated the Instrument Nitrogen (IN) compressor and caused the rupture disk to rupture. While the rupture disk was being replaced, nitrogen pressure to four Automatic Depressurization System (ADS) accumulators dropped below the Technical Specification required 150 psig, causing them to be declared inoperable. The cause of the RPS MG Set output breaker trip was an erratic voltage regulator gain potentiometer. The cause of the inoperability of multiple ADS valves was that the pressure regulator for the backup compressed gas bottle system was unable to maintain the required 150 psig ADS accumulator supply header pressure under low load conditions. Corrective actions included replacing the RPS MG set voltage regulator, replacing the IN rupture disk and returning the IN compressor to service. A long term corrective action for the IN pressure regulator will be evaluated.
3822004001 | Waterford 3 | 01/21/2004 | 03/22/2004 | ML04084052 | <strong>Failure to Provide Backup Over-current Protection Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2004, it was determined that two 120 volts electrical AC circuits, each going through separate containment electrical penetrations, did not have in-line backup over-current protection as required by the Technical Specification. The circuits in question power the plant's hydrogen analyzer panels and position indication for the hydrogen analyzer containment isolation valves. Upon this discovery, the plant followed the required action statement for the Technical Specification, 3.8.4.1, by lifting the circuit leads for the inside containment isolation valve position indication only, declaring the affected position indication and circuit inoperable and verifying every 7 days that the circuits were disconnected. The hydrogen analyzer remained capable of performing its' intended safety function. Backup over-current protection was added as the corrective measure. The cause of this event was human error in that personnel did not perform adequate peer and self checking when modifying the affected circuits in 1988 during installation of a station modification package. A contributing cause was determined to be that the control wiring diagrams for the Containment Hydrogen Analyzers did not clearly distinguish the power supply for the containment penetration isolation valves position indication. The lack of in-line backup over-current protection for the above circuits did not result in damage to the containment penetrations. Accordingly, this event did not compromise the health and safety of the public.
3822004003 | Waterford 3 | 03/31/2004 | 06/01/2004 | ML04156025 | <strong>10CFR50.46 Acceptance Criteria Exceeded for Small Break Loss of Coolant Accident Analysis</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2004, with the plant operating at 100% power, Waterford 3 identified a different worst-case single failure for the small break loss of coolant accident (SBLOCA) analysis that could have conservatively resulted in exceeding a 10CFR50.46 acceptance criterion for peak cladding temperature (PCT) of </= 2200 degrees Fahrenheit (F). Per 10CFR50.46(a)(3)(ii), any change or error discovered in an acceptable evaluation model that results in the calculated ECCS performance not conforming to the criteria of part 'b' for PCT is a reportable event per 10CFR50.72 and 10CFR50.73. The different worst-case single failure is the failure of a direct current (D.C.) bus with a coincident loss of offsite power (LOOP) which potentially results in the inability to inject charging water flow into the reactor coolant system as a supplement to high pressure safety injection flow. Upon identification of this condition, Waterford 3 initiated an evaluation that demonstrated with reasonable assurance that Waterford 3 continued to satisfy the 10CFR50.46 PCT acceptance criterion. Reanalysis of the SBLOCA event, incorporating the different worst-case single failure and taking credit for additional high pressure safety injection flow, was performed and demonstrated compliance with the 10CFR50.46 acceptance criteria. The two primary causes for this event were that (during construction) 1) an inadequate evaluation of the change in charging loop isolation valve design from a fail open air operated valve to a fail closed solenoid valve was performed resulting in conflict with the SBLOCA analysis assumptions, and 2) communication was ineffective in implementing competing design requirements (SBLOCA analysis vs. safe shutdown analysis). The major corrective action for this event is the reanalysis of the SBLOCA event, which has already been completed. The condition described in this LER represents an inaccurate assumption in the SBLOCA analysis. There was no actual occurrence which resulted in exceeding safety limits; accordingly, this condition does not compromise the health and safety of the public. This is not a safety system functional failure.
3822004004 | Waterford 3 | 11/17/2004 | 01/14/2005 | ML05021005 | <strong>Failure to Adequately Size Containment Electrical Penetration Over-Current Protection Devices Due to Latent Personnel Errors</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2004, it was determined that a 125 VDC control power circuit did not have adequately sized over-current protection devices to ensure the containment penetration physical integrity was not impaired in the event of an electrical fault. An additional circuit over-current protection device was functional and able to isolate the design fault prior to impairing the physical integrity of the associated containment electrical penetrations. This condition was identified during corrective action related to the failure to provide backup protection for Hydrogen Analyzer electrical penetration circuits identified in LER-2004-001, dated March 22, 2004. The circuit in question powers the vibration alarm circuits through separate penetrations for the Control Element Drive Mechanism Fan Cooling Units and Containment Cooling Units located inside containment. Upon this discovery, the plant declared the affected circuit inoperable and entered Technical Specification, 3.8.4.1 ACTION statement 'a'. Power to the circuits was removed and the leads disconnected for the equipment inside containment. The apparent cause of this condition is human error due to an inadequate original plant design by the Architect/Engineering firm. The overcurrent protection devices were provided during Waterford 3 original construction and are attributed to design errors made in the construction period. The inadequately sized over-current protection devices for this circuit did not result in damage to the containment penetration. Accordingly, this event did not compromise the health and safety of the public.
3872004001 | Susquehanna 1 | 03/07/2004 | 05/04/2004 | ML04133037 | <strong>Automatic Actuation of 'A' Emergency Diesel Generator When Operator Removed Incorrect 4.16 kV Bus Fuses</strong><br /><i>Abstract:&nbsp;</i>At 02:01 on March 7, 2004 with Unit 1 in Mode 5 at 0% power and Unit 2 in Mode 1 at 100% power, the 'A' Diesel Generator (DG) started due to a detected under-voltage condition on the 1 A201 4.16kV Engineered Safeguard System bus. The bus under-voltage condition was created when an in-plant operator removed fuses from an incorrect 4.16 kV bus breaker cubicle during equipment alignment activities for a planned load center / 4.16 kV bus maintenance outage. All plant equipment operated as expected. The 'A' DG was returned to standby status at 16:44 on March 7, 2004. Two root causes were found. The in-plant operators involved did not use adequate self-check / peer-check techniques during performance of the procedure step that identified the location of the breaker cubicle fuses. Additionally, the load center / 4.16 kV bus maintenance outage procedure was not written in accordance with human performance standards. Human performance training was conducted at the plant's performance simulator for all available operators and supervisors. The corrective actions to be taken include establishing a peer-to-peer human performance observation program for field operational activities and incorporating human performance standards into all station load center / 4.16 kV bus procedures. This event is reportable as an event that resulted in an unplanned automatic actuation of an emergency diesel generator per 10 CFR 50.73(a)(2)(iv)(A). There were no actual consequences to the health and safety of the public as a result of this event since there was no actual design basis accident and all station equipment responded as designed during the event.
3872004002 | Susquehanna 1, Susquehanna 2 | 03/09/2004 | 05/04/2004 | ML04139050 | <strong>Loss of Safety Function due to Both Loops of Emergency Service Water Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2004, it was identified that both the Unit 1 'A' and 'B' loops of the Emergency Service Water (ESW) system were inoperable for a period of approximately one hour on March 5, 2004. On March 5,2004, at 0100 hours, maintenance personnel erroneously removed a blank flange in the Unit 1 'B' loop of ESW instead of the 'A' loop of ESW, which was already isolated to support the U113RO outage. This resulted in a loss of safety function for the ESW system. In addition, several other systems important to safety were affected. Because the condition was not discovered until March 9, 2004, several required Technical Specification (TS) actions were not taken. As such, this LER is being submitted in accordance with 10 CFR 50.73(a)(2)(v)(D) and (a)(2)(i)(B) for a loss of safety function and for a condition prohibited by TS, respectively. The cause of this event was attributed to human performance. No pre-job brief or energy control process brief was conducted with the maintenance personnel (Crew B) assigned to assist the original maintenance personnel (Crew A) in removing the blank flange in the 'A' loop of the ESW system. In addition, a less than adequate turnover was provided by Crew A to Crew B. PPL performed a risk assessment which concluded that there was no risk impact to either Unit 1 or Unit 2 since the ESW system remained capable of supplying water to necessary heat loads on both units and common. Expectations and coaching were provided to appropriate maintenance personnel. Lessons learned will be incorporated into PPL's Human Performance/Work Standards training for plant personnel. Improvement in this area has been recognized by PPL and is one of the station's key initiatives for 2004.
3872004003 | Susquehanna 1 | 04/21/2004 | 06/16/2004 | ML04184025 | <strong>Manual Scram Following Main Turbine High Vibration</strong><br /><i>Abstract:&nbsp;</i>At 16:35 on April 21, 2004 with Unit 1 in Mode 1 at 17% power, Susquehanna Unit 1 was manually scrammed in response to main turbine bearing high vibrations experienced during startup turbine testing. The turbine had been replaced during the recently completed Unit 1 refueling outage. After approximately 35 minutes of turbine operation at 1800 rpm and no load, a rub developed in the vicinity of bearing # 2. Vibration increased to levels warranting turbine trip as directed by operating procedure. Despite the turbine trip, the rub continued to cause localized heating thus creating a rotor bow condition and a steady vibration increase. The Reactor Protection System was manually initiated and condenser vacuum was broken to allow for a more rapid decrease in turbine speed and, subsequently, vibration levels. Plant response to the manual reactor scram was in accordance with design. Causes cited for this event include: (1) Turbine startup vibration trip limits were not set sufficiently low to preclude rub induced high vibration (2) Vibration change rates were not monitored and used as a response input to high vibration conditions and (3) Project management did not establish contingency plans in sufficient depth to handle all potential vibration issues. After implementing corrective actions to address these deficiencies and performing a thorough evaluation to ensure equipment had not been adversely impacted by the high vibration, the turbine was successfully started and loaded in accordance with the established startup procedure. The manual RPS actuation and the subsequent manual initiation of the Reactor Core Isolation Cooling system, to assist with reactor level control, are unplanned actuations of systems that mitigate the consequences of significant events and are, therefore, being reported per 10CRF50.73(a)(2)(iv)(A). There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
3872004004 | Susquehanna 1, Susquehanna 2 | 08/20/2004 | 10/18/2004 | ML04314027 | <strong>Radiation Monitors Inoperable During Spent Fuel Cask Transport</strong><br /><i>Abstract:&nbsp;</i>On 8/20/2004, it was discovered that the Secondary Containment Zone III isolation relays of both process radiation monitors in the Railroad Access Shaft were disabled. Investigation determined that the instrumentation trip outputs had been bypassed on 7/16/2004 through inappropriate jumper installation. Contrary to Technical specifications, two Dry Fuel Storage Casks containing irradiated fuel had been lowered from the Refueling Floor with the radiation monitors defeated. Had an actual high radiation condition occurred, the disabled monitors would not have initiated automatic re-alignment of the Reactor Building Zone III Ventilation System and automatic starts of both the Standby Gas Treatment System and the Control Room Emergency Outside Air supply System. Less than adequate work practices and procedural direction have been cited as causes for this event. In response, human performance tools, techniques and work standards will be reaffirmed with affected plant personnel. Further, the controlling procedure for this evolution will be enhanced, as necessary, to prevent error during future evolutions. The inability of these systems to respond to radiological conditions in the railroad Access Shaft constitutes a condition that could have prevented the fulfillment of safety functions needed to control the release of radioactive material and is reportable per 10 CFR 50.73(a)(2)(v)(C). Actual radiological conditions observed in the Railroad Shaft during movement of the casks did not approach levels necessary for system actuation. There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
3892004001 | St. Lucie 2 | 03/04/2004 | 05/03/2004 | ML04132035 | <strong>Control Room Floor Fire Penetrations Not Bounded By Tested Configurations</strong><br /><i>Abstract:&nbsp;</i>On March 4, 2004, St. Lucie Unit 2 was in Mode 1 at 100 percent reactor power. FPL determined that several control room floor fire penetration seals located in the reactor-turbine generator control boards were inoperable because the as-found conditions were not per the tested configurations. A condition report was initiated for these conditions and fire impairments were logged against the affected fire seals in accordance with the St. Lucie Fire Protection Program. The inadequate change documentation for design and field installation verification activities during initial construction of St. Lucie Unit 2 led to this condition. Compensatory fire watches were verified to be in place at the time of discovery in the affected fire areas. FPL will restore the affected fire penetrations during the SL2-15 refueling outage.
3892004002 | St. Lucie 2 | 10/04/2004 | 12/03/2004 | ML04348027 | <strong>Reactor Auxiliary Building Missile Shield Doors Not Closed</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2004, St. Lucie Unit 2 was shutdown in Mode 3 preparing to start up after Hurricane Jeanne. A condition report was issued on the east side RAB 62 feet elevation exterior doors that were found open. The subsequent investigation determined that the exterior doors were credited as missile shields. The apparent reason for this condition was attributed to lack of procedural guidance to ensure that the missile shield doors are kept closed during normal plant operations and severe weather conditions. The missile shield doors were closed, and future corrective actions include procedure changes and training. The risk assessment for this condition concluded that the open missile shields had no adverse effect on the health and safety of the public.
3892004003 | St. Lucie 2 | 12/16/2004 | 02/14/2005 | ML05054060 | <strong>Panel Display Failures Caused Loss of Technical Specification Required Range</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2004, St. Lucie Unit 2 was in Mode 1 at 100 percent reactor power. FPL completed an evaluation that determined that past operation with faulty Versatile indicators for charging flow/pressure and shutdown cooling temperature at the hot shutdown panel constituted a reportable condition. In January 2004, these displays were identified as degraded and the condition was erroneously judged to only be an equipment degradation issue and not a loss of Technical Specification required range. The displays remained in service beyond Technical Specification allowed outage times. Corrective actions include replacement of the subject displays, verification that the remaining Versatile work scope did not pose any current or past separability issues, and modification of the model work order to provide additional guidance on Technical Specification range requirements.
3892004004 | St. Lucie 2 | 12/25/2004 | 02/23/2005 | ML05063024 | <strong>Manual Reactor Trip Due to Condensate Pump Motor Malfunction</strong><br /><i>Abstract:&nbsp;</i>On December 25, 2004, St. Lucie Unit 2 was operating in Mode 1 at 100 percent reactor power. At 0651 hours, the control room operators performed a manual trip of the reactor after high temperatures were observed locally at the 2B condensate pump motor terminal box subsequent to the annunciation and indication of high motor current in the control room. Auxiliary feedwater initiated as expected from a full power reactor trip. The trip was uncomplicated as all safety-related equipment responded as required to the plant trip. The 2B condensate pump motor over current condition was caused by the failure of the "A" phase motor lead that was the result of incorrect original construction motor lug installation. Corrective actions included swapping the 2A condensate pump motor with the 2B pump,changes to the 4.16 and 6.9 kV motor overhaul program to check lug installation, and inspection of 4.16 and 6.9 kV motor lug installations.
3892004005 | St. Lucie 2 | 12/27/2004 | 02/25/2005 | ML05063026 | <strong>Manual Reactor Trip Due to Steam Generator Low Level</strong><br /><i>Abstract:&nbsp;</i>On December 27, 2004, Unit 2 was in Mode 1 at 10 percent reactor power preparing to latch the turbine. At 1751 hours, the turbine was latched and the "A" steam generator inventory took a step increase. Approximately 140 seconds following the turbine latch, the 2A main feedwater (MFW) pump automatically tripped on high level in the "A" steam generator. With no MFW pump in service, the "B" steam generator narrow range water level decreased to the low level 40 percent reactor protection system pre-trip on 2 of 4 channels and the operators manually tripped the reactor at 1721 hours. The operators performed standard post-trip actions and stabilized the plant in Mode 3. The event was caused by a combination of human error and the malfunction of a main feedwater regulating valve controller that allowed the steam generator overfeed condition that ultimately resulted in manual reactor trip due to low steam generator water level. Corrective actions included controller replacement, procedure revisions, and training on the event. The unit was returned to service on January 2, 2005.
3902004001 | Watts Bar 1 | 01/16/2004 | 02/25/2004 | ML04061079 | <strong>Automatic Reactor Trip Due to a Invalid Turbine Trip Signal (P-4)</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2004, with Watts Bar Nuclear Plant Unit 1 at 100 percent power, an automatic turbine trip occurred in response to an invalid trip signal (P-4), which then caused an automatic reactor trip because reactor power was above 50 percent power (P-9). The auxiliary feedwater system started as designed. Surveillance Instruction 1-SI-99-10-B, "31 Day Functional Test of SSPS Train B and Reactor Trip Breaker B," Revision 22, was in progress when an instrument mechanic inserted test leads to take a voltage reading across the P-4 contacts without realizing that the multi-test meter was in the ohms reading position. The result of the volt-ohm meter being in the ohm position was to create a current path equivalent to P-4 contact closure which energized Train B turbine trip bus. The root cause of this event was determined to be a failure of the involved individuals to follow expectations to "stop" when unexpected conditions occurred. A contributor to the event was improper use of test leads for connection to multi-test meters. Corrective actions included: 1) appropriate personnel action, 2) requiring an additional management observer to be present during the future test performances, 3) providing lessons learned and reinforcing expectations to site personnel on the use of human performance error reduction tools and appropriate test equipment, 4) and placing affected procedures on administrative hold until precautions are added.
3902004002 | Watts Bar 1 | 09/19/2004 | 11/18/2004 | ML04328036 | <strong>Manual Reactor Trip Due to Dropped Rods</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2004, at approximately 0452 hours Eastern Daylight Savings Time (EDT), Unit 1 was in Mode 1, steady state operation at 100 percent power when the operators received simultaneously Control Rod Urgent Failure, RPI Trouble, and rods at bottom alarms. Four control rods, F14, B6, K2, P10, in control bank B group 2, fell to bottom of core and initiated the rods at bottom alarm. This event resulted in a rapid power drop to about 67 percent which then stabilized at approximately 85 percent. During this transient, operators took manual control of the main feedwater regulating valves, Operators responded to the rods at bottom indications by manually tripping the reactor at approximately 0456 EDT. Systems functioned as expected in automatic with the exception of the loop number 1 Reactor Coolant Pump which failed to transfer to its respective start bus on generator lockout. The remaining control rods inserted properly in response to the reactor trip. The Auxiliary Feedwater (AFW) System actuated in response to the trip, as expected. The root cause of the reactor trip was a malfunction of a rod control power cabinet circuit (i.e., a failed transistor on the phase control circuit card). Corrective actions included the replacement of three circuit board cards in the rod control power cabinet and stand down meetings to brief the oncoming crews of this event.
3952004001 | Summer 1 | 03/30/2004 | 05/27/2004 | ML04274012 | <strong>Reactor Trip Due to Valve Failure During Forced shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2004, while at power, VCSNS personnel were performing a reactor building inspection to identify the source of reactor coolant system unidentified leakage that was within Technical Specification (TS) limits. At 1129 hours, a pressure boundary leak was identified at the seal injection line nozzle weld to reactor coolant pump "C" (RCP C). Pursuant to TS 3.4.6.2, Action a., VCSNS commenced a controlled reactor shutdown at 1410 on March 30, 2004. During the shutdown, the main turbine experienced higher than normal vibration. At 1517, the turbine was manually tripped at approximately 43% reactor power. Subsequent to the manual turbine trip, feedwater regulating valve IFV-498 failed in the closed position while in automatic with a full open demand signal. The reactor automatically tripped at 1521 due to to-lo level in the "C" steam generator. All control rods fully inserted and all safety systems responded normally. Both motor driven emergency feedwater pumps started as required. The plant stabilized in mode 3. The cause of failure for IFV-498 is attributed to service induced fretting on the positioner pilot valve stem. All positioners on the feedwater regulating valves have been replaced and will be scheduled for future periodic replacement at appropriate intervals. The leakage for RCP C seal injection nozzle has been determined to be a weld failure caused by low-amplitude high cycle fatigue. A modification replaced the line with a new nozzle design with enhanced pipe supports.
3952004002 | Summer 1 | 06/12/2004 | 08/11/2004 | ML04226043 | <strong>Emergency Diesel Generator Start and Load Due to Momentary Fault on Incoming Feed</strong><br /><i>Abstract:&nbsp;</i>At 2029 on June 12, 2004, the normal incoming ESF feed (1DA) to the V. C. Summer Nuclear Station (VCSNS) opened on an under voltage condition. The "A" Emergency Diesel Generator (EDG) started and loads sequenced on as designed. The "A" Residual Heat Removal (RHR) pump started but did not inject any water into the Reactor Coolant System (RCS). The "A" Emergency Feedwater (EFW) pump started and ran for approximately 7 minutes. Other plant equipment and systems also responded as expected. At the time of the event a severe thunderstorm was in progress. A lightning strike upstream of the Parr Substation caused multiple breakers to open at the substation and resulted in a temporary loss of 115kV voltage to the substation. This loss of voltage de-energized the VCSNS 115kV ESF line, which was detected by the 1DA under voltage and degraded voltage relays. These relays opened the normal and emergency feed breakers to 1DA as designed and the "A" EDG started. Loads sequenced on as designed and equipment operated as expected. Operations personnel monitored the plant and verified conditions were stable prior to realigning the plant to the normal feed and securing the EDG at approximately 2300 on June 12, 2004.
3952004003 | Summer 1 | 10/26/2004 | 03/14/2005 | ML05076033 | <strong>Emergency Diesel Generator Start and Load Due to Inadvertent Actuation of 1DA Undervoltage Test Switch</strong><br /><i>Abstract:&nbsp;</i>At 2152 on October 26, 2004, the normal incoming ESF feed (1DA) to the V. C. Summer Nuclear Station (VCSNS) opened on an undervoltage condition. The "A" Emergency Diesel Generator (EDG) started and loads sequenced on as designed. The "A" Residual Heat Removal (RHR) pump started but did not inject any water into the Reactor Coolant System (RCS). The "A" Emergency Feedwater (EFW) pump started and ran for approximately 19 minutes. Other plant equipment and systems also responded as expected. At the time of the event restoration of "A" EDG from scheduled maintenance was in progress. While resetting the "A" Engineered Safety Features Loading Sequencer (ESFLS) the Operator inadvertently bumped the bus undervoltage (UV) toggle switch. This action caused the ESFLS to trip open the normal and emergency feeder breakers to 1DA, resulting in an auto-start of the "A" EDG. Closure of the "A" EDG output breaker initiated the blackout sequence on "A" train ESF equipment. Loads sequenced on as designed and equipment operated as expected. Operations personnel monitored the plant and verified conditions were stable prior to realigning the ESF bus to its normal feed and securing the EDG at approximately 2231 on October 26, 2004. A root cause evaluation determined the cause to be the operator being very casual while manipulating the reset switch and no equipment guard to prevent actuation of the undervoltage test switch.
3972004001 | Columbia | 01/23/2004 | 03/23/2004 | ML04091019 | <strong>Unanticipated inoperability of both Control Room Emergency Filtration (CREF) subsystems</strong><br /><i>Abstract:&nbsp;</i>At 1315 on January 23, 2004, with the plant in Mode 1 at approximately 100 percent rated thermal power, it was determined that a condition prohibited by the Columbia Generating Station Technical specifications (TS) existed from 1500 on October 27 through 2100 on October 29, 2003 and from 1305 on November 10 through 1052 on November 11, 2003 when testing was conducted to measure control room in-leakage. During this test, common ducts for both Control Room Emergency Filtration (CREF) subsystems were breached multiple times by removing duct access panels to install and remove test equipment. During the time the access panels removed, a flow path was created that would have challenged the CREF's ability to pressurize the control room and mitigate the consequences of an accident. Both CREF subsystems were determined to have been inoperable when the access panels were removed. With two CREF subsystems inoperable, TS 3.7.3 directs immediate entry into TS Limiting Condition for Operation (LCO) 3.0.3. The fact that removing the access panels caused both CREF subsystems to become inoperable was not recognized at the time the tests were performed because the HVAC ducts were allowed to be breached for short periods of time by the plant barrier impairments procedure. The cause of this event is attributed to inadequate guidance in the Columbia Generating Station barrier impairment procedure. The cause of the inadequate guidance in the procedure was a lack of understanding of regulatory guidance associated with barrier impairments.
3972004002 | Columbia | 02/21/2004 | 04/20/2004 | ML04118030 | <strong>Reactor Core Isolation Cooling Declared Inoperable Due to Relay Failure</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2004, Columbia Generating Station (Columbia) was in Mode 1 with the reactor operating at approximately 100 percent rated thermal power. At approximately 08:41 the Reactor Core Isolation Cooling (RCIC) system was declared inoperable due to a loss of control power to the RCIC reactor pressure vessel injection valve (RCIC-V-13). The cause was a failure of a normally energized under-voltage relay. The function of the relay is to sense a loss of voltage to the valve motor operator, interrupt valve control power and provide annunciation in the control room. The relay failed due to a failed relay coil that was subjected to long-term heating. Previous reviews to identify relays that should be periodically replaced did not capture this relay because it had no equipment part number and was not included in the master equipment list, the database used to conduct these reviews. This event posed no threat to the health and safety of the public or plant personnel. The failed relay was replaced and the RCIC system returned to operable status in 12 hours 48 minutes. Thermography was performed on 43 relays in the DC distribution system and one relay was identified for replacement. Additional actions are planned to identify other relays in the DC distribution and selected portions of the 480 Volt AC systems that need periodic replacement.
3972004004 | Columbia | 07/30/2004 | 10/04/2004 | ML04288049 | <strong>Reactor Scram Due to Failure of a Ceramic Capacitor on a NUCANA Servo Driver (NSD) Circuit Board</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2004, Columbia Generating Station (Columbia) was in Mode 1 with the reactor operating at-100 percent power. At 09:23 PDT, the reactor automatically scrammed when the reactor protection system (RPS) received trip signals from three out of four reactor steam dome pressure - high instrument channels. The high reactor steam dome high-pressure condition was a result of a turbine governor valve (MS-V-GV/1) drifting closed. The turbine governor valve drifted closed due to a failure of a bypass capacitor on a NUCANA Servo Driver (NSD) circuit board associated with the governor valve electro-hydraulic control system. The failed capacitor was a monolithic ceramic capacitor. This capacitor provides high frequency bypass filtering for the onboard power supply at one of the operational amplifiers. The capacitor failed with low resistance which caused a high current load that eventually caused the circuit board protective fuse to clear and the closure of MS-V-GV/1. This event posed no threat to the health and safety of the public. The NSD circuit board was replaced and a detailed failure analysis will be performed on the failed circuit board.
3972004005 | Columbia | 08/15/2004 | 10/13/2004 | ML04299039 | <strong>Reactor Manual Scram During Plant Startup due to High Water Level in the Pumped Drain Tank</strong><br /><i>Abstract:&nbsp;</i>During a reactor startup on August 15, 2004, with reactor power at approximately 18%, plant operators manually initiated the Reactor Protection System in response to decreasing water level in the Reactor Pressure Vessel (RPV) following a reactor feedwater pump (RFW-P-1A) trip. The steam driven RFW-P-1A tripped as designed due to high water level in the pumped drain tank. The Reactor Core Isolation Cooling system was initiated to maintain RPV level until pressure was reduced to within the capacity of the condensate booster pumps to supply water. The subsequent plant transition to mode 4 was normal in all respects and there were no safety consequences related to the event.
3972004006 | Columbia | 08/17/2004 | 10/13/2004 | ML04299039 | <strong>Reactor Manual Scram During Reactor Startup Due to Improper Restoration of Feedwater Heater</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2004, with a plant startup in progress and with the plant in Mode 1 at approximately 20% power, a licensed control room operator improperly filled a feedwater heater with condensate following maintenance. This improper filling evolution tripped the only running reactor feedwater pump initiating a loss of feedwater transient. The reactor was scrammed manually prior to level reaching the automatic trip set point and water level stabilized using the Reactor Core Isolation Cooling (RCIC) system and the recovered reactor feedwater pump. Failure of the Reactor Operator to follow written instructions resulted in uncontrolled filling of the feedwater heater and a momentary drop in condensate system pressure. The momentary drop in condensate system pressure directly resulted in a trip of the running feedwater pump on low suction pressure. This event posed no threat to the health and safety of the public or plant personnel. All safety equipment was available during this transient and performed as expected. Following the plant scram, the plant was stabilized in Mode 3 without further event.
3972004007 | Columbia | 08/09/2004 | 09/30/2004 | ML04288043 | <strong>Detection of Contraband at Protected Area Access Control Checkpoint</strong><br /><i>Abstract:&nbsp;</i>At 0549 on August 9, 2004, with Columbia Generating Station (Columbia) in mode 4, Energy Northwest security X-ray machine operators detected a loaded handgun in the backpack of an Energy Northwest employee at Columbia's Protected Area (PA) access control point (ref: Event Report 40933). Security personnel immediately controlled the handgun and the individual was segregated and searched. The individual's access to the PA was suspended and he left the owner controlled area following a fitness for duty test. Local law enforcement (Benton County Sheriff) responded and took possession of the firearm. This event meets the criteria specified in 10 CFR 73, Appendix G, paragraph I(d), as this was an attempted introduction of contraband into Columbia's PA. This report is made pursuant to the requirement of 10 CFR 73 Appendix G(I) for a 60-day follow-up written report.
3972004008 | Columbia | 11/22/2004 | 01/18/2005 | ML05031034 | <strong>Reactor Core Isolation Cooling Isolation Due to Inadvertant Closure of Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2004, Columbia Generating Station (Columbia) was in Mode 1 at approximately 100 percent of rated thermal power. At 17:30 PST, the Reactor Core Isolation Cooling (RCIC) system was declared inoperable after one of its steam supply containment isolation valves (RCIC-V-63) was inadvertently closed during the performance of a channel functional test/channel calibration procedure. The procedure was discontinued and plant operators verified that the High Pressure Core Spray System was operable as required by Technical Specifications. The RCIC system was restored to its normal standby lineup and declared operable two hours and three minutes later. The immediate cause was a personnel error by one of the I&C technicians performing the procedure. The root causes included over-reliance on self-checking and peer-checking, the procedure did not contain adequate precautionary information, no direct field supervision of the evolution, and no integrated risk assessment of the work. A briefing was conducted to explain the event to Electrical and I&C craft and supervisors. The procedure being used, and other similar procedures, will be revised to add appropriate precautions. Additional expectations for frequency, depth, and quality of supervisory field oversight are being implemented. A new integrated risk management procedure will reduce the potential for similar errors.
4002004001 | Harris | 11/17/2003 | 04/12/2004 | ML04111092 | <strong>"A" Containment Hydrogen Analyzer Inoperable</strong><br /><i>Abstract:&nbsp;</i>Harris Nuclear Plant (HNP) personnel performed surveillance testing of the "A" Containment Hydrogen Analyzer on February 9, 2004. During the test, the analyzer did not respond as expected. An investigation identified that leads had been reversed during the last performance of the surveillance test on November 17, 2003, resulting in the equipment being inoperable for a period of time greater than allowed by technical specifications. Immediate corrective action restored the leads to their correct configuration and performed the surveillance test to restore the equipment to operable condition. The ‘B' Containment Hydrogen Analyzer was also verified to be operable. The root cause of the event is that the procedure did not clearly identify the specific leads to be lifted during the performance of the test, which resulted in the wrong leads being lifted and incorrectly restored at the completion of the test. Corrective actions included revising the procedure to clearly identify which leads are to be lifted and to ensure the hydrogen analyzer is functional after termination of the wiring during restoration from the test.
4002004002 | Harris | 02/22/2004 | 04/22/2004 | ML04124014 | <strong>Containment Fan Cooler (AH-1) Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2004, Harris Nuclear Plant (HNP) personnel discovered the discharge gravity damper for containment fan AH-1A partially open with the fan out of service. With the discharge gravity damper of fan AH-1A in the open position, a recirculation path was created for operating fan AH-1 B. Therefore, some discharge flow from fan AH-1 B was being diverted through fan AH-1A rather than to its normal discharge flow path. This diversion of discharge flow from containment fan cooler AH-1 is a degraded condition that potentially existed since the last time fan AH-1A was operated on February 22, 2004. It is postulated that the discharge gravity damper of fan AH-1A failed to close when the fan was stopped at that time. This condition had potentially existed for approximately 10 days, which would have exceeded the allowed outage time per technical specifications. Immediate corrective action included closing the discharge gravity damper of fan AH-1A. The root cause evaluation of the event has not been completed to date pending further investigation. The root cause and corrective actions to prevent recurrence will be submitted in a supplemental report.
4002004003 | Harris | 05/06/2004 | 07/02/2004 | ML04190026 | <strong>Automatic Reactor Trip Due to Rod Control Card Failure</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2004 at 12:52 PM EDT, the reactor automatically tripped from 100% power due to a power range flux rate signal. The operations staff responded to the event in accordance with applicable plant procedures. The plant was stabilized at normal operating no-load reactor coolant system (RCS) temperature and pressure following the reactor trip. The trip was caused by the failure of a regulation card in the Rod Control System [AA]. This resulted in the loss of stationary gripper coil current to the Control Rod Drive Mechanisms (CRDMs) for one of the three Shutdown Banks of control rods. Loss of stationary gripper coil current resulted in the insertion of the four associated control rods into the reactor core which led to the high power range negative flux rate trip. Corrective actions included replacing the failed card with a spare and performing visual inspection and testing of additional cards in the Rod Control System Power Cabinets. These actions were completed prior to plant startup.
4002004004 | Harris | 09/27/2004 | 11/26/2004 | ML04335038 | <strong>Unanalyzed Condition Due to Inadequate Separation of Associated Circuits</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2004, the Harris Nuclear Plant (HNP) identified that certain cables for redundant components credited by the Safe Shutdown Analysis (SSA) lack the required degree of separation in one fire area. This discovery was identified during a comprehensive review of the HNP SSA as part of the corrective actions for previously reported conditions (reference HNP LER 2002-004-05 submitted November 15, 2004). As a potential result, spurious opening of multiple valves in the Reactor Coolant System (RCS) could transfer some coolant inventory to containment. However, by the design of this potential pathway, any transfer of coolant inventory is less than the make-up capacity of one charging pump. The most probable cause of this historical condition is that the drawing change requiring these cables to be protected by fire barrier material was apparently never issued during plant construction. Subsequently, the fire barrier material was never installed as required by the SSA. At the time of this discovery, a roving fire watch was already posted in the fire area of concern and remains posted. Design changes or other methods approved by the NRC will be used to restore compliance. No corrective actions are associated with the cause of this historical condition since it is the only condition of its type identified during the comprehensive review of the HNP SSA.
4002004005 | Harris | 10/18/2004 | 12/17/2004 | ML04358023 | <strong>Unplanned Start of 'A' Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2004, with the plant in Mode 5 and the Reactor Coolant System (RCS) depressurized, Emergency Bus 1A-SA lost power resulting in the automatic start and loading of the 'A' Emergency Diesel Generator (EDG). When Bus 1A-SA lost power, its associated loads, including the 'A' Residual Heat Removal (RHR) pump, were de-energized. The 'A' RHR pump had been providing shutdown cooling. The operations staff responded in accordance with plant procedures and restarted the 'A' RHR pump. RCS temperature rose approximately six degrees Fahrenheit during the 4 minute, 39 second interval in which 'A' RHR pump flow was interrupted. The 'B' safety train (including the 'B' RHR train) was the "protected" train and was operable throughout the event. The loss of power to Bus 1A-SA was caused by ineffective taping of leads that were lifted for testing. Two leads with loose tape came into contact, resulting in a bus undervoltage relay actuation on Bus 1A-SA. This caused the normal power supply breaker to the bus to open, and the 'A' EDG to subsequently start. Corrective actions include improving maintenance training on standards for taping lifted leads, changing outage planning/risk management procedures to ensure the operating train of shutdown cooling is not challenged by work activities, and providing additional guidance to operations staff on outage work control and risk management.
4002004006 | Harris | 11/07/2004 | 01/06/2005 | ML05012012 | <strong>Manual Actuation Of Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2004, with reactor power approximately 7%, the 'A' auxiliary feedwater pump was manually started in response to lowering 'C' steam generator level. The plant was subsequently cooled down and inspections conducted on the 'C' main feedwater isolation valve (MFIV) found that the stem was fractured at the backseat and the seat rings were damaged. Subsequent inspections of the 'A' and 'B'' MFIVs found that these valves had damaged seat rings; however, no stem problems were identified. The cause of the seat ring damage was a modification performed in 2000 that had insufficient margin in design, and insufficient controls over field implementation of the design, to prevent the valve discs from being fully retracted from the seat rings during the open stroke and impacting the seat rings during the close stroke. The cause of the 'C' MFIV stem failure was fatigue, due to a combination of a high stress concentrator at the stem backseat transition, cyclic loading of the actuator, and potential interaction with the damaged seat rings. The damaged seat rings were replaced or repaired, the valve stems on all three MFIVs were replaced, and a pressure regulator on the 'C' MFIV was replaced. Several design changes were made to address the causes of the valve damage. Also, small pieces of foreign material were retrieved from the feedwater system.
4102004001 | Nine Mile Point 2 | 01/28/2004 | 02/27/2004 | ML04069074 | <strong>Inoperability of a Control Room Envelope Filtration System Train Due to a Locked Closed Damper</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2004, while performing surveillance testing on the Division II Control Room Outside Air Special Filter Train (CROASFT), the required flow to establish test conditions could not be achieved. Backdraft damper 2HVC*DMP93, on the inlet ductwork to the Division II CROASFT, was determined to be in the locked closed position, causing the Division II Control Room Envelope Filtration (CREF) subsystem to be inoperable. The plant entered Action A of Technical Specification 3.7.2, which requires restoration of the inoperable CREF subsystem within 7 days. Further investigation determined that damper 2HVC*DMP93 had been locked closed for approximately 4.5 months, and that the other redundant CREF subsystem (Division I) had also been inoperable on several occasions during that 4.5 month period. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as “Any operation or condition which was prohibited by the plant's Technical Specifications," and 10 CFR 50.73(a)(2)(v) as “Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (D) Mitigate the consequences of an accident.” The cause of the event was a deficiency in the blade lock for damper 2HVC*DMP93, whereby setscrews were not holding the blade lock securely in the disengaged position. A contributing cause was inadequate acceptance criteria in the CREF system monthly surveillance test procedure. The corrective actions include modifying the blade lock to provide additional assurance that it will not inadvertently engage, and revising the CREF system monthly surveillance procedure to provide guide values for acceptable flow and differential pressure conditions.
4132004001 | Catawba 1 | 01/14/2004 | 06/15/2004 | ML04175011 | <strong>Gas Accumulation in Centrifugal Charging Pump Suction Piping</strong><br /><i>Abstract:&nbsp;</i>On January 14, 2004 gas was discovered at the suction piping of the centrifugal charging pumps. This condition resulted in the unit being in an unanalyzed condition. The system was vented and the pumps restored to an operable condition. The cause of the gas accumulation was reverse leakage from relief valve 1NV235 on the emergency boration line. Contributing to this event is the piping configuration of the pressurizer sample purge line connection to the volume control tank relief valve header. The relief valve 1NV235 has been replaced. The pressurizer sample purge alignment to the relief valve header is temporarily isolated which removes the source of gas from 1NV235 discharge piping. The long term corrective action is to relocate the Unit 1 primary sample purge line connection to the relief valve header. During the event investigation and troubleshooting, the charging pump suction piping was frequently monitored and vented to maintain the system filled with water. No pump degradation was observed. No plant transient occurred that relied upon the safety function of the charging pumps or safety injection pumps. The overall safety significance of this event was determined to be minimal and there was no actual impact on the health and safety of the public.
4132004002 | Catawba 1 | 02/22/2004 | 04/22/2004 | ML04119043 | <strong>Manual Reactor Trip Initiated Due to the Closure of a Main Feedwater Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2004, at 1729 hours, with Catawba Unit 1 operating in Mode1 at 100% power, the hydraulic system for the actuator on 1B Steam Generator Main Feedwater Isolation valve (1CF-42) failed and the valve closed. As a result, the Operators manually tripped the reactor. This event was caused by the equipment failure of the valve actuator for1CF-42. The plant response to the reactor trip remained within the limits of the Updated Final Safety Analysis Report. Corrective actions for this event included replacing the actuator for valve 1CF-42.
4132004003 | Catawba 1, Catawba 2 | 06/23/2004 | 07/18/2005 | ML05207060 | <strong>Unanalyzed Condition Due To Inadequate Evaluation of Fire Interactions ¦</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2004 Catawba identified an unanalyzed condition related to fire protection cable separation requirements. A fire in the Unit 2 A-train 4160V switchgear room (2ETA) [EIIS:EB) was postulated to cause a hot short to spuriously close centrifugal charging pump suction valve 2NV188A and damage the running pump (EIIS:CB). Because the running pump and the 4160V switchgear room maybe opposite train components, the postulated fire may result in both charging pumps being unavailable for post-fire plant recovery. A fire in 2ETA may also affect the standby makeup pump. This postulated loss of both trains of charging pumps was not analyzed in the Safe Shutdown Analysis. On June 24, 2004 Unit 1 was determined to have a similar vulnerably for a fire in the S-train 4160V switchgear room (1ETB). Further review of the cable routing for the charging pump suction valves identified a fire in 5 additional Unit 1 fire areas and 6 additional Unit 2 fire areas may result in damage to both charging pumps. The Safe Shutdown Analysis for these fire areas was based on one charging pump being available. The apparent cause is inadequate original Safe Shutdown Analysis of certain spurious hot short valve operations. Corrective actions included fire watches for the switchgear rooms until operating procedures were implemented to protect the correct train charging pump for post-fire plant recovery. The conditions addressed by this report are related to postulated accidents and potential failures and had no direct effect on the health and safety of the public.
4132004004 | Catawba 1 | 12/05/2004 | 02/02/2005 | ML05047024 | <strong>Spurious Moisture Separator Reheater High Level Actuation Resulting in an Automatic Turbine Trip and Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 5, 2004, at 2135 hours, with Catawba Unit 1 operating in Mode 1 at 100% power, an automatic reactor trip occurred due to a turbine trip above P-9 (69% power). The turbine trip was due to an invalid high water level indication from two of the three level switches for the 1B moisture separator reheater. The root cause of the reactor trip was due to micro-switch mechanisms on the two level switches being out of adjustment, concurrent with external vibration to the switches. The plant response to the reactor trip remained within the limits of the Updated Final Safety Analysis Report. Major plant equipment operated as expected. This event was of no significance with respect to the health and safety of the public. Corrective actions for this event included inspecting all Unit 1 and Unit 2 micro-switch positions, and adjusting or replacing the switch mechanisms as necessary.
4142004001 | Catawba 2 | 09/16/2004 | 11/09/2004 | ML04328050 | <strong>Reactor Coolant System Pressure Boundary Leakage Due to Small Cracks Found in Steam Generator Channel Head Bowl Drain Line on 2C & 2D Steam Generators</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2004, with Catawba Unit 2 in MODE 6 entering a refueling outage, a visual examination was performed on the steam generator (SG) 2A, 2C & 2D lower head bowl drains. Reactor Coolant System (RCS) pressure boundary leakage was identified on the 2C and 2D SG bowl drains. The 2A SG lower head bowl drain did not have any pressure boundary leakage. The pressure boundary leakage path was suspected to be the nozzle coupling to vessel weld. This event was reported to the NRCOC at 1131 on September 17, 2004 pursuant to 10 CFR 50.72(b)(ii)(A). The most probable cause of the SG Bowl Drain leak is primary water stress corrosion cracking (PWSCC). The 2C & 2D SG bowl drain leaks were subsequently repaired, examined and tested. The 2A SG bowl drain was also repaired similar to the 2C & 2D SG bowl drains as a preventive measure. The 2B SG bowl drain had been repaired in 2001 due to a similar leak (LER 414/01-002). A corrective action from the previous LER was the development of a program to address Alloy 600 issues which included the inspections that discovered the events in this LER. This issue is not applicable to Unit 1 because the SGs area different design that does not have a similar drain line. The overall safety significance of this event was determined to be minimal and there was no actual impact on the health and safety of the public.
4142004002 | Catawba 2 | 10/28/2004 | 12/15/2004 | ML04364027 | <strong>Manual Reactor Trip Initiated Due to Control Rods from Shutdown Bank D Dropping into the Core</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2004, at 0052 hours, with Catawba Unit 2 operating in Mode 1 at 100% power, all four control rods from Shutdown Bank D inserted into the core. Consequently, the Operators responded by manually tripping the reactor. The plant response to the reactor trip remained within the limits of the Updated Final Safety Analysis Report. All plant equipment operated as expected. The most probable cause of this event was an intermittent failure of a circuit card in the rod control system. Corrective actions for this event included replacing the suspect circuit card and sending the card to the vendor for further analysis. This event was of no significance with respect to the health and safety of the public.
4162004001 | Grand Gulf 1 | 02/24/2004 | 04/15/2004 | ML04112026 | <strong>Unplanned Loss of Alternate Decay Heat Removal System Operability</strong><br /><i>Abstract:&nbsp;</i>On 2/24/04 Residual Heat Removal System A was the operating shutdown decay heat removal (DHR) system with the Alternate Decay Heat Removal System (ADHR) as the operable alternate. Division 2 Electrical Bus 16AB was de-energized at 0503 for a planned bus outage. This outage de-energized isolation valves E12-F004C and E12-F064C. These valves must have power or be closed for ADHR to be operable. It was identified at 0630 that these valves were open with their motors de-energized. ADHR was declared inoperable and LCO 1-OTS-04-0015 was entered. Technical Specification (TS) 3.9.9 action A requires verification of an alternate method of decay heat removal (DHR) within one hour for each inoperable required DHR subsystem. ADHR was discovered to be inoperable1- hour and 27- minutes after the event occurred. This resulted in exceeding the one hour TS time limit. TS 3.9.9 action B was not met due to not meeting the one hour time limit of action A. At 0817 the two valves were closed. ADHR was declared operable and the LCO exited. ADHR remained functional during the event due to installed check valve E12-F031C. This check valve would have prevented flow through the isolation valves. ADHR was inoperable per the SOI, which does not consider the check valve in determining operability. This event is not considered risk significant. There were no safety system functional failures.
4162004002 | Grand Gulf 1 | 04/04/2004 | 06/03/2004 | ML04156056 | <strong>Loss of RHR B Operability Due to Misaligned Minimum Flow Valve</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2004, the Residual Heat Removal (RHR) B minimum flow line was tagged out to allow piping replacement. During welding of the piping, the RHR B minimum flow isolation valve (1E12-F018B) was closed to stop leakage through the piping. Piping replacement was completed and operators were dispatched to complete the SOI lineup which included there positioning of 1E12-F018B. The operators initialed the lineup sheets which incorrectly indicated that 1E12-F018B was in the locked-open position. When the RHR B quarterly functional test was performed on April 4, 2004, system pressure was determined to be higher than expected. Operations directed the lineup verified and found 1E12-F018B closed. 1E12-F018B was repositioned to locked-open on April 5, 2004 in addition to conducting manual valve line-ups. Subsequent testing of the B RHR Pump indicated no changes in pump performance as a result of operation of the B RHR Pump with 1E12-F018B closed. A condition report was initiated to track long term corrective actions. The condition was caused by mis-application of self checking and peer checking to ensure the valve was in its required position. LCO Required Action Completion Time for Tech Spec 3.5.1 was exceeded and this condition is reportable per 10CFR50.73(a)(2)(i)(B). This condition did not result in a Safety System Functional Failure.
4232004001 | Millstone 3 | 04/30/2004 | 04/01/2005 | ML05104032 | <strong>Technical Specification Action Statement Not Met</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2004, while operating at 0% power in Mode 5, an oncoming Shift Manager performing a main control boardwalk down (at approximately 1800) questioned if the equipment failure in the electrical distribution system that had occurred earlier required Limiting Condition for Operation (LCO) Action in accordance with plant Technical Specification(TS) 3.8.3.2 "Onsite Power Distribution - Shutdown." Plant Technical Specification 3.8.3.2 has one Action. It states, in part, 'With any of the above required electrical busses not energized in the required manner, immediately suspend all operations involving.. .positive reactivity changes..." At the time of this discovery, the plant was in the process of heating up as part of the startup sequence following a refueling outage. The Shift Manager directed that the plant heatup be suspended. The time period from the equipment failure until the plant heatup was suspended was approximately three hours.0Upon further review, it was determined that the increase in temperature from 135 to 165F over this (approximately)three hour time period did add positive reactivity. Also, upon subsequent review, two additional additions of positive reactivity were identified during the time period that TS 3.8.3.2 Action applied. At 1559 and 1659 on April 30, 2004, hydrazine and primary grade water additions were made to the reactor coolant system, constituting positive reactivity additions. Since TS 3.8.3.2 Action should have been entered at 1512 when Inverter #INV-4 failed and swapped to its alternate source, and the primary grade water additions and plant heatup constituted positive reactivity changes, this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant's Technical Specifications.The cause of the delayed entry into the Action for TS 3.8.3.2 is human error and the individuals involved have been coached. Additional corrective actions are being taken in accordance with the Millstone Corrective Action Program.
4232004002 | Millstone 3 | 05/26/2004 | 11/10/2004 | ML04323057 | <strong>Inoperable Motor Driven Auxiliary Feedwater Pump Resulting From a Degraded Service Water System Brazed Joint</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2004, while operating in Mode 1 at 100 percent power, an investigation determined that a potential existed for the operability of the 'B' motor driven auxiliary feedwater (MDAFW) pump to have been impacted by a degraded service water piping connection that was identified and corrected during the unit's most recent refueling outage on April 15, 2004 . A pipe separation at this location would create a service water spray hazard to the motor of the 'B' MDAFW pump. The spray hazard was determined to represent a potential to render the pump unavailable. This historical condition potentially affected the credited design function of the auxiliary feedwater system coincident with a seismic event. The inoperability of the 'B' MDAFW pump would constitute a condition that is prohibited by the plant's technical specifications and is being reported pursuant to reporting criteria of 10 CFR 50.73(a)(2)(i)(B). This condition is historical in nature and the apparent cause for the condition was a poor work practice during original installation. No unavailability of safety related equipment or systems, piping failure or flow diversion, had resulted from the affected joint. This condition would not have impacted the redundant 'A' train MDAFW pump or turbine driven AFW pump. This condition has a level of risk that is characterized as very small per Regulatory Guide 1.174, "An Approach for Using Probabilistic Risk Assessment in Risk-Informed Decisions on Plant-Specific Changes to the Licensing Basis. " The corrective action to prevent recurrence of this specific condition has been completed during the refueling outage. The 'A' and 'B' Engineered Safety Features (ESF) supply header tees were cut out and replaced with new 3 inch butt-welded piping and branch weldolets.
4232004003 | Millstone 3 | 11/04/2004 | 01/03/2005 | ML05013012 | <strong>Oil Leak May Have Caused Unrecognized Inoperability of Safety Injection Pump</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2004, while operating at 100% power in Mode 1, it was determined that an existing oil leak, previously assessed as not affecting the operability of safety injection pump 3SIH*P1A, may have rendered the pump inoperable. A similar, historical condition was identified for 3SIH*P1B. 3SIH*P1A had a 6 drop per minute (dpm) oil leak identified on October 14, 2004 and not corrected until November 4, 2004. The investigation of this condition identified that 3SIH*P1B was considered operable with a 4 dpm oil leak first identified on August 8, 2002 and corrected on April 16, 2003. Upon further evaluation, it was determined that oil leaks of 6 dpm and 4 dpm would have depleted the pumps' usable oil after a running period of approximately 11 and 17 days, respectively. Although 3SIH*P1A and 3SIH*P1B have a post-LOCA function, there is no established design basis run time requirement described in the FSAR for Millstone Unit 3. Actions to establish an appropriate design basis are in progress. The root cause of these conditions is determined to be a latent organizational weakness in understanding the risks and consequences of oil leaks on safety related equipment. This preliminary report documents the potential for these conditions to be reportable under 10CFR50.73(a)(2)(i)(B), related to operation in a condition prohibited by Technical Specifications, as well as the provisions of 10CFR50.73(a)(2)(v)(B) related to loss of safety function. A supplement to this LER will be submitted upon completion of the ongoing evaluation.
4242004001 | Vogtle 1 | 03/27/2004 | 05/22/2004 | ML04147012 | <strong>Manual Reactor Trip Following Loss of Main Feedwater Pump Speed Control</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2004, at 2110 EST, control room operators tied the generator to the grid. At 2150 EST, an operator observed steam flow/feed flow mismatch alarms and noticed that the speed of the inservice main feed pump, MFP B, was increasing. The feed pump speed control was switched from automatic to manual, but to no effect. Operators then changed speed control systems. This also had no effect on the increasing speed, and steam generator (SG) water levels began to fluctuate. Operators manually tripped the reactor at 2205 EST. The operators then tripped MFP B and the auxiliary feedwater system (AFW) actuated. The unit was stabilized in Mode 3 (Hot Standby) at 2209 EST. The cause of this event was a control valve hydraulic operating cylinder sticking in the open position so that the speed of the feed pump turbine could not be controlled. The valve stuck open due to misalignment of the hydraulic cylinder shaft with bushings in the cylinder cover. The bushings were properly aligned, the feed pump returned to service, and the reactor returned to normal power operations.
4242004002 | Vogtle 1, Vogtle 2 | 04/22/2004 | 06/17/2004 | ML04173024 | <strong>Closure Of Control Room Air Damper Results In Tech. Spec. Non-Compliance</strong><br /><i>Abstract:&nbsp;</i>On the morning of April 22, 2004, a shift turnover walkdown was in progress in the Unit 1 control room. At 0540 EDT, the Unit Shift Supervisor (USS) found the Control Room Normal HVAC Outside Air Damper, AHV-12153, closed. The pressure differential between control room air and the outside atmosphere was checked and found to be zero. This condition stops flow past the control room air intake radioactive gas monitors, rendering them inoperable. After verifying that there was no valid reason for maintaining AHV-12153 closed, it was re-opened, restoring the control room differential pressure. It was determined that AHV-12153 was closed the previous day, during switchgear maintenance. Because the Technical Specifications (TS) require the control room emergency filtration system (CREFS) to be placed in the emergency operating mode if the control room air intake radioactive gas monitors are inoperable for more than one hour, and this was not done, the units operated in a condition prohibited by the TS. An investigation found that maintenance was performed on de-energized switchgear, exercising a cell switch which closed the outside air damper. Therefore, the cause of this event was a failure of the work planning process to recognize the impact of the planned maintenance. Changes to this process are in progress.
4252004001 | Vogtle 2 | 04/18/2004 | 06/16/2004 | ML04170007 | <strong>Auxiliary Feedwater System Actuation While Breaking Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2004, while at 0 percent power and shutting down for a refueling outage, personnel were performing steam generator feedwater pump (SGFP) turbine testing. As the reactor coolant system temperature and pressure decreased, a caution in the operating procedure required disabling of the auxiliary feedwater (AFW) actuation signal that is initiated from a trip of both SGFPs, prior to breaking condenser vacuum. However, this would have prevented completion of the SGFP turbine testing, so the AFW actuation signal was not disabled at that time. Since problems were encountered, the testing was delayed as allowed by the surveillance procedure. Later, at 1238 EDT, the Unit Shift Supervisor (USS) directed the Balance-Of-Plant Operator (BOP) to break condenser vacuum. This was not in compliance with the caution in the procedure to ensure the AFW actuation signal was disabled. When condenser vacuum was broken, the SGFPs tripped which then generated an AFW actuation signal. The AFW discharge valves went fully open and operators acted to throttle these valves, maintaining proper SG water levels. The cause of this event was the failure of the control room staff to adequately sequence the work activities associated with the start of the refueling outage. Briefings will be held with all shifts of control room operators, discussing this event and reinforcing management expectations.
4252004002 | Vogtle 2 | 05/11/2004 | 08/04/2004 | ML04222008 | <strong>Containment Debris Could Have Resulted In Loss of Safety System Function</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2004, an evaluation was completed that determined a safety system functional failure could have occurred following the 2R10 refueling outage when unit heat-up occurred on May 11, 2004. Specifically, it was determined that the containment building held debris in an amount adequate to block the containment sump screens, which could result in inadequate net positive suction head and possible failure of the residual heat removal (RHR) pumps to perform at design limiting conditions. This may have occurred following a design basis accident had these pumps been called on to operate and draw suction from the containment sumps. The condition existed for a period of 9 hours and 53 minutes after mode 4 and Mode 3 entry. Walkdowns were conducted to remove the debris. The cause of this event is low available margin in the sump screens such that a very small amount of debris left in containment is sufficient to block the sump screens based on the very conservative assumptions used in determining the potential for sump blockage. SNC will pursue design changes to increase sump screen margin. In the interim, prior to the implementation of design changes, SNC will pursue improvements to containment building lighting (temporary lighting fixtures) and materials visibility (high visibility tools, etc.) to minimize containment debris to the extent possible.
4252004003 | Vogtle 2 | 10/22/2004 | 12/10/2004 | ML04349016 | <strong>Inoperable ESF Room Cooler Results in a Condition Prohibited By the Tech. Specs.</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2004, a system engineer found a fan compartment access door improperly secured on an Auxiliary Relay Cabinet Room Cooler. The access door was hinged, and latched at top and bottom. However, to maintain seismic qualification of this ESF room cooler, the door must be held closed either with clips that are screwed to the housing, or by utilizing a hasp with a padlock. Neither method was installed. A padlock was quickly placed into the existing hasp and the cooler was returned to operable status. However, the failure to maintain the room cooler seismically qualified represents operation of Unit 2 in a condition prohibited by the Technical Specifications. The access door to the room cooler is situated in a difficult to reach location and, in all likelihood, had not been opened since prior to initial unit start-up in 1989. Therefore, the cause of this event was improper original construction and improper start-up acceptance in failing to ensure the door met seismic qualifications by being properly secured. A walkdown of approximately 50 ESF room coolers has been completed and no similar conditions have been found that would render coolers inoperable.
4252004004 | Vogtle 2 | 11/20/2004 | 08/08/2005 | ML05221008 | <strong>AUTOMATIC REACTOR TRIP FOLLOWED BY SAFETY INJECTION</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2004, `B' Train Solid State Protection System Testing was in progress with the `B' Train in the "inhibit mode" for testing. Operators performing the test erroneously operated the `A' Train Solid State Protection multiplexer test switch which disabled `A' Train SSPS completing the logic for an automatic reactor trip at 1140 EST. Subsequent to the trip, the Loop 2 Tavg instrument channel failed at its full power value causing a full-open steam dump demand. Control room personnel responded to the decreasing reactor coolant system (RCS) temperature by initiating a Main Steamline Isolation, but the pressure drop was sufficient to result in an automatic Safety Injection (SI) actuation. As designed, the SI signal initiated a Control Room Isolation, a Containment Ventilation Isolation, start of both Emergency Diesel Generators and a Phase A Containment Isolation . After RCS pressure recovered, control room personnel secured Safety Injection and transitioned the unit to normal operation in Mode 3 (Hot Standby). The cause of the reactor trip was human error in that the operator erroneously manipulated a test switch on the `A' Train SSPS. The cause of the SI was the failure of a lead-lag circuit card that lead to the failure of the Loop 2 Tavg circuitry and subsequent full opening of the steam dump valves and RCS pressure drop. A number of actions were implemented to address the human performance errors and the failed lead-lag card was replaced and tested satisfactorily.
4402004001 | Perry | 05/22/2004 | 09/18/2004 | ML04272035 | <strong>Emergency Service Water Pump Failure</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2004, at 0150 hours with the Perry Nuclear Power Plant operating in MODE 1 at 100 percent power, Emerged Service Water (ESW) pump A was declared inoperable due to pump shaft coupling failure. At 1600 on May 21, 2004, a power reduction was ordered to shutdown the plant to complete repairs. MODE 3 (hot shutdown) was entered at 2139 on May 22, 2004. MODE 4 (cold shutdown) was entered at 0619 on May 23, 2004. Although bypassing of steam to the main condenser was available, an alternate decay heat removal system was not established in MODE 4 within the Technical Specification (TS) 3.4.10 completion time. The failure mechanism of the coupling was stress corrosion cracking (SCC). This was the second occurrence of this type of failure on the same pump in less than one year. Since the ESW pump B could not be physically inspected, an engineering evaluation for the susceptibility of ESW pump B to SCC could not support continued operability. At 1500 on May 24, 2004 ESW pump B was declared inoperable. The stress corrosion cracking failure mode was due to marginal coupling design, insufficient coupling keyway corner radius, and susceptible environmental conditions. The ESW pump B continued to operate until removed from service for inspection and upgrade to a new coupling design. Both A and B ESW pump couplings were replaced with couplings constructed of less susceptible material and additional design margin. This event is considered to be of very low safety significance.
4402004002 | Perry | 12/23/2004 | 02/21/2005 | ML05061002 | <strong>Unplanned Automatic Oscillation Power Range Monitor SCRAM</strong><br /><i>Abstract:&nbsp;</i>On December 23, 2004, at 2345 hours, both reactor recirculation system (RRC) pumps at the Perry Nuclear Power Plant (PNPP) unexpectedly downshifted from fast to slow speed. At the time of RRC pump speed downshift, the plant was stable in Operational Condition 1 at 100 percent rated thermal power. Reactor power decreased to about 44 percent and then gradually increased to 55 percent rated thermal power. The power and flow reduction placed the plant in the immediate exit region of the power-flow map . At 2354 hours a reactor scram occurred due to core oscillations being detected by the oscillation power range monitor (OPRM). All control rods fully inserted. The cause of the scram was determined to be a reactor protection system scram signal initiated from the OPRM per design and appropriate for the plant conditions. Troubleshooting of the RRC system pump speed downshift initially identified the probable cause to be a faulty card in the RRC pump control circuit. However, following a subsequent similar RRC pump downshift on January 6, 2005, the cause was determined to be an optical isolator intermittent failure as a result of an inadequate surge suppression network in the control circuit for the RRC pumps (See PNPP LER 2005-001) . This event is being reported under requirements of 10 CFR 50 .73(a)(2)(iv), any event or condition that resulted in manual or automatic actuation of any of the specified systems.
4432004001 | Seabrook | 06/22/2004 | 08/17/2004 | ML04238030 | <strong>Accident Monitoring Instruments Inoperable Due to Inadequate Indicating Range</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2004, the accident monitoring instrumentation (AMI) for containment enclosure negative pressure was declared inoperable after discovery that the instruments did not encompass the range of pressure needed to measure the variable under worst case conditions. An engineering evaluation, performed in 1991 in response to NRC Information Notice 88-76, determined that a negative pressure of (-) 0.685 inch water gauge needed to be measured at the location of the instruments to ensure that (-) 0.25 inch water gauge existed between the entire containment enclosure and the outside environment. However, the installed instruments had a range of only 0 to (-) 0.50 inch water gauge. While Technical Specification 3.3.3.6 has a 48-hour allowed outage time for two inoperable containment enclosure pressure channels, this condition existed since 1991 until discovery on June 22, 2004, resulting in a condition prohibited by the Technical Specifications. A review of previous LERS identified no similar occurrences. The cause of this event was the lack of a formal inter-discipline review of the engineering evaluation performed in 1991, resulting in a failure to recognize the AMI aspects of this instrumentation. Implementation of a design change to re-scale the containment enclosure negative pressure instruments corrected this condition. No adverse safety consequences resulted from this event.
4432004002 | Seabrook | 10/05/2004 | 12/01/2004 | ML04342016 | <strong>Accident Monitoring Instrumentation Inoperable Due to Recorder Malfunction</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2004 at 1830, while operating in Mode 1 at 100% power, it was discovered that pressurizer level recorder 1-RC-LR-460, one of the two channels of pressurizer level instrumentation required by TS 3.3.3.6, Accident Monitoring Instrumentation, had been inoperable for a period longer than the seven days permitted by Technical Specifications. The recorder, a model 227 Foxboro recorder, was inoperable for approximately 60 days from April 5, 2004 until June 4, 2004 due to the failure of a feedback potentiometer. The recorder was found not to be working during a September 24, 2004 routine analog channel operational test (ACOT). The cause of this event was inadequate failure analysis that did not identify the causal relationship between process oscillations and the design life of the potentiometer. In addition, numerous apparent cause evaluations did not adequately address the effectiveness of corrective actions for repeat failures of the potentiometers. There were no safety consequences due to the recorder failure as a second channel of pressurizer level instrumentation was operable. Corrective actions include implementing a design modification to filter out the noise signal on the recorder and periodic verification of potentiometer operability.
4432004003 | Seabrook | 11/02/2004 | 12/23/2004 | ML04365031 | <strong>Fire Scenario Results in Unanalyzed Condition Potential Loss of Charging</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2004, a review of potential fire scenarios found that fires in four plant areas could disable both charging system trains. A fire could cause a spurious closure of the volume control tank (VCT) outlet valve and cause damage to the operating charging pump. The fire could also damage the cables for the standby charging pump, rendering both charging pumps unavailable. Since the station's design basis is that one train of required systems is free of fire damage, these scenarios result in an unanalyzed condition. The analyses for fire areas, prepared in the mid-1980s, reviewed spurious equipment operation. However, the report failed to consider the unique interaction between the spurious closure of a VCT outlet valve and the operating charging pump in the redundant train. Compensatory actions that were implemented to mitigate the effects of this condition include: establishing an hourly fire patrol in the four fire areas of concern, minimizing combustible materials in the four areas, briefing the operators on this condition, and revising procedures to establish an alternate flow path to the charging pump in response to a fire alarm in any of the four areas. A design change is being planned to correct this condition. The condition resulted in no adverse safety consequences; however, it is of regulatory significance because it represented an unanalyzed condition.
4452004001 | Comanche Peak 1, Comanche Peak 2 | 03/03/2004 | 05/03/2004 | ML04126021 | <strong>Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2004, Core Performance Engineering performed a complete verification of fuel assembly configurations in the spent fuel pool. At 1110, it was discovered that fuel assembly C45 was stored in an unacceptable "4 out of 4" configuration which violated Technical Specification (TS) 3.7.17. TS 3.7.17 requires specific fuel assembly storage configurations in Region II racks based on the combination of initial enrichment and burnup of each fuel assembly. The control room was immediately notified, Shift Operations immediately initiated actions in accordance with TS Action Statements, and moved fuel assembly C45 from the Region II to the Region I racks where TS 3.7.17 is not applicable. TXU Generation Company LP (TXU Energy) believes that the cause of the event was an incorrect burnup value calculated for fuel assembly C45 which was used in determining the Region II allowable storage configuration. The incorrect burnup value resulted from inadequate conversion of the data files during a computer code migration in 1998. All times in this report are approximate and Central Standard Time unless noted otherwise.
4452004002 | Comanche Peak 1, Comanche Peak 2 | 04/02/2004 | 05/28/2004 | ML04159031 | <strong>Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2004, Comanche Peak Steam Electric Station Unit 1 was in Mode 6 during the tenth refueling outage and Unit 2 was in Mode 1 operating at 99.2 percent power. At 1500 hours, while reviewing proposed changes to response times in the Technical Requirements Manual, it was discovered that Technical Specification (TS) Surveillance Requirement (SR) 3.3.5.3 had not been completed within the required frequency for all of the functions specified in TS Table 3.3.5-1. TXU Generation Company LP (TXU Energy) believes that the cause of the event was less than adequate review of a change to the TS SR 3.3.5.3 frequency due to personnel errors in the review process and inadequate procedure referencing. Corrective actions include performing a risk assessment on Unit 2, performing the required TS surveillance tests on Unit 1, and issuing a Lessons Learned. All times in this report are approximate and Central Standard Time unless noted otherwise.
4452004003 | Comanche Peak 1 | 07/26/2004 | 09/23/2004 | ML04274042 | <strong>Condition Prohibited By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2004, Comanche Peak Steam Electric Station (CPSES) Unit I was in Mode 1 operating at 100 percent power. At 1449 hours, it was determined that the Unit 1 Containment Sump Level and Flow Monitoring System had been inoperable in the past due to a design related siphoning condition for a time period greater than the time allowed to complete the Required Actions of the applicable Technical Specification. TXU Generation Company LP (TXU Power) has determined that the cause of this event was a siphoning condition that was inherent in the original design of the system. Corrective actions include the installation of vacuum breakers in the containment sump discharge piping to break the siphoning condition. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462004001 | Comanche Peak 2 | 01/13/2004 | 03/12/2004 | ML04083060 | <strong>Condition Prohibited By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On January 13, 2004, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 operating at 99.5 percent power. At 1520 hours, Operations personnel discovered that an isolation valve associated with a Refueling Water Storage Tank (RWST) level transmitter reference leg was mispositioned. With this valve mispositioned, an RWST level channel was determined to have been inoperable for a period of time longer than allowed by the Technical Specifications. TXU Generation Company LP (TXU Energy) believes that the cause of the event was failure by an Instrument & Control (I&C) Technician to return an isolation valve to the correct position during the performance of sensor response time testing on an RWST level transmitter. Corrective actions include reinforcement of expectations, procedure revisions, and verification of the position of other similar valves. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462004002 | Comanche Peak 2 | 10/19/2004 | 03/04/2005 | ML05073025 | <strong>Actuation of Specified System: Emergency Diesel Generator and Turbine Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2004, one of the two feeder lines to the CPSES 138 kV switchyard was out of service due to modifications on the CPSES switchyard circuit breaker relays and the associated feeder circuit breaker relays at a different switchyard. At approximately 0520 on the same day, the second feeder line to the CPSES 138 kV switchyard was unexpectedly lost causing the loss of all 138 kV power to the CPSES 138 kV switchyard. As expected, both Unit 2 6.9 kV safeguards electrical trains, Trains A and B lost power, a slow transfer to the alternate 6.9 kV Class 1E bus through the 345 kV switchyard source was initiated, both blackout sequencers started, and the Turbine Driven Auxiliary Feedwater Pump started as required. Due to the cold water effects as a result of the start of Auxiliary Feedwater, the turbine load was manually reduced by 20 MW to 1170 MWe. Additionally, the Unit 2 Train B Emergency Diesel Generator (EDG) started unexpectedly, but was not required to load because power was available from the CPSES 345 kV switchyard through the alternate 345/6.9 kV transformer. Investigation revealed that the unexpected start of the EDG was due to the erratic behavior of the Preferred Offsite Source Bus Undervoltage Agastat relay. Once the relay was replaced, the preferred 138/6.9 kV Class 1E source was returned to service at 2324 feeding both safeguards buses. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462004003 | Comanche Peak 2 | 11/23/2004 | 01/21/2005 | ML05033017 | <strong>Containment Pressure Channel Inoperable Due to a Secondary Ground</strong><br /><i>Abstract:&nbsp;</i>On November 23, 2004, Comanche Peak Steam Electric Station Unit 2 was in Mode 1, Power Operation, operating at approximately 100 percent power. On November 23, Engineering personnel determined that one of the four Engineered Safety Feature Actuation System (ESFAS) intermediate range containment pressure channels had been inoperable for a period of time longer than allowed by the Technical Specifications.TXU Generation Company LP (TXU Power) believes that this event was caused by a secondary ground in the junction box associated with the pressure transmitter. Corrective actions include cleaning and rerouting the affected cable shield wire and identification and inspection of any other potential similar conditions. All times in this report are approximate and Central Standard Time unless noted otherwise.
4542004001 | Byron 1 | 08/17/2004 | 10/18/2004 | ML05227030 | <strong>Reactor Containment Fan Coolers Flow Rates Below Technical Specifications Requirements Due to Inaccurate Flow Indication</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2004, it was recognized that the Essential Service Water (SX) flow rates to the 1A, 1B, and 1C Reactor Containment Fan Coolers (RCFCs) were below the Technical Specification (TS) minimum value. The appropriate Technical Specification Action condition was entered. It was determined the flow rates were inadvertently throttled below the limit on April 20, 2004 due to inaccurate flow indicators used to re-adjust flow rates. The flow instruments are annubar flow measurement devices. On August 19, 2004, flow rates were readjusted using ultrasonic flow instrumentation and TS action condition exited. The root cause of the installed inaccurate flow indicators is currently indeterminate. A troubleshooting plan will be implemented in next refuel outage to determine the cause of the inaccurate flow indication. The findings and corrective actions to prevent recurrence will be reported in a supplement to this report. Interim corrective actions include an adverse monitoring plan to ensure flow rates to the RCFCs remain above the minimum flow and enhancing the SX system monitoring plan for better detection of adverse trends. An engineering evaluation is in progress assessing the safety significance of the low flow condition to the Unit 1 1A, 1B, and 1C RCFCs for the 119 day period. The results of the evaluation will also be reported in a supplement to this report. This is reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
4562004001 | Braidwood 1, Braidwood 2 | 03/01/2004 | 03/31/2004 | ML04097035 | <strong>Licensed Maximum Power Level Exceeded Due to Inaccuracies in Feedwater Ultrasonic Flow Measurements</strong><br /><i>Abstract:&nbsp;</i>Braidwood Station Unit 1 and Unit 2 exceeded their licensed maximum power level by up to 1.07% and 1.21%, respectively. In May 1999, an Ultrasonic Flow Measurement System (UFMS) was installed on the main feedwater lines to the steam generators to more accurately measure feedwater flow. This corrected feedwater flow was then used in the reactor power calorimetric calculation. Feedwater flow pressure pulses occurred at frequencies that affected the UFMS signal and resulted in a bias in the determinations of the flow correction factors. This resulted in a non-conservative calorimetric calculation. When reactor power was adjusted to match the calorimetric power, an overpower condition was created. When this condition was discovered, the noise-contaminated portion of the UFMS was removed from service. After further testing and analysis, the UFMS was fully removed from service. Implementation of the UFMS has been suspended. Analyses performed indicated there was no adverse safety impact for the overpower condition on each Unit. In accordance with Braidwood Station Unit 1 and Unit 2 License Condition 2.G, an ENS notification was made to the NRC at 1905 CST on March 1, 2004, due to the violation of License Condition 2.C(1) "Maximum Power Level," of each license.
4562004002 | Braidwood 1 | 06/01/2004 | 08/02/2004 | ML04223022 | <strong>1C Reactor Containment Fan Cooler discovered to be inoperable greater than required Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2004, during the monthly Reactor Containment Fan Cooler (RCFC) surveillance, the 1C RCFC Essential Service Water (SX) flow rate was found below the Technical Specification (TS)3.6.6 limit of 2660 gpm due to low flow through one bank of the RCFC. Flow had been last adjusted on May 6, 2004. The investigation determined that SX flow indicator 1F-SX118 was inaccurate when the flow was set on May 6, 2004 due to flow indicator fouling. The inaccurate flow indication was not recognized due to inadequate management decisions relating to the effects of the Braidwood lake precipitation event that occurred in February 2004. Organizational and programmatic issues were identified that contributed to the failure to recognize the flow degradation of the1F-SX118 indication loop and related piping following take precipitation event. The consequence of this event is the failure to meet the TS Limiting Condition for Operation due to inoperability of the lC RCFC. The low flow condition in the 1C RCFC may have resulted in silt build-up of the 1C RCFC cooling coils with a resulting failure of the lC RCFC thermal performance test. The safety consequences of this event are minimal. This event is being reported pursuant to10CFR50.73(a)(2)(i)(B).
4562004003 | Braidwood 1, Braidwood 2 | 06/16/2004 | 08/16/2004 | ML04238036 | <strong>OA Hydrogen Recombiner identified to be inoperable greater than required Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2004, the OA Hydrogen Recombiner was started to perform maintenance testing. At approximately 2000 hours the Recombiner heater breaker tripped. The breaker was reset and the Recombiner run was continued; however, no Technical Specification (TS) Limiting Condition for Operation entry was made at that time. It was not recognized that the tripped breaker placed the Hydrogen Recombiner in an inoperable condition. On June 16, 2004, Braidwood Station realized the OA Hydrogen Recombiner was inoperable since March 3, 2004, and therefore exceeded the TS Allowed Outage Time (AOT). The root cause for exceeding the AOT was the failure to apply an adequate technical evaluation in determining operability. Contributing to this event was the in appropriate revision of the procedure governing the startup of the Hydrogen Recombiners to allow for manual incremental increases of temperature controller setpoint during heat up of the Recombiner, which was contrary to the UFSAR description of how the Recombiner is operated. The corrective action to prevent recurrence is to implement a policy or procedure mandating the use of peer review for designated operability reviews conducted by the operating shift. A risk assessment was performed for the Hydrogen Recombiner inoperability and it was determined to be of low risk. The online risk assessment remained green with one Hydrogen Recombiner inoperable. A second Recombiner was available during the event. This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B).
4572004001 | Braidwood 2 | 09/25/2004 | 11/24/2004 | ML04341008 | <strong>Unit 2 Pressurizer Backup Heater Groups A and D Identified to be Inoperable Greater Than Required Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2004, in preparation for throttle valve and governor valve testing, the Unit 2 2D and 2A Pressurizer backup heater groups failed to energize when their control switches were placed in the “ON” manual position. At 2340 on September 25, 2004, Technical Specification (TS) Limiting Conditions for Operation (LCO) 3.4.9, Condition B was entered due to the heater groups being inoperable. The last time the heater groups were proven conclusively to be operable, based on the performance of post maintenance testing for coil replacements, was March 3, 2004 for the 2A backup heater group, and March 4, 2004, for the 2D backup heater group. This time period of inoperability exceeded the TS Allowed Outage Time (AOT). The root cause was determined to be the lack of torque specifications for the armature mounting screws in the equipment vendor manual. This improper torquing caused the mounting screws to loosen during cycling of the contactor. The loose mounting screws together with the mechanical force applied when the contactor cycles allowed the armature to drift and cause mechanical binding of the contactor armature to the armature stop assembly-mounting bracket. The corrective action to prevent recurrence is to prepare a maintenance procedure with specific torque requirements for this type of contactor assembly. The consequence of the mechanical binding of the 2A and 2D Pressurizer heater contactors is the inability to ensure adequate pressure control in response to plant transients. The overall risk significance associated with the failure of the Pressurizer heaters is low. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
4572004002 | Braidwood 2 | 12/22/2004 | 02/21/2005 | ML05063029 | <strong>Unit 2 Automatic Reactor Trip on 2C Steam Generator Low-Low Level Initiated by a Failure of the Controlling Channel Steam Flow Card</strong><br /><i>Abstract:&nbsp;</i>Braidwood Unit 2 experienced a reactor trip on December 22, 2004 at 1308 due to a low-low level in the 2C Steam Generator (SG). The reactor trip was initiated by the failure of a circuit card in the 2C steam flow instrumentation loop. The steam flow signal from this card feeds into the 2C SG level control loop. The loss of the steam flow signal to the 2C SG level control loop resulted in two automatic actions; closure of the 2C SG feedwater regulating valve in response to a steam flow-feedwater flow mismatch, and a speed reduction of the two turbine-driven feedwater pumps to reduce feedwater header pressure in accordance with a programmed feedwater header pressure versus total steam flow control response. Operator actions were unable to recover SG level prior to the automatic reactor trip. The root cause was determined to be inadequate understanding and incomplete evaluation of changes made to the Unit 2 feedwater system control settings for the feedwater regulating valves and the feedwater pump speed controller. The corrective actions to prevent recurrence include determining and setting the proper values for the feedwater regulating valve controller settings and main feed pump speed controller response for optimum plant response, and providing licensed operators the response characteristics of both Braidwood Units to feedwater type transients initiated by circuit card failures.There were no safety consequences impacting plant or public safety as a result of this event. The reactor trip system responded as designed to the low SG level condition and shut down the reactor at the required setpoint for steam generator low-low level. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A).
4582004001 | River Bend | 08/15/2004 | 10/14/2004 | ML04293061 | <strong>Automatic Reactor Scram Due to Main Generator Trip Resulting from Switchyard Fault</strong><br /><i>Abstract:&nbsp;</i>At 4:05 a.m. on August 15, 2004, with the plant operating at 100 percent power, an automatic reactor scram occurred as a result of a main turbine trip. A fault caused by failure of a 230kv transmission tower remote from the River Bend switchyard initiated a trip signal to an oil circuit breaker in the switchyard. Slow operation of some of the switchyard breakers caused a failure to clear the fault within the design time frame and the initiation of the breaker failure scheme. This resulted in a trip of one of the two main generator output breakers. Due to the slow clearing time, the ground fault protection system for the main generator step-up transformers also responded to the fault signal and tripped the remaining main generator output breaker. The resulting electrical transient also caused the loss of power to the Division 2 standby switchgear, which caused the automatic start of the Division 2 diesel generator. The reactor core isolation cooling system was initiated manually following the loss of the third main reactor feedwater pump. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(a) as an event that resulted in the initiation of the reactor protection system, the Division 2 diesel generator, the reactor core isolation cooling system. The breakers of the type that exhibited slow operation were inspected and lubricated, or left out of service for plant startup. This event was of low actual safety significance, as the plant response was within the bounds of the safety analysis. All safety systems responded as expected.
4582004002 | River Bend | 10/01/2004 | 11/29/2004 | ML04342005 | <strong>Automatic Reactor Scram and System Actuations Due to Insulator Flashover in Switchyard</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2004, at 7:17 a.m., with the plant operating at 100% power, a loss of power to the Division 1 standby switchgear caused the automatic start of the Division 1 diesel generator. Some non-safety switchgear were also deenergized by this event. At 7:30 a.m., an automatic reactor scram was initiated by a main turbine trip. Both of these events were caused by the flashover of high-voltage insulator strings in the station transformer yard. During the event, all main reactor feedwater pumps shut down, main condenser vacuum was lost, and the standby service water system initiated. The reactor core isolation cooling (RCIC) turbine steam supply valve isolated during the pressure transient associated with the main turbine trip. Operators manually started the high pressure core spray (HPCS) system to provide water to the reactor. A momentary low reactor water level caused a primary containment isolation signal. This is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the reactor protection system, Division 1 diesel generator, and standby service water system; an automatic isolation of primary containment; and the manual actuation of the RCIC and HPCS systems. There were no safety systems out of service at the time of the first event. Mitigating safety systems responded as designed. This event is bounded by the River Bend safety analysis, and was thus of minimal safety significance.
4582004003 | River Bend | 10/31/2004 | 02/17/2005 | ML05054052 | <strong>Unplanned Automatic Start of Standby Diesel Generator Due to Loss of Division 1 Switchgear</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2004, at approximately 10:36 p.m. CST, an automatic start of the Division 1 emergency diesel generator (DG) occurred as a result of the loss of the Division 1 standby switchgear. The plant was in cold shutdown for a refueling outage at the time of the event. The normal feeder breaker to the Division 1 4160kv bus tripped during the installation of test jumpers in preparation for surveillance testing. Due to inadequate use of error prevention practices, the technician inadvertently contacted an adjacent terminal, generating a trip signal to the feeder breaker. The diesel generator started as designed on a bus low voltage condition, and its output breaker automatically closed, restoring power to the bus. At the time of the event, the reactor cavity was flooded to greater than 23 feet. The reactor water cleanup system was in service and the Division 2 residual heat removal system was operating in the shutdown cooling mode. These systems were unaffected by this event and continued to provide alternate means of coolant circulation. For the remainder of the surveillance test being performed, all work involving lifted leads and jumpers was monitored directly by the test director. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of the Division 1 DG. This event was of minimal safety significance.
4582004004 | River Bend | 11/01/2004 | 02/17/2005 | ML05054052 | <strong>Unplanned Automatic Start of Standby Diesel Generator Due to Loss of Division 2 Switchgear</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2004, at approximately 4:44 p.m. CST, the Division 2 emergency diesel generator (DG) automatically started as a result of the loss of the Division 2 4160kv standby switchgear. The switchgear was de-energized as a result of an inadvertent trip signal generated during scheduled testing of the sudden overpressure relay on the preferred station service transformer supplying the switchgear. This event resulted from an inadvertent re-activation of the trip circuits served by the relay being tested. The Division 2 DG started and restored power to the standby switchgear as designed. The Division 2 residual heat removal (RHR) system was operating in the shutdown cooling mode at the time of the event, and was temporarily out of service as a result. Division 2 RHR was restarted approximately 50 minutes after the event. This is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an event that caused the automatic actuation of the Division 2 DG. At the time of the event, the plant was in cold shutdown for a refueling outage. This event was of minimal safety significance.
4582004005 | River Bend | 12/10/2004 | 06/22/2005 | ML05179023 | <strong>Unplanned Automatic Scram Due to Loss of Non-vital 120 Volt Instrument Bus</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2004, at 1:17 p .m. CST, an automatic reactor scram occurred while the plant was operating at 100 percent power. The scram was the indirect result of the failure of a 120 volt AC uninterruptible power supply (UPS) on a non-safety related instrument bus. The UPS failed due to a shorted capacitor on an internal circuit board. The loss of the instrument bus resulted in the downshift of the reactor recirculation pumps to slow speed and the lockup of the main feedwater regulating valves. The decrease in coolant flow caused a flow-biased simulated thermal power signal to be sensed in the average power range monitoring system, which actuated the reactor protection system (RPS). The reactor core isolation cooling (RCIC) system was manually started in response to the failure of the feedwater regulating system. RCIC subsequently shut down as designed due to a high reactor water level signal. While it was idle, an alarm actuated indicating the presence of water in the RCIC turbine exhaust drain trap. A conservative decision was made to leave RCIC out of service and to start the high pressure core spray (HPCS) system as needed for reactor water level control. The reactor scram occurred as designed, and reactor water level was maintained above the low-low alarm setpoint. This event is being reported in accordance with 10CFR50.73(a)(2)(IV)(A) as a condition that resulted in the actuation of the RPS, RCIC, and HPCS systems. This event was of minimal safety significance.
4612004001 | Clinton 1 | 03/22/2004 | 08/16/2004 | ML04239043 | <strong>Generator Over-Voltage / Lockout Leads to Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2004, at about 1931 hours, an automatic reactor scram occurred with the plant at 93 percent power. Operators received a trouble alarm in the Main Control Room for the Hydrogen and Stator Cooling Cabinet followed by a Main Generator neutral over-voltage trip and Generator Trip System 2 Lockout. The Generator trip caused a Main Turbine trip and Turbine Control Valve fast closure, resulting in an automatic reactor scram. All control rods fully inserted. Following the reactor scram, reactor water level dropped, as expected, to the Low Level 3 trip setpoint, initiating the Reactor Protection System. Operators entered Emergency Operating Procedures due to the low reactor water level transient. The root cause investigation determined that a failed Partial Discharge Analysis (PDA) system cable and/or a piece of aluminum laminate from a degraded bus conductor expansion joint contacted the grounded bus duct causing a ground fault and subsequent generator neutral over-voltage trip. The failures of the PDA cable and the aluminum laminate were both due to mechanical fatigue caused by an increase in design air flow rate in the bus duct implemented during the Spring 2004 refueling outage. Corrective actions include implementing a design change for the bus duct expansion joint that is not susceptible to fatigue failure.
4612004002 | Clinton 1 | 04/07/2004 | 04/12/2006 | ML06110050 | <strong>Mispositioned Standby Liquid Control Air Sparge Valve Results in High Boron Concentration</strong><br /><i>Abstract:&nbsp;</i>The air sparge valve, a normally locked closed valve, for the Standby Liquid Control (SLC) tank was left open after mixing the chemical added by an Engineering Change (Enriched Boron) during outage C1 R09 in February, 2004. Following investigation of SLC tank level lowering, the open valve was identified and closed on April 6, 2004. A sample of the SLC tank solution was taken on April 7 to verify boron concentration was within the required Technical Specification (TS) limits of TS Figure 3.1.7-1. The results indicated that the boron solution was outside the TS limit. TS 3.1.7 Action B requires restoration, to Operable, of at least one train of SLC within 8 hours. Since the concentration was high on April 7, the Boron concentration was assumed to be in excess of the TS required limit from the time the air sparge valve was closed on April 6, longer than allowed by TS 3.1.7. The open air sparge valve caused evaporation of water in the SLC storage tank resulting in boron concentration exceeding the TS required upper limit. The causes of the event were a human factor flaw in the sequencing of the procedure steps to close the valve following its use in mixing the solution in the SLC tank, and not fully implementing the locked valve program. Corrective actions are to correct the human factor flaw in the procedure, and to fully implement the locked valve program.
4612004003 | Clinton 1 | 07/13/2004 | 09/10/2004 | ML04266038 | <strong>Main Power Transformer Protective Relaying System Design and Lightning Cause Scram</strong><br /><i>Abstract:&nbsp;</i>A suspected lightning strike to the A Phase of the 345 Kilovolt (kV) line 4.5miles from the station resulted in a generator trip and automatic reactor scram. The Main Generator Trip System 2 received an instantaneous neutral phase over-current trip on the station ITH Relay. The ITH relay monitors the difference between the current in the Main Power Transformer (MPT) neutral legs and the sum of the 345kV Main Power Output breakers phase currents; the purpose of this scheme is to provide protection for the high voltage leads for a ground fault. All control rods fully inserted. The cause of the event was a legacy design vulnerability that was unknown to the Station. The design of the protective relaying system and breaker trip logic for the MPTs had some weaknesses since current transformers in the circuit had potential saturation issues. The potential for current transformer saturation along with the speed of the ITH relay made the circuit vulnerable to false tripping. The magnitude of the fault, grid conditions (load and reactance) at the time of the fault, and the timing of the fault allowed the vulnerabilities to result in an unexpected reactor trip. The corrective action was a design change to replace the ITH relay with a relay that has a time delay in the tripping circuit to permit proper sequencing of the protective relaying during transmission line faults.
4612004004 | Clinton 1 | 07/14/2004 | 09/10/2004 | ML04266039 | <strong>Reactor Scram While Placing Residual Heat Removal 'B' Into Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2004, with the plant in Mode 3 (Hot Shutdown) due to a reactor scram that occurred at 1608 on July 13, 2004, operators were warming the Residual Heat Removal (RHR) system B loop in preparation to place RHR Shutdown Cooling (SDC) in service in order to proceed to Mode 4 (Cold Shutdown). At 0044 hours, reactor pressure vessel (RPV) water level decreased from +32 inches to +9 inches, resulting in an RPV low water level (Level 3) Reactor Protection System actuation and a containment isolation (Groups 2, 3, and 20). Within six seconds of RPV water level reaching Level 3, level recovered above the scram setpoint, as feedwater flow to the RPV increased and the RHR piping was refilled. The cause of the event was determined to be a deficient RHR SDC procedure which did not provide adequate guidance for re-warming the system and introduced a latent error through valve sequencing that allowed a column separation effect to occur while warming the system. The corrective actions are to revise the RHR SDC procedure.
4612004005 | Clinton 1 | 10/06/2004 | 12/03/2004 | ML04350027 | <strong>Automatic Start of Division 2 Shutdown Service Water Pump Due to Unknown Cause</strong><br /><i>Abstract:&nbsp;</i>A control room operator was securing from a flush of the Divisions 2 and 3 Emergency Diesel Generator (EDG) heat exchangers. The operator requested and received a peer check to validate he was operating the correct hand-switch to close the Division 2 EDG heat exchanger essential Shutdown Service Water System (SX) outlet valve. Following the peer check, the operator placed the switch in the closed position, verified the valve was closing by observing the indicator lights, and then proceeded to the Division 3 panel [PL]. Within several seconds of leaving the Division 2 panel, alarms indicated the Division 2 SX pump automatically started unexpectedly. A low-pressure condition in the SX system, most likely caused by closing the non-essential Service Water System (WS) to SX system crosstie valve, resulted in the automatic start of the SX pump; however, a root cause could not be identified. Corrective action includes replacing the hand-switch for the Division 2 crosstie valve, implementing an Operations department policy for protected equipment, installing a protective cover over the hand-switches for the crosstie valves, requiring the involved operators to demonstrate proper peer and self-check behaviors, and coaching the control room supervisor on required oversight and validation that expected behaviors are occurring.
4612004006 | Clinton 1 | 10/07/2004 | 11/03/2004 | ML04322034 | <strong>Small Amount of Special Nuclear Material in Unirradiated Nuclear Instrument Detectors Unaccounted For</strong><br /><i>Abstract:&nbsp;</i>In 1991, four unirradiated Nuclear Instruments (Nls) were identified as being damaged. The disposition for the four Nls was to cut the defective detectors from the cables and place the detectors in a Special Nuclear Material (SNM) container. Tamper seals were applied to the container. The remaining cables and connectors were to be disposed of as trash. On 1017/04, Reactor Engineers opened the container to verify the contents in preparation for disposal and discovered that the container had only one of the four detectors and three unexpected signal cable connectors; thus three unirradiated NI detectors containing SNM were unaccounted for. Storage facilities were searched for the missing detectors; the detectors were not found. A search of station records identified no records of disposition. The detectors were apparently disposed of as uncontaminated connectors in the station trash that was subsequently buried in a local landfill. The apparent cause of this event is attributed to human error in cutting and placing the connectors in the SNM container rather than the detectors. The future practice for disposing of defective unirradiated NI detectors will be to leave the detector, cable and connector intact as a unit, cutting will not be allowed. The detectors contain an extremely small amount of SNM and pose no danger to the public.
4822004001 | Wolf Creek | 01/15/2004 | 03/12/2004 | ML04078066 | <strong>Inadequate Verification of Valve Position Following Testing Results in Technical Specifications Violation</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2004, at 8:30 PM, central standard time, containment spray system [EIIS: BE] isolation valve [EIIS: ISV] EN-V025 was found locked in the fully open position. The containment spray system was declared inoperable in accordance with Technical Specification (TS) 3.6.6. Valve EN-V025 was closed and the containment spray system was declared operable at 8:51 PM on January 15, 2004.This valve was unlocked and opened on December 30, 2003, during the performance of the containment spray pump in service pump test for train B, which is controlled by procedure STS EN-100B. This procedure requires that after this test has been completed, valve EN V025 is to be restored to closed and locked, and subsequently verified to be closed and locked. This condition existed prior to discovery for a period greater than 72 hours, the allowed Completion Time associated with Required Action A.1 of TS 3.6.6. As such, this situation represents a condition prohibited by Technical Specifications, and is reportable per 10CFR 50.73(a)(2)(i)(B).The root cause for valve EN-V025 being in the incorrect position is lack of information validation or verification. The two nuclear station operators did not adequately validate information, and did not adequately verify the information (i.e., valve position).
4822004002 | Wolf Creek | 02/13/2004 | 04/09/2004 | ML04107038 | <strong>Reactor Protection System Actuation and Reactor Trip due to Main Feedwater Regulating Valve Failing Closed</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2004, at 8:04 AM CST, Wolf Creek Generating Station (WCGS) experienced an automatic actuation of the Reactor Protection System (RPS) including an automatic reactor trip due to Lo-Lo water level in the "D" steam generator (SG). This actuation occurred following failure of the "D" SG main feedwater regulating valve (MFRV) resulting in valve closure. When the MFRV failed closed, "D" SG level decreased below the reactor trip setpoint, initiating a reactor trip. The unit received an expected feedwater isolation and auxiliary feedwater actuation (both motor and turbine driven pumps) because of the Lo-Lo SG level. All control rods fully inserted, and the RPS and Engineered Safety Features (ESF) systems performed as expected. The cause of the MFRV closure was separation of the valve plug from the valve stem, which caused the plug to fall into its seated (closed) position. The stem/plug assemblies were subsequently replaced in all four (4) MFRVs. The safety significance of this event is low. This event is bounded by the current licensing basis analyses as reported in WCGS Updated Safety Analysis Report (USAR) section 15.2.7 "Loss of Normal Feedwater Flow." All safety related equipment performed as expected. There were no adverse effects on the health and safety of the public.
4822004003 | Wolf Creek | 03/06/2004 | 05/05/2004 | ML04132046 | <strong>Automatic Start of "B" Emergency Diesel Generator Due To Start-Up Transformer Cable Ground Fault</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2004, Wolf Creek Generating Station (WCGS) was operating at 100 percent steady state power. At 9:47P.M. Central Standard Time, startup transformer neutral ground relays 251N-2T1 and 251N-4T1 tripped which initiated protective lockout and transformer trip relays for the startup transformer, tripping the transformer and resulting in a loss of power to the Engineered Safeguards Feature (ESF) bus NB02. The loss of power to the transformer that normally powers this bus resulted in the automatic start, and subsequent loading of the "B" Emergency Diesel Generator (EDG.) The cause of the transformer trip was due to a cable fault in the cable connected to the stamp transformer's "X" winding "C" phase (X-C) bushing, caused by water that had collected in the cable through connecting lug inspection holes . The safety significance of this event is low. This event is bounded by the current licensing basis analysis as reported in WCGS Updated Safety Analysis Report (USAR) section 15.2.6 "Loss of Non Emergency AC Power to the Station Auxiliaries." All safety-related equipment operated as expected. There were no adverse effects to the health and safety of the public.
4822004004 | Wolf Creek | 08/22/2004 | 10/20/2004 | ML04301058 | <strong>Insufficient Planning Results in Reactor Trip When Restoring From Test</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2004 at 1010 a.m. Central Daylight Time, Wolf Creek Generating Station (WCGS) experienced a reactor trip during routine surveillance testing of the "B" train Solid State Protection System (SSPS). To facilitate this testing, WCGS had entered Required Actions for Conditions A and R of Technical Specification (TS) 3.3.1, Table 3.3.1-1, Function 19, which permits operation of the plant with one train of SSPS inoperable and the associated reactor trip breaker (RTB) bypassed for up to two hours. During this testing, WCGS Instrumentation and Controls (I&C) technicians reported to the shift manager in the control room that an indication light did not illuminate as required. During restoration from the procedure, a required step to reinstate the necessary memory circuit blocks for the 25%power reactor trip signals was not performed. When the input error inhibit switch for the "B" train SSPS was returned to the "Normal" position without these memory circuit blocks in place, a reactor trip signal was generated. This was a human performance related event where an I&C technician did not perform the necessary steps to restore from the surveillance test procedure. The safety significance of this event is low. All control rods fully inserted, and all safety-related equipment operated as expected. There were no adverse effects on the health and safety of the public.
4822004005 | Wolf Creek | 10/07/2004 | 12/02/2004 | ML04343046 | <strong>Automatic Reactor Resulting From Lightning Strike In Switchyard</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2004, at 11:48 A.M., Wolf Creek Generating Station (WCGS) experienced an automatic reactor trip due to indicated high main turbine vibrations. Concurrent with this event, several lightning strikes from an electrical storm were observed in the immediate area, including one recorded in the vicinity of the steel high line tower for the Main Startup Transformer. This lightning strike created an electromagnetic interference (EMI) that caused the actuation of the Main Turbine High-High Vibration Trip circuitry. The resultant turbine trip actuated an automatic reactor trip. Subsequent investigation of Main Turbine vibration and other performance data has validated that no actual high vibration was present either at the time of the Main Turbine trip, during the ensuing turbine coastdown, or during the subsequent plant restart. All control rods fully inserted and all safety-related equipment operated as designed. The WA" train of the Residual Heat Removal System (RHR) was out of service for normal maintenance at the time of this event. The safety significance of this event is low. All control rods fully inserted, and all safety-related equipment operated as expected. There were no adverse effects on the health and safety of the public.
4822004006 | Wolf Creek | 10/11/2004 | 12/10/2004 | ML04352024 | <strong>Automatic Start of "B" Emergency Diesel Generator Due to Start-Up Transformer Fault</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2004, Wolf Creek Generating Station (WCGS) was operating at 100 percent steady power. At 7:25A.M. Central Daylight Time, the Low-Low Oil Level trip activated on the startup transformer, tripping the transformer and resulting in a loss of power to the Engineered Safeguards Feature (ESF) bus NB02. The loss of power to the transformer that normally powers this bus resulted in the automatic start and subsequent loading of the "B" Emergency Diesel Generator (EDG). In addition, an Auxiliary Feedwater Actuation Signal (AFAS) started the Turbine Driven Auxiliary Feedwater Pump (TDAFP) per the plant design. The cause of the transformer trip was due to a ground on the Low-Low Oil Level trip transmitter device, caused by degraded and cracked cable insulation immersed in moist insect debris. The safety significance of this event is low. This event is bounded by the current licensing basis analysis as reported in WCGS Updated Safety Analysis Report (USAR) section 15.2.6 "Loss of Non Emergency AC Power to the Station Auxiliaries." All safety-related equipment operated as expected. There were no adverse effects to the health and safety of the public.
4832004001 | Callaway | 11/12/2003 | 01/08/2004 | ML04015056 | <strong>Loss of Service Water system requires manual initiation of Essential Service Water.</strong><br /><i>Abstract:&nbsp;</i>On 11/12/03 while restoring the Circulating and Service Water pump house electrical bus lineups to a normal configuration, two out of three electrical buses were de-energized resulting in a loss of the service water system and necessitating manual actuation of the Essential Service Water (ESW) system. The loss of service water coupled with a reduction in circulating water system capacity required Control Room Operators to manually reduce Main Generator electrical loading to prevent a loss of condenser vacuum and automatic main turbine runback. After operator actions restored service water system operation, power stabilized at approximately 70 percent. An Event Review Team concluded the cause of the event was failure to follow an approved plant procedure. The Licensed Operator selected position 2201-2202 versus the proper position of 2201-2102, which is located on a different selector switch. A contributing cause was the fact the two bus transfer selector switches have identical name plate labels .Once the cause of the event was understood, power was increased to 100 percent and normal operation resumed. Corrective actions include revising the Main Control Board name plate labels for the bus transfer selector switches and revising plant procedures to reflect the new labels.
4832004002 | Callaway | 01/27/2004 | 03/18/2004 | ML04085055 | <strong>Reactor trip due to faulty electrical relay.</strong><br /><i>Abstract:&nbsp;</i>At 1830, 1/27/04, while at 100 percent power, Callaway Plant experienced a main electrical generator trip which in turn caused a reactor trip due to power being above 50 percent. The cause of the generator trip was a failed electrical relay. This relay was designed to sense remote faults in order to prevent exceeding thermal limits for the stator windings. Plant systems responded as designed, including automatic actuation of the auxiliary feedwater system. The faulted relay was repaired, calibrated, and reinstalled. This relay contained a second set of unused contacts which were used instead of the initial faulted contacts. This relay configuration was successfully retested and plant operation resumed without further problems. A review of relevant operating experience did not identify similar failures, and a review of past plant preventative maintenance did not reveal abnormalities. Preventive maintenance procedures will be revised to provide additional detailed instructions for inspection of these relay contacts for this failure mechanism.
4832004003 | Callaway | 02/03/2004 | 04/02/2004 | ML04099042 | <strong>Reactor trip due to faulty relay.</strong><br /><i>Abstract:&nbsp;</i>At 0439, 2/3/04, with Callaway Plant at 100 percent power, a reactor trip occurred while operating breakers in the site distribution switchyard. Plant operators responded to the event using plant procedures and stabilized the plant in Mode 3. All safety systems initially responded as required to the event. Investigations determined a faulted timer relay in the dead machine protection circuit for the main generator caused a trip of the main generator output breakers and subsequent reactor trip. 3 hours 17 minutes after the trip, the Turbine Driven Auxiliary Feedwater Pump (TDAFP) tripped. Extensive methodical investigation resulted in replacement of three components in the control system, and the TDAFP was declared operable. Due to the complexity of the TDAFP investigation, an emergency one-time change to Technical Specification 3.7.5 was requested and approved. The failed timer relay in the dead machine circuit, and the three suspect control system components were all replaced and both pieces of equipment were returned to service.
4832004004 | Callaway | 02/11/2004 | 04/09/2004 | ML04111092 | <strong>Safety Injection while conducting plant heatup to normal operating pressure and temperature.</strong><br /><i>Abstract:&nbsp;</i>At 2258, 2/11/04, with the plant in Mode 3, a Safety Injection (SI) occurred while performing a plant heat up to normal reactor coolant system operating pressure and temperature. The SI was the result of not performing a step contained in the procedure governing a plant heat up. All safety systems actuated as required and flow was initiated to the core due to plant conditions present at the start of the event. Emergency procedures were used to terminate the event and restore the plant to a normal condition. During the event, "B" Steam Generator Auxiliary Steam Dump (S/G ASD) did not properly operate and "A" Reactor Coolant Pump (RCP) exhibited high vibration. The "B" S/G ASD problem was identified as an obstruction of a balance arm within an electro pneumatic transducer which was corrected and tested to verify operability. The RCP vibration was determined to be the result of thermal transients caused by the SI and did not require additional action. A Root Cause Analysis investigation was conducted which revealed inadequate pre-job briefs, weaknesses in supervisory oversight, and cumbersome operating procedures as root causes for this event.
4832004005 | Callaway | 02/15/2004 | 04/09/2004 | ML04111092 | <strong>Inadequate feedwater heating During plant startup causes turbine trip and subsequent reactor trip.</strong><br /><i>Abstract:&nbsp;</i>On 2/15/04, during plant startup and synchronizing to the grid, Callaway experienced oscillations in Steam Generator (SIG) levels which resulted in a main turbine generator trip and subsequent reactor trip. After the reactor trip occurred, to reduce the plant cooldown rate, operators attempted to secure the Turbine Driven Auxiliary Feedwater Pump (TDAFP). However, due to an automatic actuation signal being present, the TDAFP experienced an electrical and mechanical overspeed trip. Post trip investigations determined that the SIG oscillations were due to not having aligned extraction steam to provide feedwater preheating. The overspeed trip of the TDAFP was per system design. A TDAFP actuation signal was present when the operators closed the steam supply valves, causing the valves to reopen automatically and in such a sequence as to cause an overspeed condition. A Root Cause Analysis team was assembled and identified four Root Causes, plus several Corrective Actions to Prevent Occurrence.
4832004006 | Callaway | 04/26/2004 | 05/25/2004 | ML04156000 | <strong>"A"Steam Generator tube inspection results classified as C-3.</strong><br /><i>Abstract:&nbsp;</i>At 1906 CDT, 4/26/04, in Event Notification # 40705, Callaway reported the following: "During Refueling Outage RF13, interim results of "A" Steam Generator (S/G) tube inspections indicate 59 tubes out of 5341 tubes (i.e., greater than 1 percent) have been determined to be defective. This S/G tube inspection result for the "A" S/G is classified as category C-3 in accordance with Technical Specification 5.5.9, Table 5.5.9-2. Per NUREG 1022, Section 3.2.4 Discussion (A)(3), the present C-3 classification of the "A" S/G tubes does not meet the listed criteria for serious S/G tube degradation and thus is not a degraded or unanalyzed condition. Since this report is required by Administrative Technical Specification 5.5.9, this notification is being listed as an "Other Unspecified Requirement". All defective tubes will be removed from service before the S/G is returned to service. There were no adverse safety consequences or implications as a result of this event. This event did not adversely affect the safe operation of Callaway Plant or the health and safety of the public." This LER is submitted in compliance with Technical Specification 5.5.9 and 5.6.10c requirements and not due to an actual serious S/G tube degradation. Final results from Steam Generator A examinations resulted in a total of 100 tubes being plugged.
4982004001 | South Texas 1 | 01/23/2004 | 03/23/2004 | ML04086076 | <strong>Unit 1 Reactor Trip On High Steam Generator Levels Initiated by Failure of Inverter 1201</strong><br /><i>Abstract:&nbsp;</i>On 01/23/04 with Unit 1 at 100% power, the Class 1E 7.5 KV Inverter 1201 failed, resulting in a reactor trip when steam generator level could not be controlled. The plant was stabilized, and after troubleshooting and repair, the reactor was restarted at approximately 2237 hours on 01/25/04. The cause of the inverter failure was a Ferro-Resonant transformer short due to heat-related degradation of the transformer insulation. The technical root cause of the event is that the design of the Class 1E Vital Instrument Power Supply (VA) System is not single train fault-tolerant and failure of the inverter causes significant operational challenges. Additionally, the organizational root cause is that the station did not aggressively pursue effective failure prevention strategies even though previous events have shown that the inverters are susceptible to failure and the Instrument Power Supply (VA) System is not single train fault-tolerant. Corrective actions include the replacement/repair of all Class 1E 7.5 KV Inverter Ferro-Resonant Transformers and design enhancements that will minimize inverter failures and the effects of initiating transients requiring significant operator rapid response. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. There were no challenges to plant safety.
4982004002 | South Texas 1, South Texas 2 | 03/17/2004 | 05/17/2004 | ML04142009 | <strong>Inoperable Control Room Makeup and Cleanup Filtration Systems</strong><br /><i>Abstract:&nbsp;</i>At 1242 on 3/17/04, with Units 1 and 2 operating in Mode 1, the South Texas Project (STP) declared all three trains of the Control Room Makeup and Cleanup Filtration Systems (CRMCFS) inoperable in both Units. The basis for this conclusion was the fact that the CRMCFS did not maintain the Control Room Envelope (CRE) at sufficient positive pressure relative to adjacent areas during tests performed in March 2003 for Unit 2 and early March 2004 for Unit 1, as required by a surveillance requirement. Pursuant to 10CFR50.73, STP submits this Licensee Event Report regarding the inoperability of all three CRMCFS trains of each unit as a condition prohibited by the Technical Specifications. The direct causes of this condition were degraded Unit 1 and Unit 2 CRE system health, coupled with the station's non-conservative interpretation regarding the applicability of the surveillance requirement to certain adjacent areas. The CRMCFS was capable of performing its safety function of limiting control room operator doses to less than 5 rem whole body. This condition resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. There were no challenges to plant safety.
4982004003 | South Texas 1 | 03/26/2004 | 05/17/2004 | ML04142008 | <strong>An unanalyzed condition that significantly degraded plant safety due to a valve out of position</strong><br /><i>Abstract:&nbsp;</i>The South Texas Project determined that the Train B high head safety injection pump flushing line isolation valve was partially open. A partially opened flushing line isolation valve provides a containment bypass leak path during a design-basis loss of coolant accident (LOCA) after the safety injection system switches to re-circulation. This resulted in a condition where the radiological control room dose limits of General Design Criterion (GDC) 19, Appendix A of 10CFR50 and the offsite dose limits of 10CFR100 would have been exceeded in the event of a design-basis accident. The cause of the flushing line isolation valve being out of position is indeterminate. The most likely cause is someone using the valve handle as an aid in exiting the ladder located next to it. The valve handles from the flushing line isolation valve found open and the two valves adjacent to it will be removed. The corresponding valve handles in Unit 2 will also be removed. These actions are expected to prevent recurrence of accidental misalignment of any of these valves.
4982004004 | South Texas 1, South Texas 2 | 04/06/2004 | 06/07/2004 | ML04167060 | <strong>Deviation from a Licensed Condition under 10CFR50.54(x)</strong><br /><i>Abstract:&nbsp;</i>On the morning of April 6, 2004, a Tornado Warning was issued for the South Texas Project. Unit 1 was in Mode 1 at 100% power. Unit 2 was in Mode 5 in a refueling outage. The Unit 1 Control Room directed all plant personnel to seek shelter over the public address system at 1140. Security Officers in elevated and ground positions were relocated inside the Mechanical Electrical Auxiliary buildings. Officers at the station checkpoints were relocated to the East Gate House and the Nuclear Support Center. At 1143 a Security Alert was declared by the Security Force Supervisor as defined in the Safeguards Contingency Plan. Since the requirements of 10 CFR 73.55(e) and (h) were not met, the Unit 1 Shift Supervisor invoked 10CFR50.54(x) at 1151 for the protection of security personnel. The declaration of a Security Alert is an entry condition into the site Emergency Plan at the Unusual Event level. In accordance with site procedures the Unit 1 Shift Supervisor declared an Unusual Event at 1151. The Owner Controlled Area and Protected Area patrols were secured at 1151 for their safety. At 1300, after the weather subsided, the security force began recovery by returning to the pre-tornado warning positions. At 1319, the site exited the Security Alert and the Unusual Event. The intrusion detection and threat assessment equipment were tested and compensatory measures established if appropriate. A search of the Protected Area was conducted and completed satisfactorily at 1422.
4982004005 | South Texas 1 | 08/18/2004 | 10/25/2004 | ML04307058 | <strong>Standby Diesel Generator 12 Not Being Declared Inoperable While the Auxiliary Feedwater Pump 12 Breaker Cell Switch was Being Replaced</strong><br /><i>Abstract:&nbsp;</i>In August 2004, during a work review of the Cell Switch Replacement Project a question was identified regarding the declaration of Sequencer and Standby Diesel Generator (SDG) inoperability during any associated cell switch maintenance. Subsequently, an investigation was initiated regarding this issue. The results of this investigation identified one case in November 2003 where an affected diesel generator had not been declared inoperable due to cell switch maintenance. On Monday, November 3, 2003 at 0300, Auxiliary Feedwater (AFW) pump 12 was declared inoperable in order to perform planned maintenance and Technical Specification action statements 3.7.1.2.a and 3.3.3.5.b were entered. At approximately 0815 on November 4, 2003, work start was granted to commence work to replace the cell switches in the AFW breaker cubicle. The SDG output breaker is inoperable in this condition due to its inability to recognize the AFW pump breaker as not closed. This prevents automatic closure capability of the SDG output breaker during an emergency start. There is no documented evidence that SDG 12 was considered inoperable during this time period (i.e. while the cell switch replacement in the AFW breaker cubicle was in progress). Additionally, there is no evidence of entry into the required Technical Specification 3.8.1.1.b or performance of the associated ESF Power Availability surveillance. Therefore, pursuant to 10CFR50.73(a)(2)(i)(b), this event is reportable due to Technical Specification 3.8.1.1.b not being entered and the corresponding failure to perform the associated conditional ESF Power Availability surveillance. The root cause of this event is inadequate communication to those Senior Reactor Operators responsible for the configuration management (Control Room) and work implementation processes of this condition where AFW Pump breaker maintenance affects Diesel Generator operability. This condition resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. There were no challenges to plant safety.
4982004006 | South Texas 1 | 11/17/2004 | 01/17/2005 | ML05026031 | <strong>Pressurizer Power-Operated Relief Valve Being Inoperable for a Time Period Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2004, elevated temperatures were measured on the Unit 1 Pressurizer Power Operated Relief Valve (PORV) 1-RC-PCV-0656A. On November 9, 2004, engineering analysis determined that the thermal Environmental Qualification (EQ) life of the PORV's Limit Switch Cover Gasket had been exceeded. The PORV was declared inoperable. The block valve was closed. The gasket was replaced within approximately 24 hours of discovery that its thermal EQ life had been exceeded. The PORV remains inoperable due to excessive seat leakage with the associated block valve closed and power maintained to the block valve as required by Technical Specification 3.4.4. Technical Specifications allow continued power operation in this condition. An engineering evaluation determined that the PORV had been inoperable on October 29, 2004 at the latest, and the inoperable condition was not corrected within 72 hours. This resulted in a condition prohibited by Technical Specifications. The root cause of exceeding the thermal EQ life of the PORV Limit Switch Cover Gasket is that the design of the PORV portion of the discharge header temperature alarm is inadequate. Corrective actions include evaluation of a modification for installing temperature elements with associated alarms on the Pressurizer PORVs to provide a warning of impending high gasket temperature conditions. This condition resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. There were no challenges to plant safety.
5282004001 | Palo Verde 1 | 02/03/2004 | 04/01/2004 | ML04104002 | <strong>Reactor Shutdown Due to Reactor Coolant System Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2004 at approximately 1418 MST, Unit 1 operations personnel became aware of a non-isolable reactor coolant system (RCS) pressure boundary leak from a drain valve (SIA-V056) off of a high pressure safety injection line which is connected to the RCS loop 1 hot leg. The source of the estimated 1 to 2 drops/second leak was a crack in a socket weld on the upstream side of the one-inch drain valve. At the time of discovery, Unit 1 was in Mode 1 (Power Operation) at 99 percent power at normal RCS temperature and pressure. A manual reactor shutdown was commenced at 1535 MST in accordance with Technical Specification and Technical Requirements Manual Limiting Conditions for Operation (LCO) 3.4.14 (RCS Operational Leakage) and TLCO 3.14.103 (Structural Integrity). LCO 3.4.14 requires the plant to be placed in Mode 3 (Hot Shutdown) within 6 hours and Mode 5 (Cold Shutdown) within 36 hours upon identification of RCS pressure boundary leakage. RCS boration was promptly commenced and the reactor was manually shutdown at 1731 MST. There were no automatic reactor protection system or engineered safety features actuations and no other component failures, testing, or work in progress that contributed to the leak. There was no release of radioactivity to the environment and no impact to the health and safety of the public.
5282004002 | Palo Verde 1 | 02/08/2004 | 04/02/2004 | ML04105010 | <strong>TECHNICAL SPECIFICATION VIOLATION -EXCEEDED 20%RTP WITH LCO NOT MET</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2004, during power ascension in Unit 1, power was raised above 20 percent rated thermal power without meeting the Limiting Condition for Operation (LCO) for Axial Shape Index (ASI) which is a violation of Technical Specification (TS) 3.0.4. TS 3.0.4 does not allow entry into the specified condition when LCO 3.2.5 is not met. Control Room Operators had incorrectly interpreted a provisional note in procedures 40OP-9ZZ11 Rev. 56, "Mode Change Checklist", 40ST-9ZZM1 Rev.26, "Operations Mode 1 Surveillance Log" step 8.1.17, and Surveillance Requirement (SR) 3.2.5.1, and believed they had up to two hours to restore ASI within limits after exceeding 20 percent power. LER 2001-002-00 reported a similar condition in the past three years when Unit 3 entered Mode 3 with one Auxiliary Feedwater pump inoperable; a condition prohibited by TS 3.0.4.
5282004003 | Palo Verde 1 | 05/08/2004 | 07/08/2004 | ML04195010 | <strong>Manual Reactor Trip - Slipped Control Element Assembly</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2004, at approximately 20:39 (MST), while performing Low Power Physics Testing(LPPT) in Mode 2, Palo Verde Unit 1 was manually tripped as directed by procedure 40AO-9ZZ11,"CEA Malfunction", when Control Element Assembly (CEA) #89 slipped from 136 inches withdrawn to 129.6 inches resulting in a deviation of 7.4 inches from the highest CEA in its' group. No similar condition has been reported in the past three years.
5282004004 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/18/2004 | 07/09/2004 | ML04202037 | <strong>Missed Surveillance Requirement for Temperature Detector Calibration</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2004 it was determined by Engineering personnel that the Technical Specification required calibration of the shutdown cooling heat exchanger resistance temperature devices (RTD) was not adequately addressed in station procedures. Units 1 and 3 were operating in Mode 1, Power Operation and entered Technical Specification Surveillance Requirement 3.0.3. Unit 2 was in Mode 5, Cold Shutdown, which is not an applicable Mode for the RTDs. SR 3.0.3 allows delayed entry into a Limiting Condition of Operation (LCO) required action when a surveillance requirement has not been performed within the specified frequency. The surveillance test procedure was modified and successfully completed, without any adjustment required, in Unit 2 on March 4 and Units 1 and 3 on March 5, 2004. The direct cause of the condition is an inadequate surveillance testing procedure. The apparent cause of the deficient procedure is the lack of recognition by the procedure owner and engineering personnel that the RTDs required calibration before and after improved TS implementation. One similar condition has been reported by PVNGS within the last three years.
5282004005 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/28/2004 | 09/06/2005 | ML05263036 | <strong>Missed ST on Shutdown Cooling Valve RCS Pressure Interlocks</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2004, during a review of Condition Report number 2687507 it was determined that Palo Verde was not testing SDC isolation valve interlocks as described in UFSAR section 7.6, nor were these safety-related interlocks being subjected to a complete channel calibration/functional test as intended by NRC GL96-01. Surveillance tests 36ST-9SI04 and 36ST-9SI05 were revised and tested in all three Units to meet Technical Specification surveillance requirement 3.4.15.2. Surveillance tests 36ST-9SI04 and 36ST-9SI05 were again revised to match the test procedure described in UFSAR section 7.6.2. The tests have been successfully completed in Units 1, 2 and 3. A review of other non-Plant Protection System safety-related interlocks, inhibits, permissives or bypass circuits that may not have been included in surveillance tests has been completed. Previous similar events were reported in LERs 3-2003-003, 2-2003-003 and 1-2001-005.
5282004006 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 06/14/2004 | 10/13/2005 | ML05298041 | <strong>Loss of Offsite Power - Three Unit trip</strong><br /><i>Abstract:&nbsp;</i>On June 14, 2004, at approximately 07:41 MST, a ground-fault occurred on the Western Area Power Authority 230kV Liberty substation to Westwing substation line (approximately 47 miles from the Palo Verde Nuclear Generating Station). A failure in the protective relaying resulted in the ground-fault not isolating from the local grid for approximately 38 seconds. The fault cascaded into the protective tripping of a number of 230kV and 525kV transmission lines, which ultimately led to the Loss of Offsite Power (LOOP) at the Palo Verde switchyard. In Unit 1 and 2, the LOOP caused each reactor to trip from 100 percent power on a Core Protection Calculator generated reactor trip on low Departure from Nucleate Boiling Ratio due to low Reactor Coolant Pump (RCP) shaft speed. Unit 3 tripped last and experienced a Variable Over Power Trip from approximately 109 percent power due to increased flow from the RCPs caused by an increase in voltage and frequency from the main turbine generator. The LOOP placed each Unit in a condition for "Notice of Unusual Event" (NUE). The Unit 2 Train "A"emergency diesel generator started, but failed to maintain electrical output during load sequencing and resulted in the declaration of an "Alert" in Unit 2 at 07:54 MST. The NUE for Units 1 & 3 was declared at 07:58 MST. No similar condition has been reported in the past three years.
5282004007 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 07/12/2004 | 08/13/2004 | ML04238012 | <strong>Exceeding the Maximum Power Level Specified in Operating License Condition 2.C(1)</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2004, during a review of historical operating data, Engineering concluded that the maximum Palo Verde specific calorimetric error was approximately 38.76 MW in Units 1 and 3 and 39.90 MW in Unit 2 or approximately 1 percent (1 %). The error resulted in core power levels above the Operating License limits of 3876 MW thermal for Units 1 and 3 and 3990 MW thermal in Unit 2 while the ultrasonic flow measurement (UFM) instrument was in service. The non-conservative feedwater flow input to the secondary calorimetric calculation had been in place in Units 1 and 3 since 1999 and in Unit 2 since 2000. This review and its results were based on a letter received from the vendor (Caldon) stating there maybe an error in the flow measurement. The cause of the event was an error in the velocity profile factor used by the UFM. The corrective action for this event was the removal of the UFMs from service. In the past three years, no previous similar events were reported.
5282004008 | Palo Verde 1 | 07/19/2004 | 09/15/2004 | ML04266012 | <strong>IMPROPER CONTACT CONFIGURATION ON CONTAINMENT ISOLATION VALVE</strong><br /><i>Abstract:&nbsp;</i>On July 19, 2004, at approximately 16:18 Mountain Standard Time (MST), Unit 1 was in Mode 1 at100 percent power, when troubleshooting identified a rotor cam, which actuates a bank of limit switches, on a containment isolation valve (1JHPBUV0004) out of position due to personnel error. The rotor cam was oriented such that the limit switch in this bank would actuate opposite of the desired control logic for the Safety Equipment Actuation Status (SEAS) and Containment Isolation Actuation Signal (CIAS). With valve 1JHPBUV004 in the open position, the valve's CIAS closing circuit was interrupted which would prevent the valve from closing upon a CIAS. The valve was declared inoperable and Unit 1 entered Limited Condition for Operation (LCO) 3.6.3 Condition A, (Containment Isolation) and LCO 3.6.7 Condition A (Hydrogen Recombiner B) and LCO 3.3.10 Condition A (Hydrogen Analyzer B). Valve 1JHPBUV004 was returned to service and declared operable on July 23, 2004 (11:36 MST). A similar event occurred after Unit 3's seventh refueling outage where the CIAS function of 3JHPAUV0001was disabled due to an incorrect control wire configuration. The event is documented on LER 99-001-00.
5282004009 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 07/30/2004 | 05/11/2005 | ML06138054 | <strong>Emergency Core Cooling System Piping Voids May Have Prevented Fulfillment of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2004, Units 1, 2 and 3 were operating at approximately 100 percent power, when Control Room personnel were informed that a voided section of Emergency Core Cooling System (ECCS) suction piping might prevent the fulfillment of the safety function to remove residual heat and mitigate the consequences of a Loss of Coolant Accident. The voided ECCS piping sections could cause cavitation and/or air binding of the High Pressure Safety Injection and Containment Spray pumps. Initial compensatory measures were implemented for control room operators to open the inboard containment sump isolation valves allowing 90 percent of the voided piping to fill during accident conditions. Subsequent measures were taken to return the containment sumps to their design configuration by filling the piping with borated water. These actions were completed in all three units on August 4, 2004. No similar events have been reported in the past three years. This LER supplement is being submitted to update root cause and corrective action information that was not available at the time of the original submission.
5282004011 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 11/10/2004 | 01/06/2005 | ML05013015 | <strong>Missed Surveillance Requirements for Containment IVs Test/Drain Valves</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2004, Units 1 and 2 were in MODE 1, operating at approximately 100 percent and Unit 3 was defueled for a refueling outage when it was discovered that eight (8) test and drain valves located between the Containment Isolation Valves (CIVs) were not included in the surveillance procedure for TS LCO 3.6.3. The surveillance procedure was revised to include the drain and test valves. The revised procedure was successfully performed in Units 1 and 2 on November 11, 2004 and in Unit 3 prior to reaching MODE 4 after its refueling outage. Previous similar events were reported in LER 50-528/2001-005 and LER 50-528/2004-004.
5292004001 | Palo Verde 2 | 02/19/2004 | 06/01/2004 | ML04160056 | <strong>Steam Generator Tube Leak</strong><br /><i>Abstract:&nbsp;</i>At 15:22 Mountain Standard Time (MST) on 2/19/04, the Control Room staff received ALERT radiation level alarms from the Main Steam Line N-16 Radiation Monitors, RU-142, channels 1 and 2 indicating there was primary to secondary leakage in Steam Generator #1, and entered the Excessive RCS Leakrate procedure. At 15:38 MST, the ALERT radiation level alarm was received from the Condenser Air Removal System Radiation Monitor, RU-141,channel 2 indicating primary to secondary leakage at a rate of approximately 11 Gallons Per Day (GPD). At 16:00MST, Plant Management determined they would shutdown Unit 2 in response to the apparent increase in steam generator primary to secondary leakage. Preliminary results of grab samples from the Condenser Air Removal System confirmed that primary-to-secondary leak rate had increased from the pre-event leak rate of 0.4 to 0.7 GPD to approximately 3 to 5 GPO. At 16:31 MST, a plant shutdown was commenced. The reactor was manually tripped from approximately 21% power. The Steam Generator primary to secondary leak rate did not exceed the Technical Specification limit of 150 GPD (LCO 3.4.14), the EPRI guidelines that would require a plant shutdown or the Station Administrative shutdown limit of 50 GPO. In situ testing was performed on the leaking tube and met the criteria of retaining a margin of 3.0 against burst under normal steady state full power operation and a margin of 1.4 against burst under the limiting design basis accident concurrent with a safe shutdown earthquake. The tube was plugged during the subsequent mid-cycle outage. In the past three years, Palo Verde Nuclear Generating Station has not experienced a Steam Generator tube leak that required a Unit shutdown.
5292004002 | Palo Verde 2 | 07/14/2004 | 09/10/2004 | ML04260033 | <strong>Reactor Trip on Low DNBR</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2004 at approximately 0134 Mountain Standard Time (MST) Unit 2 was operating at100 percent power, Mode 1 (Power Operations), when the Unit experienced a reactor power cutback followed by an automatic reactor trip. At the time of the event, Palo Verde was in a severe thunderstorm in which several lightning strikes had landed in the vicinity of the Palo Verde switchyard. Approximately five seconds after the series of lightning strikes, the main generator tripped which in turn initiated a reactor power cutback. Approximately 11 seconds after the reactor power cutback, a low departure from nucleate boiling ratio (DNBR) reactor trip was initiated by the core protection calculators (CPCs) in response to a conservative calculation of update DNBR for plant conditions. The main generator tripped on a loss of generator field signal which was induced by the effects of the multiple lightning strikes in the vicinity of the Palo Verde switchyard. The cause of the reactor trip is attributed to overly conservative addressable constants for planar radial peaking factor in the CPCs which are used to calculate update DNBR. A similar reactor trip occurred in Unit 3 on June 7, 2004 (LER 50-530/2004-002)
5292004003 | Palo Verde 2, Palo Verde 3 | 12/31/2004 | 02/22/2005 | ML05063027 | <strong>Actuation of Unit 2 and 3 Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2004, at approximately 1042 Mountain Standard Time (MST), Units 2 and 3 were operating in MODE 1, at approximately 100 percent power, when Arizona Public Service Company (APS) Transmission and Distribution (T&D) personnel inadvertently tested a relay for the 525 kilovolt (kV) Westwing #2 transmission line that resulted in the Westwing #2 line relaying out and disrupting power to the PVNGS NAN-XO1 startup transformer. Disruption of power to the NAN-XO1 startup transformer resulted in the loss of offsite power to the Unit 2 train "A" engineered safety features (ESF) 4.16 kV class electrical buss and Unit 3 train "B" ESF 4.16 kV class electrical buss. The loss of power to the Unit 2 and 3 ESF 4.16 kV class electrical busses caused auto-starts of the associated diesel generators to supply power to the Unit 2 "A" Train PBA-S03 class bus and the Unit 3 "B" Train PBB-S04 class bus. All equipment responded satisfactorily. By 1107 MST, power to the Westwing #2 transmission line and startup transformer NAN-XO1 had been restored. Previous similar events have been reported in LERs 50-528/2004-006 and 50-530/2003-004.
5302004001 | Palo Verde 3 | 02/29/2004 | 04/29/2004 | ML04127048 | <strong>RCS Pressure Boundary Leakage Caused by Degraded Alloy 600 Component</strong><br /><i>Abstract:&nbsp;</i>On February 29, 2004 with Unit 3 in Mode 3, Hot Standby, engineering personnel discovered boric acid on a pressurizer heater sleeve while conducting a required boric acid walkdown. The Unit had been shutdown and was being maintained in Mode 3 while trouble shooting a turbine-generator excitation problem. The cause of the boric acid leakage was attributed to primary water stress corrosion cracking of alloy 600 materials in the pressurizer heater sleeve. The amount of boric acid found was small. The pressurizer heater sleeve was repaired using a mechanical nozzle seal assembly (MNSA). Similar previous conditions of pressure boundary leakage were reported in LER 50 - 530/2003-002-00, LER 50-530/2001-003-00, and. LER 50-528/2001-001-00.
5302004002 | Palo Verde 3 | 06/07/2004 | 04/25/2006 | ML06129025 | <strong>Main Turbine Control System Malfunction Results in Automatic Reactor Trip on Low DNBR</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2004 at approximately 1458 hours (MST), Unit 3 was operating in Mode 1, Power Operations, at approximately 99 percent power when the main turbine intercept valves fast closed and the control valves ramped closed. The reactor power cutback and steam bypass control systems (RPCB and SBCS) responded to the large decrease in steam flow by inserting group 4 and 5 control rods into the core and opening steam bypass valves to reduce reactor power and maintain reactor coolant temperature. Approximately 10 seconds after the RPCB occurred, a low Departure from Nucleate Boiling Ratio (DNBR) reactor trip was initiated by the core protection calculators (CPCs) as a result of rodded radial peaking factor for the control rod configuration. The reason the main turbine intercept valves fast closed and the control valves ramped closed was attributed to a malfunction in the electro-hydraulic system. The cause of the reactor trip has been attributed to a diminished DNBR margin as a result of the rodded radial peaking factor for the control rod configuration that existed following the RPCB. Subsequent to this event, a similar event occurred when Unit 2 experienced a main turbine trip, RPCB, and subsequent reactor trip on low DNBR on July 14, 2004.