## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
1332005001 | Humboldt Bay 3 | 02/04/2005 | 06/10/2005 | ML05166032 | <strong>Missing Incore Detectors</strong><br /><i>Abstract:&nbsp;</i>During a review and cataloging of the contents of the Humboldt Bay Power Plant (HBPP) spent fuel pool (SFP), PG&E personnel determined that incore detectors were missing and notified the NRC on February 4, 2005. Incore detectors contain non-fuel special nuclear material (SNM), varying from 0.04 to 0.005 grams of uranium-235 each. HBPP records showed that 54 incore detectors should be in the SFP. However, following an investigation, PG&E determined that one complete and three partial incore detectors were missing. PG&E submitted Licensee Event Report (LER) 2005-001-00 on February 22, 2005 in accordance with 10 CFR 20.2201(b)(1), stating a supplemental LER would be issued to provide more details. The physical search for the incore detectors is complete, and relevant historical documents have been reviewed. PG&E believes the missing incore detectors were erroneously included with irradiated hardware shipped to a low level radioactive waste facility at Hanford or Barnwell. If so, the addition of these detectors would be within the design and licensing basis of these facilities and would not increase the risk to the health and safety of the public, workers, or environment. The causes of the event were determined to be use of an inadequate procedure for cutting the incore detectors from incore strings, inadequate training of SNM custodians, and failure to follow an SNM procedure for control and accountability of incore detectors. Corrective actions have been developed.
2192005001 | Oyster Creek | 03/18/2005 | 08/04/2005 | ML05224024 | <strong>Supplemental Report to "A" Control Rod Drive Pump Was Returned to Service Prior to Correcting the Cause of Failure Resulting in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>During a functional test of the 1A2 Local Shutdown Panel (LSP) at 1254 on February 17, 2005, the "A" Control Rod Drive (CRD) Pump failed to start from the Main Control Room (MCR). The cause of this failure was attributed to contact high resistance on relay TR-2 in the 1A2 LSP. It was concluded that the high resistance cleared itself during subsequent relay operation . The relay was then scheduled for future replacement . "A" CRD Pump was successfully surveilled and returned to service. On March 16, 2005 at 1834, during a regular monthly surveillance, "A" CRD Pump did not start. Subsequent investigation found the 480 VAC breaker-closing spring was not charged. The closing spring is recharged by an electric motor immediately after the breaker opens . On March 18, 2005, investigation revealed a loose terminal wire connection to relay TR-2 within the LSP, which prevented charging of the closing spring.It is believed this condition existed on February 17, 2005 and should have been corrected . Technical Specifications(TS) only allow a 7-day out of service time for CRD Pumps resulting in a violation of TS3.4.D. Corrective actions included replacing the relay, sending the relay out for failure analysis and performing verification of closing spring condition on all safety related 480 VAC breakers. This Supplemental LER is based on determination of the root causes to be a manufacturing deficiency consisting of a loose connection in the LSP, which caused the closing spring to not recharge, and a failure to detect that the closing spring was discharged prior to exceeding the Tech Spec out of service allotment. There were no previous similar events at Oyster Creek Generating Station involving a breaker failing to close on demand due to the closing spring being discharged.
2192005002 | Oyster Creek | 06/01/2005 | 07/29/2005 | ML05216004 | <strong>Actuation of Reactor Protection System Due to An Anticipatory Generator Load Reject Caused by Faulted Lightning Arrestors in a Local Sub-Station</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2005, at 21:09, with Oyster Creek at 100% power, an Anticipatory Generator Load Reject scram occurred. During restoration of a transformer by the transmission utility at their substation, a failure of lightning arrestors resulted in a phase-to-phase-to-ground short circuit. This resulted in a grid transient of sufficient magnitude that the Oyster Creek Turbine-Generator sensed a load rejection condition, which resulted in a reactor scram signal. The reactor scrammed and the turbine-generator tripped as expected for this condition. All safety systems performed as expected. The plant was stabilized in the hot shutdown mode. Corrective actions included completing restart required evaluations, testing and confirmation from the involved transmission utility that conditions in the substation would not result in recurrence of the grid disturbance. The apparent cause of this event was equipment failure of the lightning arrestors in the transmission utility substation that created a grid disturbance. There have been several grid disturbances over the life of the plant, including two LERs: LER 2003-003, Actuation of Reactor Protection System Due to a Grid Transient (August 14, 2003). LER 1994-007 was a reactor scram caused by a 230 KV bus section differential relay trip while a switchyard worker was installing a Digital Fault Recorder.
2192005003 | Oyster Creek | 07/12/2005 | 09/12/2005 | ML05263037 | <strong>Technical Specification Violation due to Missing Test Cap</strong><br /><i>Abstract:&nbsp;</i>With the plant in normal full power operation on July 12, 2005, an In-Service Test was in progress on containment isolation valves for the nitrogen make-up line. When the outboard isolation valve was cycled open, an adjacent recorder indicated flow on the order of 125 scfh (standard cubic feet per hour). The flow stopped when the outboard isolation valve was shut. Technical Specifications require an affected containment penetration to be isolated with at least one deactivated automatic valve secured in the isolation position within 4 hours. Based on information available at that time, the outboard isolation valve was deactivated in the closed position by disconnecting its operating air supply to comply with Technical Specifications. The next day, upon further investigation, the source of the leakage was found to be a test cap missing from a one-quarter inch test connection between the valves. A new test cap was obtained and installed. The location of the leak rendered the outboard valve functionally inoperable, therefore the inboard valve should have been deactivated to meet the 4 hour requirement. All similar test caps manipulated during leak rate testing that were not controlled with leak rate tags were verified to be installed and properly secured. Applicable leak rate test procedures will be revised prior to next use to require the use of leak rate tags.
2192005004 | Oyster Creek | 08/24/2005 | 10/19/2005 | ML05305039 | <strong>Actuation of an Emergency Diesel Generator due to Unexpected Breaker Opening</strong><br /><i>Abstract:&nbsp;</i>The plant was operating normally at full power on 8/24/05. At 2337 hours, the D 4160 vac breaker opened and de-energized the D bus. Emergency Diesel Generator 2 (EDG) automatically started and re-powered the D bus. The Reactor Protection System processed a half scram, both Fire Diesels started, and Dilution pumps tripped. Other equipment was momentarily de-energized. A 7 day Limiting Condition for Operation (LCO) was entered and an 8 hr Emergency Notification System call was made. The D breaker was replaced, a normal electric lineup was restored, EDG 2 was shut down, and the LCO was exited. A failed light bulb was found in the D breaker closed indicating circuit. It was also found that the current limiting resistor had been removed in that circuit. An extent of condition review determined that only one other breaker was similarly configured. The apparent cause of the event was an internal short in an indicating light in the breaker closed indicating circuit. The breaker was eliminated as a possible cause of the trip after testing by the breaker manufacturer. Corrective Action is to remove indicating bulbs from the D bus and EDG 2 breaker closed indication circuits until current limiting resistors are installed.
2192005005 | Oyster Creek | 10/13/2005 | 12/12/2005 | ML05355036 | <strong>Technical Specification due to Main Steam Safety Valve Setpoints Discovered out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>Oyster Creek Generating Station was in RUN at 100% power on 10/13/05 when a condition was discovered during routine laboratory as-found testing for Safety Valves (SVs) (EIIC: RV) removed during the 1R20 refueling Outage in November 2004. There were no structures, systems or components out of service that contributed to this event. In accordance with ASME Boiler & Pressure Vessel Code Criteria the nine SVs removed in refueling outage 1R20 were sent for as-found setpoint testing within the one-year time frame. Based on information received from the laboratory performing SV as-found testing, Site Engineering personnel determined that SV setpoint deficiencies existed with three SVs that were installed during the 1R19 refueling outage. Three (3) of the nine (9) valves exceeded the setpoint tolerance of +/-1% (+/-12 psig) as specified in the Technical Specifications paragraph 2.3. All three SVs were within the ASME Code allowable +/-3% tolerance for as found values and there were no actual safety consequences associated with this event.
2202005001 | Nine Mile Point 1 | 03/07/2005 | 05/06/2005 | ML05137040 | <strong>Automatic Reactor Scram due to a Failure in the Circuitry for a Moisture Separator Tank Level Switch</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2005, at approximately 0437 hours, with the mode switch in "RUN" and reactor thermal power at approximately 100%, Nine Mile Point Unit 1 experienced an automatic reactor scram initiated by a turbine trip caused by a failure in the circuitry of a Moisture Separator Tank level switch. A spurious actuation of the Moisture Separator Tank level switch was caused by a short circuit between two terminal points caused by water intrusion into the associated junction box. Based on inspections performed, the most probable source of the water inside the junction box was condensation of steam from a packing leak in an instrument root valve in the near vicinity. Corrosion products accumulated at adjacent terminal points due to previous water intrusions which created moisture conditions over an extended period of time leading to a short circuit. To prevent recurrence, the terminal points were cleaned and all top and side external penetrations of the junction box were sealed. A design change to the trip logic of the Moisture Separator Tank level switches to prevent a trip on a single level switch contact failure was installed and tested in refuel outage 18. Inspections and repairs were performed in refuel outage 18 on a defined population of junction boxes with similar environmental conditions.
2202005002 | Nine Mile Point 1 | 04/14/2005 | 06/13/2005 | ML05172040 | <strong>Fuel Moved with an Inoperable Source Range Monitor due to Human Error Resulting in a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2005, at approximately 1654 hours, with the reactor in the "Refueling Condition" and spiral core reload in process, fuel moves were stopped when source range monitor (SRM) 12 failed to indicate any neutron counts when a twice burnt fuel bundle was placed adjacent to the SRM to achieve the required minimum count rate. Technical Specification 3.5.3.b states, "During core alterations two SRMs shall be operable, one in and one adjacent to any core quadrant where fuel or control rods are being moved. Operable SRMs shall have a minimum of 3 counts per second except as specified in d and e below." Contrary to this, fuel was moved adjacent to an inoperable SRM (12). The SRM failed to indicate any counts because the SRM instrumentation cabling was left disconnected following maintenance activity earlier in the outage. The cause of this event involved human performance errors associated with failure to adhere to maintenance work instructions. Had the work instructions been implemented as written, the event would not have occurred.
2202005003 | Nine Mile Point 1 | 08/18/2005 | 10/12/2005 | ML05294024 | <strong>Automatic Reactor Scram During Surveillance Testing due to Inadvertently De-energizing 4160 VAC Power Board 11</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2005, at approximately 0950 hours, with Nine Mile Point Unit 1 operating at approximately. 100 percent power, an automatic reactor scram was experienced. The scram occurred when Power Board 11 (PB-11) was de-energized due to inadvertent protective over-current relay actuations. The resulting loss of power to the Channel 11 side of the Reactor Trip Bus (RTB), concurrent with planned in-progress surveillance testing that introduced a half-scram signal an the opposite (Channel 12) side of the RTB, caused a full automatic reactor scram signal to be generated. PB-11 was de-energized due to inadvertent protective over-current relay actuations caused by mechanical jarring of the relays mounted on the cubicle door. This occurred when a 4.16 kV circuit breaker was being rolled into position within its PB-11 cubicle. The underlying cause of the event is failure to adequately identify, assess, and mitigate potential risks of conducting work. The potential plant impacts that could be caused by inadvertent actuation or damage to surrounding equipment due to planned work were not identified or effectively managed. Corrective actions have been developed such that, when completed, the work control process will yield consistent and effective risk assessments of work activities that will prevent the same type of inadvertent relay actuation and other similar events (i.e., events caused by failure to identify and effectively manage potential risks associated with surrounding equipment).
2202005004 | Nine Mile Point 1 | 12/19/2005 | 02/17/2006 | ML06062051 | <strong>Operation Prohibited by Technical Specifications due to Unrevealed Inoperability of One Off-site Power Source</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2005, at 1509 hours, National Grid (NG) Regional Control notified the Nine Mile Point Unit 1 (NMP1) Control Room that a Traveling Operator had noted abnormal readings on one of the 115 KV off-site power lines (Line 4) and suggested the indication could be the result of an open phase. The James A. Fitzpatrick Nuclear Power Plant (JAF) Control Room was contacted and an investigation revealed a failure of the bus bar connector on the "A" phase of Line 4 in the JAF switchyard. The unknown failure had existed from November 29, 2005, to December 19, 2005, and during that time, NMP1 exceeded the Technical Specification (TS) 3.6.3.b, "Emergency Power Sources," allowed out-of-service time for inoperable off-site power line. Additionally, during that time, NMP1 exceeded the TS 3.6.3.c allowed out-of-service time for inoperable diesel-generator power system on two occasions. Line 4 was restored to operable status on December 20, 2005, at 1512 hours. The cause of the failure to identify the Line 4 failure is a functional design deficiency regarding the adequacy of Control Room indications and alarms. Because of the design of off-site power to JAF and NMP1, and alarms and indications, there was no interruption of power to either unit and no alarm to alert personnel of the abnormal situation. There is an ampere loading indication for both off-site lines at NMP1, but the typical operating value falls in an uncalibrated and unmarked area of the meter. Corrective actions have been developed such that, when completed, a loss of current on any of the phases of off-site power sources will be accompanied by a plant process computer alarm and will be clearly visible on control panel indications.
2372005001 | Dresden 2, Dresden 3 | 02/03/2005 | 04/04/2005 | ML05094012 | <strong>4160 Volt Relaying and Metering Single Failure Vulnerability for Units 2 and 3</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2005, at 1915 hours (CST), with Unit 2 at approximately 95 percent power and Unit 3 at approximately 96 percent power, Dresden Nuclear Power Station engineering personnel confirmed that single failure vulnerabilities existed on 4160 Volt Relaying and Metering transformers on both units. The single failure vulnerabilities defeated the independence of the offsite alternating current power supplies. If this failure occurred during a Loss of Coolant Accident, the Containment Cooling Service Water system pumps may not have been able to be started within the required time. The single failure vulnerabilities were removed on February 4, 2005, at 0009 hours, and the effected plant equipment was declared operable. The root cause of this event was determined to be an existing latent design deficiency. The corrective action to prevent reoccurrence is currently in place in the Configuration Change procedures used to install new designs at Dresden Nuclear Power Station. A preliminary engineering review for similar existing latent design deficiencies found no other similar deficiencies. A corrective action is in place for engineering to complete an extent of condition review of the alternating current, Emergency Diesel Generators, and direct current systems for latent design deficiency conditions similar to this event.
2372005002 | Dresden 2 | 03/24/2005 | 05/23/2005 | ML05143034 | <strong>Unit 2 Group 1 Isolation and Resulting Scram</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2005, at 0529 hours (CST), with Unit 2 at approximately 96 percent power, two unexpected control room alarms were received for exceeding the Electro-Hydraulic Control System maximum combined flow limit setpoint and open Turbine Bypass Valves. Several seconds later, high flow in the Main Steam System resulted in a signal to close the Main Steam Isolation Valves that initiated an automatic reactor scram. All control rods fully inserted and all other systems responded to the reactor scram as expected, except for non-safety related equipment, the Turbine Generator Lube Oil Pump and the 2B Reactor Feedwater Pump Auxiliary Oil Pump, which did not operate as required. The root cause of this event is indeterminate. The most probable cause is attributed to an increase in electrical resistance between electrical pins 13 and 22 on the "A54" card within the Electro-Hydraulic Control System. The corrective actions to prevent recurrence are to replace the "A54" card backplane connector, remake all termipoints on the connector for the A54 card and to rework the remaining connectors between electrical pins 13 and 22. The "A54" card backplane connector was replaced and the all termipoints on the connector were remade prior to startup. The remaining connectors will be reworked during the next Unit 2 refueling outage.
2372005003 | Dresden 2, Dresden 3 | 06/23/2005 | 08/22/2005 | ML05242043 | <strong>Units 2 and 3 Offsite Power Sources Declared Inoperable due to Low Voltage</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2005, at 1549 hours (CDT), with Unit 2 at approximately 99 percent power and Unit 3 at approximately 99 percent power with a nominal 352 kilo volts (kV) switchyard voltage, Dresden Nuclear Power Station was notified by Bulk Power Operations that predicted post unit trip switchyard voltages with a postulated Loss of Coolant Accident, for Unit 2 was 342.5 kV and for Unit 3 was 342.3 kV. These predicted voltages were below design assumptions and resulted in the station declaring the Technical Specification offsite power sources inoperable. The cause of this predicted low switchyard voltage level event was determined to be the result of changes in the manner that the transmission system is operated. Corrective actions include the installation of a new transformer with a load tap changer for Unit 2 (completed), installation of a new transformer with a load tap changer for Unit 3 that is currently scheduled to be installed in the next refueling outage, and submittal of an amendment request for Units 2 and 3 to allow the use of the automatic feature of the load tap changers (complete). Additionally as an interim action, Exelon Generation Company, LLC, has contracted with other power producers to provide additional electrical power to raise the grid voltage when the Dresden Nuclear Power Station switchyard voltage is low.
2372005004 | Dresden 2 | 07/25/2005 | 12/12/2005 | ML05354025 | <strong>Unit 2 Main Steam Target Rock Safety/Relief Valve As-Found Setpoint Outside of Technical Specification Allowed Value</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2005, with Unit 2 at approximately 100 percent power, Dresden Nuclear Power Station discovered during a vendor inspection of a Unit 2 Main Steam Target Rock Safety/Relieve Valve, that the valve's second stage disc and seat had steam cutting. This valve had been removed from Unit 2 service in November 2004 and subsequently did not pass its setpoint test on February 17, 2005. The valve lifted at approximately 1091 pounds per square inch gage which is lower than specified in Technical Specification 3.4.3, "Safety and Relief Valves," Allowed Value of 1135 pounds per square inch gage, plus or minus 11.4 pounds per square inch gage. The discovery of the steam, cutting of the valve's second stage disc and seat provided sufficient evidence for Dresden Nuclear Power station to conclude that the valve's setpoint did not meet its Technical Specification requirements while it was installed in the plant during 2004. The apparent cause of the Target Rock Safety/Relief Valve low setpoint and steam cutting of its second stage disc and seat, was most likely caused by foreign Material (e.g., rust, crud) lodged between the valve's second stage seat and disc that was introduced into the valve during in-plant testing with Reactor Coolant System steam in November 2003. A corrective action was previously implemented in November 2004 to eliminate the requirement for in-plant testing with Reactor Coolant System steam.
2442005001 | Ginna | 02/16/2005 | 04/14/2005 | ML05109025 | <strong>Failure of ADFCS Power Supplies Results in Plant Trip</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2005, at approximately 2112 EST, with the plant in Mode 1 at approximately100% steady state reactor power, the reactor automatically tripped. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all safety systems operated as designed, with the exception of the control function for the main steam atmospheric relief valves (ARVs). The reactor was stabilized in Mode 3. The tripping of the reactor was caused by a turbine trip as the result of an anticipated-transient-without-scram (ATWS) mitigation actuation circuitry (AMSAC) signal. The AMSAC signal was the result of low feedwater flow signals, caused by the failure of redundant advanced digital feedwater control system (ADFCS) power supplies. The ARV automatic and remote manual operation was also affected by the failed power supplies.Corrective action to prevent recurrence is outlined in Section V.B.
2442005002 | Ginna | 04/01/2005 | 05/25/2005 | ML05154030 | <strong>Emergency Diesel Generator Start Resulting from Loss of Off-Site Power Circuit 751</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2005, a faulted lightning arrester resulted in the loss of off-site Circuit 751. With the electrical system in a 50/50 alignment, the loss of Circuit 751 resulted in the loss of safeguards busses 16 and 17. The B Emergency Diesel Generator (EDG) started automatically and re-energized the safeguards busses as designed. Corrective action to prevent recurrence is outlined in Section V.B.
2442005003 | Ginna | 06/10/2005 | 08/08/2005 | ML05224025 | <strong>Emergency Diesel Generator Start Resulting From Loss of Off-Site Power Circuit 751</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2005, a lightning strike resulted in the loss of off-site Circuit 751. With the electrical system in a 50/50 alignment, the loss of Circuit 751 resulted in the loss of safeguards busses 16 and 17. The B Emergency Diesel Generator (EDG) started automatically and re-energized Bus 16. The Bus 17 feeder breaker from the BEDG failed to close resulting in the temporary loss of Bus 17. The A Service Water Pump (SWP) motor faulted and tripped when manually started per procedure. Corrective action to prevent recurrence is outlined in Section V.B.
2472005001 | Indian Point 2 | 01/19/2005 | 08/03/2005 | ML05222011 | <strong>Technical Specification Prohibited Condition Due to Exceeding the Allowed Completion Time for One Inoperable Train of ECCS Caused by an Inoperable Auxiliary Component Cooling Water Check Valve</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2005, during a quarterly surveillance test of the 21 Auxiliary Component Cooling Water (ACCW) Pump, the 22 ACCW Pump discharge check valve (755A) failed to seat resulting in reverse flow through the 22 ACCW Pump. Engineering determined on February 9, 2005, that operability of valve 755A could not be positively demonstrated after the valve's maintenance in November 2004. The last successful performance of the quarterly surveillance test for the 22 ACCW pump was on October 14, 2004. For Technical Specification (TS) purposes, one inoperable ACCW Pump is assumed to render one containment recirculation pump train inoperable. TS 3.5.2 has a completion time of 72 hours for one or more trains of Emergency Core Cooling System (ECCS) inoperable. The assumed inoperability period exceeded the TS Allowed Outage Time. The cause of the event was interference in the 22 ACCW discharge check valve hinge bushing/pin interface.The apparent cause was inadequate maintenance due to either damage during valve reassembly from a 10 year inspection in November 2004, or the relocation of an undetected pre-existing flaw to a more problematic location during or following the November 2004 reassembly. Contributing causes were insufficient valve maintenance procedure, wrong plug gasket, and inadequate post work test. Significant corrective actions included valve disassembly, repair, gasket replacement and verification of freedom of movement of the disc. A step was incorporated in a combined site valve maintenance procedure to cycle valves to check for clearance problems. Also included in the site valve maintenance procedure was lessons learned from this event. Personnel were coached on management's expectation on attention to detail. The IST Program Database was coded appropriately to ensure IST Engineers provide the requirement to verify the head of the opposite pump for post test operation. The event had no effect on public health and safety.
2472005002 | Indian Point 2 | 02/18/2005 | 04/19/2005 | ML05118014 | <strong>Technical Specification Prohibited Condition Due to Exceeding the Allowed Completion Time for One Inoperable Train of ECCS Caused by Gas Intrusion from a Leaking Check Valve</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2005 engineering determined that the amount of gas vented from the 23 Safety Injection Pump on January 27, 2005 was of such a quantity that the pump was inoperable. Prior to this event the station was dealing with SI accumulator out-leakage. The accumulator leakage was found to be migrating back to the Refueling Water Storage Tank through a circuitous path. As the accumulator has a nitrogen overpressure system normally in service there existed the potential for entrainment and subsequent dissolution of gas.As events unfolded some of the dissolution of gas resulted in gaseous void areas accumulating within the 23 Safety Injection pump casing. The cause of the event was back-leakage of accumulator water through the Safety Injection System and subsequent gas dissolution within the Safety Injection Pump casing. Corrective actions included venting the applicable portions of the system piping and components to ensure operability. A design change has been generated to install an additional test line isolation valve to prevent accumulator back leakage. In addition, venting/ultrasonic test monitoring is ongoing. The event had no effect on public health and safety.
2472005003 | Indian Point 2 | 12/22/2005 | 02/14/2006 | ML06058016 | <strong>Automatic Start of Both Motor Driven Auxiliary Feedwater Pumps due to Trip of 22 Main Feedwater Pump Caused by Low Lube Oil Pressure due to an Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2005, while performing a plant shutdown, the 22 Main Boiler Feedwater Pump (MBFP) tripped on low lube oil (LO) pressure initiating the automatic start of both motor driven Auxiliary Feedwater (AFW) pumps. The 22 MBFP tripped while operators attempted to swap the 21 LO cooler to the 22 LO cooler. Swapping to the 22 LO cooler was required because a service water control valve was not maintaining proper LO temperature. The most probable cause is that the MBFP LO experienced a pressure drop due to air in the 22 LO cooler oil side which had not been adequately vented prior to the swap. Operators stabilized SG level and secured both motor driven AFW pumps and returned them to Auto. The apparent cause was inadequate procedure guidance for filling and venting the LO coolers. Corrective actions will be to revise the System Operating Procedure for the LO coolers to provide detailed fill and vent instructions, and preparation of a refueling outage activity for inclusion in the outage schedule to fill and vent LO coolers prior to MBFP start. The event had no effect on public health and safety.
2472005004 | Indian Point 2 | 12/22/2005 | 02/14/2006 | ML06058016 | <strong>Automatic Start of Both Motor Driven Auxiliary Feedwater Pumps due to 22 Steam Generator High-High Level Signal Caused by Overfeeding due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2005, while offline for maintenance, at approximately 0550 hours, both motor driven Auxiliary Feedwater pumps (AFWPs) received an automatic actuation signal to start. Both AFWPs were in service at the time feeding the SGs with the 22 Main Goldwater Pump (MBFP) on turning gear and the 21 MBFP isolated and in recirculation. A 22 SG High-High Level signal resulted in tripping the 21 MBFP which by design initiates start of the AFWPs. The Reactor Operator (RO) assigned to feed water control failed to adequately monitor SG level and overfed the 22 SG. The RO had decreased AFW flow instead of stopping AFW flow as intended. The RO failed to adequately monitor SG Levels, check his actions or request a peer check. Operators restored the 22 SG level to normal. The apparent cause was personnel error due to failure to perform self checking, and failure to monitor alternate SG level indications to ensure appropriate SG Levels. Corrective actions include, administrative removal of the RO from licensed duties, simulator testing and evaluation and return to duty, coaching the RO on use of human performance tools, issuing a Station Clock Reset/Red Memo for this event as well as others for the shutdown to advise personnel of the event and lessons learned and convey management's expectations on use of human performance tools. The event had no effect on public health and safety.
2502005001 | Turkey Point 3 | 01/01/2005 | 02/28/2005 | ML05067034 | <strong>Mode Increase While in Technical Specification Shutdown Action Statement</strong><br /><i>Abstract:&nbsp;</i>On January 1, 2005, Unit 3 entered Mode 2 during reactor startup while in a Technical Specification (TS) shutdown action statement. This is prohibited by TS 3.0.4. During reactor startup, 3A Intake Cooling Water(ICW) basket strainer backwash was commenced. This caused 3A ICW header to be declared inoperable and a 72-hour shutdown action was entered in accordance with TS 3.7.3, Action c. The reactor startup continued and the unit entered Mode 2 with the 3A 1CW header inoperable. The ICW header was out of service for 53 minutes and the 72-hour time limit in TS 3.7.3, Action c was not challenged. The cause is attributed to improper communication from the reactor control operator (RCO) to the unit supervisor and shift manager. Corrective actions included 1) Coaching and counseling the RCO on the expectation for communicating required information at all times. 2) Updating the ICW strainer backwash procedure to obtain Shift Manager written permission prior to removing an ICW header from service and entering TS Action c. 3) Issuing a night order to all Operations personnel to reiterate that removal of any TS related equipment must follow site procedures, which requires the component to be logged in the Equipment Out-of-Service logbook, Reactor Operator Narrative log and appropriate supervision informed. The health and safety of the public were not affected by this event.
2502005002 | Turkey Point 3 | 02/09/2005 | 04/11/2005 | ML05109024 | <strong>Missed As-found Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2005 the inlet and outlet fittings of containment isolation valve CV-3-956D were tightened. CV-3-956D is located outside containment. The inlet fitting adjustment altered the leak tightness of the containment boundary. An as-found local leak rate test (LLRT) was not performed prior to fitting adjustment. This is a missed surveillance test required by Technical Specification 4.6.1.2 that could not be subsequently performed. The apparent cause of the missed as-found LLRT is a failure, during work planning, to recognize LLRT requirements when disturbing a containment boundary. Corrective actions included: 1) The condition report addressing the missed as-found LLRT was provided to and discussed with work planners. 2) Planning supervisors and lead planners were coached on quality review of work orders. 3) To enhance error prevention barrier protection Desktop Instruction DTI-701 and Procedure 0-ADM-701, Control of Plant Work Activities,will be revised to include specific action steps when encountering work involving the adjustment or repair of a containment penetration. 4) CV-3-956D periodic LLRT has been reset to the refueling cycle interval of approximately 18 months. Based on the previous as-left LLRT, the post-adjustment LLRT, no maintenance activity on the penetration since 10/26/04 and the remote possibility of excessive wear due to valve operation, there is reasonable assurance that penetration leakage was within allowable limits prior to the fitting adjustment.The health and safety of the general public were not impacted by this event.
2502005003 | Turkey Point 3 | 04/28/2003 | 06/02/2005 | ML05164033 | <strong>Missed As-Found Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2003, during troubleshooting activities, a gap was found between the valve bonnet and actuator frame on letdown isolation valve CV-3-200B. The cap screws that secure the actuator to the bonnet were tightened, closing up the gap. CV-3-200B is a containment isolation valve and the gap adjustment potentially altered the leak tightness of the containment boundary. An as-found local leak rate test (LLRT) was not performed prior to the actuator to bonnet gap adjustment. This is a missed surveillance test required by Technical Specification 4.6.1.2 that could not be subsequently performed. The apparent cause of the missed as-found LLRT is a failure to adequately communicate the intent of the work instructions among personnel involved in the review of the instructions and performance of the troubleshooting activity. Corrective actions included instructing personnel involved on the value of clear communications with all parties, revising Planners Desktop Instruction DTI-701 to provide guidance for preparing work instructions for visual inspections and resetting the periodic as-found LLRT interval for CV-3-200A, B and C (penetration 14) to at least once per 30 months. Based on the previous as-left LLRT performed during a refueling outage in March 2003 and an analysis of letdown isolation valve performance since the outage, there is reasonable assurance that penetration leakage was within allowable limits prior to the gap adjustment on CV-3-200B. The health and safety of the general public were not impacted by this event.
2502005004 | Turkey Point 3, Turkey Point 4 | 05/28/2005 | 08/12/2005 | ML05236029 | <strong>Fasting Acting Control Fuses Can Cause Inoperable Emergency Containment Filters During Degraded Voltage Conditions</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2005, the Unit 3 3A Emergency Containment Filter (ECF) fan failed to start during a scheduled surveillance test due to a blown control circuit fuse. A replacement fuse of the same type and size also blew during a subsequent start of the 3A ECF fan. It was determined that the fuse type was marginal for the application and that similar fuses were installed on two additional ECF units, 3B ECF on Unit 3 and 4C ECF on Unit 4. Three ECFs are provided in each reactor containment building to remove radioactive iodine so that offsite radiation dose is maintained within regulatory guideline values during a maximum hypothetical accident (MHA). There was a potential for two of three Unit 3 ECFs not starting if needed to mitigate an MHA with concurrent degraded voltage conditions. Using best estimate methods, analysis showed a minimal increase in offsite thyroid dose while control room thyroid dose remained within regulatory guideline values. The apparent cause for ECF 3A starter control circuit fuse opening is insufficient margin in the fuse design to ensure that the ECFs will start reliably given variations in voltage, fuse tolerances and/or starter coil inrush currents. ATM-3 and KTK-3 fuses were replaced with time delay fuses in ECF 3A, 3B and 4C motor starter circuits. Since no actual event occurred which relied on the ECFs to perform their safety function and since potential consequences increased but did not exceed regulatory limits, the health and safety of the public and plant personnel were not affected by the ECF marginal fuse application.
2502005005 | Turkey Point 3 | 10/15/2005 | 12/13/2005 | ML05349012 | <strong>Manual Reactor Trip due to Decrease in the 3C Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>At 0702 hours on October 15, 2005, the Turkey Point Unit 3 Reactor was manually tripped from 99.9 % power due to a decrease in the 3C Steam Generator (SG) level. The loss of SG level control was due to feedwater [SJ] control system malfunctions. At approximately 0701 hours, the 3C SG level started to decrease. The main feedwater flow control valve, FCV-3-498, [SJ:FCV] would not modulate open even in manual control. Subsequent to the trip, Operations closed the Main Steam Isolation Valves (MSIVs) in response to observing that one of the four steam to reheat isolation valves did not close. Closure of the MSIVs [SB:ISV] resulted in loss of the normal heat removal path. The root cause of losing control of FCV-3-498 was found to be insufficient work instructions that allowed the valve clip in the positioner to be installed with some looseness. Corrective actions include the replacement of the valve positioner for FCV-3-498, and revision to the inspection instructions to include explicit installation details. This event had no adverse effect on the operating crew's ability to safely shutdown the reactor. Therefore, this event did not adversely affect the health and safety of the public.
2502005006 | Turkey Point 3, Turkey Point 4 | 12/21/2005 | 07/12/2006 | ML06201014 | <strong>Incorrect Installation of the Inboard Journal Bearing in Auxiliary Feedwater Pump B</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2005, at about 12:30 EST with Unit 3 operating in Mode 1 at 100 percent power and Unit 4 shut down, a routine surveillance test of the "B" Auxiliary Feedwater (AFW) Pump was performed. Technical Specification 3.7.1.2 had been entered. The test was stopped due to elevated vibrations and temperature at the pump inboard journal bearing. On November 8, 2005, the "B" AFW pump was disassembled for inspection. It was found that the inboard journal bearing was installed 90 degrees from its required orientation. The maintenance history revealed that the bearing was incorrectly installed at the vendor's facility during the last pump overhaul in late August 2003. Action was taken to align the "C" AFW pump to AFW Train 2, thereby restoring the operability of two trains. An interim "past operability" assessment on December 21, 2005 reported that the pump may not have been able to fulfill its safety function mission run time. It is estimated that the "B" AFW pump would not have performed its mission run time, and was therefore inoperable from December 14, 2004 to November 11, 2005 in violation of Technical Specification 3.7.1.2. Corrective actions included replacement of the "B" AFW pump bearing verification that the other AFW pump bearings were not affected, and vendor procedure revision and training. There was no adverse impact on the health and safety of the public due to this event.
2512005001 | Turkey Point 4 | 03/22/2005 | 05/20/2005 | ML05144031 | <strong>Steam Generator Feedwater Pump Trip Leading to Manual Reactor Trip and Auxiliary Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2005, at 0346 hours the 4A Steam Generator Feed Pump (SGFP) tripped on over-current due to a fault within the pump motor. As a result, a turbine runback from 100% power to 78% power occurred and Steam Generator levels decreased to 15%. At that time, the reactor was manually tripped in accordance with station procedures. The operating crew verified the reactor and turbine were tripped, and that emergency power to the 4 KV buses and safety injection were not required. The plant was verified to be stable prior to transitioning from power operation to hot standby. All control rods inserted as expected. Auxiliary Feedwater automatically actuated as expected when Steam Generator narrow range levels decreased below 10%. Plant systems functioned as designed to remove heat and safely shut down the reactor. The health and safety of the public were not affected by this event.
2512005002 | Turkey Point 4 | 06/27/2005 | 12/21/2005 | ML06004023 | <strong>Revised Automatic Reactor Trip due to Turkey Point Unit 4 Main Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2005, at 0316, Turkey Point Unit 4 reactor was automatically tripped from 100% power following a turbine trip due to a Main Generator lock out generated from an electrical fault of the Unit 4 Main Transformer. The transformer was recently installed during the refueling outage in Spring 2005. The fault ruptured the transformer tank releasing oil and caused a fire that damaged the transformer and adjacent equipment. At 0327, an Unusual Event was declared based on the fire in the plant protected area lasting longer than 10 minutes. The site fire brigade responded and extinguished the fire. Offsite fire fighting assistance was requested, but was not used to extinguish the fire. The fire was extinguished and the Unusual Event was terminated at 0500. All plant systems functioned as designed during and after the event. The operating crew controlled and stabilized the plant, and therefore the health and safety of the public was not adversely impacted by this event. The root cause for the Turkey Point Unit 4 Main Transformer failure was a failed manufacturing process employed by the vendor's supplier of the clamping ring. Corrective actions included replacement of the Main Transformer and repair/replacement of components damaged by the resultant fire.
2512005003 | Turkey Point 4 | 06/03/2005 | 08/26/2005 | ML05251045 | <strong>Incorrectly Wired P-10 Relay Renders One of Two Inputs to P-7 Interlock Inoperable for a Single Train of At-Power Reactor Trips</strong><br /><i>Abstract:&nbsp;</i>During under-voltage time delay relay testing on June 3, 2005, an expected change of state was not detected on certain relays associated with the B train of the reactor trip system (RTS). Investigation found the wires on relay P-10-2-B that provide one of two inputs to the P-7 relays were wired to a normally closed contact rather than a normally open contact. The incorrect wiring prevented the P-10 permissive from enabling certain reactor trips when reactor power reached 10% based on nuclear instrumentation. However, the redundant turbine first stage pressure logic enabled the trips as designed at approximately the same time. The cause was a latent human error in verifying the final configuration of the relay wiring, while the post maintenance test did not appropriately challenge the work performed. Corrective action included: 1) B RTS P-10-2 relay properly wired and post maintenance test (PMT) was satisfactory, 2) all NBFD-65NR reactor protection relays used as replacements with the potential to have a similar condition with transposed contact wiring have been verified, 3) procedure 0-ADM-737, Post Maintenance Testing, will be revised to further institutionalize the requirement that all contacts are tested when relay maintenance is performed. Since reactor protection features were not affected by the incorrect wiring of the P-10-2-B relay, the health and safety of the public and plant personnel were not affected.
2512005004 | Turkey Point 4 | 07/20/2005 | 09/19/2005 | ML05278003 | <strong>Foreign Material Causes Inoperability of One Emergency Containment Cooler</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2005, Unit 4 4C Emergency Containment Cooler (ECC) fan failed to start during a scheduled monthly surveillance test. The 4C ECC fan tripped due to thermal overload during two start attempts. Inspection during a subsequent containment entry revealed a rubber shoe cover with evidence of having been lodged between the fan stationary vanes and rotating blades. The rubber shoe cover was removed and further inspection and test operation showed no resulting damage. Three ECCs are provided in each reactor containment building to remove decay heat during a maximum hypothetical accident. The most likely cause of the rubber shoe cover entering the 4C ECC outlet ductwork is human error during the recent refueling outage which concluded on June 13, 2005. It is postulated that an individual failed to pay adequate attention when ascending or descending erected scaffolding above the 4C ECC and to report the loss of the rubber shoe cover. The containment closeout inspection procedure will be revised to require inspection inside such components as the ECCs that have outlet areas with a potential for foreign material intrusion. In addition, enhancements to procedure 0-ADM-730, Foreign Material Exclusion Controls, will be evaluated. Since no actual event occurred which relied on the ECCs to perform their safety function and the remaining two ECCs were operable, the health and safety of the public and plant personnel were not affected.
2512005005 | Turkey Point 4 | 10/31/2005 | 12/22/2005 | ML06006003 | <strong>Loss of Offsite Power Causes Engineered Safety Feature Actuations</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2005 at approximately 2227 hours, Unit 4 was in Mode 3 hot standby when the 240 kV switchyard protective relays actuated causing a loss of offsite power (LOOP) to the Unit 4 startup transformer. Unit 3 was in Mode 1 at about 60% power at the time and was unaffected by the LOOP to Unit 4. As expected, the Auxiliary Feedwater System actuated, steam generator blowdown isolated and the emergency diesel generators started and loaded their respective electrical buses (4A and 4B). The 4C bus remained energized during the event. Natural circulation was established and decay heat removal was via atmospheric steam dump valves. The cause of this event is a failure to identify the extent of salt contamination due to hurricane Wilma on the 240 kV switchyard line insulators that resulted in untimely maintenance. The insulators were cleaned and the startup transformer was returned to service. Long term corrective actions include: 1) the line insulators will be incorporated into the System Performance Monitoring Program, 2) the switchyard insulators will be replaced with resistive glazed insulators with priority given to replacing the insulators associated with nuclear startup transformers, 3) a second remote contamination monitor (RCM) will be installed in the PTN switchyard, and 4) grid operations procedures will be revised to verify functionality of the RCM5 and to perform swipe checks on the test insulator if an RCM is found defective or there is any other indication of abnormality. As all systems required to respond to the LOOP actuated as designed, the health and safety of the public and plant personnel were not affected.
2512005006 | Turkey Point 4 | 11/11/2005 | 01/10/2006 | ML06019047 | <strong>Manual Reactor Trip due to Rod Control Urgent Failure Alarm</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2005 at approximately 1413 hours, Unit 4 was in Mode 3 hot standby, performing a normal reactor startup evolution, with Shutdown Bank A fully withdrawn and attempting to withdraw Shutdown Bank B, when a Rod Control Urgent Failure Alarm was actuated due to failure of the 2BD rod control power cabinet. After gathering data and indications for troubleshooting, a manual reactor trip was initiated on November 11, 2005 at approximately 1502 hours to determine the cause of the failure and effect the repairs. All rods fully inserted and the unit remained in Mode 3. There were no other required or actual Engineered Safety Features System actuations. The root cause was identified as failure of a C.P. Claire Mercury wetted multiplexing relay MXR2 in Power Cabinet 2BD. The relay was replaced and the system was returned to operable status. This event had no adverse effect on the operating crew's ability to safely shutdown the reactor; therefore, the health and safety of the public were not affected.
2512005007 | Turkey Point 4 | 11/29/2005 | 01/27/2006 | ML06041010 | <strong>Foreign Material Exclusion Cover Causes Inoperability of One Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>At approximately 1315 hours on November 29, 2005, during a walkdown of painting activity in the 4A emergency diesel generator (EDG) air receiver room, the system engineer identified an intake air flow restriction caused by the installation of a floor covering installed for the purpose of foreign material exclusion. At approximately 1330 hours, the covering was removed to provide an adequate opening. Subsequent investigation revealed that the floor covering was installed at about 0800 hours on November 29, 2005. With the air intake path completely blocked, operability of the 4A EDG could not be assured for a period of about 5.5 hours and the 4A EDG was considered inoperable during that time. While the allowed outage time in Technical Specifications (TS) was not exceeded, compensatory measures prescribed in required actions were not completed within required time limits, which is reportable. The event is attributed to inadequate guidance to station personnel performing the work. There were no procedural precautions or physical identification measures (signs in the room) to prevent this event. As interim corrective action, a highly visible notice was painted on the floor next to the grating in the air receiver rooms for the 4A and 4B EDGs stating that Engineering is to be contacted before covering the floor. Further evaluation will determine if additional work management controls are needed to reduce the probability of a similar event occurring in the future. As the level of standby onsite power was within TS required limits, as determined retrospectively, there was no increase in the plant risk profile and the health and safety of the public and plant personnel were not affected.
2542005001 | Quad Cities 1, Quad Cities 2 | 02/03/2005 | 04/01/2005 | ML05103018 | <strong>4160 Volt Relaying and Metering Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2005, at 1819 hours (CST), with Unit 1 at approximately 85 percent power and Unit 2 at approximately 85 percent power, Quad Cities Engineering personnel confirmed that a single failure vulnerability existed on 4160 Volt Relaying and Metering transformers on both units. The single failure vulnerability defeated the independence of the offsite alternating power supplies. If this failure occurred during a Loss of Coolant Accident, the Residual Heat Removal Service Water system pumps may not have been able to be start within the required ten minutes. The single failure vulnerability was removed on February 4, 2005, at 0152 hours, and the affected plant equipment was declared operable.The root cause of this event was determined to be an existing latent design deficiency. The corrective action to prevent reoccurrence is currently in place in the Configuration Change procedures used to install new designs at Quad Cities Nuclear Power Station.
2542005002 | Quad Cities 1, Quad Cities 2 | 03/27/2005 | 12/08/2005 | ML05363028 | <strong>Trip of Unit 1 Division I 4kV Emergency Bus Feed to 480 VAC Emergency Buses in Both Divisions due to Ineffective Previous Corrective Actions</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2005, at 1930 hours, with Unit 1 in Refueling Mode, the main feed breaker between the Unit 1 Division I 4kV Emergency Bus and the Unit 1 Division I 480 VAC Emergency Bus tripped. Because the 480 VAC Emergency Buses were cross-tied, power was lost to both divisions of 480 VAC emergency power. The effects of the trip included degradation of the systems used for Alternate Decay Heat Removal (ADHR) and loss of power to the Control Room Emergency Ventilation System (which applies to both units). Fuel moves were halted and power was provided to the 480 VAC Emergency Buses from the Unit 1 Division II 4kV Emergency Bus. The root cause of the trip of the feed breaker to the Division I 480 VAC Emergency Bus was ineffective corrective action for two prior similar events in 1984 and 1987. Corrective actions include revision to the procedure for cross-tying the 480 VAC emergency buses to provide more restrictive operational precautions and better guidance concerning increased monitoring of bus current when the 480 VAC emergency buses are cross-tied.
2542005003 | Quad Cities 1 | 04/05/2005 | 06/06/2005 | ML05165028 | <strong>Three Main Steam Safety Valves Outside of Technical Specification Allowed Tolerance</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2005, at 1515 hours, Quad Cities Nuclear Power Station was notified that three of the four Main Steam Safety Valves (MSSVs) removed from Unit 1 earlier during the Spring 2005 refuel outage (Q1R18, March 21 to April 19, 2005) had been found during as-found testing to have lift set pressures outside of the +/-1% Technical Specification (TS) allowed tolerance. All four of the removed valves were replaced during Q1R18 with newly refurbished MSSVs that were certified to be within the +/-1% TS tolerance. The safety significance of this event was minimal. All of the four removed MSSVs were found to have a lift set pressure below the TS nominal value. Also, all three of the MSSVs that had lift set pressures that were outside the +/-1% TS tolerance had lift set pressures inside the +/-3% Code tolerance. The cycle specific fuels and transient analyses were performed assuming a +/-3% tolerance. Therefore, the valves were capable of performing their safety function.
2542005004 | Quad Cities 1, Quad Cities 2 | 04/29/2005 | 06/28/2005 | ML05187030 | <strong>Off-Site Power Inoperable due to Low Predicted Switchyard Voltage</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2005, at 0732 hours, with both units at approximately 85% power in Run mode, Quad Cities Nuclear Power Station was notified by the Exelon Energy Delivery (EED) Load Dispatcher that the predicted switchyard voltage following a unit scram coincident with a loss of coolant accident (LOCA) would be too low to ensure that the emergency electrical buses would not trip due to degraded voltage. The station declared both sources of off-site power inoperable for both units, entered the appropriate Technical Specifications, and made an Emergency Notification System (ENS) call for a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident. At 0836 hours, the station was notified by the EED Load Dispatcher that the predicted switchyard voltage was high enough to ensure that the emergency electrical buses would not trip due to degraded voltage following a unit scram coincident with a loss of coolant accident (LOCA). The safety significance of this event was minimal. The Emergency Diesel Generators and Station Blackout Diesel Generators were all fully operable. Design changes will be implemented to replace the Reserve Auxiliary Transformers with automatic load tap changing transformers.
2542005005 | Quad Cities 1 | 06/17/2005 | 08/16/2005 | ML05235057 | <strong>Automatic Reactor Scram from High Reactor Pressure due to a Malfunction of the Electro-Hydraulic Control System</strong><br /><i>Abstract:&nbsp;</i>At 1120 hours (CDT) on June 17, 2005, the Unit 1 reactor automatically scrammed from 85% power due to a valid high reactor pressure signal. The maximum reactor pressure was approximately 1044 psig during the event. All control rods inserted to their full-in position. The reactor pressure increase was caused by a malfunction in the Electro-Hydraulic Control (EHC) system, which resulted in closure of the main turbine control valves. The main turbine bypass valves (nine) opened as expected in response to the pressure increase. No reactor pressure vessel safety or relief valves were required to actuate during the event. Reactor water level decreased to approximately -20 inches, which resulted in automatic Group 2 and 3 isolations as expected. All systems responded properly to the event. The cause of the scram was a failure in one of the Control Valve Input Circuit Cards in the EHC system. Laboratory analysis was unable to identify the specific cause of failure. The circuit cards were replaced.
2542005006 | Quad Cities 1, Quad Cities 2 | 11/30/2005 | 01/27/2006 | ML06038053 | <strong>Failure of the Control Room Emergency Ventilation Air Conditioning Compressor due to a Manufacturing Defect in an Electrical Relay</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2005, at 1500 hours, the "B" Control Room Emergency Ventilation (CREV) Air Conditioning system was declared inoperable due to the failure of the air conditioning compressor. An electrical relay designed to stop the air conditioning compressor on low suction pressure, which is a normal part of the cycling of the air conditioning system in response to the Control Room thermostat, failed in the energized position. The continued operation of the compressor caused the refrigerant system to become sub-cooled. The sub-cooled refrigerant became liquefied and eventually damaged the compressor's shaft seals, allowing lubricating oil to leak out. The loss of lubricating oil damaged the rotating portions of the compressor. The compressor and relay were replaced, the CREV air conditioning system was tested, and the system was declared operable at 0242 hours on December 5, 2005. The CREV system is a single train system. Therefore, this is being reported as a condition that could have prevented a safety function. The electrical relay failure was caused by a manufacturing deficiency (bound armature retaining pin) specific to this relay.
2552005001 | Palisades | 01/09/2005 | 03/03/2005 | ML05074013 | <strong>Reactor Protection System and Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2005, at 1117 hours, with the plant operating at approximately 100% power, a rapid plant down power was commenced following an unexpected lowering of condenser vacuum. At 1127 hours, the reactor was manually tripped from 75% power. Following the reactor trip, the auxiliary feedwater system started automatically to maintain steam generator water level. The plant was stabilized in Mode 3 to investigate and repair the cause of the low condenser vacuum. All safety systems functioned as expected during the plant trip. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the reactor protection system and automatic actuation of the auxiliary feedwater system.
2552005002 | Palisades | 02/17/2005 | 09/27/2005 | ML05277054 | <strong>Emergency Diesel Generator 1-2 Excessively Loaded In Certain Postulated Post-Accident Scenarios</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2005, with the plant operating at approximately 100% power, a latent design inadequacy was discovered which affects the emergency diesel generator (EDG) 1-2 load analysis. For certain postulated post-accident scenarios, it was determined that the pressurizer heaters that are powered from 2400V safety bus 1-D, may automatically re-energize after initially being shed. As a result of the additional load, EDG 1-2 would become overloaded, and could trip on over-current. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications, and 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The condition was caused by a circuit modification that was implemented in 1986. The modification removed an original plant design feature that blocked automatic restoration of pressurizer heaters with a safety injection signal (SIS) present. A temporary modification was subsequently completed to preclude the pressurizer heater supply breaker from automatically re-closing when pressurizer level recovers.
2552005003 | Palisades | 04/13/2005 | 05/24/2005 | ML05153030 | <strong>Positive Differential Pressure Not Maintained between Control Room Envelope and Adjacent Room</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2005, with the plant operating at approximately 100% power, a review of test data determined that, contrary to Technical Specification (TS) SR 3.7.10.4, a positive differential pressure of >/= 0.125 inches water gauge was not being maintained between the control room envelope (CRE) and the adjacent electrical equipment room (EER), when the control room ventilation system (CRV) was operating in emergency mode. Additionally, review of the surveillance procedure that is periodically performed to demonstrate compliance with the 18-month frequency of TS SR 3.7.10.4, revealed that the differential pressure between the CRE and the EER is not specifically measured. Consequently, for greater than the past three years, TS SR 3.7.10.4 has not been fully met with regard to demonstrating that the CRV can maintain a positive pressure of >/= 0.125 inches water gauge relative to the EER. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2552005004 | Palisades | 04/18/2005 | 06/07/2005 | ML05165035 | <strong>Fuel Handling Area Ventilation System Not Properly Aligned During Movement of Irradiated Fuel Assemblies</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2005, with the plant operating at approximately 100% power, it was determined that plant procedures do not ensure that the fuel handling area ventilation system is aligned in accordance with Technical Specification (TS) 3.7.12, during the specified applicability conditions. Subsequent evaluation of the previous three years identified two periods when TS 3.7.12 was not met. This occurred during core alterations and movement of irradiated fuel assemblies when irradiated fuel assemblies were present with < 30 days decay time. The two periods were each less than one week in duration and occurred in the Spring 2003, and Fall 2004, refueling outages. TS 3.7.12 was not met due to having more than the one specified exhaust fan in operation, aligned to the emergency filter bank, and also due to operating additional exhaust and supply fans in the fuel handling area ventilation system. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications.
2552005005 | Palisades | 09/01/2005 | 10/24/2005 | ML05305042 | <strong>Reactor Protection System and Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2005, at 1025 hours, with the plant operating at 100% power, the reactor was manually tripped due to a hydrogen leak associated with the main generator. The manual reactor trip was a precautionary measure to facilitate expeditious removal from service of the main generator to allow hydrogen to be isolated and purged from the main generator, and preclude the potential for formation of an explosive hydrogen/air mixture. Following the reactor trip, the auxiliary feedwater system started automatically to maintain steam generator water level. The plant was stabilized in Mode 3 to investigate and repair the cause of the hydrogen leak. The hydrogen leak was at a socket weld at a piping tee connection on the main generator's leak detection line. The socket weld was repaired by grinding out the weld area and re-welding the connection. The most probable causes are cyclic fatigue of the weld due to vibration of the line and a weld flaw. The safety significance of this event was minimal. All safety systems functioned as expected during the plant trip. This event does not involve a safety system functional failure. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the reactor protection system and automatic actuation of the auxiliary feedwater system.
2552005006 | Palisades | 10/09/2005 | 12/07/2005 | ML05343021 | <strong>Inoperable Containment due to Containment Air Cooler Through-Wall Flaws</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2005, a small service water leak (nominally 0.55 gallons per minute) was identified in containment air cooler VHX-4. Since VHX-4 cooling coil tubing is a part of the containment pressure boundary, an operability evaluation addressing containment leakage was performed which determined that containment leakage would not exceed allowable leakage (La). Subsequently, it was determined that procedural requirements were not followed with respect to the operability evaluation. The operability determination procedure requires that for discovery of pressure boundary leakage from a Class 1, 2 or 3 component, the affected component shall be declared inoperable. Since VHX-4 cooling coil tubing is a Class 3 pressure boundary, the containment should have been declared inoperable at the time of discovery. The period of time from discovery of the service water leak in VHX-4 to the subsequent repair would have resulted in the containment being inoperable for a longer time than allowed by Technical Specifications. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, and 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2552005007 | Palisades | 11/20/2005 | 01/19/2006 | ML06019054 | <strong>Inoperable Emergency Diesel Generator for a Time Longer than Permitted by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2005, during a monthly surveillance test of emergency diesel generator (EDG) 1-2, a fuel leak was observed from the fuel oil injection system at the discharge of the cylinder 5R fuel pump. Since the spraying fuel oil created a potential fire hazard, the EDG was shutdown and declared inoperable. Subsequent inspection determined that the leak occurred at the cylinder 5R snubber valve, which had cracked. Review of the cause of failure indicates that the snubber valve was unable to operate satisfactorily for the EDG's required mission time. Therefore, EDG 1-2 should be considered to have been inoperable since installation of this snubber valve. Consequently, EDG 1-2 was inoperable for a period of time longer than allowed by Palisades Technical Specifications. Additionally, during the period EDG 1-2 was inoperable, EDG 1-1 was made inoperable for performance of its monthly surveillance. Therefore, both EDGs were simultaneously inoperable for a period of time longer than allowed by Technical Specifications. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, and 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
2602005001 | Browns Ferry 2 | 01/20/2005 | 03/18/2005 | ML05080003 | <strong>Loss of High Pressure Coolant Injection (HPCI) Discharge Piping Keep-Fill</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2005, at 2353 hours central standard time, alarms were received in the Unit 2 control room indicating that the normal high pressure coolant injection (HPCI) suction source had reached a low level. As a consequence of this indicated condition, the systems suction automatically transferred from the condensate storage tank (CST) to the Unit 2 suppression pool. At the time this suction transfer occurred, the normally closed HPCI inboard discharge isolation valve had been placed in the open position and its power removed in support of work being performed on 250 VDC Unit Battery 2. With the system discharge piping in this configuration, and given the relative elevation between the suppression pool water level and the discharge piping, the suction head pressure available from the suppression pool source was not sufficient to ensure the piping was kept full. The existence of voids in the upper elevations of the discharge piping was probable. With voiding present in the discharge piping, HPCI is vulnerable to waterhammer damage should the system initiate, therefore the capability to inject to the reactor vessel via HPCI was considered to be lost as a consequence of this event. This event occurred because of a suction source transfer initiated by the spurious operation of a normal suction source level switch. The spurious operation occurred due to degraded wiring insulation in the vicinity of a CONAX seal. Corrective actions were to realign the system to the condensate storage tank (normal) suction and to replace the damaged wiring.
2602005002 | Browns Ferry 2 | 02/03/2005 | 04/12/2005 | ML05102051 | <strong>Primary Containment Isolation Valve Inoperable in Excess of Technical Specifications Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On 2/10/05, engineering personnel performed a local inspection of the reactor water clean-up systems outboard suction isolation valve This valve serves as a primary containment isolation valve (PCIV). The inspection revealed that the valves packing gland retainer was broken, the gland follower was no longer properly positioned on the valve body, and the valve stem exhibited galling. Following an evaluation by site engineering, the valve was declared inoperable. The inboard suction valve was closed at 1859 hours, and power was removed from its motor operator. This was done in accordance with Technical Specifications (TS) Limiting Condition for Operation 3.6.1.3 Action A.1 to isolate the affected flow path by at least one closed and deactivated valve when a PCIV is inoperable. Post-event review determined the valve had last been positioned to its as-found (open) condition at approximately 2121 hours CST on 2/2/05. The damage to the valve is thought to have occurred then. The valve would not have responded to a close command while in that condition and was therefore inoperable beginning at that time. The allowable TS action completion time of 4-hours expired at approximately 0121 hours on 2/3/05, and the continued operation of the system using this flow path between then and 1859 hours on 2/10/05 was in violation of the Unit 2 TS. The valve damage is thought to have occurred after the valve packing gland follower bolts loosened and allowed the follower to cock on the valve stem. The valve was repaired and tested, bolt torquing on similar valves will be verified, and preventive maintenance procedures on such bolt torquing will be evaluated.
2602005003 | Browns Ferry 2 | 04/13/2005 | 06/09/2005 | ML05161009 | <strong>Reactor Protection System Actuation from Scram Discharge Volume High Level While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2005, Unit 2 was in cold shutdown with surveillance testing being performed in support of returning the unit to power operations. At approximately 0954 hours, an unplanned actuation of one channel of the anticipated transient without scram/alternate rod insertion logic occurred. The actuation was caused by an interaction between a surveillance test being actively performed and another test which had been in conduct, but which was halted for troubleshooting an equipment issue. The plant equipment response to this logic actuation isolated and vented the control rod drive (CRD) scram air header, causing the scram inlet and outlet valves on each CRD hydraulic control unit (HCU) to open and the scram discharge volume (SDV) vent and drain valves to close. With the scram outlet valves open, per plant design a flow path exists from the reactor vessel, through the 185 individual control rod drives and the open scram outlet valve on each drives HCU, to the associated SDV (east or west), and each SDV began filling. Level switches on the associated scram discharge instrument volumes (SDIV) sensed the increasing water level, and at approximately 0955 hours, Unit 2 received a reactor scram from high water level in both the east and west SDIV's. All control rods were already fully inserted prior to the scram. There was no impact to plant operations as a result of the scram. The root cause of the event was inadequate communication between different plant testing groups. Corrective actions include re-emphasis to site personnel involved in testing of the necessity for clear, unambiguous communication.
2602005004 | Browns Ferry 2 | 04/16/2005 | 04/03/2006 | ML06093059 | <strong>Primary to Secondary Leakage in Residual Heat Removal Heat Exchanger in Excess of Analyzed Limits</strong><br /><i>Abstract:&nbsp;</i>On 3/21/05, with residual heat removal (RHR) system train 2A in service for shutdown cooling, a radiation alarm on the residual heat removal service water (RHRSW) side of the heat exchanger (HTX) was received. Sampling confirmed the presence of radioactivity. Immediate corrective actions were focused on evaluating the condition of the 2A HTX, and the potential impact of an RHR HTX leak on post-accident design basis assumptions and limitations was not initially recognized. On 4/17/05, after Unit 2 had exited the refueling outage and was in power ascension, indication of a leakage of contaminated water into the RHRSW system was again observed. Activities were undertaken to identify the specific source of the leak, which was localized to RHR HTX 2A. On 4/22/05, engineering evaluations concluded that relatively small leakage rates could result in unacceptable radioactive material release to the environment in post-accident situations if significant fuel damage was assumed to have occurred. The RHR 2A containment cooling functions of suppression pool cooling, suppression pool spray, and drywell spray were declared inoperable, and the appropriate Technical Specification Limiting Condition for Operation actions were invoked. Additionally, on 4/28/05, a manual isolation valve on the RHRSW inlet to the HTX was closed, rendering it unavailable for service. During the interval between reactor startup and closure of the manual valve, had an event occurred which involved significant fuel damage, this HTX could have been utilized for reactor or containment cooling, and its use could have resulted in an unanalyzed release of radioactive material to the environment. The root cause of this condition was raw water corrosion of soft iron gasket and gasket seating surfaces within the HTX. Corrective actions include revising relevant maintenance procedures, evaluating RHR HTX maintenance histories, estimating the rate of gasket material loss, and scheduling and performing preventive maintenance as appropriate.
2602005005 | Browns Ferry 2 | 09/02/2004 | 09/26/2005 | ML05269040 | <strong>Primary to Secondary Containment Leakage via the Residual Heat Removal System in Excess of Analyzed Limits</strong><br /><i>Abstract:&nbsp;</i>On 9/2/04 with the residual heat removal (RHR) system in suppression pool cooling service, the control room received high level annunciation on the Pressure Suppression Chamber (PSC) head tank. An apparent leakage flow path existed from the operating RHR system into this tank through two series check valves, which are part of the RHR system discharge piping keep-fill system. The primary containment isolation valve function of these leaking check valves was declared inoperable, and the required Technical Specifications actions were completed. It was apparent that both of the series keep-fill system check valves had stuck in the open position during stand-by service, such that they failed to check reverse system flow when the RHR system was started. Subsequent local leak rate testing (LLRT) was performed in an attempt to quantify the system leakage flow rate and to determine the as-found condition of the check valves. One of the two valves passed the as-found leak rate testing, while the second valve failed. It is believed that pressure pulsations involved with the starting and stopping of the RHR system were sufficient to free the internal movement of the valve which passed the post-event LLRT. With the check valves stuck in an open condition, had an actual event occurred which involved significant fuel damage, utilization of this loop of RHR could have resulted in a release of radioactive material to the secondary containment beyond that analyzed in the BFN design and licensing bases. The check valve sticking occurred due to internal corrosion on the guide pin and disc, exacerbated by past cleaning practices and the use of dissimilar metals in the design. The valve internals are being changed to all-stainless material.
2602005006 | Browns Ferry 2, Browns Ferry 3 | 07/22/2005 | 09/19/2005 | ML05263015 | <strong>Low Voltage on Shutdown Battery Cells Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 22, 2005, during performance of a quarterly surveillance of 4-kV Shutdown Board Battery A, the associated 250 VDC subsystem was declared inoperable due to low cell voltage for two battery cells not meeting Technical Specifications (TS) acceptance criteria. Concurrently, a second DC subsystem was inoperable in support of scheduled maintenance activities. The concurrent inoperability of two DC subsystems resulted in an unplanned entry of Unit 2 into TS Limiting Condition for Operation (LCO) 3.0.3 at 0220 hours CDT. Unit 2 commenced shutdown activities at 0316 in accordance with TS. At 0450, the DC subsystem that was inoperable for maintenance was returned to service. Unit 2 then exited TS LCO 3.0.3, shutdown activities were terminated, and the unit was returned to full power. The cause of the low voltage condition on the two Battery A cells was determined to be battery plate material shedding. This can cause micro shorts due to scale bridging between the positive and negative plates on individual cells, which lowers cell voltage. The condition is associated with battery aging and is fixed by replacing the affected cells or temporarily remedied by high level equalizing, single cell charging, or agitation. Although the condition results in lower measured voltages for individual cells, it does not appreciably affect the overall capacity of the battery. TVA plans to replace the entire battery by December 2005 after procurement of new cells. In the meanwhile, the battery has been placed on an accelerated surveillance schedule to monitor the condition of the battery. In accordance with 10 CFR 50 .73 (a)(2)(i)(B), this report is being made as a condition prohibited by TS.
2602005007 | Browns Ferry 2 | 08/05/2005 | 09/30/2005 | ML05278011 | <strong>Reactor Scram Due To Low Reactor Water Level Caused By Loss Of Feedwater Pumps.</strong><br /><i>Abstract:&nbsp;</i>At 1708 hours Central Daylight Time (CDT) on August 5, 2005, the Unit 2 Reactor automatically scrammed on low reactor water level from 100 percent power following a sequential loss of Reactor Feed Pumps (RFP) 2C and 2B. RFP 2C was lost when the RFP turbine main steam flow control valve (FCV) control linkage failed. RFP 2A and RFP 2B increased flow in an attempt to maintain reactor feedwater level, however; RFP 2B tripped when the thrust bearing wear detector trip actuated. Loss of RFP 2C and RFP 2B resulted in low reactor water level, an automatic runback and trip of the Reactor Recirculation System pumps, and a reactor water level automatic scram. When the reactor water level reached the low low water level, the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems auto initiated recovering reactor water level.The cause of the event was a low reactor water level resulting from the sequential loss of RFP 2Cand RFP 2B. First, the control valve linkage for RFP 2C came disconnected from the low pressure steam admission FCV actuator. The FCV failed closed and RFP 2C stopped. Second, RFP 2B turbine thrust bearing wear detector actuated and tripped the pump turbine. The investigation into the root cause of the main steam control valve linkage failure of for RFP 2C was inadequate installation of a locking device. The investigation into the root cause for RFP 2B turbine trip is ongoing. Oil samples do not indicate any thrust bearing wear and a calibration check of the turbine thrust bearing wear detector indicated satisfactory operation.
2602005008 | Browns Ferry 2 | 04/06/2005 | 02/15/2007 | ML07057028 | <strong>Main Steam Relief Valve Inoperability LCO Exceeded During Operating Cycles 11, 12, and 13 as a Result of Lift Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>Testing of main steam relief valves (MSRVs) removed from Unit 2 following operating cycles 11, 12, and 13 respectively, revealed that multiple valves mechanically actuated at pressures greater than 3% above their nominal setpoint. The Unit 2 Technical Specifications require that 12 MSRVs be operable in reactor Mode 1 (power operation), Mode 2 (startup), and Mode 3 (hot shutdown). If less than 12 MSRVs are operable, the unit is to be placed into Mode 3 within 12 hours and Mode 4 (cold shutdown) within 36 hours. Since each BFN unit has 13 installed MSRVs, any concurrent MSRV inoperability would require the above actions to occur. The condition is deemed to have developed and existed while the valves were in service. The exact interval during which these MSRVs operated with lift setpoints beyond the TS allowable values is unknown, but it is probable that the allowed time frame was exceeded. Similar MSRV performance prior to calendar year 2001 was reported by TVA to NRC via LER. However, TVA did not report the failure to meet TS following the Unit 2 Cycles 11, 12, and 13 in 2001, 2003 and 2005. The failure to report the occurrences have been addressed by the TVA Corrective Action Program. This LER, 260/2005-008, addresses the past conditions (i.e., 2001, 2003, and 2005) which had not been previously reported. The root cause of this condition was MSRV pilot valve disc-seat corrosion bonding which can develop during normal reactor operations. The affected valves were refurbished and their lift-setpoints re-established prior to their re-installation in the plant. There was no actual safety consequences associated with this condition.
2632005001 | Monticello | 02/04/2005 | 06/06/2005 | ML05157047 | <strong>Single Failure Identified that Could Prevent Energizing Buses 15 and 16</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2005, with the plant operating at 98% power, NMC staff reviewed a recent event at Crystal River (NRC Event #41362) concerning a single failure vulnerability between essential buses. NMC staff determined the single point vulnerability was applicable between the 4.16 kV vital bus circuit breakers 152-610 and 152-511 for the Monticello Nuclear Generating Plant (MNGP). MNGPs single point vulnerability issue was reported on February 4, 2005. The apparent cause of the single point vulnerability issue was a failure to recognize an original plant construction design, which was noncompliant to 10CFR50 Appendix A "General Design Criteria." Further evaluation of the issue revealed previously undiscovered 10CFR50 Appendix R non-compliance implications. This Appendix R non-compliance was reported on February 23, 2005, and both issues were documented under LER 2005-001 Revision 0 on April 4, 2005. The apparent cause of the Appendix R vulnerability is a failure to implement original Alternate Shutdown System (ASDS) design recommended by General Electric Safe Shutdown Analysis reports. NMC performed a comprehensive review of the ASDS isolation adequacy as part of the extent of condition review. On April 5, 2005 as a result of this review, NMC identified an additional related issue. Station personnel discovered that the Bus 16 source to Load Center #104 had a similar potential vulnerability with the ASDS isolation design that could result in Load Center #104 being locked out in the event of a Control Room or Cable Spreading Room fire. This extent of condition issue was reported on April 5, 2005 to the NRC in Event notification #41567. A contributing cause of the Appendix R vulnerabilities was a failure to recognize Appendix R circuit design noncompliances during the initial implementation of the Appendix R rule by MNGP staff. Plant modifications have been completed to remove the 10CFR50 Appendix R vulnerabilities.
2632005002 | Monticello | 02/24/2005 | 04/25/2005 | ML05115033 | <strong>Failure of #11 Reactor Protection System Motor-Generator Set Results in an Engineered Safety Feature Actuation</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2005 with the unit operating at 90 percent power, operators were notified of smoke and a flash of light in the vicinity of the #11 Reactor Protection System (RPS) Motor-Generator (MG). Operators were dispatched to the area and found the RPS MG set tripped. With the loss of the MG set, the following occurred: a partial Group II isolation, isolation of secondary containment, and the autostart of the "A" Standby Gas Treatment system. Based on the Engineered Safety Feature actuations, an event notification (ENS # 41441) was made to the NRC on February 24, 2005 at 2139. The cause of the event was a phase to ground short which is believed to be due to age related degradation of the motor winding insulation material. Corrective actions planned or taken for the event are: rewinding of the motor and performance of an evaluation for the frequency for re-winding or replacement of various motors on the plant critical equipment list.
2632005003 | Monticello | 03/08/2005 | 05/09/2005 | ML05129043 | <strong>Loss of Shutdown Cooling due to #12 Residual Heat Removal Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2005 the Monticello Nuclear Generating plant was shutdown in a refueling outage. The reactor head was removed and the reactor was flooded up to the flange with the main steam-line plugs installed. At 0454, the station was in the process of performing an equipment isolation to support replacement of the Safety Relief Valve solenoids. While performing the isolation several unexpected alarms annunciated in the Control Room. Operations Shift Supervision decided to remove the isolation and re-evaluate the tagged components. When the isolation was removed the #12 RHR pump sensed a loss of suction flow path. The sensed loss of suction flow path caused the pump to trip and resulted in the loss of the in-service Shutdown Cooling train. Based on the loss of shutdown cooling, an NRC Event Notification Report (#41468) was made on March 8, 2005 at 1041 under 10 CFR Part 72(b)(3)(v)(B) "Event or Condition that could have Prevented Fulfillment of a Safety Function." The Root Cause was determined to be failure of Operations Management and Station Management to effectively oversee implementation of the outage isolation process.
2632005004 | Monticello | 03/09/2005 | 05/12/2005 | ML05132020 | <strong>Voluntary LER for Control Rod Drive Insert Line Leakage</strong><br /><i>Abstract:&nbsp;</i>A voluntary License Event Report is being provided for the following event: On March 5, 2005 with the Monticello Nuclear Generating plant in a refueling outage, during a scheduled under-vessel walk down, a small water leak was noted on a control rod drive flange. On March 9, Nuclear Management Company (NMC) determined that the leakage was from the top surface of the flange adjacent to the Control Rod Drive (CRD) insert line. The leakage was determined to be active and the result of a flaw in the insert line to CRD flange weld. Metallurgical examination determined that the leak initiated at a small weld void in the weld between the insert line and the CRD housing flange created during original construction. Corrective action taken included performance of a metallurgical, chemical and visual examination of the leaking section of the CRD insert line, replacement of a section of the insert line to re-make the weld at the CRD flange, and a 100 percent visual inspection of the other control rod drive flanges for leakage.
2632005005 | Monticello | 04/02/2005 | 06/01/2005 | ML05152036 | <strong>Inadvertent Engineered Safety Function Actuations During Testing</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2005 at 1648, Operations was performing a Post Maintenance Test (PMT) in accordance with a procedure, following replacement of a relay. During the performance of the procedure, the #16 4KV Safety Related Bus was de-energized. Operations entered the appropriate procedures for the loss of Bus 16, and power was restored at 2140. A review of the event determined that the PMT procedure did not contain the correct steps to permit the test to be successfully completed. This resulted in a knife switch being left in the open position that caused a relay to sense a loss of bus voltage, even though the voltage was actually available. This caused the bus transfer logic to seek a new source of power that resulted in Bus 16 de-energizing. The Root Cause Evaluation determined that the procedures for preparation, review and approval of complex PMTs lack sufficient detail with respect to responsibilities and actions required. Corrective actions planned or completed include: restoration of the bus, and planned revision of station procedures regarding the development and review process for PMTs.
2632005006 | Monticello | 10/18/2005 | 12/19/2005 | ML05355019 | <strong>Unrecognized Plant Configuration Change</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2005, during a review of a planned Emergency Filtration Train (EFT) maintenance work order, a shift manager recognized that the isolation used for this activity affected the Emergency Core Cooling Systems (ECCS) due to impacts on the associated Emergency Service Water (ESW) pump start logic. This maintenance work had already been approved for implementation; however, the compensatory measures planned for the EFT maintenance were determined to be inadequate and the work was put on hold prior to implementation. On October 18, 2005 during the extent of condition review for the issue, it was determined that a similar condition had previously existed. The impact on ECCS during the previous isolation was not recognized or evaluated in advance and resulted in a plant configuration control error. The root cause evaluation for the event determined that management and supervision did not provide the necessary direction and oversight of isolation activities to ensure expectations were clear, appropriate resources were applied, and roles and responsibilities in the isolation preparation/approval, work order impact, and work order approval processes were clear.
2652005001 | Quad Cities 2 | 05/25/2005 | 10/21/2005 | ML05103018 | <strong>Core Spray Discharge Pressure Switch Out of Calibration Due to Apparent Manufacturing Defect</strong><br /><i>Abstract:&nbsp;</i>At 0040 hours (CDT) on May 25, 2005, during calibration of a discharge pressure switch on the Unit 2 Core Spray System, the pressure switch was found to be outside the Technical Specification (TS) allowed range. The switch was recalibrated to within the TS allowed range. At 1640 hours on May 26, 2005, after review by Engineering, the pressure switch was declared inoperable due to inconsistent operation and TS 3.3.5.1, Condition G, allowing operation with the inoperable switch for eight days, was entered. The switch was removed, a replacement switch was installed and calibrated, the pressure switch was declared operable and the TS condition was exited at 0900 hours on May 27, 2005. This switch provides a permissive signal to the Auto Blowdown System indicating that the Core Spray pump is operating. The inconsistent operation of the pressure switch was caused by a manufacturing defect such that the switch actuating arm was able to pivot between its stop tabs due to the bend angle of the arm. The safety significance of this event was minimal. The other three switches on Unit 2 were operable and would have provided the permissive.
2652005002 | Quad Cities 2, Quad Cities 1 | 12/30/2005 | 07/27/2007 | ML05363028 | <strong>Main Steam Relief Valve Actuator Degradation due to Failure to Correct Vibration Levels Exceeding Equipment Design Capacities</strong><br /><i>Abstract:&nbsp;</i>Between December 30, 2005, and January 19, 2006, each unit at Quad Cities Nuclear Power Station was shut down twice to inspect and/or repair Main Steam Line (MSL) Electromatic Relief Valve (ERV) actuators. The actuator damage was caused by MSL vibration levels that exceeded the design capabilities of the components during operation at Extended Power Uprate (EPU) power levels. The root cause was failure to correct the source of the MSL vibrations identified soon after original startup of the plant. The safety significance of this issue was minimal. The eight MSL Safety Valves and the Target Rock Safety/Relief Valve were not affected by this issue, and remained operable throughout these events. Additionally, for the most limiting case two ERVs were available. Acoustic Side Branches have been installed on the main steam system for both Unit 1 and Unit 2. Subsequent testing has shown that overall MSL vibrations have been reduced to a level to support safe and reliable operation of the MSLs and attached components during future operating cycles at EPU.
2662005001 | Point Beach 1, Point Beach 2 | 06/08/2005 | 08/05/2005 | ML05228035 | <strong>UNANALYZED CONDITION DUE TO INADVERTANT OMISSION OF SAFE SHUTDOWN EQUIPMENT FROM FIRE ORGANIZATIONAL PLAN</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2005, NMC staff determined that Revision 8 of Point Beach Fire Organizational Plan (FOP) 1.2, omitted some safe shutdown equipment. Because of these omissions, FOP 1.2, Revision 8, was not aligned with the Safe Shutdown Analysis. As a result, some of the manual actions that would be necessary to accomplish safe shutdown were no longer identified. FOP 1.2 guides operators on plant operation for fires within safe shutdown areas. This guidance includes a list of safe shutdown equipment affected by a postulated fire and the manual actions that may be required to compensate for the fire damage. Investigation determined the omissions were introduced in FOP 1.2, Revision 6 (effective November 1, 2004). The missing procedural guidance may have resulted in the omission of safety significant operator actions (which are credited in the Safe Shutdown Analysis) had a fire occurred while FOP 1.2, Revision 6 was in effect. FOP 1.2, Revisions 7 and 8, also carried on the omission of some safety equipment. A temporary change corrected this condition on June 8, 2005 . FOP 1.2 Revision 9, was issued to correct this condition on June29, 2005. On July 18, 2005, NMC identified a similar issue with Revision 9 of FOP 1.2. FOP 1.2 Revision 10, was issued to correct this condition on July 22, 2005.
2662005002 | Point Beach 1, Point Beach 2 | 06/07/2005 | 08/08/2005 | ML05228035 | <strong>UNANALYZED CONDITION DUE TO DEFICIENCY IN APPENDIX R SAFE SHUTDOWN STRATEGY FOR CHARGING PUMP CAPABILITY</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2005, NMC staff identified a potential deficiency in the Point Beach Appendix R Safe Shutdown Strategy. A review of the physical routing of Unit 1 Charging Pump 2C (1 P-2C) control cables indicated that those control cables located within Fire Area A06 would be damaged and prevent remote operation from the control room following postulated fire damage to these control cables. Fire Organizational Plan (FOP) 1.2 was revised on April 15, 2005, to ensure adequate manual actions are in place to establish and maintain Unit 1charging pump capability and coolant pump seal cooling. On June 7, 2005, a continuing review determined that this condition affected available charging pump capability. The condition could have resulted in losing the availability of all but a single charging pump operating at slow speed, which would not provide sufficient seal cooling to the reactor coolant pump (RCP), thereby degrading the level of plant safety. On April 28, 2005, a similar issue was documented for the Unit 2 charging pumps. Specifically, neither FOP1.2, nor the safe shutdown Analysis Compliance Strategies provide adequate guidance for manual actions necessary to restart the charging pumps. This is necessary to ensure adequate RCP seal cooling is established or maintained. FOP 1.2 was revised on May 9, 2005, to ensure adequate manual actions are in place to establish and maintain Unit 2 charging pump capability and reactor coolant seal cooling.
2662005003 | Point Beach 1, Point Beach 2 | 07/15/2005 | 09/13/2005 | ML05263036 | <strong>Potentailly Inoperable Safety Injection Pumps</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2005, at 2245 CDT, NMC identified a potential condition that during a design basis accident with degraded safeguards bus voltage, the Unit 1 "A" safety injection (SI) pump motor could trip and lockout undercurrent prior to the associated safeguards bus stripping on undervoltage. The SI pump lockout could then prevent an auto start of the SI pump during emergency diesel generator load sequencing. Based on the results of this evaluation, the Unit 1 "A" SI pump was declared out of service. The Unit I "A" SI pump motor time overcurrent setpoint was subsequently adjusted to correct this condition and was returned to service on July 17 at 2230 CDT. The Unit 2 Train "A" SI pump motor time overcurrent setpoint was also reset as a conservative measure. On August 1, 2005, at 2000 CDT, an evaluation of motor design data and the time overcurrent setpoint for both units' Train "B" SI pump motors and the Unit 2 "A" SI pump motor identified a similar condition. Both units' Train "B" SI pumps were consequently declared out of service as a result of this new data. The Unit 2 "A" SI pump motor remained operable because its setpoint had been previously reset. This condition is being reported under 10 CFR 50 .73(a)(2)(v)(D) due to the potential to prevent fulfillment of a safety function to mitigate the consequences of an accident. The earlier corrective action for both units' "A" SI pump motors had been completed prior to discovery of the similar condition on the "B" train pumps; therefore, both units' "A" train pumps were operable and capable of fulfilling design safety function upon discovery of the second condition on August 1, 2005.
2662005004 | Point Beach 1, Point Beach 2 | 07/20/2005 | 09/16/2005 | ML05263028 | <strong>Auxiliary Feedwater Recirculation Capability in Local Operating Mode</strong><br /><i>Abstract:&nbsp;</i>While performing a test to validate proper operation of a local control station for auxiliary feedwater (AFW), a deficiency was discovered in Procedure AOP-10, "Control Room Inaccessibility", which could have potentially led to damage of a motor-driven AFW pump. AOP-10 provides direction for evacuation of the control room for reasons other than a fire as postulated in 10 CFR 50, Appendix R. One purpose of the procedure is to maintain the plant in safe shutdown condition by locally controlling the turbine-driven AFW pumps until control room accessibility is restored. In the event that supplemental AFW flow was required, AOP-10 directed the operator to place the motor-driven AFW pump in local control and start the pump. The sequence of procedure steps in AOP-10 did not account for the local control station circuitry isolating the control function of the AFW flow recirculation valve. This recirculation flowpath provides minimum required flow for cooling the motor-driven AFW pumps when discharge flow is below the recommended flow rate. Consequently, if a motor-driven AFW pump were to be started from the local control station, a flowpath would not exist until a discharge valve was opened. Once the procedure deficiency was identified, operators were briefed on the condition and the procedure was revised to correct it. This procedure deficiency did not result in any damage to the AFW pumps.
2662005005 | Point Beach 1, Point Beach 2 | 09/27/2005 | 11/18/2005 | ML05341017 | <strong>Postulated Faults with Electrical Current in Excess of Maximum Interrupt Ratings and Nonconservative Technical Specification for Degraded Voltage Time Delay Relay Settings</strong><br /><i>Abstract:&nbsp;</i>NMC has identified certain equipment in the PBNP electrical distribution system that would not ensure, under certain conditions, interruption of a three phase bolted fault short circuit. These postulated faults would have electrical current in excess of the maximum listed interrupting ratings for designated circuit breakers and associated bus bar bracing. This condition affects the 13.8 kV, 4.16 kV, and 480 V power panels, motor control centers (MCCs), and switchgear. The PBNP Appendix R analysis relies on breaker coordination and fault current interruption to prevent loss of safe shutdown equipment due to common enclosure/power supply associated circuit concerns. The postulated condition presents the possibility of a fire causing bolted faults that may ignite fires in one or more remote fire areas resulting in additional unanalyzed fire losses due to direct fire damage or uncleared faults on associated circuits. Consequently, this condition could result in a loss of safe shutdown equipment functionality beyond that previously postulated. Related to this condition is the identification of a nonconservative Technical Specification for degraded voltage time delay relay settings and their setting tolerance range in calibration procedures that could have resulted in certain safety system motors and switchgear tripping on overcurrent. Such an event could have prevented the fulfillment of the motors' safety function to mitigate the consequences of an accident. Under a design basis loss of coolant accident concurrent with a reduced voltage condition, safety related motors and switchgear may trip their protective devices on overcurrent without the degraded voltage relays being actuated. Affected equipment included certain safeguards 480 VAC switchgear, 480 VAC motor control centers, both auxiliary feedwater pump motors, and 1 component cooling water pump motor.
2662005006 | Point Beach 1, Point Beach 2 | 11/08/2005 | 01/09/2006 | ML06010003 | <strong>Calculation Errors in Model for ECCS Long Term Cooling</strong><br /><i>Abstract:&nbsp;</i>This report describes the discovery of errors in the calculations that were used as the basis for the licensee's response to NRC Generic Letter GL 98-04. Two significant errors were involved: 1. A correlation for head loss across a mixed fiber and particulate debris bed on a screen was improperly applied to a debris bed consisting only of coatings chips, and 2. While interpreting the resulting calculated head loss, the total submergence depth of the screens was used rather than the average submergence depth. This resulted in an erroneous conclusion that the available submergence would be sufficient to ensure adequate flow to the residual heat removal (RHR) pumps. Since the screens would be only partially submerged, air intrusion and loss RHR pumping function would have been the correct conclusion reached. Further investigation found that the flow path created by a partially blocked strainer had not been considered and that the increase in expected head loss created an additional challenge to RHR pump operability. These errors and deficiencies in modeling and interpretation of results impact the analytical basis for demonstrating compliance with the acceptance criteria in 10 CFR 50.46 (b)(5), "Long-term Cooling." This condition was reported to the NRC via the Emergency Notification System on November 8, 2005 (EN# 42129). An operability analysis of this condition demonstrated that adequate net positive suction head (NPSH) would be available to the emergency core cooling system (ECCS) pumps to ensure long-term cooling pending final resolution of generic PWR sump screen issues.
2662005007 | Point Beach 1, Point Beach 2 | 11/15/2005 | 01/16/2006 | ML06019050 | <strong>Control Rod Movement with Refueling Cavity Water Level below TS 3.9.6 Limit</strong><br /><i>Abstract:&nbsp;</i>This report describes the November 15, 2005, discovery that Unit 1 control rods had been moved without refueling cavity water level being at the minimum value specified in Technical Specification (TS) LCO 3.9.6, "Refueling Cavity Water Level". During performance of rod latching and unlatching in accordance with procedure RP-4A, "Full-Length Control Rod Drive Shaft Unlatching and Latching", operators had also performed control rod drag testing, which involves grasping a coupled rod with the rod latch tool and raising the control rod assembly approximately 10 feet while monitoring a load cell for weight changes. This procedure was performed with the cavity water level at rod latch height, which is less than the required 23 feet of water above the fuel assemblies per TS LCO 3.9.6. This activity was performed on October 21, 2005 and during previous refueling outages. Subsequent to this discovery, on November 16, 2005, operators identified that Unit 1 control rod F08 remained latched after completing of the procedure for unlatching. Difficulties had been experienced on the previous shift in moving the rod shaft with a special tool shortly after completing the initial unlatching procedure. Based on these difficulties, it appears that the rod may have relatched when the tool was set down on it. Although the condition could not be verified, the potential existed that the coupled rod may have been moved with the rod shaft, prior to discovery that it remained latched, while the cavity water level was less than the required 23 feet of water.
2662005008 | Point Beach 1 | 12/13/2005 | 02/13/2006 | ML06053051 | <strong>Manual Reactor Trip and Auxiliary Feedwater Actuation due to Circulating Water Pump Failure</strong><br /><i>Abstract:&nbsp;</i>This report describes the December 13, 2005, manual reactor trip due to a loss of main condenser vacuum caused by a mechanical failure of the operating circulating water pump. Major plant systems responded normally, including an auxiliary feedwater actuation due to the resultant low steam generator level. This condition was reported to the NRC via the Emergency Notification System on December 13, 2005 (EN# 42199).
2692005001 | Oconee 1, Oconee 2, Oconee 3 | 05/24/2005 | 10/06/2005 | ML05285038 | <strong>Exceeded Tech Spec: Emergency Power Path Aux Power Source Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 5/24/2005, with three Oconee Units at 100% power in Mode 1, Oconee Operations and Engineering concluded that both Keowee Emergency Power Paths could be lost following certain single failures. An electrical contactable in the "Normal" supply to the cooling system of the Overhead Path Main Transformer. The "Back up" supply from the redundant Underground Path closed automatically. This line up would allow loss of both Emergency Power Paths on certain single failures. At 1350 hours TS 3.8.1 condition C was entered. The system was realigned and the TS condition was exited at 1540 hours. An investigation determined that the unacceptable alignment had existed since0820 on 4/21/2005. Operations personnel found parts from the failed contactor on 5/3/2005, and notified their supervision but it was assumed the parts were from a different component with a known problem and did not take further action. The component failed primarily due to age and was replaced. Root Causes are 1) the operability assessment failed to detect inadequate train separation, and 2) failure of the supervisor to verify his assumption. On 07/18/2005, a corrective action revealed another single failure mode based on power alignment resulting from an original design deficiency. TS 3.8.1condition C was entered briefly until the system was realigned and the condition exited. These events have no significance with respect to the health and safety of the public.
2712005001 | Vermont Yankee | 07/25/2005 | 09/22/2005 | ML05271017 | <strong>Reactor Trip Caused by an Electrical Insulator Failure in the 345 kV Switchyard due to a Manufacturing Defect</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2005 at 1525, with the reactor at full power, a generator load reject trip and subsequent reactor trip occurred as a result of an electrical transient that originated in the 345 kV Switchyard. The electrical transient was due to a failure of the 345 kV Motor Operated Disconnect (MOD) Switch, T-1, "C" phase that was caused by the failure of an electrical insulator. An off-site laboratory performed an examination of the porcelain insulator revealing that the failure was caused by a manufacturing defect. The appropriate NRC 4-hour notifications were completed at 1735 in accordance with 10 CFR 50.72(b) as NRC Event Number 41868. This event is being reported as an LER pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of systems listed within 10 CFR 50.73(a)(2)(iv)(B). Plant equipment and operator response to the event was as expected, and the reactor was shutdown with no complications. No release of radioactivity or personnel injury occurred as a result of this event. Therefore, this event did not increase the risk to the health and safety of the public.
2712005002 | Vermont Yankee | 10/04/2005 | 12/01/2005 | ML05342036 | <strong>Primary Containment Leak Rate Testing Program Second Barrier Isolation Valve Found Mis-Positioned</strong><br /><i>Abstract:&nbsp;</i>On 10/04/05, with the reactor at full power, a sample line isolation valve, V10-198A on the Residual Heat Removal (RHR) "A" Loop was found open. V10-198A is a second barrier that supports Primary Containment integrity and is required to be closed per the Primary Containment Leakage Rate Testing Program (PCLRTP). Upon discovery, Operators closed V10-198A and placed it under administrative control. This condition was identified while reviewing a Safety Classification Worksheet for a different valve in the RHR System sample line. The RHR System procedure valve line-up listed V10-198A as "open" and the RHR System Piping and Instrumentation Diagram (P&ID) displayed it as "closed". The open valve provided a potential flow path of water from Primary Containment to Secondary Containment. Two air operated valves and a manual sample valve located downstream of V10-198A provided reasonable assurance that effective isolation for this flow path was maintained during plant operation. The cause of this condition was the application of an insufficient change process in 1996 during implementation of the Qualified Closed Loop Outside Primary Containment modification that lacked sufficient documentation and reviews to effectively implement the change. There was no significant increase in radiological risk to plant workers or the public as a result of this condition.
2722005001 | Salem 1, Salem 2 | 01/26/2005 | 04/25/2005 | ML05123035 | <strong>Carbon Dioxide Migration Impacts Ability to Perform Safe Shutdown in the Event of a Fire</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2005, the preliminary results of an engineering assessment identified that in the event of a carbon dioxide (CO2) system actuation, areas requiring operator access may be inaccessible. In the event of a CO2 system actuation due to a fire in the 4160 volt or 460 volt Switchgear Rooms, or Lower Electrical Penetration Areas, CO2 migration would result in some of the adjacent areas having concentration levels that would require the use of self-contained breathing apparatus (SCBAs) for entry or would be restricted to transit activities only. Some of these adjacent areas are required to be accessible by operators to perform actions in the field to achieve and maintain safe shutdown in the event of a fire in the Switchgear Rooms. Based on the timeliness established in Salem's Manual Action Feasibility Study, the ability to safely shutdown in the event of a fire in the 4160 volt and 460 volt Switchgear Rooms could be impacted. The cause of the unwanted CO2 system migration during system discharge is due to insufficient system design. Immediate corrective actions consisted of the isolation of the carbon dioxide system and the establishment of compensatory measures in accordance with the Salem Fire Protection Program. The resolution strategy of the CO2 migration currently consists of assessing the use of SCBAs to perform manual actions, changes to the post fire safe shutdown procedures, operator training and development of plant modifications. The above event is being reported in accordance with 10CFR50.73(a)(2)(v)(A) and Salem Unit 2 License Condition 2.1 which requires a 14-day special report to be submitted for violations of Licensing Condition 2.C.10.
2722005002 | Salem 1 | 04/19/2005 | 06/20/2005 | ML05179015 | <strong>Technical Specification 3.0.3 Required Plant Shutdown -Sample Line Leak</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2005 at approximately 0400 hours, an operator identified a small leak of approximately 200 drops per minute at the weld of a 45-degree Y44-inch elbow that was located immediately upstream of the Boron Injection Tank sample valve 1SJ6. It was determined that characterizing the flaw for a structural integrity evaluation could not be performed in accordance with Technical Specification (TS)3.4 .10.1, Action b, and isolating the leak would have resulted in isolation of all Safety Injection flow via the charging pumps to the Reactor Coolant System. At 2052 hours on April 19, 2005, the Boron Injection Tank flow path was declared inoperable due to the weld failure and TS 3 .0.3 was entered. At 2105 hours Salem Unit 1 began a shut down to perform appropriate repairs. The crack in the pipe weld was caused by stress corrosion cracking that was influenced by the presence of dissolved oxygen in the water located inside the pipe. Corrective actions included replacing the piping with the cracked weld, performing extent of condition walk-downs and modifying the associated Unit 2 Boron Injection Tank sample valve piping during the recent Refueling Outage2R14 to preclude a similar failure.This event is being reported pursuant to 10CFR50.73(a)(2)(i)(A), Plant Shutdown Required by Technical Specifications .
2722005003 | Salem 1 | 05/03/2005 | 07/05/2005 | ML05194020 | <strong>ECCS Leakage Outside Containment Exceeds Dose Analysis Limits (Seal Injection Filter Replacement)</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2005, the 11 seal water injection filter was removed from service in preparation for filter replacement.A local leak rate was performed following the tag out and determined that the leakage was well within the acceptable administrative limit for Emergency Core Cooling System (ECCS) leakage outside the containment. Subsequent Reactor Coolant System (RCS) water inventory surveillances completed at 0900 and 2318 hours on May 3 indicated an unidentified RCS leakrate of 0 .3 gallons per minute (gpm). On May 4 at approximately 0600 hours the seal water injection filter work was completed and the filter returned to standby mode. A third RCS water inventory was completed on May 4 showing an unidentified leak rate of 0 .055 gpm. At this point it was determined that the increased leakage was associated with the seal replacement work. This leakage (approximately 68,000 cubic centimeters/hour (cc/hr)) exceeded the 3800 cc/hr limit stated in the Final Safety Analysis Report (FSAR) Section6.3.2.11 for ECCS leakage outside the containment. The apparent cause for the excessive leakage was inadequate isolation of the seal injection filter. Some of the corrective actions taken are: The seal water injection filter isolation valves are scheduled to be repaired in the next refueling outage, the human performance deficiencies have been documented in the corrective action program, Operations procedures will be revised to provide enhanced guidance on anomalous RCS leakrate trends, and the ownership for the leakage monitoring and reduction program will be transferred from Engineering to Operations.This event is reportable in accordance with 10CFR50.73(a)(2)(v), any event or condition that could have prevented the fulfillment of the safety function of structures or system that are needed to : ...(C) control the release of radioactive material ; or (D) mitigate the consequences of an accident."
2722005004 | Salem 1 | 10/26/2005 | 12/27/2005 | ML06005045 | <strong>Containment Sump As-found Condition not in Accordance with Design Documents</strong><br /><i>Abstract:&nbsp;</i>During the seventeenth Salem Unit 1 refueling outage (1R17), PSEG (licensed and non-licensed personnel) performed an inspection of the Salem Unit 1 containment sump. The inspection revealed gaps of approximately 0.75 inches between the top of the containment sump cage mesh and the removable sump cover, and at the top of the containment sump steal plate where pipe and conduits penetrate into the containment sump. Gaps internal to the sump were also noted in the containment sump upper screen mesh that provides clearance for the vortex plate support rods. The apparent cause for the gaps noted in the sump upper screen mesh that provides clearance for the vortex plate support rods has been attributed to poor implementation and maintenance practice during the installation of vortex breakers within the sump and original sump construction. The deficiencies that could have allowed debris to enter the containment sump were corrected during the seventeenth refueling outage. This condition is reportable per 10CFR50.73(a)(2)(v) as condition that could have prevented the fulfillment of a safety function of structures or system designed to remove heat or mitigate the consequences of an accident.
2722005005 | Salem 1 | 11/03/2005 | 12/30/2005 | ML06010045 | <strong>11 Safety Injection Pump Discharge Valve Found Shut</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2005, at 2100 hours, the 11 Safety Injection (SI) pump discharge valve (11SJ35) was found closed. The normally locked open valve was discovered closed by operators performing a pretest valve lineup for a normally scheduled SI pump surveillance test. The valve had been unlocked and closed on November 3, 2005 for check valve leak rate testing during refueling outage 1R17. Following discovery of the closed discharge valve, Technical Specification Action Statement (TSAS) 3.5.2 b was entered and the valve placed in its proper position (locked open) and the TSAS exited. The SI pump discharge valve being inappropriately left shut effectively disabled one of the redundant trains of Safety Injection. The direct cause was procedure non-compliance. The root cause was attributed to less than adequate application and enforcement of operator fundamentals. Corrective action was taken to revise the procedures and corrective actions are taking place to improve operator fundamentals. This event is reportable under 10CFR 50.73(a)(2)(i)(B) "Any operation or condition which was prohibited by the Plants Technical Specifications."
2752005001 | Diablo Canyon 1 | 11/11/2005 | 11/25/2005 | ML05341039 | <strong>Steam Generator Tube Plugging Due to Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2005, at 1200 PST, with Unit 1 in Mode 6 (refueling, with the reactor defueled), analysis of eddy current testing on Steam Generator (SG) 1-1 and SG 1-2 indicated that greater than one percent of the tubes were defective. Pacific Gas & Electric Company (PG&E) made a non-emergency report to the NRC as required by Technical Specification (TS) Table 5.5.9-2, "Steam Generator (SG) Tube Inspection," at 1230 PST, via NRC Event No. 42136. On November 9, 2005, PG&E discussed the preliminary results of the SG eddy current inspection during a phone conference with the Office of Nuclear Reactor Regulation (NRR). The primary cause of the SG tube cracking was circumferential outside diameter stress corrosion cracking at the hot leg tube support plates and at the hot leg top of tube sheet. In accordance with TS 5.5.9, "Steam Generator (SG) Tube Surveillance Program," PG&E has plugged all defective Unit 1 tubes identified during the current refueling outage. All defective tubes met condition-monitoring requirements at the end of Cycle 13. PG&E maintains a comprehensive program to minimize SG tube degradation, and plans to replace the SGs at the end of Cycle 15.
2772005001 | Peach Bottom 2 | 07/10/2005 | 09/02/2005 | ML05251043 | <strong>Unit 2 Automatic Scram due to Incorrect Assumptions when Aborting a Main Turbine Test</strong><br /><i>Abstract:&nbsp;</i>On 7/10/05, at approximately 0318 hours, a Unit 2 automatic scram occurred as a result of a Main Turbine Stop Valve closure signal. The Main Turbine Stop valves had closed as a result of a Main Turbine trip signal generated during performance of the weekly Main Turbine Mechanical Trip Valve routine test. The Main Turbine trip signal was generated when a failed test was being aborted and did not reflect any actual adverse Main Turbine condition that required the Main Turbine to be tripped. As a result of the automatic scram, the Reactor Vessel water level 3 set point was reached as expected. This resulted in Primary Containment Isolation System (PCIS) Group II and III isolations. Also, a Reactor Vessel high pressure condition occurred resulting in automatic operation of the C, D, and E Main Steam Safety Relief Valves. There were no actual safety consequences associated with this event. The Main Turbine trip was caused by incorrect assumptions concerning the status of the Main Turbine trip system and not involving additional personnel while aborting the routine test. Corrective actions include remediation and re-evaluation of involved personnel and reinforcing management expectations regarding human performance practices.
2772005002 | Peach Bottom 2, Peach Bottom 3 | 09/21/2005 | 11/16/2005 | ML05325036 | <strong>Recirculation Motor / Pump Modification Activities Unanalyzed for Postulated Seismic Conditions</strong><br /><i>Abstract:&nbsp;</i>On 9/21/05, Engineering personnel identified that there was insufficient analysis of the interim configuration of system supports for planned modification work to replace the 3B Recirculation (Recirc) motor / pump during the Unit 3 15th Refueling Outage. Although the replacement of the 3B Recirc motor / pump was deferred, it was determined that similar modification work was performed in previous refueling outages on Units 2 and 3. During previous outages, the interim condition of associated loop of Recirc / Residual Heat Removal (RHR) piping was not analyzed for seismic conditions. This condition also affected the operability of the Shutdown Cooling (SDC) and Low Pressure Coolant Injection (LPCI) modes of RHR while in the interim configuration. There were no actual safety consequences. There were no seismic events during the brief periods of time while in the interim configuration. The event was caused by less than adequate review of the interim configuration of the Recirc system associated with Recirc motor / pump modification activities. Engineering analyses will be performed to design an acceptable temporary piping support configuration and revise appropriate implementing procedures in support of future Recirc motor / pump replacements.
2772005003 | Peach Bottom 2, Peach Bottom 3 | 12/22/2005 | 02/10/2006 | ML06047054 | <strong>E-2 Emergency Diesel Generator Technical Specification Required Actions Not Performed</strong><br /><i>Abstract:&nbsp;</i>On 12/27/05 at approximately 2030 hours, while preparing for a surveillance test of the E-2 EDG, an Equipment Operator identified that approximately 10 gallons of water had previously leaked in the vicinity of the E-2 EDG cooling subsystem. The leakage was determined to be pump shaft packing leakage associated with the E-2 EDG Air Coolant Auxiliary Pump. The leak rate was later determined to be approximately 10 gallons per hour, but existed only when the E-2 EDG was operating. This leak rate resulted in inoperability of the E-2 EDG. It was determined that the E-2 EDG Air Coolant Auxiliary Pump had been returned to service on 12/22/05 following the pump packing maintenance Post-Maintenance Test (PMT). However, as a result of weaknesses in the PMT, the high rate of pump shaft packing leakage was not identified. As a result of the unknown inoperability on 12/22/05, the Required Actions for Technical Specification 3.8.1, Condition B for one EDG being inoperable were not performed. It was determined that a condition prohibited by Technical Specifications occurred when Required Actions B.2 and B.4.1/8.4.2 were not performed. The unknown inoperability of the E-2 EDG between 12/22/05 and 12/27/05 was the result of a less than adequate PMT when the Air Coolant Auxiliary Pump was returned to service on 12/22/05. The Air Coolant Auxiliary Pump was removed from service, thereby allowing the E-2 EDG to be declared operable on 12/28/05 at approximately 1815 hours. There were no actual safety consequences associated with this event.
2782005001 | Peach Bottom 3 | 03/03/2005 | 04/26/2005 | ML05125039 | <strong>Loss of High Pressure Coolant Injection System Function as a Result of Inoperable Flow Controller</strong><br /><i>Abstract:&nbsp;</i>On 3/3/05, at approximately 1825 hours, during the performance of routine Main Control Room panel walk downs for the High Pressure Coolant Injection (HPCI) system, Licensed Operations personnel discovered that the HPCI system flow controller faceplate had a blank indicator reading. Subsequently, the flow controller was determined to not be able to perform its HPCI flow control function. Therefore, HPCI was declared inoperable. The inoperability was discovered promptly since the faceplate had been observed to have proper indication approximately 10 minutes prior to discovery. Troubleshooting of the HPCI system confirmed that the HPCI system flow controller was inoperable resulting in the HPCI system not being capable of developing sufficient flow rates if it had been required for a design basis event. The flow controller was promptly replaced. HPCI was satisfactorily tested and returned to an operable status on 3/4/05 by 1800 hours. The flow controller had previously been dedicated for safety related usage by a qualified off-site vendor in December 2002 and was installed in March 2004. The preliminary failure analysis report has determined that the internal power supply of the flow controller failed. Additional corrective actions are being evaluated in accordance with the corrective action program including the need to ensure appropriate rebuilding of components sent to off-site vendors for dedication. There were no actual safety consequences associated with this event. This event was not considered to be risk significant.
2782005002 | Peach Bottom 3 | 03/21/2005 | 05/12/2005 | ML05138034 | <strong>Technical Specification Non-Compliance due to a Unit 3 HPCI Suction Valve Logic Limit Switch Out of Adjustment</strong><br /><i>Abstract:&nbsp;</i>On 3/21/05, at approximately 1640 hours, during preparations for the performance of a routine surveillance test for the Unit 3 High Pressure Coolant Injection (HPCI) system, Operations personnel discovered that the Condensate Storage Tank (CST) suction source Motor Operated (MO) Valve (MO-17) did not automatically close when the Suppression Pool Suction source valves (MO-57 & MO-58) were opened during the surveillance test. It was subsequently determined that a condition prohibited by Technical Specifications existed as a result of the Technical Specification 3.3.5.1 function of transferring the HPCI suction from the CST to Suppression Pool being inoperable for a time period longer than allowed in Technical Specification 3.3.5.1. Troubleshooting determined that the automatic closure of the MO-17 failed to occur due to a limit switch being out of adjustment. The limit switch is within the motor operator housing for the MO-58 valve and provides an auto-close input into the MO-17 valve logic. The HPCI CST - Suppression Pool transfer logic was returned to an operable condition on 3/22/05. There were no actual safety consequences associated with this event.
2782005003 | Peach Bottom 3 | 09/20/2005 | 10/28/2005 | ML05311015 | <strong>Residual Heat Removal System Small Bore Piping Leak due to Weld Deficiency</strong><br /><i>Abstract:&nbsp;</i>On 9/20/05 at approximately 0500 hours, Licensed Operations personnel determined that a small amount of Reactor Coolant System (RCS) pressure boundary leakage existed on Unit 3. This determination was made based on review of a Primary Containment inspection performed subsequent to a Reactor shutdown on 9/19/05 for a Refueling Outage. The RCS pressure boundary leakage was determined to exist on a one-inch equalizing line for the 'A' Residual Heat Removal injection testable check valve located within the normally inaccessible Primary Containment. The leak was at a pipe coupling socket weld. The leak was determined to exist during Unit 3 Cycle 15 operations. The peak Containment unidentified leakage rate totaled approximately 1 gpm during the operating cycle. The cause of the weld deficiency was due to lack of fusion associated with the weld. The welded joint was replaced and appropriately inspected and tested successfully during the Unit 3 refueling Outage. An extent of condition evaluation was performed for additional inspections associated with similar welds on Unit 3. Other evaluations will be performed for Unit 2 similar welds. There were no actual safety consequences associated with this event.
2782005004 | Peach Bottom 3 | 10/02/2005 | 11/22/2005 | ML05327022 | <strong>Laboratory Analysis Identifies Safety Relief Valve Set Point and Performance Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Based on information received on 10/2/05 from a laboratory performing Safety Relief Valve (SRV) as-found testing, Site Engineering personnel determined that SRV set point and performance deficiencies existed with five SRVs that were installed during the 15th operating cycle for Unit 3. Four of the SRVs were determined to have their as-found set points in excess of the Technical Specification allowable 1% tolerance. In addition,one additional SRV was found to not properly re-close when tested. The cause of the four SRVs being outside of their allowable as-found set points is due to set point drift. Concerning the failure of the SRV to re-close, the preliminary laboratory failure analysis identified that the main valve disc had not properly re-seated when closing due to misalignment of the main valve disc spring. The valve was last refurbished in February 2001.The five SRVs were replaced with different SRVs for the 16th Unit 3 operating cycle. Additional assessment and appropriate corrective actions concerning SRV refurbishment vendor work practices will be further assessed as part of the Corrective Action Program. There were no actual safety consequences associated with this event.
2802005001 | Surry 1 | 02/07/2005 | 04/04/2005 | ML05104040 | <strong>Manual Reactor Trip Initiated Due to Misaligned Control Rod</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2005 at 2024 hours, with Unit 1 undergoing a reactor startup, a manual reactor trip was initiated due to a control rod misalignment on rod B1 0. At the time of the manual trip, reactor power was in the source range at approximately 210 counts per second. All required systems functioned as designed during the manual reactor trip and the operating staff acted promptly and appropriately to stabilize the unit at hot shutdown.On February 8, 2005 at 0856 hours, after ensuring no hardware concerns existed, control rod exercising began on the misaligned rod. At 1013 hours, four tests were completed Anthe rod with no issues noted. After completing the test on rod B10, all control and shutdown rods were exercised, one bank at a time. The probable cause of this event is build up of particulate (debris) in the control rod drive mechanism internals. Control rods will be exercised prior to any unit startup to mitigate the effects of particulate in CRD Minternals. The unit was taken critical at 1859 hours on February 8, 2005 and placed on line on February 9, 2005 at 0420 hours. This report is being submitted pursuant to 10 CFR50.73(a)(2)(iv)(A) for a manual actuation of the reactor protection system.
2802005002 | Surry 1, Surry 2 | 07/25/2005 | 09/11/2005 | ML05263035 | <strong>Radiation Monitors Inoperable due to Condensation - Voluntary Special Report</strong><br /><i>Abstract:&nbsp;</i>Units 1 and 2 were operating at 100% power on July 25, 2005, when a control room annunciator alarmed, indicating a problem with the effluent radiation monitors. The appropriate annunciator response and abnormal procedures were promptly performed and a low sample flow condition was identified for the gaseous vents system radiation monitor, 1-GW-RM-130-1. The monitor was declared inoperable at 23:30 and the preplanned alternate method of monitoring was initiated in accordance with Technical Specifications (TS) Table 3.7-6. An action statement was entered in accordance with TS Table 3.7-6, requiring restoration of the monitor within seven days or the submittal of a Special Report within 30 days. Investigation of the problem revealed formation of condensation, which restricted sample flow through the system. Additional heat trace was installed on the monitor sample lines to further reduce moisture accumulation. This Voluntary Special Report is being submitted pursuant to TS Table 3.7-6.
2802005003 | Surry 1, Surry 2 | 06/11/2005 | 10/06/2005 | ML05292004 | <strong>Fuel Leak Into Engine Oil Causes Emergency Service Water Pump Inoperability</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2005, with both units at 100% reactor power, the results from the monthly engine oil samples for Emergency Service Water Pump (ESWP) 1B indicated an increase in fuel contamination. Evaluation of the previous monthly engine oil samples indicated an increasing trend of fuel contamination with a corresponding decrease in viscosity. The indication of fuel intrusion into the engine oil began with the June11, 2005 sample at a rate such that satisfactory operation of the ESWP could not be sustained for an extended period of time. The ESWP was declared inoperable on August 11, 2005 at 1900 hours. A root cause evaluation determined that fuel was entering the engine oil system from a leak at the connection between the fuel inlet jumper and the #1 L fuel injector. The leak occurred due to a flat spot on the injector flared fitting mating surface. The leak was repaired and ESWP 1B was returned to service. Procedures will be revised to inspect the fuel line seating surface and to perform a timed fuel line pressure drop test. A risk assessment determined that the impact of the unavailability of ESWP 1B on core damage frequency was negligible at less than 5E-9/year. During the period when the 1B pump was assumed to be inoperable, a second pump was taken out of service. The integrated risk with two ESWPs out of service remained at very low safety significance.
2812005001 | Surry 2 | 04/01/2005 | 06/24/2005 | ML05188004 | <strong>Low Head Safety Injection Pump Breaker Failed to Close due to Binding</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2005 at 0230 hours, while performing an engineered safety feature actuation test with Unit 2 in cold shutdown, breaker 24J-3 for low head safety injection (LHSI) pump 1B failed to close while in the test position when a simulated automatic closure signal was generated. At the time of the failure, Unit 1 was at 100% reactor power. An interim root cause evaluation determined that the most probable cause of the circuit breaker 24J-3 failure was binding of the close latch roller in conjunction with a burr or plating on the edge radius of the primary close latch. A spare safety related breaker was installed, tested, and the LHSI pump returned to service. Other safety related Unit 2 breakers were tested for a similar restriction. No problems were found, which provided confidence that breakers on Unit 1 were satisfactory. All remaining susceptible safety related Unit 1 and Unit 2 breakers will be inspected for similar issues. A risk assessment determined that the potential unavailability of the LHSI pump 1B on cumulative core damage probability was a low risk significant event. An evaluation considered the breaker to have been inoperable since the previous successful test on April 1, 2005. During this time period, the redundant LHSI pump 1A was briefly inoperable related to tests and maintenance on its associated emergency diesel generator.
2822005001 | Prairie Island 1 | 02/05/2005 | 04/06/2005 | ML05096055 | <strong>Discovery of Single Failure Vulnerability of Unit 1 Safeguards Buses</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2005, Prairie Island Nuclear Generating Plant (PINGP) Staff completed an evaluation of an event reported at Crystal River dealing with the single failure vulnerability of safeguards buses. The review determined that the Prairie Island Unit 1 safeguards buses did have a single failure vulnerability due to current transformer (CT) circuits for the source breakers for these buses from the CT11 (Cooling Tower 11 transformer) source that are tied together with a secondary CT on the common wires which feeds metering equipment. At approximately 8:45 pm Central Standard Time (CST), plant operators declared affected Unit 1 safeguards buses 15 and 16 inoperable and declared one path from the grid inoperable. At approximately 10:15 pm CST, operators restored buses 15 and 16 to operable status after they were transferred to an alternate source (1RY transformer) and the CT11 breakers and relaying disconnects were opened. Since a single failure vulnerability of the Unit 1 safeguards buses (which are required to meet the single failure criterion) was identified, this event is reportable per 10 CFR 50.73(a)(2)(ii)(B).<br /><br /> Temporary modification of the CT11 relaying scheme was completed on February 8, 2005 .
2852005001 | Fort Calhoun | 02/26/2005 | 04/27/2005 | ML05123014 | <strong>Unplanned Reactor Trip Due to a Feedwater Transient at Low Power During Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2005, operators completed a scheduled power reduction to 12% power. At 2100 CDT, the turbine was tripped with no noted complications. At 2121, the turbine was reset in preparation for turbine testing. The reactor operator (RO) noticed that intermediate stop valve (ISV-2) did not open as expected. At 2134, while troubleshooting ISV-2, a RO informed the control room supervisor that pressurizer level and pressure were lowering and another RO informed the control room supervisor that he was experiencing a problem with feedwater control. The operations crew identified that reactor coolant system (RCS) temperature was lowering and power was rising. The reactor protection system loss of load trip units enabled and the reactor automatically tripped. The immediate cause for the reactor trip was due to control board operator performance errors related to control of RCS temperature and steam generator (SG) level. These errors resulted in a lowering of RCS temperature, which, resulted in an increase in reactor power activating the loss of load trip. The root cause of this event was that administrative controls are overly biased towards full power operation. The reactor shutdown was completed as required. SG level and reactor temperature were returned to normal control bands. Procedure changes are being completed to address the root cause.
2852005002 | Fort Calhoun | 08/02/2005 | 10/03/2005 | ML05285032 | <strong>Inoperability of Pressurizer Power Operated Relief Block Valve Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>The circuit breaker providing power to the motor for one of the power operated relief valve (PORV) block valves (HCV-151) had an incorrect instantaneous overcurrent setting that led to an intermittent tripping problem. HCV-151 was inoperable from October 4, 2003, when the circuit breaker was set incorrectly to March 9, 2005, when the problem was discovered. The condition was identified during review of the incident, following completion of a plant refueling outage. While testing HCV-151 on March 9, 2005, to satisfy post-maintenance stroke time testing of the valve following stem lubrication, the circuit breaker feeding the valve tripped twice. The control room cycled the valve closed, then, on the open stroke, the circuit breaker tripped after minimal observed valve travel. After the circuit breaker was reset, the valve opened properly. When the valve was cycled closed, and the circuit breaker tripped again with no observable travel. The root cause is that the system engineer provided incorrect information to a preventive maintenance task due to incomplete verification practices. Following this event, the system engineering supervisor familiarized appropriate engineers, who supply critical data to maintenance groups, with this event, and provided expectations on the use of the most current data. The work instruction shave been updated to include correct test and setting information.
2862005001 | Indian Point 3 | 05/01/2001 | 03/24/2005 | ML05091014 | <strong>Plant in a Condition Prohibited by Technical Specifications due to Error Making Control Room Ventilation System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2005, at approximately 1900 hours, with steady state reactor power at 100%, Indian Point Energy Center (IPEC) determined that the Control Room Ventilation System (CRVS) "B" damper was operating with linkage in the reverse position and therefore was inoperable (it would open on a close signal and close to the incident mode on an open signal). Damper B is designed to allow filtered outside air intake in the 10 Percent Incident mode and to isolate outside air intake during normal operation and the 100 Percent Incident mode. This condition was determined to have existed since May 5, 2001. The apparent cause of this event was incomplete work instructions in that no details as to how to connect the linkage were included in the installation work package. These details were not available when the work package was issued. Contributing was the failure of the post work test to determine that damper B was not closed in the Normal and 100 Percent Incident mode. The condition was determined to be a violation of Technical Specifications. Corrective action was taken to repair damper B. Additional corrective action will be taken to determine why the post work test did not detect that damper B was incorrectly configured and to initiate corrective action on how to determine the damper is closed. There was no significant effect on the public health and safety since the system maintained required functional capability.
2862005002 | Indian Point 3 | 05/06/2005 | 07/05/2005 | ML05250048 | <strong>Automatic Reactor Trip due to 32 Steam Generator Steam Flow/Feedwater Flow Mismatch Caused by Low Feedwater Flow due to Inadvertent Condensate Polisher Post Filter Bypass Valve Closure</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2005, at approximately 10:32 hours, an automatic reactor trip was initiated due to a 32 steam generator (SG) steam flow/feedwater flow mismatch with low SG level trip during Instrumentation & Control (I&C) troubleshooting of the condensate system(CS). All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary FW system automatically started as expected due to a SG low level. The cause of the event was personnel error due to poor work practices during troubleshooting of the CS. The control switch for the condensate polisher (CP) post filter bypass valve was in auto when a wire was disconnected from a relay of a seal-in circuit causing the post filter bypass valve to close. The post filter bypass valve closure caused inadequate feedwater flow that resulted in the mismatch and low SG level. Operations and I&C personnel failed to verify and recognize the required switch position for the condition due to overconfidence. Corrective actions include counseling operations and I&C personnel and applicable plant staff on management expectations for a questioning attitude, pre-job briefs, peer checking; and use of the formal work process. The CP system operating procedure was revised for proper CP valve control switch position and seal-in circuit clearance. The work control procedure will be revised to define when work becomes troubleshooting and decide the level of risk assessment to be performed. The event had no effect on public health and safety.
2862005003 | Indian Point 3 | 05/16/2005 | 07/15/2005 | ML05207075 | <strong>Inadvertent Actuation and Automatic Start of the Auxiliary Feedwater Pumps During Reactor Protection Logic Testing Due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2005, at approximately 10:39 hours, both motor driven auxiliary feedwater (AFW) pumps automatically started after exceeding the actuation circuit 28 second time delay during performance of the low-low level steam generator water level section of procedure 3-PT-M13B1, Reactor Protection Logic Channel Functional Test. The steam driven AFW pump did not start. Upon recognition of pump start, operators secured the pumps. The apparent cause was personnel error due to failure to utilize adequate work practices. An Instrumentation and Control technician timing the AFW actuation circuit after being armed, stepped into the control room board area and became distracted and failed to notify the test technician for release of the arming signal. Corrective actions included briefing I&C personnel on the event and counseling I&C personnel on management expectations for remaining focused on the job. The test procedure will be revised to eliminate the need to leave the test area and minimize the time needed for an arming signal to be present. High intensity training will be established for I&C personnel on selection and use of human performance tools. The event had no effect on public health and safety.
2862005004 | Indian Point 3 | 06/10/2005 | 08/09/2005 | ML05228035 | <strong>Manual Reactor Trip Due to a Service Water Leak Inside the Main Generator Exciter Enclosure Caused by Exciter Cooler Gasket Leaks</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2005, at approximately 0924 hours, operations initiated a manual reactor trip following discovery of service water (SW) leakage inside the main generator exciter enclosure. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by theming condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator shrink effect. The cause of the leakage was a split gasket on the 32B exciter cooler due to over tightened heat exchanger head bolting. The root cause of the condition was the level and extent of training associated with resilient gasketed joint installation which does not encompass the effects of an improper tightening sequence encountered during the return to service test phase. Corrective actions included repair/replacement of applicable exciter cooler gaskets, leak inspections, counseling maintenance personnel on management's expectation on questioning attitude, self checking, use of the formal work process, and workmanship quality. Applicable heat exchanger maintenance procedures and training program will be reviewed and revised as necessary for proper gasket application/material and proper cooler bolt torque values and sequencing. The event had no effect on public health and safety.
2862005005 | Indian Point 3 | 10/04/2005 | 12/05/2005 | ML05343021 | <strong>Technical Specification Prohibited Condition due to Mode Change without Performing Required Actions with the 32 Containment Fan Cooler Unit Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2005, Operations discovered the 32 Containment Fan Cooler Unit (FCU) supply breaker in the test position and it was declared inoperable. Technical Specification (TS) 3.6.6 requires three FCU trains to be operable in Modes 1 through 4. On October 4, 2005, during startup from a forced outage, the plant entered Mode 4, with the 32 FCU inoperable violating the TS. The cause of the TS violation was failure to perform the required actions of TS 3.0.4. prior to changing Modes with an inoperable 32 FCU. The failure to identify the inoperable FCU was due to ineffective use of a systematic and rigorous problem resolution process. The inoperable 32 FCU was caused by an improper FCU breaker installation due to human error. Significant corrective actions included breaker inspection and re-installation, brief personnel on the event and advise of management's expectation of using a rigorous, systematic process to resolve problems, coaching Operations and Outage & Work Control personnel on the need for rigor in problem resolution and operability evaluations, providing focused training of operators for verifying breaker position, including event in operator requalification training and engineering training reinforcing the need to examine evidence questioning operability, revising applicable procedures for verifying proper breaker rack-in, requiring confirmatory observations of major equipment starts, and revising the startup procedure to require verification that Operability Evaluations are performed prior to mode changes. The event had no effect on public health and safety.
2872005001 | Oconee 3 | 08/30/2005 | 10/31/2005 | ML05312036 | <strong>TS LCO Condition Allowed Outage Time and Required Action Completion Time Exceeded due to Blockage of LPI/BS Pump Room Air Flow Path</strong><br /><i>Abstract:&nbsp;</i>On August 30, 2005, while at 100% power, the stairwell into Room 81 on Unit 3 was found to be covered with a tent enclosure. Room 81 contains the B Train pumps for the Low Pressure Injection System (LPI) and the Building Spray System (BS). Calculations credit an air flow path through the stairwell to ensure acceptable environmental conditions within the room. The tent enclosure blocked this air flow path. Another adverse condition was identified, involving temporary filters installed in the inlet and exhaust grilles for the air handling units serving the room. Consequently, for certain design basis accidents, the room temperature could have exceeded the qualification limits for the 3B LPI Pump and 3B BS Pump and their associated motors. The enclosure had been in place approximately 34 days, thus exceeding Technical Specification required action times for these systems. There was no loss of function, as redundant trains of LPI and BS were not affected. This event was caused by failure to provide adequate controls on critical inputs to safety analyses. Corrective actions included removal of the tent from the stairwell outside Room 81, removal of filters from ventilation grilles in Room 81, and placement of signs outside of all HPI, LPI, and BS pump rooms cautioning against blockage of these air flow paths. This event has no significance with respect to public health and safety.
2872005002 | Oconee 3 | 08/31/2005 | 10/31/2005 | ML05312036 | <strong>Unit 3 Trip with ES Actuation due to CRD Modification Deficiencies</strong><br /><i>Abstract:&nbsp;</i>At 1428:27, on 8-31-05, Unit 3 tripped from 100% rated power, Mode 1. The trip transient reduced Reactor Coolant System temperature and pressure, resulting in Engineered Safeguards (ES) actuations of the High Pressure Injection, Containment Isolation (partial), and Emergency Power Systems. Operators took actions per the Emergency Operating Procedure to stabilize the unit in Mode 3. All challenged ES components operated as expected. The causes of the trip and ES actuations were two design deficiencies in a recent (late 2004) modification to the Control Rod Drive system. Redundant power sources were not sufficiently verified nor tested individually in the as-built configuration. Also, a system interface issue was detected both in design review and in testing but was not resolved prior to contributing to the event. Corrective actions include design changes to correct the deficiencies and enhancements to the design change process. This event is considered to have no significance with respect to the health and safety of the public.
2892005001 | Three Mile Island 1 | 02/03/2005 | 04/18/2006 | ML06121003 | <strong>Control Building Ventilation Fan Inoperable due to Cracked Fan Hub</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2005, it was discovered that a condition, which existed from August 20, 2003, until September 29, 2004, should have been reported under the following criteria: 1) a condition which was prohibited by the plants Technical Specifications (TS), (10 CFR 50.73 (a)(2)(i)(B)), and 2) a condition that could have prevented the fulfillment of the safety function related to Post Accident Control Room habitability, 10 CFR 50.73 (a)(2)(v). The condition involved Control Building Ventilation Return Air Fan "B" (AH-E-19B). AH-E-19B is a vane-axial fan, model number 48-21-900AP, manufactured by Howden Buffalo. An evaluation of past operability concluded that the Control Room Emergency Filtration System would not have been able to meet its mission time of 30-days during several time intervals within the above specified time frame, when its redundant fan was not available. On December 12, 2001, AH-E-19B was identified as being noisy. On August 20, 2003, the noise level increased and the fan was designated as non-preferred use. During the motor replacement on September 29, 2004, the fan hub was discovered cracked. The evaluation of past operability concluded that the fan would not have been capable of performing its 30-day mission time. The root cause of the event was that Engineering, Maintenance, and Operations did not use the correct processes to ensure adequate rigor was applied to the troubleshooting, operability determination, and decision-making regarding component health. The corrective actions are: 1) Establish and communicate clear expectations for entry into the Troubleshooting, Operability Evaluation, Non-Preferred Use, and Operational and Technical Decision Making Processes for Engineering, Maintenance, and Operations personnel; and 2) Establish and implement a mechanism for periodic reinforcement of these expectations.
2892005002 | Three Mile Island 1 | 04/27/2005 | 06/23/2005 | ML05180025 | <strong>Safe Shutdown Analysis For Control Building Fire Area 1 Was Discovered To Have Flaws In The Fire Mitigation Stategey Due To Insuffcient Technical Rigor</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2005, a previously unidentified error associated with an Appendix R fire scenario involving multiple high impedance faults (MHIF), in the 306' elevation of the Control Building, was identified. An engineering evaluation has determined that the operations procedure for recovery of vital power for instrumentation and control, following a postulated fire/MHIF scenario in this area, would not be successful . The original evaluation of this fire/MHIF concern (in the 1987 time frame) considered this event to be very improbable and incorrectly assumed that the recovery of vital power following a bus trip would be successful. The historical procedure incorrectly assumed that DC power (which is assumed lost in the fire) was not required to restart the necessary electrical recovery equipment. The root cause is determined to be insufficient technical rigor applied in the technical analysis of the MHIF strategy and in the older procedure review process. The corrective action to address the root cause is addressed by IR213719, which included establishing Exelon technical human factors procedure, HU-AA-1212. This condition was determined to meet the following reporting criterion: the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety (10 CFR 50 .73 (a)(2)(ii)(B)).
2932005001 | Pilgrim | 02/13/2005 | 03/30/2005 | ML05095043 | <strong>High Pressure Coolant Injection System Inoperable due to Fuse Failure in Motor Operated Valve Control Power Circuit</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2005 at about 1900 hours, the HPCI system was declared inoperable due to the discovery of a failure of a fuse in the control circuit that powers the normally closed HPCI system indicating light motor operated injection valve. The failure was discovered when the valve's position was observed not illuminated during a shift turnover. The failed fuse and the accompanying fuse that power the valve's control circuit were replaced, and the system was returned to operable, standby status by 2150 hours on February 13, 2005.The direct cause of the fuse failure was separation of the fuse element from the fuse end cap (ferrule)that was most likely due to manufacturing defect(s) introduced when the fuse was manufactured(pre-1994). The fuse was a Bussman Limitron, Class RK1, KWN-R-1 0 type fuse. The root cause was utility non-licensed supervisory personnel error. Two supervisors failed to follow corrective action program procedure requirements for performance and tracking of corrective actions in that a generic equipment issue was not adequately dispositioned in the corrective action process. Corrective actions planned include additional training on corrective action program responsibilities, and the replacement of additional fuses.This condition posed no threat to public health and safety.
2932005002 | Pilgrim | 04/14/2005 | 06/13/2005 | ML05172041 | <strong>One Less than the Technical Specifications Required Minimum Number of Operable Drywell Pressure Instrument Channels due to Licensed Operator Error</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2005 at 0955 hours, one drywell pressure transmitter was found isolated (valved out of service) and therefore, inoperable. The transmitter is part of one of two Division 'B' instrument channels that function to initiate safety systems in the event of a high-pressure condition inside the drywell. The transmitter was mistakenly isolated at 0905 hours on April 14, 2005. The Division 'A' pressure transmitters and related instrument channels that provide a similar function were not impacted. The condition existed during reactor power operation for a period longer than allowed by technical specifications. The root cause of the condition was licensed operator error. The operator mistakenly closed the isolation valve of the pressure transmitter instead of another valve. The error was the result of inadequate use of human performance error prevention tools, i.e. self-checking and a questioning attitude. Corrective actions taken included opening the isolation valve and walk-downs to ensure other instrumentation was correctly configured. The condition posed no threat to public health and safety.
2932005003 | Pilgrim | 05/11/2005 | 07/05/2005 | ML05202029 | <strong>Target Rock Relief Valves' Test Pressures Exceeded Technical Specification Tolerance Limit</strong><br /><i>Abstract:&nbsp;</i>On May 11, 2005, Pilgrim Station was notified that three Target Rock relief valve pilot assemblies exceeded the Technical Specification (TS) tolerance limit of 1115 psig t 11 psi ( 1%) during routine testing at the Wyle Laboratories test facility. Certified replacement relief valve pilot assemblies we reinstalled in the plant at the time of the notification. The most probable cause of the as-found initial popping pressures exceeding the TS tolerance limit was corrosion bonding of the pilot valve assembly disk and seat. The corrosion bonding most likely developed while the pilot valve assemblies were in service. Poor fitting insulation was also identified As a contributing cause. Corrective action taken includes replacing the pilot valves with certified tested replacements. Engineering is evaluating options for resolving the high popping pressure reliability concern. The condition posed no threat to public health and safety.
2962005001 | Browns Ferry 3 | 02/11/2005 | 04/12/2005 | ML05103001 | <strong>Automatic Reactor Scram Due to False Main Transformer Differential Signal</strong><br /><i>Abstract:&nbsp;</i>At 1629 hours Central Standard Time on February 11, 2005, the Unit 3 reactor scrammed from 100% power. The scram was caused by a simultaneous false trip signal generated to the main generator circuit breaker 234, switchyard circuit breakers 5264 and 5268, and a main generator trip. This signal was generated when a PK block (disconnect device 26W), which had been pulled as par t of a clearance for breaker 5264, was re-inserted as part of a switching order from the Load Dispatcher for returning the breaker to service. When the PK block 26W was inserted (out of sequence of the switching order), the associated current transformer (CT) circuit was momentarily grounded resulting in a false differential. T he correct sequence of the switching order was to actuate the trip cutout switches for the differential trip functions prior to inserting any of the PK blocks. The generator trip resulted in a turbine trip and opening of the output breakers caused a power-load unbalance trip. The control valve (CV) fast closure caused the reactor to SCRAM. All rods inserted. Reactor water level lowered, as expected, and was recovered by normal feed water flow. All expected Primary Containment Isolation System (PCIS) isolations were received along with the auto start of Control Room Emergency Ventilation (CREV), and the three Standby Gas Treatment (SGT) trains. The root cause of this event was determined to be personnel error, in that the Operator (Utility Licensed) failed to follow the task sequence identified in the switching order.
2962005002 | Browns Ferry 3 | 09/17/2005 | 11/10/2005 | ML05319038 | <strong>Reactor Scram from Main Turbine Trip on Low Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On 9/17/05 Unit 3 was in steady state operation at approximately 73% power. A maintenance activity was in progress to repair a level control valve on a high pressure feedwater heater. During the work on the valve, an air-leakage pathway to the main condenser was created, and due to an unanticipated mechanical failure of the valve internals, the valve could not be readily reassembled to isolate the in-leakage path. Over a period of approximately 10 minutes, the main condenser vacuum decreased to the low vacuum trip setpoint for the main turbine, and a main turbine trip and subsequent reactor scram occurred at 1129 hours CDT. All expected system responses occurred. Actuation of primary containment isolation system Groups 2, 3, 6, and 8 occurred due to the expected temporary lowering of reactor water level below the actuation setpoint. This logic isolates shutdown cooling (if in service), isolates the reactor water cleanup system, isolates the normal reactor building ventilation,initiates the standby gas treatment system, initiates the control room emergency ventilation system, and retracts traversing in core probes (if inserted). The normal heat rejection path (from the reactor to the main condenser via the steam lines with reactor water make-up provided by the condensate/feedwater systems remained in service.Neither the high pressure coolant injection nor reactor core isolation cooling systems were used during this event.No safety-relief valve (SRV) operation occurred during the trip transient, and post-trip review confirmed that peak reactor pressures remained below the nominal SRV lift setpoints. The event was caused by the unanticipated failure mode of the valves internals, and the work control process was not effectively managed to assess all possible failure modes. Corrective actions include revisions to operating procedures and the provision of training to managers/supervisors on effective operational decision making.
2962005003 | Browns Ferry 3, Browns Ferry 2 | 10/31/2005 | 12/19/2005 | ML05356033 | <strong>Reactor Scram from Main Turbine Trip During Switching Operation</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2005, while Unit 3 was in steady state operation at 100% power, a main turbine trip and resultant reactor scram occurred. At the time, operators were in the process of returning 500-kV switchyard Bus-2, Section 2 to service using a switching order. When the Power Circuit Breaker (PCB) to the 500-kV Trinity 2 transmission line was closed, the PCB immediately tripped back open. The post-scram investigation subsequently determined that this was due to a closed ground switch at an offsite substation on this transmission line. The PCB properly tripped open to clear the Trinity 2 line ground; however, the electrical power transient resulting from the ground and its clearing caused speed perturbations on the Unit 3 main turbine. The rate of speed change seen on the turbine was slightly greater than the maximum rate anticipated by the turbine control system logic and, therefore, the turbine speed feedback signals were designated as invalid by the turbine control logic. With all turbine speed feedback signals designated as invalid, a main turbine trip on loss of speed feedback occurred in accordance with the system design and a reactor scram occurred due to the turbine trip. This event was an uncomplicated plant scram with major plant safety systems responding as expected and in accordance with the plant design. The event cause was that actual turbine speed change exceeded that anticipated as possible by the turbine control logic, causing valid speed signals to be designated as invalid. Additionally, the switching order was deficient in that instructions to open the closed ground switch were in a separate switching order and were not performed. Corrective actions include modifying the Unit 3 turbine control logic and strengthening the process used by the transmission system organization for switching activities.
2982005001 | Cooper Station | 04/15/2005 | 06/14/2005 | ML05171024 | <strong>Reactor Scram due to Reactor Level Transient and Inadvertent Rendering of High Pressure Coolant Injection Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2005 at 0436 Central Daylight Time, from 100 percent power, steady state, Cooper Nuclear Station (CNS) had a feedwater and reactor level transient followed by a low level alarm and scram. Level reached 70 inches below Instrument Zero, all control rods inserted, and reactor pressure was controlled by turbine bypass valves. High pressure coolant injection (HPCI) and reactor core isolation cooling (RCIC) automatically injected. All automatic actuations functioned as required. Level recovered with HPCI and RCIC injecting. After stopping the level drop, HPCI was rendered inoperable by erroneously positioning its auxiliary oil pump switch to PULL-TO-LOCK (PTL) . It was repositioned to AUTO twenty seconds later. Cause of the level transient was a manufacturing deficiency in the installed feedwater master level controller obtained as an equivalent part from a different manufacturer to replace the previous unit. The master controller was replaced with the previous unit. The cause of the operator error was inadequate management of change for a revision to the HPCI operating procedure versus ingrained practice of placing HPCI in PTL. HPCI procedure was enhanced. Additional actions are planned to obtain a spare master level controller and to provide simulator training to operators. CNS started up and returned to power on April 17, 2005.
2982005002 | Cooper Station | 05/16/2005 | 07/11/2005 | ML05199030 | <strong>Technical Specification Prohibited Operation Due to Safety Relief Valve Test Failures</strong><br /><i>Abstract:&nbsp;</i>On May 16 and May 19, 2005, a review of Target Rock safety relief valve (SRV) test data, provided by Wyle Laboratories,determined that three of eight SRV pilot valve assemblies failed to lift within their Technical Specification (TS) lift set point. Specifically, three SRVs with a set point of 1090 +/- 32.7 psig lifted at 1173 psig, 1132 psig and 1127 psig, respectively. The discovery was made as a result of routine TS surveillance testing of pilot valve assemblies removed during Refueling Outage (RFO) 22. Cooper Nuclear Station(CNS) was in Mode 1 at 100 percent power at the time of the determination.The remaining valves tested within their TS lift set point tolerances. Examination determined that sufficient corrosion bonding existed between the SRV pilot valve assembly Stellite 21 discand the pilot valve Stellite 6 in-body seat to cause the SRV pilot valves to lift outside TS set point tolerances. As documented in CNS Licensee Event Report 1999-004-01, this is a recurring problem at CNS and within the industry. The valves were replaced with tested spare valves certified to lift within 1% of set point. This event is considered to have no safety significance from a probabilistic safety assessment risk evaluation standpoint. This event does not create a core damage scenario. There is no change to the CNS core damage frequency or the large early release frequency. This condition also has no impact on the reactor pressure vessel pressure relief function capability. Even under postulated failure conditions, there is no associated risk increase to the plant.
2982005003 | Cooper Station | 06/21/2005 | 08/17/2005 | ML05235019 | <strong>Both Diesel Generators Inoperable in Mode 4 Leads to Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 6/21/2005 in Mode 1 at 100 percent power, CNS determined the Diesel Generator (DG) Diesel Oil (DC) transfer pump in-service test (IST) flow test performed on 11/5/2004 while in Mode 4 resulted in a condition prohibited by Technical Specifications (TS) Revision 16 of the surveillance procedure dated 5/14/2004 allowed quarterly exercising of the two normally closed manual cross connects between Fuel Tanks 1 and 2 by disabling fuel transfer pumps (from the main storage tank to the day tank) by placing their switches to the OFF position and then validating cross-connect valve operation. The surveillance was performed on 7/13/2004 and 10/7/2004 in Mode 1, and on 11/5/2004 in Mode 4, without declaring both DG's inoperable. On 12/30/2004, prior to the fourth surveillance performance, operators recognized that steps to place the transfer pump switches to OFF required declaring both DG's inoperable. The procedure was revised to avoid placing both transfer pump switches to OFF, and the surveillance was subsequently performed . A Condition Report (CR) was initiated for the inadequate procedure and noted the 3 prior surveillances . In all 3 cases, there was no loss of safety function. For July and October, the surveillances were completed within the 2 hour TS action limit for Mode 1 which satisfied the TS requirement. However, for November, the TS "immediate" action limit for Mode 4 was exceeded which resulted in a condition prohibited by TS. The root cause was that Revision 16 of the surveillance procedure was inadequate in that it did not require or caution that performing procedure steps would render both DG's inoperable. The surveillance procedure was revised on 1/22/2005 to correct the inadequacy.
2982005004 | Cooper Station | 09/23/2005 | 11/17/2005 | ML05326042 | <strong>Loss of Condenser Vacuum Due to Failed Drain Line Results in Manual Scram</strong><br /><i>Abstract:&nbsp;</i>On September 23, 2005, at 0022, Operations noted condenser vacuum degrading and Steam Jet Air Ejector air flow rising. The decline occurred after starting a backwash of Condenser B-2 Waterbox. Operations performed actions per Abnormal Procedures,and reduced power. Condenser vacuum continued to decline. By 0040, condenser vacuum had dropped to 23.1 inches of Mercury. The minimum acceptable value for vacuum is 23 inches of Mercury. Operators manually scrammed the reactor due to degrading condenser vacuum which was caused by significant air in leakage. The air leak was through a turbine bearing slop (waste oil and water) drain line that failed due to high-cycle fatigue. Inadequate support of slop drain lines in the Main Condenser led to piping vibration induced by Low Pressure (LP) Turbine exhaust steam flow. An evaluation of plant response determined that all control rods were fully inserted, and systems controlling reactor pressure and level responded as designed. Condenser vacuum was maintained to support Bypass Valve operation during the event. The interim corrective action to address the Root Cause was to remove the slop drain lines from the condenser and to plug the condenser penetration holes. This was completed prior to unit restart.
2982005005 | Cooper Station | 11/16/2005 | 01/11/2006 | ML06017032 | <strong>High Pressure Coolant Injection Valve Control Power Fuse Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>At 0422 Central Daylight Time (CDT) on November 16, 2005, a Control Room Operator identified that both position indicating lights for the normally closed High Pressure Coolant Injection (HPCI) Injection Valve were not illuminated. Indication could not be restored by bulb replacement or verified locally at the starter rack. This resulted in the HPCI Pump being declared inoperable. Trouble shooting by maintenance personnel determined that the fuse (Bussman type FRN-R-1) installed on positive portion of the 125 Volt Direct Current (VDC) valve control circuit was open. Both HPCI control power positive and negative side fuses were replaced with new fuses, circuit integrity was validated, and operability of the valve was verified. HPCI was returned to operable at 1055 CDT on November 16, 2005. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident." The cause of the event was determined to be an intermittent over current condition in the control circuit and/or fuse weakness due to voids in the solder and poor wetting of the solder. Corrective actions to address causes include replacement and analysis of fuses with the same manufacture and date code, monitoring of the control power circuit current to validate normal operation, and replacement and analysis of the closed indicating light socket for the HPCI Injection Valve.
3012005001 | Point Beach 2 | 04/20/2005 | 06/20/2005 | ML05182033 | <strong>Main Steam Safety Valve 2MS-02008 Lift Set Point Exceeds Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>This report describes the discovery during routine Technical Specification (TS) surveillance testing that one main steam safety valve (MSSV), 2MS-02008, had a lift set point that exceeded the licensee's acceptance criteria. The lift set point for 2MS-02008 also exceeded the ASME OM Code 1995 Edition, 1996 Addenda acceptance criteria . No conclusive cause for the test failure has yet been determined. This valve was last refurbished on November 3, 2000. Four as-left set-pressure tests performed following valve refurbishment all passed the Licensee's acceptance criterion of 1125 psig 1%. These type valves are tested off site at A vendor facility using full pressure boiler testing. PBNP TS Surveillance Requirement (SR) 3.7.1.1 requires MSSV testing in accordance with the 1ST program. The Inservice Testing (1ST) program requires scope expansion if the set point test is failed. This scope expansion resulted in two additional MSSVs being sent offsite for testing . The lift set points for all other MSSVs tested were found to be acceptable.
3022005001 | Crystal River 3 | 01/27/2005 | 03/23/2005 | ML05091011 | <strong>Design Change Creates Engineered Safeguards Bus Protective Relay Scheme Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>At 18:30, on January 27, 2005, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. A non-emergency eight-hour notification was made to the NRC Operations Center under 10CFR50.72(b)(3)(ii)(B) to report a design configuration subject to a single failure that could prevent both onsite and both offsite power sources from supplying power to their respective 4160 volt Engineered Safeguards buses. This condition was identified by NRC inspection personnel during the NRC Triennial Fire Protection Inspection. No failure modes effects analysis was performed during the design change process in effect at the time the Offsite Power Transformer and Back-up Engineered Safeguards Transformer were installed in 1990 and 1993, respectively. Also, inadequate technical rigor was exercised during the design, verification, and acceptance of the modification packages developed by the Architect Engineer. Modifications to remove the single failure vulnerability have been implemented. This report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(B) and 10CFR50.73(a)(2)(ix)(A). This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported.
3022005002 | Crystal River 3 | 03/23/2005 | 05/16/2005 | ML05144037 | <strong>Emergency Diesel Generator Inoperable due to Fuel Oil Header Check Valves Leaking Past Their Seats</strong><br /><i>Abstract:&nbsp;</i>At 14:16, on March 23, 2005, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE1 (POWER OPERATION) at 100 percent RATED THERMAL POWER. During performance of surveillance procedure SP-354A, "Monthly Functional Test of the Emergency Diesel Generator EGDG-1A," EGDG-1A did not achieve steady state voltage and frequency in less than or equal to 10 seconds from standby conditions as required by Technical Specifications. The cause for this event was a loss of fuel oil header prime due to leakage past diesel fuel header check valves DFV-39 and DFV-61. Contributing to the event was an inadequate fuel oil header design in which the fuel oil header is the system high point. These conditions allowed fuel oil to gradually drain back through the header to the diesel fuel oil day tank, partially depleting the fuel oil header prime. The check valves were replaced with a new design check valve. Based on engineering judgment, EGDG-1A was inoperable for a period of time longer than allowed by Technical Specifications. This condition is being reported under 10CFR50.73(a)(2)(i)(B) as condition prohibited by Technical Specifications. This condition does not represent a reduction in the public health and safety. A similar occurrence was reported in LER 50-302/2004-002-00 on June 21, 2004.
3022005003 | Crystal River 3 | 10/29/2005 | 11/30/2005 | ML05342036 | <strong>Manual Reactor Trip and Subsequent Emergency Feedwater Actuation due to Condensate Pump Loss</strong><br /><i>Abstract:&nbsp;</i>At approximately 01:26, on October 29, 2005, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE 1 (POWER OPERATION) at approximately sixteen percent RATED THERMAL POWER when a manual reactor trip was initiated in anticipation of an Emergency Feedwater System actuation. The plant was being shutdown for a refueling outage when the only operating Condensate Pump motor tripped on electrical overload and resulted in a loss of both Underwater Pumps. The second Condensate Pump had been shutdown by procedure and removed from service for maintenance. The cause for loss of the operating Condensate Pump was insufficient guidance and information available to the Reactor Operators to prevent operation at critical speeds. The Condensate Pump motor/magnetic coupling/pump assembly has been replaced. Procedural guidance is being developed to ensure operation at critical speeds is avoided. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A). The Reactor Protection System and Emergency Feedwater System performed as designed. This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported to the NRC.
3022005004 | Crystal River 3 | 10/28/2005 | 12/14/2005 | ML05355036 | <strong>Motor-Operated Main Feedwater Isolation Valve Inoperable due to Motor Rotor Oxidation/Corrosion</strong><br /><i>Abstract:&nbsp;</i>At 19:10, on October 28, 2005, Progress Energy Florida, Inc., Crystal River Unit 3, was in MODE 1 (POWER OPERATION) at 51 percent RATED THERMAL POWER when the breaker for a B Train motor-operated Main Feedwater Isolation Valve motor tripped soon after the valve started cycling closed. This occurred during power reduction in preparation for a refueling outage. Technical Specification 3.7.3 requires two Main Feedwater Isolation Valves in each Feedwater System flow path to be operable with at least one Main Feedwater Isolation Valve capable of isolating Feedwater within the required isolation time while in MODES 1, 2 and 3. The Main Feedwater Isolation Valve was determined to be inoperable for a period longer than allowed by Technical Specifications. The cause for the motor-operated valve failure was oxidation/corrosion of the motor rotor magnesium fans and shorting ring. The motor-operated valve motor has been replaced. Other motor-operated valve motors have been found with rotor magnesium and shorting ring damage. This report is being submitted pursuant to 10CFR50.73(a)(2)(i)(B). The redundant Main Feedwater Isolation Valves were operable. This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported.
3022005005 | Crystal River 3 | 11/14/2005 | 01/11/2006 | ML06019051 | <strong>Inadvertent B Train Engineered Safeguards Actuation due to Inadequate Procedure Guidance</strong><br /><i>Abstract:&nbsp;</i>At 05:34, on November 14, 2005, Progress Energy Florida, Inc., Crystal River Unit 3 was operating in MODE 6 (REFUELING) at zero (0) percent RATED THERMAL POWER when an inadvertent Engineered Safeguards actuation occurred while restoring power following a planned electrical bus outage. The actuation caused the automatic start of the B Train Emergency Diesel Generator, Emergency Nuclear Service Seawater Pump, Emergency Nuclear Services Closed Cycle Cooling Pump and Decay Heat Closed Cycle Cooling Fan. All remaining equipment that would normally be actuated from this signal was removed from service due to the current refueling outage conditions and was unaffected. The cause for this event was inadequate guidance in the shutdown procedures for removal of the Engineered Safeguards System from service. The guidance only required the system to be placed in "bypass" which did not disable the system actuation in all conditions. Successful recovery from the actuation was achieved. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A). The equipment that was available operated as designed. There were no equipment failures or damage as a result of the inadvertent actuation. This condition does not represent a reduction in the public health and safety. No previous similar occurrences have been reported.
3052005001 | Kewaunee | 01/31/2005 | 04/01/2005 | ML05144029 | <strong>Reactor Thermal Power Eight-Hour Average Limit Exceeded</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2005, Kewaunee Nuclear Power Plant was in operation at 100 percent power. Instrument and Control (I&C) personnel were performing two surveillance test activities -- Surveillance Procedure (SP) 47-316A (Channel 1 (Red) Instrument Channel Test) and SP 05A-34C-1 (Feedwater Flow Transmitter Channel 1 (Red) Calibration). At approximately 1200 hours, these surveillances caused the reactor thermal power 1-minute, 15-minute, and 8-hour average indications to become inaccurate. The Control Room operators entered procedure A-CP-46 (Abnormal Plant Process Computer System) to determine appropriate actions. The Alternate Reactor Thermal Output (ARTO) system was being used to monitor reactor power. At approximately 1330 hours, the 1-minute thermal power readings returned to approximately 1772 megawatts thermal (MWth), 100 percent power. Procedure A-CP-46 was exited at approximately 1345 hours, and use of ARTO was stopped. At the time the 8-hour Reactor Thermal Output (RTO) average was viewed as not valid. During shift turnover there was no direction given concerning the expected affect on the 8-hour average. At 1952 hours, the shift performed an 11 gallon dilution to compensate for normal core burn up. At both 2047 hours and at 2057 hours, the RTO 15-minute average PPCS alarm came in at 1773 MWth. This computer annunciator cleared within minutes. As the effects of the earlier l&C surveillances were being dropped from the 8-hour average calculation, indicated 8-hour average power started to increase, resulting in a high power alarm at 2131 hrs. Indicated 8-hour average reactor power peaked at 1772.07 MWth. A 3.4 gallon boration was performed at 2141 hours, and power reduced to less than 1772 MWth at 2216 hours. Management provided insufficient expectations for remaining less than the limit for RTO; therefore Operations routinely operated close to the 8-hour average limit, often exceeding the 15 minute average RTO with no adverse consequences. Corrective actions have been initiated to revise procedures, to change the alarm setpoint for the 8-hour average RTO, and add the 15-minute average RTO to the alarm response procedure. This event is not identified as a Safety System Functional Failure.
3052005002 | Kewaunee | 02/11/2005 | 01/30/2006 | ML06041010 | <strong>Auxiliary Feedwater Pumps Assumed to Fail from Postulated Loss of Primary Water Source - Safe Shutdown and Accident Analysis Assumptions Not Assured - Inadequate Design of Pump Protective Equipment</strong><br /><i>Abstract:&nbsp;</i>On 2/11/2005, while the plant was operating at full power, and while following up on Nuclear Regulatory Commission High Risk Low Margin Pilot Inspection inquiries, engineering personnel discovered that the auxiliary feedwater (AFW) system discharge pressure switches may not operate in time to protect the AF pumps from damage in the event of a loss of condensate storage tank (CST) water caused by a tornado. During a tornado that causes substantial plant equipment damage and a loss of offsite power, the AF pumps are required equipment to conduct a safe plant shutdown. On 2/19/2005, while the plant was operating at full power, during investigative efforts for AFW system operability related to AFW pump protection from a loss of CST water, the potential for a loss of the AFW pumps from a high energy line break (HELB) was discovered. The AFW pumps could be damaged during a feedwater system HELB due to damaged common suction piping. The damaged common piping is postulated to create the same effect on the AFW pumps as the loss of CST inventory. Consequently, the AFW pumps could not be assured to be operable under all postulated design basis HELB event scenarios. As a consequence of the 2/19/2005 discovery, a plant shutdown was completed on 2/20/2005. These events are being reported as a single Licensee Event Report (LER) due to their common system functional loss, their commonality in design cause, and the first event leading to identification of the second event in a short period of time. The direct cause of this event is an inadequate pump protection design. A plant modification was completed that installed a new design of the AFW suction piping system to provide pump protection against failure. A root cause evaluation was completed for these events, identifying further corrective actions. These events are considered to have low to moderate safety significance. This report describes a safety system functional failure.
3052005003 | Kewaunee | 02/20/2005 | 05/23/2005 | ML05152047 | <strong>Inadvertent Reactor Protection Trip While Shutdown - Caused by Procedure Adherence Deficiencies and Inadequate Shift Management Oversight</strong><br /><i>Abstract:&nbsp;</i>On February 20, 2005 while the Kewaunee Nuclear Power Plant (KNPP) was in the Intermediate Shutdown mode, an inadvertent Reactor Protection System (RPS) trip signal was initiated. The RPS signal was initiated when the Lo-Lo Level setpoint (17%) was reached in the "B" Steam Generator (SG). The low level condition occurred while cool-down operations were in progress with SG levels being maintained outside of the normal operating procedure control band. Operating the plant during the cool-down evolution outside of procedure requirements and inadequate Supervisory/Management oversight of overall plant operations caused this event. Corrective actions include the enhancement of procedure use and adherence expectations, with the documentation of these expectations recorded in an existing plant procedure. The Operations crews will be trained and assessed, regarding knowledge of the existing and enhanced procedure use and adherence expectations. Additionally, a simulator exercise will be conducted for each operating crew that reinforces the appropriate behavior required to conduct a plant cool down. The scenario for the simulator exercise will include the obstacles that were encountered during this event. Individual performance issues associated with this event have been addressed. There were no plant or public health and safety consequences to this event. This report does not describe a safety system functional failure.
3052005004 | Kewaunee | 03/15/2005 | 06/09/2006 | ML06171043 | <strong>Safe Shutdown Potentially Challenged by Unanalyzed Internal Flooding Events and Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2005 with the plant in Refueling Shutdown Mode, station personnel determined that the Kewaunee plant design for protection against internal flooding would not ensure that required equipment would be protected from the postulated failure of non-safety related piping in the turbine building. High water level in the turbine building would result in water flowing into certain Engineered Safety Features equipment rooms. Documentation which considers specific flooding events from postulated failures of plant equipment exists, however, a complete internal plant flooding analysis was not developed during or subsequent to the plant's original design. In response to inadequate plant design, physical changes were made to minimize challenges to plant equipment and personnel in combating potential flooding events. Although this LER is not associated with an event resulting in actual flooding of any portion of the plant, the potential for certain piping and tank failures resulting in unacceptable flooding existed. A past operability evaluation has been completed to assess what equipment would have failed during postulated flooding events. The Significance Determination Process assessed the safety consequences and implications for any equipment that would have failed. This condition was determined to be characterized as Yellow. This report describes a safety system functional failure.
3052005005 | Kewaunee | 03/24/2005 | 09/29/2005 | ML05279050 | <strong>Emergency Diesel Generator Exhaust Ductwork Not Adequately Protected from Potential Tornado Winds & Missiles</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2005, with unit in the refueling shutdown condition, a walk-down was being conducted in the Kewaunee Power Station (KPS) Turbine Building, as part of an evaluation of the Turbine Building response to design basis tornado winds. Sections of sheet metal panel siding on the Turbine Building are designed to blowout / blow in due to tornado wind loading, as given in Updated Safety Analysis Report (USAR) Appendix B.However, loss of this siding would expose the Class 3 portion of the A and B Emergency Diesel Generator(EDG) exhaust ductwork to tornado wind loads. The response of the sheet metal panels would be that the ductwork could be subjected to full design basis tornado force. Exposure to tornado winds would likely result in deformation of the ductwork for each EDG. On April 19, 2005, during the evaluation to determine a resolution to the tornado wind EDG ductwork deformation problem, it was determined that the EDG exhaust ductwork was also susceptible to turbine and tornado missiles. Appendix B of the USAR evaluates turbine and tornado missiles for Class 1 portion of the EDG. It does not address how the Class 3 structures and components associated with the EDG could impact its operation if impacted by a missile. Deformation of the EDG exhaust ducts could result in some reduction of EDG capacity, due to postulated increase in exhaust back pressure. The apparent cause relative to this condition is the original design of the plant, which did not take these effects into account. Design Change Request DCR-3582 was completed and it reinforced the guides for the EDG exhaust ducts and reinforced the existing structural steel to carry the guide loads. A probabilistic evaluation of tornado missiles, utilizing the TORMIS computer program, was performed. An evaluation of the effects of turbine missiles on the 'B' EDG exhaust duct was also performed.
3052005006 | Kewaunee | 03/26/2005 | 05/25/2005 | ML05153031 | <strong>Auxiliary Feedwater Pumps Postulated to Fall due to Air Ingestion through Pump Packing</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2005, while the Kewaunee Nuclear Power Plant (KNPP) was in the refueling shutdown mode, Nuclear Management Company, LLC, (NMC) personnel determined a potential may exist for damage to the Auxiliary Feedwater (AFW) pumps due to air ingestion through the pumps' packing glands. A conservative calculation has shown that during certain main steam line break post-accident conditions the pressure in the pump's inlet chamber can be sub-atmospheric for short periods. During those postulated short sub-atmospheric periods cooling and lubrication of the pump's packing would stop, air may flow through the packing and into the inlet chamber, potentially causing damage to the pump due to air entrainment. Communication with the pump's vendor indicates, "...the pump can handle up to 5% gas by volume without distress. At 20% gas by volume there is a good chance that the pump will lose prime and run gas bound. Seizure of the rotor would then occur almost immediately." Therefore, the potential existed that during certain post-accident conditions the inlet chamber pressure may become sub-atmospheric, which may cause sufficient damage to the pump's packing to allow air ingestion in to the pump, which may reach 20% where there is a good chance for the pump to lose prime and be damaged. This event report does not constitute a safety system functional failure as this failure was found during the evaluation of the failure documented in KNPP LER 2005-002-00.
3052005007 | Kewaunee | 03/28/2005 | 05/27/2005 | ML05154004 | <strong>Unanalyzed Condition: Design Deficiency - Component Cooling Water System Inoperable Due to Pump "Run Out" Conditions</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2005 with the plant in Refueling Shutdown Mode, a past operability concern was identified with the plant's Component Cooling Water System. Specifically, on January 23, 2002, plant personnel identified a potential "run out" concern with the Component Cooling Water pumps. The condition assumed Component Cooling Water being aligned to both Residual Heat Removal heat exchangers and both Component Cooling Water pumps running. If a loss of power caused the loss of one Component Cooling Water train and the associated train's isolation valve to the Residual Heat Removal heat exchanger could not be closed, there would be a potential concern with pump "run out" and pump damage for the Component Cooling Water pump that continued to run. The plant's original design did not preclude the Component Cooling Water pump "run out" condition. There were no safety significant issues involved with this event. Plant design changes were implemented to alleviate the Component Cooling Water pump "run out" concern. No further corrective actions are necessary. This report involves a safety system functional failure.
3052005008 | Kewaunee | 04/20/2005 | 11/09/2005 | ML05321018 | <strong>Turbine-Driven Auxiliary Feedwater Pump Inoperable Due to Insufficient Net Positive Suction Head</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2005, with the plant in refueling shutdown mode, it was determined that the turbine-driven auxiliary feedwater pump would have been rendered inoperable due to insufficient net positive suction head following a postulated main steam line break event. Consequently, for greater than the past three years, plant Technical Specifications have not been met for having the turbine-driven auxiliary feedwater train operable with the reactor coolant system heated >350 degrees F. This is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The cause of the occurrence is an original system design error. Previous calculations and testing that were performed for auxiliary feedwater system response to a main steamline break event were focused on ensuring that adequate auxiliary feedwater flow would be provided by the turbine-driven AFW pump without due consideration of all suction head parameter concerns. Auxiliary feedwater system changes, including suction pressure protection, revised discharge pressure switch settings, and procedure changes were completed to compensate for the design deficiency. This occurrence is deemed to have very low risk significance and does not constitute a safety system functional failure.
3052005010 | Kewaunee | 06/18/2005 | 08/16/2005 | ML06214044 | <strong>Inadequate Engineering Analysis to Support Service Water Pump Operability</strong><br /><i>Abstract:&nbsp;</i>On June 18, 2005, with the Kewaunee Power Station in refueling shutdown mode, it was determined that the manual actions necessary to support service water pump operability were not supported by engineering analysis. The review of pump operability was prompted by questions from the Nuclear Regulatory Commission (NRC) Senior Resident Inspector. The NRC concerns were with the basis for the time period that the service water pumps could operate without bearing/seal water. This time period was not supported by any vendor documentation. The probable cause of this event is inadequate engineering analysis. A cause evaluation will be performed. Compensatory measures were put in place to ensure operability of the service water pumps. A plant modification will be installed to alert the control room when the service water pumps are switching from the station's equipment water supply to the station's service water supply. Evaluation continues on the existing design of the service water pump bearing/seal water system. A risk significance analysis is being performed. This analysis will determine if this event is a safety system functional failure.
3052005011 | Kewaunee | 06/20/2005 | 08/18/2005 | ML05238026 | <strong>The Setting of a Permissive (P-10) in the Power Range Channels of the Nuclear Instrumentation System was Outside of Plant Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2005, with the station in refueling shutdown mode, it was determined that the setting for Permissive P-10 did not match the Technical Specification (TS) requirement of TS Table TS 3.5-2. An initial investigation into the cause of this event identified that the station Technical Specification is not aligned with the basis for the reactor protection permissive. On June 20, 2005 a Reactor Protection System Engineer questioned the station setting for P-10 compared to the TS requirements. The subsequent review determined that the station setting and the TS did not match. Corrective actions completed include revising the settings of P-10 to match the requirements of Table TS 3.5-2 and an evaluation of the past acceptability and effect of P-10 not meeting TS requirements. Corrective actions to be completed include revising the Nuclear Power Range Channel Calibration surveillance procedures for the current P-10 set/reset values and revising the training material to refer to the current P-10 settings. This occurrence is deemed to have no safety significance and does not constitute a safety system functional failure.
3052005012 | Kewaunee | 06/10/2005 | 09/01/2006 | ML06256004 | <strong>Residual Heat Removal Pump Run-out Upon Loss of Instrument Air While Aligned for Sump Recirculation</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2005 with the Kewaunee Power Station in refueling shutdown mode, a possible run-out condition of the residual heat removal (RHR) pumps was identified. The possible run-out condition exists upon loss of instrument air (IA) to the RHR flow control valves (RHR-8A (B)). These flow control valves are fail-open air operated valves that are not supplied by a safety related IA source. This issue would have been a concern if the internal containment spray (ICS) pump operation would be required during the post loss of coolant accident (LOCA) containment sump recirculation phase. This is reportable in accordance with 10 CFR 50.73(a)(2)(vii) as a condition causing one independent train in multiple systems to become inoperable. The cause of this condition is inadequate consideration of component failure modes for the accident scenario of RHR supplying ICS while in containment sump recirculation. This resulted in a failure to recognize the consequences of the RHR-8A (B) valve failing open while ICS is being supplied from RHR during containment sump recirculation. Station procedures were revised to prevent aligning RHR to ICS for all design basis events. This report does not involve a safety system functional failure.
3052005013 | Kewaunee | 07/13/2005 | 09/11/2005 | ML05258022 | <strong>The Throttle Valves to the Turbine Bearing Oil Coolers for the Turbine Driven AFW Pump Could be Blocked by Debris</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2005, while the plant was operating at full power, it was determined that a reportable condition existed for an extended period. Valves throttled to the turbine driven auxiliary feedwater pump turbine bearing coolers could potentially plug from service water (Lake Michigan) debris if the system were aligned to service water. The service water system has strainers that strain larger than 0.125 inch debris from the service water. The turbine bearing cooler supply valves were throttled such that the clearances through the valves were less than 0.125 inches. If the service water system was lined up to the auxiliary feedwater system to feed the steam generators, cooling to the turbine driven auxiliary feedwater pump turbine bearing oil coolers could be lost due to plugging of the throttled valves from service water debris. There was very low risk significance associated with this event. A plant design change was implemented to reroute the auxiliary feedwater pump lubrication flow paths which included calculations to define the valve minimum throttle position when using service water. No further corrective actions are necessary. This report does not describe a safety system functional failure.
3052005014 | Kewaunee | 06/06/2005 | 10/10/2005 | ML05292005 | <strong>Technical Specification LCO Not Entered for Diesel Generators Inoperable While In Refueling Shutdown</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2005 with the unit in refueling shutdown mode, it was identified that Technical Specification (TS)operability was not applied correctly for the impact of tornado missiles and wind on Emergency Diesel Generator(EDG) equipment. It was not recognized that one train of EDG equipment was required to support the Residual Heat Removal system (RHR) whenever the RHR system is required to be operable. Evaluations that were performed revealed tornado impacts on various EDG components could render the EDGs inoperable. At that time the RHR system should have been declared inoperable and a Limiting Condition for Operation entered.The initial operability concern was identified on March 24, 2005 for the EDG engine exhaust ductwork. On this date the EDGs were determined to be capable of starting and assuming bus loads. It was also determined that they were not required to be operable during the station's current plant mode of refueling shutdown. The cause of this event was a misinterpretation of TS for auxiliary electrical systems during specific plant modes. Once the EDGs were determined to be inoperable, both RHR trains should have been declared inoperable. The RHR trains were available providing decay heat removal and the EDGs were available as a support system for RHR.This occurrence does not constitute a safety system functional failure.
3052005015 | Kewaunee | 09/18/2005 | 11/16/2005 | ML05329016 | <strong>Both Trains of Component Cooling Water Inoperable During Shifting of Running Equipment</strong><br /><i>Abstract:&nbsp;</i>On Sunday, September 18, 2005 while the plant was operating at full power, "Diesel Generator 'A' Availability Test" was being performed in conjunction with the "Bi-Monthly Rotation of Running Equipment." This diesel generator test (not normally run on Sunday) was scheduled from 0700 -1359. Shifting of running equipment is routinely scheduled every 1st and 3rd Sunday of the month. At 0709, as part of the diesel generator test, 'A' Diesel generator was declared inoperable and was restored to an operable status at 1345. In parallel, Operations proceeded through the normal component cooling water (CCW) operating procedure for shifting running equipment with peer checking by the Unit Supervisor. 'B' CCW pump discharge valve CC-4B was closed and the 'B' CCW pump was stopped. CC-4B was then reopened per procedure at approximately 0915.Total duration at which the pump discharge valve was closed is estimated to be approximately 3 minutes.Closure of the pump discharge valve CC-4B rendered the 'B' CCW pump inoperable. The 'A' CCW pump became inoperable when the redundant piece of equipment (B' CCW pump) was inoperable with the 'A' diesel generator (emergency power supply for 'A' CCW pump) inoperable for testing. Opening of CC-4B returned both the 'A' and 'B' CCW pumps to operable status. The cause of this event has been determined to be inadequate procedural guidance. Procedure revisions to the normal operating procedures will be performed. This event is considered a Safety System Functional Failure. Both trains of CCW were inoperable which could have prevented the fulfillment of the residual heat removal safety function and mitigating the consequences of an accident safety function.
3052005016 | Kewaunee | 11/28/2005 | 02/10/2006 | ML06053037 | <strong>Automatic Reactor Trip due to Main Feedwater Pump Motor Failure</strong><br /><i>Abstract:&nbsp;</i>On November 28, 2005 at 2219 central standard time (CST), while the plant was operating at 100 percent power with no abnormal indications, the 'B' main feedwater pump tripped on a bus 2 feeder breaker trip (overcurrent trip on a 4160 volt bus). During the transient, 'B' steam generator reached its low-low level setpoint actuating a reactor protection system reactor trip at 2220 CST. All systems responded as designed. Subsequent inspection of the 'B' main feedwater pump identified a short to ground in all three phases of the motor. This event was reported as a non-emergency in accordance with 10 CFR 50.72(b)(2)(iv)(B) for actuation of the reactor protection system when the reactor is critical and 10 CFR 50.72(b)(3)(iv)(A) for valid actuation of the auxiliary feedwater system. Since all safety systems operated as expected, this event is considered to have negligible safety significance. This is not considered a safety system functional failure. The 'B' main feedwater pump motor was replaced and the reactor startup was completed on November 29, 2005 at 2236 CST with the plant output breaker being closed on November 30, 2005 at 0335 CST. Full power was reached on December 2, 2005 at 1938 CST.
3062005001 | Prairie Island 2 | 03/30/2005 | 05/31/2005 | ML05159010 | <strong>Unit 2 Shutdown Required by Technical Specifications Due to Two Trains of Containment Cooling Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2005 a Corrective Action Process (CAP) item identified potential non-code repairs had been made to 21, 22, and 23 Containment Fan Coil Units (CFCUs) since January 2005. The repair performed was an overlay described as filling a pinhole leak with brazing material in the copper tubing of the CFCU. This repair may not have removed the flaw and was not done in accordance with a code approved weld repair procedure. An Operability Recommendation performed by Engineering examined the qualifications of the repair techniques utilized on previous Unit 2 CFCU leakage events and concluded that while the structural integrity could be assured the repair constituted a non-code repair. Temporary non-code repairs are not acceptable, per NRC Generic Letter 90-05, without prior NRC approval. This conclusion resulted in 3 of the 4 CFCUs, being declared inoperable and required Unit 2 to be shutdown per Technical Specifications until code repairs were completed. Code repair of the 21, 22, and 23 CFCUs were completed on April 3, 2005.
3062005002 | Prairie Island 2 | 04/15/2005 | 10/31/2005 | ML05305016 | <strong>Unit 2 Shutdown Required by Technical Specifications due to Inoperable Emergency Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2005, the Train A Unit 2 Emergency Diesel Generator (D5) was removed from service for a monthly slow start test. At approximately 0830 CDT the test was halted on indications of high crankcase pressure on Engine 2 (D5 is a tandem engine generator). The test procedure specifies shutting down the diesel generator (DG) if crankcase pressure exceeds 30mm for more than a few minutes (the setpoint for the crankcase pressure trip is 52 mm). During the test crankcase pressure increased to 48 mm and D5 was unloaded early per the procedure. With D5 inoperable, Technical Specification 3.8.1 (AC Sources - Operating), Required Action B.4, requires returning the inoperable diesel generator to operable status within seven days. A troubleshooting plan was initiated and actions were taken to diagnose and return D5 to operable status. An assessment of the scope of work to return D5 to operable status and the schedule for completing the work indicated that repairs could not be completed within the 7 days allowed outage time. Based on this assessment an orderly shutdown of Unit2 was initiated on April 15, 2005. Unit 2 entered Mode 5 (Cold Shutdown) on April 17, 2005. D5 engines were rebuilt and D5 was declared operable and returned to service on April 25, 2005.
3062005003 | Prairie Island 2 | 02/11/2005 | 07/08/2005 | ML05189037 | <strong>Declaring Train of Containment Cooling Operable with One Fan Cooler Isolated Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2005, Nuclear Management Company, LLC, (NMC) Staff identified leaks in the 22 and 23 containment fan coil units (CFCUs). Since 22 CFCU is Train B containment cooling and 23 CFCU is Train A Containment cooling, both trains of containment cooling were declared inoperable. Since Technical Specification (TS) 3.6.5 contains no condition for two trains of containment cooling inoperable, TS Limiting Condition for Operation (LCO) 3.0.3 was entered. NMC staff completed an evaluation that determined 21 CFCU (by itself) could perform the required safety function for Train A of containment cooling and declared Train A operable and exited LCO 3.0.3. 22 and 23 CFCUs were isolated (in order to exit TS 3.6.1, Containment) and subsequently repaired with Unit 2 at power. NRC Inspection Report 2005-003 (received by NMC on May 11, 2005) concluded that this action constituted a violation because TS Surveillance Requirements (SRs) 3.6.5.2 and 3.6.5.3 could not be met for the train with 23 CFCU isolated, thus, TS LCO 3.0.3 was improperly exited. Since this resulted in a violation, it is required to be reported per 10 CFR 50.73(a)(2)(i)(B).
3112005001 | Salem 2 | 03/24/2005 | 05/23/2005 | ML05152046 | <strong>ECCS Leakage Outside Containment Exceeds Dose Analysis Limits (23 Charging Pump)</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2005 at 2015, during a routine surveillance to determine Reactor Coolant System (RCS) leakage, a licensed Reactor Operator (RO) observed a decreasing Volume Control Tank (VCT) level corresponding to RCS leakage of approximately 0.5 gpm. It was determined that the initiation time for the indicated leak corresponded to the opening of the Chemical and Volume Control System (CVCS) cross tie valve (2CV462) used to fill and vent the 23 CVCS Positive Displacement pump (PDP) upon restoration following maintenance. Valve 2CV462 was closed and the leakage back to the Refueling Water Storage Tank (RWST) was terminated. The event was caused by the failure to perform an in-depth review of the known leakage of the PDP manual discharge valve 2CV64 and its impact on leakage outside containment. Corrective actions include a change to the Operations work-week procedures to ensure ECCS leakage work/tags are properly identified in the schedule and reviewed, and evaluating the addition of the CV462 valves as RCS Boundary valve with appropriate IST requirements. This event is reportable in accordance with 10CFR50.73(a)(2)(v), "any event or condition that could have prevented the fulfillment of the safety function of structures or system that are needed to:...(C) control the release of radioactive material; or (D) mitigate the consequences of an accident."
3112005002 | Salem 2 | 04/04/2005 | 06/03/2005 | ML05165034 | <strong>Reactor Coolant Instrument Line Through-Wall Leak</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2005, during a Boric Acid program field walkdown, an accumulation of boric acid was identified on 3/8-inch instrument tubing, low-pressure side, associated with 21 Reactor Coolant Pump (RCP) flow transmitter 2FT416. The 2FT416 instrument tubing line was field examined in an effort to assess structural integrity of the tube. The low-pressure tubing was found to possess an accumulation of crystallized dried boric acid, which indicates that the leak was relatively new. The boric acid was removed. A tubing tray pressure plate restraint was then removed, revealing a corrosion point spot. The removed pressure plate had evidence of corrosion at the same location as the corroded point spot on the tubing. Extensive walkdowns of instrumentation tubing in containment revealed evidence of additional instrumentation tube leakage. Corrective actions included replacement of instrumentation tubing, tightening loose fittings, swiping, sampling and cleaning, as necessary. This event is reportable in accordance with 10CFR50.73(a)(2)(ii), "Any event or condition that resulted in: (A) The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded".
3112005004 | Salem 2 | 06/15/2005 | 08/15/2005 | ML05236023 | <strong>Operation in a Condition Prohibited by Technical Specification-Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On June 15 and June 17, 2005 Salem Generating Station identified two containment isolation valves (CIVs) that did not have the required post maintenance testing performed following corrective maintenance. This was discovered during an extent of condition investigation for a related issue regarding post-maintenance testing of valves. Because of their particular system location and configuration these valves could not be retested in their as-found condition.The valves were declared inoperable and the appropriate Technical Specification actions were taken. The apparent cause of this event was the failure of the Maintenance Planning organization to incorporate a leak rate testing (LLRT) activity into the work order after the scope of the order had become defined. A contributing cause of this event was these activities were handled as WIN (Work IT Now) activities. Planned corrective actions are to perform the LLRT in the fall 2006 refueling outage. In the interim the flow path is isolated per TS 3.6.3 action statements. The procedure used by planners has been revised to include an activity for the in-service testing group (IST) to assist with determining work instructions and post maintenance testing requirements. The procedure used by the WIN team and the procedure used by the planning department will be combined. This report is being made in accordance with 10CFR50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications ..."
3132005001 | Arkansas 1 | 10/13/2005 | 12/12/2005 | ML05361016 | <strong>Movement of Irradiated Fuel Assemblies in the Reactor Building with Reactor Building Purge Effluent Monitor Inoperable and Purge Isolation Valves Open Resulted in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2005, during a scheduled refueling outage, with fuel offload in progress, super particulate iodine noble gas (SPING) effluent monitor, SPING-1, was removed from service for required surveillance testing. Operations personnel failed to recognize that Technical Specifications (TS) require SPING-1 to be operable when the reactor building purge isolation valves are open and fuel movement is in progress in the reactor building. Sampling was performed and SPING-1 was returned to service. On October 14, 2005, prior to removing SPING-1 from service again for sampling, operations personnel recognized that this configuration was not allowed with fuel movement in progress in the reactor building and realized that the removal of SPING-1 from service the previous day resulted in operation prohibited by TS. This event can be attributed to inadequate guidance regarding the TS requirement to maintain SPING-1 operability during fuel movement in the reactor building. Procedures will be revised to ensure SPING-1 is not removed from service during fuel handling operations in the reactor building unless TS requirements are satisfied.
3132005002 | Arkansas 1 | 12/01/2005 | 01/27/2006 | ML06038052 | <strong>Movement of Irradiated Fuel Assemblies with One Channel of Source Range Nuclear Instrumentation Inoperable due to a Power Supply Failure Resulted in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 2134 on December 1, 2005, during reactor core reload activities, operators identified that source range nuclear instrumentation channel NI-0502 was inoperable. The reload sequence had begun with the loading of four twice-burned fuel assemblies. As the fourth assembly was placed near NI-0501, operators noticed a disparity between the two source range channels. When the second fuel assembly was placed close to NI-0501, its indication increased to approximately 0.12 cps, whereas NI-0502 indicated approximately 0.04 cps with two assemblies close to it. Upon identification of the disparity, core alterations were immediately secured. The source range channel failed due to failure of its high voltage power supply. Prior to resumption of reload activities, the failed power supply was replaced and the channel was proven operable. The source range instrumentation design does not provide sufficient continuous functional monitoring capability for detection and annunciation of a channel failure during core alterations when indicated count rates are at the extreme low end of the scale. However, an alarm inside the source range signal processing drawers does provide indication of power supply failure. The "Control of Unit 1 Refueling" procedure was revised to require inspection of these drawers prior to beginning refueling activities.
3132005003 | Arkansas 1 | 12/26/2005 | 02/24/2006 | ML06067031 | <strong>Reactor Trip due to Automatic Actuation of the Reactor Protection System on Main Turbine Trip and Invalid Actuation of the Emergency Feedwater System</strong><br /><i>Abstract:&nbsp;</i>At 1047 CST, on December 26, 2005, Arkansas Nuclear One, Unit 1 (ANO-1), experienced an automatic actuation of the Reactor Protection System due to a Main Turbine trip caused by low turbine bearing lube oil pressure. The Reactor Protection System performed as designed resulting in a reactor trip from 95 percent power. Analysis of the event has determined that the reduction in turbine bearing lube oil pressure was caused by a failure of the lube oil ejector discharge check valve, LO-79. Subsequent analysis established that a weld failure within the valve internals had caused the disc to separate from the hinge resulting in blockage of lube oil flow. Examination of the failed welds indicated that they were undersized for the applied load. To correct this condition, a replacement valve assembly, meeting original equipment manufacturer design requirements, was installed. Following the reactor trip, a spurious actuation of Emergency Feedwater (EFW) occurred which was caused by an invalid low steam generator level signal generated by the Emergency Feedwater Initiation and Control system. To reduce the likelihood of recurrence of an invalid EFW actuation, a Technical Specification amendment was prepared and implemented upon NRC approval, allowing a reduction of the EFW low steam generator level initiation setpoint and an increase in the low level actuation time delay.
3152005001 | Cook 1 | 04/26/2005 | 06/24/2005 | ML05188007 | <strong>Reactor Trip following Intermediate Range High Flux Signal</strong><br /><i>Abstract:&nbsp;</i>At 0002 hours on April 26, 2005, the Donald C. Cook Nuclear Plant Unit 1 reactor automatically tripped while at 8% reactor power. Preparations were being made to synchronize the main generator with the offsite electrical power grid. The post-trip investigation determined that the trip was caused by an intermediate range high flux reactor trip signal. The intermediate range high flux reactor trip occurred below the reactor protection system actuation normally set at 22% reactor power. This reactor trip has a one-of-two channel trip logic. The trip is interlocked to be active below 10% reactor power. It was determined the cause was a spurious lowering of the trip setpoint due to age-related degradation of the level adjust potentiometer in the circuitry of 1-NRI-35, Nuclear Instrumentation Channel 1 Intermediate Range Neutron Flux Detector. The affected bistable and relay driver assembly, 1-NRI-35-NC35F, for the intermediate range channel 1-NRI-35, was replaced. Additionally, preventive maintenance tasks for periodic replacement of nuclear instrument bistable relay drivers will be developed. All plant systems functioned normally following the reactor trip. The auxiliary feedwater system actuated and performed as expected during this event. This event was reported under event notification system number 41639 per 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A), as a valid reactor trip and actuation of the auxiliary feedwater system, respectively. This LER is being reported per requirements of 10 CFR 50.73(a)(2)(iv)(A).
3152005002 | Cook 1, Cook 2 | 08/30/2005 | 10/28/2005 | ML05312036 | <strong>Failure to Comply with Technical Specification Requirements Pertaining to Undervoltage Protection Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On August 30, 2005, at approximately 1000 hours, it was identified that an equipment clearance implemented to support planned maintenance on the Unit 1 CD Emergency Diesel Generator (EDG) disabled 4 kV Bus loss of voltage relays required by Custom Technical Specification (CTS) 3.3.2.1, "Engineered Safety Features Actuation System Instrumentation." The equipment clearance was placed and the relays de-energized on August 30, 2005, at 0813 hours. The relays were restored at approximately 1011 hours on August 30, 2005. The relays were required to be operable per CTS 3.3.2.1, Table 3.3-3, Item 6b and 8a, "4 kV Bus Loss of Voltage," associated with the Motor Driven Auxiliary Feedwater Pumps and Loss of Power functional units, respectively. The CTS required three channels per bus, with a minimum of two channels per bus operable. In the configuration rendered by the equipment clearance, all three undervoltage relays were de-energized. There was no CTS action stated for this configuration, which would have required entry in to CTS 3.0.3. However, this condition was not recognized. This configuration did not meet the requirement of the CTS, and therefore is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operational condition prohibited by the plant's CTS. The cause of this condition was a failure to assure CTS requirements were met prior to removing the equipment from service. Corrective actions will provide additional information within the equipment clearance software to prompt clearance reviewers of the technical specification impact of de-energizing the circuit and reviewing existing EDG clearances that de-energize circuit 2 of distribution panels TDAB or TDCD, for either unit, to clearly identify technical specification requirements and prevent use of the equipment clearances when the relays are required to be operable.
3162005001 | Cook 2 | 11/08/2005 | 01/09/2006 | ML06011021 | <strong>Reactor Trip from RCP Bus Undervoltage Signal Complicated by Diesel Generator Output Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>At 0358 hours on November 8, 2005, Donald C. Cook Nuclear Plant Unit 2 experienced an automatic reactor trip due to reactor coolant pump bus undervoltage (UV). The trip resulted from problems with the main generator exciter slip ring brushes which caused a UV condition and tripped the reactor and main turbine. The B train Emergency Diesel Generator (EDG) automatically started and loaded B train emergency bus T21A (one of two B train emergency buses). However, the trip was complicated in that the other B train emergency bus, T21B, failed to energize automatically on the start of the B train EDG. The A train emergency buses transferred to reserve feed as expected. The A train EDG was out of service for scheduled maintenance. An additional anomaly occurred at 0510 hours when the EDG output breaker supplying the T21A bus opened and re-closed after 23 seconds without manual action. The cause of the event was poor brush contact on the exciter rotor. This resulted in a loss of main generator excitation, which caused a UV condition. The root cause was identified as inadequate exciter brush preventive maintenance. Corrective actions taken included repairs to the exciter, and investigation and repair of the B train EDG output breaker failures. This report is made in accordance with 10 CFR 50.73(a)(2)(iv)(A), "any event or condition that results in manual or automatic actuation of any systems listed ...," specifically reactor trip, auxiliary feedwater, and emergency AC electrical power system actuations. This report is also required per 10 CFR 50.73(a)(2)(i)(B), "any operation or condition which was prohibited by the plant's technical specifications." This is due to a latent defect in the EDG output breaker control circuit, revealed during this event, which rendered the EDG inoperable. It is also reported under 10 CFR 50.73(a)(2)(v)(A), as a condition which could have prevented the fulfillment of a safety function, for periods of time (approximately 16 hours in total) when both Unit 2 EDGs were inoperable simultaneously.
3172005001 | Calvert Cliffs 1 | 04/10/2004 | 03/31/2005 | ML05096009 | <strong>Main Feedwater Isolation Valve Inoperability Due to Handswitch Wiring</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2004, with Unit 1 shutdown in Mode 5, the 12 Main Feedwater Isolation Valve, 1-FW-4517-MOV, failed to shut on Steam Generator Isolation Signals (SGIS) during performance of surveillance test procedures . Additional surveillance testing revealed the valve also would not operate upon receipt of a Containment Spray Actuation Signal (CSAS). Investigation and troubleshooting into the cause of the malfunction determined that a lead was terminated at the wrong location on the handswitch for 1-FW-4517-MOV . The handswitch, 1HS4517, is located on Control Panel 1C03 in the Control Room . The improperly wired handswitch caused an open electrical circuit for the 1-FW-4517-MOV SGIS/CSAS functions. The lead was relocated to the proper terminal and subsequent testing of 1-FW-4517-MOV was satisfactorily performed on April 10, 2004. The improperly wired handswitch termination was the result of Human Performance errors, which directly challenged the operability of 1-FW-4517-MOV . Calvert Cliffs Nuclear Power Plant addressed an overall weakness in Human Performance with a site-wide initiative. Procedure changes have also been implemented to allow the use of ring-tongue lugs when performing wire terminations on new or re-worked wiring during maintenance in control panels.
3172005002 | Calvert Cliffs 1 | 03/01/2005 | 05/02/2005 | ML05126022 | <strong>Reactor Scram Due to Main Turbine Vibrations During Power Reduction</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2005 during a planned Unit 1 power reduction to Mode 2 for performance of maintenance on 11 Moisture Separator Reheater drain tank vent line piping, a manual reactor scram was initiated from 15 percent power. An automatic turbine trip followed the manual reactor scram as designed. The reactor was manually scrammed per Abnormal Operating Procedure-7E "Main Turbine Malfunction," when bearing number 5 exceeded 12 mils vibration. The excessive vibration was due to rotor bowing caused by friction heat developed during rotor rubbing. The rubbing most likely developed because the packing to rotor clearances were tight and the steam path was subjected to temperature transients causing shell thermal distortions. Corrective actions include review of previous turbine roll ups/shutdowns for rub levels and rub locations, and incorporating lessons learned from this event into the appropriate operating instruction. The turbine was placed on turning gear during the maintenance outage and was returned to service without problems. The Unit 1 reactor was restarted and paralleled to the grid on March 2, 2005 at 10:30 am.
3172005003 | Calvert Cliffs 1, Calvert Cliffs 2 | 09/12/2005 | 12/14/2005 | ML05354021 | <strong>Overpower Condition Resulting from Non-conservative Flow Correction Factors</strong><br /><i>Abstract:&nbsp;</i>Tracer testing results received on September 12, 2005 indicated that main feedwater flow venturi correction factors calculated using ultrasonic flow meters (UFMs) had been set non-conservatively low. Immediate corrective actions included returning main feedwater flow correction factors on Unit 1 and Unit 2 to (1.000). This effectively removed the UFMs from service. The non-conservative correction factors were installed in July, 2003. Unit 1 and Unit 2 operated at rated thermal power levels of up to 100.4 and 100.74 percent, respectively during this period. The correction factor errors did not represent a failure of any installed components. A root cause for this event was a failure to consider data, within the design basis document, indicating that piping/component configuration could distort flow farther downstream than analyzed. A contributing cause was weak oversight by the vendor in 2004 which prevented earlier detection of the condition. Corrective actions included additional evaluation requirements within the vendor Topical Report and vendor procedure revisions to require independent corroboration of performance prior to commissioning future installations. The maximum analyzed steady state reactor core power levels, of 102 percent of rated thermal power or 2754 MWth, were not exceeded during operation with the non-conservative correction factors installed.
3182005001 | Calvert Cliffs 2 | 02/26/2005 | 04/21/2005 | ML05118001 | <strong>Ultrasonic Testing Identifies Two Alloy 600 Nozzles Requiring Repair</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2005, with Unit 2 in Mode 5, ultrasonic (UT) inspections of the Reactor Coolant System (RCS) Alloy 600 piping penetrations were performed in accordance with the Calvert Cliffs In-Service Inspection Program. As a result of the inspections, two RCS nozzles were identified with indications of flaws requiring disposition. No through wall leakage was detected during the inspections. Both nozzles were determined to have a flaw or flaws that could not be found acceptable under American Society of Mechanical Engineers (ASME) Section XI, IWB-3600. The RCS nozzles requiring repair were the 21 Hot Leg Drain Line and 22A Cold Leg Letdown Line. Evaluation of the nozzles determined repairs were required prior to returning Unit 2 to service. Although the nozzles required repair, the structural integrity of the nozzles was not compromised prior to discovery and repair. Weld overlay repair techniques we reemployed to restore each nozzle to ASME Section XI compliance. Code relief was requested from the Nuclear Regulatory Commission (NRC) to allow final disposition of the resulting configuration. This relief request was verbally approved by NRC via teleconference on March 10, 2005, prior to the restart of Unit 2.
3182005002 | Calvert Cliffs 2 | 03/06/2005 | 05/04/2005 | ML05129006 | <strong>Personnel Air Lock Containment Penetration Closure Requirements Violation</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2005 at 1415, control element assembly coupling activities were commenced following reactor fuel shuffle activities. At that time the Personnel Air Lock (PAL) door interlocks were removed and both PAL doors were open. In this condition the plant's Technical Specifications require the PAL to be capable of being closed by an operable PAL door under administrative control, which require a designated individual available immediately outside the PAL to close the operable door. However, when the control element assembly coupling commenced on March 6, 2005 at 1415 there was no one available immediately outside the PAL specifically designated to close the PAL door. The designated individual had been released from that responsibility at approximately 0630 on March 6, 2005 by the Containment Job Path Manager. The initiating error was failure to contact the Operations Work Control when the PAL watch was secured. The Operations Work Control has ownership and responsibility for containment closure controls. The root cause of this event is not having a formal process for documenting and communicating the transfer from one closure control method to another. Corrective actions include procedure changes to establish a formal process.
3212005001 | Hatch 1 | 06/29/2005 | 08/24/2005 | ML05237043 | <strong>Failure to Use an Appendix J, Option B, Type C Tested Component to Isolate Primary Containment Penetration</strong><br /><i>Abstract:&nbsp;</i>On 7/01/2005 at 1545 ET, Unit 1 was in the Run Mode at an approximate power level of 2793 CMWT (100 percent rated thermal power). At that time, it was determined that on 6/29/2005 a valve used to isolate primary containment during work on component 1P70-N003 (a barrier for primary containment penetration 22) was not tested in accordance with Technical Specification 3.6.1.3 Condition C. This resulted in a condition prohibited by the plant's Technical Specifications. Component 1P70-N003 associated with penetration 22 functions as a single barrier for the penetration and when it is INOPERABLE it is governed by Technical Specification 3.6.1.3 Condition C. The work associated with 1P70-N003 was completed and the clearance associated with the work restored on 6/30/2005 and verified to be leak tight the next day. The controls contained in two procedures associated with this event were determined to be inadequate in that they did not ensure the appropriate personnel reviewed the work package and they did not clearly identify that the safety related containment function for this work activity would be affected. These procedures will be revised to strengthen the controls that were identified as being inadequate during the investigation of this event.
3212005002 | Hatch 1 | 10/29/2005 | 12/21/2005 | ML05356036 | <strong>Main Transformer Failure Causes Turbine Trip and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 10/29/2005 at 1330 EST, Unit 1 was in the Run mode at an approximate power level of 2804 CMWT (100 percent rated thermal power). At that time, the reactor tripped on turbine control and stop valve fast closures. The turbine and generator tripped when the main power transformer experienced a fault which resulted in a main generator neutral ground overcurrent lock-out. Following the reactor scram, water level decreased due to void collapse from the rapid reactor pressure increase, reaching a minimum of approximately sixteen inches below instrument zero (about 142 inches above the top of the active fuel). The decrease in water level resulted in closure of the Group 2 primary containment isolation valves per design. The operating reactor feedwater pump restored level to its design set point. Reactor pressure peaked at approximately 1145 psig, resulting in all eleven main steam safety relief valves opening as designed to reduce pressure. The event was caused by an internal fault in the main power transformer. Heat from the fault resulted in an explosive rupture of the transformer shell at its top edge, and a subsequent fire within the transformer. A Notice of Unusual Event was declared, and the installed fire suppression system along with the on-site fire brigade extinguished the fire. The transformer was replaced, and all systems and components affected by the fire or the transformer fault were inspected and repaired.
3212005003 | Hatch 1 | 11/10/2005 | 09/19/2006 | ML06264001 | <strong>Discrepancy in Special Nuclear Material Inventory</strong><br /><i>Abstract:&nbsp;</i>During a review of Special Nuclear Material (SNM) inventory and accounting records initiated in response to industry events, a licensee-initiated corrective action, and Nuclear Regulatory Commission (NRC) Bulletin 2005-01, it was determined that a discrepancy existed between the amount of spent fuel that exists in the Spent Fuel Pool (SFP) and the amount recorded within the SNM physical inventory records. This was reported as NRC Event Number 42135 on November 10, 2005, pursuant to 10CFR20.2201(a)(1)(ii) and 10CFR50.72(b)(2)(xi). After an extensive review of documentation, a thorough inspection of the SFPs, and an inspection of fuel bundles, Southern Nuclear Operating Company (SNC) has determined that fragments/segments of fuel rods and/or fuel pellets, amounting to approximately 18 inches (in the aggregate) of fuel rod, is unaccounted for. A follow-up notification was made on 8/21/2006, pursuant to 10 CFR20.2201(a)(1)(ii), 10CFR50.72(b)(2)(xi), and 10CFR 74.11. Based on the nature of the fuel rod segments, fragments, pellets, pellet chips, and small particles, and the barrier provided by in-plant radiation monitoring instrumentation, a high degree of confidence exists that the unaccounted for SNM is either still in the SFP, was washed out during reactor operation, or was inadvertently shipped to a licensed low level waste processing facility. Throughout its investigation and review, SNC has identified no evidence to indicate the possibility of theft or diversion of the missing quantity of SNM material. This event was caused by an inadequate procedure which did not require tracking of parts of fuel rods in the SNM inventory. The applicable plant procedure has been revised to prevent the recurrence of this problem.
3232005001 | Diablo Canyon 2, Diablo Canyon 1 | 01/27/2005 | 01/31/2006 | ML06052056 | <strong>TS 3.4.10 Not Met During Pressurizer Safety Valve Surveillance Testing due to Random Lift Spread</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2005, during scheduled testing in accordance with Surveillance Test Procedure M-77, "Safety and Relief Valve Testing," Pacific Gas and Electric Company (PG&E) identified two of three pressurizer safety valves (PSVs) outside the Technical Specification (TS) 3.4.10, "Pressurizer Safety Valves, ... lift setting of >=2460 and <=2510 psig." The as-found lifts were 4.4 and 3.6 percent low, and within analyzed safety limits; thus, this condition did not adversely affect the health and safety of the public. The PSVs were disassembled, inspected, and reset within the TS 3.4.10 lift setting requirements. PG&E believes the cause of the PSVs being outside the TS allowance is random lift spread. PSV lift setting repeatability has been recognized as an industry-wide problem. PG&E has participated in extensive investigative test programs, both jointly with the nuclear steam supply system vendor, Westinghouse Owners Group, and independently. The results of the industry investigations are documented in WCAP-12910, "Pressurizer Safety Valve Set Pressure." PG&E has reanalyzed PSV capability, revised TS 3.4.10 bases, and enhanced the PSV testing procedures consistent with the revised analysis criteria.
3232005002 | Diablo Canyon 2 | 11/19/2005 | 01/18/2006 | ML06031035 | <strong>Unplanned Emergency Diesel Generator Auto-start During Testing due to Personnel Error in Relay Testing</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2005, at 15:51 PST, with Unit 1 in Mode 6 (Refueling) and Unit 2 in Mode 1 (Power Operation), relay testing resulted in a sudden pressure relay trip of the Unit 1 startup transformer (SUT) 1-1, resulting in a loss of startup power to both units. All three Unit 2 Emergency Diesel Generators (EDGs) started as designed. Unit 2 power continued to be supplied from the auxiliary transformers. Unit 1 was unaffected as startup power was cleared for maintenance. At 16:15 PST, Operations cut out the sudden pressure relay on SUT 1-1 and restored 230 kV offsite power to Unit 2. Plant operators made a nonemergency event notification (EN 42157) in accordance with 10 CFR 50.72(b)(3)(iv)(A) at 1721 PST. This event was due to human performance errors in that utility personnel failed to review applicable drawings and take appropriate actions prior to relay testing. Contributing causes included failure to implement testing standards, inconsistent relay work package quality, and inadequate procedural guidance. Corrective actions involve improved training, work order revisions, procedure enhancements,and process simplifications to ensure consistent testing standards are met.
3242005001 | Brunswick 2 | 03/31/2005 | 05/23/2005 | ML05153018 | <strong>Compliance with Single Control Rod Withdrawal-Cold Shutdown Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2005, at approximately 0545 hours, with Unit 2 in day 26 of a refuel outage and operating in Mode 4, operators were dispatched to disarm a five by five array of control rod drives (CRDs) in accordance with the Technical Specification (TS) 3.10.4, "Single Control Rod Withdrawal-Cold Shutdown," to support replacement of a CRD. During the disarming effort, an error was made that resulted in the failure to disarm one of the required CRDs which ultimately resulted in the failure to comply with TS 3.10.4, Required Actions. At 2245 hours, shortly after initiating the CRD replacement activity, the disarming error was discovered. Immediate actions were taken to establish compliance with the TS. The cause of the error is attributed to a procedural deficiency associated with the equipment control process. The failure of the individuals involved with the disarming activity to meet the work standards for equipment control, as established in procedures and through management expectations, is considered a contributing cause. Corrective actions include providing additional process barriers by establishing an interim Standing Instruction to preclude recurrence until a revision to the equipment control procedure can be implemented. In addition, a review of the event with appropriate individuals will be performed. The significance of this occurrence is considered minimal in that no control rod manipulations were made during the time the condition existed that could have affected reactor core shutdown margins.
3242005002 | Brunswick 2 | 04/09/2005 | 06/08/2005 | ML05165023 | <strong>Automatic Shutdown due to Condensate System Transient</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2005, Unit 2 was operating at 65 percent of rated thermal power. At 0049 hours, a Condensate system transient tripped the Condensate Booster Pumps and the running 2B Reactor Feed Pump (RFP). Vessel water level lowered, resulting in an automatic reactor protection system actuation at 0050 hours. Vessel water level was restored with the 2A RFP, the Reactor Core Isolation Cooling system, and Control Rod Drive system flow. All appropriate system isolations and actuations occurred as designed. After the shutdown, Reactor Coolant system (RCS) heat up rates were exceeded; however this was not recognized at the time of occurrence and an engineering evaluation was not performed, per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.9 Required Action A.2, until after Unit 2 had changed operating modes to commence restart and power operation. This is prohibited by TS LCO 3.0.4. The cause of the shutdown was a failure to establish Condensate system flow limitations, which resulted in failure to maintain adequate pressure to the suction of the RFPs. The cause of the failure to evaluate RCS heatup rates prior to mode change was attributed to procedures that were deficient in addressing the operating configuration that occurred after the shutdown. Applicable operating procedures will be revised to provide appropriate guidance. The safety significance of this event is minimal because vessel water level was restored, all appropriate safety system actuations occurred, and the RCS was evaluated as acceptable for continued operation.
3252005001 | Brunswick 1, Brunswick 2 | 04/09/2005 | 06/08/2005 | ML05165023 | <strong>Operation Prohibited by Technical Specification - Inoperable Feedwater and Main Turbine High Water Level Trip</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2005, an anomaly was identified between indicated reactor vessel water level and actual reactor vessel water level for Unit 2. During subsequent investigations, it was determined that the high water level trip instrumentation, required by Technical Specification 3.3.2.2, "Feedwater and Main Turbine High Water Level Trip Instrumentation," had been rendered inoperable by adjustment of a time constant in the Digital Feedwater Control System (DFCS) software. This adjustment was made in April 2003, for Unit 2 and April 2004, for Unit 1. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plants' Technical Specifications. The root cause of this condition is attributed to a lack of a sufficient questioning attitude related to the impact of the software parameter change on all system output responses combined with a lack of detailed knowledge and documentation associated with the DFCS software. Corrective actions include: (1) re-adjustment of the time constant, returning the instrumentation to operable status, (2) development of design configuration data for the DFCS software and (3) review of existing digital software which provide control or interactive functions to ensure design and configuration control of the software are adequate.
3252005002 | Brunswick 1 | 04/15/2005 | 06/14/2005 | ML05172038 | <strong>Reactor Core Isolation Cooling System Manual Actuation During Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2005, at approximately 2200 hours, as part of a pre-planned sequence of events, Unit 1 control room operators manually inserted a Reactor Protection system trip to shut down the reactor from approximately 23 percent of rated thermal power to begin a planned maintenance outage. At 2222 hours, the Reactor Core Isolation Cooling (RCIC) system was manually started to maintain reactor pressure vessel (RPV) coolant level after the 1A and 1B Reactor Feedwater Pumps (RFPs) could not be restarted to maintain level. The RCIC system started and maintained RPV coolant level until the 1A RFP could be returned to service. The cause of the event is attributed to coincident failures of the 1A RFP Minimum Flow Valve and the 1B RFP Suction Valve to reposition upon demand and provide start permissives to the associated RFP start logic. The 1A RFP Minimum Flow Valve was repaired by replacing galled internal parts, most likely caused by the presence of foreign material in the system. Replacement of RFP suction flange gaskets will remove the suspected source of the foreign material. The 1B RFP Suction Valve, a motor-operated gate valve, would not open due to the setting of the open torque switch bypass allowing the open torque switch to stop the motor before the gate could unwedge from its seat. Torque switch bypass adjustment and procedure changes will prevent recurrence. The safety significance of this occurrence is considered minimal.
3252005003 | Brunswick 1 | 04/20/2005 | 06/16/2005 | ML05179019 | <strong>Inappropriate Use of Technical Specification 3.0.5 During Control Rod Manipulations</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2005, Unit 1 was in Mode 5 for a fuel bundle replacement outage. Following completion of maintenance to the position indicating probe (PIP) for control rod 46-15, a PIP position simulator, being used to provide full-in indication to the one-rod-out interlock, was not removed prior to performing single control rod subcriticality testing and operability testing for the control rod. Plant operators determined that performance of single control rod subcriticality testing was a prerequisite for performing operability testing of the control rod. Operators incorrectly used Technical Specification (TS) 3.0.5 to return control rod 46-15 to service before beginning the single control rod subcriticality testing. Following single control rod subcriticality testing for two control rods and encountering problems with the operability testing for control rod 46-15, operators continued to use TS 3.0.5 while performing testing of another control rod. This resulted in a failure to comply with Technical Specification required actions. To prevent recurrence of this event, training on the proper use of TS 3.0.5 will be provided to licensed operators. In addition, enhancements are planned to the plant procedures which govern the installation and removal of PIP jumpers and to plant procedures to prohibit use of the PIP position simulator as a jumper for the one-rod-out interlock.
3252005004 | Brunswick 1, Brunswick 2 | 05/12/2005 | 07/11/2005 | ML05201004 | <strong>Loss of Electrical Power to Emergency Bus E1</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2005, at 0411 hours, with Emergency Diesel Generator (EDG) 1 inoperable for planned maintenance, electrical power was lost to the 4160 VAC Emergency Bus El. As a result of this power loss,Unit 1 Reactor Coolant System Leakage Detection Instrumentation became inoperable, and Unit 1 received Division 1 Primary Containment Isolation system actuations for Groups 2, 3, and 6 isolation valves.Additionally, the redundant control building air compressor did not start, which resulted in inoperable Control Room Air Conditioning (AC) and the Control Room Emergency Ventilation (CREV) systems for Units 1 and 2. The cause of the loss of electrical power to bus El is attributed to a design feature, associated with the EDG control logic, that can result in the reduced reliability of the offsite power source to the Emergency Buses in the event of a particular electrical alignment. The redundant control building air compressor did not start due to a wire lug that had broken and interrupted the control power circuit. The wire lug was replaced and the Control Room AC and CREV systems were returned to service. Electrical power was restored to bus El and additional controls were implemented for the electrical alignment that resulted in the loss of power to bus El. The safety significance of this event is considered minimal.
3252005005 | Brunswick 1 | 07/13/2005 | 09/12/2005 | ML05263037 | <strong>Automatic Reactor Protection System Actuation due to No Load Disconnect Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2005, at 0917 hours, Unit 1 received a Main Turbine trip followed by an automatic Reactor Protection System (RPS) actuation. The cause of the Main Turbine trip was the failure of the B phase of the Main Generator No Load Disconnect Switch (NLDS). Plant systems responded per design. All control rods fully inserted. An expected Reactor Pressure Vessel coolant level shrink resulted in the coolant level decreasing below the Reactor Vessel Water Level - Low Level 1 setpoint, which resulted in appropriate Primary Containment Isolation System (PCIS) isolations. Additionally, coolant level momentarily satisfied the Low Level 2 actuation logic requirements, at which point an additional PCIS isolation occurred and the High Pressure Coolant Injection (HPCI) system initiated but did not inject. Safety/Relief valves B, C, D, and E operated to control pressure. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in valid actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). The root cause of this event is inadequate design and testing of the NLDS by the vendor, resulting in the NLDS not meeting its nameplate design rating. A temporary modification has been installed on both Unit 1 and Unit 2 which replaced the NLDSs with removable bus bars.
3252005006 | Brunswick 1, Brunswick 2 | 08/06/2005 | 09/30/2005 | ML05285027 | <strong>Voluntary Report - Shutdown of Units 1 and 2 Due to Emergency Diesel Generator Operability Concerns</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2005, Units 1 and 2 were shutdown due to operability concerns potentially affecting the site's four Emergency Diesel Generators (EDGs). Unit 1 entered Mode 3 at 0531 hours and Unit 2 entered Mode 3 at 0446 hours. The EDG operability was questioned due to concerns that the setpoint for the installed EDG differential overcurrent protective devices (i.e., 87DP relays) was not appropriate. Subsequently, it was determined that the setpoint for the 87DP relays, while not optimal, did not result in the EDGs being inoperable. As such, reporting of this condition is considered voluntary. The root cause of this event is replacement of the EDG 87DP differential overcurrent relays, in 1982, without adequate confirmation that the trip setting of the new model was appropriate. This reduced the margin between the 87DP relay trip setpoint and the normal operating current, thereby reducing the EDGs' tolerance to electrical disturbances. The existing 87DP relays were replaced with new solid state relays with increased margin to the operating current.
3272005001 | Sequoyah 1 | 04/09/2005 | 06/07/2005 | ML05164031 | <strong>Automatic Reactor Trip Following Loss of Turbine Auto Stop Oil (ASO) Pressure</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2005, at approximately 1111 Eastern daylight time, an automatic reactor trip occurred followed by a turbine trip. The reactor trip was initiated by low ASO pressure input to the reactor protection system. The unit was operating with no abnormal indications prior to the trip. The reduction in pressure was the result of the failure of a red rubber gasket installed between the turbine protective trip block and the turbine governor pedestal. A tear in the gasket allowed oil in the ASO supply port to bypass the trip block and bleed directly to the drain port. The root cause of the event is improper machining of the turbine front pedestal oil ports during original manufacturing by Westinghouse Electric Company. This resulted in oil port misalignment and oil seepage between the turbine protective trip block and the turbine governor pedestal. Because of oil port misalignment, sheet gasket material had been used in place of the originally designed O-rings to seal the mating surfaces. The gasket material was not fully compatible with turbine oil and design of the connection did not support use of sheet gasket material. To correct the condition, the trip block and governor pedestal were reassembled with O-rings at the oil ports and gasket sealant on the metal to metal surfaces. Follow-up inspection found the interface to be leak free.
3282005001 | Sequoyah 2 | 02/23/2005 | 04/25/2005 | ML05115048 | <strong>Unit 2 Reactor Trip Following Closure of Main Feedwater Upon Inadvertent Opening of Control Breakers</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2005, at approximately 2030 Eastern standard time (EST), Maintenance personnel were performing pre-refueling outage maintenance activities on a 125-Volt (V) direct current (dc) vital battery board molded case circuit breaker. After removing the breaker from the panel, Maintenance personnel began installation of a breaker board panel cover to its normal position. While aligning the cover, it shifted downwards, opening two adjacent breakers. One of the adjacent breakers controlled a fuse column providing power to all four main feedwater regulation valves, which subsequently closed on loss of control power. A reactor trip was initiated by the reactor protection system on low-low steam generator level. The control room operators responded to the event in accordance with plant procedures. They diagnosed the plant condition, took actions to stabilize the unit, and maintained the unit in Hot Standby, Mode 3. The root cause of the inadvertent closure of the trip sensitive breakers was determined to be insensitivity to trip risks. The maintenance procedure has been revised to provide positive position control of panels when working on molded case breakers. Moreover, SQN has implemented a procedure that provides additional processes for review and control of site work activities concerning potential nuclear safety and generation risk above and beyond that specified in the TVA nuclear online and outage work management procedures.
3282005002 | Sequoyah 2 | 02/01/2005 | 07/08/2005 | ML05195025 | <strong>Incorrect Unit 2 Nuclear Instrumentation System Calibration</strong><br /><i>Abstract:&nbsp;</i>During a Unit 2 refueling outage, on May 10, 2005, Maintenance personnel were performing a channel calibration of the Unit 2 power range Nuclear Instrumentation System (NIS) ChannelN41 and determined the channel was out of technical specification limits. Prior to this, during the same refueling outage on May 4, 2005, Maintenance personnel had performed a channel calibration of the Unit 2 power range NIS Channel N42 and determined the channel was out of technical specification limits. A problem evaluation report (PER) was initiated to evaluate these two out of limits conditions. It was determined that the condition was the result of an incorrect calibration performed during the last functional test. The root cause of the incorrect calibration was inadequate work practices by the individual performing the functional test. The remaining NIS channels on both units were verified to be within calibration. Maintenance management held standown meetings with Maintenance Instrument Group (MIG) personnel concerning this event and instructed MIG personnel to have the technical specification compliance equipment calibration data verified by a minimum of two people before making any adjustments. Appropriate disciplinary action for personnel involved was taken.
3312005001 | Duane Arnold | 06/02/2005 | 08/01/2005 | ML05215022 | <strong>Failure to Demonstrate the Capability to Achieve and Maintain Safe Shutdown Conditions</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2005, with the plant operating at 94% power in Run Mode, while reviewing an event at Monticello (LER 2005-001), it was determined that Duane Arnold Energy Center (DAEC) was vulnerable to a similar failure. Specifically, it was determined that the Remote Shutdown Panel (RSP) did not meet design criteria for Appendix R in that metering circuits in the control room could cause a lock out of an essential bus. To correct this issue, a temporary modification was implemented on June 17, 2005. The cause of this event was the failure to identify the potential vulnerability of the DAEC remote shutdown system design to a fault in the metering circuits. There were no actual safety consequences associated with this event. There was no effect on public health and safety as a result of this event . This event is reportable under10CFR50 .73(a)(2)(ii)(B).
3312005002 | Duane Arnold | 06/20/2005 | 08/19/2005 | ML05243043 | <strong>Both Standby Gas Treatment Trains Briefly Inoperable During Testing</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2005, with the plant operating at 96% power in Mode 1, during the performance of the monthly 10-hour testing of the 'B' Standby Gas Treatment (SBGT) train, it was discovered that the flow-indicating controller was not controlling flow at the required setpoint. As a result,the 'B' SBGT train was declared inoperable at 0308. As part of this testing, the 'A' SBGT train Mode Select switch was in Manual with the inlet damper closed rendering the 'A' SBGT train inoperable. During the short period of time (approximately 4 minutes) between the discovery of the 'B' SBGT controller failure and the return of the 'A' SBGT train to an operable condition, both SBGT trains were inoperable which is a condition that could prevent the fulfillment of the safety function of the SBGT system to control the release of radioactive material. To correct this issue, the 'A' SBGT train was restored to operable status at 0312 on June 20, 2005, when its inlet damper was reopened and its Mode Select switch was returned to AUTO per the surveillance test. The cause of this event was the failure of a capacitor in the 'B' SBGT flow controller. There were no actual safety consequences and no effect on public health and safety as a result of this event. This event is reportable under 10CFR50.73(a)(2)(v)(C).
3312005003 | Duane Arnold | 04/26/2005 | 08/19/2005 | ML05243042 | <strong>Inadequate Procedure Leads to Unplanned Mode Change while Performing Scram Time Testing</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2005, with the reactor shutdown for refueling in Mode 4, a violation of the requirements of TS 3.10.1 occurred. Specifically, after completion of the reactor coolant system hydrostatic test and code required Visual Test (VT) - 2 inspections, a violation of the requirements of TS 3.10.1 occurred by remaining above 212 degrees F, an unplanned transition from Mode 4 to Mode 3 without completing all of the Mode 3 TS requirements, while conducting control rod scram time testing. The noncompliance of TS 3.10.1 continued through April 27,2005, when control rod scram time testing was completed and a reactor coolant system cool-down commenced. To correct this issue, on July 22, 2005, STPs 3.10.1-01 and 3.10.1-02 were quarantined to prevent scram time testing during vessel hydro. The cause of this event was the failure to recognize that the procedure changes made to allow for Scram Time Testing under extended vessel hydro conditions was contrary to TS. There were no actual safety consequences and no effect on public health and safety as a result of this event. This event is reportable under 10CFR50.73(a)(2)(i)(B).
3312005004 | Duane Arnold | 09/29/2005 | 11/28/2005 | ML05336026 | <strong>Unplanned Inoperability of the High Pressure Coolant Injection Pump</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2005, with the plant operating at 96% power in Mode 1, the High Pressure Coolant Injection (HPCI) system at the Duane Arnold Energy Center was declared inoperable following unsatisfactory venting results of the HPCI system injection piping. This venting was being performed to ensure the discharge piping was filled with water. Specifically, the venting operation was intended to satisfy Technical Specifications (TS) requirement that the system is full of water (SR 3.5.1.1) and to quantify any air accumulation in the system piping. During HPCI discharge line venting on September 29, 2005, a steady stream of water was not obtained for approximately 30 minutes and therefore, HPCI was declared inoperable for not being able to meet SR 3.5.1.1. To correct this issue, on October 12, 2005, an operability recommendation was completed and approved that concluded that HPCI was operable but degraded and non-conforming. The cause of this event was the failure to take into account the effects of "turbulent penetration" into the original HPCI system design. There were no actual safety consequences and no effect on public health and safety as a result of this event. This event is reportable under 10CFR50.73(a)(2)(v)(D).
3332005001 | FitzPatrick | 11/13/2003 | 03/31/2005 | ML05096010 | <strong>Inoperable Offsite Circuit In Excess of Technical Specifications Allowed Out of Service Time</strong><br /><i>Abstract:&nbsp;</i>On November 13, 2003,115 kV transmission line #4, an integral part the James A. FitzPatrick (JAF) switchyard, was deenergized due to arcing on a disconnect switch in the Nine statement but rather entered a Technical Mile Point (NMP) Unit I switchyard. JAF did not enter a TS Action Requirements Manual (TRM) Action statement for one inoperable offsite circuit based on the Operability offline #3 and the fact that both qualified offsite circuits, as defined in the TS LCO Bases and TRM Bases,had misinterpreted the TS remained operable. The NRC reviewed this issue and determined that JAF requirements and as a result, did not correctly declare the applicable offsite power source inoperable in accordance with the TS and did not take the appropriate TS required actions.The cause of the event was inadequate work practices of the preparer and reviewer of a change to the JAF Improved Technical Specifications (ITS) amendment request.Corrective actions included revising the TS LCO Bases definition of qualified offsite circuit to include the 115 lines, briefing personnel onkV transmission lines, deleting the TRM Section for the 115 kV transmission lessons learned, and performing an extent of condition review of other similar ITS submittal documents.
3332005002 | FitzPatrick | 04/05/2005 | 06/03/2005 | ML05166023 | <strong>Safety Relief Valve Setpoints Outside of Allowable Tolerances</strong><br /><i>Abstract:&nbsp;</i>Review of the as-found setpoints for 11 Safety Relief Valve (SRV) [SB] pilot assemblies, removed at the end of Cycle 16, determined that 5 SRVs were outside the allowable as-found tolerance of 1145 psig +/- 34.3 psig (+/- 3%) required by Technical Specifications (TS) Surveillance Requirement (SR) 3.4.3.1. This report documents the failure to meet this SR for 5 of the 11 SRVs. The effect of 5 SRVs being out of tolerance during Cycle 16 is analyzed in this report. The results of this analysis show that Reactor Pressure Vessel (RPV) overpressure protection and nuclear plant safety were not adversely affected. Each of the five out of tolerance SRV setpoints was determined to be caused by corrosion bonding between the SRV pilot disc and seat, a recognized industry generic problem. One of the five out of tolerance SRV pilots (serial number 1047) remained high out of tolerance during the three subsequent tests. This was caused by internal binding between the SRV pilot rod and spherical collar which resulted from a lack of a chamfer on the spherical collar. This is considered a unique case as industry operating experience as well as Target Rock Corporation refurbishment experience reveals that there were no previous similar failures.
3332005003 | FitzPatrick | 06/27/2005 | 12/13/2005 | ML05363025 | <strong>Plant Shutdown due toThrough-Wall Crack in Torus</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2005, while the plant was operating at 100 percent power, inspectors discovered a small leak (1-2 drops/minute) through the Torus shell. A subsequent engineering evaluation determined that the Primary Containment was inoperable, the plant was shutdown in accordance with normal shutdown procedures. The declaration of containment inoperability resulted in entering the site emergency plan and declaring an Unusual Event (UE). The plant's High Pressure Coolant Injection (HPCI) exhaust line, although consistent with original GE design specifications, does not include a HPCI turbine exhaust line sparger. A properly designed sparger is expected to reduce local Torus shell stresses resulting from HPCI turbine exhaust pressure pulses. The plant did not install a HPCI sparger due to inadequate information transfer to JAF from General Electric (GE) and other nuclear facilities regarding concerns with pressure instability and vibration inside the Torus. As a result of this design deficiency, the Torus shell experienced localized stress, high cycle fatigue due to rapid condensation of the HPCI exhaust steam at the ring girder weld heat affected zone, resulting in a Torus shell through-wall crack. As part of the corrective actions, an ASME Code repair was performed to repair the Torus shell. In addition, the HPCI exhaust line and ring girder gusset attachment will be modified as required to reduce the associated stresses. There were no actual safety consequences associated with this event.
3332005004 | FitzPatrick | 07/04/2005 | 08/29/2005 | ML05251005 | <strong>Residual Heat Removal (RHR) Shutdown Cooling Line Through-Wall Crack</strong><br /><i>Abstract:&nbsp;</i>On July 4, 2005, while the plant was shutdown in Mode 4, a small leak (70 drops per minute) due to a through-wall crack was discovered on the Residual Heat Removal (RHR) Shutdown Cooling (SDC) system common suction piping. At the time of discovery, the "B" RHR SDC subsystem was in service. As a result, both trains of the RHR SDC system were declared inoperable and Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.8 Condition "A" was entered. The RHR SDC system remained in-service and continued to perform its decay heat removal function. The leakage was immediately reduced to 2 drops per minute when an adjacent support was repaired to provide adequate pipe engagement. A visual inspection revealed that the leak was located at the weld connecting the pipe support (PFSK-2285) to the RHR SDC common suction pipe. The cause of the crack in the RHR SDC piping was determined to be low-stress, high-cycle fatigue at the heat affected zone of the weld which was caused by inadequate pipe engagement of an adjacent pipe support (PFSK-2084), during original installation. As part of the corrective actions, an ASME Code repair was performed to repair the pipe crack and the adjacent pipe support was restored to its design condition. In addition, extensive walkdowns of pipe supports on large bore piping were performed as part of the Extent of Condition review. No degraded or nonconforming conditions were identified during this review. There were no actual safety consequences associated with this event.
3332005005 | FitzPatrick | 09/14/2005 | 11/07/2005 | ML05322002 | <strong>Automatic Reactor Scram on Low Reactor Vessel Water Level Durinq Reactor Feed Pump Control Reset</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2005, at approximately 0213, with the plant operating at 100% power, an automatic reactor scram on low reactor water level occurred following a momentary loss of the Uninterruptible Power Supply (UPS) system. The power loss resulted in a lockout of the Reactor Feed Pump (RFP) controls, as designed. Following reset of the RFP controls, a level transient occurred causing reactor water level to lower, resulting in an automatic reactor scram on low reactor pressure vessel (RPV) water level (Level Ill). A Group 2 Primary Containment Isolation System (PCIS) isolation occurred, resulting in multiple system isolations. The Reactor Core Isolation Cooling system (RCIC) and the High Pressure Coolant Injection system (HPCI) auto initiated on "low-low" RPV water level (Level II). All systems operated as designed during and after the reactor scram. The level transient was caused by a RFP controller low output signal which is a design characteristic of the controller following a momentary loss of power. The operator did not verify the output signal prior to resetting the RFP control,which would have identified the low signal. Contributing to this human error was an inadequate abnormal operating procedure. As part of the corrective actions, the applicable procedure has been revised and the requirement to verify the controller output signal prior to resetting has been reinforced.There were no safety system functional failures or other safety consequences associated with this event.
3332005006 | FitzPatrick | 12/19/2005 | 02/13/2006 | ML06061007 | <strong>Inoperable 115 kV Line in Excess of Technical Specification Allowed Out of Service Time</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2005, with the James A. FitzPatrick Nuclear Power Plant (JAF) operating at 100 percent power, National Grid (local grid operator) notified the Nine Mile Point Nuclear Station, Unit 1 (NMP1) Control Room that abnormal amperage readings on the 115 kV off-site power lines were noted and may be indicative of an open phase. JAF was contacted by NMP1 regarding the abnormal readings. JAF Operators walked down the 115 kV switchyard and observed an open circuit on the "A" phase of 115 kV Line #4, caused by a broken bus bar connector. Line #4 was declared inoperable and removed from service for repairs. The bus bar connector was promptly repaired and Line #4 was returned to service on December 20, 2005. An Engineering evaluation of the NMP1, JAF, and National Grid data indicated that the bus bar connector failure existed, undetected, since November 29, 2005, resulting in a Line #4 out of service time of approximately 21 days. This resulted in one redundant offsite power supply exceeding its Technical Specifications (TS) 3.8.1 allowed out of service time. The cause of the undetected inoperability of Line #4 was an inadequate surveillance test (ST-9W). ST-9W records 115kV bus voltages and confirms power availability, via communication with National Grid, but does not confirm that all three phases are intact by monitoring current flow in the 115 kV transmission lines. As part of the corrective actions, a once per shift check of Line #4 phase amperage has been implemented to verify intact 115 kV phases and flow of electricity through the JAF switchyard. This criteria will be added to ST-9W. There were no nuclear, radiological or safety consequences associated with this event.
3342005001 | Beaver Valley 1 | 06/09/2005 | 07/28/2005 | ML05214030 | <strong>Protection System Channel Delta Temperature Time Constant Switch Found Out of Position</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2005, a Beaver Valley Power Station (BVPS) Unit 1 control room operator questioned whether the Channel 1 Over Temperature Differential Temperature (OTDT) setpoint indicator in the Reactor Protection System was operating less dynamically than Channel 2 and Channel 3. A subsequent check of the Channel 1 lead/lag time constant modules in the instrument rack revealed that the lead/lag switches for dynamic compensation module TM-1 RC-412E were in the OFF position, providing a lead time constant of zero seconds. BVPS Unit 1 Tech Spec 3.3.1.1 Table 3 .3-1, Item 7 for OTDT requires that the value for Tau 1 (lead time constant) be greater than or equal to 30 seconds. This condition existed since the last maintenance surveillance procedure utilized on this Channel performed on June 1, 2005. The time that the Tau 1 was set at zero seconds exceeded the 6 hours Technical Specification allowed outage time.Therefore, this was a condition prohibited by plant Technical Specifications, and is reportable pursuant to10 CFR 50.73(a)(2)(i)(B). Channel 1 OTDT lead module switches were restored to their proper positions, and the Channel was returned to service. On June 7 and on June 9, Channel 3 OTDT had been removed from service for routine maintenance actions, which resulted in unknowingly entering Technical Specification 3.0.3 for 2 of 3 OTDT channels inoperable, which is also reportable pursuant to 10 CFR50.73(a)(2)(i)(B). The procedure preparation and review process regarding channel restoration was inadequate. The procedure validation was inadequate for the complexity of the change . The safety significance of the OTDT Channel 1 lead module being set to zero seconds between June 1 and June 9 at BVPS Unit 1 was very low.
3342005002 | Beaver Valley 1 | 11/18/2005 | 01/13/2006 | ML06019051 | <strong>Latent Fire Protection Issue Regarding Possible Loss of Reactor Coolant System Makeup Function</strong><br /><i>Abstract:&nbsp;</i>In response to a corrective action from a previous Latent Issues Review performed in 2004, Engineering identified a new concern where the loss of the Beaver Valley Power Station Unit No. 1 (BVPS-1) Component Cooling Water System (CCR) could potentially result in saturation conditions at the suction of the operating Charging System pumps, leading to pump cavitation. The BVPS-1 Fire Protection Appendix R Report, does not take credit for operation of the CCR system since the original circuit "analyses used other systems for its shutdown strategy. However, the BVPS-1 Fire Protection Appendix R Report did credit the Charging System with providing Reactor Coolant System (RCS) make-up during all postulated fire events. Cavitation at an operating Charging Pump suction could lead to subsequent pump damage, preventing this system from performing its credited safety function during certain postulated fire events. This event is reportable pursuant to 10 CFR 50.73(a)(2)(v)(A) since the make-up function to the RCS, which is credited for maintaining the reactor in a safe shutdown condition, may not be available during certain postulated fire events. The root cause of this event is that wrong assumptions were made in the original basis for not needing CCR for seal water heat exchanger cooling in 1983. The risk is considered to be of very low safety significance. Applicable BVPS Unit 1 procedures were revised to eliminate the identified concern.
3352005001 | St. Lucie 1 | 03/17/2005 | 05/12/2005 | ML05144026 | <strong>Operation with Inoperable Steam Generator Water Level Channel</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2005, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. Maintenance personnel initiated a condition report to troubleshoot a 3 to 4 percent high deviation between the 1B steam generator narrow range water level indicator, LIC-9023A, and its three redundant level channels. The subsequent Engineering evaluation concluded that steam generator level channel indication deviations greater than 2 percent were outside the accuracy assumed in the analysis, and Operations declared the channel out of service on March 22, 2005. A leak in the reference leg caused a false high indicated water level. The leak was repaired, and on March 25, 2005, the channel was declared back in service. Additional corrective actions include enhanced procedural guidance for steam generator water level cross-channel check acceptance criteria.
3352005003 | St. Lucie 1 | 05/18/2005 | 07/18/2005 | ML05207058 | <strong>1A Emergency Diesel Generator Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2005, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. The 4160V emergency bus undervoltage load shed relay test was in progress. During the undervoltage load shed relay test of the offsite feeder breaker to the lA3 bus, breaker 1-20219, the breaker tripped. The 1A3 bus undervoltage condition caused the start of the emergency diesel generator, load shed, and load sequence initiated. All equipment was loaded except for containment cooling fan HVS-1B. The emergency diesel generator start and load shed event was due to a design weakness that could allow the operation of an undervoltage load shed relay test switch to cause a breaker trip, in this case the offsite power feeder breaker to the safety-related 1A3 4160V bus. HVS-1B failed to load as expected due to a faulty time delay relay in its control circuit. Immediate corrective actions included replacement of the HVS-1B time delay relay and procedure changes to ensure that operation of the undervoltage load shed relay test switch compensates for the design weakness.
3352005005 | St. Lucie 1 | 10/16/2005 | 12/15/2005 | ML05357022 | <strong>Multiple MSSV As-Found Setpoints outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2005, St. Lucie Unit 1 was in Mode 1 and holding at approximately 68 percent reactor power for Technical Specification testing of the main steam safety valves setpoints. Three main steam safety valves, V8207, V8210, and V8212, lifted outside the Technical Specification limits of +1 percent to -3 percent. The cause of the high as-found settings for V8210 and V8212 was setpoint drift, and either setpoint drift or micro-galling for V8207. V8210 and V8212 were adjusted, and V8207 was overhauled and reinstalled during the refueling outage. Operation of the facility with the as-found settings was within analytical bounds. Therefore, this event had no impact on the health and safety of the public.
3352005006 | St. Lucie 1 | 10/17/2005 | 12/15/2005 | ML05357022 | <strong>Equipment Failure Led to Inadvertent Mode Change During Cooldown</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2005, St. Lucie Unit 1 was offline and cooling down for a scheduled refueling outage. The atmospheric dump valves were used for the cooldown. While in Mode 4 conditions, a malfunction of the 1A steam generator atmospheric steam dump valve caused an unplanned heatup and subsequent inadvertent change to Mode 3 conditions. Local manual control of the valve was taken and the plant cooldown recommenced. The event investigation concluded that the valve actuator diaphragm failed and caused the valve to close. Inadequate work instructions led to the conditions that caused the diaphragm failure. Corrective actions included rework of the valve actuator and revising the model work order. This event had no impact on the health and safety of the public. The Mode change occurred without the required number of operable boration injection flowpaths. However, there was no effect on the boration injection flowpath from the refueling water tank, the allowed outage time for only one boration injection flowpath was not exceeded, and the boric acid makeup tanks remained available if needed.
3362005001 | Millstone 2 | 02/07/2005 | 03/17/2005 | ML05088040 | <strong>Nonconformance with Surveillance Requirements</strong><br /><i>Abstract:&nbsp;</i>On 2/7/05, at approximately 1254 hours, with Unit 2 at 100% power, a Training individual identified that the manual operator on Unit 2 valve 2-SI-306, Shut Down Cooling (SDC) [BP] Total Flow Control Valve, was not pinned as intended and required by Technical Specification 4.5.2.b. The pin was found inserted in a location between the handwheel shaft and the valve shaft (a dead space), and thus the valve and handwheel were in fact, not attached. This resulted in the manual operator not being engaged (not attached to the valve shaft). This event/condition is being reported pursuant to 50.73(a)(2)(i)(B), related to operation in a condition prohibited by the Technical Specifications. The cause of this event was determined to be inadequate procedure guidance as to the actual required location of the pin. The valve handwheel was unlocked, rotated until the hole in the valve sleeve lined up with the valve shaft, the pin was inserted, and the valve handwheel was relocked. Unit procedures will be revised as required strengthening the guidance as to the final pin position location to ensure the manual operator on 2-SI-306 is engaged to the valve plug.
3362005002 | Millstone 2 | 04/10/2005 | 06/06/2005 | ML05165024 | <strong>Reactor Coolant System Pressure Boundary Leakage from PWSCC in a Pressurizer Heater Sleeve</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2005, with the plant in Mode 5 (Cold Shutdown) for refueling outage 16 (2R16), an in-service visual inspection of the pressurizer heater penetrations was being performed. One heater sleeve penetration was found to show indications of minor leakage as evidenced by water and a tacky build up on the outside of the penetration. It is conservatively assumed that the leakage could have existed in Modes 1 through 4. Technical Specification 3.4.6.2 states that in Modes 1 through 4 "Reactor Coolant Leakage shall be limited to no Pressure Boundary Leakage." This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The cause of this event was a through-wall crack in one pressurizer heater sleeve at nozzle penetration location B-2 from Primary Water Stress Corrosion Cracking (PWSCC) of the Alloy 600 nozzle. The leakage was identified during visual examinations prior to any significant degradation of the reactor coolant system pressure boundary. The eddy current testing identified one axial through wall indication about 1/2 inch long from the bottom of the J-groove weld. The axial cracking of the extent shown in this heater sleeve would not have created a susceptibility to a catastrophic failure of the nozzle. The overall safety significance of this condition was determined to be minimal. There was no actual impact on the public health and safety due to this condition. The leaking heater sleeve was repaired during the refueling outage by the use of a Mechanical Nozzle Seal Assembly (MNSA). Long term resolution of PWSCC of Alloy 600 in the pressurizer will be resolved with the replacement of the pressurizer during the next refueling outage.
3362005003 | Millstone 2 | 05/18/2005 | 09/20/2005 | ML05271017 | <strong>Non-Compliance with Technical Specifications due to Installation of Unqualified Test Equipment</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2005, with the plant in mode 1 at 29% power, a non-safety related test instrument was discovered installed and connected across the voltage sensing potential transformer of the Millstone Power Station Unit 2 (MPS 2) "B"emergency diesel generator (EDG)[EK]. The subject test instrument is used while testing an inoperable EDG. The subject test equipment is not provided with a qualified isolation device used to provide the necessary separation from the safety related equipment. If the subject test equipment or associated leads shorted or grounded due to a failure or seismic event, it may have caused the subject potential transformer to fail rendering the "B" EDG inoperable. Although the test equipment was still installed, the "B" EDG was (incorrectly) declared operable while in Mode 5 at 2144 on May 13, 2005 following completion of testing. TS 3.0.4 requires that entry into an operational mode or another specified condition shall not be made when the conditions for the limiting conditions for operation are not met and the associated action requires a shutdown if they are not met within a specified time interval. The "B" EDG is required to be operable by Technical Specification (TS) 3.8.8.1 during modes 1, 2, 3, and 4. MPS 2 entered mode 4 at 1504 on May 15, 2005, with the "B" EDG inoperable due to the installed unqualified test equipment. The subject test instrument was subsequently removed. Since the TS requirement was not met, this is a condition prohibited by the TS and is reportable pursuant to 10 CFR50.73(a)(2)(i)(B).
3382005001 | North Anna 1, North Anna 2 | 10/03/2005 | 11/29/2005 | ML05341037 | <strong>Condition Prohibited by Technical Specification - Low Temperature Overpressure Protection</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2005, with Unit 2 in Mode 5 for a scheduled refueling outage it was determined that all required actions for Low Temperature Overpressure Protection (LTOP) System controls were not implemented. A second independent means to prevent more than one low head safety injection (LHSI) pump and charging pump from being capable of injecting into the Reactor Coolant System (RCS) was not being performed. The procedures controlling LHSI and charging pumps operations only required the pumps to be placed in pull to lock. The Technical Specifications (TS) Bases states two independent means are required to prevent a pump start such that a single failure or single action will not result in an injection to the RCS. This condition was applicable to Units 1 and 2. This event is reportable pursuant to 10 CFR 50.73 (a)(2)(i)(A) for a condition prohibited by the TS. This event posed no significant safety implications since the LTOP System design basis pressure and temperature limit curve were never violated. Therefore, the health and safety of the public were not affected by this event.
3392005001 | North Anna 2 | 08/05/2005 | 09/28/2005 | ML05278004 | <strong>Automatic Reactor Trip Due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2005, at 2227 hours, North Anna Unit 2 experienced an automatic Reactor trip from 100 percent power during a severe thunderstorm. A lightning strike was the direct cause of this event. The lightning strike caused an Overtemperature Delta T (OTDT) Unit 2 Reactor Trip signal without an actual over temperature condition. The control room team responded to the reactor trip in accordance with procedure 2-E-0, Reactor Trip or Safety injection. All Engineered Safety Feature equipment responded as designed. A non-emergency 4-hour report was made to the NRC Operations Center at 0020 hours on August 6, 2005, in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8-hour report was also made in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System (AFW). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in automatic actuation of the reactor protection system and the AFW system. This event posed no significant safety implications since the reactor protection systems functioned to trip the reactor safely. Therefore, the health and safety of the public were not affected by this event.
3412005001 | Fermi 2 | 01/24/2005 | 03/23/2005 | ML05089032 | <strong>Manual Reactor Shutdown Due to Containment Cooler Leak</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2005 at 1619 hours, the Fermi 2 power plant was manually shutdown (tripped) from 100% power due to unidentified drywall leakage that exceeded the technical specification requirements. The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. The reactor water level decreased from a normal level of 197 inches to a level of 123 inches above the top of active fuel, and recovered to normal without operator intervention. The main steam isolation valves (MSIVs) remained open and reactor water level was maintained in the normal band. Reactor water was supplied by the condensate and reactor feedwater systems. Pressure control was maintained by the turbine bypass valves. There was no increase in reactor dome pressure as a result of this event, and none of the Safety Relief Valves (SRVs) lifted. Reactor water low level (Level 3) isolations occurred as expected. These included isolation Group 4 (Residual Heat Removal Shutdown Cooling and Head Spray), Group 13 (Drywell Sumps), and Group 15 (Traversing In-core Probe System) isolations. The operation of all of these systems was as expected in response to this event. At 1321 hours on January 25, 2005, the plant entered cold shutdown (Mode 4). The source of the leak was determined to be from a failed end bell gasket on drywell cooler number 4. After appropriate repairs, plant restart commenced at 1710 hours on February 2, 2005.
3412005002 | Fermi 2 | 03/30/2005 | 05/18/2005 | ML05144076 | <strong>Combustion Turbine Generator 11-1 Unable to Perform as Designed During Certain Appendix R Scenarios</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2005, a condition assessment and resolution document was initiated to document several possible design and operating procedure deficiencies affecting 10 CFR 50 Appendix R and Station Blackout (SBO) events. The deficiencies were identified during development of a proposed modification affecting the Alternate AC power source used for Appendix R and SBO. On March 30, 2005, it was determined that applicable Appendix R success criteria could not be assured under all postulated scenarios described in the Updated Final Safety Analysis Report (UFSAR). Under certain conditions where Combustion Turbine Generator (CTG) 11-1 (the dedicated Appendix R alternate AC source) or other station CTGs (11-2, 11-3 or 11-4) are operating in parallel with the grid, availability of the dedicated alternate AC source cannot be assured. Actions to address the potentially affected Appendix R scenarios were put in place on March 7, 2005, when the deficiencies were identified. Additional scenarios have been identified and additional corrective actions are being evaluated within the plant's corrective action program. The cause of these problems was determined to be a lack of coordination, dating back to the mid-1980's, between all of the parties involved in implementing the use of CTG 11-1 as the Alternate AC source for Appendix R scenarios involving a loss of offsite power.
3412005003 | Fermi 2 | 05/18/2005 | 06/29/2005 | ML05189003 | <strong>Design and Operating Procedure Deficiencies Related to Appendix R Events</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2005 during a review of the dedicated shutdown procedure, design and operating procedure deficiencies were identified relating to 10 CFR 50 Appendix R events. Battery charger 2C-1 is relied upon to feed post fire emergency shutdown loads. Although a circuit breaker supplying power to a battery charger 2C-1 was re-closed by procedure after a trip or loss of division 1 power, an additional action was required to return the battery charger to service. The additional action was determined to involve circuitry that is not isolated from cables in the fire affected zone which is a requirement of the Appendix R circuit design. In addition to the same issues identified for battery charger 2C-1, the dedicated shutdown procedure did not provide for reclosure of the circuit breaker feeding power to battery charger 2C1-2 after a trip. Battery charger 2C1-2 is required to power 260VDC motor operated valves used by the standby feedwater system to provide reactor cooling water and to control reactor water level after a shutdown due to an Appendix R fire. In these scenarios, power would be initially supplied by the associated batteries, but the batteries are not sized to provide power for the entire duration of the Appendix R event. Therefore, a safe shutdown was not assured using the dedicated shutdown panel during all Appendix R scenarios. The cause of these problems was determined to be design and procedure coordination issues, dating back to the mid-1980's. Interim procedural changes have been put in place, and permanent design and procedure changes are planned to address this issue.
3412005004 | Fermi 2 | 06/16/2005 | 08/10/2005 | ML05229028 | <strong>Both Residual Heat Removal Low Pressure Coolant Injection Divisions Inoperable Due to Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2005 at 0923 EDT, with the plant in Mode 1 at 100% reactor power, both divisions of Residual Heat Removal (RHR) were declared inoperable for the Low Pressure Coolant Injection (LPCI) mode of operation due to a failure of E1150-F017B, the division 2 LPCI outboard injection valve. While performing the division 2 RHR pump and valve operability surveillance test following a planned Division 2 RHR system outage, E1150-F017B closed properly but failed to open during its required stroke time test. With this valve closed and unable to automatically open, LPCI injection into the RPV from both divisions of RHR would be prevented if the LPCI loop select logic selected the division 2 recirculation loop for injection, or if no recirculation loop break were detected.Therefore, this failure rendered both divisions of RHR inoperable for the LPCI function. Technical Specification limiting condition for operation (LCO) 3.5.1.J was entered, which requires immediate entry into LCO 3.0.3. The cause of the failure was subsequently identified as a high resistance condition on the open contactor auxiliary interlock contact associated with the closing contactor. Valve E1150-F017B was returned to its normally open position which restored the full LPCI loop select function.At 1146 EDT, division 1 RHR was declared operable for the LPCI function, and LCO 3.5.1J and LCO 3 .0.3 were exited. The plant remained at 100% power throughout the event.
3412005005 | Fermi 2 | 06/30/2005 | 08/25/2005 | ML05244036 | <strong>Potential Loss of Standby Feedwater Pumps due to Lack of Fuse Coordination</strong><br /><i>Abstract:&nbsp;</i>During an NRC triennial fire protection inspection, a fuse coordination issue was identified between 130 VDC supply circuit and breaker trip circuit fuses for the standby feedwater pump switchgear. At 1931 EDT on June 30, 2005, this condition was determined to have the potential to significantly affect the ability to provide makeup water to the reactor vessel under certain scenarios which require evacuation of the main control room. The specific scenarios involved postulate that a fire occurs in the control center that affects standby feedwater related control circuitry such that a fault occurs that causes the fuse for that circuitry to isolate. Since the fuse size ratio was less than the ratio specified by Detroit Edison and the fuse manufacturer for proper fuse coordination, it was assumed that the upstream 130 VDC supply fuse also isolates. That fuse provides the power to the control circuitry for both standby feedwater pump circuit breakers and to upstream circuit breakers that provide the 4160 volt power supply to the standby feedwater pumps. If this condition were to occur in the related breaker control circuitry before the control is transferred to the dedicated shutdown panel, the standby feedwater pump breakers would not have the 130 VDC control power needed to operate. The inadequate fuse coordination was determined to be due to a design deficiency dating back to the early 1980's. The affected 10 CFR 50 Appendix R equipment was declared inoperable until a design change was prepared and implemented on July 2, 2005 to provide the proper fuse coordination.
3412005006 | Fermi 2 | 07/17/2005 | 09/15/2005 | ML05266023 | <strong>Potential Fire Scenario Affecting Opposite Division Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>During review of 10 CFR 50 Appendix R, III.G.2 compliance on July 17, 2005, it was discovered that a fire in a divisional switchgear room affecting maintenance tie breakers 64T or 65T could adversely affect the emergency diesel generators (EDGs) in the alternate division. Specifically, a combination of hot shorts between bundled conductors in the maintenance tie breaker switchgear in either divisional switchgear room could result in closure of the associated emergency safety system maintenance tie feeder breakers. Since a loss of offsite power must also be considered concurrent with an Appendix R fire, the EDGs are assumed to be running. This could result in the asynchronous paralleling of the EDGs from the opposite division which could result in damage to those EDGs. Because the conductors bundled within the maintenance tie breakers are in close proximity to each other, they are treated as if they are part of a single cable. This combination of hot shorts is considered to be credible in accordance with the guidance provided in NRC Regulatory Issue Summary 2004-03 Revision 1. The original associated circuit assessment review was performed in 1984, but the analysis performed was not of sufficient scope and rigor to fully identify all Appendix R associated circuit issues. That analysis was not structured to evaluate multiple spurious fire induced actuations which were considered not to be Appendix R requirements at the time of the review. The maintenance tie feeder breakers have been racked out which eliminates the immediate concern. Permanent procedure changes have been completed to require that those breakers be racked out in Modes 1, 2, and 3.
3462005001 | Davis-Besse | 01/13/2005 | 03/14/2005 | ML05075040 | <strong>Inadvertent Loss of Essential Bus and Start of Emergency Diesel Generator During Testing</strong><br /><i>Abstract:&nbsp;</i>On January 13, 2005, at 0849 hours with the plant at approximately 100 percent power, surveillance testing was in progress on the 4160 Volt Essential Bus D1 under voltage relays. While moving a test lead towards a test lug, the technician inadvertently touched the test lead to an open energized knife switch in close proximity, shorting the potential transformer circuit, clearing the circuit's fuse and actuating the undervoltage relays. Emergency Diesel Generator (EDG) 2 started automatically due to actuation of the undervoltage relays, but was subsequently manually shutdown by plant operators when it was noted that it was operating without its ultimate source of cooling water. The shutdown of the EDG resulted in de-energization of Essential Bus D1. Due to the loss of power to the train 2 station battery chargers, a plant shutdown was initiated at 0949 hours in accordance with Technical Specification 3.0.3. The cleared fuse was replaced, the affected equipment re-energized, and the plant shutdown terminated at 1051 hours. Corrective actions include requiring use of shielded test plugs and/or two-part test leads/jumpers during testing of equipment that could affect a critical system function or have a significant plant impact. This event is being reported in accordance with the 10CFR50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of an Emergency Diesel Generator.
3462005002 | Davis-Besse | 12/28/2003 | 07/01/2005 | ML05187021 | <strong>Mode Change - Inoperable Battery due to Procedure Deficiency and Inadequate Reviews</strong><br /><i>Abstract:&nbsp;</i>On December 4, 2003, in Mode 5, a Technical Specification (TS) surveillance was performed for Battery 2N. Battery 2N Cell 60 voltage reading was 2.114 vdc . This is below the TS Table 4.8-1, 2.13 vdc limit, but above the 2.07 vdc allowable value (allowing the battery to be considered operable for 7days). This low reading went undetected and the Cell 60 voltage was not determined to be >/= 2.13 vdc on or before the TS required time limit. On December 28, 2003 (event date), the plant entered Mode 4 requiring two operable battery trains. Based on a lack of demonstrated operability, the plant was in a condition prohibited by TS because Battery 2N Cell 60 was below TS Table 4.8-1, 2.13 vdc limit longer than 7 days. Therefore, Battery 2N was inoperable. This is a condition prohibited by TS 3.0.4 and TS 3.8.2 .3 Limiting Condition for Operation. On March 4, 2004, during the next test, Battery 2N Cell 60 voltage met the 2.13 vdc limit. The causes of this event are procedure inadequacy and human performance error. Corrective actions include revising the test and adopting electronic data recorders. On May 4, 2005 (discovery date), Battery 2N was determined to have been inoperable during a review of past battery surveillance tests in support of an NRC inspection. This event is reportable in accordance with the 10CFR50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS.
3462005003 | Davis-Besse | 05/13/2005 | 07/12/2005 | ML05195025 | <strong>Containment Electrical Penetration Not Equipped With Backup Electrical Fault Protection</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2005, with the plant in Mode 1 at 100 percent power, it was discovered that a circuit feeding a lighting panel inside containment had not been included in the calculation performed to evaluate primary and backup circuit protection for power circuits associated with containment electrical penetrations. Without reasonable assurance that the penetration could withstand the potentially available fault current assuming a single failure of the supply breaker, the circuit was isolated. Further evaluation determined there were no other elements besides the single 30-amp breaker that could protect the containment electrical penetration. Therefore, on May 13, 2005, it was determined that the penetration was not adequately protected in the event of a single failure of the 30-amp breaker, and is being reported in accordance with 10CFR50 .73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety.This event is the result of an inadequate design in that a single drawing was used as the sole design input for the identification of applicable circuits for the calculation, and this drawing did not uniquely identify lighting circuits. The circuit will have the required backup fault protection installed or will be procedurally de-energized during plant operations.
3462005004 | Davis-Besse | 09/29/2005 | 11/28/2005 | ML05334026 | <strong>Containment Hydrogen Analyzers Inoperable due to Presence of Check Valves in Moisture Removal System</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2005, with the plant in Mode 1 at approximately 100 percent power, a periodic test of the Channel 1 Containment Hydrogen Analyzer moisture removal system showed the condensate did not drain as required. Investigation of the system revealed the presence of a check valve which required approximately 2 pounds per square inch pressure to operate. This check valve prevented the gravity-drainage system from functioning properly, and during accident conditions the accumulated condensate would fill the analyzer piping and cause the thermal conductivity detector to falsely indicate an off-scale high hydrogen concentration. A similar check valve was also found in the Channel 2 analyzer, but this check valve had a displaced O-ring seal at the time of discovery, which allowed the channel to successfully pass the periodic test of the moisture removal system. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications because at the time of discovery, the Technical Specifications required two independent containment hydrogen analyzers be operable. The probable cause of the presence of these check valves is a lack of configuration control of the Containment Hydrogen Analyzers during earlier plant operating cycles. The check valves have been removed from the system.
3462005005 | Davis-Besse | 11/03/2005 | 12/22/2005 | ML05362002 | <strong>Boric Acid Addition System Unable To Meet Technical Specification Required Boration Rate</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2005, with the plant in Mode 1 at approximately 100 percent power, review of a calculation determined that non-conservative parameters were used to determine the performance requirements of the Boric Acid Pumps. Rather than assuming the most limiting conditions for the Makeup Filter differential pressure, Makeup Tank pressure, Reactor Coolant System Letdown flow rate, and Boric Acid Addition Tank levels permitted by plant procedures, the calculation utilized normal system operating parameters. This calculation was used to establish the original Technical Specification Limiting Condition for Operation value for pump flow rate. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications because plant parameters existed in the past three years that would have prevented the pumps from attaining the Technical Specification required flow rate without operator intervention, and the necessary operator actions were not captured in plant procedures. Operating procedures have been modified to provide guidance in regards to the required plant configuration necessary to perform an emergency boration with these pumps.
3462005006 | Davis-Besse | 11/14/2005 | 01/17/2006 | ML06019051 | <strong>Technical Specification Action Missed due to Improper Valve Positioning by Operator</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2005, with the plant at 100% power, SW-38, Component Cooling Water (CCW) Heat Exchanger 2 Manual Isolation Valve, was found closed. Upon discovery of SW-38 being closed, the valve was opened. CCW train 2 was the standby train and, therefore, SW-38 should have been open to provide cooling to essential equipment, including the Emergency Diesel Generator (EDG) 2 in the event the EDG was required to operate. The as-found position of SW-38, closed, rendered CCW train 2 and EDG 2 inoperable. With SW-38 closed, CCW train 2 and EDG 2 were inoperable for approximately 18 hours beginning on November 14, 2005. Because Technical Specification 3.8.1.1 Action "b" (breaker alignment and indicated off-site power availability) was not completed within the action statement specified timeframe of one hour with EDG 2 inoperable, this condition is reportable as an Operation or Condition Prohibited by Technical Specifications per 10CFR50.73(a)(2)(i)(B). The root cause(s) were determined to be: 1) worker practice error; and 2) less than adequate pre-job briefing. Corrective actions include: addressing the individual human performance issues; and issuing a Standing Order reiterating the standards for Independent Verification and requiring additional sign offs to document completion of the independent verification (to be identified during the pre-job brief).
3482005001 | Farley 1 | 04/28/2005 | 06/23/2005 | ML05179004 | <strong>Technical Specification 3.3.2.C Violation due to Solid State Protection System Card Failure Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2005, with the unit operating at 100% power, it was determined that Unit 1 had operated in a condition prohibited by Technical Specification (TS) 3.3.2.C from 16:22 on April 28, 2005 until 03:41 on April 29, 2005 in that a Solid State Protection System (SSPS)[JC] logic circuit for Main Steam Line (MSL) differential pressure Safety Injection actuation had failed at 04:22 on April 28, 2005, and the failed logic train Limiting Condition for Operation (LCO) Required Action Statement (RAS) was not applied. At 04 :22 on April 28, 2005, a trip status indicating light, main control board alarm, and associated computer alarm actuated. TS 3 .3.2.D was entered based on a suspected failed channel. Historically, this symptom set has been due to a failed channel.Troubleshooting determined at 01:34 on April 29, 2005, that the failure was not a failed channel but a failed AT rain Engineered Safety Features Actuation logic circuit. The failed circuit was repaired, tested, and returned to service at 03:41 on April 29, 2005.The circuit failure event was caused by the failure of a new card installed in October 2004. The operation in a condition prohibited by TS was caused by the time required to troubleshoot the failure. The failed card has been returned to the vendor for analysis. Preplanned systematic diagnostic guidance will be developed and provided to planning personnel that will include lessons learned from this event by August 15, 2005.
3482005002 | Farley 1 | 11/11/2005 | 01/03/2006 | ML06003036 | <strong>Technical Specification 3.8.1 Violation due to 1F Bus Synchroscope Failure</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2005, with the unit operating at 100% power, it was determined that Unit 1 had operated in a condition prohibited by Technical Specification (TS) 3.8.1 from 1149 on November 11, 2005, until 1647 on November 14, 2005, in that an unrecognized failure of the 1F (Train A Engineered Safety Features 4kv bus) synchroscope existed which rendered the 1-2A (Train A) Emergency Diesel Generator (EDG) inoperable. Troubleshooting of a failed 4kv bus voltmeter determined that the voltage indication was lost due to blown fuses that also disabled the bus synchroscope, resulting in TS 3.8.1 required action B.1 not being met. The synchroscope is required per TS Surveillance Requirement (SR) 3.8.14 for the ability to synchronize the 1-2A EDG to an offsite source following power restoration after an LOSP. The ability of the EDG to start and load in response to an LOSP was unaffected by this failure. The 1-2A EDG was declared inoperable for Unit 1 only, per TS 3.8.1 on November 14, 2005 at 1647, and returned to service at 2200 following fuse replacement. The synchroscope failure event was caused by a short in a degraded voltmeter phase selector switch. The operation in a condition prohibited by TS was caused by cognitive personnel error and knowledge deficiency in that it was unclear to the operating crew that loss of the voltmeter indicated that the synchroscope might also be inoperable. The switch has been tagged to prevent use pending switch replacement. Guidance on actions to take based on loss of certain unique Emergency Power Board indications has been made.
3522005001 | Limerick 1, Limerick 2 | 01/21/2005 | 03/08/2005 | ML05068036 | <strong>Loss of Licensed Material in the Form of a Radiation Detector Calibration Source</strong><br /><i>Abstract:&nbsp;</i>A 0.0154 microcurie Thorium-230 source that is used to calibrate alpha counters was discovered missing from its storage box in a locked cabinet. The activity of this source exceeded the reporting threshold of 10 times the limit in 10CFR20 Appendix C. The Appendix C limit is 0.001 microcuries resulting in a reporting threshold of 0.01 microcuries. The source has not been located despite an extensive search. A peer check of restoration to within the locked cabinet has been added for handling sources.
3522005002 | Limerick 1, Limerick 2 | 04/06/2005 | 06/02/2005 | ML05153020 | <strong>Offsite Source Trip due to Water Intrusion into Transformer Winding Temperature Switch</strong><br /><i>Abstract:&nbsp;</i>One of two offsite sources tripped due to a false actuation of the 4B transformer protective relays. The false actuation was caused by water intrusion into the B phase winding hot spot high temperature switch. The tripping of the transformer de-energized the 13 kV feed from the 500 kV substation to the safeguard transformer. Four of eight 4 kV safeguard busses were de-energized which resulted in four of eight emergency diesel generators (EDGs) automatically starting and running unloaded as designed. The 4 kV safeguard busses were automatically re-energized when the four feeder breakers from the energized offsite source automatically closed as designed. Both loops of emergency service water (ESW) automatically started due to the start of the EDGs. The 4B transformer temperature switch was removed from service and the offsite source was re-energized.
3522005003 | Limerick 1 | 07/18/2005 | 09/15/2005 | ML05258054 | <strong>Scram due to Invalid Actuation of Main Generator Output Breaker Position Monitor Circuit</strong><br /><i>Abstract:&nbsp;</i>A valid automatic actuation of the reactor protection system was initiated by a main turbine trip that was caused by an invalid main generator lockout relay actuation. A corroded disconnect position switch and concurrent ground on the balance of plant DC power distribution system adversely affected the main generator output breaker position monitoring circuit and caused the circuity to falsely sense that both main generator output breakers were open. The corroded switch and ground were repaired and the unit was restarted. Monitoring of the generator output breaker position monitoring circuit relays has been added to the operator rounds. Enhancements to the ground elimination processes, training and test equipment are planned.
3522005004 | Limerick 1 | 05/29/2004 | 11/18/2005 | ML05332021 | <strong>Minimum Critical Power Ratio Limiting Condition for Operation Noncompliance</strong><br /><i>Abstract:&nbsp;</i>An evaluation of the impact of a General Electric Part 21 report determined that Limerick Unit 1 operated in non-compliance with Technical Specification 3.2.3 Minimum Critical Power Ratio on two occasions during control rod pattern adjustments. Unit 1 is no longer vulnerable to a repeat occurrence of this condition. GE is currently reviewing previous cycles for Unit 1 and Unit 2. A new databank and coding will be installed in 3D Monicore following issuance of the GE review.
3522005005 | Limerick 1, Limerick 2 | 10/05/1992 | 12/30/2005 | ML05364042 | <strong>Missed Surveillance Resulted in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>An offsite circuit calculation credited a ten second time delay on 101 and 201 safeguard transformer tap changers automatic voltage controls to maintain operability of the offsite circuits. The associated offsite circuit should have been considered inoperable when the automatic voltage control was operating in manual mode under certain configurations of the safeguard buses. A subsequent review of the three year reporting period identified occasions when the station operated in these configurations and did not take the required Technical Specification action. A modification will be implemented to change the automatic voltage control time delays on the safeguard and station auxiliary transformers. As a result the offsite circuits will remain operable when 101 and 201 safeguard transformer automatic voltage controls are placed in manual mode.
3532005001 | Limerick 2 | 03/12/2005 | 05/06/2005 | ML05126029 | <strong>Core Alterations Performed with Source Range Monitor Alarm Horn Inoperable</strong><br /><i>Abstract:&nbsp;</i>Refueling operations were in progress on Unit 2 when the source range monitors (SRMs) were rendered inoperable as a result of loss of the SRM audible alarm function; SRM visual alarms remained functional. The operators failed to recognize that the Technical Specification (TS) requirement for an SRM audible alarm was not satisfied prior to granting permission to conduct core alterations, which resulted in a condition prohibited by TS. The SRM audible alarm was restored and core alterations were resumed. The procedure for loss of main control room annunciators was revised to address the TS impact of a loss of the SRM audible alarm function.
3532005002 | Limerick 2 | 03/28/2005 | 05/26/2005 | ML05146033 | <strong>High Pressure Coolant Injection System Inoperable due to a Degraded Control Power Fuse Clip</strong><br /><i>Abstract:&nbsp;</i>The Unit 2 High Pressure Coolant Injection System (HPCI) was declared inoperable due to loss of the suction automatic transfer function when the HPCI outboard suppression pool suction motor operated valve (MOV) lost control power due to a manufacturing defect in the control power fuse clip for the MOV. The fuse clip was replaced and the HPCI MOV was satisfactorily tested. The HPCI system was then declared operable. The procedure for periodic maintenance of Westinghouse 250 VDC magnetic starters will be revised to include a closer examination of the fuse block rivets.
3532005003 | Limerick 2 | 05/31/2005 | 06/28/2005 | ML05179035 | <strong>Operation Exceeding License Maximum Power Level</strong><br /><i>Abstract:&nbsp;</i>An unplanned reactor power increase to approximately 107% of rated thermal power occurred due to a failure of the speed control for the 2A reactor recirculation pump motor generator. A printed circuit card soldered connector failure resulted in the fluid coupler scoop tube moving to the maximum speed mechanical stop . Operators immediately reduced power to less than 100% by reducing the speed on the 2B reactor recirculation pump. The failed circuit card was replaced and the pump speed control was returned to service.
3532005004 | Limerick 2 | 10/12/2005 | 12/08/2005 | ML05342065 | <strong>Automatic Scram due to EHC Malfunction that Closed the Main Turbine Control Valves</strong><br /><i>Abstract:&nbsp;</i>A valid automatic actuation of the reactor protection system was initiated by a malfunction of the Electro-Hydraulic Control (EHC) system that closed the main turbine control valves at power. The most likely cause was a transient malfunction of a circuit card. The four circuit cards that most likely caused the malfunction were replaced and tested.
3542005002 | Hope Creek | 03/27/2005 | 05/26/2005 | ML05154002 | <strong>Through-Wall Leak on 'B' Reactor Recirculation System Decontamination Port</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2005, reactor power was reduced to approximately 6% power (Operational Condition 2) to perform a primary containment entry to identify the source of increasing unidentified reactor coolant system (RCS) leakage. Beginning on February 8, 2005, unidentified RCS leakage had been trending upward and was at approximately 0.73 gpm on March 27, 2005. Hope Creek personnel identified a steam leak coming from the insulated decontamination port that is connected to the 'B' reactor recirculation system between the suction of the pump and the suction isolation valve. At 2329 hours on March 27, 2005, the reactor mode switch was taken to shutdown to perform a controlled shutdown and cooldown of the plant to precisely identify and repair the leakage source. At 1035 hours on March 28, 2005, after removal of the insulation from the decontamination port, the steam leakage was determined to be coming from a crack located on the 4-inch nominal pipe size (NPS) portion of the decontamination port. The through-wall crack in the decontamination connection was determined to be fatigue initiation and propagation as caused by the following: presence of an original subsurface weld defect and presence of a decontamination port geometry that experienced damaging high cycle vibration during certain recirculation system operating conditions. Corrective actions consisted of the modification of the A and B reactor recirculation decontamination ports and an extent of condition review to determine if other connections to the reactor recirculation system were vulnerable to the decontamination port failure. This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(A), "any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded."
3542005003 | Hope Creek | 06/07/2005 | 09/29/2005 | ML05285036 | <strong>Reactor Coolant System Leak from Check Valve Position Indicator</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2005, at 1413 hours, the reactor recirculation pumps were taken to minimum speed and the reactor mode switch was locked in shutdown to scram the reactor due to increasing drywell pressure and drywell floor drain leakage. An Unusual Event (UE) was declared at 1437 hours due to drywell floor drain leakage exceeding 10 gpm.The operating crew took action to bring the plant to a cold shutdown condition and a drywell entry was performed. At 0240 hours on June 8, 2005, the source of the leak was determined to be from the F050A residual heat removal (RHR) check valve position indicator. On June 8, 2005, at 0336 hours, the B RHR loop was placed in shutdown cooling and Operational Condition 4 was entered at 0456 hours. The UE was terminated at 0515 hours on June 8,2005. The cause of the reactor coolant system leak was the result of an approximately 280 degree circumferential crack in the position indicating tube for the F050A RHR check valve. The through wall leak was caused by the vibration of the attraction sleeve (which is on the end of actuator rod) in the presence of the switch magnetic force resulting in the attraction sleeve fretting/wearing through the position indicating tube. Corrective actions consist of modification of the F050A and F050B RHR check valves, ultrasonic testing of the six other check valves with the same position indicating tubes, development of preventative maintenance activities and an engineering review of components and sub-components communicating with the pressure boundary of the loop 'A' and 'B' reactor recirculation piping. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(A), "the completion of any nuclear plant shutdown required by the plant's Technical Specifications," 10CFR50.73(a)(2)(iv)(A), 'any event or condition that resulted in manual or automatic actuation of ...reactor protection system (RPS) including: reactor scram or reactor trip," and 10CFR50.73(a)(2)(ii)(A), "any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded."
3542005004 | Hope Creek | 05/09/2005 | 07/08/2005 | ML05202029 | <strong>A Control Room Emergency Filtration (CREF) Train Inoperable with B CREF Out Of Service</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2005, at approximately 1020 hours, plant personnel reported that the guide vane pivot arm for the1AK400 chiller appeared to have slipped . The 1AK400 chiller supports the 'A' Control Room Emergency Filtration (CREF) train . At that time, the 1 BK400 chiller (which supports the 'B' CREF train) was removed from service for maintenance . A follow up operability assessment performed several weeks later concluded that with the guide vane pivot arm slippage, the 1AK400 chiller was not capable of performing its design function of maintaining temperatures in the control room envelope. A review of plant data determined that the guide vane slippage for the 1AK400 chiller most likely started at approximately 0950 hours on May 9, 2005. Therefore, the 'A' CREF train was inoperable from May 9 to May 12 . With the 'B' CREF train inoperable during this same time period, Technical Specification (TS) 3.0.3would have been applicable for having both trains of CREF inoperable. The slippage of the 1AK400 guide vane actuator arm was the result of loose set screws on the drive arm and vane-actuating arm. Corrective actions include corrective maintenance completed to restore the 'A' CREF chiller, maintenance procedure revision, lesson learned communication, and assessment of maintenance technician training changes. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B), as "a condition which was prohibited by technical specifications," and 10CFR50.73(a)(2)(v)(D), "any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: mitigate the consequences of an accident ."
3542005005 | Hope Creek | 06/28/2005 | 08/29/2005 | ML05250048 | <strong>'A' Control Room Emergency Filtration (CREF) Train Inoperable for Greater than Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2005, a review of logs associated with the operation of the 'A' CREF train identified that in January 2005 and February 2005 that the 'A' CREF train was inoperable for greater than the Hope Creek Technical Specification 3.7.2 allowed outage time of 7 days. As discussed in LER 354/05-007-00, the 'B' CREF train was inoperable from January 2005 to June 2005. With both trains of CREF inoperable for greater than one hour the requirement of TS 3.0.3 was also exceeded. The cause of the inoperability of the 'A' CREF train was the entrainment of air in the chilled water train following maintenance on the evaporator. The entrainment of air in the system was due to inadequate filling and venting of the chilled water train. Procedure HC.OP-SO.GJ-0001, "Control Area Chilled Water System Operation," was revised on April 1, 2005 to improve the venting process for the control room chilled water system and the 'A' CREF train was returned to a fully operable status on June 3, 2005. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as a, "condition which was prohibited by the plant's technical specifications."
3542005007 | Hope Creek | 06/19/2005 | 08/18/2005 | ML05237033 | <strong>'B' Control Room Emergency Filtration (CREF) Train Inoperable Greater Than Allowed By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2005, maintenance personnel identified that the fan flow controller for the 'B' control room emergency filtration (CREF) train was found with a reset setting different than required by the instrument calibration data (ICD) record. The reset was found at 1.0 X 10 rep/min when it should have been set at 10 X 10 rep/min. Upon identification of the incorrect controller setting, the 'B' CREF train was declared inoperable on June 19, 2005 at 1747 hours until the controller was adjusted to the proper settings on June 20, 2005 at 1505 hours. The CREF train is required to run following a loss of coolant accident (LOCA) or a LOCA in conjunction with a loss of offsite power (LOP). Testing determined that with the June 19, 2005 as-found settings, the 'B' CREF train was not capable of clearing the low fan flow trip setting in the event of a LOP/LOCA. Based on a review of work history for the 'B' CREF train fan controller, the controller switch was most likely mis-positioned by the maintenance technician following testing of the 'B' CREF train in January 2005. Therefore, the 'B' CREF train was inoperable for longer than the 7-day allowed outage time for a single CREF train inoperable as required by Technical Specification (TS) 3.7.2. During the period of time the 'B' CREF train was assumed to be inoperable, the 'A' CREF train had experienced periods of inoperability. With both trains of CREF inoperable for greater than one hour the requirement of TS 3.0.3 was also exceeded. The cause of the incorrect 'B' CREF train fan controller setting was due to human error. The 'B' CREF controller was restored to the proper settings and returned to operable on June 20, 2005. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B), as "a condition which was prohibited by technical specifications."
3542005008 | Hope Creek | 08/28/2005 | 10/27/2005 | ML05311026 | <strong>Technical Specification Shutdown due to 'B' Suppression Chamber to Drywell Vacuum Breaker Not Closed</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2005, at 0325 hours, the 'B' drywell to suppression chamber vacuum breaker {BF} indication was observed to cycle from closed to intermediate open. Attempts made to close the vacuum breaker from the control room and to establish a differential pressure between the drywell and suppression chamber were not successful. Technical Specification 3.6.4.1.b states, "with one or more suppression chamber-drywell vacuum breaker not closed, close the vacuum breaker within 2 hours; or be in at least HOT SHUTDOWN within the next 12 hours and in COLD SHUTDOWN within the following 24 hours." Due to the 'B' drywell to suppression chamber vacuum breaker not remaining closed, a plant shutdown was commenced at 1200 hours. At 1715 hours, Operational Condition 3 was entered (HOT SHUTDOWN). On August 29, 2005, at 0933 hours, Operational Condition 4 (COLD SHUTDOWN) was entered. The cause of the 'B' drywell to suppression chamber vacuum breaker failure to remain closed is attributed to a loose locknut on the left hand side latch plate self-aligning screw. The 'B' vacuum breaker was repaired and inspection of the remaining suppression pool vacuum breakers was performed. Maintenance procedures will be revised and training will be provided to appropriate maintenance personnel. This event is being reported in accordance with 10CFR50.73(a)(2)(i)(A) "the completion of any nuclear plant shutdown required by the Technical Specifications."
3612005001 | San Onofre 2 | 02/03/2005 | 03/04/2005 | ML05069018 | <strong>Automatic Reactor Trip due to Unit Auxiliary Transformer Differential Relay Trip</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2005, at 1223 PST, Unit 2 was operating at about 99 percent power when a phase C differential current protection relay for Unit Auxiliary Transformer (UAT) 2XU1 tripped the Main Generator. An automatic Turbine Trip and automatic Reactor Trip followed as designed. The Auxiliary Feedwater System automatically started as expected on a Reactor Trip from full power. There were no complications experienced during the event and no other safety systems were actuated or required. The Unit trip was initiated by the UAT 2XU1 phase C differential relay. Subsequent comprehensive testing and inspections of the UAT 2XU1, phase C protection circuit, and Digital Fault Recorder (DFR) components have not revealed any defects or degraded conditions. The most likely cause of the trip has been determined to be an invalid signal introduced during DFR testing, which was in progress at the time of the trip. As corrective action, SCE has placed administrative restrictions on DFR testing. The phase C differential relay and DFR isolation circuit boards for Unit 2 were replaced as precautionary actions. SCE will assure that associated electrical protection circuits are not in service or that the DFR is completely isolated from electrical protection circuits prior to DFR testing. This event was of very low to no safety significance because all safety systems responded as designed.
3612005002 | San Onofre 2 | 02/15/2005 | 04/12/2005 | ML05105035 | <strong>Missing Taper Pins on CCW Valve Cause Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 02/14/2005, at 2155 PST, with Unit 2 at 96 percent power, plant operators manually initiated a plant shutdown to repair 2HV6500, a Component Cooling Water (CCW) valve. In accordance with 10 CFR 50.72(b)(2)(i), SCE reported initiation of the shutdown to the NRC on02/14/2005 (Log No. 41410) at 2213 PST. The plant reached Mode 5 at 1804 PST on 02/15/2005. SCE is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(A). 2HV6500 is the Train "B" CCW outlet isolation valve for the Shutdown Cooling (SDC) heat exchanger. The Containment Spray (CS) system depends on SDC heat exchanger availability for system operability. In response to an abnormal reduced flow condition in 2HV6500, plant operators declared the valve inoperable on 02/10/2005 at 2315 PST and entered the 7-day allowed outage time to restore the CS system. SCE conservatively decided to shutdown the plant to repair the valve. Upon disassembling 2HV6500, the two taper pins securing the valve disc to the stem were missing. New pins were installed and staked to the disc and the valve was returned to service. SCE will screen similar valves to determine which valves require follow-up inspection. Safety significance was minimal. The CS system has two independent trains. During the time Train "B" CS was declared inoperable, Train "A"remained operable and available to fulfill its safety function.
3612005003 | San Onofre 2, San Onofre 3 | 03/14/2005 | 05/11/2005 | ML05133017 | <strong>Relay Settings For The Degraded Grid Voltage Protection System Could Cause Early Separation from Offsite Power Sources During a Design Basis Event</strong><br /><i>Abstract:&nbsp;</i>In 1995, Southern California Edison (SCE) installed degraded voltage protection systems to ensure San Onofre Nuclear Generating Station (SONGS) separates from offsite power if the voltage supplied by the offsite power system dips and remains below the voltage needed for plant safety equipment operability. SCE had calculated 218 kV to be the minimum switchyard voltage that would support plant safety equipment operability. During an assessment of the SONGS switchyard the week of March 14, 2005, personnel questioned the validity of 218 kV as the minimum voltage required for offsite circuit operability with one unit shutdown and one unit operating. SCE performed evaluations after March 14, 2005 which indicate 222.2 kV is required for operability of the immediate access offsite power circuit. If post-trip switchyard voltage would have been between 218 kV and 222.2 kV, degraded voltage protection systems could have caused SONGS to separate from offsite power even though offsite power would have provided sufficient voltage to support plant safety equipment operability. SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(v)(D). SCE is continuing to evaluate hardware and electrical setpoint changes to reduce the voltage required at the SONGS switchyard from 222.2 kV to a lower value.
3612005005 | San Onofre 2 | 12/07/2005 | 01/23/2006 | ML06027027 | <strong>Inoperable Class 1E Supply Breaker Causes Pressurizer Heater to be Inoperable for Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 3, 2005 at 1235 PST and again on December 7, 2005, pressurizer heater class 1E supply breaker 2B0602 failed to close upon demand from the control room in preparation for a routine surveillance test. Based on the cause evaluation performed after the second failure, SCE concluded that breaker 2B0602 was not functional between December 3 and 9, 2005. Because the Class 1E powered pressurizer heater bank 2E129 was inoperable for greater than the 72 hours allowed by Technical Specification 3.4.9, this report is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TS. The breaker failure to close was caused by the combined effects of misalignment and interferences between the breaker and the cubicle, which caused intermittent discontinuity in the breaker close control circuit. SCE modified the breaker to eliminate the interference with the cubicle and adjusted the alignment of the breaker in the cubicle. Additional actions are planned including inspection of other similar breaker/cubicles and revising procedures, as necessary, to include more detailed checks for breaker-to-cubicle alignment. Since the redundant bank of pressurizer heaters remained available and operable throughout the duration of this occurrence, the safety significance of this event was low.
3622005001 | San Onofre 3 | 06/26/2005 | 08/23/2005 | ML05238029 | <strong>Emergency Diesel Generator (EDG) 3G003 Declared Inoperable due to Loose Wiring Connection on Emergency Supply Fan</strong><br /><i>Abstract:&nbsp;</i>On 06/25/2005, at about 1335 PDT, during a routine surveillance test of EDG 3G003, Emergency Supply Fan 3MA276 did not start. SCE operators declared 3G003 inoperable. SCE traced the fan failure to start to a loose electrical connection. SCE also found the same contact for 3G003 fan 3MA277 loose, but the fan still started. These connections were tightened; other connections were confirmed to be acceptable. EDG 3G003 was start tested and declared operable at 0406 PDT on 06/26/2005. EDG 3G002 was inspected and other connections were found not completely tight. SCE could not conclusively determine if those connections would have caused 3G002 inoperability and conservatively declared 3G002 inoperable at 0459 PDT on 06/26/2005. This event was reported to the NRC on 06/26/2005 (Event Log No. 41798) in accordance with 10CFR50.72(b)(3)(v)(D). It was subsequently determined that the connections found on 3G002 did not affect its operability and 3G002 remained operable and available to fulfill its design and safety function. On 08/23/2005, SCE retracted its 06/26/2005 phone report (Event Log No. 41798) and is providing this LER to document this event and inform the NRC of the corrective actions taken.
3622005002 | San Onofre 3 | 12/23/2004 | 11/30/2005 | ML05336040 | <strong>Emergency Containment Cooling Inoperable for Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2005 at 0825 (discovery date) Containment Emergency Cooling Unit Train "A", 3ME399, did not start during its monthly surveillance test. SCE discovered 3BLP0303, Containment Emergency Fan 3ME399 Backup Breaker had tripped open. SCE's review determined this breaker (and also breaker 3BLP0304 for Train "A" ECU 3ME401) had been installed with incorrect setpoint tolerances. Because SCE installed these breakers during the last refueling, ECUs 3ME399 and 3ME401 were considered inoperable from December 23, 2004 to October 5, 2005. SCE is submitting this report in accordance with 10CFR50.73(a)(2)(i)(B) and10CFR50.73(a)(2)(v)(D). This event was initiated by incorrect field implementation of an engineered change package. This condition went undetected after the September 4, 2005 surveillance because the surveillance procedure did not provide sufficient instruction to determine that 3BLP0303 tripped during the surveillance. SCE corrected the breaker setpoint tolerances, and improved the ECU surveillance procedure. Since redundant Containment Cooling systems remained available and operable throughout the duration of this occurrence, the safety significance of this event is low.
3642005001 | Farley 2 | 12/04/2005 | 01/31/2006 | ML06032072 | <strong>Gas Binding of the Unit 2 A Train High Head Safety Injection Pump</strong><br /><i>Abstract:&nbsp;</i>On December 4, 2005, with the reactor at 29 percent power, while shifting on-service trains of High Head Safety Injection (HHSI) during power ascension following a refueling outage, the 2A HHSI Pump was found to be inoperable, due to gas accumulation in its suction line. Although the actual time of inoperability is not known, it is apparent that the pump became inoperable some time prior to Mode 3 entry on November 30, 2005. On December 4, 2005, at 0358, the A Train HHSI Pump was started, and the B Train HHSI Pump was secured. Charging and seal injection flow went to zero and then began to oscillate. The operator immediately restarted the B Train HHSI Pump to restore flow and secured the A Train HHSI Pump. TS Limiting Condition for Operation (LCO) 3.5.2 Required Action Statement (RAS) for inoperable A Train Emergency Core Cooling System (ECCS) was entered at 0400. The swing HHSI Pump was aligned to A Train, and TSLCO 3.5.2 was exited at 0635. Root cause investigation determined the cause of the event to be gas bubble formation in the pump suction line due to excessive variations in Volume Control Tank (VCT) pressure over a short time period. After discovery of the gas intrusion, the A Train HHSI pump was vented, tested, and returned to service. Operations personnel have been trained on this event, and procedures have been enhanced to address the possibility of gas intrusion under these conditions.
3662005001 | Hatch 2 | 02/20/2005 | 04/08/2005 | ML05102011 | <strong>Both Inboard and Outboard Main Steam Isolation Valves for the `A' Penetration Failed Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On 2/20/2005 at 1435 ET, Unit 2 was in the Refuel mode with fuel in the vessel and the reactor cavity flooded for refueling operations. At that time, plant engineers and technicians were performing Local Leak Rate Testing (LLRT) on Primary Containment Isolation Valves (PCIVs) when it was discovered that two Main Steam Isolation Valves (MSIVs) had failed their associated LLRT. Both valves are located in the same penetration involving the 'A' Main Steam Line. The leakage acceptance criteria for the MSIVs are contained in the plant's Technical Specifications.The primary cause of the failure for the inboard (2B21 -F022A) MSIV appears to be degradation over period of time. The failure of the outboard (2B21-F028A) MSIV appears to be the methodology used for testing the valve. Corrective actions for this event included repairing the valves and performing another LLRT with successful results. Finally, additional procedural guidance is being provided for the performance of Local Leak Rate Testing when using blocking pressure against the Main Steam Line plugs as a course of action to prevent recurrence.
3662005002 | Hatch 2 | 03/02/2005 | 07/13/2005 | ML05199035 | <strong>Secondary Containment Bypass Leakage Requirements Exceeded</strong><br /><i>Abstract:&nbsp;</i>On 3/02/2005 at 1500 ET, Unit 2 was in the Refuel mode with fuel in the vessel and the reactor cavity flooded for refueling operations. At that time, plant engineers and technicians were performing Local Leak Rate Testing (LLRT) on Primary Containment Isolation Valves (PCIVs) when it was discovered that two Reactor Core Isolation Cooling (RCIC) valves had failed their associated LLRT. Both of these valves are located in the same penetration and are associated with Secondary Containment bypass leakage. The leakage acceptance criteria for Secondary Containment bypass are contained in the plant's Technical Specifications. The primary cause of the failures for the inboard (2E51-F007) RCIC valve, and the outboard (2E51-F008) RCIC valve appears to be degradation over a period of time. Corrective actions for this event included repairing the valves by installing new wedges and performing another LLRT with successful results.
3662005003 | Hatch 2 | 05/23/2005 | 07/13/2005 | ML05196037 | <strong>Manual Reactor Scram Inserted in Response to Reactor Water Chemistry Event Caused by a Condenser Tube Leak</strong><br /><i>Abstract:&nbsp;</i>On 5/23/2005 at 1747 EST, Unit 2 was in the Run mode at an approximate power level of 1598 CMWT (57 percent rated thermal power). At that time, Operations personnel manually scrammed the reactor per procedure 34GO-OPS-014-2, "Fast Reactor Shutdown." This procedure was entered because of a condenser tube leak that resulted in an undesirable reactor water chemistry trend. Following the manual scram, water level decreased due to void collapse from the rapid reduction in power, reaching a minimum of approximately thirteen inches below instrument zero (about 145 inches above the top of the active fuel). The decrease in water level resulted in receipt of a subsequent reactor scram, a Group 2 Primary Containment Isolation System (PCIS) isolation signal and thus closure of the Group 2 Primary Containment Isolation Valves per design. The operating Reactor Feedwater Pumps restored level to its designed set point.Personnel confirmed that all control rods fully inserted and reset the Group 2 isolation signal and restored the isolation valves to normal per procedure 34AB-C71-001-2, "Scram Procedure." The manual scram was initiated as the result of a condenser tube leak. An investigation determined that the condenser tube leak was caused by the loss of a plug that was installed previously in April 2005. The receipt of the Group 2 PCIS isolation and the subsequent reactor scram was the result of a vessel water level decrease due to void collapse from the rapid reduction in power following the insertion of the manual scram.The leaking condenser tube was re-plugged with a plug of a different design.
3682005001 | Arkansas 2 | 03/09/2005 | 05/09/2005 | ML05131023 | <strong>Reactor Coolant System Pressure Boundary Leakage due to Primary Water Stress Corrosion Cracking of Pressurizer Heater Sleeves</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2005, following shutdown for a scheduled refueling outage, a visual inspection of the reactor coolant system pressurizer revealed indications of leakage below the insulation around three pressurizer heater sleeves. On March 12, 2005, with the insulation removed from the heater sleeves and bottom head of the pressurizer, a total of eight heater sleeves and one pressurizer heater penetration containing a plug were found to be leaking. Leakage was identified by small amounts of boron discovered at the sleeve penetration interfaces. On March 15, 2005, with the pressurizer filled with water, one additional leaking pressurizer heater sleeve was identified by visual observation of moisture on the sleeve. Leakage was confirmed in nine pressurizer heater sleeves and one plugged penetration. The failure mechanism for the ten leaking pressurizer penetrations was primary water stress corrosion cracking of Alloy 600 material. Non-destructive examination of the penetrations confirmed the presence of axially oriented flaws. Inspection of the pressurizer base material surrounding each penetration indicated that no boric acid wastage had occurred. The leaking heater sleeves were repaired using NRC approved ASME Code-qualified mechanical nozzle seal assemblies. The leaking plugged penetration was replaced with an Alloy 690 sleeve and plug. The pressurizer will be replaced during the refueling outage scheduled for the fall of 2006.
3692005001 | McGuire 1, McGuire 2 | 12/15/2004 | 05/02/2005 | ML05131016 | <strong>Reactor Coolant System Leakage Detection Instrumentation Inoperable</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 and Unit 2 were in MODE 1 (Power Operation) at 100 percent power. Event Description: On December 15, 2004, an initial evaluation of the adequacy of the radioactivity detection sensitivities of both Unit's Containment Atmosphere Particulate Radioactivity Monitor (EMF38L) and both Unit's Containment Atmosphere Gaseous Radioactivity Monitor (EMF39L) concluded these EMFs were operable. However, on March 2, 2005, McGuire concluded the sensitivities of these EMFs were inadequate for them to perform their intended function of detecting a one gallon per minute leak from the Reactor Coolant System within one hour. In consequence, with regard to the Reactor Coolant System leakage detection function, these monitors were inoperable for periods in excess of Technical Specification requirements. These instances represented a Technical Specification prohibited operation reportable under the requirements of 10 CFR 50.73 (a)(2)(i)(B). A risk assessment has determined this event to be of no significance to the health and safety of the public. Event Cause: The initial evaluation of EMF38L and EMF39L did not recognize that, even though their sensitivities appeared to comply with original licensing basis requirements, current Reactor Coolant System radioactivity levels precluded EMF38L and EMF39L from satisfying their intended function of detecting a one gallon per minute Reactor Coolant System leak within one hour. Corrective Action: Additional training will be conducted related to what is to be addressed when evaluating the capability of a structure, system, or component to perform its specified function(s). License Amendment Request will be submitted clarifying the capabilities of the RCS leakage detection instrumentation.
3692005002 | McGuire 1 | 04/10/2004 | 01/18/2006 | ML06038051 | <strong>Main Steam Isolation Valve Inoperable due to Internal Binding</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in MODE 4 (Hot Shutdown) at 0 percent power. Event Description: In April 2004, stroking of 1SM-1 ("D" Steam Generator Main Steam Isolation Valve (MSIV)) introduced valve stem scoring. This scoring was indicative of conditions which probably prevented the valve from fully closing. The inability to close renders 1SM-1 inoperable. Since the applicable Technical Specification required actions and completion times were not satisfied, this represented a Technical Specification prohibited operation reportable as per the requirements of 10 CFR 50.73(a)(2)(i)(B). This event was not significant with respect to the health and safety of the public. Event Cause: The most probable cause was high valve friction due to main poppet tipping and plowing of the guide rib, actuator to stem misalignment, stem side loading and abnormal packing friction. Corrective Action: The guide ribs for 1SM-1 were repaired and returned to specifications. A new valve main poppet was installed along with an anti-vibration kit and a stem guiding system with carbon bushing and packing material which will not induce a corrosive environment. The clearance between the valve stem and cover bushing was also increased. The air assist feature has also been installed to provide additional closing margin on Unit 1 MSIVs during Refueling Outage 1EOC17.
3692005003 | McGuire 1 | 09/20/2005 | 11/15/2005 | ML05341040 | <strong>Containment Closure Requirements Not Met During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time this historical condition was identified, Unit 1 was in Mode 5 (Cold Shutdown) at 0 percent power and Unit 2 was in Mode 1 (Power Operation) at 100 percent power. Event Description: In September 2005, the historical practice of re-filling the Ice Condenser ice baskets by blowing ice through a containment penetration during refueling outages was reviewed as a transportability corrective action from Problem Investigation Process (PIP) M-05-1608 and LER 370/2005-03. It was concluded that this practice did not meet Technical Specification (TS) 3.9.4 LCO requirements when performed during core alterations or fuel movement and thus represented an operation prohibited by McGuire's Technical Specifications. McGuire interprets TS 3.9.4 to only allow the Containment Purge(VP) system penetrations to provide direct access from the containment atmosphere to the outside atmosphere during core alterations or fuel movement. This event was not significant with respect to the health and safety of the public. Event Cause: The cause for this historical condition was the use of a non-conservative interpretation of TS 3.9.4 when the safety evaluation for this practice was originally performed. Corrective Actions: All affected procedures were revised to prohibit opening the ice blowing containment penetration during core alterations or fuel movement.
3692005004 | McGuire 1 | 09/17/2005 | 11/14/2005 | ML05341042 | <strong>Ice Condenser Lower Inlet Door Failed Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in Mode 5 (Cold Shutdown) at 0 percent power. Event Description: On September 17, 2005, testing of the forty-eight Ice Condenser Lower Inlet Doors (LIDs) was performed in accordance with Technical Specification (TS) Surveillance Requirement (SR) 3.6.13.6. The "as-found" testing was performed in Mode 5 during the unit shutdown as a first time evolution. This SR ensures all LIDs open uniformly by quantifying resistance in the door hinges and springs through a series of force tests. Two of the forty-eight LIDs failed to meet a portion of the SR test acceptance criteria (TAC). McGuire subsequently determined that these two LIDs could have been previously inoperable in Modes 1-4 for a period longer than allowed by TS. Event Cause: The failure of the two doors has been attributed to excessive spring tensioning caused by corrosion of the rod end/clevis brackets. Inadequate preventive maintenance resulted in excessive force being required to open the two LIDs. Corrective Action: All rod end/clevis brackets on the forty-eight LIDs have been cleaned, lubricated and satisfactorily retested in accordance with SR 3.6.13.6.
3692005005 | McGuire 1 | 09/21/2005 | 11/21/2005 | ML05333012 | <strong>Inoperable Source Range Neutron Flux Monitors During Mode 6 and Core Alterations</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the start of the event, Unit 1 was in Mode 6 (Refueling) at 0% power, and Unit 2 in Mode 1 (Power Operation) at 100% power. Event Description: On September 21, 2005, while Unit 1 was in Mode 6 all source range neutron monitors became inoperable when annunciator alarm circuitry failed. Subsequently, on September 22, 2005 core alteration activities commenced with these monitors inoperable. The inability of the required source range monitors to generate an audible high flux at shutdown alarm was not discovered until September 23, 2005. All other Control room source range neutron flux indications were functioning properly during this period. This event, which constitutes conditions prohibited by Technical Specifications, was determined to be of no significance to the health and safety of the public. Event Cause: The causes of this event are attributed to an inadequate Operator Aid Computer (OAC) alarm response procedure, and the common alarm circuitry of the high flux at shutdown. Corrective Action: Further core alterations were suspended while repairs were made to the annunciator system. Procedural enhancements will be made to ensure a more prescriptive OAC alarm response. Redundant and diverse alarms will be provided for the high flux at shutdown circuitry via the Operator Aid Computer. The source range neutron flux monitor procedures will be enhanced to clarify required features for operability of the components, and Operations training will be strengthened to emphasize the importance of annunciators on operability of components.
3692005006 | McGuire 1 | 12/17/2005 | 02/13/2006 | ML06054043 | <strong>Automatic Reactor Trip and Auxiliary Feedwater System Actuation due to Steam Generator Hi-Hi Water Level</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, both Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On December 17, 2005, the 1A Steam Generator experienced High-High water level when its controlling channel for main feedwater flow failed low. A main feedwater isolation occurred along with a turbine trip, trip of both CF pumps, automatic start of the motor driven CA pumps, and reactor trip. All safety systems needed to respond to this event operated as designed. This event is considered to be of no significance to the health and safety of the public. Event Cause: The cause of this event was intermittent degraded voltage to transmitter 1A SG Channel 1 flow loop (1CFFT5000). Corrective Action: Selected components were replaced. Lessons learned from this event will be incorporated in appropriate training to further strengthen operator response time to steam generator level deviations.
3702005001 | McGuire 2 | 03/02/2005 | 04/25/2005 | ML05125028 | <strong>Automatic Actuation of Motor Driven Auxiliary Feedwater Pumps During Outage</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 3 (Hot Standby) at 0 percent power. Event Description: On March 2, 2005, McGuire Unit 2 experienced an automatic actuation of the 2A and 2B Motor Driven Auxiliary Feedwater (MDCA) pumps. The 2A Main Feedwater (CF) pump was in recirculation mode and, as per procedure, the 2B CF pump was in a tripped condition and out of service. While performing system evolutions, Unit 2 CF system pressure unexpectedly dropped to a level that caused initiation of a low CF pump suction pressure signal which tripped the 2A CF pump. Since the 2B CF pump had previously been placed in a tripped condition, the logic for automatic start of the 2A and 2B MDCA pumps was satisfied and these pumps started as designed. Since the 2A and 2B MDCA pumps started in response to actual plant conditions or parameters satisfying the requirements for initiation of the Auxiliary Feedwater (CA) System safety function, this represented a valid actuation of the CA system. This event was not significant with respect to the health and safety of the public. Event Cause: The cause of this event is attributed to a procedural deficiency. PT/2/B/4250/024, "Feed Water Heater Tube Integrity Test" did not prohibit the restoration portion of the procedure from being performed prior to blocking the CA autostart signal, a procedurally driven task performed upon entry into Mode 4. Corrective Action: Procedure PT/1(2) /B/4250/024 will be revised to ensure blocking of the CA autostart signal (in accordance with the Technical Specifications) has been completed prior to performing the restoration section of the test.
3702005002 | McGuire 2 | 03/03/2005 | 05/02/2005 | ML05131016 | <strong>Ice Condenser Lower Inlet Door Failed Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 2 was in Mode 5 (Cold Shutdown) at 0 percent power. Event Description: On 3/3/05, as-found torque testing of the forty-eight Ice Condenser Lower Inlet Doors (LIDs) was performed in accordance with Technical Specification (TS) Surveillance Requirement (SR) 3.6.13.6. Seven of the forty-eight LIDs failed to meet their test acceptance criteria. These seven LIDs were retested on 3/25/05 (in the as-found condition) and five of the seven LIDS failed to meet their test acceptance criteria. Subsequently, McGuire determined that one or more of these five LIDs could have been previously inoperable in Modes 1-4 for a period longer than allowed by TS. Event Cause: The five doors failing the verification tests on 3/3/05 and 3/25/05 were due to LID spring tension being out of adjustment. Corrective Action: The five LIDs were repaired. All forty-eight LIDs were satisfactorily retested on 3/30/05 (in the as-left condition). LID corrective and preventative maintenance practices will be reviewed for possible enhancements. TSSR 3.6.13.6 and associated Bases will be reviewed for possible enhancements.
3702005003 | McGuire 2 | 03/28/2005 | 05/26/2005 | ML05154030 | <strong>Containment Closure Requirements Not Met During Core Alterations</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 6 (Refueling) at 0 percent power. Event Description: On March 28, 2005, during core alterations on McGuire Unit 2, the Containment Air Release and Addition System (VQ) was aligned to reduce Containment pressure. This became necessary because the Containment Purge Ventilation System (VP) was temporarily out of service and isolated. Since Technical Specification (TS) 3.9.4 only allows the VP System to provide direct access from the Containment atmosphere to the outside atmosphere during core alterations or movement of irradiated fuel assemblies, this activity represented an operation prohibited by McGuire's Technical Specifications. This event was not significant with respect to the health and safety of the public. Event Cause: The cause of this event was omission of relevant information in the VQ System operating procedure and the Bases for TS 3.9.4. Also, an inadequate procedure revision was performed in 2001 on the Containment Closure and Integrity procedure. This revision allowed the VQ System to be in service during core alterations. Corrective Actions: The Containment Closure and Integrity procedure for both units was placed on hold. All relevant procedures will be revised to prohibit VQ operation during the applicable modes of TS 3.9.4. TS Bases 3.9.4 will be revised to clarify the use of automatic isolation valves.
3702005004 | McGuire 2 | 04/08/2005 | 06/06/2005 | ML05166047 | <strong>Actuation of Main Steam Isolation Valves Due to Human Error</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the start of the event, Unit 2 was in MODE 3 (Hot Standby). Event Description: On 4/8/2005, during startup from a Unit 2 refueling outage, Operations was increasing primary system pressure and temperature. During this evolution, Operations misjudged the rate at which Pressurizer pressure and steam line pressure would rise relative to each other. As a result, Pressurizer pressure was not maintained below the value which blocks generation of a Main Steam Line Isolation Signal due to a steam line low pressure condition. Given that Main Steam pressure had not yet increased sufficiently to clear the steam line low pressure condition, a valid and unplanned Main Steam Isolation Signal was generated which closed the Main Steam Isolation Valves. This represented a system actuation reportable as per the requirements of 10 CFR 50.73 (a)(2)(iv)(A). This event was not significant with respect to the health and safety of the public. Event Cause: The primary system temperature and pressure increase was a first time evolution for the Operator controlling primary system temperature and pressure. His lack of experience resulted in misjudgments and inappropriate actions on the part of the Operator. In addition, the Control Room Supervisor misjudged the level of oversight required. Corrective Action: Applicable procedures will be revised as needed to ensure adequate Pressurizer pressure margin is maintained until all steam line low pressure bistables have reset.
3702005005 | McGuire 2 | 03/02/2005 | 06/22/2005 | ML05188004 | <strong>Failure of Main Steam Line Isolation Valve (MSIV) to Close</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 3 (Hot Standby) at 0 percent power. Event Description: On March 2, 2005, 2SM-1, 2D Steam Generator Main Steam Isolation Valve (MSIV), failed to stroke closed during testing. This event, which constitutes a condition prohibited by Technical Specifications, was determined to be of no significance to the health and safety of the public. Event Cause: The cause of this event is attributed to binding caused by insufficient clearance between the valve stem and cover bushing. Corrective Action: 2SM-1 was repaired by improving its packing configuration, installing stronger actuator springs, and increasing the inside diameter of the cover bushing. The MSIVs will be repacked with packing material which will not induce a corrosive environment. An air assist closure feature that was previously removed will be restored to all MSIVs. Until that feature is restored, shutdown stroke testing will be performed for all MSIVs.
3702005006 | McGuire 2 | 06/09/2005 | 07/28/2005 | ML05221037 | <strong>Failure of Containment Floor and Equipment (CFAE) sump discharge outside containment isolation valve to fully close.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in Mode 1 (Power Operation) at 100 percent power and Unit 2 was in Mode 1 at 100 percent power. Event Description: On June 9, 2005, 2WL-65B Containment Floor and Equipment (CFAE) sump discharge outside containment isolation valve (CIV), was determined to be inoperable. 2WL-65B had failed penetration Local Leak Rate Testing (LLRT) during Refueling outage in April 2005. In addition, there were several periods when 2WL-64A (CFAE sump discharge inside CIV) and 2WL-65B were simultaneously inoperable. This event is reportable as a condition prohibited by Technical Specifications and a condition which could have prevented fulfillment of a safety function. This event was not significant with respect to the health and safety of the public. Event Cause: The Apparent Cause of this event is attributed to 2WL-65B's unique design and lack of understanding as to how manual operation of a diaphragm valve equipped with a Rotork Actuator can adversely affect the component. Corrective Action: 2WL-65B's actuator limit switch was readjusted and a successful penetration LLRT was performed. Transportability Analysis determined that 2WL-65B's failure mode is transportable to 15 other valves; 7 on Unit 1 and 8 on Unit 2. A review of valve stroke timing records for these valves confirmed that the valves were operable. Additional corrective actions have been planned to improve operator knowledge and reliability of valves' performance.
3702005007 | McGuire 2 | 10/08/2005 | 12/01/2005 | ML05347032 | <strong>Power Reduction due to Entry into LCO 3.0.3 Caused by Inoperable Control Room Area Cooling Water System</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in Mode 6 (Refueling) at 0% power and Unit 2 was in Mode 1 (Power Operation) at 100% power. Event Description: On October 8, 2005, at 03:20, both trains of the Control Room Area Cooling Water System (CRACWS) were declared inoperable, a condition prohibited by Technical Specifications (TS). Even though one CRACWS train was fully functional and provided cooling to the Control Room during this event, it was determined to be administratively inoperable. A Unit 2 shutdown was initiated when the problems with the CRACWS could not be resolved in the time allowed by the TS. This led to Duke Energy Corporation (Duke) requesting a Notice of Enforcement Discretion (NOED). Following the approval of the NOED, shutdown of Unit 2 was discontinued. This event was determined to be of no significance to the health and safety of the public. Event Cause: The cause of this event is attributed to a defective oil pressure switch on the CRACWS "A" Chiller while the CRACWS "B" Chiller was administratively inoperable due to its reliance on shared and unit designated equipment aligned to the outage unit. Corrective Action: A temporary modification was made to the "A" Chiller during the NOED period. Permanent repairs were subsequently made by replacing the defective oil pressure switch.
3732005001 | LaSalle 1, LaSalle 2 | 02/02/2005 | 03/28/2005 | ML05096036 | <strong>Single Failure Vulnerability of Division 1 and 2 Protective Relay Circuitry Due to Latent Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2005, LaSalle determined that transformer (CT) circuits associated with the 4160 VAC relaying and metering current on any of the CT with the Division 1 and 2 safety related buses. An open circuit an unbalanced phases downstream of a common point in the circuit would have resulted in current condition that would have tripped the associated System Auxiliary Transformer feed breakers. The lockout relay for the bus would have subsequently tripped the other of any of the breakers, including the Emergency bus breakers and prevented closure in a loss of all onsite and Diesel Generator output breaker. This would have resulted buses.offsite AC power to both the Division 1 and 2 safety related A temporary modification was installed on February 2, 2005, to eliminate this vulnerability on both Units 1 and 2. A permanent modification was installed on Unit 2outage. A similar modification will be installed on during the February 2005 refueling The root cause was an existing latent design Unit 1 during its next refueling outage. deficiency not identified in subsequent design reviews.
3732005002 | LaSalle 1 | 04/07/2005 | 09/09/2005 | ML05258022 | <strong>Reactor Core Isolation Cooling (RCIC) Barometric Condenser Vacuum Pump Discharge Check Valve 1E51-F028 Failed Local Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On 4/7/05, local leak rate testing (LLRT) was being performed on LaSalle County Station Unit 1 Reactor Core Isolation Cooling (RCIC)[BN] Barometric Condenser Vacuum Pump Discharge isolation valves 1E51-F069 and 1E51-F028. The procedurally required test pressure could not be achieved between these valves, and the measured leakage was therefore classified as indefinite. Acceptable test pressure and measured leakage were achieved when the test operator mechanically agitated check valve 1E51-F028. The 1E51-F028 check valve was declared inoperable and the 1E51-F069 motor-operated globe valve was closed. The 1E51-F028 valve was replaced and tested acceptably. A root cause investigation determined that the valve selected for this application was not optimal for this application because it was susceptible to internal corrosion and binding. Corrective actions include replacing the current piston lift check valve with a swing check valve, and modifying the pipe slope as needed to eliminate low points that accumulate water.
3732005003 | LaSalle 1 | 05/06/2005 | 07/01/2005 | ML05193007 | <strong>Main Steam Line High Flow Main Steam Isolation Valve Isolation Differential Pressure Switches Failed Due to Manufacturing Error</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2005, during performance of LIS-MS-102 "Main Steam Line High Flow MSIV Isolation Calibration," the high flow differential pressure switch (1E31-NO08B) for theming steam line could not be calibrated within the required band. The switch was replaced and tested successfully. LIS-MS-102 was resumed, and the high flow differential pressure switch for the `C' main steam line (1E31-NO10B) also failed its calibration. It was also replaced and tested successfully. The failed switches were sent to SOR for failure analysis, and the analysis report states that the causes of the failures were silicone contamination on the switch contacts, rusted bearings, and rust sediment in the low side pressure port cavity. The rust resulted from water intrusion into the switch, likely caused by a manufacturing defect. The failures were determined to be from a common cause. The corrective action was to replace the failed differential pressure switches with an improved model that is expected to provide more reliable service.
3732005004 | LaSalle 1 | 08/18/2005 | 10/14/2005 | ML05305037 | <strong>Trip of the System Auxiliary Transformer (SAT) Feed Breaker to Bus 143 Due to Ground Fault in Potential Transformer</strong><br /><i>Abstract:&nbsp;</i>On 08/18/05, the 1B diesel generator (DG) was being run in accordance with surveillance procedure LOS-DG-R1B, "1B Diesel Generator Twenty-Four Hour Run." During this test,the DG output breaker is closed onto Bus 143 and the DG is loaded in parallel with the grid. At approximately 1440 hours CDT, the SAT feed breaker (ACB 1432) to bus 143tripped. The 1B DG continued to run and supply power to bus 143; however, the control room operators observed that the 1B DG cooling water pump was not running and promptly shutdown the 1B DG, leaving bus 143 de-energized. This resulted in bus 143 being de-energized, with no power available to the High Pressure Core Spray System. The cause of the ACB 1432 trip was a phase-to-ground fault in the primary winding of potential transformer (PT) T1 in the 1B DG voltage regulator. The PT was replaced and the 1B DG was restored to operable status at 1410 hours on 8/22/05. Corrective actions include replacement of the Basler model PTs in the voltage regulator circuits of the remaining DGs, and evaluation of a modification to add a load limiting capability to the DG voltage regulators.
3742005002 | LaSalle 2 | 03/12/2005 | 05/04/2005 | ML05137010 | <strong>Pressure Boundary Leakage Discovered in 2D MSIV Drain Line Weld During Refueling Outage VT-2 Examination</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2005, during a scheduled refueling outage on Unit 2, a pinhole leak in a class 1 weld on the outboard Main Steam Isolation Valve drain line (2B21-F028D) was discovered during a hydrostatic test of the reactor coolant pressure boundary. The apparent cause of the leak was a weld inclusion or defect from a Class 1 weld made in 1995. The weld was repaired, non-destructive surface examination performed, and the hydrostatic test was re-performed successfully within acceptance criteria. The subject weld will receive another VT-2 examination during the next refueling outage on Unit 2.
3742005003 | LaSalle 2 | 06/21/2005 | 08/19/2005 | ML05238025 | <strong>Multiple Containment Isolations following Loss of 480 VAC Safety Related Buses due to Failed Neutral Overcurrent Relay</strong><br /><i>Abstract:&nbsp;</i>On June 21, 2005, at 2340, the feed breaker (2AP04E) from 4160 VAC bus 241Y to 480 VAC safety related buses 235X and 235Y tripped open due to a neutral over-current fault on bus 235X. This trip caused a loss of the 2A Reactor Protection System (RPS) Motor-Generator (MG) Set, which resulted in multiple containment isolation valve closures and a Unit 2 half scram. The loss of power also resulted in a loss of the battery chargers for the Division 1 125VDC and 250VDC systems. The 2A Standby Liquid Control (SBLC)subsystem, 2A Residual Heat Removal (RHR), Low Pressure Core Spray (LPCS) and Reactor Core Isolation Cooling (RCIC) systems were declared inoperable due to the loss of Division 1 power. The cause of the breaker trip was a failed silicon controlled rectifier in ABB Type GR-5 neutral over current relay 2451-AP055. The relay was replaced and the inoperable systems were subsequently restored. Long term corrective actions include replacing all safety-related Type GR-5 relays installed at LaSalle County Station.
3822005001 | Waterford 3 | 04/19/2005 | 06/16/2005 | ML05171035 | <strong>RCS Pressure Boundary Leakage due to Primary Water Stress Corrosion Cracking of a Pressurizer Heater Sleeve</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2005, following entry into Mode 5 for the scheduled Waterford 3 Refuel 13 Outage, a visual inspection of the pressurizer (PZR) nozzles and heater sleeves revealed indications of Reactor Coolant System pressure boundary leakage. A small amount of boric acid was discovered in the annulus around PZR heater sleeves C-4 and D-2. Inspection of the PZR carbon steel base metal material surrounding each penetration indicated that no boric acid material wastage had occurred. The boric acid is evidence of Primary Water Stress Corrosion Cracking (PWSCC) of the Alloy 600 heater sleeve and is consistent with industry operating experience for equivalent Alloy 600 PZR heater sleeve configurations and existing root cause analysis for PWSCC in RCS small bore nozzles. Non-destructive examination of the two penetrations revealed the presence of two axially oriented flaws in heater penetration C-4. NDE results of heater penetration D-2 did not identify any discernible defect, therefore, this penetration was excluded as a RCS pressure boundary leak. The one leaking heater penetration was repaired using Alloy 690 half-sleeve material replacement, as part of the scheduled refueling 13 outage preventive weld repair/replacement plan for all the Alloy 600 PZR sleeves and small bore instrument penetrations. There were three previous LERs submitted over the past five years involving evidence of leakage from a principal safety barrier attributed to PWSCC of Alloy 600 material. Plant operations were unaffected and this condition did not compromise the health and safety of the public or plant personnel. This condition is not considered a Safety System Functional Failure (SSFF).
3822005002 | Waterford 3 | 06/09/2005 | 01/12/2006 | ML06018025 | <strong>RCS Leakage Detection Instrumentation and Regulatory Guide 1.45 Non-conformance</strong><br /><i>Abstract:&nbsp;</i>On August 8, 2005, Waterford 3 reported in LER 2005-002-00 that the plant was operated in a condition prohibited by the Reactor Coolant System (RCS) Leakage Detection Technical Specification (TS) 3.4.5.1 due to inadequate testing of the Containment Fan Cooler (CFC) Condensate Flow Switches. On November 17, 2005, an evaluation determined that TS 3.4.5.1 was inadequate in that the leak detection methods specified in TS 3.4.5.1 did not meet the requirements of Regulatory Guide (R.G.) 1.45. The cause of this condition is a historical error in the original configuration of TS 3.4.5.1. Administrative controls have been implemented for TS 3.4.5.1 which take credit for existing TS leakage detection instrumentation that measure the condensate flow from all containment fan coolers and which meets R.G. 1.45 requirements. A TS change request will be submitted to the NRC which accurately describes the leak detection instrumentation which meets R.G. 1.45 requirements. This condition did not compromise the health and safety of the public or plant personnel. This condition is not considered a Safety System Functional Failure (SSFF). This condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition that was prohibited by the plants TS.
3822005003 | Waterford 3 | 07/05/2005 | 09/05/2005 | ML05263007 | <strong>TS Minimum Volume Requirement in DG Fuel Oil Storage Tank B Not Met due to Bent Transmitter Tubing</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2005, with Waterford 3 (W3) in Mode 1, it was determined that Waterford 3 operated in a condition prohibited by Technical Specifications (TS). TS 3 .8.1.1.b.2 requires a minimum volume of 39,300 gallons (97.9%) in the Diesel Generator (DG) fuel oil storage tanks (FOSTs), or a fuel oil volume less than 39,300 gallons and greater than 37,000 gallons (92.3%) of fuel for a period not to exceed 5 days provided replacement fuel is onsite within 48 hours. Contrary to TS 3 .8.1.1.b.2, W3 operated with DG FOST B at 96.8% level (approx. 38,800 gallons) from May 28, 2005, when W3 entered Mode 4 following Refuel 13 to June16, 2005, when fuel was added to the DG FOST B. Therefore, W3 was not in compliance with TS Action b of TS 3.8.1.1 which requires restoration within 72 hours. The cause of this event was inadequate venting of trapped air in the level transmitter process tubing due to the tubing being damaged (bent) during a previous DG B maintenance outage between February 28, 2005 and March 6, 2005. This condition did not compromise the health and safety of the public or plant personnel. Only one DG is required to safely shutdown the plant and the DG FOSTs can be cross-tied. Also, fuel oil is readily available in the near vicinity of Waterford 3. This condition is not considered a Safety System functional failure.
3822005004 | Waterford 3 | 08/29/2005 | 10/27/2005 | ML05304046 | <strong>Loss of Offsite Power During Hurricane Katrina</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2005 at 07:59, a Loss of Offsite Power (LOOP) occurred with the plant in Mode 4. At the time of the LOOP, the plant site was experiencing tropical storm winds of approximately 48 miles per hour. All loads supplied by the non-safety 6.9 kV busses were lost including the Reactor Coolant Pumps 1A, 1B, 2A and 2B. The two emergency diesel generators (EDG) started in response to the LOOP conditions and safe shutdown loads were sequenced onto the two safety busses. Offsite power was available on August 31, 2005; however, Waterford 3 continued to run the safe shutdown loads on the EDGs as grid restoration progressed. After analysis of the surrounding infrastructure and continuing grid restoration activities, the decision was made to cool the plant down to Mode 5 on September 1, 2005. Following grid evaluations, offsite power for Train A was declared OPERABLE at 23:21 on September 1, 2005 and offsite power for Train B at 22:20 on September 2, 2005. The loss of offsite power occurred due to the Entergy transmission system damage caused by Hurricane Katrina. Following continued grid and infrastructure restoration activities and authorization to resume operation by the NRC and Federal Emergency Management Agency (FEMA), the plant was returned to service on September 13, 2005 at 12:16. This condition did not compromise the health and safety of the public or plant personnel.
3822005005 | Waterford 3 | 11/11/2005 | 01/11/2006 | ML06013019 | <strong>Manual Reactor Trip Upon Loss of All Circulating Water Pumps and Lowering Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2005, at approximately 20:34, with the plant operating at 100% power (Mode 1), Waterford 3 manually tripped the reactor due to lowering Main Condenser vacuum, caused by a loss of all Circulating Water (CW) Pumps. Subsequently Emergency Feedwater Actuation Signals (EFAS-1 and EFAS-2) were received due to low Steam Generator Levels. The plant was then maintained in Mode 3 with both Steam Generators being fed from the Auxiliary Feedwater System with Steam Generator levels in the normal operational band for Mode 3. Failure Mode identified a degraded timer relay in the CW Pump discharge valve control circuit as the most likely cause. The relay was replaced prior to plant restart. Emergency Feedwater actuated automatically. Adequate water level was maintained in the Steam Generator to ensure decay heat removal from the RCS. The event is not considered a Safety System Functional Failure. The event did not compromise the health and safety of the general public.
3872005001 | Susquehanna 1, Susquehanna 2 | 11/22/2004 | 09/20/2005 | ML05270024 | <strong>Primary Containment Instrument Lines Located Outside Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On 11/22/2004, it was identified that six Primary Containment instrument lines penetrated the Unit 1 Reactor Building's Railroad Bay. Although the area can be aligned to Secondary Containment, it has not normally been maintained in this configuration. The instrument lines that are located in the Railroad Bay, and have been typically located outside Secondary Containment due to ventilation system alignment practices, are not consistent with assumptions currently found in station licensing documents. This situation was reported in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented structures or systems needed to control the release of radioactive material from fulfilling their safety function. PPL was able to eliminate the non-conforming condition by reconfiguring Secondary Containment in a manner that encompassed the Railroad Bay. On four occasions, however, as noted in the referenced NRC Integrated Inspection Report, PPL temporarily returned the Railroad Bay to its normal configuration (e.g., ventilation outside of secondary containment) to support plant maintenance activities. A misinterpretation of GL 91-18 guidance and PPL's belief that the Secondary Containment function was not affected by returning the plant to its normal and customary ventilation alignment caused PPL to complete the reconfiguration without entering the Secondary Containment LCO 3.6.4.1. Because the Secondary Containment was not restored within LCO Required Action completion times, this situation also constitutes an operation prohibited by the plant's Technical Specifications and is reportable per 10CFR50.73(a)(2)(i)(B). Administrative controls have since been enacted to ensure the Railroad Bay is aligned to Secondary Containment when the Railroad Bay door is not open. The appropriate Tech Spec LCO is being entered when the door must be opened. PPL is planning a modification that will place the instrument lines inside Secondary Containment at all times. There were no adverse consequences to the health and safety of the public as a result of this situation.
3872005002 | Susquehanna 1 | 10/28/2005 | 12/21/2005 | ML06004023 | <strong>TS Required Shutdown due to Excessive Control Cell Friction</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2005 at 1600 hours, Susquehanna operators began the process of shutting down Unit 1 for a planned maintenance outage to address known control cell friction issues. The cell friction issues had manifested during Unit 1's14th fuel cycle when multiple control rods failed to settle into their targeted latched position. At the time of the shutdown, four control rods had been declared inoperable because of excessive rod to fuel channel friction. Other rods, previously known to exhibit slow settling characteristics, would be inserted during the controlled shutdown. It was conservatively determined that any control rods experiencing long settling times would be declared inoperable so that the shutdown would not be slowed by additional testing necessary to prove operability. Technical Specification 3.1.3, Control Rod Operability, would be entered when nine rods had been declared inoperable. Entry into TS 3.1.3.f requires that the unit be taken to Mode 3, Hot Shutdown, within 12 hours. At the time the ninth control rod was declared inoperable at 2332 hours on October 28, Unit 1 had already been reduced to 18% power. The controlled shutdown continued until 0805 hours on October 29, 2005 when insertion of all rods was completed and Mode 3 had been entered by placing the mode switch to the Shutdown position. Entry into the shutdown TS occurred because of a decision strategy that emphasized timely shutdown progress. Additional operability testing, if performed, would have likely precluded any need to enter the TS. With no substantive benefit attainable from such testing, the strategy was sound. Even though the plant shutdown was planned and in-progress, the shutdown became a Technical Specification mandate at 2332 hours on October 28 when the ninth control rod was declared inoperable. Accordingly, this event is being reported as a Tech Spec required shutdown per 10 CFR 50.73(a)(2)(i)(A). There were no safety consequences or compromises to public health and safety as a result of this event.
3882005001 | Susquehanna 2 | 03/20/2005 | 05/12/2005 | ML05144035 | <strong>Degradation of Primary Coolant Pressure Boundary due to Recirculation Pump Discharge Valve Bonnet Vent Connection Weld Flaw</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2005, during the performance of the Unit 2 ASME Class 1 Boundary Leakage Test, a socket weld at the connection to the abandoned bonnet vent piping for the "B" Reactor Recirculation Pump Discharge Valve HV243F031B was found leaking approximately 10 drops per minute. Subsequent investigation revealed a crack in the toe of the weld at the valve's bonnet vent socket weld. The connection was an abandoned piece of 3/4-inch piping that contained a 16-inch long pipe stub that had been cut and capped in 1997 due to a previous vibration-induced weld failure. This condition constituted a degradation of the reactor coolant pressure boundary, and on March 21, 2005, an ENS Notification (#41506) was made to the NRC. The cause of the weld failure was due to inadequate implementation of GE SIL 512 recommendations. The cracked weld was repaired by removing the pipe stub and welding a plug directly into the bonnet connection. A new review of Unit 1 and Unit 2 recirculation lines identified by GE SIL 512 will be performed. The original Recirculation gate valve vent, drain, and stem leak-off lines, previously abandoned will be plugged at the welded joint. Other vibration-prone small bore piping will also be evaluated for susceptibility to weld cracking and corrective actions taken as necessary to prevent future weld failures. There were no safety consequences or compromises to public health and safety as a result of the failed weld.
3882005002 | Susquehanna 2 | 04/10/2005 | 06/06/2005 | ML05165023 | <strong>Degraded 125 VDC Battery Charger Results in Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2005, with Susquehanna Unit 2 in Mode 1 at 100% power, a 125-VDC (EIIS Code: EJ) battery charger's output failed low. Because the DC electrical power subsystem could not be returned to normal operating status within the required LCO action statement time, Unit 2 was shutdown (Mode 3) at 1728 hours as mandated by Technical Specifications. Root cause analysis concluded that a short circuit caused three fast acting fuses to actuate. The short circuit was most probably caused by contact of circuit wiring that had experienced insulation heat damage because of its close proximity to a resistor. However, damage to the wiring itself was not observed, thus rendering this explanation less than conclusive. It is also possible, but less likely, that capacitors or surge suppressors associated with the battery charger shorted but subsequently cleared the condition. Future testing is planned to further investigate these possibilities at the next 125-volt battery charger outage of sufficient duration. Engineering evaluation concluded that Battery 2D630 maintained adequate reserve to meet all accident profile requirements and Station Blackout loads despite the discharge that occurred when the charger failed. In response to this event, circuit wiring was rerouted away from the resistor heat source in all Unit 2 125-VDC chargers. The same rerouting effort is planned for Unit 1. Additionally, preventive maintenance work instructions will be revised to specifically identify and provide inspection criteria for the resistor and wiring. Following repairs, the plant was re-started on April 12. This event is being reported in accordance with 10 CFR50.73(a)(2)(i)(A) as a plant shutdown required by Technical Specifications. There were no safety consequences or compromises to public health and safety as a result of this event.
3882005003 | Susquehanna 2 | 04/28/2005 | 06/21/2005 | ML05188004 | <strong>Reactor Manual Scram due to Loss of Main Transformer Cooling</strong><br /><i>Abstract:&nbsp;</i>At approximately 0700 hours on 4/28/2005 with Unit 2 in Mode 1 at 100% power, the Control Room received a B Phase Main Transformer alarm. Operators were dispatched and found the cooling system for the transformer not operating. Without cooling, plant alarm procedures require removal of the transformer from service. Reactor power was reduced from 100% to 75% while attempting to restore transformer cooling to minimize any adverse impact to the transformer. Attempts to restore the B Main Transformer cooling were unsuccessful and the reactor was manually scrammed at 0719 hours. The event was determined to be reportable under 10 CFR 50.72, reference ENS Notification EN #41646. Following the manual scram, the Unit 2 electrical output breakers automatically opened as designed removing the electrical load from the Main Transformers. The other plant systems also responded per design. RPV water level decreased to -30" due to the SCRAM, which resulted in RCIC initiating. Normal Feedwater and RCIC systems restored water level. The manual scram and subsequent injection of the RCIC system are considered unplanned actuations of systems that mitigate the consequences of significant events and are reportable per 10 CFR 50.73(a)(2)(iv)(A). This event resulted in no actual adverse consequences to the health and safety of the public.
3882005004 | Susquehanna 2 | 03/02/2005 | 07/18/2005 | ML05209037 | <strong>Common Mode Failure of the Inboard 'A' and 'B' Loop RHR Shutdown Cooling Testable Check Valves due to Vibration-induced Seat Damage</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2005, during performance of the as-found LLRT for the 'A' RHR Shutdown Cooling containment penetration X-13A line, the penetration failed to pressurize. During the as-found LLRT for the 'B' RHR Shutdown Cooling containment penetration X-13B line on March 4, 2005, the penetration failed to pressurize. Subsequent investigation identified leakage past the inboard HV251 F050A and B RHR Shutdown Cooling testable check valves. Both valves were disassembled for examination and were found to have significant damage on the body and disk seats. The cause of the LLRT failure was determined to be HV251 F050A and B gross seat leakage. The seat damage was caused by fretting of the valve seats due to cyclic disk motion during plant operation. The valve disks were permitted to move due to pressure across the valves being equalized during the operating cycle and vibration and/or pump pressure pulses from the Reactor Recirculation system provided the motive force for the cyclic disk motion. The valves were repaired and satisfactory as-left LLRT results were obtained. Core flow restrictions we reimposed for Unit 2 fuel cycle 13 to prevent damage to the HV251 F050A and B valves. Planned corrective actions include evaluation of a possible modification solution to provide a differential pressure across the check valve.Also, Unit 2 procedure TP-264-034, Reactor Recirculation/RHR Injection Loop Hydraulic Response evaluation will be performed to allow stroking of the Unit 2 HV251 F015A and B outboard isolation valves at power, and monitoring of vibration effects. There were no actual safety consequences as a result of the damage found in the check valves.
3882005005 | Susquehanna 2 | 06/06/2005 | 09/16/2005 | ML05270037 | <strong>Reactor Automatic Scram due to a Main Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>At 1233 hours on 6/6/2005 with Unit 2 operating in Mode 1 at 100% power, the reactor automatically scrammed as a result of a turbine trip from a generator lockout. The main generator excitation system had failed to positively respond to changes to the offsite grid, which resulted in a loss of generator field, causing the lockout. Although plant data was inconclusive in determining what initiated the event, the most probable cause was an increased resistance in the main generator exciter field circuitry. Based on the unplanned actuation of RPS, this event was determined to be reportable under 10 CFR 50.72, reference ENS Notification EN #41746. Following the automatic scram, two Main Steam Safety Relief Valves opened and then closed to initially control reactor pressure. The Main Steam Bypass Valves were subsequently able to control pressure. Several balance of plant systems were impacted by the generator voltage perturbation but there were no unusual electrical transients or challenges to the station's safety-related electrical systems. All plant safety systems responded per design. Reactor water level dropped to -6 inches and was restored to +35 inches by normal feedwater level control. There were no challenges to containment or evidence of fuel failure. The automatic scram was an unplanned actuation of a system designed to mitigate the consequences of a significant event and is reportable per 10 CFR 50.73(a)(2)(iv)(A). This event resulted in no actual adverse consequences to the health and safety of the public.
3892005001 | St. Lucie 2 | 02/10/2005 | 04/08/2005 | ML05105035 | <strong>Degradation of ASME Class 1 and 2 Safety Injection Instrumentation Lines</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2005, St . Lucie Unit 2 was in Mode 3 less than 1750 psia, Hot Standby, as work continued to complete the SL2-15 refueling outage . FPL identified leakage from two locations on the 2B1 safety injection piping pressure transmitter instrumentation line. The cause of the leakage was due to cyclic fatigue failure caused by operationally induced vibration . The piping was repaired and a vibration tie-back support was added to reduce vibration loading .
3892005002 | St. Lucie 2 | 05/13/2005 | 07/01/2005 | ML05195033 | <strong>Valve Mispositioning Led to Inoperable Iodine Removal System Train</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2005, with Unit 2 in Mode 1 operation at 100 percent reactor power, valveV07408, the 2A hydrazine pump discharge to storage tank relief bypass valve, was found to be locked open instead of its required locked closed position. This rendered the`A' train of the iodine removal system inoperable. The valve was immediately closed. The investigation revealed that the train was inoperable due to non-licensed operator human errors during the restoration from a previous surveillance test, and that the condition existed longer than allowed by the Technical Specifications. The operators involved received remediation and a non-licensed operator human fundamentals class is being developed to train on this event. The redundant train was not affected by this condition. Additionally, the use of alternate analytical methods concluded that dose consequences were not impacted. Therefore, this event had no adverse impact on the health and safety of the public.
3892005003 | St. Lucie 2 | 08/11/2005 | 10/10/2005 | ML05292006 | <strong>Personnel Error Caused Partial Loss of Feedwater and Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2005, St. Lucie Unit 2 was in Mode 1 operation at 100 percent reactor power. Personnel errors by a non-licensed maintenance supervisor caused a de-energization of two electrical buses which resulted in a partial loss of feedwater event and manual reactor trip based on lowering steam generator levels. The event occurred when the maintenance supervisor opened the incorrect breaker cubicle during an equipment clearance order walkdown, and caused the spurious operation of a lockout relay when the breaker cubicle door was closed. In addition to the manual reactor trip, there were automatic actuations of the A train emergency diesel generator and auxiliary feedwater system. Safety related equipment responded to the event as required. Corrective actions included maintenance stand-downs and training. There were no adverse safety consequences as a result of this event.
3902005001 | Watts Bar 1 | 03/11/2005 | 05/10/2005 | ML05133025 | <strong>Two Trains of ABGTS Inoperable</strong><br /><i>Abstract:&nbsp;</i>In support of the Unit 1 Cycle 6 refueling outage, the Containment Hatch was opened and the Containment Purge System was placed in operation on March 3, 2005. Fuel movement in the Spent Fuel Pool was initiated on March 9, 2005, for the inspection of fuel assemblies. On March 11, 2005, the Operations staff was notified that having the plant in a configuration where the Containment Hatch was open while the Containment Purge System was in operation, made both trains of the Auxiliary Building Gas Treatment System (ABGTS) inoperable. Limiting Condition for Operation (LCO) 3.7.12, "ABGTS," requires that the system be operable during the movement of irradiated fuel assemblies in the fuel handling area. The basis for not operating the Containment Purge System if the Containment Hatch is open during the conditions when the ABGTS is required to be operable is contained in two System Descriptions. Based to these restrictions, Operations personnel entered Action D of LCO 3.7.12 at 08:30 on March 11, 2005, for both trains of ABGTS being inoperable. At the time Operations entered the action, fuel movement had been suspended. The inoperablity of both trains of the ABGTS is being reported under 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function.
3902005002 | Watts Bar 1 | 11/14/2005 | 04/18/2007 | ML07109045 | <strong>G45 Fuel Assembly Clad Damage</strong><br /><i>Abstract:&nbsp;</i>On November 14, 2005, WBN Unit 1 was at 100 percent power and inspection results were being reviewed to establish the cause of a cladding leak in fuel assembly G45. The existence of a cladding leak was initially established during Cycle 6 operation through sampling of the Reactor Coolant System (RCS) that identified elevated levels of Iodine 131 (1-131) and Xenon 133 (Xe-133). This condition was documented in TVA's corrective action program and one element of the planned actions was the examination of the spent fuel during the Cycle 6 refueling outage. In-mast sipping was performed during the outage and established that fuel assemblies E59, G45 and H03 were leaking. The inspections identified a one-inch gap in the fuel cladding on fuel rod P-9 of fuel assembly G45. The visible damage to the rod was located approximately six inches above grid number 7. Due to this damage, it was concluded that some fuel pellet material (up to three fuel pellets) has been dislocated from rod P-9. Fragments of the pellets appeared to be lodged on the top of grid number 7. The corrective actions include measures to limit the radiological consequences of the fuel degradation and establish limitations on power escalation.
3952005001 | Summer 1 | 05/18/2005 | 11/29/2005 | ML05336029 | <strong>Emergency Diesel Generator Start and Load due to a Loss of Vital Bus</strong><br /><i>Abstract:&nbsp;</i>At 0154, May 18, 2005, during performance of relay testing, differential lockout 86T3 was manually actuated resulting in lockout of transformers XTF0031 and XTF0032. This resulted in a loss of all balance of plant (BOP) busses, loss of vital bus 1DB, an auto start of 'B' Diesel Generator (DG), and the sequencing of required ESF loads. Plant Engineered Safeguards Features (ESF) systems responded per design as the "B" DG started and sequenced ESF loads. There were no major problems due to the event; however, the Diesel Fire Pump did not start as expected on a loss of BOP bus 1C2. A review of plant response data showed the Residual Heat Removal (RHR) flow was in the process of coasting down and was restored to full flow within 20 seconds. The inlet temperature of the RHR Heat Exchanger increased approximately 0.3 degrees F due to this event. There was no change in Reactor Coolant System (RCS) level. VCSNS was shutdown in Mode 5 during Refueling Outage 15. The 1DB bus was placed on normal feed at 0240 and power was completely restored to the BOP busses at 0306. A root cause evaluation determined the following causes: (1) nothing indicated this was a new or first time performed task, (2) labeling of the lockout relay did not associate the task with the transformers, (3) the maintenance procedure did not contain precautions or information related to manual actuation of the lockout relay, (4) the task sheet did not contain any reference to the transformers, and (5) the work package review failed to identify plant effects of the relay actuation.
3952005002 | Summer 1 | 05/28/2005 | 04/06/2006 | ML06101024 | <strong>Mode 3 Entry with an Inoperable Emergency Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2005 at 2000 hours during Operator walkdown of the main control board, the oncoming nightshift crew discovered the "A" Motor Driven Emergency Feedwater Pump (MDEFP) switch was in Pull-To-Lock (PTL) with the plant in Mode 3. South Carolina Electric & Gas Company (SCEG) was performing start-up of V. C. Summer Nuclear Station (VCSNS) following the recent refueling outage. The plant entered Mode 3 on 5/28/05 at 1545 hours. In Mode 3 the Emergency Feedwater (EFW) pumps are required to be Operable. The "A" MDEFP switch was apparently placed in Pull-To-Lock (PTL) following extensive retesting of the EFW pumps over the previous 24 hours. The last test occurred at approximately 1100 hours on 5/28,05. With the "A" MDEFP inoperable, the plant was in a condition prohibited by VCSNS Technical Specification (TS) 3.7.1.2. Upon discovery, the "A" MDEFP switch was placed in Normal-After-Stop and the pump was declared Operable. This event is attributed to procedural weaknesses in conducting multiple tasks concurrently for plant startup influenced by insufficient administrative controls. Also, an additional contributing factor was that the Bypass Inoperable Status Indication (BISI) program did not provide a back up indication that the EFW system was out of alignment due to the Integrated Plant Computer System (IPCS) computer being upgraded and not fully functional at the time of the event.
3952005003 | Summer 1 | 08/25/2005 | 03/27/2007 | ML07088003 | <strong>Plant Trip and Associated Fire in B Condensate Pump Motor</strong><br /><i>Abstract:&nbsp;</i>On 08/25/2005, at approximately 1126, the B Condensate Pump tripped and the A Condensate Pump was started immediately. The A Condensate pump discharge valve was extremely slow to respond to the open signal, resulting in a decreasing Deaerator (DA) level. At 1129, smoke was reported coming from the B Condensate Pump motor. There was no visible flame at this time. At 1133, all Feedwater Booster Pumps (FWBP) and Main Feedwater Pumps (MFP) tripped due to LO-LO DA level. As a result, the Main Turbine tripped causing a Reactor trip with Reactor power greater than 50%. At 1138, the Fire Brigade was assembled to respond to the fire. At 1141, a Notification of Unusual Event (NUE) was declared due to the fire in the Protected Area greater than 15 minutes in accordance with Emergency Plan Procedure (EPP) 001.1. Telephone notification was made in accordance with 10CFR72(A). At 1317, the fire was declared out in the B Condensate Pump. At 1327, the Site downgraded from the NUE. After repairs were completed the unit was restarted and achieved criticality on 08/27/05 at 0603. The Main Turbine was placed on line on 08/27/05 at 1724. The unit returned to full power operation on 08/28/05 at 1800. The delayed opening of the A discharge valve was determined to be due to wear and galling that led to binding under high dP conditions. All three Condensate Pump discharge valves were replaced or restored to original design in refueling outage (RF16) and will be placed in the plant preventive maintenance program.
3972005001 | Columbia | 02/24/2005 | 04/21/2005 | ML05123032 | <strong>Potential Breach of Secondary Containment Following Seismic Event</strong><br /><i>Abstract:&nbsp;</i>On 2/25/05, Energy Northwest reported (ref: Event Report 41442) a condition at Columbia Generating Station that was discovered while reviewing plant service water (TSW) [KG] system design documents. Energy Northwest determined that seismic category II TSW piping in the turbine (TG) [NM] and radwaste (RW) [NE] buildings could rupture and drain during a seismic event. Draining of the loop seal in this piping would result in an inoperable secondary containment (SC) [NG] because two TSW system high point vent valves located within the secondary containment would automatically open resulting in direct communication between SC atmosphere and the TG/RW atmospheres. Such an occurrence would exceed the SC leakage rate assumed in Columbia's accident analysis. To prevent an excessive leakage rate during such an event, one of the two vent valves has been deactivated in the closed position. Columbia's safety analysis does not postulate a release of radioactive material in excess of Part 100 limits for a Safe Shutdown Earthquake (SSE) that causes SC to become inoperable in this fashion. Analysis shows that the SSE will not in itself cause a LOCA and it is beyond design and licensing bases to assume a LOCA coincident with a seismic event. In the event that the SSE made SC inoperable, the Technical Specifications (LCO 3.6.4.1.B) require that the plant be in mode 3 in 12 hours and in mode 4 in 36 hours. Since this is achievable it is reasonable to conclude that, in the event described in the report, plant shutdown can be accomplished without radiological release and within the completion time of the action required by the Technical Specifications. Although safe shutdown of the plant without radiological release is assured post SSE, SC would not be considered operable in the reported condition because seismic requirements were not met. Therefore this condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) because SC was inoperable for a greater period of time than allowed by Technical Specifications.
3972005002 | Columbia | 03/16/2005 | 05/10/2005 | ML05137043 | <strong>High Pressure Core Spray System Inoperability Due to Cracks in the Pump Motor's Upper Air Deflector</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2005, Energy Northwest took the High Pressure Core Spray (HPCS) pump out of service to investigate the source of a motor oil leak. During the course of this inspection, personnel discovered cracks in the HPCS pump motor upper air deflector. The root cause for the degraded air deflector is critical dimensions were not maintained during the motor reassembly process in 1992. The degraded air deflector was removed and replaced within the completion time allowed by the Technical Specifications. Long term corrective actions include the development and implementation of a procedure to ensure Energy Northwest has or obtains the available critical information and vendor representation necessary to successfully perform major overhaul or refurbishment work on insignificant plant equipment. Prior to completing refueling outage 17, a visual examination of selected large motors will be performed. This event did not adversely affect the health and safety of the public. Although this event is reported as a safety system functional failure, the ability and the duration of the system to perform its safety function in the as-found condition is the subject of a separate evaluation. By plant design, the emergency core cooling functions can be performed by several diverse systems that were not impacted by this condition. A similar event was reported by Energy Northwest as LER 92-025.
3972005003 | Columbia | 06/15/2005 | 08/15/2005 | ML05235017 | <strong>Reactor Trip due to Digital Electro-Hydraulic (DEH) Control System Failure</strong><br /><i>Abstract:&nbsp;</i>On June 15, 2005 at 1400 hours, the reactor tripped from 100% power. The trip resulted from a Reactor Protection System (RPS) actuation due to a failure in the Digital Electro-Hydraulic (DEH) system that caused the four turbine throttle valves to spuriously stroke from full open to full close. Although no specific DEH system failure could be identified, the three circuit cards providing the control signals to the four turbine throttle valves were replaced. These cards were identified as the most likely source of the DEH system failure. The root cause of this event is the DEH Control System design has single point vulnerabilities and the cards in this system do not exhibit a predictable failure mechanism which would allow replacement prior to failure. Long-term corrective actions are being pursued as identified in Problem Evaluation Request 205-0424. Energy Northwest is performing a single Failure Vulnerability Assessment to identify and address single failure vulnerabilities. This event did not adversely affect the health and safety of the public. A similar event was reported by Energy Northwest as LER 2004-004-00.
3972005004 | Columbia | 06/23/2005 | 08/22/2005 | ML05242048 | <strong>Reactor Scram During Plant Startup due to Reactor Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2005, Columbia Generating Station was in Mode 1 with the reactor operating at approximately 23 percent power. At 13:46 PDT, an automatic reactor scram occurred due to a low water level condition in the reactor vessel. The low reactor water level condition was caused by an inadvertent loss of reactor feedwater pump RFW-P-1B due to a false low suction pressure signal caused by human error during planned maintenance activities. Control room operators entered appropriate Emergency Operating Procedures and stabilized the plant following the reactor scram. Plant systems responded as designed with the exception of RCIC as discussed below. As long term corrective action, a time delay will be installed or the low suction pressure trip removed to prevent spurious RFW pump trips. The RCIC system was manually started to restore reactor water level and was later manually tripped. The system had to be reset locally due to tripped mechanical overspeed trip linkage. During two subsequent attempts to restart RCIC the pump tripped on low suction pressure. Operators were then able to successfully start RCIC with the flow controller in manual. A time delay has been added to the RCIC low suction pressure trip logic to resolve this issue.
3972005005 | Columbia | 07/28/2005 | 09/26/2005 | ML05278004 | <strong>Inoperable Standby Liquid Control Pump due to Incorrect Fuse</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2005, an incorrect fuse was found to have been installed in the circuitry associated with Standby Liquid Control System Pump 1A. This condition resulted in the pump being inoperable for a period of approximately 22.5 days. The fuse was promptly replaced with the correct fuse and the pump was restored to an operable status. The cause of this event was an inadequate self verification process combined with a less than adequate implementing procedure for controlling the fuse replacement process. An extent of condition review has identified additional instances of incorrect fuses; however, no additional operability concerns have been identified. Long term corrective actions to prevent recurrence are being developed within the Energy Northwest Corrective Action Program. A risk assessment of this condition was performed and this condition was not safety significant. No recent similar events have been reported by Energy Northwest.
4002005001 | Harris | 01/27/2005 | 03/28/2005 | ML05087038 | <strong>Reactor Auxiliary Building Emergency Exhaust System Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>At approx. 14:00 on Jan. 27, 2005, with reactor power approximately 100%, Harris Nuclear Plant identified a single failure vulnerability for both trains of the Reactor Auxiliary Building Emergency Exhaust System (RABEES). When the RABEES filtration trains are in their standby alignment, the cooling bleed valve associated with the train that was last running remains open. This bleed valve is a motor operated valve located at the inlet to the opposite train's filter unit and shuts when the associated train fan starts. If a Safety Injection Signal occurs coincident with a loss of the electrical bus for the last running train, the open bleed valve would fail to shut upon start of the associated train's fan creating an air flow leakage path that was not considered in the design bases for RABEES. This leak path could reduce the exhaust flow from the RABEES boundary and prevent the system from establishing the required negative 1/8 inch water gauge pressure in the areas served by RABEES. The root cause is a deficiency from initial plant design. Procedure changes were implemented on 1/28/05 to ensure that both bleed valves are shut when both RABEES fans are secured. When a single RABEES fan is in service, the applicable Tech Spec LCO is entered because one of the bleed valves must remain open. An engineering change has been initiated to eliminate the single failure vulnerability.
4002005002 | Harris | 05/01/2005 | 06/30/2005 | ML05194042 | <strong>Manual Reactor Trip Following a Trip of the "B" Condensate Pump Motor</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2005 with the reactor at approx . 100% power, operators at the Harris Nuclear Plant (HNP) manually tripped the reactor in response to an automatic trip of an operating condensate pump (CP) . The "B" CP tripped due to a motor shaft shear at the top of the motor coupling hub. By design, the trip of the "B" CP caused subsequent trips of the "B" condensate booster pump and the "B" main feedwater pump (MFP). As directed by plant procedures, the operators manually tripped the reactor upon the trip of a MFP with initial reactor power greater than 90% . The manual reactor trip coupled with the trip of the "B" condensate and feedwater (FW) train resulted in a reduction of steam generator (SG) water levels. The subsequent low-low SG levels resulted in an auto-start of the auxiliary FW pumps as designed. Safety systems functioned as required. The cause of this unplanned trip was the loss of FW to the steam generators initiated by the motor shaft shear for the "B" CP . The root cause of the motor shaft shear is inadequate controls for a vendor weld repair. Completed corrective actions include replacing the failed motor . Planned corrective actions include improving process controls for shaft weld repairs and subsequent non-destructive examination, improving seal installation techniques, establishing coupling inspection criteria, and improving monitoring capability of the CPs.
4002005003 | Harris | 06/05/2005 | 08/03/2005 | ML05222032 | <strong>Equipment Drain System Isolation Valve Inoperable Longer Than Its Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2005, upon review of troubleshooting data for an equipment drain system isolation valve, the Harris Nuclear Plant (HNP) identified that the valve had sufficient leakage past its seat to result in declaring the valve inoperable. Operations was notified immediately, and the valve was declared inoperable per Technical Specifications (TS) 3.6.3. Upon review, it was determined that this condition had existed since June 5, 2005. Thus, the approximately three-day delay before completing the review of the troubleshooting data and declaring the valve inoperable resulted in exceeding the allowed outage time for this condition (i .e., the 4-hour action statement per TS 3.6.3). The condition was rectified immediately upon discovery. The root cause of this event is that the troubleshooting procedure did not provide guidance specific to troubleshooting this operable equipment. This lack of guidance allowed troubleshooting to be performed on this equipment without fully understanding the limits for operability. The valve was repaired, tested satisfactorily, and returned to operation. The corrective action to prevent recurrence is to revise the troubleshooting procedure to provide specific guidance requiring acceptance criteria to be established for troubleshooting on operable components .
4002005004 | Harris | 07/12/2005 | 09/09/2005 | ML05258017 | <strong>ESCW Inoperable for a Period Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 5, 2004 Engineering Change (EC) 51444 inadvertently introduced reliance on a manual action to ensure operability of the Essential Services Chilled Water System (ESCW) in the event of a sustained loss of Service Air (SA) pressure. On March 5, 2005 temporary modification EC 60425 manually isolated the expansion tank, and issued detailed procedure guidance, meeting the requirements of Information Notice (IN) 97-78, to maintain ESCW expansion tank pressure. Between November 5, 2004 and March 5, 2005, instructions provided to the operator, while feasible, did not have sufficient detail to meet NRC guidance for manual actions (IN 97-78). Although functional, both trains of ESCW are considered to have been inoperable for a period longer than allowed by Technical Specification (TS) 3.7.13. The root cause of this event was that site personnel failed to recognize that the plant had inadvertently introduced reliance on an operator manual action to ensure operability, in the event of a sustained loss of SA, without fully documenting actions taken to meet the guidance of IN 97-78 and Nuclear Energy Institute (NEI) 96-07. The corrective actions to prevent recurrence are to provide 10CFR50.59 refresher and real time training covering operator manual actions. The procedure governing the EC process will be revised to provide guidance concerning requirements for manual actions.
4102005001 | Nine Mile Point 2 | 03/17/2005 | 12/07/2005 | ML05357022 | <strong>Both Standby Gas Treatment Subsystems Inoperable due to an Original Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2005, Nine Mile Point Nuclear Station, LLC determined that on several occasions during the last three years, the plant had operated with both subsystems of the Standby Gas Treatment (SGT) system simultaneously inoperable, that appropriate Technical Specification (TS) Limiting Conditions for Operation were not entered, and that actions prescribed by the TS were not initiated. Plant operating procedures for primary containment inerting, de-inerting, and purging permitted operation of an SGT subsystem with the filter train recirculation line pressure control valve (PCV) in the manual control mode and not fully closed. In this configuration, the SGT subsystem was not capable of automatically performing its design basis secondary containment drawdown function and, therefore, should have been considered inoperable. Subsequent review and evaluation determined that the operating procedures also allowed the cross-connect line between the two SGT subsystems to remain open during purging operations, thereby resulting in the potential loss of both SGT subsystems in the event of a loss of coolant accident during purging. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's Technical Specifications and 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented fulfillment of a safety function of the SGT system. The cause of this event was an original design deficiency in that the PCVs do not return to the automatic operating mode on an SGT system initiation signal. Also, personnel involved with development and review of the original operating procedures apparently did not recognize potential system impacts when operating an SGT subsystem in the purge mode. Plant operating procedures associated with primary containment purging were revised to require (1) declaring an SGT subsystem inoperable when operated with a pressure control valve in manual and (2) that at least one valve in the cross-connect line be verified closed.
4122005001 | Beaver Valley 2 | 07/19/2005 | 11/18/2005 | ML05329009 | <strong>Containment Isolation Valve Relay Failure Unknowingly Leads to Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2005, one of the two Main Steam System isolation valves (2MSS-S0V105C) on the steam supply line from 21C steam generator leading to the steam turbine-driven auxiliary feedwater pump (TDAFWP) unexpectedly opened at Beaver Valley Power Station (BVPS) Unit No. 2. The control room verified that no start signal to the TDAFWP existed or was necessary and that the redundant steam isolation valve (2MSS-S0V105F) on that steam line remained closed. 2MSS-SOV105C was declared inoperable. During follow-up investigation actions, it was determined that a sequence of three cascading component failures occurred, the third of which was a passive failure of an auxiliary control circuit relay (3D-SSRAB) in such a manner as to prevent it from being able to perform its intended automatic containment isolation signal transfer function. The passive failure wasnot discovered until July 19, 2005. Since it was unknown on July 14, 2005 that Relay 3D-SSRAB failed making four containment isolation valves inoperable, the containment penetrations associated with these four valves were not isolated with a deactivated closed valve within four hours as required by Technical Specification3.6.3.1 Action a. This is a condition prohibited by plant Technical Specification, and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The plant risk associated with the BVPS Unit 2 event that occurred on July 14, 2005 is considered to be very low. The root cause was a process deficiency for personnel to look for collateral failures.
4122005002 | Beaver Valley 2 | 08/02/2005 | 09/30/2005 | ML05278029 | <strong>Automatic Actuation of Standby Service Water Pump Following Unexpected Service Water Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On August 2, 2005 at 1448 hours, Beaver Valley Power Station (BVPS) Unit No. 2 unexpectedly experienced a trip of the "A" Service Water Pump (2SWS-P21A) which was operating on the "A"Service Water System (SWS) pipe header. The pump motor tripped on ground over current.The "B" Standby Service Water System pump (2SWE-P21 B) automatically started on low Service Water header pressure on the "B" piping train header and recovered pressure in both the "A" and"B" SWS headers. The "C" Service Water Pump (2SWS-P21 C) continued to operate normally during this event supplying "B" SWS header.This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) / (a)(2)(iv)(B)(9) as a condition that resulted in the actuation of an emergency service water system that does not normally run and that serves as ultimate heat sink since the actuation of 2SWE-P21 B was valid. The unexpected trip of the BVPS Unit 2 Service Water Pump 21A was the direct cause for the automatic actuation of the BVPS Unit 2 Standby Service Water Pump 21 B, due to a motor stator insulation breakdown that resulted in a turn-to-turn short. The safety significance associated with the over-current trip of the running service water pump 2SWS-P21A that occurred at BVPS Unit 2 on August 2, 2005 is considered to be very low.
4162005001 | Grand Gulf 1 | 02/11/2005 | 04/06/2005 | ML05096057 | <strong>Reactor SCRAM Due to Loss of Service Transformer 11 Caused By Animal Intrusion</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2005 at 1959, Grand Gulf experienced an automatic reactor scram as a result of breaker 552-1105 tripping due to a ground fault on the 34.5 kV bus work of Service Transformer ST11. Loss of ST11 resulted in the loss of power to 12HE, 13AD and 15AA buses. Emergency Diesel Generator (EDG) 11 started on a loss of power and connected to the 15AA bus. All control rods inserted to 00 position. Reactor vessel water level dropped to approximately minus 75 inches on wide range level instrumentation before the High Pressure Core Spray (HPCS) and Reactor Core Isolation Cooling (RCIC) systems, initiated at Reactor Vessel Water Level Low Low, Level 2 (minus 41.6 inches), and restored level to the normal operating band. Concurrent with this event, EDG 13 (Division III) started on Reactor Vessel Water Level Low Low, Level 2. Standby Service Water (SSW) started to support EDG operation. Containment isolation occurred as a result of Reactor Vessel Water Level Low Low, Level 2. The affected bus was lined up to other available power sources. The safety related bus was synchronized back to the grid and the EDGs were secured. Normal feedwater level control was established and both HPCS and RCIC were secured.
4162005002 | Grand Gulf 1 | 04/27/2005 | 06/27/2005 | ML05179038 | <strong>Incorrect Assumption Used In Development Of Air Operated Valve Program</strong><br /><i>Abstract:&nbsp;</i>On April 28 and 29, 2005 Grand Gulf Nuclear Station made eight hour non-emergency calls (EN#s 41645 and 41650) to the NRC pursuant to 10 CFR 50.72(b)(3)(v)(D), Accident Mitigation. The calls were the result of discovery that original assumptions used in development of the Air Operated Valve (AOV) program did not consider instantaneous loss of the non safety related Instrument Air system. Failure to include loss of Instrument Air in the original assumptions produced negative margin for secondary containment isolation valve (SCIV) closure under some postulated accident conditions. All of the affected valves are flex wedge gate valves equipped with double acting Ralph A. Hiller Company actuators . It was determined that the actuator mounted accumulators would not provide sufficient air pressure to ensure positive closure of these SCIVs against postulated maximum expected differential pressure (MEDP) concurrent with loss of the Instrument Air system. A detailed review of all AOV primary and secondary containment isolation valves equipped with Ralph A. Hiller actuators was performed. The majority of the valves were determined to be operable or operable but degraded . The small number of valves that were determined to be inoperable were placed in their Technical Specification required closed position.
4162005003 | Grand Gulf 1 | 10/07/2005 | 12/19/2005 | ML05354003 | <strong>LER 2005-003-00 - Mode Change Contrary to Technical Specification LCO 3.0.4</strong><br /><i>Abstract:&nbsp;</i>The Division I Load Shed and Sequencer power supply was replaced on October 7, 2005 as part of routine preventative maintenance. During a Technical Specification (TS) Surveillance performed on October 25, the as found voltages for the Division I Engineered Safety Features Degraded Voltage set points were found to be higher than the TS Allowable Values. This condition was immediately corrected; however, since the cause of the setpoints being outside the allowed values occurred during the power supply replacement on October 7, the setpoints had been out of the allowable values from October 7 until October 25. TS require that the setpoints be brought to within allowable values within 12 hours or declare the associated emergency diesel generator (EDG) inoperable (which prohibits changing plant operational modes). Since the impact of the power supply replacement on the Bus Under Voltage bistable setpoints was not recognized and the appropriate TS action statement was not entered, the station violated TS 3.0.4 when the plant was brought into Mode 2 on October 16 and again on October 18 when the plant was brought into Mode 1. This condition was determined to be reportable in accordance with 10CFR50.73(a)(2)(i)(B) since the plant was in an Operation or Condition prohibited by TS 3.0.4. There was no loss of safety function since it was limited to a single division and was a deviation in a setpoint. The system would have actuated somewhat earlier on a low voltage transient but would have functioned properly otherwise.
4232005001 | Millstone 3 | 02/24/2005 | 08/25/2005 | ML05257042 | <strong>Hydrogen Recombiners Out of Service</strong><br /><i>Abstract:&nbsp;</i>On 2/24/05, with Unit 3 at 100% power, during the performance of a surveillance test (SP3613A.2-1) on the"A" Hydrogen Recombiner [BB], the system failed leak tightness causing the "A" Hydrogen Recombiner to be declared inoperable. Investigation revealed that a routine maintenance activity conducted on September 7, 2004, required a compression fitting in the system to be disassembled. This fitting was reassembled improperly. Following the work, a post maintenance test was successfully completed. A surveillance test conducted on February 24, 2005, revealed the compression tubing fitting failure. It is hypothesized that the fitting began to leak when it was stressed (either mechanically or thermally) between the tests. The period when the "A" Hydrogen Recombiner was inoperable exceeded the Technical Specification (TS) Allowed Outage Time (AOT) of 30 days. Additionally, the "B" Hydrogen Recombiner was taken out of service for routine maintenance on October 20, 2004, and January 11, 2005, causing a loss of safety function. This event/condition is being reported pursuant to 50.73(a)(2)(i)(B), related to operation in a condition prohibited by the Technical Specifications and 50.73(a)(2)(v)(D), related to a condition that could have prevented the fulfillment of the safety function of a system. The apparent cause was poor workmanship resulting in a poorly assembled compression fitting. The threaded tubing compression connection was galled and not fully tightened onto the ferrule.
4232005002 | Millstone 3 | 04/17/2005 | 06/16/2005 | ML05179019 | <strong>Inadvertent Reactor Trip and Safety Injection</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2005 at 0829, during normal 100% power operating conditions the solid state protection system (SSPS) generated an "A" Train SSPS Steam Line Pressure Low SI/MSI signal that tripped the reactor, closed the main steam isolation valves, and started one train of the emergency core cooling system (ECCS). Following the trip, all control rods inserted and the auxiliary feedwater system actuated automatically as expected, however the turbine driven auxiliary feedwater pump tripped on startup. One of the "B" steam generator safety valves lifted. Control room operators entered the emergency operating procedure network, manually initiated "B" safety injection (SI)actuation so as to have a two-train SI condition, and continued to place the plant in a stable condition. Based on plant indications during the event an NRC emergency classification of Alert was declared (Event No. 41607). Within one hour of event initiation, plant parameters were stabilized and ECCS systems were stopped and placed in a standby condition.The root cause of the event was that diode leads on a universal logic card in the SSPS were coated with a material susceptible to whisker growth that eventually shorted the card output and produced an inadvertent SI signal. Corrective actions included replacing the affected card and inspecting, cleaning and replacing additional cards in the SSPS. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A). In addition, this report satisfies the Technical Specification 3.5.2 special reporting requirement and satisfies the 10 CFR 21 evaluation, notification and reporting obligation.
4232005003 | Millstone 3 | 09/29/2005 | 11/10/2005 | ML05326041 | <strong>Manual Reactor Trip Due to Loss of Two Circulating Water Pumps in Same Condenser Section</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2005, at approximately 1313 with the unit in Mode 1 at 100 percent power, Millstone Unit 3 reactor was manually tripped due to the loss of two circulating water [CW] pumps in the same condenser section. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of any of the systems listed in 50.73(a)(2)(iv)(B). This includes Reactor Protection System [RPS], actuation Reactor trip. At approximately 1313 on September 29, 2005, Millstone Unit 3 reactor was manually tripped due to the loss of two [CW] pumps in the same condenser section resulting from deteriorating conditions related to a storm consisting of high winds and waves. At approximately 1311, the 'A' CW pump automatically tripped due to high traveling screen differential pressure. At 1313, the 'B' CW pump also automatically tripped due to high traveling screen differential pressure. The operators then tripped the reactor in accordance with operating procedures.The event review team (ERT) concluded that environmental factors such as tide, wave height, wind speed and direction, and debris contributed to the event. Plant systems performed as designed and plant personnel operated the plant in a safe manner following the procedural guidance provided.
4232005004 | Millstone 3 | 10/18/2005 | 12/16/2005 | ML05363004 | <strong>Pressurizer Spray Nozzle Weld Indications</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2005 a prompt notification to the NRC was made per 10CFR50.72(b)(3)(ii)(A) to report discovery of flaws in the pressurizer spray nozzle [AB] to safe-end bimetallic weld region. With the plant in Mode 6 (Refueling), engineering personnel performing preplanned radiography (RT) examinations in accordance with the Alloy 600 weld inspection program (as committed to in response to NRC Bulletin 2004-01), discovered two linear indications. In an effort to better characterize the indications, additional ultrasonic examinations were performed which identified three indications. The indications were conservatively identified as degradation of the reactor coolant system pressure boundary in that corrective action to restore the barrier's capability was necessary. A request was made and the NRC granted approval for Millstone to utilize an alternate repair method from that specified in the ASME Code. The weld was repaired utilizing a weld overlay process. This event/condition is being reported pursuant to 50.73(a)(2)(ii)(A), as a condition that resulted in the nuclear power plant, including its principal safety barriers, being degraded.
4232005005 | Millstone 3 | 12/01/2005 | 05/18/2006 | ML06153026 | <strong>Automatic Reactor Trip of Millstone Unit 3 due to Low-Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>At approximately 14:45 on December 1, 2005, with Millstone Unit 3 (MP3) in Mode 1 at an indicated power level of 38%, an automatic reactor trip occurred on C Steam Generator Low-Low level (S/G Low-Low level). At the time of the reactor trip, downpower to 30% was in progress to facilitate a containment entry to locate and repair a Reactor Coolant System (RCS) leak. As turbine load and reactor power were reduced, main turbine vibrations increased above allowable limits and the main turbine was manually tripped in accordance with procedure. After the turbine was manually tripped, the reactor automatically tripped on 'C' S/G Low-Low level. All safety systems performed as designed, including auto actuation of the auxiliary feedwater system. The balance of the plant shutdown was uncomplicated. The direct cause of the reactor trip was a Low-Low level in the 'C' S/G that resulted from the shrink in S/G water level created by the manual turbine trip. The plant is designed to maintain the reactor critical following a turbine trip below 45% power. At the time of the trip, the Reactor Protection System S/G Low-Low Level Trip setpoints were being maintained at 27% vice the nominal value of 18% to address Westinghouse identified S/G level inaccuracies associated with the S/G mid-deck plate differential pressure. Operation at the increased set point reduced the margin available to accommodate S/G level transients that occur following a turbine trip at power. The automatic reactor trip and auxiliary feedwater system actuation are reportable in accordance with 10CFR50.73(a)(2)(iv).
4242005001 | Vogtle 1 | 01/11/2005 | 03/02/2005 | ML05066027 | <strong>Automatic Reactor Trip due to Broken Wire Connector</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2005, an automatic turbine trip/reactor trip occurred due to a main generator protective relay lockout. A normal reactor trip sequence ensued and the control room staff responded by transitioning the unit to operation in Mode 3 (Hot Standby). A continuity check of field connections for the protective relay showed very high resistance through an auxiliary potential transformer which is connected to the secondary of the generator neutral grounding transformer. Inspection of the connection revealed that a wire on a terminal strip in the secondary circuit wiring of the auxiliary potential transformer had failed and disconnected when touched. The high resistance measurement at the potential transformer was apparently due to this failed connection. An analysis of the failed connection determined there was prior damage to the wire at the point where the lug was attached. The damage most likely occurred when the lug was first installed prior to initial plant startup. Over time, the remaining conductors fatigued due to vibration until the high resistance connection developed. As a result of the high resistance the relay sensed an invalid fault. The connection was repaired and the unit was returned to power operation.
4242005003 | Vogtle 1 | 04/29/2005 | 06/27/2005 | ML05181023 | <strong>Feedwater Valve Failure Leads To Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2005, operators responded to closure of loop 1 feed water regulating valve, 1FV-510, by taking manual control in accordance with the abnormal operating procedure. Trouble shooting determined the cause to be a failed controller card. Replacement of the failed card was initiated in accordance with a card replacement procedure.During maintenance, the loop 1 feedwater regulating valve unexpectedly shut. As steam generator water level approached the low-low setpoint, operators took action to trip the reactor. However, an automatic reactor trip on low-low steam generator water level occurred V4 second before the manual trip at 2155 EDT. Operators responded properly to stabilize the plant at normal operating temperature and pressure in Mode 3 (Hot Standby). The causes of this event were: a) technical inaccuracies and incomplete information in the procedure used for controller card replacement, and b) inadequate technician training regarding replacement procedure limitations for recent design changes. The failed card was replaced and the unit returned to power. Further corrective actions have been taken to clarify the procedure for intended purpose and limitations and to clarify technical training for the intended purpose of the procedure. Corrective actions are in progress to revise procedures to include replacement directions for the card failure that was experienced and train appropriate personnel on the replacement procedure for the failure that was experienced.
4242005004 | Vogtle 1 | 10/17/2005 | 12/16/2005 | ML05353005 | <strong>Manual Reactor Trip following Main Feed Regulating Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2005, at 1816 EDT, Unit 1 was manually tripped from 100% power due to a rapidly decreasing Steam Generator (SG) #2 water level. The Loop 2 Main Feedwater Regulating Valve (MFRV), 1FV0520, closed unexpectedly and could not be re-opened from the control room. A review found that 1FV0520 closed due to an electronic circuit board failure resulting from moisture intrusion into the air operated valve's electro-pneumatic transducer. The transducer was mounted in an inverted manner that did not prevent water ingress and allow drainage. Washdown activities in this area allowed moisture into the transducer, causing the subsequent failure. The failed transducer was replaced and mounted in the upright configuration. Furthermore, the appropriate procedure has been revised to ensure that electro-pneumatic transducers are mounted in the preferred position, and all washdowns within the power block have been halted until proper administrative controls have been established.
4252005001 | Vogtle 2 | 06/02/2005 | 08/01/2005 | ML05214012 | <strong>High Flux At Shutdown Alarm Inoperable - Operation In A Condition Prohibited By The Tech. Specs.</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2005, Unit 2 was in Mode 5 (Cold Shutdown) and personnel were performing surveillance testing of neutron flux instrumentation. The high flux at shutdown alarm (HFASA) annunciator did not actuate when tested. At 0115 EDT, it was found that both trains of the solid state protection system (SSPS) were in "input error inhibit," which rendered both channels of HFASA inoperable. Further review determined that this condition had existed since May 25, 2005. Because the alarm was inoperable longer than the completion time for the required actions of Technical Specification (TS) LCO 3.3.8Condition B, the unit had operated in a condition prohibited by the TS. Following the discovery of this event at 0115 EDT, on June 2, 2005, TS action requirements were met by 0417 EDT, and HFASA was returned to service at 1100 EDT. The cause of this event is the improper use of a procedure on May 25, 2005, when SSPS was removed from service while the unit was shutdown. The procedure, 13503-2, "Reactor Control Solid State Protection System," did not have a section written specifically for placing both trains of SSPS in TEST. A portion of the procedure section for de-energizing both trains of SSPS was used, thereby rendering both trains of HFASA inoperable. Procedures 13503-1/2 have been revised, other procedures utilizing SSPS will be reviewed and revised as appropriate, and this event will be addressed in operator training.
4252005002 | Vogtle 2 | 07/21/2005 | 09/19/2005 | ML05262046 | <strong>Instrument Setpoint Drift Leads to Operation of the Unit in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Reactor Coolant System Loop 2 Overtemperature Delta-T (OTDT) instrument channel 2T-421 was restored to service on February 26, 2005, following maintenance to correct overtemperature setpoint (OTSP) drift by replacing a summing amplifier. After the channel was returned to service, the OTSP signal continued to drift until March 3, 2005, when 2T-421 was again removed from service and a different summing amplifier replaced, correcting the drift anomaly. On July 21, 2005, an engineering evaluation of the instrument channel drift evolution concluded that this channel's OTSP signal had drifted outside of the Technical Specifications (TS) allowable values for the input signals for a period of time longer than allowed by the action requirements. Therefore, the unit had operated in a condition prohibited by the TS. The causes of this event include the failure to perform adequate troubleshooting and post-maintenance testing on February 26, 2005. I&C technicians and their supervision were advised of the proper course of action expected for this type of event, and procedures were revised to clarify the expectations for functional testing following corrective maintenance.
4252005003 | Vogtle 2 | 12/10/2005 | 01/30/2006 | ML06030060 | <strong>Reactor Coolant System Leakage Leads to Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On December 8, 2005, control room operators received indication of an increase in radioactivity in the containment building atmosphere. On December 9, 2005, a robotic camera sent inside the containment building bioshield wall observed water running down the inside of the wall. Unit 2 was placed in Mode 3 (Hot Standby). On December 9, 2005, at 1544 EST, an inspection team found leakage at a Reactor Coolant System (RCS) welded 3/4" piping connection located inside the bioshield wall. Because the connection was non-isolable, this constituted RCS pressure boundary leakage, and Unit 2 was placed in Mode 5 (Cold Shutdown) on December 10, 2005, at 1019 EST, per the requirements of the Technical Specifications. The leak occurred in a 3/4" socket weld between a flow restrictor and a half-coupling. A linear weld defect, approximately 1/2" long, was found near the toe of the weld nearest the half-coupling. The probable cause of the defect is a lack of fusion in the start/stop point of the weld. This is a fabrication flaw that occurred when this weld was installed in 2002 as part of a design change. The weld was repaired and the unit returned to power operations. Similar Unit 2 welds made during the design change were inspected and found to be satisfactory. Other non-isolable socket welds made during the design change on Unit 1 will be inspected no later than the next refueling outage on Unit 1.
4402005001 | Perry | 01/06/2005 | 02/21/2005 | ML05061002 | <strong>Manual Reactor SCRAM Following Unexpected Reactor Recirculation Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2005, at 0106 hours, while operating at approximately 100 percent rated thermal power, the Perry Nuclear Power Plant (PNPP) reactor recirculation system (RRC) pumps A and B unexpectedly downshifted from fast to slow speed. Reactor power decreased to approximately 44 percent power. This power and flow reduction placed the plant in the immediate exit region of the power-flow map. While operators were inserting control rods in accordance with the applicable off normal operating instructions, RRC pump A unexpectedly tripped from slow speed to off at 0110 hours. At 0112 hours, a manual reactor scram was initiated by the control room crew. All control rods fully inserted. At 0119 hours, following reactor level reduction below level 8 (219 inches above top of active fuel), the motor feedwater pump could not be manually started. At 0122 hours, a reactor core isolation cooling (RCIC) pump was started for injection to the reactor vessel and continued to provide reactor level control. It was determined that the RRC pumps downshift originated from a degraded optical isolator in the RRC logic circuitry. The installed resistor/capacitor surge suppression network on the optical isolator was insufficient to protect the output transistors from the inductive kick experienced during normal operation, allowing intermittent malfunctioning output. To minimize this kick, diodes were installed across applicable optical isolators, downstream trip logic relays to limit the inductive loads on the optical isolator card transistors. This event is being reported under requirements of 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the specified systems.
4402005002 | Perry | 02/17/2005 | 04/17/2005 | ML05116019 | <strong>All Emergency Diesel Generators Declared Inoperable due to Degraded Testable Rupture Discs</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2005, at 1730 hours, with the plant operating at approximately 93% power, division 1, 2, and 3 emergency diesel generators (EDGs) were declared inoperable due to degraded testable rupture discs (TRDs) on their respective exhaust systems. The cause of the inoperability was determined to be inadequate workmanship in the preparation and testing of the design. Design personnel did not have adequate skills and experience to perform the design or to prepare and direct the testing. The management oversight of the design was unable to detect the inadequate results. A design change will be completed that removes each TRD and eliminates the possibility that a TRD can fail to open when required. Training will be conducted to provide guidance on the requirements for design testing and include this event as a case study or example. This training shall include a discussion of the need to consider if the task is within the assigned engineers' level of training and expertise. Design Engineering management will develop guidelines to ensure that tasks are assigned to personnel with the appropriate level of skills and expertise required to perform engineering tasks. Supervisory personnel will be instructed on use of these guidelines in assigning tasks. This event was reported per 10CFR50.72(b)(3)(ii)(B), unanalyzed condition and 10CFR50.72(b)(3)(v), loss of safety function on ENF 41417. This event was determined to be of very low safety significance.
4402005003 | Perry | 09/20/2005 | 11/18/2005 | ML05333012 | <strong>Lack of Suction Row Path Causes High Pressure Core Spray to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2005, with the Perry Nuclear Power Plant operating in Mode 1 at 100 per cent power, a review of the High Pressure Core Spray (HPCS) Pump and Valve Operability test instruction revealed that steps in the instruction closed both suction valves and caused a loss of HPCS pump suction flow path without declaring HPCS inoperable. While the valve stroking sequence is appropriate for the system design, the inappropriate action was not declaring the system inoperable. It was also determined that the manual shifting of HPCS suction flow path from the Suppression Pool (SP) to the Condensate Storage Tank (CST) per the System Operating Instruction (S01) would result in the same condition. Both conditions would only occur for a short (less than 5 minutes) duration during valve timing for the quarterly testing or during manual shifting of the HPCS suction source. The cause of this event was determined to be a long-standing procedure and knowledge deficiency. Since the inoperability was only for a very short duration during actual valve stroking, the increase in risk is very small. The SOI and the test instruction have been revised to include entry into the required TS LCO. The training program for licensed operators is being revised. This issue is considered to be a condition that could have prevented the fulfillment of a safety function of a system needed to mitigate the consequences of an accident in accordance with 10CFR50.73(a)(2)(v)(D).
4432005001 | Seabrook | 01/15/2005 | 03/15/2005 | ML05081048 | <strong>Noncompliance with the Requirements of Technical Specification 3.6.3</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2005 at 0750, with the plant in Mode 1 at 100% power, it was determined that Containment Isolation Valve CC-V-1095 had been inoperable for a period of time longer than allowed by the Technical Specifications (TS) due to the failure to perform a post maintenance retest. The valve's power supply was removed from service for maintenance on January 13, 2005. TS 3.6.3, Containment Isolation Valves, was not entered and the required post maintenance retest was not performed prior to returning the valve to operable status, resulting in a condition prohibited by TS. The cause of the event was an inadequate process for Operations department review of work orders in preparation for and execution in the work week. On January 15, 2005, after discovery of the missed retest, TS 3.6.3 was entered and CC-V-1095 was satisfactorily retested and restored to operable status. Corrective action is to assign an Operations Department Work Week Coordinator to the Work Management Process and to define personnel responsibilities in the Work Management Manual. There were no safety consequences as a result of this event.
4432005002 | Seabrook | 02/22/2005 | 04/19/2005 | ML05116028 | <strong>Momentary Loss of Power to Emergency Bus While Transferring Power Supplies</strong><br /><i>Abstract:&nbsp;</i>While operating at 100% power on February 22, 2005, a momentary deenergization of the 4,160 volt, train A emergency bus resulted in an automatic start and loading of the train A emergency diesel generator and actuation of the emergency feedwater system. The loss of power occurred while transferring the emergency bus power supply from the unit auxiliary transformer (UAT) to the reserve auxiliary transformer (RAT) to support planned maintenance on the UAT circuit breaker. During the transfer, the circuit breaker from the RAT attempted but failed to close and initiated opening of the UAT supply to the emergency bus as designed. This condition initiated a loss of power signal for the emergency bus, and the emergency diesel generator (EDG) automatically started and re-energized the bus. The RAT breaker failed to close because the mechanical interlock associated with the breaker racking mechanism was not properly engaged due to inadequate cleaning and lubrication. Approximately nine hours later, power was restored to the emergency bus via the UAT. The actuated safety systems performed as expected and no adverse consequences resulted from this event.
4432005003 | Seabrook | 03/22/2005 | 05/16/2005 | ML05144042 | <strong>Plant Shutdown due to Inoperable Reactor Trip Breaker</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2005 at 1022 during operation in Mode 1 at 100% power, Seabrook Station entered the action statement of Technical Specification (TS) 3.3.1, Reactor Trip System Instrumentation, for an inoperable train A reactor trip breaker. While performing routine surveillance testing on the solid state protection system, the reactor trip breaker unexpectedly tripped open and subsequently failed to close upon initiation of a close signal. As a result, the station entered action 9 of TS Table 3.3-1, which requires the unit to be in Hot Standby within the next 6 hours. A plant shutdown commenced at 1102. The NRC was notified of the initiation of this TS-required shutdown in a four-hour report (event #41513) in accordance with 10CFR50.72(b)(2)(i). The plant entered Mode 3 at 1547 on March 22, 2005. The apparent cause of this event was a malfunctioning switch associated with the Auto Shunt Trip Test push button. The reactor trip breaker was restored to operable status at 0101 on March 23, 2005. No adverse consequences resulted from this event.
4432005004 | Seabrook | 03/29/2005 | 05/19/2005 | ML05144042 | <strong>Noncompliance with the Technical Specification for Offsite AC Sources</strong><br /><i>Abstract:&nbsp;</i>During operation in Mode 1 at 95% power on March 29, 2005, plant personnel identified a previous failure to comply with Technical Specification (TS) 3.8.1.1, AC Sources. On February 14, the circuit breaker for the reserve auxiliary transformer (RAT) supply to the train A 4,160 volt emergency bus was removed from service with the bus energized from the unit auxiliary transformer, rendering inoperable one of the two offsite AC sources required by TS 3.8.1.1. The station had historically implemented the TS such that only one offsite AC source was required for each train of emergency buses, provided the sources to the two trains of emergency buses were physically independent. Consequently, the periodic surveillance requirement specified in TS 3.8.1.1, action a, was not performed, resulting in a condition prohibited by the TS. This condition continued for approximately 9.5 days and exceeded the 72-hour allowed outage time permitted by TS 3.8.1.1. A subsequent review of the station's electrical configuration in August 2003 found that an AC source had been removed from service for 85 hours, exceeding the 72-hour allowed outage time. The cause of these noncompliances with the TS was a misapplication of the electrical configuration needed to meet the TS for two independent offsite AC sources. No adverse consequences resulted from this event.
4432005005 | Seabrook | 04/13/2005 | 06/06/2005 | ML05160044 | <strong>Reactor Protection System Actuation on Steam Generator Low Level in Mode 6</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2005 at 0350 with the plant in Mode 6 and core reload in progress, an actuation of the reactor protection system (RPS) resulted from a low water level in steam generator (SG)-B. While SG-B was in wet lay-up recirculation, an incorrect valve alignment resulted in an inadvertent transfer of water from SG-B to SG-D. This transfer of water lowered the level in SG-B to the low water level reactor trip setpoint, resulting in an actuation of the RPS. This valid actuation of the RPS did not actuate any other components because the reactor trip breakers were already open and the emergency feedwater system was removed from service. The cause of this event was an inadequate procedure. The procedure that controlled filling and recirculation of the SGs during shutdown did not include sufficient instructions to prevent transferring water between SGs. The corrective actions for this condition included revising the procedures to prevent cross-connecting the SG flow paths. No adverse consequences resulted from this event.
4432005006 | Seabrook | 05/01/2005 | 06/29/2005 | ML05186007 | <strong>Manual Reactor Trip due to Main Turbine High Vibration</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2005 at 1109, Seabrook Station initiated a manual reactor trip from 17% power. During initial start-up of the main turbine following refueling outage 10, the turbine automatically tripped at approximately 1045 rpm when turbine vibration exceeded the trip setpoint of 12 mils. Following the turbine trip, vibration levels continued to increase and the operators manually tripped the reactor in preparation for breaking condenser vacuum to slow the turbine. Condenser vacuum was broken until the high vibration condition cleared and was then subsequently restored to provide a secondary heat sink. The emergency feedwater system actuated on low steam generator levels following the reactor trip. The cause of the turbine high vibration condition was a turbine rub (contact between the rotor and stationary components in the turbine). The rub creates a hot spot on the rotor that causes the shaft to bow, which will change the center of mass of the rotor. Once a rub starts it will typically spread to multiple locations as the rotor bows and vibration levels increase. Corrective action will be taken to add a precaution to operating procedures to minimize thermal distortion and rapid changes in steam flow through the Turbine to reduce the possibility of initiating a rub.
4432005007 | Seabrook | 07/07/2005 | 08/31/2005 | ML05250041 | <strong>Noncompliance with the Technical Specifications due to Circuit Card Failure</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2005 while at 100% power, Seabrook Station discovered that a condition prohibited by the Technical Specifications (TS) had existed. On June 20, 2005 the train-B containment building spray (CBS) pump failed to start during a post-maintenance retest using a slave relay test to start the pump. Subsequent troubleshooting determined that the cause of the pump's failure to start was a failed relay driver card in the train-B emergency power sequencer (EPS). The card failure prevented the CBS pump from automatically starting on an engineered safety features actuation signal and also rendered the train-B emergency diesel generator (EDG) inoperable. Further review determined that this condition existed for approximately 57 days, beginning on April 24, and exceeded the 72-hour allowed outage times of TS 3.6.2.1 and TS 3.8.1.1 for the CBS pump and EDG, respectively. While EDG-B and CBS pump-B were inoperable, the redundant EDG and CBS were rendered inoperable during this period to perform surveillance testing. The unplanned, concurrent inoperability of both EDGs and CBS pumps resulted in a condition that could have prevented the fulfillment of the safety functions of these systems. The cause of the card failure was a random, premature failure of the card. The corrective action consisted of replacing the failed circuit card. No adverse consequences resulted from this event.
4432005008 | Seabrook | 11/30/2005 | 12/28/2005 | ML06003047 | <strong>Technical Specification Violation due to Inoperable Instrument Bus Inverter</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2005 at 0924, Seabrook Station entered a condition prohibited by theTechnical Specifications (TS) when vital instrument bus inverter 1F was inoperable for greater than 30 hours. The TS provide a 24-hour allowed outage time for an inoperable vital inverter, and if the inverter is not restored to operable status within 24 hours, the TS require the plant to shutdown to Mode 3 within the following 6 hours. The inverter was inoperable for approximately 36 hours. At 0220 on November 30, 2005, prior to the expiration of the 24-hour allowed outage time, the NRC granted a Notice of Enforcement Discretion that extended the allowed outage time by 18 hours. As a result, Seabrook Station operation continued at 100% power for the duration that the inverter was inoperable. The cause of the inoperability of the inverter was a circuit card failure. The faulty card was replaced and the inverter was restored to operable status at 1522 on November 30, 2005. No adverse consequences resulted from this event.
4462005001 | Comanche Peak 2 | 01/18/2005 | 03/14/2005 | ML05081048 | <strong>Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2005, Comanche Peak Steam Electric Station Unit 2 was in Mode 1, Power Operation, operating at approximately 100 percent power. On January 18, Engineering personnel determined that one of the two Unit 2 containment personnel airlock doors had been inoperable for a period of time longer than allowed by the Technical Specifications. TXU Generation Company LP (TXU Power) believes that this event was caused by incorrect installation of the door gaskets for the Unit 2 containment personnel airlock doors due to an inadequate procedure. Corrective actions include revising procedures to provide instructions for the correct orientation of the door gasket and evaluating the post work test requirements for the door gaskets. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462005002 | Comanche Peak 2 | 02/23/2005 | 04/25/2005 | ML05123035 | <strong>Auxiliary Feedwater System Actuation Due to Momentary Loss of the 138kV Switchyard</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2005, Comanche Peak Steam Electric Station (CPSES) Unit 2 was in Mode 1 operating at 100 percent power. At 0153 hours, a momentary interruption of power to the 138kV switchyard occurred causing the Unit 2 6.9kV safeguards buses to transfer to their alternate power source. This resulted in actuation of the Unit 2 black out sequencers (BOS) with an actuation, as expected, of the Unit 2 Auxiliary Feedwater System (AFW). TXU Generation Company LP (TXU Power) believes that this event was caused by a misconfigured jumper in the power line communication equipment located at another TXU Power generating plant. Corrective actions include correcting the misconfigured jumper and verifying other similar jumper settings. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462005003 | Comanche Peak 2 | 04/27/2005 | 06/27/2005 | ML05188008 | <strong>Two Pressurizer Safety Valves Found with Unsatisfactory Lift Setpoints</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2005, TXU Generation Company LP (TXU Power) discovered that two of the three Pressurizer Safety Valves (PSVs), which had been removed from the system and shipped off-site for surveillance testing in support of the eighth refueling outage on Comanche Peak Unit 2, failed their as-found lift tests with lift pressures below the Technical Specification (TS) 3.4.10 setpoint of >/= 2460 psig and </= 2510 psig (2485 psig +/-1 %). These failures resulted in the determination that this condition was reportable pursuant to10CFR50.73(a)(2)(i)(B); "Any operation or condition which was prohibited by the plant's Technical Specifications." On April 18, 2005 the valves were returned to operable status using normal rework for these components. On May 15, 2005 during the root cause analysis investigation for the above event, it was discovered that a similar condition existed during the previous (seventh) Unit 2 refueling outage for these same PSVs in October of 2003. Since the underlying situation and material conditions of this October 2003 event have been evaluated as identical in both root cause and consequences to the above April 2005 event, this Licensee Event Report (LER) is submitted by TXU Power to encompass both reportable events. There are no material condition issues associated with the PSVs that contributed to the test failures. The PSVs are performing within their design capabilities. The root cause of the test failures was determined to be the close tolerance required by the TS acceptance criteria and the inability of the valves to repetitively perform within that tolerance during as-found surveillance testing. The long term corrective action is for TXU Power to investigate revising the safety analysis to support a relaxation of the +/-1% TS Limiting Condition for Operation (LCO) requirement for the PSV lift setpoint tolerance.
4542005001 | Byron 1, Byron 2 | 01/25/2005 | 03/28/2005 | ML05087054 | <strong>Failed Technical Specification Ventilation Surveillance Requirements During Surveillance Requirement 3.0.3 Delay Period</strong><br /><i>Abstract:&nbsp;</i>On January 13, 2005, 15 Technical Specifications (TS) Ventilation surveillance procedures were discovered not performed due to willful falsification of documents by a non-licensed employee. An ensuing investigation found 12 additional falsified surveillance procedures. These surveillance procedures were used to perform and credit TS surveillance requirements (SRs). As a result, these TS SRs exceeded their TS frequencies. TS SR 3.0.3 was immediately entered and a risk evaluation performed that concluded the risk was acceptable to perform these surveillance procedures within a five week delay period. Of the 27 surveillance procedures re-performed, six SRs failed. Specifically these SRs were the charcoal filter penetration test for the 0B Fuel Handling Building (FHB) ventilation train and the 0C Auxiliary Building non-accessible area ventilation train, both the 0A and 0B Main Control Room make-up flow rate tests, the 0B Main Control Room Ventilation System (VC) make-up charcoal bank bypass leakage test and the 0B VC recirculation charcoal bank bypass leakage test. The responsible individual's employment was terminated and extensive corrective actions taken to identify and correct this inappropriate activity in a more timely manner. In each of surveillance failures, (except for the FHB SR where the failure was not applicable in the current mode of operation), the ventilation train was declared inoperable and returned to service within the TS allowed outage time. The risk significance of the missed SRs was evaluated to be low. Failure of a surveillance within the SR 3.0.3 delay period is reportable as a condition prohibited by TS in accordance with 10 CFR 50.73 (a)(2)(i)(b). Additionally, concurrent inoperability of both trains of VC is also reportable in accordance with 10 CFR 50.73 (a)(2)(vii).
4542005002 | Byron 1, Byron 2 | 09/26/2004 | 04/15/2005 | ML05109053 | <strong>One of Two Trains of Hydrogen Recombiners Inoperable Longer Than Allowed by Technical Specifications Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2005, the System Engineer for the hydrogen recombiner (OG) system discovered a flow transmitter test tap pipe cap was not installed on the 0A train. This condition rendered the 0A OG train inoperable and Technical Specification (TS) 3.6.8, Hydrogen Recombiners action condition A was entered. This condition allows one train of OG to be inoperable for 30 days. A cap was installed and TS 3.6.8 condition A exited. The last maintenance activity on the 0A OG train was the August 27, 2004 execution of the 18 month surveillance calibration procedure, Byron Instrument Maintenance Surveillance Requirement (BISR) Z.6.A.1-202, Surveillance Calibration Of Hydrogen Recombiner Inlet Flow Loop. During this calibration activity, the flow transmitter test tap pipe cap was removed as setup for the calibration activity and not replaced at the conclusion of the calibration. As a result, the 0A OG train was inoperable since August 27, 2004. Consequently, 30 days later, on September 26, 2004 both units were inadvertently in a condition prohibited by TS 3.6.8. This condition existed from September 26, 2004 until February 14, 2005. The 0B train was always operable in this time period. The cause of the event was inadequate procedure and poor enforcement of managements expectation that procedural inadequacies be fixed. Corrective actions will fix the procedure and institute activities that will re-enforce expectations. There were minimal safety consequences. Any operation or condition prohibited by Technical Specifications is reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(i)(b).
4542005003 | Byron 1, Byron 2 | 09/20/2002 | 09/15/2006 | ML06261008 | <strong>Technical Specification (TS) 3.9.4 Violation Due to Imprecise Original TS and TS Bases Wording</strong><br /><i>Abstract:&nbsp;</i>An NRC inspector raised an issue with Technical Specification (TS) 3.9.4, "Containment Penetrations," as to whether Byron Station was violating item "c" of the Limiting Condition for Operations by causing direct access from containment atmosphere to the outside atmosphere during the performance of local leak rate test (LLRT) on containment isolation valves while core alterations or movement of irradiated fuel within containment were in progress. The NRC's position is contrary to how Byron Station has historically applied this TS. Byron Station has always viewed this wording to mean those penetrations that have a direct air path from within containment to the outside atmosphere (i.e., not through an intermediate area or building such as the auxiliary building). Byron Station decided to not further contest the issue and adopted the NRC's position on the intent of this TS. The most probable cause is the authors and reviewers of the original TS and TS Bases wording inadvertently used imprecise language. The outage schedule was reconfigured to not allow the performance of LLRTs that provide direct access from containment to the auxiliary building during core alterations or movement of irradiated fuel within containment. An engineering evaluation concluded that there are no adverse safety consequences. This is an event or condition prohibited by the Technical Specifications and consequently, reportable to the NRC in accordance with 10 CFR 50.73 (a) (2) (i) (b).
4542005004 | Byron 1, Byron 2 | 05/24/2005 | 07/25/2005 | ML05207006 | <strong>Technical Specification Required Action Not Satisfied Due to Ambiguous Implementing Procedure.</strong><br /><i>Abstract:&nbsp;</i>On May 23, 2005, at approximately 2105 hours, the Unit 1 Control Room Supervisor (CRS) (licensed) entered Action Condition "A" of Technical Specifications (TS) 3 .8 .4, "DC Sources - Operating" due to planned work on Division 11 Battery Charger. One of the required TS Actions was to verify battery float current to be within limits once every 12 hours. The Unit 1 CRS incorrectly convinced himself that the procedure to conduct one of the TS Action Requirements was one other than those procedures listed in the operating procedure (i.e., 1 BOL 8.4) as possible options to implement the TS Action Requirements. The Unit CRS made an incorrect procedure revision to 1BOL 8.4 to what he believed was the correct procedure but did not obtain the required procedure revision reviews. The battery float current was verified using this procedure at 0452 hours on May 24, 2005 . The next shift Unit 1 CRS questioned this change and evaluated it further. As a result it was determined that the procedure revision was in error and the procedure to be used was in fact correctly reflected in 1 BOL 8.4. The Shift Manager concluded that with the Required Action and Associated Completion Time not met, then Action Requirement E, to enter Mode 3 within 6 hours, was not correctly satisfied within the allowed TS Completion Time and consequently was a violation of TS. The float current was immediately verified using the correct procedure. The root cause of this event was determined to be 1 BOL 8.4 being ambiguous and less than adequate personal performance by the Unit CRSs . This event has minimal safety significance. Corrective actions include revising 1 BOL 8 .4 and training of Operating personnel. This event is reportable to the NRC in accordance with 10 CFR 50.73(a)(2)(i)(b).
4542005005 | Byron 1, Byron 2 | 06/01/2005 | 10/14/2005 | ML05287048 | <strong>Both Trains of the Ultimate Heat Sink Water Makeup Trains Exceeded Technical Specification Required Action Completion Time Due to Contaminated Fuel Oil Resulting From Inadequate Tank Cleaning Procedure</strong><br /><i>Abstract:&nbsp;</i>Both trains of the safety related Ultimate Heat Sink (UHS) Water Makeup system were declared inoperable on August 16, 2005 due to fuel oil samples indicating water and sediment contamination. The fuel oil supplies the diesel engine of the UHS Makeup pumps. Appropriate Technical Specification (TS) action conditions we reentered. An investigation concluded that the contamination was the result of residual water and cleaning agent after a fuel oil tank cleaning process for each tank in June 2005. Consequently, the two trains we reconsidered inoperable for a time period greater than allowed by TS. The cause was determined to be inadequate work instructions and post maintenance testing (PMT) requirements provided to the tank cleaning vendor. The instructions provided did not contain sufficient detail to ensure the tanks were clean prior to refilling with fuel oil. Corrective actions include developing a permanent tank cleaning procedure with sufficient details and controls to ensure cleanliness and a review of other vendor activities to ensure proper work instructions are used. An engineering evaluation concluded this event had minimal safety significance due to other operable makeup sources. This is reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by TS. In addition, this is a condition where a single cause caused two independent trains in a single system to become inoperable and therefore reportable in accordance with 10 CFR 50.73(a)(2)(vii).
4552005001 | Byron 2, Byron 1 | 10/19/2005 | 12/19/2005 | ML06093049 | <strong>Unit 2 Automatic Reactor Trip due to Low Steam Generator Level Resulting from a Software Fault on the Turbine Control Power Runback Feature</strong><br /><i>Abstract:&nbsp;</i>On October 19 2005, attempts to execute an automatic Turbine Runback in response to a trip of a Condensate/Condensate Booster (CD/CB) Pump were ineffective and ultimately resulted in an automatic Reactor Trip on low Steam Generator Level. The root cause was determined to be the failure of the Digital Electro-Hydraulic system to automatically runback the turbine as designed. This was due to an application software fault. The software fault effectively rendered all automated Turbine Runbacks inoperable. Corrective actions include the development of procedural controls to monitor and identify software issues of this nature. There were no safety consequences impacting plant or public safety as a result of this event. The automatic turbine runback feature is a non safety related design feature and is not credited in any Updated Final Safety Analysis Report chapter 15 accident and transient analyses. The actuation of the reactor protection system was reported to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B) and 10 CFR 50.73 (a)(2)(iv)(A).
4562005001 | Braidwood 1, Braidwood 2 | 06/02/2005 | 07/05/2005 | ML05194030 | <strong>Potential Technical Specification (TS) 3 .9 .4 Violation Due to Imprecise Original TS and TS Bases Wording</strong><br /><i>Abstract:&nbsp;</i>At Byron Station during their March 2005 refueling outage on Unit 1, an issue was raised with regards to Technical Specification (TS) 3 .9.4, "Containment Penetrations," as to whether Byron was violating item "c" of the Limiting Condition for Operations by causing direct access from containment atmosphere to the outside atmosphere during the performance of local leak rate tests on containment isolation valves while core alterations or movement of irradiated fuel within containment were in progress . This was contrary to how Braidwood and Byron Stations had historically applied this TS. Both Stations had always viewed this wording to mean those penetrations that have a direct air path from within containment to the outside atmosphere (i .e., not through an intermediate area or building such as the auxiliary building). The most probable cause is the authors and reviewers of the original TS and TS Bases wording inadvertently used imprecise language. An engineering evaluation concluded that there are no adverse safety consequences. Because Braidwood and Byron are of similar design and outage execution, it is possible that Braidwood Station was in a similar plant configuration in three refueling outages in the past three years. Braidwood Station is reporting this as a voluntary LER.
4562005002 | Braidwood 1 | 09/06/2005 | 11/07/2005 | ML05320018 | <strong>Braidwood Unit 1 - Feedwater Isolation Valve 1 FW039A Fails to Stroke in the Required Time Due to Failure of Valve Air Regulator to Maintain Set Pressure</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2005, feedwater isolation valve 1 FW039A failed its quarterly stroke time test with a measured stroke time of 6.58 seconds and a Technical Specification limit of 6.0 seconds. 1FVV039A was declared inoperable and Technical Specification Limiting Condition for Operation (LCO) 3.6.3 Condition C was entered. In accordance with LCO3.6.3 Condition C, the upstream isolation valve, 1FW041A was closed and administrative actions were taken to ensure 1 FW039A and 1 FW041A remained in the closed position. The cause of the failed stroke time for 1FVV039A was foreign material entry into the regulator main seat area. This caused the regulator supply pressure to be greater than its setpoint, and resulted in additional time for the actuator and solenoid valves to exhaust the supplied air to allow the valve to close. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
4562005003 | Braidwood 1 | 11/18/2004 | 01/03/2006 | ML06055007 | <strong>Licensed Maximum Power Level Exceeded due to Feedwater Heater Transient</strong><br /><i>Abstract:&nbsp;</i>On November 18, 2004, at 1119, Braidwood Unit 1 experienced an isolation of extraction steam to the 15A and 15B low pressure feedwater heaters during maintenance on a level controller for the 15A emergency level control valve. At 1121, reactor power increased above the overpower delta-temperature set point on 2-of-4 channels, which initiated an auto rod-stop and a turbine runback. An initial evaluation was performed to determine whether reactor power exceeded reportable levels during the event. The conclusion was that reactor power did not exceed 102.0%. Based on this conclusion, the transient was not considered to be a reportable event. On December 2, 2005, at 1700, following further evaluation, it was determined that peak power likely exceeded 102% of rated thermal power. The value could have been as high as 103.3% for approximately one minute. On December 3, 2005, at 1125, a 24-hour ENS notification was made in accordance with Braidwood Station Unit 1 License Condition 2.G, due to the violation of License Condition 2.C(1) "Maximum Power Level." The root cause for the initiating event, completed in January 2005, was determined to be a lack of understanding for a potential adverse internal component interaction during the calibration of a level controller on the same level column as the Magnetrol level switches. The corrective actions to prevent recurrence included creation of a work package standard to ensure uniformity for alignment, adjustments and calibration of the tandem float Magnetrol level control assemblies. There were no safety consequences impacting plant or public safety as a result of this event.
4572005001 | Braidwood 2 | 01/11/2005 | 03/11/2005 | ML05077045 | <strong>Incorrect Installation of Flow Element Resulted in Service Water Flow Below the Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2005, during the removal of a reactor containment fan cooler (RCFC) annubar flow element, it was discovered that the flow element was installed backwards. Because of this, the actual essential service water flow may have been less than the indicated flow. All other RCFCs at Braidwood Unit 1 and Unit 2 were inspected for similar problems and no discrepancies were found. Based on past surveillance data, there were four occasions where flow readings were determined to be potentially lower than the Technical Specification surveillance limit. This low flow condition was assumed to be present for greater than the Limiting Condition for Operation (LCO) Completion Time for one or more inoperable RCFC trains per LCO 3.6.6, which is seven days. Therefore, the 2A RCFC was determined to be inoperable for greater than the allowed LCO Completion Time per LCO 3.6.6. The condition of the annubar flow element was determined to exist since original construction. Corrective actions included inspecting the flow elements for all Unit 1 and Unit 2 RCFCs for correct installation. Additionally, a technical evaluation was performed on the annubar flow error as a result of the backward installation to determine the effect of the potential low flow condition on the heat removal capability of the RCFC. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
4572005002 | Braidwood 2 | 03/28/2005 | 05/27/2005 | ML05154004 | <strong>Braidwood Unit 2 Reactor Trip due to Main Generator 'C' Phase Bushing Failure due to Overheating</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2005, at 1246, the Unit 2 main generator tripped as a result of a fault on the main generator "C" phase (T-3) bushing, followed by a turbine trip and reactor trip. Operator response to the trip was proper and all safety equipment operated as expected, with minor exceptions. The root cause of the Unit 2 trip was determined to be the lack of technical rigor applied during the redesign of the bushing in the 2000 time period. Contributing to this event was the unavailability of spare parts and lack of Original Equipment Manufacturer expertise due to the sale of the bushing product line. Corrective actions include implementation of a Technical Human Performance Program, evaluating the addition of the demography windows to allow online monitoring of the bushings, and formalizing of the corporate high voltage bushing strategy. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A).
4582005001 | River Bend | 01/15/2005 | 05/31/2005 | ML05158015 | <strong>Unplanned Manual Scram Due to Indication of Ground Fault in Main Generator</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2005, at 2:12 a.m. CST, while the plant was operating at 100 percent power, a manual reactor scram was initiated. This action was procedurally required in response to an alarm received at 2:10 a.m. which indicated a ground fault in the main generator. The plant shutdown proceeded normally, and safety systems responded as required. This event is being reported in accordance with 10CFR50.73(A)(2)(iv)(a) as a condition that required the manual actuation of the reactor protection system. Reactor water level was adequately controlled by the main feedwater system. No actuations of emergency core cooling systems, reactor safety relief valves, or standby diesel generators were required. The ground fault alarm relay was found to be overly sensitive to a low ground current, causing it to actuate early. Absent an intrusive internal examination of the generator, the most likely cause of the ground leakage current is deposition of copper oxide in the rectifier banks. These deposits resulted from an abnormally low dissolved oxygen concentration in the stator water cooling system due to a small hydrogen leak into the system. There were no safety systems out of service at the time of the event. This event was of minimal safety significance.
4582005002 | River Bend | 06/24/2005 | 08/23/2005 | ML05241014 | <strong>Unplanned Automatic Actuation of Standby Service Water due to Procedure Error</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2005, at approximately 1:13 a.m. CDT, an unplanned automatic start of a Division 2 standby service water pump occurred. The plant was in cold shutdown at the time. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as a condition that resulted in the automatic initiation of an emergency service water system. The Division 2 subsystem was being aligned to support diagnostic testing of a motor-operated valve in the system. The other Division 2 pump had already been started in accordance with the system operating procedure, and the subsequent steps directed the operator to open the inlet valve to the standby cooling tower. At this point, the pressure in the normal service water supply header decreased momentarily below the trip set point of the Division 2 automatic start circuitry. The second Division 2 pump started as designed. The causal analysis determined that the system operating procedure was inadequate for the alignment being performed, as it did not preserve sufficient margin in the normal service water supply pressure to avoid actuation of the low pressure trip units that start the standby system. The system operating procedure has been changed to correct this deficiency. No loads being supplied by service water were adversely affected by the actuation of the second Division 2 standby service water pump. Thus, this event was of minimal safety significance.
4582005003 | River Bend | 09/09/2005 | 11/04/2005 | ML05318017 | <strong>Operation Prohibited by Technical Specifications due to Diesel Generator Malfunction</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2005, with the plant operating at 100 percent power, the results of an ongoing investigation concluded that the Division 1 emergency diesel generator had been inoperable for approximately 23 days during July 2005. This was due to a cracked tube in the engine jacket water cooling system that may have prevented the generator from fulfilling its safety function. River Bend Technical Specifications allow a maximum outage time of 14 days for the emergency diesel generator. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(b) as operations prohibited by Technical Specifications. The tubing was replaced on July 31, 2005, thus the condition no longer existed at the time of discovery.
4612005001 | Clinton 1 | 05/04/2005 | 07/14/2005 | ML05207069 | <strong>Inadequate Procurement Specification for Charcoal Results in Inoperable Control Room Ventilation Subsystem</strong><br /><i>Abstract:&nbsp;</i>On 5/16/05 with the plant at power, and 12 days after charcoal adsorber samples were taken from Division 1Control Room Ventilation (VC) subsystem recirculation bed filter for penetration testing per Technical Specification (TS) 3.7.3.3, the methyl iodide penetration level of the charcoal sample was determined to be unacceptable. As a result of the unsatisfactory test results, TS 3.7.3 was not met. Additionally, during 5 of the 12 days, the Division 2 VC subsystem was inoperable due to a planned emergency diesel generator (EDG) maintenance outage; however, the EDG was restored to operable status prior to receipt of the charcoal sample results. Thus both subsystems were inoperable during 5 days;however, an analysis concluded that the degraded charcoal would have been capable of performing its safety function. The cause of this event is the industry standards providing the basis for charcoal purchasing requirements were inadequate for the unique application at Clinton Power Station (CPS) and had no limit on as-manufactured moisture levels. Corrective actions for this event included replacing the charcoal in the Division1 VC Subsystem with acceptable charcoal, evaluating other charcoal beds in the VC system as acceptable,and establishing a purchasing requirement for charcoal to limit moisture to 8 percent or less by weight.
4822005001 | Wolf Creek | 01/07/2005 | 03/08/2005 | ML05074036 | <strong>Corrective Action to Fire Wrap Raceway for Valve EMHV8803A Not Included in Design Change Package</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2005, conditions were discovered where a postulated fire could cause the loss of a fire safe shut down success path. During reviews associated with post-fire safe shutdown reanalysis work, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel discovered that power and control cables for Boron Injection Tank (BIT) inlet valve, EMHV8803A, could be damaged by a fire in Fire Area A-1. This could cause the loss of the centrifugal charging pump's (CCP's) capability to successfully inject borated water, through the BIT, into the reactor. This does not meet WCNOC's commitments to 10 CFR 50 Appendix R.lIl.G as reflected in the approved Fire Protection Plan. A 1-hour fire watch was implemented in the fire area. The safety significance for this event is low.
4822005002 | Wolf Creek | 04/15/2005 | 06/14/2005 | ML05172038 | <strong>Reactor Coolant System Pressure Boundary Leakage due to Small Cracks in Steam Generator Lower Head Bowl Drain Lines</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2005, during Wolf Creek Generating Station (WCGS) refueling outage number 14, during performance of Alloy 600 bare metal visual examinations, the presence of boric acid deposits indicated a leak in a weld in the steam generator (SG) D lower head bowl drain line. Subsequently on April 20, 2005, boric acid deposits indicating a leak in a weld in the SG C lower head bowl drain line were discovered. The Reactor Coolant System (RCS) leakage constitutes degradation of a principal safety barrier and is considered reportable to the requirements of 10 CFR 50.73(a)(2)(ii)(A), "The condition of the nuclear power plant, including its principal safety barriers, being seriously degraded." SG C and D bowl drain leaks were subsequently repaired, examined and tested. SG A and B bowl drains were also repaired similar to the SG C and D bowl drains as a preventive measure. The completed weld repairs were all found acceptable. The pressure boundary leakage path is suspected to be the nozzle coupling to vessel weld. The most likely technical cause of the SG bowl drain leak is primary water stress corrosion cracking (PWSCC). The safety significance of this event is low. Although welds of the steam generator bowl drains may be susceptible to PWSCC that can result in small leaks, industry experience with PWSCC shows that complete failure of the weld joints is considered to be very unlikely.
4822005003 | Wolf Creek | 04/30/2005 | 06/29/2005 | ML05187032 | <strong>Failure to Maintain Closure of Containment Penetrations During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2005 with the plant in Mode 6, Refueling, Wolf Creek Nuclear Operating Corporation (WCNOC) personnel discovered two instances where containment closure, per Technical Specification 3.9.4 was not met. In the first instance, an air-to-air pathway existed through the exterior equalizing valve of the auxiliary access hatch. A temporary closure device was installed on the auxiliary access hatch. The evaluation conducted for the temporary closure device was not sufficient to ensure complete closure of the air-to-air pathway through the equalizing valve. Fuel movement was stopped and the equalizing valve was placed under administrative controls. In the second instance, the 'B' Steam Generator had an air-to-air pathway through the containment wall to the auxiliary building. The 'B' Steam Generator manways were removed, opening the interior of the steam generator to the containment. The auxiliary building was open to the interior of the 'B' steam line through valves ABV0071 and ABV0070 which were uncapped and open under a clearance order. Upon discovery, the penetration was immediately placed under administrative control.
4822005004 | Wolf Creek | 05/10/2005 | 07/08/2005 | ML05199037 | <strong>Failure of Auxiliary Building Ventilation Dampers to Close on Safety Injection Signal</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2005, during Wolf Creek Generating Station (WCGS) refueling outage number 14, during performance of integrated testing of the Emergency Diesel Generator and Safeguards Actuation System, four condenser air removal filtration dampers located in the auxiliary building failed to close following a safety injection signal due to a design inadequacy of the actuation circuitry. The function of the dampers is to support operability of the Emergency Exhaust System per Technical Specification LCO 3.7.13, which limits the release of radioactivity from the Auxiliary Building following certain accident conditions. This condition is considered reportable to the requirements of 10 CFR50.36(c)(2), 10 CFR 50 .73(a)(2)(i)(B), 10 CFR 50 .73(a)(2)(v)(C), and 10 CFR 50 .73(a)(2)(ii)(B). The design inadequacy was determined to have occurred in 1981, prior to commercial operation. The deficiency in the design of the actuation circuitry was corrected and modifications were implemented in the field prior to entering the mode requiring operability of the Emergency Exhaust System. The four modified dampers were tested and all were found acceptable.
4822005005 | Wolf Creek | 09/29/2005 | 11/28/2005 | ML05341014 | <strong>Validation of Post Fire Safe Shutdown (PFSSD) Capabilities of Fire Area A-8</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2005, conditions were discovered where a postulated design basis fire could cause the loss of a safe shut down success path. During reviews associated with post fire safe shutdown reanalysis work, Wolf Creek personnel discovered that the ability to perform diverse means (operator manual actions) required to mitigate spurious actuations came into question for Fire Area A-8. This could cause the loss of the centrifugal charging pump's (CCP's) capability to successfully inject borated water into the reactor, due to a potential for gas intrusion into the suction of the pumps. This does not meet Wolf Creek's commitments to 10 CFR 50 Appendix R.III.G as reflected in the approved Fire Protection Plan. A 1-hour fire watch was implemented in the fire area. The safety significance for this event is low.
4822005006 | Wolf Creek | 11/16/2005 | 01/13/2006 | ML06023005 | <strong>Unanalyzed Condition Related to Loss of RCP Seal Cooling During a Postulated Appendix R Fire Event</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2005, conditions were discovered where a postulated fire could cause the loss of a safe shut down success path. During a timed walk down of an Off Normal Operations procedure for shut down outside the Control Room, the demonstrated response time for restoring Reactor Coolant Pump (RCP) seal cooling did not meet the required time. Failure to restore the RCP seal cooling in an appropriate time could result in damage to the RCP seals. Failure of the RCP seals could result in an inability to maintain pressurizer level during plant shutdown, thus not satisfying the 10CFR50 Appendix R, Section 111.L.2.b requirement. A 1-hour fire watch was implemented in the Control Room.
4832005001 | Callaway | 01/19/2005 | 03/18/2005 | ML05083025 | <strong>Reactor Trip while Replacing RP043 Control Cabinet Power Supply</strong><br /><i>Abstract:&nbsp;</i>At 1251, 1/19/05, a reactor trip occurred while replacing the primary power supply in Control Cabinet RP043. During replacement of the failed power supply, pressure was applied to the top of the secondary power supply located beneath the failed power supply. The top cover of the secondary power supply flexed inward and shorted out an energized heat sink that caused a momentary failure of that power supply. This resulted in "A" Main Feedwater Regulating Valve going closed and causing a reactor trip on Low-Low level in "A" Steam Generator (S/G). The plant was stabilized in Mode 3 and both the primary and secondary RP043 power supplies were replaced. Callaway Plant returned to power at 1735 on 1/20/05. A Root Cause Analysis was conducted and concluded that the impact of not placing pressure on top of a power supply was not clearly understood, work instructions did not adequately address power supply removal techniques, and appropriate tools were not available. Corrective actions include additional training, procurement or fabrication of necessary tools, and development of improved work instructions for future power supply replacements.
4832005002 | Callaway | 03/26/2005 | 05/19/2005 | ML05146034 | <strong>Plant Shutdown Required by Technical Specification 3.7.8 for an Inoperable Train of Essential Service Water</strong><br /><i>Abstract:&nbsp;</i>At 0300, 3/23/05, 72-hour Technical Specification Action 3.7.8.A was entered when a pinhole leak was discovered in "B" Essential Service Water (ESW) system between the "B" ESW pump strainer and discharge isolation valve. Subsequent ultrasonic testing (UT)determined that approximately seven linear feet of piping in the "B" ESW train was affected and required replacement. UT testing was satisfactorily performed on the identical section of "A" ESW train to ensure a similar problem did not exist. "B" ESW train piping replacement was performed in accordance with planned work documents, however at 2100, 3/25/05 all necessary repairs and retests had not been completed. Although only 66 hours had expired since entering 72-hour Technical Specification Action 3.7.8.A, Callaway Plant proactively decided to commence a reactor plant shutdown in accordance with Technical Specification Action 3.7.8.B for an Inoperable "B" Essential Service Water train. At 0624, 3/26/05 the reactor was declared shutdown and Callaway Plant entered Mode 3. At 0249, 3/27/05 all repairs and retests were completed on the "B" ESW train and it was declared Operable. Instead of beginning a return to operation, plant management decided to perform additional discretionary work to enhance unit reliability and as a result, Callaway did not return to power until 1907, 4/2/05.
4832005003 | Callaway | 03/29/2005 | 05/19/2005 | ML05146033 | <strong>Lo-Lo Steam Generator Level Results in Actuation of Reactor Protection System and Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On 3/29/05 while in Mode 3, preparations were underway to perform a leak test of "C" Steam Generator (S/G) Main Feedwater Isolation Valve AEFV0041. While establishing necessary initial conditions, S/G level oscillations began to occur. As part of the leak test, main feedwater flow was isolated to the "C" S/G. Due to a low differential between the discharge pressure of the condensate pump being used to maintain S/G levels and main steam header pressure, leakage past AEFV0041 sustained "C" S/G level until the "C" S/G Bypass Feedwater Regulating Valve was manually isolated. This isolation of flow to "C" S/G resulted in level decreasing until a low level alarm actuated. After initiating auxiliary feedwater flow, level initially increased but subsequently began decreasing until a reactor trip occurred due to low-low water level in "C" S/G. Plant systems responded as required and all systems were stabilized at normal Mode 3 conditions. A Root Cause Analysis team concluded that this event occurred because the general operating procedure and the leak test procedure were deficient and on-shift operators decided not to utilize a start-up feed pump verses the condensate pump. Corrective actions included revising the test procedure and covering this event in future licensed operator training.
4992005001 | South Texas 2 | 02/09/2005 | 04/05/2005 | ML05098011 | <strong>Shutdown of STP Unit 2 due to Reactor Coolant System Pressure Boundary Leak</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2005 at 1222 hours, South Texas Project (STP) Unit 2 commenced a reactor shutdown required by Technical Specification (TS) 3.4.6.2, "Reactor Coolant System - Operational Leakage".Following investigation into an increasing containment atmosphere particulate radiation monitor trend, primary leakage(steam plume) was discovered coming from a 3 inch vent line off of the UAW Cold Leg Safety Injection line. The leak was determined to be unisolable Reactor Coolant System Pressure Boundary leakage and Unit 2 was shutdown to MODE 5 in accordance with TS 3.4.6.2. At the time of discovery, the total unidentified reactor coolant system leak rate was determined to be 0.13 gallons per minute.This event is reportable in accordance with 1 OCFR50.73(a)(2)(i)(A) as completion of a shutdown required by the Technical Specifications and in accordance with 10CFR50.73(a)(2)(ii)(A) as serious degradation of a principal safety barrier.The root cause of the pressure boundary leak was a crack propagating from a flaw in a socket weld to due to high cycle fatigue.This condition resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment other than the leaking weld joint. There were no challenges to plant safety.The leak was repaired by cutting off the leaking vent line and plugging the connection. Vibration measurement forsusceptible lines has been performed for STP Unit 1 and is planned for Unit 2 to identify any further extent of condition.
4992005002 | South Texas 2 | 02/28/2005 | 04/27/2005 | ML05123036 | <strong>Essential Chiller 22C Inoperable Longer Than Allowed By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2005 at 0207, a start of Essential Chiller 22C was attempted. The chiller failed to start. Concurrently, the "C" train Essential Chilled Water expansion tank low level alarm annunciated and low discharge pressure on Essential Chilled Water pump 2C was observed. The cause of the chiller failure to start was that "C" train Essential Chilled Water had been partially drained to the point that air binding of the chilled water pump occurred. Periodic draining of the system was determined to have started 10 days prior to the attempted start of the chiller, at which time the chiller became inoperable. Because the chiller allowed outage time is 7 days, this condition was in violation of the plant Technical Specifications. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." The "C" train of the Essential Chilled Water System was filled and vented in accordance with plant procedures and returned to service on February 28, 2005 at 2048. No loss of safety function occurred. The cause of this event was the action taken to drain the expansion tank level back into the normal operating band to keep the level alarm clear caused an unknown amount of water to be drained from the system. This resulted in air binding in the system upon startup. The need to establish additional controls on draining this system was identified by this event. The core damage risk impact associated with the inoperability of Essential Chiller 22C is 1.6E-7. The analysis assumes that train "C" Essential Chilled Water was non-functional for 10 days.
4992005003 | South Texas 2 | 03/31/2004 | 05/10/2005 | ML05133025 | <strong>Inoperable Cold Overpressure Mitigation System</strong><br /><i>Abstract:&nbsp;</i>On Monday, March 7, 2005, preparations were being made to implement a modification to Unit 1 during its refueling outage. Isolation of two actuation cabinets of the Solid State Protection System was required to complete the modification. Prior to isolation, it was determined that this would make the Cold Overpressurization Mitigation System (COMS) inoperable when Technical Specification 3.4.9.3 required that it be operable. This was resolved by rescheduling the system isolation. Subsequent review found that while installing a similar modification on Unit 2 during the preceding Unit 2 refueling outage, two actuation cabinets were de-energized, making COMS inoperable without compensatory action as required by Technical Specifications. This was found to be reportable on March 11, 2005. The root cause of this event was that the operational impact on COMS of de-energizing the 'A' and 'B' SSPS actuation cabinets for maintenance was not recognized. Detailed information regarding which equipment/components would be affected was not readily available in a usable format for review. For corrective action, a load list will be developed for each of the Solid State Protection System actuation cabinets identifying the affected components and their state when the cabinet is de-energized. This information will be included in the applicable operating procedure. As a compensatory action until the corrective action is completed, the system engineer will be contacted to confirm the extent of impact on plant equipment/components prior to implementation of scheduled work activities that include de-energizing SSPS equipment. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
4992005004 | South Texas 2 | 07/11/2005 | 11/30/2005 | ML05341015 | <strong>Essential Cooling Water Inoperable Longer than Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>In May 2005, cavitation damage was discovered in the slip-on flange assembly immediately downstream of the Component Cooling Water (CCW) Heat Exchanger 1B Essential Cooling Water (ECW) Return Throttle Valve, 1-EW-0064. Work requests were initiated to inspect the CCW heat exchanger return throttle valves in all trains of both units. Capitation pitting, circumferential pipe cracking, secondary axial pipe cracking, and pipe end to flange weld separation were discovered in the aluminum bronze pipe inside a slip-on flange immediately downstream of the CCW Heat Exchanger 2A ECW Return Throttle Valve, 2-EW-0027. Structural integrity of the pipe could not be verified using the requirements of NRC Generic Letter 90-05, "Guidance for Performing Temporary Repair of ASME Code Class 1, 2, and 3 Piping." Because structural integrity could not be demonstrated, ECW Train 2A was declared non-compliant with ASME Code requirements and INOPERABLE per Technical Specification requirements. STP Nuclear Operating Company (STPNOC) has determined, based on metallurgical analysis of the failed parts, that ECW Train 2A was inoperable for an undetermined period of time. The condition logically existed for a period longer than the Technical Specification 3.7.4 Allowed Outage Time although the length of time is not known. As a result STPNOC considers this event reportable pursuant to 10CFR50.73(a)(2)(i)(B) as a Condition Prohibited by Technical Specifications. In addition, on August 15, 2005 an inspection of the corresponding Train 2B throttle valve, 2-EW-0064, discovered a similar condition. Therefore, this event is also reportable pursuant to 10CFR50.73(a)(2)(vii) as a Common-cause Inoperability of Independent Trains. The root cause is the failure to incorporate requisite inspection activities for ECW piping into station programs. ECW 2A and 2B conditions have been repaired using ASME code requirements.
4992005005 | South Texas 2 | 10/19/2005 | 12/21/2005 | ML06009029 | <strong>125 VDC Switchboard De-energized without Placing FHB HVAC in Emergency Recirculation Mode</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2005, with Unit 2 shut down for refueling, during movement of fuel assemblies in the Fuel Handling Building (FHB), Class 1 E 125 VDC Switchboard E2C11 was de-energized as part of scheduled bus maintenance without placing the FHB Heating, Ventilation, and Air Conditioning (HVAC) system in the Emergency Recirculation mode as required by Technical Specification 3.3.2 Action 30. The Train C FHB HVAC actuation relays are located in Relay Rack (RR) 145C and powered from 125V DC Panel 039C; which is in turn powered from Switchboard E2C11. These relays require DC power to automatically place the FHB HVAC in the Emergency mode and would not have actuated with Switchboard E2C11 de-energized. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(b) as a event or condition prohibited by Technical Specifications. The root cause of this event is the over-reliance on highly qualified and experienced individuals to plan and schedule Electrical Bus Outages and the failure to develop and implement procedures to provide guidance for these evolutions. This event did not adversely affect the safety of the public or station personnel.
4992005006 | South Texas 2 | 10/18/2005 | 12/20/2005 | ML05362002 | <strong>Missing Motor-Operated Valve T-Drains</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2005, with Unit 2 shut down for refueling, it was discovered that the Limitorque motor on valve 2-SI-MOV-0019C had ordinary pipe plugs installed in the two drilled holes designed to contain T-drains, which are required as part of the motor's environmental qualification. During the subsequent inspection of other Unit 2 MOVs, valve RA-MOV-0003 was discovered to have one ordinary pipe plug and one T-drain installed rather than the two required T-drains. It was determined that the condition was reportable because the lack of T-drains would have rendered the associated systems inoperable for a period of time in excess of that allowed in the Limiting Condition for Operation.
5282005001 | Palo Verde 1 | 02/06/2005 | 09/20/2006 | ML06272013 | <strong>Actuation of an Unit 1 Emergency Diesel Generator (EDG) and Plant Shutdown Required by TS</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2005, at 22:19 a valid actuation of the PVNGS Unit 1 Train "B" Emergency Diesel Generator (EDG) occurred as a result of under-voltage on its respective safety bus (1E-PBB-S04). EDG "B" started and loaded as designed to energize 1E-PBB-S04. The loss of power to the safety bus was the result of a fault associated with a 13.8KV load breaker cubicle which caused the breaker for the normal power supply to switchgear 1E-NAN-S06 to trip open on over-current. The PVNGS Fire Department and Auxiliary Operators responded to a report of smoke and upon arrival found no fire. The Fire Department verified the fire was completely extinguished and there were no secondary fires. Unit 1 entered Technical Specification Limiting Condition for Operation (LCO) 3.8.1, Condition "A," for one (of two) required offsite circuits inoperable. Various other Technical Specifications LCO's were momentarily entered and exited for 1E-PBB-S04 being de-energized for approximately 7 seconds. On February 9, 2005 at 03:12 Unit 1 was shutdown to meet the TS LCO 3.8.1, Condition "H." No Emergency Plan declaration was made and none was required. Unit 1 was at approximately 100 percent power, at normal operating temperature and pressure prior to and following the EDG actuation. No other engineered safety feature actuations occurred and none were required. The event did not adversely affect the safe operation of the plant or the health and safety of the public. Previous similar events have been reported in LERs 50-528/2004-006, 50-529/2004-003-00 and 50-530/2003-004.
5282005002 | Palo Verde 1 | 02/17/2005 | 04/18/2005 | ML05122011 | <strong>Technical Specification Violation: Mode Change with Safety Injection Valve Not in Its Required Position</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2005 at approximately 17:52 hours MST, Unit 1 was in Mode 3, Hot Standby, and increasing reactor coolant system temperature and pressure to return the unit to power operation when a technical specification violation occurred. Specifically, mode changes were performed with a safety injection valve not in its required position. The condition was discovered on February 21, 2005 when an auxiliary operator noted dual light position indication at the valve breaker. The cause of the event is under evaluation and is most probably a human error. Corrective actions include revising procedures to ensure adequate position verification is performed. There have been 3 previous similar events reported to the NRC in the last 4 years.
5282005003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 03/24/2005 | 05/20/2005 | ML05152047 | <strong>Calibration Method That Might Have Failed to Provide Reactor Protection During Low Power Operation</strong><br /><i>Abstract:&nbsp;</i>A valid question was raised concerning the Excore Log Safety Channels. The condition is fundamentally a concern about the instrument channels, whether they are linear over their entire span. The condition is primarily related to the behavior of the cards in the channel drawer, not including the detector and the preamplifier. The channels are calibrated at essentially full power, which is in the Mean Square Voltage (MSV) region. However, the safety function is of concern at low powers in the Log Count Rate (LCR) region. The concern was that the LCR and MSV regions did not adequately align so that the channels would be unacceptably inaccurate at low powers. This appeared to be caused by the calibration method provided by the vendor and implemented by Palo Verde which introduced 'tolerance creep" that might have failed to provide reactor protection during very low power operation. Corrective actions have been implemented to ensure there is no loss of a safety function. There have been no previous similar licensee events reported in the last three years.
5282005004 | Palo Verde 1 | 08/12/2005 | 10/07/2005 | ML05292007 | <strong>Technical Specification Required Reactor Shutdown on EDG B Voltage Regulator Failure</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2005 at 0019 Palo Verde Unit 1 was in Mode 1 (Power Operations), operating at approximately 94 percent power, when Control Room personnel commenced a reactor shutdown required by Technical Specification 3.8.1. Prior to the event, on August 9, 2005, Emergency Diesel Generator "B" failed to maintain proper steady state output voltage during the performance of a routine monthly surveillance test. Engineering and Maintenance personnel were unable to identify and correct the cause of the fluctuating generator output voltage within the 72 hour required action completion time associated with Limiting Condition for Operation 3.8.1 which would have expired August 12,2005 at 0420. At 0216 on August 12, 2005 Control Room personnel manually tripped the reactor from 23 percent reactor power. At 0217, Palo Verde Unit 1 entered Mode 3 (Hot Standby), completing a reactor shutdown required by Technical Specification 3.8.1. At 2237 on August 12, 2005, Unit 1 entered Mode 5 (Cold Shutdown) and exited LCO 3.8.1. All times in this report are approximate and Mountain Standard Time unless noted otherwise.In the past three years, Palo Verde reported reactor shutdowns required by Technical Specifications but none associated with the same root cause.
5282005005 | Palo Verde 1 | 08/26/2005 | 10/24/2005 | ML05307001 | <strong>Unplanned Reactor Trip and Engineered Safety Feature Actuation - Unit 1</strong><br /><i>Abstract:&nbsp;</i>On August 26, 2005 at approximately 18:24 (MST), Unit 1 reactor tripped during a plant startup. Main Feedwater had been placed in service and the digital feedwater control system (DFWCS) was in automatic. Uncomfortable with the system performance, the secondary control room operator attempted to maintain steam generator (SG) level by taking manual control of the DFWCS and adjusting the level. After several attempts selecting the DFWCS from automatic to manual, excessive feed rate increased the SG water level to near its trip setpoint before feeding was secured. As the cooler water expanded, the high SG level setpoint was reached resulting in an engineered safety feature (ESF) actuation of the Main Steam Isolation System (MSIS) and a reactor Trip once the S/G reached 91.5 percent narrow range (NR) level. The high level trip was caused by a combination of individual and team human performance deficiencies and inadequate resolution of identified DFWCS issues. Operation's management removed affected personnel from shift duties until preliminary investigation determined extent of performance deficiencies and coached those individuals on personal accountability to ensure compliance with Operations Department Principles and procedures prior to resumption of shift duties. No similar condition has been reported in the past three years.
5282005006 | Palo Verde 1 | 03/18/2005 | 04/25/2006 | ML06129054 | <strong>TS Required Reactor Shutdown on EDG "A" Failure to Start During Post Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2005 at 15:00 Mountain Standard Time (MST) Palo Verde Unit 1 was in Mode 1 (Power Operations), operating at approximately 100 percent power, when Control Room personnel commenced a reactor shutdown required by Technical Specification 3.8.1. On March 17, 2005, at approximately 04:11 MST, Unit 1 Diesel Generator "A" failed to start during its post maintenance retest. The diesel generator (DG) tripped on incomplete sequence. Prior to tripping, the DG reached approximately 100 RPM for fifteen seconds. It has been determined that the cause of the DG failure was due to a governor failure, whose speed controller showed signs of oil contamination. The failed governor has been replaced. At 17:50 MST on March 17, 2005, DG "B" was tested satisfactorily to confirm there was no common cause failure. Unit 1 was shutdown because the load rejection retest of DG "A" which was required to be performed is prohibited from being performed in Modes 1 through 4. LCO 3.8.1 expired at 04:00 MST, March 19, 2005 requiring initiation of a shut down required by Technical Specifications. At 08:48 MST on March 19, 2005, Unit 1 entered Mode 5 (Cold Shutdown) and exited LCO 3.8.1. In the past three years, Palo Verde reported reactor shutdowns required by Technical Specifications but none associated with the same root cause.
5282005007 | Palo Verde 1 | 10/04/2002 | 02/10/2006 | ML06053051 | <strong>Potential Loss of Low Pressure Safety Injection (LPSI) due to a Seismic Event</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2005 a maintenance technician discovered a screwdriver inside the limit switch compartment for the motor operated safety injection valve SIAUV0635, "A" Train Low Pressure Safety Injection (LPSI) valve. The screwdriver was left in the limit switch compartment the last time the compartment was accessed during refueling outage 10 on October 4, 2002. A Maintenance Rule Functional Failure evaluation was completed on December 13, 2005. Engineering personnel determined that the screwdriver could have been dislodged during a seismic event potentially rendering SIAUV0635 inoperable. Based on Engineering's evaluation, this condition could have prevented the LPSI system train "A" from performing its safety function and as such LPSI was considered inoperable from October 4, 2002 through October 26, 2005. The screwdriver was removed. SIAUV0635 was satisfactorily retested and is currently considered Operable. A briefing was conducted with the technicians in the valve services shop and the responsible individuals were coached. There have been no previous similar licensee events reported in the last three years.
5282005008 | Palo Verde 1 | 10/30/2005 | 07/12/2006 | ML06201019 | <strong>Inverter Failure - Technical Specification Violation - Unit 1</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2005 at approximately 12:26 (MST), Unit 1 was de-fueled when distribution panel 1EPNBD26 failed (lost power). This failure resulted in the following actuations in the Control Room: Train B Containment Purge Isolation Actuation Signal (CPIAS), Fuel Building Essential Ventilation Actuation Signal (FBEVAS) and Control Room Essential Filtration Actuation Signal (CREFAS). Since the core was de-fueled and no irradiated fuel movement was in progress, no Technical Specification (TS) LCO entries were required. While evaluating the loss of power to 1EPNBD26, an undervoltage condition was identified on inverter 1EPNBN12. The inverter subsequently failed with the local inverter alarm indicating a blown fuse. The cause of the inverter failure was from a failed capacitor within the inverter. Troubleshooting revealed the capacitor was defective (lacking dielectric oil). Eight of the fifteen capacitors were found without oil. Upon completion of the equipment root cause of failure on December 15, 2005, engineering determined that due to the lack of dielectric oil, it could not be justified to declare the inverters operable, and as such, it did not meet the requirements of Technical Specification 3.8.7, "Inverters - Operating". No similar condition has been reported in the past three years.
5282005009 | Palo Verde 1 | 12/21/2005 | 05/22/2006 | ML06157021 | <strong>Technical Specification Violation for Operation without Both Reactor Coolant System Loops Operable</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2006 vibration testing was being performed in Unit 1 to obtain data to correct an issue with vibration of the shutdown cooling train A suction line. The test data unexpectedly indicated that stopping one reactor coolant pump (RCP) in loop 2 with all four RCPs operating resulted in vibration levels at the shutdown cooling suction valve, 1JSIAUV0651, which exceeded the design vibration limit. The apparent cause of the vibration is a latent design deficiency which allowed the shutdown cooling suction line to form an acoustic resonator that produced the high vibration. Corrective action includes relocating valve SI 651 to alter the fundamental frequency of the acoustic resonator. There have been no previous similar reports made by Palo Verde Nuclear Generating Station in the last three years.
5292005001 | Palo Verde 2 | 04/23/2005 | 06/20/2005 | ML05188007 | <strong>Reactor Head Vent Axial Indications caused by Degraded Alloy 600 Component</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2005, engineering personnel performing preplanned in-service examinations of the reactor vessel head vent penetration discovered two axial indications in the reactor vessel head vent penetration. The indications were located on the inner diameter surface of the pipe adjacent to the J-weld to the head and are part of the RCS pressure boundary. As soon as Engineering determined that the reactor head vent pipe had two axial indications, they promptly notified the Shift Manager who made the decision to enter TLCO 3.4.103 condition "A" and conservatively make an 8 hour ENS notification. The indications were conservatively identified as abnormal degradation of the reactor coolant system pressure boundary and necessitated taking corrective action to restore the barrier's capability. The indications were repaired prior to the unit's return to power operations. Similar previous conditions of pressure boundary leakage were reported in LER 50/528-2004-001-00, LER 50/530-2004-001-00 and LER 50/530-2003-002-00.
5292005002 | Palo Verde 2 | 06/10/2005 | 08/03/2005 | ML05224028 | <strong>T/S 3.0.4 Violation; mode change made with one of two required LPSI pumps inoperable</strong><br /><i>Abstract:&nbsp;</i>This LER reports an event resulting in a Technical Specification violation when a mode change occurred with one of two required Low Pressure Safety Injection (LPSI) trains unknowingly inoperable due to a degraded mechanical pump seal. On May 16, 2005 at approximately 09:50 hours MST Unit 2 entered MODE 3 with pressurizer pressure greater than or equal to 1837 psia while LPSI pump 'A' had a degraded mechanical seal. This is contrary to LCO 3.0 .4 which precludes entry into a MODE or other specified condition in the Applicability statement when an LCO is not met . LCO 3 .5.3 requires two Emergency Core Cooling Systems to be Operable in Modes 1, 2, and in Mode 3 when pressurizer pressure is greater than or equal to 1837 psia or when RCS cold leg temperature is greater than or equal to 485 degrees Fahrenheit. There have been three previous similar licensee events reported in the last three years.
5292005003 | Palo Verde 2 | 06/23/2005 | 08/13/2005 | ML05238024 | <strong>Two Independent Trains of Auxiliary Feedwater Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2005 at approximately 0823 Mountain Standard Time (MST) Unit 2 was operating at 100 percent power, mode 1 (power operations), when work control personnel notified the control room that door C-A06 was found opened by maintenance personnel with no compensatory measures established. Door C-A06 is a watertight fire door that functions as the train separation barrier between Auxiliary Feedwater (AFW) pump room "A" and "B." When door C-A06 is open with the unit operating in mode 1, compensatory action must be taken in order to maintain both AFW trains "A" and "B" operable. The maintenance crew that discovered door C-A06 open, established appropriate compensatory measure while they performed their task and closed C-A06 when they exited the area. Based on a review of security computer transaction logs, control room personnel determined that door C-A06 was opened with no compensatory actions taken between 0712 and 0755 (approximately 43 minutes). As such, AFW trains "A" and "B" were considered inoperable between 0712 and 0755. Based on further review and personnel interviews, an investigation concluded that a security officer had failed to close C-A06 after leaving the AFW pump room area. The investigation classified the event as an isolated human performance error. The security officer was coached on securing watertight fire doors. In the past three years, no previous similar events were reported.
5292005004 | Palo Verde 2 | 08/22/2005 | 07/01/2006 | ML06193014 | <strong>Technical Specification Required Shutdown due to Core Protection Calculators Inoperable</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2005 at approximately 1750 Mountain Standard Time (MST), Unit 2 completed a reactor shutdown required by the Technical Specifications. The shutdown was required due to all four channels of the Core Protection Calculators (CPC) being declared inoperable on August 22 at 1326 MST based on information from the CPC vendor that software changes that had previously been implemented in Unit 2 CPCs changed the way the CPCs would operate for a failed sensor. The direct cause of the Unit 2 CPC software issue was a 2002 revision of the software requirements specification led to an inconsistency with the system requirements specification. The root cause was determined to be that no formal communication plan existed within the internal Westinghouse users of the reactor trip function in the CPCs. The Unit 2 software has been corrected. Unit 1 had the correct software installed when the software change was made. Unit 3 has not installed the new software at this time. Although other Technical Specification required shutdowns have been reported in the last three years none were due to similar causes or equipment.
5292005005 | Palo Verde 2, Palo Verde 3 | 10/11/2005 | 12/08/2005 | ML05354022 | <strong>TS Required Reactor Shutdown - LCO 3.0.3A Inoperable ECCS, Containment Spray & Refueling Water Tank</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2005 at 13:33 Mountain Standard Time (MST) Palo Verde Unit 2 and Unit 3 were in Mode 1 (Power Operations), operating at approximately 100 percent power, when Control Room personnel entered LCO 3.0.3.a due to Units 2 & 3 declaring both trains of Emergency Core Cooling (ECCS) and Containment Spray INOPERABLE due to the Refueling Water Tank (RWT) being declared INOPERABLE. At 16:03 MST on October 11, 2005, Unit 2 initiated a TS required shutdown IAW the requirements of LCO 3.0.3. On October 12, 2005 at 07:06 MST Unit 2 entered MODE 5 and exited LCO 3.0.3. At 16:55 MST on October 11, 2005, Unit 3 initiated a TS required shutdown IAW the requirements of LCO 3.0.3. On October 12, 2005 at 02:33 MST Unit 3 entered MODE 5 and exited LCO 3.0.3. In the past three years, Palo Verde reported reactor shutdowns required by Technical Specifications but none associated with this same root cause.
5292005006 | Palo Verde 2 | 05/15/2005 | 04/20/2007 | ML07122008 | <strong>Condition Prohibited by Technical Specifications Due to Partial Fouling of B Diesel of Generator (EDG) Fuel Oil Strainer</strong><br /><i>Abstract:&nbsp;</i>During the period May 15 through November 3, 2005, Unit 2 operated in Modes 1 through 5 following are fueling outage with an inoperable "B" train emergency diesel generator (EDG 2B), contrary to Technical Specifications 3.0.3, 3.0.4, 3.8.1, and 3.8.2. Even though EDG 2B successfully completed required surveillance tests during the period, duplex fuel oil strainers and filters exhibited increasing differential pressures caused by particulates suspended in the fuel oil day tank. Filter elements were found in the strainer housing instead of the required strainer elements on November 3, 2005. At least one EDG remained functional throughout the period. The root cause was accumulated day tank sediment that became suspended in the fuel oil when the tank was refilled following an outage Inspection. Ineffective equipment trending and work priority management resulted in untimely identification and correction of the partially loaded strainers. The EDG 2B fuel oil day tank was subsequently cleaned. Other corrective actions include scheduled cleaning of the other 5 station EDG fuel oil day tanks, and improvements to equipment trending and management of work priorities. No similar events were reported in the previous three years.