## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192007001 | Oyster Creek | 07/17/2007 | 09/17/2007 | ML07267013 | <strong>Automatic Reactor Scram following Trip of Reactor Feed Pump</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2007 at 05:21 while operating at 100% power, an automatic reactor scram occurred due to low reactor water level following a trip of the "C" Reactor Feed Pump (RFP). The cause of the "C" RFP trip is attributed to an electrical fault internal to the motor. This transient led to an automatic scram on low reactor water level and subsequent reactor isolation on a low-low reactor level. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to the automatic reactor protection system and subsequent ECCS actuations.
2192007002 | Oyster Creek | 07/20/2007 | 09/18/2007 | ML07267012 | <strong>Intermediate Range Monitor 16 Inoperable During Startup</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2007, a plant startup from forced outage 1F12 commenced with Intermediate Range Monitor (IRM) 17 in the bypassed mode. At 14:40, operators noted that IRM 16 was not responding to an increase in reactor power. Both IRM 16 and IRM 17 are part of Reactor Protection System (RPS) Trip System 2. Three of four IRMs in each of two Trip Systems are required to be operable by Technical Specifications for the Startup Mode. The apparent cause for IRM-16 failure is a failure of the detector. Corrective actions included replacing the failed detector, notifying the industry of the failure, and developing a plan to restore all nuclear instrumentation to an (a)(2) Maintenance Rule status. There were no safety consequences impacting plant or public safety as a result of this event: This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) due to the station being in a condition prohibited by Technical Specifications Table 3.1.1, Protective Instrumentation Requirements, Function 9, Intermediate Range Monitor.
2192007003 | Oyster Creek | 12/19/2007 | 02/13/2008 | ML08051069 | <strong>Unplanned Manual Reactor Scram following Trip of Reactor Feed Pump due to Lowering Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>At 1145 on 12/19/2007, an Unplanned Manual Reactor Scram occurred due to critical omission of technical information regarding the minimum Circulating Water (CW) system configuration necessary to maintain the Main Condenser water boxes filled. At the time of the event, the station CW system was being operated in accordance with procedural guidance and available design basis information. Based upon a review of historical documents since 1968, a critical omission of technical information existed regarding the minimum CW system configuration necessary to maintain the Main Condenser water boxes filled. Two corrective actions to prevent recurrence were developed; (1) revise the CW operating procedure to provide minimum system configuration and pressure to maintain the Main Condenser water boxes filled, and (2) revise design basis documentation to provide minimum system configuration and pressure to maintain the Main Condenser water boxes filled. Additional corrective actions were developed including a Technical Human Performance case study to reinforce failed or ineffective barriers.
2372007001 | Dresden 2 | 01/18/2007 | 03/20/2008 | ML08091006 | <strong>Unit 2 Standby Liquid Control System Tank Inoperable due to A Small Linear Crack</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2007, at 2110 hours (CST), with Unit 2 at approximately 100 percent power, Dresden Nuclear Power Station control room personnel were notified of a through wall linear crack at the Unit 2 Standby Liquid Control System Tank temperature switch well. The Unit 2 Standby Liquid Control System was declared inoperable and Technical Specification 3.1.7, "Standby Liquid Control System," was entered. The repair to the tank could not be completed within the allowed Completion Time of Technical Specification 3.1.7 and Dresden Nuclear Power Station requested a Notice of Enforcement Discretion to allow Unit 2 to remain at power during the repair. The NRC granted the Notice of Enforcement Discretion on January 19, 2007. The system was restored to operable status by encapsulating the cracked component on January 20, 2007 at 0015 hours (CST) within the time allowed by the Notice of Enforcement Discretion. The cause of the event was the result of transgranular stress corrosion cracking that initiated from the threaded inner diameter of the Type 304 stainless steel 1 inch to 3/4 inch Hex-Reducing bushing.
2372007002 | Dresden 2 | 05/04/2007 | 07/03/2007 | ML07278058 | <strong>Unit 2 Reactor Scram due to Loss of Feedwater</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2007, at 2305 hours (CDT), with Unit 2 at approximately 100 percent power, Dresden Nuclear Power Station control room personnel noted decreasing reactor water level and manually scrammed the reactor. All controls rods inserted into the core. The decreasing reactor water level was due to a loss off feedwater transient caused by an unexpected closure of all Unit 2 Condensate Prefilter System valves. Prior to this event, technicians were replacing a failed Condensate Prefilter System Central Processing Unit card. The High Pressure Coolant Injection System was utilized to restore reactor water level. During the event, the Main Steam Isolation Valves closed, the Reactor Recirculation Pumps were tripped and the Unit 2 and 3 Emergency Diesel Generators automatically started as designed. Unit 2 was restored to the electrical grid at 1638 hours (CDT) on May 8, 2007. The root cause of the unexpected closure of all Unit 2 Condensate Prefilter System valves and the subsequent loss of feedwater transient was a vendor latent software deficiency that caused the valves to close when the new Condensate Prefilter Central Processing Unit card was energized. The corrective actions to prevent reoccurrence are to proceduralize the requirements for performing Condensate Prefilter System troubleshooting, maintenance and system restoration; and to develop a design specification for the Condensate Prefilter System Central Processing Unit software.
2372007003 | Dresden 2 | 07/26/2007 | 09/24/2007 | ML07275066 | <strong>Unit 2 High Pressure Coolant Injection System Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2007, at 1706 hours (CDT), with Unit 2 at approximately 98 percent power, Dresden Nuclear Power Station control room personnel were notified of a very small through-wall leak on a Unit 2 High Pressure Coolant Injection System Inlet Drain Pot line elbow. To repair the leaking location, the associated piping was required to be isolated which resulted in the isolation of the Unit 2 High Pressure Coolant Injection System. The Unit 2 High Pressure Coolant Injection System was declared inoperable and Technical Specification 3.5.1, "ECCS Operating," was entered. The elbow was replaced and the Unit 2 High Pressure Coolant Injection System was declared operable on July 27, 2007, at 1809 hours (CDT). The apparent cause of the through wall leak was liquid impingement erosion of the exterior curve of the 90 degree elbow. Corrective actions include the performance of non-destructive testing inspections of piping components in the Unit 2 and 3 High Pressure Coolant Injection System Inlet Drain Pot drain lines, and evaluation of modifying the material or design of the line to reduce the susceptibility to liquid impingement erosion.
2442007001 | Ginna | 01/27/2007 | 03/23/2007 | ML07131038 | <strong>Loss of Electrical Generation Results in Plant Trip</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2007, at approximately 2040 EST, with the plant in Mode 1, initially at 100% steady state reactor power, an event occurred resulting in an automatic reactor trip. The Control Room operators performed the appropriate actions of procedures E-0 and ES-0.1. Following the reactor trip, all safety systems operated as designed. The reactor was stabilized in Mode 3. The reactor trip was the result of a loss of electrical load transient, which is attributed to a failure in the Main Turbine Electro Hydraulic Control (EHC) system that caused the four high pressure turbine control valves to rapidly close simultaneously. The loss of electrical generation resulted in a heat-up of the reactor coolant system and an actuation of the Reactor Protection System (RPS) on Over-Temperature Differential Temperature. Corrective action to prevent recurrence is outlined in Section V.B.
2442007002 | Ginna | 03/16/2007 | 05/14/2007 | ML07141028 | <strong>Closure of Main Steam Isolation Valve Results in Safety Injection Signal and Plant Trip</strong><br /><i>Abstract:&nbsp;</i>On March 16, 2007, at approximately 2209 EST, with the plant in Mode 1, initially at 100% steady state reactor power, an event occurred resulting in a safety injection signal and an automatic reactor trip. The Control Room operators performed the appropriate actions of procedures E-0 and ES-1.1. Following the reactor trip, all safety systems operated as designed. The reactor was stabilized in Mode 3. The safety injection signal and subsequent reactor trip resulted from the B Main Steam Isolation Valve (MSIV) unexpectedly closing and a low steam line pressure condition occurring when the 'A' Steam Generator attempted to handle the full steam load requirements at the time. The cause of this event was a lack of configuration control associated with the actuator for the 'B' MSIV. Corrective action to prevent recurrence is outlined in Section V.B.
2472007001 | Indian Point 2 | 01/02/2007 | 02/28/2007 | ML07065040 | <strong>Technical Specification Prohibited Condition due to Exceeding the Allowed Completion Time for an Inoperable Residual Heat Removal Pump due to an Electrical Supply Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On January 2, 2007, during quarterly surveillance testing of the 21 Residual Heat Removal pump (RHRP), there was a failure of the pump to start on demand. Investigation into the cause of the condition identified that the pump electrical supply breaker control power fuse had blown due to a breaker malfunction. The supply breaker was a DB-50, 480 volt AC breaker. The apparent cause of the breaker failure to close was a mispositioned inertia latch. The lack of inertia latch reset caused the breaker closing coil to remain energized following breaker closure initiation until the control fuses actuated. The inertia latch is designed to reset following a breaker trip to allow for future breaker closures. The binding inertia latch was not resetting as required resulting in the failure of the breaker to close. A contributing cause was the presence of a residue found on the inertia latch and pivot pin mating surfaces. Corrective actions included breaker cleaning, re-lubrication, testing and return to service. Subsequently, the 21 RHRP breaker was replaced with a refurbished breaker. An examination of the breaker residue material will be performed by the breaker manufacturer and a report provided. Engineering will review the report and any necessary corrective actions will be performed. Although Engineering believes the breaker had freedom of movement, the breaker maintenance and modification procedures were enhanced to assure freedom of movement of the inertia latch. An inspection of the remaining DB-50 breakers except closed breakers was performed. All inspected breakers were found to be in working order. The event had no effect on public health and safety.
2472007002 | Indian Point 2 | 01/03/2007 | 02/28/2007 | ML07065040 | <strong>Technical Specification Prohibited Condition due to Exceeding Containment Air Temperature Limit Allowed Outage Time as a Result of Changes in Instrument Uncertainty</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2006, during a review of operator daily surveillance rounds (DSR), Engineering noted that the DSR had a containment temperature limit of 125 degrees F and a reference to Technical Specification (TS) 3.6.5 for actions when the limit was exceeded. TS 3.6.5, for Containment Air Temperature, requires that the containment average air temperature be between 50 degrees F and less than or equal to 130 degrees F. The Bases for the TS states the limits are analytical limits therefore, an appropriate allowance for instrument uncertainty must be applied to ensure the limits are met. Engineering review of the calculation for Containment Temperature Indication Instrument Loop Uncertainty, showed the uncertainty would result in containment temperature potentially exceeding the TS limit at approximately 122 degrees F and not the DS referenced 125 degrees F limit. A completion of review of past containment temperature documentation on January 3, 2007, indicated that the TS limit was exceeded August 16-17, 2005 by approximately 1.25 degrees F. The direct cause was a failure to update procedure 2-PT-D001 to reflect revised criteria from the uncertainty calculation. The apparent cause was inappropriate closure of a corrective action (CA). The initial CA was closed without performing the task and no tracking activity was issued to ensure the document was updated. CAs included revising 2-PT-D001 for the correct temperature. Condition report (CR) quality issues were addressed in previous CR CAs addressing a similar issue. Previous CAs to the impact review process enhanced the engineering request response and closeout process for identifying and updating effected documents. The event had no effect on public health and safety.
2472007003 | Indian Point 2 | 01/03/2007 | 03/30/2007 | ML07096024 | <strong>Plant in a Condition Prohibited by Technical Specifications due to Operation with Control Room Ventilation System High Flow</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2007 at approximately 1950 hours, with steady state reactor power at 100 percent, Indian Point determined that the Control Room Ventilation System (CRVS) booster fans were exceeding the required flow range of 2000 cfm +/-10 percent. The CRVS was considered inoperable at the time for testing. The CRVS was returned to operability on January 4, 2007. Subsequent evaluation determined that the CRVS had been out of specification with high flow from October 26, 2006, following maintenance work on the 21 Control Room Fan (CRF), until January 4, 2007. The fans operate in series. This was operation outside the Technical Specifications. The apparent cause was the human performance weakness in failing to foresee the effects of the maintenance work and a contributing factor was lack of procedural testing requirements. The time frame of this condition is 71 days. Corrective action was taken to brief appropriate engineers on the effects of RPM change and to place a non-adjustable sheave in the 21 CRF for constant fan speed. Corrective action will be taken to revise procedures to prevent recurrence. There was no significant safety hazard since the CRVS safety function was capable of being performed at all times.
2472007004 | Indian Point 2 | 02/28/2007 | 04/30/2007 | ML07128069 | <strong>Manual Reactor Trip due to Decreasing Steam Generator Levels Caused by Loss of Feedwater Flow as a Result of Feedwater Pump Suction Pressure Transmitter Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2007, control room operators manually initiated a reactor trip (RT) at approximately 0633 hours, after receiving speed control trouble alarms for the 21 and 22 Main Boiler Feedwater Pumps (MBFPs) and observing decreasing MBFP speed and steam generator (SG) levels. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect. The cause of the RT was loss of main feedwater (FW) flow due to the failure of the power supply (PQ-408B) for the MBFP suction pressure transmitter (PT-408B). The power supply failed due to a failure of its filter capacitors as a result of age degradation. The root cause of the power supply failure was insufficient verification of the existing plant programs to address capacitor age degradation due to human error. Significant corrective actions include replacement of power supply PQ-408B and pressure transmitter PT-408B. An instrument power supply Preventive Maintenance (PM) will be implemented in accordance with the ENS PM template, and a capacitor program will be developed and implemented to address age degradation of capacitors. The event had no effect on public health and safety.
2472007005 | Indian Point 2 | 11/08/2007 | 01/07/2008 | ML08016012 | <strong>Technical Specification Prohibited Condition due to Exceeding the Allowed Completion Time for an Inoperable Recirculation Pump Caused by a Potential Strong Pump-Weak Pump Interaction During a Small Break LOCA</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2007, during a Unit 3 NRC Component Design Basis Inspection, a condition was identified where a pump of the Emergency Core Cooling Internal Recirculation (IR) System would be inoperable during operator response actions for certain Small Break Loss of Coolant Accidents (SBLOCAs). An extent of condition review determined this condition was also applicable to Unit 2. The condition is due to a procedure requirement (Emergency Operating Procedures ES-1.3 and ES-1.4) to start a second IR pump resulting in a potential strong pump/weak pump interaction that would result in a less than acceptable flow rate through the weak pump causing it to become inoperable. During past plant operation, this unknown condition resulted in exceeding the allowed outage time of Technical Specification 3.5.2 for an inoperable train. The apparent cause of the condition was inadequate analysis during original plant design due to insufficient engineering rigor which failed to identify the strong pump/weak pump interaction of the recirculation pumps for SBLOCAs. Immediate corrective actions were to declare a train of IR inoperable and revise ES-1.3 and ES-1.4 to eliminate the requirement to start a second IR Pump for a SBLOCA. The UFSAR was revised and a review of other applicable safety related pumps will be performed for potential impact from strong pump/weak pump interactions and necessary actions taken. The event had no effect on public health and safety.
2492007001 | Dresden 3 | 03/02/2007 | 05/01/2007 | ML07128026 | <strong>Unit 3 High Pressure Coolant Injection System Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2007, at 1912 hours (CST), with Unit 3 at approximately 100 percent power, Dresden Nuclear Power Station control room personnel were notified of a very small through wall leak on the Unit 3 High Pressure Coolant Injection System Inlet Drain Pot drain piping. To repair the leaking location, the piping was isolated which resulted in the isolation of the Unit 3 High Pressure Coolant Injection System. The Unit 3 High Pressure Coolant Injection System was declared inoperable and Technical Specification 3. 5.1, "ECCS Operating," was entered. The piping was replaced and the Unit 3 High Pressure Coolant Injection System was declared operable on March 3, 2007, at 0403 hours (CST). The apparent cause of the through wall leak was the existence of carbon steel piping in the Unit 3 High Pressure Coolant Injection System Inlet Drain Pot drain piping that was susceptible to Flow Accelerated Corrosion. This piping was originally scheduled for replacement under the Flow Accelerated Corrosion Program in 1997; however the work documentation associated with this piping replacement failed to adequately identify that not all of the original work scope was completed. As a result, the carbon steel piping was incorrectly removed from the Flow Accelerated Corrosion Inspection Program. Corrective action include the incorporation of all Unit 2 and Unit 3, High Pressure Coolant Injection System carbon steel piping susceptible to Flow Accelerated Corrosion into the Flow Accelerated Corrosion Inspection Program and the scheduling of the replacement of this carbon steel piping in future outages.
2502007002 | Turkey Point 3 | 06/06/2007 | 04/02/2008 | ML08105002 | <strong>Completion of Shutdown Required by Technical Specifications due to Inoperable Rod Position Indication for Two Control Rods in the Same Control Bank</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2007, Turkey Point Unit 3 was operating at 100% power. At 0650, Operators observed that Rod Position Indication (RPI) [IG] for control rod F-4 in Control Bank C [AA] began to oscillate above and below 218 steps. The RPI for rod M-6 in the same Control Bank C had been inoperable since September 1, 2006. At 0745, unable to comply with Technical Specification (TS) 3.1.3.2 Action a., i.e., maximum of one analog rod position indication per bank inoperable, TS 3.0.3 was entered to place the Unit 3 in Hot Standby. At 0746, a plant shutdown was initiated. The cause of the failed RPIs is the incorrect application of the coil stack connector [IG:CON] insert material (neoprene) for the required environment. The root cause for this event is that the Integrated Head Assembly Vendor Quality Assurance Program implementation failed to ensure the proper connectors were used in the fabrication of the RPI pigtail assemblies supplied to FPL during the reactor vessel head replacement in 2004. Additionally, FPL's nuclear material management technical reviewer failed to review design basis documentation and to ensure proper engineering documentation was prepared for the new stock code part. The Unit 3 RPI coil connectors were removed, the RPI pigtail assembly wires were spliced to the RPI intermediate vessel head cables and upon completion of repairs Unit 3 was returned to service. Unit 4 was proactively shutdown to replace the same type of connectors with qualified cable splices, similar to the Unit 3 repairs.
2502007004 | Turkey Point 3 | 09/08/2007 | 02/28/2008 | ML08072067 | <strong>Reactor Coolant System Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>During a Unit 3 Turkey Point Refueling Outage (PT3-23), water was found inside the Resistance Temperature Detector (RTD) enclosures for TE-3-420A/B and TE-3-422B2. The source of leakage into the enclosures is unknown. Evaluations of past moisture intrusion into TE-3-420A/B concluded that leakage was not from the thermowell and was not Reactor Coolant System (RCS) water; however, water samples found in the RTD enclosures this outage showed some constituents of RCS water. This indicated the potential for through-wall pressure boundary leakage from the thermowell or external leakage of RCS water into the RTD enclosure through seals, o-rings or threaded joints. Moisture inside the RTD enclosure resulted in shunts-to-ground and low-megger readings, which can affect instrument response. The TE-3-420A/B RTD is designed to be installed in a normal-response thermowell to detect changes in primary coolant loop temperature for input to the plant's accident monitoring system. The TE-3-422B2 RTD is designed to be installed in a fast-response thermowell for rapid detection of changes in coolant loop temperature for input to the plant's Reactor Protection System (RPS). The RTD thermowells are part of the RCS pressure boundary and pressure boundary leakage is not permitted by Technical Specifications 3.4.6.2.a. RTD housings are designed as leak-tight environmental enclosures to assure RTD functions are met as required by Technical Specifications for the reactor protection or accident monitoring functions. The root cause for TE-3-422B2 leakage was a combination of leakage thru a union assembly and exposure to an external RCS leak. Causal analysis was inconclusive for TE-3-420 A/B.
2542007001 | Quad Cities 1 | 05/16/2007 | 07/16/2007 | ML07219060 | <strong>Two Main Steam Safety Valves and One Main Steam Safety/Relief Valve Outside of Technical Specification Allowed Tolerance due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On May 16, 2007, Quad Cities Station received as-found test results that showed that two of the four tested Main Steam Safety Valves actuated outside of the +/- 1% set pressure band required by Technical Specifications. On May 22, 2007, as found test results were received showing that the Main Steam Safety/Relief Valve set pressure was outside of the +/- 1% band required by Technical Specifications. In all cases, the results were within the +/- 3% ASME Code criteria. Based on the results of testing and valve disassembly and inspection, the cause of the out-of-tolerance condition for the SRV is setpoint drift. No mechanical wear, degradation or foreign material associated with the pilot section of the valve was identified. Based on the results of testing and historical performance, the cause of the out-of-tolerance condition for the MSSVs is also setpoint drift. The safety significance of this event was minimal. Both of the MSSVs and the SRV were found to actuate inside the +/-3% Code tolerance. The accident analyses for the fuel cycle during which these valves were installed assumed 3% tolerance for all installed MSSV and SRV valves. This 3% requirement is likewise utilized for the current fuel cycles on both units. Therefore, the valves were capable of performing the safety function.
2542007002 | Quad Cities 1 | 11/16/2007 | 01/15/2008 | ML08023050 | <strong>Safety Function Not Met due to Out of Tolerance Turbine First Stage Pressure Switches</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2007, during 100% power operation of Unit 1, Instrument Maintenance Department surveillances determined that both Division I main turbine first stage low pressure scram enable switches were found out of tolerance high and therefore would have prevented fulfillment of a reactor scram safety function during power ascension between 38.5% Rated Thermal Power (RTP) and the as-found switch setpoint. All four Unit 1 switches were replaced by a plant modification in May 2007 (refueling outage Q1 R19). The original Barksdale model B1T-M12SS-TC switches were replaced with Ashcroft model B450SXCH-400PSI. The new switches were selected due to their improved deadband properties needed to resolve a relay chatter issue, and were procured under a commercial grade dedication process by an approved vendor. The 1-0504A/B/C/D switches sense the main turbine first stage pressure, and are part of the Reactor Protection System (RPS) logic. The purpose for the switches is to provide an enable of the turbine stop valve closure RPS function and an enable of the turbine control valve fast closure (trip oil pressure-low) RPS function. Both functions are enabled to provide a reactor scram signal when reactor power is greater than or equal to 38.5% RTP. Since both switches in Division I exceeded their allowed tolerances in the high direction, their trip enable function would have been unavailable if the unit was ascending in reactor power through the 38.5% RTP level. However, since power ascension was not in progress and the Unit was at full power (97%) during this event, Technical Specification requirements were not exceeded. There were no plant or public safety consequences as a result of this event.
2542007003 | Quad Cities 1, Quad Cities 2 | 11/20/2007 | 01/18/2008 | ML08025005 | <strong>Safety Function Not Met due to Control Room Emergency Ventilation System Air Filtration Unit Heater Flow Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2007, at 0505 hours during full power operation, Operation's surveillances determined that the Control Room Emergency Ventilation System (CREVS) (also described as Train B Control Room HVAC), Air Filtration Unit (AFU) heaters were not operating as required. The surveillance requirement for Technical Specification (Tech Spec) 3.7.4 is a 10 hour run to be performed once every 31 days with the heaters operating. CREVS was declared inoperable and Tech Spec Limiting Condition for Operation 3.7.4, Action A, was entered which requires the CREVS to be restored to operable status in seven days. This event was reported to NRC on November 20, 2007, per 10CFR50.72(b)(3)(v)(D), (ENS Number 43793), as an event of condition that could have prevented the fulfillment of a safety function, because the CREVS is a single train system required to mitigate the consequences of an accident. Troubleshooting of the AFU heater indicated that flow switch FS 0-5795-350 had an open contact that was preventing the heater from energizing and operating as required. By 1625 hours this flow switch was replaced, retested satisfactorily, CREVS was declared operable, and Tech, Spec 3.74, Action A, was exited. Initial failure analysis indicated a problem with the open switch contact which would not close when it reached its setpoint on several different occasions when tested. The resultant failure is attributed to infant mortality, since this switch had only been installed for one month and its failure occurred during its second installed actuation. This is the first issue the station has had with this make and model flow switch since its initial installation in 1985. There were no plant or public safety consequences as a result of this event.
2552007001 | Palisades | 01/04/2007 | 03/01/2007 | ML07060063 | <strong>Failure to Perform Offsite Power Source Check</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2007, an evaluation of the past operability status of startup transformer 1-2 was concluded for the period between May 16, 2006, and May 22, 2006. The results of the evaluation of past operability for startup transformer 1-2 during this period were that startup transformer 1-2 should have been declared inoperable on three separate occasions based on the recorded output voltage of the transformer. The inoperable periods occurred on May 18, May 19 and May 22; with the duration of each inoperable period not exceeding 16 hours. Startup transformer 1-2 is associated with one of the two credited offsite power sources required by Technical Specification (TS) Limiting Condition For Operation (LCO) 3.8.1, "AC Sources - Operating." Consequently, during the three identified periods of inoperability, TS LCO 3.8.1.A for one offsite circuit inoperable was applicable. However, since the startup transformer's past periods of inoperability were not recognized at the time, the required action of TS LCO 3.8.1.A.1 to perform an offsite source check for the operable offsite circuit was not performed in accordance with the specified completion time of 1 hour and once per 8 hours thereafter. The failure to perform the offsite source check within the specified completion time is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2552007002 | Palisades | 01/19/2007 | 03/19/2007 | ML07087104 | <strong>Inoperable Containment due to Containment Air Cooler Through-Wall Flaw</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2007, with the plant in Mode 1, a small service water leak (approximately 60 drops per minute) was identified in VHX-4 containment air cooler (CAC). The leak was subsequently determined to be from a pin-hole in a single cooling coil tube at the H-bend fitting. The CAC cooling coil is a part of the containment boundary, and is required to be structurally sound to ensure that post accident containment leakage will not exceed allowable leakage (La). Therefore,Technical Specification Limiting Condition For Operation 3.6.1, "Containment," is initially applicable for any through-wall defect noted in a CAC cooling coil. Although the size of the identified pin-hole would not have challenged La, it was not possible to characterize the flaw to verify the operability of the cooling coil for post-accident conditions over the CAC's mission time. This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
2552007003 | Palisades | 02/25/2007 | 04/25/2007 | ML07123012 | <strong>Potential for Reduced Component Cooling Water Cooling Capability</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2007, it was discovered that cables in a cable tray that are primarily associated with Component Cooling Water (CCW) and Service Water system components had sustained damage to their cable jackets from the radiant heat effects of an un-insulated hot pipe that was in close proximity to the cable tray. On February 25, 2007, it was conservatively determined that all of the cables in the cable tray that were potentially affected by the radiant heat damage were inoperable due to loss of qualification life and the potential for cable-to-cable interaction from degradation of the cable insulation. Subsequently, on February 25, 2007, it was recognized that a specific combination of two postulated cable faults could result in a condition in which there would be less than 100% of the required post accident CCW cooling. For this condition, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.7.0 was entered along with the specified action to enter TS LCO 3.0.3. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(v)(B) as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat.
2552007004 | Palisades | 04/25/2006 | 05/03/2007 | ML07136010 | <strong>Shutdown Cooling Train Inoperable</strong><br /><i>Abstract:&nbsp;</i>In the period between April 25, 2006, and April 30, 2006, maintenance was performed on a valve that necessitated the isolation of shutdown cooling heat exchanger (SDCHX) E-60B to facilitate the work. Isolating one SDCHX was considered to have no effect on the requirement to maintain two operable shutdown cooling (SDC) trains, as it was considered acceptable to credit a single SDCHX to both operable SDC trains, provided that sufficient heat removal capacity could be obtained with one SDCHX. Subsequently, on March 5, 2007, it was determined that the practice of simultaneously crediting a single SDCHX to both operable SDC trains was not supported by the plant licensing bases, and that a distinct SDCHX is required for each operable SDC train. Therefore, during the time SDCHX E-60B was isolated in April 2006, one train of SDC was inoperable when two trains were required, and action to immediately restore the inoperable SDC train to operable status in accordance with Technical Specification (TS) 3.9.5 Condition A and TS 3.4.8 Condition A was not taken. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the Technical Specifications.
2552007006 | Palisades | 07/25/2007 | 08/24/2007 | ML07250007 | <strong>Emergency Diesel Generator Inoperable in Excess of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2007, a past operability evaluation was completed which concluded that during the 23 days between October 28, 2005, and November 20, 2005, emergency diesel generator (EDG) 1-2 would have been unable to operate satisfactorily for the EDG's required 30-day mission time, and therefore, was inoperable. This period corresponds to the time during which defective snubber valves on cylinders 5R and 5L were installed in EDG 1-2. While a failure of one snubber valve would not make EDG 1-2 inoperable, EDG 1-2 would not be able to meet design loading requirements with two failed snubber valves. Consequently, EDG 1-2 was inoperable for a period of time longer than the 7 days allowed by Palisades Technical Specification (TS) 3.8.1.B.4. Additionally, during the period EDG 1-2 was inoperable, EDG 1-1 was made inoperable for approximately 8 hours for the performance of its monthly surveillance. Therefore, both EDGs were simultaneously inoperable for a period of time longer than the 2 hours allowed by TS 3.8.1.E.1. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2552007007 | Palisades | 10/01/2007 | 11/27/2007 | ML07332036 | <strong>Fuel Handling Area Ventilation System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2007, with reactor refueling activities in progress, a door was discovered to be open in the boundary of the fuel handling area ventilation system. The open door constituted a bypass of the boundary, causing the fuel handling area ventilation system to be inoperable. The door is estimated to have been open for approximately 10 minutes. Upon discovery, movement of fuel assemblies was suspended in accordance with Technical Specification (TS) 3.7.12.A, until the door was closed. However, since the fuel handling area ventilation system was inoperable for approximately 10 minutes prior to discovery, the TS Required Action and associated Completion Time to immediately suspend movement of fuel assemblies was not met. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2552007008 | Palisades | 10/11/2007 | 12/06/2007 | ML07344020 | <strong>Auxiliary Feedwater Pump Inoperable in Excess of Technical Specification Requirements due to a Postulated Steam Line Break</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2006, it was determined that the effects of a postulated steam line break occurring in the turbine building had not been rigorously evaluated for the potential effects on safety related components within the area; specifically, auxiliary feedwater (AFW) pumps P-8A and P-8B, and their associated support components. Subsequently, a bounding engineering analysis was performed, which considered a circumferential break of a 36-inch main steam line in the turbine building. The engineering analysis determined that the resultant ambient conditions in the turbine building constituted a harsh environment under the electrical environmental qualification program, due to the combination of steam, temperature and pressure. A subsequent evaluation of operability on October 11, 2007, determined that P-8B would have been inoperable following a steam line break in the turbine building from the harsh environment created from building pressurization. Therefore, over the previous three years, P-8B and its corresponding AFW train were inoperable for periods of time longer than allowed by Technical Specifications. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications, and 10 CFR 50.73(a)(2)(v)(B) as a condition that could have prevented the fulfillment of the safety function of a system that is needed to remove residual heat.
2552007009 | Palisades | 12/18/2007 | 02/14/2008 | ML08050029 | <strong>Automatic Valve in Emergency Core Cooling System Inoperable in Excess of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>CV-3047 is a normally closed boundary valve associated with the emergency core cooling system (ECCS). In the event of a postulated loss of coolant accident, CV-3047 is required to close (or remain closed) on receipt of a safety injection signal to ensure that all available safety injection flow is directed to the primary coolant system (PCS). On November 26, 2007, CV-3047 had exceeded its stroke time to close during testing. Pending further troubleshooting, administrative controls were established with the intent to maintain CV-3047 closed. Subsequently, on December 18, 2007, investigation determined that CV-3047, although indicating closed, was not fully closed. Technical Specification (TS) Surveillance Requirements (SR) 3.5.2.2 and 3.5.2.5 require that each ECCS automatic valve in the flow path be verified to be in the correct position, and to actuate to the correct position, respectively. Since CV-3047 was not fully closed, it was incapable of meeting SRs 3.5.2.2 and 3.5.2.5. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2552007010 | Palisades | 12/27/2007 | 02/21/2008 | ML08059059 | <strong>Technical Specification Action Requirements Not Met for Battery Cell Parameter Outside Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On December 27, 2007, during the performance of Technical Specification (TS) surveillance testing of the main station batteries, the float voltage of battery cell 43 on the right train station battery was found to be below the allowable TS limit for this parameter. However, at the time of this discovery, it was not recognized that the parameter was actually below the specified TS battery cell limit. Subsequently, on December 28, 2007, during review of the surveillance data and discussion with members of the electrical maintenance department who had performed the surveillance, an on-duty senior reactor operator recognized the low reading for battery cell 43. The delay of over 24 hours in recognizing that battery cell 43 float voltage was below the TS limit for this parameter resulted in not meeting the TS completion time for required actions in accordance with TS 3.8.6.A and TS 3.8.6.B, that were applicable from the initial discovery time. The failure of the electrical maintenance crew to initially recognize that the battery cell 43 voltage was below the TS limit was attributed to an inadequate pre-job brief. Pre-job brief performance expectations will be re-iterated to maintenance personnel. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
2592007001 | Browns Ferry 1 | 05/21/2007 | 07/20/2007 | ML07204017 | <strong>Average Power Range Monitors Inoperable in Excess of Technical Specification Allowable Outage Time in Mode 2</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2007, during restart activities for Unit 1, it was identified that the Average Power Range Monitors (APRM) channels were indicating reactor power level lower than expected for the plant condition. Investigation identified that the gain factors for the individual Local Power Range Monitor (LPRM) channels that provide input signals to the APRM channels were set lower than expected. The lower gain factor settings for all of the LPRM channels reduced the signals to the APRMs to the point where the APRM gain factor adjustments could not compensate for the reduced LPRM channel signals. With the APRM channels indicating a power level lower than the actual reactor power, Technical Specification 3.3.1.1, "RPS Instrumentation," Table 3.3.1.1-1 Function 2.a (APRM Neutron Flux - High, Setdown) would not be operable as required in Mode 2. This condition existed when Mode 2 was entered initially on May 21, 2007. The root cause of this condition was inadequate verification of post-modification testing and work order closure. The original planners for the LPRM replacement work order excluded the normal procedure steps to set the LPRM gains because they presumed later stages of testing would perform this action. The original planners associated with the LPRM replacement are no longer employed at BFN. Current Instrument & Controls planners and craftsmen have been briefed on this event.
2592007002 | Browns Ferry 1 | 05/24/2007 | 02/27/2009 | ML09063042 | <strong>Manual Scram due to an Unisolable EHC Leak</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2007, at 0211 CDT, Unit 1 operators initiated a manual scram due to an Electro-Hydraulic Control (EHC) [TG] leak that could not be isolated. The reactor was in the startup mode and the generator was not tied to the grid. TVA's causal analysis indicates the inadequate application of the work control process during Unit 1 recovery activities. Weakness in the work control process used during Unit 1 restart activities allowed work to be performed on the EHC System using a generic work order while the system was pressurized. A common practice during recovery of Unit 1 restart effort was to use generic work orders to provide the broadest scope of work and maximum flexibility for the craft personnel. The current work control process has checks and balances to ensure that work is properly evaluated, planned and documented, commensurate with the sensitivity of the equipment and the risk of the activity. The damaged tubing was removed and the connection repaired. TVA is reporting this event in accordance with 10 CFR 50.73(a)(2)(iv)(A). This scram event is reportable within 4 hours under 10 CFR 50.72(b)(2)(iv)(B), any event or condition that results in a valid actuation of the Reactor Protection System, and within 8 hours under 10 CFR 50.72(b)(3)(iv)(A), any event that results in an actuation of the specified systems. This event also required a 60-day written report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
2592007003 | Browns Ferry 1 | 06/04/2007 | 08/03/2007 | ML07218015 | <strong>Main Steam Line High Flow Instrument Inoperable in Excess of Technical Specification Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2007, during the performance of the channel check required by Technical Specifications (TS) 3.3.6.1, it was discovered that main steam line (MSL) 1D flow instrument 1-PDIS-001-0050D was indicating zero while the other three flow instruments on MSL 1D ranged from 8 to 13 psid. Based on this indication, 1-PDIS-001-0050D was declared inoperable at 2300 hours CDT on June 4, 2007. It was determined that the instrument isolation valves for 1-PDIS-001-0050D were closed. Investigation of this event could not determine when the instrument isolation valves were closed. Therefore, it is postulated that 1-PDIS-0001-0050D was inoperable when Unit 1 was restarted in late May 2007. Since this condition was not identified until June 4, 2007, the completion times for the required TS Actions were not met. The root cause of the closed instrumentation isolation valves for 1-PDIS-001-0050D could not be determined. Actions were taken to verify that all Analog Trip Unit (ATU) channels were indicating as expected for current plant conditions. The Integrated Computer System was also reviewed for abnormalities. Additional Instrument Inspection Checklists have been re-performed and no additional mispositioned valves were identified.
2592007004 | Browns Ferry 1 | 06/03/2007 | 08/02/2007 | ML07214073 | <strong>Main Turbine Control Valve Fast Closure Turbine Scram Function Inoperable for a Period Longer than Allowed by the Plant's TSs</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2007, TVA determined that BFN Unit 1 operated in a condition prohibited by the Technical Specifications (TSs). Previously, Unit 1 commenced start-up from an extended outage in late May of 2007. On June 2, 2007, at approximately 1727 hours central daylight time, BFN Unit 1 attained 30 percent rated thermal power (RTP). On June 2 and 3, 2007, TVA performed scram time testing activities. Subsequent to the testing activities, TVA noted that during the test, the scram initiation signal was being bypassed when RTP was between 32 and 34 percent RTP. As such, the scram initiation signal for the turbine control valve (TCV) and the turbine stop valve closure (TSV) is also bypassed. TS 3.3.1.1 require that the bypass occur when reactor power is < 30 percent RTP. TS 3.3.1.1 Action E requires, within 4 hours, reduce reactor power to < 30 percent RTP. This condition existed from June 2, 2007, when 30 percent RTP was attained until the scram time testing was completed June 3, 2007. The design calculation that determines first stage turbine pressure at 30 percent power was incorrect. BFN established an operator action that requires the operator to either trip the first stage pressure switches, which will enable the scram function, or requires that the RTP be less than 30 percent power. TVA revised the turbine first stage pressure calculation to reflect the Unit 1 high pressure turbine first stage pressure at 30 percent RTP with the feedwater heaters out of service. At the first opportunity TVA will implement the change.
2592007005 | Browns Ferry 1 | 06/09/2007 | 08/08/2007 | ML07222043 | <strong>Automatic Reactor Scram due to Turbine Trip as a Result of Invalid High Level in Moisture Separator Drain Tank</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2007, at approximately 1100 hours central daylight time (CDT) Unit 1 automatically scrammed following a turbine trip from a 1A2 main steam moisture separator tank high level signal. Prior to the scram, at 1019 hours CDT, the Moisture Separator Reservoir High Level Dump Valve was noted opening. At approximately 1040 hours CDT operations received a low level alarm for the 1A2 moisture separator. Subsequently, at approximately 1100 hours CDT a turbine trip signal was initiated from an indicated main steam moisture separator high tank level. This was followed by an automatic reactor scram. The root cause of the event is the sizing of the Moisture Separator 1A2 Level Control Dump Valve. TVA is reviewing the design for the Moisture Separator Dump Valve and controls to determine if modifications are required. If necessary will either modify or replace the Unit 1 valves and controls.
2592007006 | Browns Ferry 1 | 08/07/2007 | 10/09/2007 | ML07283026 | <strong>Inoperable Reactor Core Isolation Cooling Primary Containment Isolation Instrumentation for a Period Longer Than Allowed by the Plants Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2007, at approximately 1100 hours central daylight time (CDT), TVA determined that BFN Unit 1 was operating in a condition prohibited by the plants Technical Specifications (TS) when the Reactor Core Isolation Cooling (RCIC) Steam Hi Flow Primary Containment Isolation Instrument was found inoperable. The sense lines for the RCIC Steam Line high Flow Instrument (1-PDT-071-001 B) were installed reversed. The high pressure sense line was connected to the low pressure port on the transmitter and the low pressure sense was line connected to the high pressure port on the transmitter. TVA postulates that poor verification techniques were used in the installation of 1-PDT-071-001B sense lines by both the Craftsmen and Quality Control (QC) Inspectors. Those involved in the installation failed to verify proper sense line alignment to the instrument panel. Unit 1 commenced start-up activities in late May 2007, following an extended outage. There is firm evidence this condition existed prior to the startup and was not identified until August 7, 2007; therefore, the completion time for the LCO action was not met and TVA exceeded the LCO action time limit. TVA is submitting this report according to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications.
2592007007 | Browns Ferry 1 | 08/11/2007 | 02/18/2009 | ML09054023 | <strong>Automatic Reactor Scram from a Neutron Monitoring Trip Signal</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2007, at 1751 hours central daylight time (CDT) Unit 1 automatically scrammed from a Neutron Monitoring Average Power Range Monitor (APRM) signal. Just prior to the scram, a Reactor Recirculation system flow sensing line separated from the Recirculation Pump 1B Flow Transmitter (1-FT-068-081B). This resulted in a false indicated recirculation system low flow with a high reactor core thermal power (100 percent) to the Neutron Monitoring system. Based on these conditions, the neutron monitoring system initiated an APRM Simulated Thermal Power Flow Biased Reactor Scram. TVA's causal analysis concluded the root cause of this event was a lack of rigorous worker practices in the use of place keeping and flagging to keep up with the work steps during the Unit 1 recovery activities. This resulted in inadequate assembly of the compression fitting. TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(iv)(A); as an event that resulted in a manual or automatic actuation of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B) (i.e., reactor protection system including reactor scram or trip, and general containment isolation signals affecting containment isolation valves in more than one system).
2592007008 | Browns Ferry 1 | 09/03/2007 | 11/02/2007 | ML07309009 | <strong>Manual Reactor Scram due to an Electro Hydraulic Control System Leak</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2007, at approximately 1955 hours CDT, Unit 1 Operations was notified that there was a small EHC leak in the Unit 1 Moisture Separator (MS) room in the Turbine Building. Unit 1 was operating at 100 percent power. Video monitoring was established by 0657 hours CDT. Operations noted the leak rate was approximately 120 drops per minute. On September 3, 2007, at 0214 hours CDT Operations noted that the leak rate was increasing and manually scrammed the reactor from approximately 72 percent power. This report is submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in a manual or automatic actuation of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B) (i.e., reactor protection system including reactor scram or trip, and general containment isolation signals affecting containment isolation valves in more than one system).
2592007009 | Browns Ferry 1 | 10/12/2007 | 12/11/2007 | ML07345084 | <strong>Invalid High Level In Moisture Separator Results in Turbine Trip and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2007, at 0803 hours central daylight time (CDT), Unit 1 automatically scrammed following a turbine trip from a 1A1 main steam system moisture separator false high level signal. At approximately 0739 hours CDT, prior to the automatic turbine trip, the Unit 1 operator received an alarm indicating a low level in the 1A1 moisture separator drain tank. At 0803 hours CDT, Unit 1 received a moisture separator 1A1 high level turbine trip signal followed immediately by a reactor scram. TVA submits this report in accordance with 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in a manual or automatic actuation of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B) (i.e., reactor protection system including reactor scram or trip, and general containment isolation signals affecting containment isolation valves in more than one system).
2602007001 | Browns Ferry 2 | 01/11/2007 | 03/02/2007 | ML07064028 | <strong>Automatic Turbine Trip and Reactor Scram due to Equipment Failure During Performance of the Main Generator Rheostat Test</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2007, at 0818 hours Central Standard Time the Unit 2 reactor automatically scrammed on a turbine generator load reject signal during the performance of Operating Instruction 2-OI-47, Main Generator Voltage Control Rheostat Test. Just prior to the reactor scram, with the main generator voltage regulator in the automatic mode, the operations personnel were in the process of performing a rheostat cleaning operation on the generator field voltage manual adjust rheostat (70P) by cycling the rheostat to its upper limit and back to zero. Following this step, per the OI the voltage regulator was placed in the manual mode. After a short time delay, Unit 2 received a turbine trip and subsequent automatic reactor scram. The turbine trip and reactor scram resulted from the failure of a relay in the main generator voltage regulator. During the performance of 2-OI-47, a contact on the regulator mode transfer relay (43A relay) in the auto/manual portion of the main generator voltage regulator control circuit failed. TVA replaced the 43A relay in the main generator voltage regulator circuit.
2602007002 | Browns Ferry 2 | 05/16/2007 | 07/16/2007 | ML07198014 | <strong>Main Steam Relief Valve As Found Setpoint Exceeded Technical Specifications Lift Pressure</strong><br /><i>Abstract:&nbsp;</i>Surveillance testing of main steam relief valves (MSRVs) removed from Unit 2 following Cycle 14 operation revealed that four valves mechanically actuated at pressures greater than 3% above their Technical Specifications (TS) setpoint, thus; deemed inoperable. The Unit 2 TSs requires that 12 MSRVs be operable in reactor Mode 1 (power operation), Mode 2 (startup), and Mode 3 (hot shutdown). If less than 12 MSRVs are operable, the unit is to be placed into Mode 3 within 12 hours and Mode 4 (cold shutdown) within 36 hours. Since each BFN unit has 13 installed MSRVs, any concurrent MSRV inoperability would require the above actions to occur. The condition is deemed to have developed and existed while the valves were in service. The root cause of this condition was MSRV pilot valve disc-seat corrosion bonding which develops during normal reactor operations. The affected valves were refurbished and their lift-setpoints re-established prior to their reinstallation in the plant. There was no actual safety consequences associated with this condition.
2612007001 | Robinson 2 | 05/15/2007 | 07/11/2007 | ML07194025 | <strong>Reactor Trip due to a Loose Wire in the Main Transformer Monitoring Circuitry</strong><br /><i>Abstract:&nbsp;</i>At 1116 hours EDT on May 15, 2007, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at approximately 84% power, a generator lockout signal tripped the main turbine-generator [TG:TA,TB], which resulted in a reactor trip. The generator lockout signal was caused by an electrical fault in the circuitry for the "C" phase main transformer [XFMR:EL] alarm panel. The root cause of this event was the failure to crimp and inspect the tightness of the lug connecting the current transformer (CT) to the transformer alarm panel, which allowed the wire to disconnect and cause an AC electrical voltage from the "C" main transformer neutral bushing CT to be superimposed on the Train "A" DC system. The Train "A" motor-driven auxiliary feedwater (MDAFW) pump [P:BA] failed to start automatically, but it was started manually within about one minute after the reactor trip by an operator. The cause of the Train "A" MDAFW pump failure was subsequently determined to be a failure of the control switch [HS:BA], which prevented the automatic start signal. The equipment was repaired and the unit was placed back on-line at about 1211 hours on May 17, 2007. Planned corrective actions include procedure changes to verify proper connections in the main transformer equipment during work on that equipment and replacement of the Train "B" MDAFW pump control switch during the next refueling outage. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
2632007001 | Monticello | 01/10/2007 | 03/12/2007 | ML07079024 | <strong>Reactor Scram due to Turbine Control Valve Housing Support Failure</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2007, the turbine control valves [JJ] ramped from approximately 50 percent open to 100 percent open in two seconds without a demand from the pressure control system. A Group 1 isolation and automatic scram ensued. Review of plant conditions immediately after the scram disclosed that the main turbine [TRB] control valves [SCV] did not close following the scram. During a post scram plant walk down it was identified that the supports for the turbine control valve enclosure [SPT] had failed, allowing the enclosure to transition downward approximately six inches. The root cause of this event was determined to be latent shortcomings in the design and construction of the turbine control valve enclosure support system during initial construction. Corrective actions include modifying and strengthening the enclosure support system, performing inspections of associated piping and systems, and performing an extent of condition review.
2632007002 | Monticello | 03/17/2007 | 09/27/2007 | ML07271046 | <strong>Supplement 1 of LER 2007-02, Unexpected De-energizing of Bus 16 During Refuel Outage 23</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2007 at 2346, with the unit in MODE 5 (Refueling) and on Division I of shutdown cooling [BO], an unexpected loss of Bus [BU] 16 (the Division II safety related 4KV [EA] bus) occurred. The loss occurred while implementing a clearance order isolation in support of a modification to control room metering [MTR] for Bus 16. One step of the isolation withdrew the potential drawer for the bus. When this occurred, the protective relaying [27] sensed a bus under voltage, causing the aligned power supply to automatically isolate from the bus. The cause of the event was that the Plant Impact Assessment Process failed to properly identify the impact of opening BUS #16 Potential Transformer (POT) [FD] drawer during the development and sequencing of the isolation. Corrective actions currently in progress are: Develop training for licensed and non-licensed operators, revise the Operations Manuals to include system description information and precautions and limitations on Bus POT drawers and switchgear protective schemes, and identify other vulnerable electrical components that are infrequently operated. This supplemental LER identified a second root cause: The process for development, review and execution of critical outage activities was not aligned for strong ownership of the scope of work.
2632007003 | Monticello | 04/20/2007 | 08/30/2007 | ML07253029 | <strong>Failure to Enter a Required Technical Specification Action During Control Rod Drive Exercising</strong><br /><i>Abstract:&nbsp;</i>Note: This LER is being revised to annotate that the interlock failure was a safety system functional failure and to clarify the safety significance of the event. On April 20, 2007 while the plant was in Mode 4 for refueling outage 23, control rod exercising was being performed. While exercising control rod 26-31, the operators realized they did not get the same numerical light indication for the control rod they had previously tested (rod 26-35). The incorrect light indication meant that the one rod out interlock for control rod 26-35 was inoperable. The one rod out interlock for control rod 26-35 should have been declared inoperable and appropriate Technical Specification Action 3.9.2.A should have been entered prior to commencing testing on the control rod 26-31. Exercising control rod 26-31 without the appropriate actions taken for 26-35 was a violation of Monticello Technical Specifications. The cause of the event was incorrect acceptance criteria in the procedure being used. Contributing to the event was the lack of operator proficiency and operator misdiagnosis of the issue. Corrective actions taken for the event were to replace the control rod position indication probe, revise the procedure, and additional training was requested for the operators.
2632007004 | Monticello | 07/02/2007 | 08/30/2007 | ML07253030 | <strong>Degradation of Emergency Service Water Flow to Emergency Core Cooling System Room Cooler</strong><br /><i>Abstract:&nbsp;</i>During performance of the 13 FSW Quarterly Pump and Valve tests on July 2, 2007 a low flow condition was identified to the A RHR Room. This required the RHR and Core Spray pumps in the A RHR room to be declared inoperable due to inadequate room cooling. With multiple components of Low Pressure Emergency Core Cooling System declared inoperable, Technical Specification (TS) LCO 3.0.3 was entered requiring a plant shutdown. Operations flushed the system, restoring adequate flow and exited the TS 3.0.3 LCO prior to reduction of reactor power. There were two causes of the event: (1) throttling of the FSW ECCS Room Cooler outlet valve during the most recent refueling outage led to plugging of the line which resulted in reduced flow and (2) inadequate acceptance criteria and testing methodology for the FSW system resulted in the failure of site personnel to recognize the FSW system was operating at low margin. The corrective actions for this event are: the normal position of the throttled valve was changed to fully opened, the surveillance was re-performed satisfactorily, and initiation of a project to improve system margin.
2632007005 | Monticello | 07/12/2007 | 12/22/2010 | ML10357003 | <strong>Discovery of Appendix R - Non-compliant Manual Actions Review During of NFPA 805</strong><br /><i>Abstract:&nbsp;</i>During performance of NFPA-805, Transition Project Task SUP-1 'Manual Action Compliance,' it was, determined that manual operator actions credited in IX/12-A Lower 4KV Room and XII/14-A Upper 4KV Room to achieve and maintain Appendix R hot safe shutdown are non-compliant. The manual actions provide supplemental ventilation to the 4KV rooms in order to assure continued operability of vital switchgear. These manual actions are specified in an Appendix R Section III.G.1/G.2 fire area; however, they do not meet the criteria for allowable manual actions specified in RIS 2006-10, 'Regulatory Expectations with Appendix R paragraph III.G.2 Operator Manual Actions.' The cause of the event was prior to the issuance of RIS 2006-10, MNGP considered the manual actions to provide supplemental ventilation to the 4KV rooms acceptable. The RIS defined actions that the industry had considered acceptable, as non-compliant with Appendix R requirements and as a result MNGP's manual actions to provide supplemental ventilation to the 4KV rooms are not acceptable. The corrective action for this event is to evaluate the non-compliant manual actions as acceptable due to detailed fire modeling and/or risk assessment or to correct the non-compliant manual actions.
2632007006 | Monticello | 07/26/2007 | 09/20/2007 | ML07267030 | <strong>HELB Door Found in Closed Position due to Fusible Link Failure</strong><br /><i>Abstract:&nbsp;</i>At 0902 on July 26, 2007, an out plant operator identified that Door-18, which is a normally opened fire door, had closed due to a failed fusible link. With this door closed, the pathway for a potential flood due to a high energy line break (HELB) is blocked and therefore closed a relied upon drain path for the water. This represented an unanalyzed condition where both divisions of essential switchgear were declared inoperable and Technical Specification (TS) LCO 3.0.3 was entered. At 0955 on July 26, 2007, the door was restored to an operable HELB condition. Both divisions of the switchgear were declared operable and TS LCO 3.0.3 was exited. No safety system actuations occurred due to this event. The cause of the event was a failure of the fusible link which allowed the door to close. The corrective action for this event was to replace the fusible link with a link that meets the temperature and load ratings and procure a permanent fusible link.
2652007001 | Quad Cities 2 | 02/28/2007 | 04/27/2007 | ML07128029 | <strong>Manual Reactor Scram on Increasing Condenser Backpressure due to a Decrease in 2A Offgas Train Efficiency</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2007 at 2300 hours, control room operators commenced a power reduction on Unit 2 to 725 MWe to effect repairs on the 2C Reactor Feed Pump (RFP) due to a seal leak. At approximately 2352 hours, a pressure controller malfunction in the auxiliary steam supply to the 2A offgas train caused a reduction in its noncondensible gas removal efficiency. This malfunction impacted the 2A Offgas Preheater, Unit 2 steam dilution, and the 2A steam jet air ejector (SJAE) operation, and caused increased condenser back pressure. On February 28, 2007, at 0120 hours, Quad Cities Station Unit 2 Reactor was manually scrammed due to increasing condenser back pressure. This event was caused by a blockage of the pressure sensing line to pressure controller (PC) 2-3041-3A with fine sized corrosion products. The increase in demand of PC 2-3041-3A caused relief valve (RV) 2-3099-129 to open, which ultimately caused a reduction in 2A SJAE efficiency and an increase in condenser back pressure. The safety significance of this event was minimal. While this event required action to diagnose and initiate a manual scram, the reactor, turbine, condenser, and supporting systems performed as expected and within Technical Specifications and UFSAR limits. All safety systems remained fully functional during this event.
2662007001 | Point Beach 1 | 02/06/2007 | 04/05/2007 | ML07096003 | <strong>CREFS Inoperability, Both Control Room Charcoal Filter Fans Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2007, TS-9, Control Room Heating and Ventilation System Monthly Checks, was conducted on the Control Room Emergency Filtration System (CREFS) to satisfy Technical Specification (TS) 3.7.9 surveillance requirements. W-14B, Control Room Charcoal Filter Fan, was declared inoperable at 1957 CST when the fan supply breaker tripped on thermal overload. Technical Specification Action Condition (TSAC) 3.7.9.A.1, with a completion time of 7 days, was entered. During follow-up extent of condition and troubleshooting activities on the W-14A fan on February 6, it was determined that the W-14A fan would not have operated under degraded grid voltage conditions with minimum design outside air temperature. The W-14A fan was declared inoperable at 1415 hours. With both fans inoperable, an 8-hour non-emergency Event Notification (EN 43149) was made in accordance with 10 CFR 50.72(b)(3)(v)D). The overload heater element size was increased for the W-14A and W-14B fans based on design basis requirements. Follow-up testing demonstrated the system to be operable and CREFS was returned to service. A root cause evaluation (RCE) determined that some process procedures in the areas of design-control, maintenance and margin-management need improvement. Process and procedure corrective actions will be tracked via the site's corrective action program. Plant-specific probabilistic risk analysis modeling and the defined system safety function determined the event to be of very low safety significance.
2662007002 | Point Beach 1, Point Beach 2 | 05/09/2007 | 07/05/2007 | ML07190023 | <strong>Non-Compliant Manual Actions Performed in Response to Appendix R Fires</strong><br /><i>Abstract:&nbsp;</i>From May 9 through May 17, 2007, Point Beach Nuclear Plant (PBNP) identified non-compliant, procedurally specified manual operator actions used to achieve and maintain hot safe shutdown. These manual actions don't meet the expectations set forth in Regulatory Issue Summary (RIS) 2006-10, "Regulatory Expectations with Appendix R Paragraph III.G.2 Operator Manual Actions." The discovery was as a result of the National Fire Protection Association Standard 805 (NFPA 805) transition project review of manual actions associated with PBNPs Appendix R Safe Shutdown assessment. The review concluded that some of the manual actions performed in response to fires postulated for Appendix R Paragraph III.G.2 fire areas do not meet the criteria for allowable manual actions as specified in RIS 2006-10. These findings were documented in PBNP's corrective action process, compensatory measures were initiated and long-term resolution of the issue will be addressed as part of the NFPA 805 transition project.
2662007003 | Point Beach 1, Point Beach 2 | 04/07/2007 | 06/06/2007 | ML07157053 | <strong>ESFAS Instrumentation, Lead/Lag Time Constraints for Steam Line Pressure Outside Technical Specification Values</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2007, procedure 1 ICP 04.001 E, Reactor Protection and Safeguards Analog Racks Steam Pressure Refueling Calibration was completed to satisfy Technical Specification (TS) 3.3.2 Table 3.3.2-1 Function 1e, surveillance requirement (SR) 3.3.2.8. Five of the six steam pressure compensator modules were found to have lag time constants greater than 2.0 seconds (TS requirement =/<2). The sixth module was found to have a lead time constant less than 12.0 seconds (TS requirement >/=12). An engineering review of waveform graphs used during the calibration procedures identified a non-ideal curve and subsequent determination that a resistor was not appropriately bypassed resulting in the lead function not at zero during graph generation. On May 21, 2007, the calibration of Unit 2 steam pressure compensator modules was checked using procedure 2 ICP 04.001E. All six steam pressure compensator modules were found to have lag time constants greater than 2.0 seconds; two had lead time constants less than 12.0 seconds. The corrective actions, a new methodology for curve generation combined with increased electronic noise filtering, is applicable to both Unit 1 and Unit 2, and has been in place since each unit’s last refueling outage. A review of historical data shows the condition may have existed since initial plant operation. The safety analysis results demonstrated the minimal deviation from TS limits is of very low safety significance.
2662007004 | Point Beach 1 | 06/05/2007 | 08/02/2007 | ML07215009 | <strong>Manual Reactor Trip due to Loss of Feedwater Regulating Valve Control</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2007, Unit 1 was operating in Mode 1 at 100% power. At 1512 hours water level in B steam generator was observed to be cycling between 70% and 78%. Abnormal Operating Procedure (AOP) 2B, Feedwater System Malfunction, was entered. An immediate in-plant inspection of main feedwater regulating valve 1 CS-476 B identified the positioner feedback arm was disconnected, with the connecting bolt nut located on the insulation covering the valve. Due to the inability to control steam generator level, operators initiated a manual reactor trip at 1517 hours and entered Emergency Operating Procedure (EOP) 0. An unexpected electrical lockout of 345 kV switchyard Bus Section 2 occurred. One moisture separator reheater drain valve failed to automatically shut and was manually shut. One turbine bearing oil lift pump failed to automatically start and was manually started. Reactor trip response was not negatively impacted by the unexpected conditions. After the reactor trip steam generator water levels were controlled using the feedwater regulating valve bypass valves. The plant was stabilized in Mode 3. A root cause evaluation is in progress and initial indications are that less than adequate maintenance procedure guidance caused the loss of the positioner arm nut. Vendor guidance had not been included in maintenance procedures. Changes to the maintenance procedure will be tracked via the site's corrective action program. A safety function review has determined there was no safety impact from this event because the position controllers have no safety function.
2662007005 | Point Beach 1 | 06/15/2007 | 08/14/2007 | ML07227025 | <strong>Manual Reactor Shutdown Required by Technical Specification; LCO 3.7.5 Auxiliary Feedwater Not Met</strong><br /><i>Abstract:&nbsp;</i>An orderly shutdown of Unit 1 commenced at 1819 hours on June 14, 2007, when it was recognized that repair and testing of 1P-29, turbine-driven auxiliary feedwater (TDAFW) pump, would not be successfully completed within the 72 hours allowed by Technical Specification Action Condition (TSAC) 3.7.5.B.1. The pump had initially been declared inoperable on June 12, 2007, at 0131 hours when the outboard turbine bearing experienced elevated temperatures during a performance of inservice test procedure IT-08A. Unit 1 entered MODE 3 on June 15, 2007, at 0407 hours and MODE 4 at 1712 hours with both conditions being achieved within the completion time limits of Technical Specification (TS) 3.7.5. The IT-08A test being performed on June 12 was a follow-up test in response to a bearing temperature increasing trend observed on June 9, 2007, during performance of scheduled surveillance testing using IT-08A. The pump was not restored to an operable condition within the Limiting Condition for Operation (LCO) allowed time period due to: 1) procedure inadequacies associated with the 10-year overhaul of the pump, and 2) failure to perform adequate post-maintenance testing (PMT) following the 10-year overhaul. Changes to the maintenance procedure for equipment overhaul, and changes to the process and procedures for specifying PMT, are being tracked via the plant's Corrective Action Program (CAP). The nuclear safety significance of the TS-required shutdown was low because all Required Actions to satisfy the TS were completed within the stated Completion Times.
2662007006 | Point Beach 1, Point Beach 2 | 07/12/2007 | 09/10/2007 | ML07253051 | <strong>Fire Inspection Analysis of Pressurizer Power-Operated Relief Valves and Block Valves</strong><br /><i>Abstract:&nbsp;</i>During a review of abnormal operating procedure (AOP)-10A, Safe Shutdown-Local Control, it was identified that fire damage to the pressurizer power-operated relief valve (PORV) and block valve circuits as a result of a fire in the cable spreading room could also result in simultaneous damage to a block valve circuit and spurious actuation of a PORV. While the actions included in abnormal operating procedure (AOP-10A), provide reasonable assurance that positive control of reactor coolant system (RCS) inventory is maintained, these steps do not ensure that simultaneous failure of the block valve circuit and spurious operation of a PORV will not result in RCS pressurization. Therefore, a postulated fire may potentially remove the ability to fully implement the Safe Shutdown Strategy. This condition was reported via an 8-hour non-emergency report, EN 43487, on July 12, 2007, pursuant to 10 CFR 50.72(b)(3)(ii)(B), as an unanalyzed condition that had the potential to significantly degrade plant safety. Compensatory measures in the form of twice-per-shift fire rounds in the cable spreading room have been implemented.
2662007008 | Point Beach 1, Point Beach 2 | 10/19/2007 | 12/17/2007 | ML07352004 | <strong>Non-conservative Low Temperature Overpressure Protection System Basis</strong><br /><i>Abstract:&nbsp;</i>On October 25, 2007, at 1930 CDT Point Beach Nuclear Plant (PBNP) Unit 1 and Unit 2 low temperature overpressure protection (LTOP) systems were declared inoperable as a result of the determination that the current LTOP actuation setpoint was non-conservative based on new calculation information. Changes were made to operating procedures to delineate operation of reactor coolant pumps and charging pumps during low temperature conditions. These changes provided the guidance required to ensure that the current LTOP setpoints remain conservative. Operability of LTOP was restored for both Unit 1 and Unit 2 on October 26, 2007, at 1751 CDT upon issuance of the revised procedures. This issue was discovered as part of the ongoing corrective actions associated with pressure and temperature limit report (PTLR) issues at the plant. This condition was reported via an 8-hour non-emergency report, EN 43750, on October 26, 2007, pursuant to 10 CFR 50.72(b)(3)(v)(D), as a condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The basis for the report was subsequently re-reviewed and it was determined that it should have been reported, pursuant to 10 CFR 50.72(b)(3)(ii)(A), as a condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.
2692007001 | Oconee 1, Oconee 2 | 02/15/2007 | 07/02/2007 | ML07193015 | <strong>Dual Unit Trip from Jocassee Breaker Failure</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2007 at 1654 hours, a breaker failure occurred in the Jocassee Hydro Station switchyard, causing one phase to fault to ground. The phase-to-ground fault was isolated at the Oconee 230 KV switchyard, but the resulting prolonged (less than 1 second) grid disturbance led to a trip of Oconee Units 1 and 2. A wiring design error on the loss-of-excitation relays caused a generator lock-out, turbine trip, and bus transfer from normal to startup sources on Oconee Units 1 and 2. Both reactors were subsequently tripped by the reactor coolant pump power monitors, which correctly sensed the voltage transient and resultant power sag. Incorrect settings on the auxiliary switch fast contacts of the normal main feeder bus breakers caused a slow bus transfer of 4160 volt loads on Oconee Unit 1, leading to a loss of normal feedwater flow. This necessitated cooldown to Mode 4, which was accomplished by procedure with emergency feedwater and atmospheric dump valves. Unit 2 secondary systems performed as expected. Appropriate post-trip reviews were performed and recovery actions completed per station procedures. Unit 2 was returned to power operation on February 18, 2007 and Unit 1 returned to service on February 23, 2007. This event is considered to have no significance with respect to the health and safety of the public.
2692007002 | Oconee 1 | 09/24/2007 | 11/20/2007 | ML07330055 | <strong>Cask Shipments Include Startup Neutron Sources Not Listed in CofC</strong><br /><i>Abstract:&nbsp;</i>On 9/24/2007, personnel at McGuire Nuclear Station (MNS) performed an inspection of two fuel assemblies stored in the MNS spent fuel pool and confirmed obstructions in one guide tube on each assembly. This provided confirmatory information that these assemblies contained neutron sources used at Oconee Nuclear Station (ONS) during initial startup in the early 1970's. The fuel assemblies had been shipped to MNS in 1987 due to storage limitations at ONS. Upon review, it was recognized that the Certificate of Compliance (CofC) for the TN-8L shipping cask used in 1987 did not list such sources as components acceptable for inclusion with the fuel assembly during shipment. This event is being reported per 10 CFR 71.95(b) as "instances in which the conditions in the certificate of compliance were not followed during a shipment." This event is considered to have no significance with respect to the health and safety of the public.
2712007001 | Vermont Yankee | 04/24/2007 | 06/18/2007 | ML07173004 | <strong>High Pressure Coolant Injection System Isolation Time Delay Relay Surveillance Test Failures due to Inadequate an Calibration Methodology</strong><br /><i>Abstract:&nbsp;</i>On 04/06/2007,with the reactor at full power, technicians were performing a surveillance on the High Pressure Coolant Injection (HPCI) system isolation logic. During performance of the surveillance, the as-found time delay for the "A" channel isolation logic relay, 23A-K49, actuated at 36.5 minutes. The required set-point is 30.0 minutes +/- 2.5 minutes (27.5 to 32.5 minutes) with an allowable as-found tolerance of+/- 4.0 minutes (26.0 to 34.0 minutes). The as-found value for this relay was greater than the allowable per the Technical Specification requirement of </= to 35 minutes.Three of the last four surveillances,performed once per operating cycle, also had as-found settings that were found to have exceeded the Technical Specification requirement. Due to the multiple test failures, this condition is being reported pursuant to 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. During the period the "B" channel HPCI isolation logic relay (23A-K48) successfully passed all calibration tests, there by maintaining the design function of the system to isolate the HPCI system in accordance with the Technica lSpecification requirement. The root cause of this condition was that the surveillance procedure was inadequate as it did not account for relevant manufacturer information that applies when setting the relay with an extended time delay.
2712007002 | Vermont Yankee | 06/08/2007 | 10/25/2007 | ML07305031 | <strong>High Pressure Coolant Injection (HPCI) System Valve Failed to Open</strong><br /><i>Abstract:&nbsp;</i>On 06/08/07 with the reactor power at 81 percent, the High Pressure Coolant Injection (HPCI) Pump Injection Isolation Valve V23-19 did not open on a manual signal from the Control Room during HPCI System surveillance testing. V23-19 is a Motor Operated Valve (MOV) powered by 125 VDC. The valve is normally closed, and opens automatically on a HPCI initiation Signal. The valve can also be operated manually using a control switch in the Control Room. The MOV power supply circuit breaker contains two sets of contactors that control valve direction. One contactor is for the open direction, and one is for the close direction. Each contactor has two sets of electrical contacts connected in series. Troubleshooting by Electrical Maintenance determined that one of the two close contacts was in the intermediate position causing electrical and mechanical interlocks to prevent the open contactor from energizing. The interlocks are part of the system design to prevent the motor from being energized in both open and close directions at the same time. The Root Cause Team identified that the Preventative Maintenance required to be performed on the V23-19 valve's motor operator control circuitry was not fully effective for the application.
2712007003 | Vermont Yankee | 08/30/2007 | 10/25/2007 | ML07305031 | <strong>Reactor Trip Caused by Turbine Stop Valve Closure due to Inadequate Preventative Maintenance</strong><br /><i>Abstract:&nbsp;</i>On 08/30/07, with the reactor at approximately 62 percent power, a reactor trip occurred due to at least three of the four Turbine Stop Valves (TSV) going greater than 10% closed. This condition actuated the Reactor Protection System (RPS) logic which shutdown the reactor as designed. The reactor trip was attributed to the lack of preventative maintenance on the number 2 TSV Bell Crank Mechanism. Binding in the Bell Crank Mechanism resulted in the number 2 TSV failing to open after a closure test. When the mechanism was freed, the valve opened rapidly causing a rapid pressure change in the TSV actuator hydraulic oil system that resulted in all four TSVs going closed. The appropriate initial NRC notifications were made per 10CFR50.72 (b)(2)(iv)(B) and 10CFR50.72 (b)(3)(iv)(A). Plant safety system response was as expected and the plant automatically shutdown. No release of radioactivity or personnel injury occurred as a result of this event. No similar events have occurred in the last 5 years. This event is reportable as a Licensee Event Report per 10CFR50.73(a)(2)(iv)(A) as an event that resulted in the automatic actuation of systems identified in 10CFR50.73(a)(2)(iv)(B).
2722007001 | Salem 1 | 03/27/2007 | 05/23/2007 | ML07150021 | <strong>ESF Actuation of Auxiliary Feedwater Pumps in Mode 3.</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2007 at approximately 2050, Salem Unit 1 was in Mode 3 following a planned manual reactor trip to begin a scheduled refueling outage. Operators had established initial Reactor Coolant System cooldown using the steam dumps for heat removal and the 11, 12, and 13 Auxiliary Feedwater (AFW) pumps for steam generator make-up. Steam Generator levels were being maintained lower than normal in preparation for an AFW full flow test. As plant cooldown proceeded, narrow range levels in 11, 12, and 13 Steam Generators reached the low steam generator setpoint trip, resulting in a valid ESF actuation (i.e., start signal to the AFW pumps); however all AFW pumps were already in service. The actuation signal also generated a reactor trip signal; however, the plant was already in a shutdown condition with the reactor trip breakers open. The lowest level during this transient occurred in 13 Steam Generator and was 11.3% narrow range level. Steam generator water level was restored to a normal value and the RCS cooldown recommenced. There were no equipment failures that contributed to this event. The cause of this event is attributed the failure of the operating crew to establish clear termination criteria for stopping the cooldown based on low S/G levels and the lack of clear termination criteria guidance in the procedure for maintaining S/G levels during a cooldown. This event is reportable in accordance with10CFR50.73 (a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section."
2722007002 | Salem 1 | 04/24/2007 | 06/25/2007 | ML07193026 | <strong>Manual Reactor Trips due to Degraded Condenser Heat Removal</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2007 at approximately 2248, a manual reactor trip was initiated with reactor power level at approximately 40%. The manual reactor trip was initiated in response to a degraded Circulating Water System (CWS) and in accordance with operating procedures. The degradation of the CWS was due to extremely heavy river debris loadings that affected the ability of plant equipment to operate under the condition. The unit was returned to service on April 26, 2007 at 1236 following the cleaning of the condenser water boxes and lowering river debris conditions. On April 30, 2007, at approximately 1502, with the unit at approximately 80% power a sudden localized high amount of river water debris again affected the CWS intake resulting in the loss of four (4) circulating water pumps due to high screen differential levels, and a manual reactor trip. The cause of manual reactor trips is attributed to unusual and severe external environmental conditions resulting in record high amounts of river debris loadings, which challenged the design of the CWS. Following cleaning and inspection of the Circulating Water Traveling Screens, condenser water boxes, and lowering river debris conditions the unit was returned to service on May 3, 2007 at 0310. A root cause investigation has been initiated to improve the plant operation and to minimize challenges to the CWS design by: (a) Improving predictive tools and actions on high river debris conditions, and (b)Improving the availability and reliability of the Circulating Water System. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...."
2722007003 | Salem 1 | 12/28/2007 | 02/25/2008 | ML08066018 | <strong>Salem Unit 1 Automatic Reactor Trip due to the Failure of 12 Station Power Transformer Load Tap Changer</strong><br /><i>Abstract:&nbsp;</i>At 1754 on December 28, 2007, Salem Unit 1 experienced an automatic reactor trip due to low Reactor Coolant System loop flow when the 12 Station Power Transformer (SPT) failed. The loss of the 12 SPT resulted in a loss of power to the 1 "F" and 1 "G" Group Busses and associated 13 and 14 Reactor Coolant Pumps causing a subsequent reactor trip on low Reactor Coolant System loop flow. Inadequate scope of maintenance procedures performed on 12 SPT Load Tap Changer (LTC) internal components and insufficient performance monitoring of degrading LTC conditions resulted in the failure of the collector rings and stationary and moving contacts on the LTC. There were no complications associated with the unit trip. The failed components were replaced, the transformer was tested satisfactorily and the unit was returned to service on December 31, 2007. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...."
2752007001 | Diablo Canyon 1, Diablo Canyon 2 | 05/12/2007 | 07/11/2007 | ML07199009 | <strong>Emergency Diesel Generator Auto-start on Loss of Offsite 230kV Startup Power</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2007, at 10:25 PDT, with Unit 1 in no Mode (core offloaded to the spent fuel pool) and Unit 2 in Mode 1 (Power Operation) at approximately 100 percent power, an emergency diesel generator (EDG) system actuation was initiated on loss of 230kV startup power supply due an offsite transmission system nonceramic insulator (NCI) failure and unanticipated protective relay response. Two Unit 1 EDGs started and loaded to provide onsite power. Unit 1 had one EDG and auxiliary offsite power cleared for maintenance. All three Unit 2 EDGs started as required but did not load due to normal power supply being maintained via the auxiliary transformers. At 14:30 PDT, Operations restored 230kV offsite power to the site. Plant operators made a nonemergency event notification (EN 43360) in accordance with 10 CFR 50.72(b)(3)(iv)(A) at 15:09 PDT. This event was due to an offsite transmission system NCI failure resulting in a phase to phase short and unanticipated instantaneous protective relay response. Corrective actions include resetting the startup power protection relays to establish a time delay and replacing NCIs in the 230kV supply to Diablo Canyon Power Plant.
2752007002 | Diablo Canyon 1 | 05/27/2007 | 07/27/2007 | ML07213017 | <strong>Manual Reactor Trip in Mode 3 During Control Rod Testing</strong><br /><i>Abstract:&nbsp;</i>At 11:17 PDT, operators manually actuated the reactor protection system causing all rods to fully insert. While operators were performing post outage surveillance testing, Control Bank C was being inserted. At 42 steps withdrawn, Control Rod N-13 indicated a position change to 24 steps withdrawn. In response to this 18-step deviation, and in accordance with the test procedure, operators manually initiated the reactor trip. The apparent cause of the event was crud accumulation on the drive mechanism for Control Rod N-13. The slippage occurred two additional times during mitigation activities which were part of troubleshooting and vendor recommendations. Ultimately, operations successfully completed five event free full-length traverse cycles to ensure the drive mechanism was clear of crud. Corrective actions include implementing the relevant portions of Westinghouse Technical Bulletin TB-06-17 for prevention and mitigation.
2752007003 | Diablo Canyon 1 | 05/28/2007 | 07/27/2007 | ML07215037 | <strong>Emergency Diesel Generator Actuation due to a Transient Undervoltage Condition</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2007, at 2250 PDT, with Unit 1 at approximately 8 percent power, preparations were being made to parallel the Main Generator to the grid. All 12kV and 4160V electrical busses had been transferred to the Startup-Standby power supply (230kV System). Operations started Circulating Water Pump 1-2, a large 12kV motor. Starting this motor caused a transient voltage dip in the Startup Standby System voltage. The voltage dip duration was sufficient to time-out the under voltage diesel generator start time delay relay on the 4160V Vital Bus G, causing a start of the associated Emergency Diesel Generator (DG) 1-2. The 4160V Vital Bus G continued to be powered by the Startup-Standby power source; loads were not transferred and DG 1-2 remained in operation unloaded. DG 1-2 was verified not to be required and returned to its normal standby condition. On May 29, 2007, at 0501 PDT, an eight-hour nonemergency report was made pursuant to 10 CFR 50.72 (b)(3)(iv)(A) via the Event Notification System (ENS Number 43393). Corrective actions to prevent recurrence include incorporation of precautions in plant operating procedures to minimize the transient voltage effects due to the start of large motors.
2782007001 | Peach Bottom 3 | 10/04/2007 | 11/26/2007 | ML07340042 | <strong>Laboratory Analysis Identifies Safety Relief Valves and Safety Valve Set Point Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Based on information received during the 10/4/07 - 10/6/07 time period from a laboratory performing Safety Relief Valve (SRV) / Safety Valve (SV) as-found testing, Site Engineering personnel determined that SRV / SV set point deficiencies existed with two SRVs and one SV that were in place during the Unit 3 16th operating cycle. The SRVs / SV were determined to have their as-found set points in excess of the Technical Specification allowable +/- 1% tolerance. All three SRVs / SV outside of their Technical Specification allowable range were within the ASME Code allowable of +/- 3%. The cause of the three SRVs / SVs being outside of their allowable as-found set points is due to set point drift. The three SRVs / SV were replaced with refurbished SRVs / SV for the 17th Unit 3 operating cycle. There were no actual safety consequences associated with this event. There were two previous LERs identified.
2822007001 | Prairie Island 1 | 04/03/2007 | 10/26/2007 | ML07299032 | <strong>Unit 1 Train B ECCS Inoperable Longer Than Allowed by Technical Specifications due to Inoperable Breaker</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2007, Prairie Island Nuclear Generating Plant (PINGP) operators discovered the closing springs on the breaker for the 12 safety injection (SI) pump were discharged with the breaker open. NMC believes the charging motor failed the last time the breaker was closed to run the pump, which was March 15, 2007. Thus, the 12 SI pump was inoperable longer than the Completion Time of Technical Specification (TS) 3.5.2, Condition A, allows and this event is being reported in accordance with 10 CFR 50.73.(a)(2)(i)(B) as a condition prohibited by Technical Specifications. The breaker was replaced with a spare and on April 4, 2007, TS 3.5.2, Condition A, was exited after successful testing of the breaker. The cause of the charging motor failure was determined to be the motor brushes having exceeded their useful life. The planned corrective actions to prevent recurrence are to inspect all safeguards switchgear charging motors and to establish a maintenance procedure for charging motor inspection and replacement.
2822007002 | Prairie Island 1, Prairie Island 2 | 06/04/2007 | 08/01/2007 | ML07213050 | <strong>Unanalyzed Condition due to Manual Actions That Do Not Comply with 10 CFR 50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2007, Nuclear Management Company, LLC (NMC) staff working on the transition to National Fire Protection Association (NFPA) standard NFPA-805 discovered non-compliant manual operator actions were credited to achieve safe shutdown in Fire Area 29. Subsequent review for extent of condition identified a number of additional fire areas with non-compliant manual operator actions that were credited for safe shutdown. NRC Regulatory Information Summary (RIS) 2006-10 provided clarification of the regulatory expectations associated with the use of manual operator actions in 10 CFR 50 Appendix R III.G.1 and III.G.2 fire areas. The non-compliant manual operator actions are considered equivalent to a missing fire barrier, thus, this event is being reported in accordance with 10 CFR 50.73.(a)(2)(ii) as an unanalyzed condition. Compensatory measures have been taken in all affected fire areas and this issue is slated to be resolved as part of implementation of NFPA-805.
2822007003 | Prairie Island 1, Prairie Island 2 | 08/09/2007 | 01/25/2008 | ML07296041 | <strong>Unanalyzed Condition Due to Breached Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On August 9, 2007, Nuclear Management Company, LLC (NMC) staff documented an apparent breach between the Train A and Train B auxiliary feedwater pump rooms. The floor trench in the rooms is separated by a 12-inch thick concrete barrier. One of the penetrations in the barrier was a 4-inch pipe sleeve through which a 3-inch rubber hose has been run for several years. An evaluation of the as-found configuration determined on August 24, 2007, that the as-found configuration could have adversely affected the ability to safely shutdown in the event of a fire and NMC notified the NRC per 10 CFR 50.72(b)(3)(ii) as an unanalyzed condition. Thus, this event is being reported in accordance with 10 CFR 50.73(a)(2)(ii) as an unanalyzed condition. The hose was removed and the fire barrier was restored (filled with fire-retardant wool and capped with threaded caps). A root cause evaluation concluded there were two root causes for the condition: (1) requirements for use of the auxiliary feedwater pump (AFWP) room trench and trench fire barrier pipe sleeve are not procedurally controlled, and (2) insufficient procedural direction, guidance, or criteria for evaluators to help them determine an appropriate threshold for issuing a new action request as a consequence of their evaluation findings.
2822007004 | Prairie Island 1 | 12/21/2007 | 01/19/2009 | ML09021023 | <strong>Technical Specification Required Shutdown due to Both Emergency Diesel Generators Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2007, with the Unit 1 Train B emergency diesel generator (D2) out of service for planned maintenance, Nuclear Management Company, LLC (NMC) staff were conducting a required surveillance test on the Unit 1 Train A 4kV Bus (Bus 15) load sequencer. The load sequencer failed the surveillance and the Unit 1 Train A emergency diesel generator (D1) was declared inoperable as a result. With both D1 and D2 inoperable, Technical Specifications requires the affected Unit to be shutdown. Shutdown to Mode 3 was completed at approximately 0700 on December 21, 2007. Thus, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) as a Technical Specification required shutdown. Unit 1 resumed Mode 1 power operation at approximately 1600 on December 24, 2007, after the Bus 15 load sequencer (and D1) and D2 were returned to service. A root cause evaluation has been completed. The equipment cause is age related degradation of load sequencer input/output cards. The organizational root cause is lack of a comprehensive preventive maintenance strategy for the load sequencers and their subcomponents.
2822007005 | Prairie Island 1, Prairie Island 2 | 12/12/2007 | 04/18/2008 | ML08109045 | <strong>One Tram of SCWS Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2007, Nuclear Management Company, LLC (NMC) staff identified leakage under the insulation on the 121 (Train A shared between Units 1 and 2) Control Room Chiller. The leakage was attributed to a flange leak and a work order was initiated. On December 11, 2007, NMC staff determined that the leakage was not due to a flange leak, but due to a through wall leak on the associated flexible spool piece. On December 12, 2007, NMC staff determined the 121 Control Room Chiller was inoperable as a result of the leaking flexible spool piece. Thus, the 121 Control Room Chiller and Train A Safeguards Chilled Water System (SCWS) was inoperable for more than 60 days. Technical Specification (TS) 3.7.11 (SCWS) Condition A requires that an inoperable SCWS loop be returned to operable status within 30 days. TS 3.7.11 Condition B requires that if Condition A is not met, both units must be in Mode 3 in 6 hours and Mode 5 in 36 hours. Since neither unit was shutdown pursuant to TS 3.7.11 Condition B, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. The leaking flexible spool piece was replaced and the Train A SCWS was returned to operable status on December 15, 2007. A root cause evaluation determined the cause of the leak to be corrosion that progressed from the outside surface. The corrosion was caused by condensation.
2852007001 | Fort Calhoun | 02/01/2007 | 03/29/2007 | ML07102016 | <strong>Inoperability of a Post Accident Main Steam Line Radiation Monitor Due to Procedural Error</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2007, a station employee, who was cleaning, identified that all four manual steam isolation valves for RM-064 were closed. RM-064 is the post-accident main steam line radiation monitor. Investigation determined that RM-064 had most probably been isolated since November 29, 2006. This condition is in violation of the Fort Calhoun Station technical specifications. The root cause of this event was that a procedure was written assuming its performance prior to completing the main steam system valve lineup. The procedural guidance closed the isolation valves which is contrary to the previously completed main steam system valve lineup. The isolation valves were opened and the appropriate procedures will be corrected.
2852007002 | Fort Calhoun | 02/08/2007 | 04/09/2007 | ML07107029 | <strong>Common Mode Failure of Medium Voltage (4160) Circuit Breaker</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2007, the 4160 volt circuit breaker for raw water (RW) pump AC-10B closed on demand, but the auxiliary contacts did not actuate. The failure was determined to be a broken mechanical linkage rod. The rod was replaced. The failure was determined to be due to cyclic fatigue. A visual inspection of the other three RW pump circuit breakers, performed at that time, did not reveal any similar damage. AC-10B was returned to service. On February 8, 2007, a similar event occurred where the circuit breaker for RW pump AC-10C closed on demand, but its auxiliary contact switch did not actuate. Again, the failure was determined to be the same mechanical linkage rod. The root cause of this failure was that the processes involving the identification of critical interface/operating configurations when specifying material procurement requirements failed to identify the usage of a test flag as a critical constraint. The mechanical linkages of RW pumps AC-10C, A and D were rebuilt with rods having less than 1000 cycles of operation (the limit established for linkage operability). All other affected circuit breakers having more that 1000 cycles of operation have been rebuilt with rods having fewer than 1000 cycles of operation. A replacement strategy for the mechanical linkages is being developed. Implementation of this strategy will be controlled by the corrective action system.
2852007003 | Fort Calhoun | 02/16/2007 | 05/21/2008 | ML08142071 | <strong>Inoperability of a Diesel Generator with an Inoperable Containment Cooling Fan from the Opposite Bus</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2007, during the monthly surveillance testing of diesel generator (DG) 1, field flashing of the diesel did not occur. The diesel was shutdown and declared inoperable. Investigation determined that DG-1 had been inoperable since February 14, 2007. This is due to the field flash auxiliary contacts which were observed to be stuck open when they should have been closed. The containment cooling fan powered from DG-2 was declared inoperable for approximately 2.5 hours on February 15, 2007 to perform surveillance testing. Since DG-1 was inoperable during the time the containment cooling fan was inoperable, there was only the one small containment cooler operable for approximately 2.5 hours. The root cause analysis determined that this event was caused by a post-maintenance testing (PMT) process that did not follow industry standards. This process was over-reliant on the knowledge base in work management and engineering. Corrective actions included replacing the field flash auxiliary contacts. Procedural guidance for PMT has been enhanced to improve the quality of PMT to ensure additional problems are not created by the work activities.
2852007004 | Fort Calhoun | 04/12/2007 | 06/11/2007 | ML07170008 | <strong>Inadvertent Isolation of All Containment Spray Due to an Inadequate Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2007, during preparations for performing periodic testing of the safety injection, containment spray and recirculation actuation signals the operating crew identified a condition that would render the containment spray system inoperable during the performance of the surveillance test. The problem had existed since 1990 for one train of containment spray and since 2006 for the other train. The root cause for this event was an error in evaluating the operability of components during performance of surveillance tests for the 1990 modification of the containment spray actuation system. Although proper techniques were used to identify the components that would be operable during testing, an incorrect assumption for operability was used. The affected procedures were revised to eliminate the problem. Additional actions will be implemented in the corrective action system.
2852007005 | Fort Calhoun | 09/12/2007 | 12/17/2007 | ML07358007 | <strong>Inadequate Operability Determination Results in Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On September 12, 2007, it was discovered that the testing frequency for raw water (RW) pump AC-10D should have been increased in response to the results of testing on July 11, 2007. The date for complying with the increased frequency had passed when the condition was discovered. Technical Specification (TS) 3.0.4 requires equipment to be declared inoperable when a surveillance requirement has not been met, except as provided in TS 3.0.5. This TS provides alternatives to immediately declaring inoperability, but has a 24-hour time limit during which actions are required. Contrary to TS 3.0.5, a risk assessment was not performed nor was the surveillance test performed as required. The actions required by TS 3.0.5 were not taken. The root cause analysis determined that the operability determination process was not effectively implemented. Corrective actions included completing the surveillance test on September 14, 2007. RW pump AC-10D was determined to have been able to perform its required safety function. The procedures documenting the RW pump curves have been updated as appropriate. The RW pump quarterly tests have been revised to require the system engineer to verify that the correct pump curve is used before the test is performed. In addition, operations and engineering training will be conducted to address the root cause.
2862007001 | Indian Point 3 | 04/03/2007 | 06/04/2007 | ML07162012 | <strong>Manual Reactor Trip Due to Decreasing Steam Generator Levels as a Result of the Loss of Feedwater Flow Caused by the Failure of 32 Main Feedwater Pump Train A Control Logic</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2007, with the 31 Main Boiler Feedwater Pump (MBFP) shutdown, the 31 MBFPcontrol circuit was de-energized in preparation for maintenance, when unexpectedly the logic control circuit for the 32 MBFP was lost resulting in loss of feedwater (FW)flow. Control room operators manually initiated a reactor trip (RT) at approximately 0417 hours, after observing rapidly decreasing steam generator (SG) levels. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat initially being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect.The cause of the RT was decreasing SG levels due to loss of 32 MBFP FW control as a result of the failure of the 32 MBFP Train A Lovejoy control logic power supply when the 31 MBFP instrument bus power supply was isolated. The 32 MBFP Train A control logic power supply failure was due to a bad pin connection on the power supply voltage regulator. The root cause was a failure of an auctioneered power supply that was not self revealing and was undetectable until it was required to carry load. Significant corrective actions include replacement of 32 MBFP Train A control logic power supply, establishment of a the 10 year Preventive Maintenance (PM) to replace all power supplies in the Lovejoy system, performance of an assessment for identification of other auctioneered power supplies and verification that PMs confirm that the power supplies can carry their load. The event had no effect on public health and safety.
2862007002 | Indian Point 3 | 04/06/2007 | 06/05/2007 | ML07162012 | <strong>Automatic Reactor Trip Due to a Turbine-Generator Trip Caused by a Fault on the 31 Main Transformer Phase B High Voltage Bushing</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2007, at 1109 hours, an automatic reactor trip (RT) occurred due to a turbine-generator trip as a result of a fault on the 31 main transformer. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. The Emergency Diesel Generators did not start as adequate offsite power remained available. Two of three 138 kV offsite power substation feeder stripped as a result of the event. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect. Control Room (CR) operators were notified of a fire at the 31 main transformer with the fire protection deluge system actuated. The plant fire brigade responded to the fire and applied foam.The fire brigade leader reported to the CR the fire was extinguished at 1121 hours.The CR was notified at approximately 1140 hours that a visible explosion had previously occurred. Based on the report of an explosion, the CR declared a Notice of Unusual Event (NUE) in accordance with the emergency plan which was terminated at 1254 hours.The direct cause of the RT was due to the actuation of the 86P and 86BU relays that sensed a fault from the failure of 31 main transformer 345 kV phase B bushing. The most probable cause was a design weakness associated with the type bushing used in the Phase B bushing. Significant corrective actions included replacement of 31 main transformer, and inspection, repair and replacement of damaged components as required associated with the 32 main transformer, the unit auxiliary transformer, and high voltage components. The event had no effect on public health and safety.
2862007003 | Indian Point 3 | 11/08/2007 | 01/07/2008 | ML08016012 | <strong>Technical Specification Prohibited Condition due to Exceeding the Allowed Completion Time for an Inoperable Recirculation Pump Caused by a Potential Strong Pump-Weak Pump Interaction During a Small Break LOCA</strong><br /><i>Abstract:&nbsp;</i>On November 8, 2007, during an NRC Component Design Basis Inspection, a condition was identified where a pump of the Emergency Core Cooling Internal Recirculation (IR) System could be inoperable during operator response actions for certain Small Break Loss of Coolant Accidents (SBLOCAs). The condition is due to a procedure requirement (Emergency Operating Procedures ES-1.3 and ES-1.4) to start a second IR pump resulting in a potential strong pump/weak pump interaction that could result in a less than acceptable flow rate through the weak pump causing it to become inoperable. During past plant operation, this unknown condition resulted in exceeding the allowed outage time of Technical Specification 3.5.2 for an inoperable ECCS train. The apparent cause of the condition was inadequate analysis during original plant design due to insufficient engineering rigor which failed to identify the strong pump/weak pump interaction of the recirculation pumps for SBLOCAs. This condition was also determined to be applicable to unit 2. Immediate corrective actions were to declare a train of IR inoperable and revise ES-1.3 and ES-1.4 to eliminate the requirement to start a second IR Pump for a SBLOCA. The UFSAR will be revised and a review of other applicable safety related pumps will be performed for potential impact from strong pump/weak pump interactions and necessary actions taken. The event had no effect on public health and safety.
2932007001 | Pilgrim | 03/17/2007 | 05/16/2007 | ML07142009 | <strong>Primary Containment Isolations following a Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2007, at approximately 1655 hours, a manual scram was initiated while at 30 percent reactor power during an orderly shutdown of the unit. The orderly shutdown was a management decision based on observing an increasing trend in reactor coolant system (RCS) unidentified leak rate. The manual scram was performed because the increase in RCS unidentified leak rate reached administrative limits during the shutdown. There were no complications encountered during the response to the scram. Following the scram, the collapse of steam voids caused a shrink in the reactor water level and resulted in automatic actuation of the Primary Containment Isolation Control System (PCIS) and Reactor Building Isolation Control System (RBIS). No actuations of emergency core cooling systems, reactor safety/relief valves, or standby diesel generators were required. The root cause of the increase in unidentified leakage was the failure of the valve packing for Reactor Water Clean-up (RWCU) valve MO-1201-85, which is located inside primary containment in the drywell and is not accessible during power operation. The failure was due to inadequate preventive maintenance of the valve packing. Corrective action taken included replacement of the valve packing. Corrective action planned includes developing a packing adjustment procedure and scheduling preventive maintenance for packing adjustments to critical valves in the drywell and other inaccessible areas using guidelines published by EPRI. The event posed no threat to public health and safety.
2932007002 | Pilgrim | 02/23/2007 | 07/10/2007 | ML07198040 | <strong>Emergency Diesel Generator Kilowatt (KW) Power Oscillations</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2007 while operating the "B" Emergency Diesel Generator (EDG)", oscillations in Kilowatt (KW) output were observed that reached administrative abort criteria of > 200 KW total span. The "B" EDG was manually shutdown. Previously on January 25, 2007 during an operability test following an overhaul of the "B" EDG, unexpected KW oscillations up to 150 KW were observed but these oscillations did not reach the abort criteria. The root cause of the oscillations was clogging of internal passages in the Woodward hydraulic governor due to the intrusion of foreign material. It was discovered that the oil in the governor was contaminated with particles of aluminum of varying size. The source of the particles was an aluminum label from the shutdown solenoid that separated from the solenoid and was free to move about inside the governor. Corrective action taken includes replacement of the Woodward hydraulic governor and retest of the "B" EDG to demonstrate operability. Pilgrim verified similar conditions did not exist in "A" EDG and Station Blackout Diesel Generator. Maintenance personnel were trained on the lessons learned from these events. An Operating Experience (OE) report was issued to the industry and Entergy fleet concerning potential for the valve label being introduced as foreign material into the hydraulic governor.
2932007003 | Pilgrim | 04/26/2007 | 06/25/2007 | ML07184019 | <strong>Reactor Coolant Pressure Boundary Leakage due to Reactor Vessel Nozzle Weld Crack Propagation</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2007, at approximately 1930 hours, the N2K recirculation system inlet nozzle experienced slight water seepage while repairs were being performed to install a full structural weld overlay.The cause of the leakage is attributed to a planar-type, circumferential flaw in N2K safe-end-to-nozzle weld. The weld was installed in 1984 and included Inconel 182 butter and filler which is a material now known to be susceptible to interdentritic stress corrosion cracking (IDSCC). Subsequent to the weld repair, crack propagation continued via IDSCC due to high residual weld stresses in the weld material. Ultra-sonic testing performed in Refueling Outage 16 (RFO 16) detected planar indication in the Inconel weld material that was indicative of cracking. This prompted the installation of the weld overlay. Corrective action taken included nozzle weld repair consisting of a full structural weld overlay. The event posed no threat to public health and safety.
2932007004 | Pilgrim | 06/13/2007 | 08/13/2007 | ML07233009 | <strong>Target Rock Relief Valves' Test Pressure Exceeded Limit due to Corrosion Bonding and Setpoint Variance</strong><br /><i>Abstract:&nbsp;</i>On June 13 2007, Pilgrim Station was notified that three of the four Target Rock relief valve pilot assemblies exceeded the Technical Specification (TS) tolerance limit of 1115 +/-11 psi (+/-1%) during routine testing at the Wyle Laboratories test facility. Certified replacement relief valve pilot assemblies were previously installed in the plant. The cause of the as-found initial popping pressures exceeding the TS tolerance limit for two of the pilot valves was "setpoint variance". The cause of the as-found initial popping pressure exceeding the TS tolerance limit for the third pilot valve was corrosion bonding. Corrective actions taken include replacing the pilot valves with certified tested replacements. The conditions posed no threat to public health and safety because an evaluation of the effect of the as-found set pressures concluded that no design or licensing basis limits would have been exceeded had the SRVs been required to operate.
2932007005 | Pilgrim | 07/10/2007 | 09/10/2007 | ML07261060 | <strong>Reactor Scram Resulting from Low Vacuum Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2007 at 1954 hours, an automatic scram occurred with the plant operating at approximately 48 percent reactor power. The automatic scram initiated from a valid Reactor Protection System (RPS) signal resulting from fast closure of the turbine steam control valves. The turbine steam control valves closed in response to an unexpected turbine on low vacuum. The low vacuum signal resulted from a calibration error on the low vacuum turbine trip low vacuum trip mechanism (VTS-1). The trip mechanism was calibrated and set incorrectly during the April/May 2007 Refueling Outage. Corrective action taken included calibrating the vacuum pressure trip mechanism. Additional corrective actions planned include training improvements relative to calibrating the turbine vacuum pressure alarm and trip setpoints and procedure enhancements. The automatic scram occurred while the reactor mode selector switch was in the "RUN" position. Reactor vessel pressure was approximately 957 psig. The event occurred during a scheduled thermal backwash of the main condensers. The event posed no threat to public health and safety.
2952007001 | Zion 1, Zion 2 | 02/28/2007 | 03/15/2007 | ML07081051 | <strong>Inadequate Special Nuclear Material (NM) Record Keeping Practices for Exempt Quantities</strong><br /><i>Abstract:&nbsp;</i>In the process of reviewing Special Nuclear Material (SNM) records, it was identified that all disposition records for reactor incore detectors could not be found. The reactor incore detectors contain very small quantities of U-235 and were used to monitor reactor power during plant operation. The unaccounted for material was classified as missing on February 28, 2007 due to lack of records documenting the current location of forty-three detectors that were received onsite between 1972 and 1987. Based on interviews with former Zion Nuclear Material Custodians and other relevant personnel, it is believed that these detectors were shipped as radioactive waste to the Barnwell Low-Level Radioactive Waste Disposal Facility located in South Carolina. Additionally, select historical records indicate that it was common practice for Zion Station to dispose of detectors as radioactive waste. A search of storage locations at Zion was performed, but the detectors were not located. There is no evidence of theft or diversion of these detectors.
2962007001 | Browns Ferry 3 | 02/09/2007 | 04/10/2007 | ML07101044 | <strong>Reactor Scram due to Low Reactor Water Level Caused by Loss of Feedwater</strong><br /><i>Abstract:&nbsp;</i>At 1208 Central Standard Time, on February 9, 2007, Unit 3 received an automatic reactor scram on low water level following the loss of condensate flow. Just prior to the scram, operations attempted to establish manual operation of the condensate and demineralizer system. Personnel were in the process of modifying the control logic for the condensate and demineralized water system backwash controller. With the primary controller in run mode and the secondary controller in the program mode, personnel were loading new software into the secondary controller. The personnel involved were experiencing difficulties loading the software onto the secondary controller, so they attempted to load software onto the primary controller. They placed primary controller, which was previously in the run mode, into the program mode. However, the secondary controller was not returned to the run mode. With neither controller the run mode the condensate and demineralizer water system demineralizers isolated. This resulted in a decrease in reactor water level and an automatic reactor scram. The root cause of this event was the individuals involved in the planning and implementation of the work order did not fully understand manual operation of the system. Additionally, there is inadequate guidance or limitations on the use of in-field decision making. TVA is revising the operating instructions for the condensate demineralizer system. TVA is revising trouble shooting guidance to eliminate trouble shooting under the direction of the system engineer or other individuals except under tightly controlled circumstances.
2962007002 | Browns Ferry 3 | 07/24/2007 | 09/24/2007 | ML07268118 | <strong>Unplanned Inoperability of the Unit 3 High Pressure Coolant Injection System due to Loss to 120 VAC Instrument Power</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2007, at 1645 hours central daylight time (CDT) the Unit 3, Division II Emergency Core Cooling Systems (ECCS) Analog Trip Unit (ATU) Inverter failed due to a cleared fuse during a 250 VDC Reactor Motor Operated Valve (RMOV) board power supply transfer. The inverter provides power to the High Pressure Coolant Injection (HPCI) pump discharge flow controller. TVA declared HPCI inoperable and entered a fourteen day Technical Specification (TS) Limiting Condition for Operation (LCO). Following fuse replacement at 2318 hours, Unit 3 HPCI was declared operable and the fourteen day LCO was exited. The fuse cleared due to an overcurrent condition during the power supply transfer. The transfer was performed with the inverter in service. The probable cause for the fuse clearing was a voltage transient on the ECCS inverter during the 250 VDC RMOV Board power supply transfer that resulted in a higher than normal inrush current across the input fuse. TVA will revise the operating instructions to require the affected ECCS ATU Inverters de-energized prior to a scheduled transfer of the input voltage source. Because HPCI was inoperable during the time frame the inverter was out of service, TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(v)(B) and (D) as; any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: remove residual heat; and to mitigate the consequences of an accident.
2962007003 | Browns Ferry 3 | 09/22/2007 | 11/21/2007 | ML07327007 | <strong>Leak in an ASME Class I Code Reactor Pressure Boundary Pipe</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2007, at approximately 1000 hours Central Daylight Time (CDT), with BFN Unit 3 in Mode 3, an entry into the primary containment (drywell) identified an American Society of Mechanical Engineers (ASME) Class I reactor pressure boundary leak that could not be isolated. During the drywell entry, TVA identified a one inch test line associated with a Residual Heat Removal (RHR) system testable check valve had a through wall leak in a welded connection. At 1245 hours CDT, following confirmation that the leak was part of the ASME Class I pressure boundary, operations placed the reactor in Mode 4 per the Technical Specifications. This report is submitted in accordance with 10 CFR 50.73(a)(2)(ii)(A) as an event or condition that resulted in the nuclear power plant, including principal safety barriers, being seriously degraded.
2962007004 | Browns Ferry 3 | 11/30/2007 | 01/28/2008 | ML08029004 | <strong>Manual Isolation of High Pressure Core Injection due to Steam Leak</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2007, at approximately 1052 hours Central Standard Time (CST), during the process of shutting down for a planned maintenance outage, Operations isolated the Unit 3 High Pressure Coolant Injection (HPCI) steam supply, with the reactor at 950 psig. Operations verified by administrative means that the Reactor Core Isolation Cooling system and two Control Rod Drive system pumps were available as a high pressure injection water source, and entered Technical Specification Limiting Condition for Operation (LCO) 3.5.1.C. A previously identified steam leak on the packing of the HPCI steam line condensate inboard drain valve had increased. This leak was identified prior to entering the maintenance outage and plans were in place to remove HPCI from service and repair the leak. However, because the volume of the leak increased, operations removed HPCI from service earlier than planned. LCO 3.5.1.C was exited at 1435 hours CST when the reactor pressure was less than 150 psig. TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73(a)(2)(v)(D) as "any event or condition that could have prevented the fulfillment of a safety function of structures of systems that are needed to: Remove residual heat or mitigate the consequences of an accident."
2962007005 | Browns Ferry 3 | 12/31/2007 | 03/17/2008 | ML08078023 | <strong>Automatic Reactor Scram due to Main Generator Load Reject</strong><br /><i>Abstract:&nbsp;</i>On December 31, 2007, at 2140 hours Central Standard Time (CST), Unit 3 reactor received an automatic scram signal following a main generator load reject. The reactor scram from the generator load reject was expected. All systems responded to the scram as expected. All control rods inserted. During the initial pressure transient, which peaked at 1141 psig, six of the main steam system relief valves opened. The reactor pressure was subsequently controlled with the main steam system bypass valves. The reactor water level was controlled by the Feedwater system, the normal heat removal path through the main condenser was maintained during the event. The reactor scram was reset December 31, 2007, by 2146 hours CST. TVA is submitting this report according to 10 CFR 50.73(a)(2)(iv)(A), as an event that resulted in a manual or automatic actuation of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B) (i.e., reactor protection system including reactor scram of trip, and general containment isolation signals affecting containment isolation valves in more than one system.)
2982007001 | Cooper Station | 02/07/2007 | 05/23/2007 | ML07150010 | <strong>High Pressure Coolant Injection Inverter Circuit Failure Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>Between 0430 and 0457 Central Standard Time (CST) on February 7, 2007 High Pressure Coolant Injection (HPCI) inverter circuit failure alarms were received intermittently indicating a loss of the inverter output. HPCI was in a standby status at the time of the alarms. The loss of inverter output was confirmed by the HPCI flow controller output lowering to approximately 30% and returning to 100% upon, alarm reset. The power indicating light on the inverter was observed to go off on the last alarm, returning when the alarm was reset. HPCI was declared inoperable at 0430 resulting in entry into Technical Specification Limiting Condition for Operation 3.5.1 Condition C, HPCI System inoperable and 3.5.1Condition D, HPCI System inoperable AND Condition A entered. Condition A was previously entered for Core Spray System Loop A, which was inoperable for planned maintenance. The failure was the result of an intermittent open circuit caused by corrosion which resulted from solder flux residue remaining on copper conductors during the manufacturing process. The inverter was replaced and HPCI was declared operable at 1602 on February 7, 2007. This LER also satisfies the reporting requirements of 10 CFR 21.
2982007002 | Cooper Station | 03/05/2007 | 04/30/2007 | ML07123026 | <strong>Technical Specification Prohibited Operation Due to Safety Relief Valve Test Failure</strong><br /><i>Abstract:&nbsp;</i>The results of Target Rock safety relief valve (SRV) tests performed on February 28 through March 2, 2007 by Wyle Laboratories, identified that one of eight SRV pilot valve assemblies failed to lift within its Technical Specification (TS) lift set point of 1090 +/- 32.7 psig. The SRV lifted at 1127 psig. The discovery was made as a result of routine TS surveillance testing of pilot valve assemblies removed during Refueling Outage 23. Cooper Nuclear Station (CNS) was in Mode 1 at 100 percent power at the time of the determination. The remaining valves tested within their TS lift set point tolerances. The failure was a result of sufficient corrosion bonding between the SRV pilot valve assembly Stellite 21 disc and the pilot valve Stellite 6 body seat to cause the SRV pilot valve to lift outside TS set point tolerances. As documented in CNS Licensee Event Report 2005-002-00, this is a recurring problem at CNS and in the industry. The valves were replaced with tested spare valves certified to lift within 1% of setpoint. This event is considered to have no safety significance and has no impact on the reactor pressure vessel pressure relief function capability.
2982007003 | Cooper Station | 04/23/2007 | 06/13/2007 | ML07170024 | <strong>Incorrectly Installed Fuse Block Resulted in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2007, during a step in the 4160 volt bus 1G under voltage relay and relay timer functional test procedure, an operator placed his finger on the exterior of a fuse block casing, at which time, the fuse block dropped onto the bottom of the breaker cubicle. Because a contact had been temporarily sleeved, no trip actions occurred, annunciators alarmed as expected and the bus remained energized. The fuse block was securely replaced and the condition was corrected prior to surveillance completion. The incorrectly installed fuse block condition had existed for 35 days, traceable to the last surveillance completion. This condition violated technical specification (TS)3.8.1, AC Sources-Operating,Condition A, One Offsite Circuit Inoperable, for 7 days. Consequently,this condition violated CNS TS 3.8.1, AC Sources-Operating, Condition F, Required Action and Associated Completion Time of Condition A, B, C, D, or E, to be in Mode 3 within 12 hour sand Mode 4 within 36 hours.The cause of this event is that no expectation or training existed for verifying tightness following installation. Other corrective actions are to revise procedures and train operators on proper fuse holder installation.
2982007004 | Cooper Station | 05/19/2007 | 07/16/2007 | ML07201001 | <strong>Manual Reactor Trip due to Hydraulic Control Unit Valve Bonnet Leak into Reactor Building</strong><br /><i>Abstract:&nbsp;</i>On 5/19/2007 at 00:25 CDT, Cooper Nuclear Station (CNS) was in Mode 1 at 50%Power in Single Loop Operation when a small water leak developed from a Control Rod Drive Hydraulic Control Unit (HCU) directional control valve (DCV) during maintenance. The leak degraded to the point of a visible steam plume, and prompted a precautionary Reactor Building evacuation. After several unsuccessful attempts to isolate the leak operators made the conservative decision to remove the unit from service. At 02:12 CDT, the operators manually scrammed the reactor. Control rods inserted normally. A Group 2 Primary Containment isolation signal isolated required systems. The scram was uncomplicated with systems functioning as required. No off-site releases occurred due to the HCU valve leak which stopped after the scram. The manual scram and controlled shutdown were not nuclear risk significant. Leakage past a manual isolation valve is the most probable direct cause of the DCV internal pressure. The cause of the leak was that tag-out implementation and acceptance for maintenance did not require verification that HCU was de-pressurized, nor were contingencies in place if it was not. Corrective actions are being tracked in CNSs corrective action program.
2982007005 | Cooper Station | 06/14/2007 | 10/24/2007 | ML07303004 | <strong>Inadequate Post Fire Procedure Could Have Prevented Achieving Safe Shutdown</strong><br /><i>Abstract:&nbsp;</i>On June 14, 2007, during validation of plant procedures associated with achieving safe shutdown during and after an Appendix R fire, Cooper Nuclear Station (CNS) determined there was no readily available success path to secure High Pressure Coolant Injection (HPCI) when required. Based on a conservative analysis and assumptions, the postulated scenario involves a fire-induced spurious HPCI initiation that must be terminated within 10 minutes to prevent flooding main steam lines and disabling both Reactor Core Isolation Cooling and Automatic Depressurization System, each representing available strategies for achieving hot shutdown. As written, the postfire procedure steps would not have been sufficient to isolate steam to the HPCI turbine. CNS took immediate actions to revise procedures to provide adequate and effective validated instructions to isolate HPCI when required after a spurious initiation. This event was reported June 14, 2007 under 10 CFR 50.72(b)(3)(v)(A) by Emergency Notification Number 43421 as a condition that could have prevented the plant from achieving safe shutdown. The condition has been determined to be of low safety significance.
2982007006 | Cooper Station | 09/11/2007 | 11/08/2007 | ML07318025 | <strong>Procedural Guidance Leads to Rendering Second Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 14:49 Central Daylight Time on September 11, 2007, Diesel Generator (DG) 1 was declared inoperable when the DG 1 fuel oil day tank inlet high level float shutoff valve and solenoid shutoff valve leaked by causing the potential for DG 1 day tank to overfill. DG 2 was already inoperable and unavailable due to scheduled maintenance. Acceptance criteria of a surveillance procedure (SP) were applied to DG 1 that required DG 1 to be declared inoperable. At 15:09, the DG 1 maintenance lockout switch was positioned to OFF for replacement of the solenoid shutoff valve which rendered DG 1 inoperable and unavailable. Two DGs inoperable and unavailable constitutes a loss of safety function for on-site emergency power. This event was caused by the SP containing a requirement to declare DG 1 inoperable following the failure to meet acceptance criteria when other options for maintaining operability of the system were available. Immediate actions consisted of separating DG fuel oil transfer subsystems by closing the fuel oil day tank inlet cross-tie valve and revising the SP to provide alternative actions that maintain operability following day tank solenoid shutoff valve failure. This condition was not risk significant.
2982007007 | Cooper Station | 12/03/2007 | 01/25/2008 | ML08029065 | <strong>Damaged Lead on Emergency Filter System Fan Motor Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On December 3, 2007, the Control Room Emergency Filter (CREF) System was inoperable for preventive maintenance when motor leads for the control room exhaust booster fan, a required support feature for the CREF System, were found degraded. At 20:51 Central Standard Time, although the control room exhaust booster fan had been operating prior to being secured for preventive maintenance, it was determined the CREF System may not perform its safety function due to the degraded condition of the fan motor leads. Immediate action was taken to replace the control room exhaust booster fan motor. The CREF System was returned to operable status at 17:48 on December 4, 2007. The condition was caused by inadequate preventive maintenance to ensure reliability of the control room exhaust booster fan motor. A corrective action to prevent recurrence is being tracked to implement a routine preventive maintenance plan for the control room exhaust booster fan. This event was not risk significant.
3012007007 | Point Beach 2 | 08/22/2007 | 10/19/2007 | ML07295023 | <strong>One Overpower Delta T Channel Setpoint outside Technical Specification Allowed Value</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2007, at 0830 hours Instrument & Control (IC) technicians began performance of procedure 2 ICP-2.001WH, Reactor Protection & Engineered Safety Features White Channel Analog 92 Day Surveillance Test. Several steps in the procedure had been temporarily changed to accommodate the replacement of module 2TM-402V with a refurbished module, in accordance with work order 333737. The affected channel, which provides an input to the Overpower delta T Reactor Protection System (RPS), was removed from service at 0843 hours, and returned to service at 1002 hours. The technicians continued with other channel calibrations as directed by procedure. The shift manager acknowledged completion of all calibrations and restoration of instruments at 1211 hours. lC personnel, upon reviewing the test data that had been recorded, identified as-left voltage settings for 2TM-402V that were outside Technical Specification (TS) limits. At 1417 hours the Shift Manager was notified of the inoperable channel. TS LCO 3.3.1 Required Action D.1 was subsequently met when the channel was placed in trip at 1451 hours. Recalibration activities commenced at 1549 hours and were completed satisfactorily with channel operability restored at 1632 hours on August 22, 2007. The cause of the event was personnel error as technicians failed to identify that as-left readings did not meet specified acceptance criteria. A safety function review has determined the safety significance to be low.
3022007001 | Crystal River 3 | 01/11/2007 | 03/09/2007 | ML07079013 | <strong>Design Oversight Results In 10 CFR 50, Appendix R, Cable Separation Criteria Not Being Met</strong><br /><i>Abstract:&nbsp;</i>At 19:01, on January 11, and at 13:16, on January 23, 2007, Progress Energy Florida, Inc., Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER when conditions not meeting 10CFR50, Appendix R, Section III.G.2 cable separation criteria were identified for high/low pressure interface valves. During performance of the CR-3 Safe Shutdown Analysis Revalidation Project Fire Area Assessment for the Intermediate and Reactor Buildings, respectively, reviews revealed that the power cable for Decay Heat Removal (DH) System valve DHV-3 and the power and control cables for DHV-4 were routed with other energized cables. Low probability three-phase external cable hot shorts of the proper voltage due to a hypothetical fire could cause spurious opening of both valves, resulting in an unanalyzed loss of coolant condition in the Auxiliary Building. The cause for this event was a misunderstanding of 10CFR50, Appendix R cable separation criteria in 1997 and 2002 pertaining to high/low pressure interfaces resulting in missed opportunities to correct the identified conditions. Appropriate compensatory measures have been put into place. This report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(B). This condition does not represent a reduction in the public health and safety. Previous similar occurrences have been reported to the NRC.
3022007002 | Crystal River 3 | 02/21/2007 | 04/19/2007 | ML07113000 | <strong>Reactor Trip Caused by Failed Circuit Board in the Main Feedwater Integrated Control System</strong><br /><i>Abstract:&nbsp;</i>At 19:14, on February 21, 2007, Crystal River Unit 3 (CR-3), operated by Florida Power Corporation (FPC) doing business as Progress Energy Florida, Inc., was in MODE 1 (POWER OPERATION) at approximately 71 percent RATED THERMAL POWER. CR-3 was at reduced power for planned maintenance on one of four main condenser water boxes when the Integrated Control System (ICS) for Main Feedwater (FW) became erratic causing actual FW flow to drop to zero in both FW trains which underfed the Once-Through Steam Generators. The Reactor Protection System (RPS) actuated on high Reactor Coolant System (RCS) Pressure causing a reactor trip. Emergency Feedwater Initiation and Control (EFIC) actuated on low steam generator levels. The cause for this event was inadequate human performance in the implementation of the ICS circuit card refurbishment program which resulted in an age-related failure of the zener diodes in the +15 volt regulator circuit for a Bailey 820 Control Module in the ICS. RPS and Emergency Feedwater System valid actuations are reportable under 10CFR50.73(a)(2)(iv)(A). This condition does not represent a reduction in the public health and safety. LER 50-302/2004-001-00 documents a previous similar event at CR-3.
3052007001 | Kewaunee | 01/12/2007 | 11/20/2007 | ML07332056 | <strong>Reactor Trip During Turbine Trip Mechanism Testing</strong><br /><i>Abstract:&nbsp;</i>At 10:39 on 1/12/2007, with the reactor at 1660MWt (93.7%), while performing a turbine mechanical trip test, the turbine and reactor tripped due to low auto stop oil pressure. MS-201B1, Reheat Steam to MSR B1 failed to close, which resulted in additional RCS cooldown to 536 degrees F. Per contingency procedures, action was taken to isolate the reheat steam, which halted the cooldown, and Tave was restored to 547 degrees F. The additional cooldown resulted in letdown isolation on low pressurizer level. Feedwater isolated and auxiliary feedwater initiated, as designed, due to low-low level in the steam generators. No other safeguards systems actuated during the transient. The direct cause was a loss of auto stop oil pressure to the interface valve that resulted in a turbine-reactor trip. The probable cause of this pressure loss was either the overspeed trip test valve linkage out of adjustment, undetected test valve lever movement on the part of the operator, or a combination of the two. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of the reactor protection system and the auxiliary feedwater system. This event was originally reported in LER 2007-001-00. This supplemental report updates the cause and corrective action.
3052007002 | Kewaunee | 01/03/2007 | 02/19/2007 | ML07060014 | <strong>Issues with AMAG/Westinghouse Calculations for Full Power Result In Reduced Power Operation</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER, being reported per the guidelines of Step 5.1.4 of NUREG-1022. Kewaunee Power Station has determined that a potentially larger uncertainty exists in the feedwater flow measurement system than that assumed during initial system analysis and calibration. The feedwater flow measurement system installed in 2003 improved the accuracy of feedwater flow measurement allowing the power calorimetric uncertainty to be reduced from 2.0% to 0.6%. System data was collected and analyzed to provide a better understanding of the actual system performance and to confirm system measurement uncertainty. Based on this data, the vendor (AMAG/Westinghouse) could not support the originally assumed calorimetric error. If a larger than analyzed system measurement uncertainty is determined to have existed, the Technical Specification rated thermal power level could have been exceeded. However, at the present time there is reasonable assurance that Kewaunee has not exceeded its rated thermal power limit. Item 2.C.1 of the Facility Operating License (Maximum Power Level) states: The licensee is authorized to operate the facility at steady-state reactor core power levels not in excess of 1772 megawatts (thermal). Additionally, TS Definition 1.0.m states: RATED POWER is the steady-state reactor core output of 1772 MWt. Short term corrective action was taken to conservatively limit calculated steady-state reactor power to no more than 99.69% (1766.5 MWt). This limit will remain in effect pending completion of the long term corrective action. Long-term corrective action is to perform a full system recalibration during the next refueling outage.
3052007003 | Kewaunee | 02/03/2007 | 04/04/2007 | ML07100030 | <strong>Emergency Diesel Generator Design Loading Calculations Non-conservative due to Old Design Issues</strong><br /><i>Abstract:&nbsp;</i>On 2/3/07 and 2/26/07, (with the plant at 99.69% power), and again on 3/8/07 (shutdown), additional loads were identified that had not been included in the emergency diesel generator design loading calculations. In the first two occasions, based on the diesel engine derating curves and the existing ambient temperature, the emergency diesel generators were determined to be operable. For the 3/8/07 occasion, a procedure change restored diesel operability. Together, these three events identified potential loading for both emergency diesel generators in excess of their 18 month surveillance loading of 2950 kW. At various times during the reporting period, ambient temperatures have existed that would have prevented the diesel generators from meeting their 18 month surveillance loading. The majority of these temperature events would also have prevented the diesels from meeting their newly calculated design loads. During the reporting period, there were periods when only one diesel was inoperable with no concurrent inoperability of opposite train engineered safety features equipment. There were other periods when only one diesel was inoperable but with concurrent inoperability of the opposite train engineered safety features equipment. Finally there were periods where both diesels were concurrently inoperable (both with and without concurrently operable opposite train engineered safety features equipment). This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plants Technical Specifications", and 10 CFR 50.73(a)(2)(v)(B) and (D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to (B) remove residual heat and (D) mitigate the consequences of an accident."
3052007004 | Kewaunee | 02/27/2007 | 04/25/2007 | ML07123025 | <strong>Reactor Trip During Quarterly Nuclear Instrumentation Calibration Procedure</strong><br /><i>Abstract:&nbsp;</i>On 2/27/2007 at 23:33 CST, with the reactor at approximately 100% power, while performing a quarterly channel calibration on nuclear instrument channel N-43, the reactor tripped. MS-201 B1, Reheat Steam to MSRBl, failed to close, (a repeat occurrence), which resulted in a reactor coolant system cooldown to 537 degrees F. Per contingency procedures, action was taken to manually isolate the turbine moisture separator reheat steam, which halted the cooldown, and Tave was restored to 547 degrees F. The additional cooldown resulted in a chemical and volume control system letdown isolation on low pressurizer level. Main feedwater isolated and auxiliary feedwater initiated, as designed, due to low-low level in the steam generators. No other safeguards systems actuated during the transient. The direct cause of the event appears to have been a Westinghouse BF66 relay contact failure in the reactor protection system trip matrix associated with nuclear instrumentation. The specific relay could not be determined. The most probable root cause has been determined to be blind contact relay failures due to a combination of relay contact sulfidation caused by poor circuit design, manufacturing defects in some installed relays, and installation practices from the original installation 30 years ago being inconsistent with current standards and practices. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of the reactor protection system and the auxiliary feedwater system.
3052007005 | Kewaunee | 03/03/2007 | 05/02/2007 | ML07128048 | <strong>Incorrect Control Power Transformers Results In Inoperable Safety-Related Loads</strong><br /><i>Abstract:&nbsp;</i>On 3/3/2007, with the reactor shutdown, it was determined that circuits for several safety-related loads had inadequately sized control power transformers. The loads connected to these circuits may not have actuated when required during a postulated accident with safety injection loads operating and off-site power still connected, at its minimum voltage limit. The affected loads were: - Train A Containment Dome Ventilation Fan - Train A Zone Special Ventilation Exhaust Fan - Train A Shield Building Ventilation Recirculation Fan - Train A and B Safety Injection Accumulator Discharge Isolation Valves When their accident mitigation function was required, the safety injection accumulator discharge isolation valves were aligned in their required accident positions and de-powered. However there were periods when both trains of the affected fans were unavailable for accident mitigation. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications", and 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident."
3052007006 | Kewaunee | 11/24/2004 | 05/31/2007 | ML07158023 | <strong>Reactor Coolant System Pressure-Temperature Limits Momentarily Exceeded During Solid Plant Operation</strong><br /><i>Abstract:&nbsp;</i>On 4/5/2007, during an engineering review of past computer data in response to undesirable solid plant cooldown and pressure control situations, the following previously unreported condition was discovered. On 11/24/2004 at 06:55 CST, with the plant shutdown under solid conditions, a reactor coolant system pressure transient occurred when a reactor coolant pump was started during system dynamic venting. Due to heat contained in the steam generator, the pump start caused a reactor coolant system heat up which resulted in a sudden increase in indicated reactor coolant system pressure from 371.9 psig to 509.8 psig and exceeded the heatup and cooldown curve pressure limit of 493 psig. The pressure transient was transferred to the connected residual heat removal system. The maximum RCS heatup and cool down rate limits were not exceeded. The residual heat removal pump discharge pressure increased to 626.5 psig which exceeded the system design pressure of 600 psig, and the 600 psig setpoint of residual heat removal system relief valves. The residual heat removal pump suction pressure increased to 502 psig which exceeded the setpoint of the residual heat removal suction header relief valve (set at 480 psig) and the low temperature overpressure protection relief valve (set at 500 psig). One or more of the relief valves described above lifted resulting in a loss of approximately 8 gallons of primary system inventory. This event is being reported under 50.73(a)(2)(i)(B) as an operation which was prohibited by the plants Technical Specifications.
3052007007 | Kewaunee | 03/23/2007 | 05/22/2007 | ML07150032 | <strong>Unexpected Safety Injection Response With Safeguards Buses Connected To The Reserve Auxiliary Transformer</strong><br /><i>Abstract:&nbsp;</i>On 3/23/2007 at 15:16 CST, with the plant at approximately 100% power, it was determined that automatic sequencing both trains of engineered safety features (ESF) equipment while both ESF buses are aligned to a single transformer could not meet design basis assumptions. The analysis shows that, in this arrangement, bus 5 and 6 degraded voltage relays may trip and subsequently shift both buses to their respective diesel generators. The plant design basis is for both safety buses to remain connected to offsite power when it is available. Both safety buses were manually aligned to the reserve auxiliary transformer (for relatively short durations) seven times during last three years. The electrical distribution system was normally aligned such that this lineup could have automatically occurred following a degradation of bus 5 voltage (fast bus transfer).The following example is provided in NUREG-1022, Event Reporting Guidelines, for reportability under 10 CFR50.73(a)(2)(v): "Both offsite electrical power (transmission lines) and onsite emergency power (usually diesel generators) are considered to be separate functions by [General Design Criteria] GDC 17. If either offsite power or onsite emergency power is unavailable to the plant, it is reportable regardless of whether the other system is available. GDC 17 defines the safety function of each system as providing sufficient capacity and capability, etc., assuming the other system is not available. Loss of offsite power should be determined at the essential switchgear buses.” This event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as an operation which was prohibited by the plant’s Technical Specifications, and 10 CFR 50.73(a)(2)(v)(A),(B),(C), and (D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to (A) Shutdown the reactor and maintain it in a safe shutdown condition, (B) Remove residual heat, (C) Control the release of radioactive material, and (D) mitigate the consequences of an accident."
3052007008 | Kewaunee | 06/19/2007 | 08/17/2007 | ML07235012 | <strong>Inadequate Emergency Diesel Generator Testing When Redundant Emergency Diesel Generator Was Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2007, Dominion Energy Kewaunee was verbally informed that NRC staff determined that a load test of the emergency diesel generator (EDG) was needed for demonstrating compliance with Technical Specification (TS) 3.7.b.2. This determination was made in response to a review of past operating practice at Kewaunee Power Station (KPS) regarding performance of a daily test of the redundant (other) EDG required by TS 3.7.b.2 when one EDG is inoperable. Historically, a start test of the redundant (other) EDG was performed to satisfy the daily test required by TS 3.7.b.2. However, the recent communications with NRC staff indicated that a start test of an EDG was insufficient for demonstrating compliance with TS 3.7.b.2. Rather, a load test in addition to a start test should have been performed. A record review identified two recent instances where daily surveillance testing of the redundant (other) EDG required by TS 3.7.b.2 had been performed (May 31 and July 26, 2006). This daily testing did not include a load test. However, subsequent monthly start and load testing performed per TS 4.6.a.1 confirmed that the EDGs had been operable.
3052007009 | Kewaunee | 09/18/2007 | 11/16/2007 | ML07330046 | <strong>Both Trains of Shield Building Ventilation Inoperable due to Damper Controller Failure on One Train While Second Train Inoperable for Routine Maintenance</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2007, at 12:00 pm CDT, Dominion Energy Kewaunee (DEK) identified a failure on the Shield Building Ventilation (SBV) Train A damper controller that rendered the train inoperable. Coincident with the Train A failure, Train B SBV was inoperable for routine maintenance. Consequently, both trains of SBV were inoperable simultaneously, rendering their associated safety function unavailable. Both trains of SBV being inoperable requires a reactor shutdown within 12 hours. Following discovery of this condition, the routine maintenance on SBV Train B was completed and the train was restored to operable status at 1331 CDT the same day, within the specified allowance. The 12-hour shutdown condition was then exited and the plant remained in a 7-day Action Statement for the other train of SBV (A) inoperable per TS 3.6.c. Two unrelated causes were responsible for both SBV trains being inoperable concurrently. SBV Train B was rendered inoperable for routine planned maintenance. Train A became inoperable due to a damper controller failure. The failed SBV Train A damper controller was not discovered until after the routine maintenance was in progress on the other SBV train. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(C), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material."
3052007010 | Kewaunee | 09/21/2007 | 11/20/2007 | ML07332016 | <strong>Allowed Outage Time of the Function for Automatic Initiation of the Control Room Post-Accident Recirculation System on a High Radiation Signal Not Met</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2007, during performance of an evaluation of the control room radiation monitor (R-23) failure mode, Dominion Energy Kewaunee (DEK) staff identified that the 12-hour shutdown requirement in Technical Specification (TS) 3.12, "Control Room Post-Accident Recirculation System", had been exceeded on previous occasions during performance of R-23 troubleshooting. R-23 provides a signal for automatic initiation of control room recirculation on high radiation. This event occurred during past performances of corrective maintenance on R-23 when the monitor's trip function was disabled in excess of 12 hours with the reactor critical. Under conditions when R-23 is isolated from the system, the control room post-accident recirculation system cannot meet its surveillance requirement specified in TS 4.17. Kewaunee Power Station (KPS) Technical Specifications require that such a condition constitutes failure to meet the operability requirements for the associated limiting condition for operation (LCO). Therefore, TS 3.12 is not met under such conditions, even if the control room post-accident recirculation system is placed in operation to meet its safety function. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications."
3062007001 | Prairie Island 2 | 04/05/2007 | 07/26/2007 | ML07208005 | <strong>Unit 2 Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2007, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was operating at 100% power. At approximately 0908 CDT, during surveillance testing of Unit 2 Train A safeguards logic at power, a spurious Train A Safety Injection (SI) actuation occurred resulting in Reactor Protection System (RPS) actuation. Train A SI was in "Test" at the time and should not have caused the RPS trip. At approximately 0913 the operating crew manually actuated Train B SI as required by emergency operating procedures. Reactor Coolant System (RCS) pressure momentarily decreased below the shutoff head of the high head Emergency Core Cooling System (ECCS) pumps during the transient, resulting in ECCS discharge to the RCS. At approximately 0920 safety injection was terminated per emergency operating procedures. All systems operated as expected and operator response and recovery actions were as expected. Initial investigation of the cause of the automatic reactor trip was determined to be a deficiency with the safety injection relay equipment. Instrument and Control technicians discovered a safety injection relay with high contact resistance. The high resistance contact caused the relay to not reset when exiting the safeguards logic test. With the relay not reset, and safeguards logic not in test, a spurious SI actuation occurred. The defective relay was replaced and tested to verify proper operation prior to Unit 2 reactor startup.
3062007002 | Prairie Island 2 | 10/08/2007 | 04/18/2008 | ML08109059 | <strong>Emergency Diesel Generator Inoperable Longer than Allowed by Techincal Specifications Due to Loose Switch</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2007, the 22 Diesel Room Cooling Fan failed to start automatically upon the starting of the Train B Unit 2 emergency diesel generator (D6). The room cooling fan is required for D6 operability (to preclude eventual overheating of equipment in the room). The past operability evaluation concluded that D6 had been inoperable between approximately September 3, 2007 and the date of the event. The September 3 date was an estimate, since procedurally operators are directed to run the fan manually until the room cools off after a diesel run. The past operability evaluation concluded the switch was left in an intermediate position (neither in Auto nor in Run - the two normal positions of the switch). This was attributed to a loose switch assembly - upon shutting down the fan after the September D6 run, the operator turned the switch to the Auto position (the switch is a break before make) on the control board, but the entire switch assembly below the control panel rotated such that the switch was in an intermediate position (even though it appeared to be in the Auto position). The switch assembly was repaired and the room cooling fan and D6 were returned to operable status. The cause of the fan failure was confirmed to be as described above following a cause evaluation. Planned corrective actions include instituting new preventive maintenance procedures to periodically check the switches and to install anti-rotation devices in the switches.
3092007001 | Maine Yankee | 04/05/2007 | 05/31/2007 | ML07157036 | <strong>Uncompensated Degradation in a Security System</strong><br /><i>Abstract:&nbsp;</i>This report is submitted pursuant to the requirements of 10 CFR 73.71(d) for a 60-day written report and contains no Safeguards Information (SI). On April 5, 2007 the Maine Yankee Independent Spent Fuel Storage Installation (ISFSI) management discovered an uncompensated degradation in a security system located in the isolation zone for the protected area. The contract security force had bypassed security equipment in constant alarm due to environmental conditions. Compensatory measures were established in accordance with Physical Security Plan and procedural requirements. The method of compensatory measures for the bypassed security equipment was subsequently modified due to concerns of hazardous weather conditions. The alternate compensatory measures established did not fully meet Physical Security Plan or procedural requirements. The time line for the event on Thursday April 5, 2007 is as follows: 0502 - Completed the normal compensatory measures for the bypassed security system zones in accordance with the Physical Security Plan and implementing procedure requirements. At this time a decision was made to change the method of compensatory measures due to environmental conditions. 0532 - Safeguards Event Log was filled out for bypassed security system zones in accordance with 73.71(C) as described in Appendix G paragraph II(a) which is required within 24 hours of discovery. 0628 to 0643 - Maine Yankee management review conducted to access the compensatory measures in place against the Physical Security Plan and implementing procedures. The alternate compensatory measures were determined to be not fully compliant. 0643 to 0656 - Maine Yankee Management discussed event with on shift crew 0701 - Commenced performing the original compensatory measures for the bypassed security system zones in accordance with the Physical Security Plan and implementing procedures.
3112007001 | Salem 2 | 05/01/2007 | 06/29/2007 | ML07197004 | <strong>Inoperability of the Chilled Water System - (21 and 22 Chillers Inoperable)</strong><br /><i>Abstract:&nbsp;</i>At 2013 hours on April 25, 2007, the 22 Chiller was declared inoperable due to emergent maintenance and Technical Specification (TS) 3/4.7.10 "Chilled Water System" Action a was entered. At 2130 hours on May 1, 2007, 21 Chiller was declared inoperable because it failed to start with the initiating conditions present. With two chillers inoperable TS 3/4.7.10 Action B requires that the opposite control room Control Room Emergency Air Conditioning System (CREACS) be placed in single train filtration within four (4) hours. Action b requirements were completed within the allowable TS time from 2130 hours. However, further investigation revealed that 21 Chiller had been inoperable since 1500 hours on May 1. Therefore, the actions of TS 3/4.7.10 Action b were not performed within the four (4) hour allowable TS time. The cause for 21 Chiller inseparability was that the key switch was loose in its mounting hole, such that repositioning the switch did not change the state of the internal contacts. Corrective actions included the repair of the faulty switch, and verifying that the switches on the other chillers, including the ones in the opposite unit, were in proper operating condition. This report is being made in accordance with 10CFR50.73(a)(2)(i)(B), "Operation or Condition Prohibited by Technical Specification."
3112007002 | Salem 2 | 05/24/2007 | 07/23/2007 | ML07212058 | <strong>Reactor Trip due to a Breach in the Condensate System</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2007 at 0232, Salem Unit 2 tripped due to 22 Steam Generator (SG) low-low level. The cause of the low SG level trip was the failure of the 24 Demineralizer Vessel (DMV) upper sight glass, which resulted in a loss of condensate inventory and suction pressure and ultimately the trip of 21 Steam Generator Feedwater Pump (SGFP). The 21 SGFP trip resulted in a turbine runback signal and level decrease in the 22 SG. An automatic reactor trip occurred when 2 of 3 channels reached the low-low level set point on the 22 SG. The root cause for failure of the 24 DMV upper sight glass is attributed to the latent failure to control vendor documents pertaining to the installation and maintenance of these sight glass windows. Corrective actions included replacing all Unit 2 sight glass windows prior to placing the DMVs back into service and the replacement of Unit 1 sight glass windows as the DMVs were removed from service during routine operation. All DMV sight glasses have been replaced. This event is reportable in accordance with 10CFR50.73 (a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B) of this section."
3112007003 | Salem 2 | 08/06/2007 | 11/16/2007 | ML07332055 | <strong>Reactor Trip due to Spurious Feedwater Interlock Signal</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2007, the Salem Unit 2 reactor tripped due to 22 Steam Generator water level reaching its low low level set point. The cause of steam generator low low level was a faulty Solid State Protection System (SSPS) output driver card A517 that initiated a spurious feedwater interlock signal and resulted in the closure of the feedwater regulating valves. It was determined that the failed circuit card was due to a defective solder joint. The root cause was attributed to inadequate post soldering test practices. The failed circuit card was replaced and the system tested satisfactorily. The test and inspection procedure for refurbished SSPS safety related circuit cards will be revised to include: (1) the use of soldering standards with inspections of both sides of the circuit card and (2) a manual test of the circuit card with agitation. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
3152007001 | Cook 1 | 08/28/2007 | 10/22/2007 | ML07305032 | <strong>Unit 1 Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2007, at 1354 hours, Donald C. Cook Nuclear Plant (CNP) Unit 1 received a reactor trip and main turbine trip signal as a result of low Steam Generator #11 water level coincident with a steam flow - feedwater flow mismatch. All control rods fully inserted and the Auxiliary Feedwater System (AFW) started and performed as designed. The reactor trip was uncomplicated and all major plant components functioned as designed. The reactor trip was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and the AFW actuation was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). The reactor trip and AFW actuation are reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A). The trip was the result of an over voltage condition on one of the Digital Control System (DCS) power supplies. The over voltage condition caused the controller for the East Main Feed Pump control valve to automatically trip, causing an inadequate feedwater flow condition to the steam generators. Corrective actions included replacement of the DCS power supply.
3152007002 | Cook 1 | 10/05/2007 | 12/20/2007 | ML08003004 | <strong>Failure to Declare Essential Service Water Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2007, while verifying equipment status to assure compliance with Technical Specifications (TS), the Shift Technical Advisor identified a previously unrecognized entry into Unit 1 TS 3.8.4 and 3.8.9 action requirements due to outage activities in Unit 2 that had removed a 250-volt DC plant battery from service. Because the Unit 2 Essential Service Water (ESW) train associated with the battery was cross-tied to the Unit 1 West ESW train, Unit 1 was placed in a condition where Unit 1 TS 3.8.4 and 3.8.9 required the Unit 1 West ESW pump to be declared inoperable. In this case, the Unit 1 West ESW pump was already considered inoperable for other reasons. A review was performed to identify any similar unrecognized entries into TS 3.8.4 and 3.8.9 action requirements during the Unit 2 outage or during the Unit 1 refueling outage in 2006. Three cases were identified where unrecognized entry into TS 3.8.4 and 3.8.9 action requirements resulted in failure to meet the requirements (i.e, declaration of ESW train inoperability). These events are reportable as a licensee event report in accordance with 10 CFR 50.73(a)(2)(i)(B). The cause of these events was a failure of the Improved TS implementation process to establish appropriate barriers to ensure that the requirements of TS 3.8.4 and 3.8.9 would be met. Corrective actions include operating procedure revisions and operator training.
3162007001 | Cook 2 | 10/28/2007 | 06/13/2008 | ML08176028 | <strong>As-Found Local Leak Rate Tests Not Performed</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2007, Donald C. Cook Nuclear Plant (CNP) failed to perform the required as-found local leak rate tests (LLRT) prior to performing emergent maintenance that had the potential to affect the leak tightness of CNP Unit 2 Containment Isolation Valves. Originally identified were 2-WCR-942, Non-Essential Service Water (NESW) to Reactor Coolant Pump (RCP) No. 2 Motor Air Coolers and 2-WCR-946, RCP No. 2 Motor Air Coolers NESW Outlet. An extent of condition investigation noted that additional as-found LLRTs were not performed prior to maintenance performed September 26, 2007, on 2-WCR-922 and October 7, 2007, on 2-WCR-923; these are series Containment Isolation valves for NESW. This condition prohibited by Technical Specifications (TS) was not recognized initially. This Licensee Event Report supplement adds these two additional valves which were not previously reported as extent of condition. The 2-WCR-942 and 2-WCR-946 LLRTs were missed due to human error in assuming that the as-found LLRTs were no longer required and inadequate validation of that assumption. The 2-WCR-922 and 2-WCR-923 as-found LLRTs were not performed due to apparent blockage in the line, and the missed reporting was due to a mindset that this was not a condition prohibited by TS because of the inability to perform the required as-found testing. Corrective Actions included the performance of acceptable as-left leak rate tests following the maintenance on each of the valves, the addition of initial and recurring training for the work package planners that focuses on LLRT requirements, and the appropriate Engineering procedure revisions to clearly specify required actions for a missed test, whether inadvertent or intentionally not performed due to system/component conditions. The failure to meet Surveillance Requirement 3.6.1.1 is reportable in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
3172007001 | Calvert Cliffs 1 | 01/17/2007 | 03/19/2007 | ML07081050 | <strong>Reactor Coolant System Pressure Boundary Leakage in Pump Cover Heat Exchanger</strong><br /><i>Abstract:&nbsp;</i>Results from the hydrostatic pressure test performed in January 2007 on the Pump Cover Heat Exchanger (FIX) previously installed on 11B Reactor Coolant Pump (RCP), indicates that a Reactor Coolant System (RCS) pressure boundary leak existed when the component was installed in Unit 1. The HX was removed during the 2006 Unit 1 refueling outage as a corrective action to address failures of the lower seal stage and RCS detected in the Component Cooling Water (CCW) system. The RCS leakage was documented in September 2004. The RCS leak rate was so small (approximately 0.016 gallons per day) that the exact location could not be identified by sampling. The leakage was considered unidentified RCS operational leakage, and was less than the one gallon per minute Technical Specification allowable. The Technical Specifications limit RCS pressure boundary leakage to zero. Chemistry tests performed on the CCW system subsequent to startup from the 2006 refueling outage indicated that the active RCS leak was no longer present. The hydrostatic pressure test results, and the fact that the RCS leakage stopped after the 11B RCP HX was replaced, confirm that an RCS pressure boundary leak existed.
3182007001 | Calvert Cliffs 2 | 04/02/2007 | 05/29/2007 | ML07151020 | <strong>Channel C Linear Range Nuclear Instrument Inoperable During Startup</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2007, while in Mode 1 during a Unit 2 startup, Operations staff determined that Channel C Linear Range Nuclear Instrument (LRNI) did not provide indication on the Reactor Protective System Calibration and Indication Panel. Troubleshooting determined that a circuit card was in the wrong slot on the circuit board, resulting in an inoperable condition for Channel C LRNI. This condition was created during the 2007 Unit 2 Refueling Outage while the plant was shutdown and the LRNI channels were not required to be operable. The inoperability of Channel C LRNI was related to human performance. Technician error led to the incorrect installation of the circuit card which resulted in a Reactor Protective System channel out-of-service. Additionally, post-maintenance testing failed to find the mis-located A3 circuit card prior to the mode of applicability for the affected channel. Operations personnel bypassed the inoperable channel until the problem was corrected. Maintenance, operations, and surveillance test procedure revisions are planned to prevent recurrence of this condition.
3182007002 | Calvert Cliffs 2 | 09/14/2007 | 11/08/2007 | ML07318043 | <strong>Dual Containment Spray Train Inoperability due to Latent Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2007, 21 Containment Spray (CS) Train was found to be inoperable during surveillance testing due to a failed shut Shutdown Cooling Heat Exchanger Component Cooling Outlet Valve. The valve actuator stroked in response to Control Room handswitch manipulation, however the valve stem did not move. The cause of this failure to stroke was a broken woodruff key between the valve actuator and the valve stem. A review of prior plant data indicates the key failed on September 7, 2007. Further investigation determined that 22 CS Train was removed from service for planned maintenance from 0300 on September 11, 2007 until 2121 on September 12, 2007. This action resulted in a period of time where both CS trains (21 and 22) were inoperable. The apparent cause of the dual CS train inoperability was incorrect valve travel setup, which damaged the valve liner. A temporary alteration was installed on September 15, 2007 to lock the failed valve in its post-accident open position until the valve can be replaced. Maintenance procedures will be modified to ensure proper valve travel setup after installation or overhaul. Surveillance test procedures will be modified to include available, redundant verification of physical system parameters during restoration steps.
3212007001 | Hatch 1 | 02/07/2007 | 04/09/2007 | ML07103015 | <strong>High Pressure Coolant Injection Inoperable Due To Component Failures</strong><br /><i>Abstract:&nbsp;</i>On 2/7/07 at 1640 EST, Unit 1 was in the Run mode at approximately 100 percent of rated thermal power. At that time, a control room operator was performing a control board walk-down when he noticed the position indicating light for the High Pressure Coolant Injection (HPCI, EIIS Code BJ) system's minimum flow control valve was extinguished. Further investigations discovered a degraded resistor on the position indicating light and a blown control power fuse in the valve's motor control center (MCC). As a result, the minimum flow valve was incapable of operating, rendering HPCI inoperable. On 2/8/07 at 0431 EST, with Unit 1 in the Run Mode at approximately 100 percent of rated thermal power, operations personnel were performing a HPCI pump operability test when the turbine steam supply valve failed to open. As a result, turbine speed did not increase and the HPCI system did not initiate as required. In each case, the HPCI system was declared inoperable and the appropriate Technical Specifications Required Action Statement was entered. The cause of the failed minimum flow valve was a degraded resistor which resulted in a blown control power fuse in the valve's MCC. The turbine steam supply valve did not open due to a failed motor which investigations determined likely resulted from past bonnet pressurization events and thermal aging. Pressurization could occur if water enters the valve bonnet and is subsequently heated. Corrective actions for the failed minimum flow valve included replacing the fuse and resistor. Also, resistors with indicating lamps for DC motor operated valves of the HPCI and RCIC systems will be checked and replaced as necessary. The failed steam supply valve motor was replaced and the HPCI procedure was revised to ensure any water is drained from the valve bonnet following events which result in the HPCI steam line being filled with water.
3212007002 | Hatch 1 | 03/07/2007 | 05/07/2007 | ML07128011 | <strong>ATTS Card Failure Results in High Pressure Coolant Injection System Isolation</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2007 at 8:50 pm EST Hatch Unit 1 was in the run mode at approximately 100 percent of rated thermal power. At that time during the performance of the Analog Transmitter Trip System (ATTS) panel Functional Test and Calibration procedure the High Pressure Coolant Injection (HPCI) inboard isolation valve 1E41-F002 closed. The HPCI system was declared inoperable and the appropriate Technical Specifications Required Action Statement was entered. Troubleshooting of the HPCI isolation logic circuit was performed. The most probable cause of the valve closure was determined to be a faulty ATTS card, 1F41-N670A. The board was inspected and evidence of chipped insulation and fractured solder connections of the board's components were found. These faults contributed to an erroneous trip signal being sent, resulting in the valve closure. The failed ATTS card and an associated ATTS card were replaced. In addition, related ATTS Agastat relays were replaced to avoid age-related problems or failures.
3242007001 | Brunswick 2 | 03/26/2007 | 05/22/2007 | ML07151008 | <strong>Operation Prohibited by Technical Specification 3.3.1.2, "Source Range Monitor Instrumentation"</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2007, at approximately 1015 hours (EDT), Operations began returning seven Unit 2 control rods to service. To confirm operability of the control rod position indication, each control rod was to be withdrawn one notch and subsequently re-inserted. Surveillance Requirement 3.3.1.2.2 of Technical Specification (TS) 3.3.1.2, "Source Range Monitor Instrumentation," requires, in part, that there be an operable source range monitor (SRM) in the core quadrant where core alterations are being performed. Contrary to this requirement, control rod 10-35 was withdrawn a single notch in a fueled quadrant of the core where there was not an operable SRM. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's TSs. The root cause of this event was inadequate procedures. Existing operating procedures did not provide adequate guidance identifying prerequisites required to be met prior to performing core alterations, due to control rod movement. To prevent recurrence, appropriate plant procedures will be revised.
3242007002 | Brunswick 2 | 04/17/2007 | 06/22/2009 | ML09181011 | <strong>Mode Change Made with Reactor Core Isolation Cooling System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2007, at approximately 1300 hours (EDT), Unit 2 achieved a reactor steam dome pressure of greater than 150 psig in Mode 2 (i.e., the Applicability of Technical Specification (TS) 3.5.3, "RCIC System") following startup from a refueling outage which began on March 3, 2007. Subsequently, on April 18, 2007, the Reactor Core Isolation Cooling (RCIC) system was declared inoperable. It has been determined that RCIC was inoperable when the Applicability of Technical Specification (TS) 3.5.3, "RCIC System," was entered. Limiting Condition for Operation (LCO) 3.0.4 prohibits entry into a mode or other specified condition in the applicability unless, subject to certain exceptions, the LCO is met. As such, restart of Unit 2 with RCIC inoperable is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's TSs. The root cause of this event was the lack of a time delay relay on the low suction pressure switch; increasing the likelihood that the RCIC system would trip due to small pressure perturbations, combined with a section of RCIC injection piping which was sloped incorrectly and, as a result, contained air voiding. Air voids were introduced as a result of system maintenance and inspection performed during the refueling outage. These voids, which collapsed as a result of starting RCIC, introduced a pressure wave of sufficient magnitude to actuate the RCIC low suction pressure trip logic but not sufficient to cause a water hammer large enough to result in physical damage to affected components. The corrective actions to prevent recurrence consisted of installation of time delay relays to eliminate spurious trips due to momentary pressure oscillations and modification of the injection piping to resolve the air voiding concerns.
3242007003 | Brunswick 2 | 06/26/2007 | 10/18/2007 | ML07299011 | <strong>As-Found Values for Safety/Relief Valve Lift Setpoints Outside Technical Specification Allowed Tolerance</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2007, the Brunswick Steam Electric Plant received the results of as-found testing of 11 safety/relief valves (SRVs); which had been removed from Unit 2 during the spring 2007, refueling outage (i.e., B218R1). These results indicated that four of the 11 valves mechanically actuated at pressures outside of the 3 percent tolerance allowed by Technical Specification 3.4.3, "Safety/Relief Valves." Since Technical Specification 3.4.3 requires 10 of the 11 installed SRVs to be operable, this condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's Technical Specifications. The cause for the setpoint drift for valves 2-B21-F013B and 2-B21-F013D was an incomplete understanding of proper lapping techniques when the BSEP SRV rebuild program began; leading to improper lapping of the pilot disc. The cause for the setpoint drift for valve 2-B21-F013F was misalignment between the pilot rod and set spring causing mechanical binding between the pilot rod and guide. The cause for the setpoint drift for valve 2-B21-F013K was lack of maintenance on the pilot valve assembly, which allowed the accumulation of deposits/tarnish on the pilot disc and lead to the formation of an oxide bond between the pilot disc and seat. Corrective actions for these items include: (1) incorporation of additional industry guidance into the SRV Rebuild Program, (2) rebuilding of the 2-B21-F013F pilot valve assembly, and (3) allowing a pilot valve assembly to be recertified as-found only one time before a mandatory rebuild is performed.
3242007004 | Brunswick 2 | 10/10/2007 | 01/29/2008 | ML08037051 | <strong>High Pressure Coolant Injection (HPCI) System Inoperable due to Main Pump Seal Leak</strong><br /><i>Abstract:&nbsp;</i>On October 10, 2007, at 2245 hours Eastern Daylight Time (EDT), during performance of the High Pressure Coolant Injection (HPCI) system operability test, the HPCI system was declared inoperable due to a leak on the main pump turbine side seal. The approximate five gallon per minute leak was isolated by securing the pump and isolating the keep-fill. No automatic system isolations or actuations occurred. All Emergency Core Cooling Systems (ECCS) and the Reactor Core Isolation Cooling (RCIC) system were operable. The safety significance of this event is considered minimal because HPCI was still available for injection, though in a degraded condition, and adequate core cooling was ensured by the operability of the redundant low pressure ECCS injection subsystems in conjunction with the Automatic Depressurization System (ADS). The RCIC system would also automatically provide makeup water at high reactor operating pressures. The root cause of this event was an inadequate evaluation of foreign material in the Unit 2 Condensate Storage Tank (CST) performed in 1999, leading to legacy foreign material in the HPCI system seal purge piping, combined with the configuration of the line which is intolerant to foreign material intrusion. The HPCI system was returned to service following the replacement of the HPCI main pump seal, and the inspection and removal of foreign material from the seal purge water piping. A detailed engineering analysis has been completed and has concluded that the effected system maintained its ability to fulfill its safety functions in the degraded condition. Based on the results of the engineering evaluation, this LER is formally withdrawn. Event Notification 43711 was also retracted.
3252007001 | Brunswick 1, Brunswick 2 | 01/27/2007 | 03/27/2007 | ML07094068 | <strong>E1 to E3 Cross-tie Breaker Unavailable due to Misalignment</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2007, at approximately 1600 EDT, while performing a periodic surveillance of breaker alignment, the Emergency Bus 1 (E1) to E3 cross-tie breaker, located on E1, was found with the racking lever misaligned slightly from the required vertical position, and the trip pushbutton was found to be depressed (i.e., not flush with the breaker cover as required). The E1 cross-tie breaker and the E3 cross-tie breaker are two breakers in series between emergency buses E1 and E3 and allow cross-tying of the two buses during emergency conditions. Control power to the cross-tie breaker is supplied via a local manual switch and is used for Station Black Out (SBO), Fire (i.e., as directed by Alternate Safe Shutdown (ASSD)), and maintenance procedures. The breaker was determined to be racked-in past the normal connected position and would have prevented closure of the breaker. This event is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B), as an event or condition that resulted in the plant being in an unanalyzed condition that significantly degraded plant safety. It appears that the breaker was in the tripped condition since April 29, 2006, the date of the last documented activity affecting this breaker. The select cause of this event is a failure to properly rack-in the breaker in accordance with procedure 1OP-50, "Plant Electric System Operating Procedure."
3252007002 | Brunswick 1, Brunswick 2 | 04/01/2007 | 05/30/2007 | ML07157036 | <strong>Technical Specification Required Shutdown Due To Emergency Diesel Generator 4 Inoperability</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2007, at approximately 1528 Eastern Daylight Time (EDT), Unit 1 entered Mode 3 in accordance with Required Action H.1 of Technical Specification (TS) 3.8.1, "AC Sources - Operating;" Mode 4 was entered at approximately 1215 EDT on April 2, 2007. The TS required shutdown was due to inoperability of emergency diesel generator (EDG) 4, which was removed from service on March 25, 2007, for planned maintenance. Unit 2 was in Mode 4, having been previously shutdown on March 3, 2007, for refueling. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A), due to the completion of a plant shutdown required by the plant's TSs. The direct cause of the TS required shutdown of Unit 1 was the inability to return EDG 4 to operable status within the seven day completion time of Required Action D.4 of TS 3.8.1. The extended out-of-service time was due to multiple equipment issues, including two failed refurbished governors and latent design problems discovered during the Allen-Bradley relay replacements only after extensive post-maintenance testing. Each individual equipment issue was manageable within the allowed outage time, but the number and sequence of discovery was such that the cumulative effect of these issues precluded EDG 4 recovery within the allowed out-of-service time.
3282007001 | Sequoyah 2 | 01/23/2007 | 03/20/2007 | ML07086027 | <strong>Reactor Trip Following Closure of Main Feedwater Valve due to Control Air Line Failure</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2007, at 1244 Eastern standard time (EST) with Unit 2 operating at 100 percent power, an automatic reactor trip occurred because of a low-low steam generator level on Loop 2. The immediate cause was closure of the Loop 2 main feedwater regulating valve as a result of a failed control air line. At approximately 1030 EST, it was identified that the air line tubing to the Loop 2 main feed regulating valve appeared to be damaged and leaking. Operations discussed the condition with plant management and agreed to pursue dogging the valve open so maintenance could be performed online. During the evolution to open and place the bypass regulating valve in automatic, a swing in control signal was seen and feedwater flow decreased rapidly. The SRO directed that a manual reactor trip be initiated. The automatic trip occurred before the manual trip was initiated. Following the reactor trip, the plant systems responded as designed. The unit entered Mode 3 and an event investigation was initiated. The feedwater regulating valve's control air line was damaged as a result of improper routing of field tubing during a recent outage modification. The routing of the control air line did not sufficiently account for movement of the valve due to thermal growth.
3282007002 | Sequoyah 2 | 03/13/2007 | 05/14/2007 | ML07137006 | <strong>Manual Reactor Trip Following Partial Loss of Main Feedwater Flow</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2007, at 1527 Eastern standard time with Unit 2 operating at 100 percent power, a manual reactor trip was initiated because of a partial loss of main feedwater flow to the steam generators. The immediate cause was failure of the 2A main feedwater pump control system. During normal power operations, Operations noticed that the steam generator levels on all four steam generators had begun to decrease. The 2A main feedwater pump speed controller output was noted to be decreasing. The controller was placed to manual but the controller failed to respond to the operator's attempt to increase output. The steam generator Loop 2 low-level alarm annunciated and the reactor was manually tripped. Following the reactor trip, the plant systems responded as designed. The unit entered Mode 3 and an event investigation was initiated. Troubleshooting determined the problem to be within the 2A main feedwater speed indicating controller. The root cause of the event was determined to be a faulty local/remote switch which is internal to the speed indicating controller.
3312007001 | Duane Arnold | 01/24/2007 | 03/26/2007 | ML07086069 | <strong>Unplanned Inoperability of the High Pressure Coolant Injection Pump</strong><br /><i>Abstract:&nbsp;</i>In preparation for an upcoming Refueling Outage, during a pre-construction inspection of the High Pressure Coolant Injection (HPCI) system injection line (pipe support EBB-5-SR-9), one of the two pipe clamp bolt assemblies (i.e., stud, nut, and spacer) was found to be missing. Initial engineering evaluation determined that with the bolt missing, the ASME Code Section III, Appendix F allowable stresses would not be met at the HPCI-to-Feedwater tee connection. Consequently, HPCI was declared inoperable on 1/24/07. Work Order A73452 was initiated and necessary repairs were completed to replace the missing bolt assembly and HPCI was subsequently declared operable on 1/24/07. The cause of this event was determined to be incomplete field work that occurred some time after 4/21/84, which left the pipe clamp without one of the required bolt assemblies. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312007002 | Duane Arnold | 02/12/2007 | 04/13/2007 | ML07107031 | <strong>Loss of Control of Control Building Boundary</strong><br /><i>Abstract:&nbsp;</i>On February 12, 2007 during Refueling Outage 20 in Mode 5, testing was performed to determine how the control building envelope was affected by opening 2 four inch penetrations from the turbine building into the cable spreading room. Subsequent to the completion of the testing, it was discovered that three additional penetrations had been opened between the control room and cable spreading room, rendering the control building boundary inoperable for a period of time longer than that allowed by Technical Specification 3.7.4,Condition F. Core Alterations had been in progress at the time and were suspended upon discovery that the control building boundary was inoperable. The control room and cable spreading room are both within the control building boundary. Previously, it was not understood that opening of penetrations within the control building envelope compartments could render the control building boundary inoperable. Additionally, workers were not required to inform the control room operators when penetrations between control building compartments were opened. There were no actual safety consequences and no effect on public health and safety as a result of this event. This report is submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B).
3312007003 | Duane Arnold | 02/18/2007 | 04/20/2007 | ML07115031 | <strong>Linear indications found During UT examination of safe-end to nozzle welds</strong><br /><i>Abstract:&nbsp;</i>Safe-end to nozzle weld RRF-F002 was scheduled in RF020 as an examination under BWRVIP-75 and as a successive examination under ASME Section Xl. On 2/18/07, the examination revealed a linear indication at the bottom of the weld that did not meet the acceptance criteria (IWB-3500) of ASME Section Xl. Based on this unacceptable linear indication a scope expansion was required for both programs (BWRVIP-75 and ASME Section XI). The scope expansion included safe-end to nozzle weld RRC-F002. On 2/21/07, this weld also was determined to not meet the acceptance standards (IWB-3500) of ASME Section Xl. Both welds were subsequently overlaid under an NRC verbally approved relief request. The root cause of the indications in both welds (RRF-F002 and RRC-F002) was determined to be lntergranular Stress Corrosion Cracking (IGSCC). This is based on the signal discrimination of the Ultrasonic Test examination, a review of the operating experience (OE) and the independent review of the event by outside organizations. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312007004 | Duane Arnold | 02/24/2007 | 04/26/2007 | ML07117057 | <strong>Severe Weather Causes Grid Disturbance Resulting In Loss of Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>On February 24, 2007, while the plant was shutdown and In Mode 5 for Refueling Outage 20, a severe winter storm brought freezing rain, ice and high winds to the Duane Arnold Energy Center (DAEC) grid area causing degraded voltage conditions on the essential busses. The DAEC was performing Core Alterations and the B Standby Diesel Generator (SBDG) was being manually run for post maintenance testing at the time. Beginning at 1654, transmission lines to the DAEC switchyard began to be lost due to severe weather. At 1755, the A SBDG automatically started on bus under voltage. At 1756 Core Alterations were secured based on indications that the grid was becoming unstable. At 1757 a full scram occurred due to loss of B Reactor Protection System (RPS) and Neutron Monitoring System Trip on the A RPS, and Groups 1 through 5 isolations (excluding the Main Steam Isolation Valves) occurred, resulting in a loss of Shutdown Cooling. At 1820, bus degraded voltage conditions caused both running SBDGs to load onto their respective busses, causing a loss of Fuel Pool Cooling,General Service Water, and B Control Building Chiller. At 1825, grid voltage recovered, however subsequent conversations with the grid operator indicated that the area grid, including the DAEC switchyard, was isolated from most of the offsite power sources and that only two 161KV lines remained powered into the DAEC switchyard. At 1835, all work activities in the power block were suspended. The essential busses remained powered by their respective SBDG. Grid repair and recovery allowed the essential bus 1A4 power supply to be transferred from the B SBDG to the Startup Transformer at 1148 on February 25, 2007. The essential bus 1A3 power supply was transferred from the A SBDG to the Startup Transformer at 0049 on February 26, 2007. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312007005 | Duane Arnold | 03/02/2007 | 04/26/2007 | ML07117057 | <strong>Automatic Reactor Scram Due To Scram Discharge Volume High Water Level During Performance of a Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2007, during Refueling Outage 20, Surveillance Test Procedure NS550002 was being performed for testing of the Control Rod Drive System Back-up Scram Valves. The procedure required insertion of a manual reactor scram, however, the procedure did not require bypassing the Scram Discharge Volume High Level Scram signal prior to resetting the manual scram. Subsequently, an automatic reactor scram occurred on March 2, 2007 at approximately 2332 hours due to Scram Discharge Volume high level. All control rods were already fully inserted prior to beginning the Surveillance Test, therefore, control rod motion did not occur as a result of either the manual or automatic scram during performance of the Surveillance Test. Operators bypassed the Scram Discharge Volume high water level signal and successfully reset the Scram at approximately 2332 hours on March 2, 2007.The cause of this event was determined to be inadequate guidance in the surveillance procedure to bypass the Scram Discharge Volume High Level Signal prior to resetting the reactor scram. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312007006 | Duane Arnold | 03/18/2007 | 05/17/2007 | ML07141006 | <strong>Reactor Shutdown as a Result of a Chemistry Excursion</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2007, while operating at 28% power, a chemistry excursion occurred shortly after Condensate Filter Demineralizer 1T-13D was placed in service. The magnitude of the chemistry excursion required operators to shutdown the reactor in accordance with abnormal operating procedure sand plant chemistry procedures. As a result of inserting the manual scram, Primary Containment Isolation System (PCIS) groups 2, 3, and 4 isolations occurred when reactor water level dropped below 170 inches. All isolations went to completion. The reactor water level decrease is normal following as cram from 28% power due to void collapse in the reactor vessel. Reactor water level was subsequently restored to normal and the PCIS group isolations were reset. Troubleshooting subsequently determined that the chemistry excursion was the result of resin intrusion from Condensate Filter Demineralizers into the Condensate System. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312007007 | Duane Arnold | 04/02/2007 | 06/01/2007 | ML07158020 | <strong>Reactor Scram Due to 1A2 Non-essential Bus Lockout</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2007, while operating at 98% power, during performance of planned preventative maintenance on Non-essential Electrical 4160V AC Bus 1A2, a bus lockout occurred at 11:25. The loss of the 1A2 switchgear resulted in the loss of B Reactor Feed Pump and B Condensate Pump. At 11:25, a manual reactor scram was inserted due to Reactor Pressure Vessel level approaching 170 inches (automatic scram level). The scram went to completion. After the scram, vessel level rose to 211 inches, causing the A Reactor Feed Pump to trip. Before the ‘A’ Reactor Feed Pump could be restarted and adequate feed flow established, another scram signal was received when reactor level dropped below 170 inches. Control rods were already inserted and isolations had been completed prior to this second scram signal being received. The Reactor Operator successfully restored level using the Feedwater Regulating Valve as directed by the Operations Shift Manager. The cause of this event is the failure to recognize the risk associated with performing the maintenance on-line without putting physical and process protections in place. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312007008 | Duane Arnold | 04/11/2007 | 06/11/2007 | ML07170012 | <strong>Condition Prohibited by Technical Specifications; 'B' Emergency Diesel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 11,2007, while operating at 100% power, during STP 3.8.1-04 for the 'B' Emergency Diesel Generator (EDG), a 0.21 gallon per minute lube oil leak from the Lube Oil Filter (LOF) was observed.The engine was shutdown and investigation determined that an incorrect o-ring had been installed. The o-ring was installed on February 12, 2007 under Preventative Work Order 1135811 during a cylinder liner replacement in Refuel Outage (RFO) 20. A past operability evaluation has determined that the 'B' EDG was inoperable from February 12, 2007 until time of discovery. The lube oil filter o-ring was replaced to correct the leak, and the EDG was subsequently declared operable on April12, 2007. The cause of this event was the installation of a wrong sized o-ring during RFO 20. There were no actual safety consequences and no effect on public health and safety as a result of this event due to the fact that the EDG was functional during this time period.
3312007009 | Duane Arnold | 10/05/2007 | 12/04/2007 | ML07348017 | <strong>Loss of Essential Bus Resulted in a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On 10/05/07 at 0408, with the plant at 100% power and in Day 5 of 8 Limiting Condition for Operation (LCO) for the 'A' Emergency Diesel Generator (EDG), a loss of 480 Volt AC essential bus 1B42 occurred during a clearance application on breaker 1B4234A. The loss of bus 1B42 resulted in a loss of 'B' Emergency Service Water (ESW). The loss of 'B' ESW resulted in the 'B' EDG being incapable of performing its safety function. The loss of 'B' EDG resulted in a loss of the onsite emergency power safety function. At the time of this event, the 'A' ESW pump was inoperable, but available following pre-planned maintenance. The primary cause or the event was an equipment failure related to an underlying equipment deficiency that was exacerbated by Operator action. Essential bus 1B42 was repaired and returned to service at 0715 on 10/05/07 after completion of maintenance.
3312007010 | Duane Arnold | 11/30/2007 | 01/29/2008 | ML08031036 | <strong>Safety System Functional Failure of Alternate Preferred Offsite Power Source</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2007 at 1339, with the plant at 100% power, an analysis identified that at the minimum grid contingency voltage (98.8%), the Standby Transformer was not capable of providing adequate voltage to the 4160 volt essential buses under Loss Of Coolant Accident (LOCA) conditions. Based on the analysis, the Standby Transformer was declared inoperable. The Standby Transformer is the alternate preferred offsite power source. The preferred source is the Startup Transformer. The Startup Transformer was removed from service on April 10, 2006, May 18, 2006, December 13, 2006, and September 17, 2007. With both the preferred and alternate offsite power sources unavailable, a loss of safety function for offsite power occurred. This also resulted in a condition prohibited by Technical Specifications. The primary cause for the event was attributed to latent errors in protective relay setting calculation for the Standby Transformer. Engineering Change Package (ECP) 1846 was implemented under Modification Work Order (MWO) 1143077 to change the Standby Transformer tap setting to boost transformer secondary voltage by approximately 2.8%. The Standby Transformer was declared operable on December 14, 2007.
3312007011 | Duane Arnold | 12/01/2007 | 01/29/2008 | ML08031036 | <strong>Undervoltage Condition Resulted in the Actuation of the Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2007 at 1435, while operating at 100% power with the Standby Transformer inoperable, a fault developed on the 161 KV electrical transmission line to the Fairfax substation causing Duane Arnold Energy Center (DAEC) switchyard voltage to dip to approximately 62%. Switchyard Circuit Breakers (CB) 3110 and CB 8090 opened to clear the fault in approximately 3 cycles. At that time, the essential buses (1A3 and 1A4) were supplied from the Startup Transformer (1X003). Since the Startup Transformer is supplied directly from the switchyard, the essential buses experienced a voltage drop similar to the switchyard voltage and dropped approximately 62% for 3 cycles, resulting in the sequencing under-voltage relays sending a start signal to the Emergency Diesel Generators (EDGs). Neither EDG connected to its respective bus and loaded. The electrical transmission line fault was caused by ice and high winds. The 'A' EDG was secured at 1507 on December 1, 2007. The 'B' EDG was secured at 1514 on December 1, 2007. On December 1, 2007 at 1825, an eight-hour non-emergency report was made pursuant to 10 CFR 50.72 (ENS Number 43817).
3332007001 | FitzPatrick | 06/06/2007 | 08/06/2007 | ML07226042 | <strong>Safety Relief Valve Setpoints Outside of Allowable Tolerances</strong><br /><i>Abstract:&nbsp;</i>Review of the as-found setpoints for 10 Safety Relief Valve (SRV) [SB] pilot assemblies, removed at the end of Cycle 17, determined that 7 SRVs were outside the allowable as-found tolerance of 1145 psig +/- 34.3 psig (+/- 3%) required by Technical Specifications (TS) Surveillance Requirement (SR) 3.4.3.1. Additionally, one pilot removed at the end of Cycle 17 could not be tested as required by TS SR 3.4.3.1. This report documents the failure to meet this SR for 8 of the 11 SRVs. The effect of these SRVs being out of tolerance was analyzed and the results of this analysis show that Reactor Pressure Vessel (RPV) overpressure protection and nuclear plant safety were not adversely affected. Consequently, the safety significance of this event was minimal. Each of the seven out of tolerance SRV setpoints was determined to have a most probable cause of corrosion bonding between the SRV pilot disc and seat, a recognized industry generic problem.
3332007002 | FitzPatrick | 09/12/2007 | 12/18/2007 | ML08002000 | <strong>Manual Reactor Scram due to Blocked Circulating Water Intake Screens</strong><br /><i>Abstract:&nbsp;</i>On September 12, 2007, while the plant was operating at 100 percent power, operators inserted a manual reactor scram due to low intake flow caused by traveling water screen (TWS) blockage. All equipment responded as expected and the plant condition was stable in MODE 3, Hot Shutdown. While transitioning to Mode 4, the Reactor Protection System (RPS) automatically actuated when Reactor Pressure Vessel (RPV) level decreased to less than 177 inches above top of active fuel (TAV). This event was reported as NRC Event 43635 pursuant to 10CFR50.72(b)(2)(iv)(B) for RPS actuation (manual scram) (4 hour report) and 10CFR50.72(b)(3)(iv)(A) for specified system actuation (Group 2 PCIS isolations) (8 hour report). The cause of the manual scram was determined to be due to environmental debris induced overloading of the traveling screens, and the cause of the RPS signal was determined to be sluggish operation of the feed water startup flow control valve. The safety significance of this event is considered low and did not decrease the effectiveness of plant barriers from providing safety to the public. On October 28, 2007, while the root cause evaluation was in progress for the TWS blockage event, a similar event involving TWS screen blockage occurred that resulted in a manual scram (NRC Event 43752).
3342007001 | Beaver Valley 1 | 07/13/2007 | 09/11/2007 | ML07260001 | <strong>Valve Testing Program Change Inadvertently Leads to Condition Beyond Design Basis During Test</strong><br /><i>Abstract:&nbsp;</i>During preparation to perform a routine quarterly valve stroke surveillance procedure at Beaver Valley Power Station (BVPS) Unit No. 1, it was determined that stroking the isolation valve in the Low Head Safety Injection (LHSI) System piping was not appropriate with the plant in Mode 1 with the tested configuration. Opening this valve would permit simultaneously injecting emergency core cooling flow through both the Reactor Coolant System Hot and Cold Legs immediately following a design basis accident. This arrangement was not analyzed and could not be shown to maintain current safety analyses conclusions valid. This unanalyzed configuration had been previously entered during each quarterly valve stroke surveillance performances for the isolation valve in both trains since May, 2006.This is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B), 50.73(a)(2)(v)(D), and 50.73(a)(2)(vii). The cause was a process weakness of the procedure change, review, and approval process. The safety significance of this event was low.
3342007002 | Beaver Valley 1 | 11/27/2007 | 01/25/2008 | ML08028059 | <strong>Undetected Loss of 138 kV 'A' Phase to System Station Service Transformer Leads to Condition Prohibited by Plant Technical Specification</strong><br /><i>Abstract:&nbsp;</i>During a non-routine walkdown of the offsite switchyard on 11/27/2007, a site construction supervisor discovered that the 'A' phase conductor on a Beaver Valley Power Station Unit No. 1 (BVPS-1) three-phase 138 kV power line had broken off in the switchyard. This break occurred between the offsite feeder breaker and the line running onsite to the 'A' train System Station Service Transformer (SSST) located inside the site security fence. The station declared the 'A' train offsite power circuit inoperable and entered BVPS-1 Technical Specification (TS) 3.8.1 Condition A for one of the two required offsite circuits inoperable. Subsequent evaluation concluded that the break on the 138 kV phase 'A' occurred on 11/01/2007 based upon review of offsite and onsite computer-based grid line information. Since the undetected SSST failure that occurred on 11/01/2007 was not restored within 72 hours as required by TS 3.8.1 Action A, this was a condition prohibited by plant Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The root cause of this event is knowledge-based error. Site personnel did not fully recognize the characteristics of the three legged WYE-G / WYE-G WYE-G secondary core form transformer design, leading to a surveillance procedure weakness in detecting power line failures. With this type of transformer, it is difficult to sense a phase loss through only voltage measurements, even under moderate loading conditions. If site personnel had known the characteristics of this type of transformer, adequate indication and surveillance acceptance criteria may have been provided to detect an open phase. The safety significance of this event was very low.
3352007001 | St. Lucie 1 | 06/06/2007 | 08/03/2007 | ML07226043 | <strong>Mispositioned Service Air Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2007, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power and while performing a surveillance to verify position of administratively locked valves for the containment and shield building integrity, two containment isolation valves, (CIVs), service air header to containment isolation (non-safety class system) were found locked open, versus the required locked closed position. The valves are required to be locked closed prior to entering Mode 4 in accordance with Technical Specifications 3.6.1 and plant procedures to ensure containment vessel integrity. The valves were restored to the locked closed position upon discovery. It was estimated the valves were left open for approximately 3 weeks from the time when Unit 1 entered into Mode 4 until time of discovery. The apparent cause, along with contributing causes, was determined to be human error in which implementation of existing configuration control processes were incorrectly implemented by the Clearance Center Senior Reactor Operator (SRO). Corrective actions included re-performance of the procedure, creation and issuance of an Operations Event Report 07-008, and immediate standdown with all personnel.
3352007003 | St. Lucie 1 | 10/17/2007 | 12/14/2007 | ML07362022 | <strong>Floor Penetration Seals Outside Appendix R Design Basis</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2007, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power. In August 2007, FPL identified that certain fire penetration seal configurations in the floor of the Unit 1 Cable Spread Room (CSR) may not meet the three-hour fire rating requirements. On October 17, 2007, FPL concluded that the noncomplying seal configurations were reportable under 10 CFR 50.72 and 10 CFR 50.73 requirements. The existing penetration configurations, as installed, represent an unanalyzed condition which significantly degraded plant safety. The apparent cause was determined to be a legacy issue stemming from inadequate original construction and installation of the fire seals. At the time of discovery condition reports were initiated and general fire barrier impairments logged in accordance with the Fire Protection Program. The degraded penetrations continue to be compensated by a roving fire watch in accordance with the Fire Protection Program. Corrective actions planned include installing penetration seal configurations or restoring the barrier under the Vital AC Bus #1 and the 1A Load Test Panel. Further inspections will be conducted on similar electrical penetrations within Unit 1 and Unit 2 to determine if other occurrences of this condition may exist.
3382007001 | North Anna 1 | 01/03/2007 | 02/27/2007 | ML07065034 | <strong>Reactor Trip due to Steam Generator Low Level Coincident with a Steam Flow Feed Flow Mismatch</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2007, at 1803 hours with Unit 1 operating at 100 percent power an automatic reactor trip occurred. The initiating signal was the "B" steam generator (SG) low level coincident with a steam flow greater than feed flow mismatch caused by closure of the "B" main feed regulating valve (MFRV). This resulted in a reactor and turbine trip. Closure of the "B" main feed regulating valve was due to a shorted capacitor on the final control card that provides input to the "B" MFRV. At 1932 hours a 4 hour Non-Emergency Report was made to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(B). An 8 hour Non-Emergency Report was also made to the NRC in accordance with 10 CFR 50.72 (b)(3)(iv)(A). This event is reportable pursuant to 10 CFR 50.73 (a)(2)(iv)(A) for a condition that resulted in an automatic actuation of any engineered safety feature including the reactor protection system. This event posed no significant safety implications because the Reactor Protection System and Engineered Safety Features Actuation Systems functioned as designed following the reactor trip. Therefore, the health and safety of the public were not affected by this event.
3382007002 | North Anna 1 | 09/26/2007 | 11/26/2007 | ML07338122 | <strong>Voluntary LER - Feedwater Flow Venturi Calibration Delta from Installed Flow Discharge Coefficients</strong><br /><i>Abstract:&nbsp;</i>The main feedwater (FW) flow venturis installed on Unit 1 were removed from the piping system during the September 2007 refueling outage and sent to a vendor lab for calibration. The calibration resulted in flow discharge coefficients for the FW venturis that were higher than the installed flow discharge coefficients and led to a reduction in generated power output. The average flow coefficient for the FW venturis measured at the vendor lab was 0.758% higher than the average of the coefficients previously installed. Adjustments to the new FW venturi flow coefficients resulted in a decrease in operating power by 0.758% or about 7.4 MWe. The change in FW flow coefficients is bounded by the analysis of record for the calorimetric uncertainty and no accident analysis limits for Unit 1 were exceeded. The health and safety of the public were not affected.
3392007001 | North Anna 2 | 02/27/2007 | 04/27/2007 | ML07127027 | <strong>Damper Leak-by During PREACS Testing Results in Unanticipated Power Reduction</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2007, at 1620 hours, with North Anna Unit 2 operating at 100% power (Mode 1), Unit 2 Safeguards exhaust bypass dampers 2-HV-AOD-228-1 and 2-HV-AOD-228-2 were found to have leak-by during the performance of Periodic Test (PT) 0-PT-77.14A, Emergency Core Cooling System (ECCS) Pump Room Exhaust Air Cleanup System (PREACS) Train A Filter In-Place Test (1-HV-FL-3A). This condition rendered both trains of Safeguards exhaust inoperable. This placed Unit 2 in Technical Specification (TS) Limiting Condition of Operation (LCO) 3.0.3. Operations personnel began a unit ramp-down at 1947 hours and a 4-hour Non-Emergency Report was made to the NRC at 2215 hours, in accordance with 10 CFR50.72(b)(2)(i), for the initiation of any nuclear plant shutdown required by the plant's Technical Specifications. At 2220 hours, with Unit 2 at 32% power, the TS action was cleared after installation of a temporary modification that restored the system to OPERABLE. The cause of the event was improper linkage adjustment and actuator preload that resulted in less than full damper closure. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), 10 CFR50.73(a)(2)(v)(C), and 10 CFR 50.73 (a)(2)(vii). No significant safety implications existed because the ECCS PREACS ventilation filters were not called upon to perform their safety function and the unfiltered ECCS leakage limit was not being challenged.
3392007002 | North Anna 2 | 03/07/2007 | 06/29/2007 | ML07190020 | <strong>Automatic Start of 2H EDG on Loss of B Reserve Station Service Transformer Due To Cable Fault</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2007, at 0305 hours, with North Anna Unit 2 operating at 100% power (Mode 1), the "B" Reserve Station Service Transformer (RSST) tripped and locked out. The Unit 2 "H" Emergency Diesel Generator (EDG) automatically started on a Degraded Voltage/Under Voltage signal due to the loss of the "B" RSST. The Unit 2 "H" EDG loaded onto the Unit 2 "H" emergency bus as designed. Condition "A" of Technical Specification (TS) 3.8.1 was entered due to the inoperable RSST. An 8-hour Non-Emergency Report was made to the NRC at 0611 hours, in accordance with 10 CFR 50.72 (b)(3)(iv)(A), for an event that results in valid actuation of an EDG.The event was caused by damage during original construction installation due to a hole in the cable jacket allowing moisture intrusion resulting in corrosion and then breakage of the zinc shield tape on one of the "B" phase cables associated with the low side on the "B" RSST. On March 7,2007, at 1929 hours, the power sources were realigned and the Unit 2 "H" EDG was shutdown and placed in automatic, clearing Condition "A" of TS 3.8.1. This event is reportable pursuant to 10CFR 50.73(a)(2)(iv)(A) for an event that resulted in the automatic actuation of an EDG. No significant safety implications existed since the Unit 2 "H" EDG started as designed and re-energized the emergency bus. Therefore, the health and safety of the public were not affected at any time during the event.
3392007003 | North Anna 2 | 06/29/2007 | 08/27/2007 | ML07248067 | <strong>Automatic Reactor Trip Due to Invalid Safety Injection Relay Actuations</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2007 at 1752 hours, with Unit 2 in Mode 1 at 100% power, an automatic turbine trip, reactor trip and Phase "A" Containment Isolation occurred due to an invalid Train "B" Safety Injection actuation. Following the trip, some Train "B" Safety Injection equipment would not reset from the Main Control Room. Manual actions were performed to secure Safety Injection flow. During this process, the Pressurizer filled and spilled over to the Pressurizer Relief Tank rupturing one of the rupture disks. This allowed Reactor Coolant System water to reach the Unit 2 Containment basement. The cause of this event was the failure of zener diode CR34 on Universal card A313 located in the "B" Train of the Solid State Protection System. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for an event that resulted in the automatic actuation of the Reactor Protection System and Engineered Safety Function Systems. Unit 2 was cooled down to Mode 5 conditions at 0839 hours on June 30, 2007. The health and safety of the public were not affected at any time during the event.
3392007004 | North Anna 2 | 12/25/2007 | 05/29/2008 | ML08162043 | <strong>Automatic Reactor Trip due to Loss of Coolant Flow with Power Greater Than 30 Percent</strong><br /><i>Abstract:&nbsp;</i>On December 25, 2007 at 2110 hours, with Unit 2 in Mode 1 at 100% power, an automatic reactor trip occurred. The automatic reactor trip was a result of a loss of coolant flow with power greater than 30 percent. The loss of coolant flow was the result of the "B" Reactor Coolant Pump (RCP) motor trip. A review of the event determined that the breaker supplying the "B" RCP motor opened due to a response by the neutral over current protection relay. Post-event testing of the "B" RCP motor trip identified a "B" phase to ground fault. The ground fault of the motor winding was caused by a manufacturing defect leading to premature aging of the coil insulation system. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for an event that resulted in the automatic actuation of the Reactor Protection System and Engineered Safety Features Actuation Systems. All Engineered Safety Feature equipment responded as designed with the exception of the steam driven auxiliary feedwater pump which tripped due to actuation of the over-speed trip valve and was manually reset and subsequently placed in service. The health and safety of the public were not affected at any time during the event.
3412007001 | Fermi 2 | 10/07/2007 | 12/06/2007 | ML07346044 | <strong>Excessive Feedwater Check Valve Leakage at Containment Penetration</strong><br /><i>Abstract:&nbsp;</i>At 0114 hours on 10/07/2007, Fermi 2 feedwater line check valves, B2100F010B and B2100F076B, failed their local leak rate test (LLRT). The air leakage rate of the inboard check valve B2100F010B was 297.3 standard cubic feet per hour (SCFH), and the leakage rate of the outboard check valve B2100F076B was above the measurement capability of the leak rate monitor. The penetration (X-9B) minimum-pathway air leakage value was determined to be 297.3 SCFH which is greater than the allowable containment leakage rate (La) value of 296.3 SCFH per Technical Specification 5.5.12 and higher than the allowable secondary containment bypass leakage rate of 0.1 La or 29.63 SCFH per Technical Specification Surveillance Requirement 3.6.1.3.11. The LLRT leakage measured for this penetration also caused the calculated as-found integrated leak rate test (ILRT) to exceed acceptance criteria. The valve failures were primarily attributed to soft seat erosion by feedwater flow to the point that the seats were not providing an effective seal. It was also determined that the soft seat replacement frequency of two operating cycles was less than adequate to reliably ensure LLRT requirements are met. The soft seats were replaced for all four of the LLRT feedwater check valves during the recently completed refueling outage (RF12). The soft seat replacement frequency has also been increased to require a replacement of all LLRT feedwater check valve soft seats each refueling outage. All four valves were retested and met their associated LLRT acceptance criteria prior to restart of the unit.
3412007002 | Fermi 2 | 11/15/2007 | 01/14/2008 | ML08023071 | <strong>Automatic Initiation of Alternate Rod Insertion and Manual Reactor Scram due to Perturbations in the Reference Leg Backfill System</strong><br /><i>Abstract:&nbsp;</i>At 03:13 EST November 15, 2007, during restart of the reactor, an initiation of the alternate rod insertion/recirculation pump trip (ARI/RPT) system occurred due to an invalid reactor water level 2 (Level 2) signal from the Division 1 reactor water level instrumentation. In response, control room operators placed the reactor mode switch to shutdown inserting a manual scram. When performing a safety tag-out of the Division 1 reactor water level reference leg, an operator first cracked the isolation valve open and then immediately closed the valve. This action caused a short pressure perturbation on the level instrumentation reference leg that initiated a false Level 2 Division 1 ARI/RPT system initiation, half-scram, and a reduction in feedwater flow. Due to the short duration of the false water level signal, the High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems operated properly and did not automatically initiate, nor was an automatic reactor scram initiated. The lowest reactor vessel water level reached was 183 inches above top of active fuel, and the standby feedwater pumps were placed in service to maintain reactor water level in the desired range. The cause of the event was attributed to a failure to adhere to procedures and a less than adequate pre-job brief. The Operations Manager met with each of the Operations shifts and set expectations for the use of human performance techniques as a means to reduce human errors. The Plant Manager met with all site personnel to review recent human performance events and to reinforce expectations. There were no safety consequences as a result of this event.
3462007001 | Davis-Besse | 10/16/2007 | 12/28/2007 | ML08002001 | <strong>Station Vent Radiation Monitor in Bypass due to Faulty Optical Isolation Board</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2007, with the plant at approximately 100 percent power, it was determined that both trains of Station Vent Normal Range Radiation Monitors were inoperable for more than one hour (on two occasions) without isolating the Control Room Normal Ventilation System as required by Technical Specification (TS) 3.7.6.1. The train 2 monitor was unknowingly inoperable due to installation of a faulty optical isolation board on October 15, 2007, which caused the monitor to be in the bypass mode for approximately 13 days. This was in excess of the seven days allowed by TS 3.7.6.1 with the ventilation not isolated. The train 1 monitor was removed from service on October 16 and 22, 2007 for routine maintenance and sampling activities. On October 23, when it was determined that train 2 monitor was in bypass mode, the monitor was declared inoperable until repairs were completed on October 25. This issue, which is due to a faulty optical isolation board and inadequate testing specified in the Post Maintenance Test Manual and Quarterly Functional Test Procedures, is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the Technical Specifications, and 10 CFR 50.73(a)(2)(v)(D) as conditions that could have prevented fulfillment of a safety function for systems needed to mitigate the consequences of an accident.
3462007002 | Davis-Besse | 12/30/2007 | 02/28/2008 | ML08063027 | <strong>Decay Heat Removal Discharge Piping Void due to Inadequate Procedure for Venting following Maintenance</strong><br /><i>Abstract:&nbsp;</i>On December 30, 2007, with the plant in Mode 5, a step decrease of approximately six inches in the Reactor Coolant System Pressurizer was observed when aligning Decay Heat Removal (DHR) Pump 1 suction from Low Pressure Injection mode to DHR mode. The alignment was suspended, and a piping void was discovered in the discharge piping of DHR Pump 1. The void was vented from the high point vent valve inside Containment to restore train Operability. It was determined that this void was formed during on-line maintenance on October 31, 2007, due to an inadequate procedure for recovering the DHR train following on-line maintenance. This void redered DHR Train 1 inoperable for approximately 59 days due to the inability to successfully meet Technical Specification Surveillance Requirement 4.5.2.b, which requires the train to be full of water while in Modes 1 through 3. An evaluation determined DHR Train 1 remained capable of performing all required safety functions as a result of the estimated 17 cubic feet of voided piping that existed while the plant was operating. This issue is being reported in accordance with 10CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by the Technical Specifications. The procedure will be revised to properly vent the system following maintenance, and procedures for other standby safety systems will be reviewed for similar issues.
3482007001 | Farley 1 | 04/26/2007 | 06/22/2007 | ML07176033 | <strong>Technical Specification 3.8.1 Violation Due to Failure of Breaker/Mechanism-Operated Cell (MOC) Switch</strong><br /><i>Abstract:&nbsp;</i>While performing Emergency Diesel Generator (EDG) 1C Operability Test on April 26, 2007, FNP determined that the mechanism-operated cell (MOC) switch of the 1C EDG output breaker 1-DH07 was not being fully activated when the breaker was closed. This resulted in the EDG being declared inoperable. An inspection determined that the MOC switch rotation was not sufficient to fully engage the normally open contacts. The event was the result of a fit-up discrepancy during replacement of the existing Allis Chalmers breakers with new Cutler Hammer breakers within the Allis Chalmers switchgear. The fit up discrepancy went unrecognized because of inadequate procedural guidance on how the replacement breakers were to be setup during initial installation and testing. Because the breaker had been in this condition since November 1, 2006, this event was determined to be reportable per IOCFR50.73(a)(2)(i)(B), "any operation or condition which was prohibited by the plant's Technical Specifications." Due to the fact that the opposite train 1B EDG was unavailable during maintenance activities on five occasions during this time period, the event is also reportable per 10CFR50.73(a)(2)(v)(B), "any event or condition that could have prevented the fulfillment of the safety function of structures or systems which are needed to remove residual heat." At the time ofdiscovery, the 1 B EDG was fully operable and available. After the the event, plant procedures were updated to provide detailed instructions on setup of the MOC switches. All installed Cutler Hammer breakers with MOC switches that provide essential functions have been adjusted per the new procedural guidance and have been functionally tested.
3482007003 | Farley 1 | 09/05/2007 | 11/14/2008 | ML08319081 | <strong>Component Cooling Water Pump Breaker Failures</strong><br /><i>Abstract:&nbsp;</i>From September 4, 2007 at 17:00 until September 5, 2007 at 00:15, the Farley Unit 1 Component Cooling Water (CCW) system [CC] was inoperable due to failures of two different types of breakers, concurrent with a planned maintenance outage on the swing pump. Although Pump 1A (B Train pump) was in fact in operation during this period, no assurance of CCW pump capability to start on demand existed. The 1C (A Train) CCW pump breaker and the 1A (B Train) CCW pump breaker failed to start on independent start demands, associated with a period in which the 1B CCW (swing) pump was out of service for maintenance. The 1A CCW pump breaker was an Allis-Chalmers breaker scheduled for replacement which failed due to wear related degradation. The 1C CCW pump breaker was a new Cutler-Hammer breaker recently installed which failed due to a combination of operator manipulation of the breaker foot pedal and inadequate linkage margin caused by the setup of the breaker linkage. To ensure proper operation of Cutler-Hammer breakers, operator guidance for breaker pre-start checks has been revised. Both the failed Cutler-Hammer breaker and the failed Allis-Chalmers breaker were replaced. All Allis Chalmers 4kv breakers supplying safety related loads were replaced by March 31, 2008. To provide increased reliability margin, all installed Cutler Hammer breakers in safety related applications will be verified to be within revised linkage setup specifications by August 31, 2009. All Cutler Hammer breakers scheduled for installation in safety related applications will be verified to be within revised linkage setup specifications prior to installation.
3532007001 | Limerick 2 | 03/10/2007 | 05/09/2007 | ML07130008 | <strong>Scram Discharge Volume Vent and Drain Valves Opened due to Fuse Removal</strong><br /><i>Abstract:&nbsp;</i>The scram discharge volume vent and drain valves opened with a scram signal present during application of a clearance for maintenance on the reactor protection system contactors and scram air header during an outage. The event was caused by a clearance planning error that resulted in removal of fuses to the back-up scram valves without necessary precautions. The back-up scram valves re-positioned resulting in restoration of the scram air supply to the scram discharge volume vent and drain valves causing them to open. This created a breach of primary containment in Operational Condition 3 (Hot Shutdown) and discharge of reactor coolant into the liquid radwaste system. A System Specific Tagging Guide has been implemented to address backup scram valve fuse removal. The guide requires closing the manual valves in the scram discharge volume vent and drain lines prior to removing the fuses.
3532007002 | Limerick 2 | 03/12/2007 | 05/11/2007 | ML07131011 | <strong>Automatic Actuation of Main Condenser Low Vacuum Isolation Logic During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>Two of four channels of main condenser low vacuum isolation logic automatically actuated while breaking main condenser vacuum during a refueling outage. The main steam isolation valves were previously closed but would have automatically isolated on the actuation of the two channels. This event was caused by a procedure performance error that resulted in only two of four low vacuum isolation channels being bypassed when four channels where to be bypassed by procedure. The procedure has been revised to address a weakness involving two actions in a single step. The procedure now provides four steps with individual sign offs for bypassing the four low vacuum isolation channels.
3532007003 | Limerick 2 | 04/24/2007 | 06/22/2007 | ML07173027 | <strong>Automatic Actuation of the Reactor Protection System at Power</strong><br /><i>Abstract:&nbsp;</i>An invalid feedwater runback demand was initiated due to a failure of a redundant reactivity control system (RRCS) circuit card coincident with surveillance testing on the system. The feedwater runback resulted in an automatic actuation of the reactor protection system due to a valid reactor low-level condition. The high pressure coolant injection (HPCI) and reactor core isolation cooling (RCIC) systems initiated and injected on the low level condition and successfully restored reactor level. HPCI and RCIC were placed in manual flow control mode during the level recovery due to flow oscillations caused by incorrect flow controller gain and reset settings. The failed RRCS circuit card was replaced and tested successfully. The HPCI and RCIC flow controller gain and reset settings were adjusted to the required settings to ensure stable automatic flow control.
3542007001 | Hope Creek | 01/29/2007 | 03/30/2007 | ML07102014 | <strong>Low Reactor Water Level Scram</strong><br /><i>Abstract:&nbsp;</i>On January 29, 2007 during a plant startup from a planned outage with the reactor at 21% power and the main generator synchronized to the grid, an automatic reactor scram occurred due to low reactor water level. The root cause of the scram was a failure of the instrument tap weld at the flow nozzle for the C Reactor Feed Pump (RFP) Minimum Flow Line. This failure caused reduced indicated flow to the "C"RFP minimum flow control system logic and an increased minimum flow valve opening demand signal. As a result of these conditions reactor level could not be maintained and fell below the reactor low-level set point. Corrective actions include repair of the affected weld and an extent of condition review to identify other potential weld deficiencies.
3542007002 | Hope Creek | 05/29/2007 | 01/16/2008 | ML08025002 | <strong>Performance of Vital Bus Surveillance Caused a Partial Loss of Feed Resulting in a Manual Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2007 while operating with the reactor at 100% power and the main generator synchronized to the grid, a manual scram was initiated in anticipation of low reactor water level condition. An unexpected slow (dead bus) transfer of a 4 KV Class 1-E bus from the normal to alternate source occurred during monthly relay testing. The slow (dead bus) transfer and subsequent loss of a non-safety related motor control center (MCC) resulted in a loss of feed water followed by a reactor scram. A personnel error initiated the slow bus transfer and a low margin condition asscciated with the reactor feed pump oil system design caused a loss of 2 reactor feed pumps. As a result of these conditions reactor level could not be maintained and operators took the action to manually scram the reactor. After the scram, reactor water level lowered to Level 2 and a valid ECCS initiation signal caused HPCI and RCIC to start and inject to the core. The ECCS injection required a 4-hour report that was transmitted to the NRC in accordance with 10 CFR 50.72 (b)(2)(iv)(A). Corrective actions included revising the surveillance procedure to require testing only be performed on an open breaker and to verify that the relay contacts are in the correct state upon completion of the surveillance. Operating procedures were revised to maintain both Reactor Feedwater Pump (RFP) Lube Oil pumps operating for each RFP.
3542007003 | Hope Creek | 07/01/2007 | 08/30/2007 | ML07249020 | <strong>Grab Samples Not Performed As Required by Technical Specification 3.3.7.1</strong><br /><i>Abstract:&nbsp;</i>On July 01, 2007, offgas flow started rising. In anticipation of offgas flow approaching its upper limit of 75 standard cubic feet per minute (scfm) for instrument operability, Operations directed Radiation Protection (RP) to enter correction factor changes into the Offgas Pretreatment Radiation Monitoring System (RMS) as directed by Note 4 of the Main Condenser Vacuum abnormal operating procedure (AOP). Offgas Pretreatment RMS must be declared inoperable when offgas flow increases to 75 scfm, and can be declared operable once the required correction factor changes are entered into the RMS. On July 04, 2007, when offgas flow decreased below 75 scfm, Operations requested RP to remove the correction factors that had been entered into the Offgas Pretreatment RMS on July 01, 2007. RP communicated to Operations that no correction factors were entered into the Offgas Pretreatment RMS, instead, alert setpoint changes had been made. Operations then declared the Offgas Pretreatment RMS inoperable, and had been inoperable since Offgas Flow went above 75 scfm on July 01, 2007. Tech Spec 3.3.7.1 required grab samples were not performed during the period of inoperability. The root cause of this event was inadequate procedural direction to guide the RP technicians to perform the action as required by the Operations AOP. The RP procedure, Control of Radiation Monitoring System Setpoints, will be revised to include guidance to make temporary correction factor changes to the RMS when required.
3542007004 | Hope Creek | 07/31/2007 | 09/28/2007 | ML07284004 | <strong>HPCI System Inoperability due to Feedwater Injection Valve Failure to Stroke Open</strong><br /><i>Abstract:&nbsp;</i>On 7/31/2007, at 0051 hours with the quarterly In service Test (IST) for High Pressure Coolant Injection(HPCI) system valves in progress, HPCI Feedwater injection valve BJ-HV-8278 failed to stroke open. The valve tripped on electrical overloads 10 seconds after the open pushbutton was depressed. Failure of the valve to open resulted in HPCI inoperability and an unplanned 14-day hot shutdown Limiting Condition for Operation (LCO). HPCI was inoperable from May 29, 2007 to July 31, 2007. The cause of the HPCI Feedwater injection valve not opening on July 31, 2007 was that it was thermally bound as a result of a short duration HPCI injection event on May 29, 2007. The root cause is that thermal binding was not anticipated during the design of the system. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 50.73 (a)(2)(v)(D).
3612007001 | San Onofre 2 | 06/20/2007 | 08/17/2007 | ML07240028 | <strong>Instrument Air System Failure Results in Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2007, at about 2240 PDT, Unit 2 was operating in Mode 1 at about 96 percent power when a line in the instrument air system separated at a soldered connection. The resulting loss of Instrument Air (IA) pressure caused the loss of control of the Steam Generator Feedwater Regulating valves. One steam generator level rose uncontrolled necessitating the control room Operators to trip the reactor manually at about 2250 PDT, June 20, 2007. Operators subsequently manually tripped the Main Feedwater pumps to stop excess feedwater to the steam generators and actuated the Auxiliary Feedwater System. As designed, loss of IA system pressure isolates cooling water to the normal containment coolers and Operators manually started the Containment Emergency Cooling Units as a conservative measure. Southern California Edison (SCE) reported this occurrence to the NRC Operations Center at 0024 PDT on June 21, 2007 (NRC Event Log Number 43435). SCE is providing this follow-up written report in accordance with 10CFR50.73(a)(2)(iv)(A). The soldered connection failed due to improper fit and slow acting corrosion. SCE inspected the IA system piping and installed pipe clamps to strengthen piping joints where needed to add additional margin.
3612007002 | San Onofre 2 | 06/21/2007 | 08/17/2007 | ML07240028 | <strong>Operator Error Results in a Missed Shutdown Margin Verification Required by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2007, Unit 2 was operating in Mode 1 at about 96 percent power. At about 1030 PDT, one channel of source range monitoring did not pass its surveillance requirements and was declared inoperable. Consistent with plant procedures, Operators placed a Limiting Condition for Operation Action Requirements/Equipment Deficiency Mode Restraint (LCOAR/EDMR) tag next to the channel indicator (the channel indicator continued to function). At about 2240 PDT the same day, a line in the instrument air system separated at a soldered connection joint. Plant Operators manually tripped the unit, entering Mode 3. The details of that event are provided in LER 2-2007-001. When completing the post trip actions required by Emergency Operating Instructions, a control room operator failed to notice that one channel of source range monitoring channels was out of service and failed to complete the Shutdown Margin verification by 0250 PDT, June 21, 2007, required by Technical Specification 3.3.13, Action A.2. SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). The cause of this event is individual personal error. The Reactor Operator (RO) failed to respond to the LCOAR/EDMR tag posted next to the Startup Channel indicator. Southern California Edison has coached the Operator and discussed this event with all other Licensed Operators.
3612007003 | San Onofre 2, San Onofre 3 | 10/02/2007 | 11/27/2007 | ML07334063 | <strong>Saltwater Cooling System Surveillance Performed Incorrectly due to Improper Flow Meter Calibration by M&TE</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) Surveillance Requirement (SR) 3.7.8.3, Salt Water Cooling System, requires inservice testing (IST) for each SWC pump in the flow path servicing safety related equipment. On October 2, 2007 (discovery date), SCE determined the installed SWC flowmeters had not been properly calibrated using the portable M&TE and that TS SR 3.7.8.3 had not been properly performed. Therefore, SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(i)(B). SCE determined that the installed flowmeters were incorrectly adjusted due to errors in the set-up of the M&TE portable flowmeters. The work plan for performing the annual calibration of the installed flowmeters was not sufficiently detailed, relying on the skill of the individual technician. Also, plant personnel did not have adequate knowledge of the set-up and use of the M&TE portable flowmeters that are used to calibrate the installed flowmeters used in ISTs. TS SR 3.7.8.3 has been completed for all eight SWC pumps with satisfactory results. SCE is reviewing the site training on the use of the M&TE portable flowmeters and will enhance training where appropriate. Because the operability of the SWC system was unaffected by this occurrence, there was no safety significance to this event.
3612007005 | San Onofre 2 | 03/01/2007 | 10/16/2008 | ML08291013 | <strong>Loose Electrical Connection Results in Inoperable Pump Room Cooler</strong><br /><i>Abstract:&nbsp;</i>On 3/1/07 with Unit 2 at about 99 percent power, the Spent Fuel Pool (SFP) Pump [DA] Room Emergency Air Conditioning Fan was started for air flow measurement and tripped on thermal overload. SCE found the phase A connection loose with evidence of arcing. SCE concluded this caused high current in the other 2 phases and the trip. SCE subsequently determined the loose connection likely resulted from incomplete maintenance on 10/27/06 when the thermal overloads were replaced. SCE considers the fan was inoperable from 10/27/06 to 3/1/07. The Bases for Technical Specification 3.7.10, Emergency Chilled Water [KM], requires SCE to enter the applicable Action for supported equipment if an inoperable room cooler is not restored within 14 days. This Action was Licensee Controlled Specification 3.7.106.A. The inoperability was not recognized and the Action was not entered. Failure to enter this Action does not violate TS, but it does not meet its expectations. SCE verified that there was no increase in decay heat load in the SFP from 10/27/06 to 3/1/07. Therefore, there was little safety significance to the event. SCE identified this event in an 8/18/08 audit of previous occurrences of loose electrical connections. The audit and assessment for reportability is part of corrective actions resulting from previous events (LER 2- 2008-006, submitted 9/17/08 and LER 3-2005-01, submitted 8/23/05).
3612007006 | San Onofre 2, San Onofre 3 | 06/09/2007 | 05/07/2009 | ML09148018 | <strong>Loose Electrical Connection Results in One Train of Emergency Chilled Water (ECW) System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 6/9/07 with Units 2 and 3 at about 99 percent power, SCE found the control panel for the Train A Emergency Chiller, E336, de-energized. In a separate power panel, SCE found a cable pulled out of the breaker supplying the 120VAC. The chiller provides a safety function to both units. SCE determined the retaining screw anchoring the cable to the supply breaker in the power panel was stripped, preventing securing the cable tightly. The loose connection was most likely due to over tightening the screw on 6/28/05 when the breaker was replaced. From 6/28/05, Emergency Chiller panel was observed to be energized each shift. However, SCE has concluded that it may not have performed its safety function in a seismic event, rendering it inoperable. Technical (TS) 3.7.10, ECW System [KM], requires restoring an inoperable train within 14 days, else initiate shutdown. Failure to enter this action violated the TS. SCE replaced the breaker and returned the chiller to Operable. There was very little risk significance to the condition.
3612007007 | San Onofre 2 | 02/13/2007 | 03/25/2010 | ML10088032 | <strong>Inoperable SFP Cooling Pumps Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2007, at 1249 PST, the Train B Spent Fuel Pool (SFP) cooling pump tripped on over current. The Train A SFP cooling pump was out of service for scheduled maintenance at the time. With both SFP cooling pumps inoperable, the plant entered the loss of SFP cooling Abnormal Operating Instruction. Train B SFP cooling pump was successfully restarted at 1407 PST, restoring SFP cooling. The temperature of the SFP increased from 71.5 to 73.0 degrees F while the pump was off. SCE determined the cause of the over current trip was a high temperature in the motor control center (MCC) due to malfunctioning of a heater thermostat in the MCC. This event was not reported previously because it was not considered a loss of safety function at the time of the event. Based on recent NRC guidance, SCE is reporting this occurrence under 10 CFR 50.73(a)(2)(v)(B) as a loss of safety function to remove decay heat. The safety significance of this event is minimal since the temperature of the SFP remained well below the maximum allowed 140 degrees F, all applicable licensee controlled specifications were met, and alternate methods of cooling were availablif required.
3622007001 | San Onofre 3 | 12/22/2007 | 02/22/2008 | ML08057008 | <strong>Failure to Declare Emergency Diesel Generator Inoperable and Enter TS Action</strong><br /><i>Abstract:&nbsp;</i>On 12/22/08, SCE performed a surveillance test for Emergency Diesel Generator (EDG) 3G002. Results were initially assessed as acceptable although unusual behavior was observed in some data parameters. A subsequent surveillance on 12/31/07 found the EDG inoperable due to a failed speed probe. Although not known at that time, SCE should have taken the Actions required by TS 3.8.1 for an inoperable EDG. SCE repaired the speed probe for EDG 3G002 and returned it to operable status on 1/1/08. SCE also inspected the speed probes for the opposite train EDG at Unit 3 (3G003) and both EDGs at Unit 2 and verified all other speed probes were unaffected and remained operable. SCE's root cause evaluation is ongoing. SCE may implement additional corrective actions when the RCE is completed. During this occurrence, San Onofre remained connected to offsite power. Addtionlly, the opposite train EDG, 3G003, remained operable and capable of performing its required safety function. Therefore, the delay in declaring EDG 3G002 inoperable had no safety significance.
3622007004 | San Onofre 3, San Onofre 2 | 10/18/2007 | 12/19/2007 | ML07362044 | <strong>Technical Specification Violation Caused by Moisture Contamination in Hydraulic Dump Valve Solenoids</strong><br /><i>Abstract:&nbsp;</i>On October 9, 2007, SCE initiated a shutdown of Unit 3 for a maintenance outage. During the shutdown, Unit 3 Main Feedwater Isolation Valve to Steam Generator (SG) E-088 and Main Feedwater Block Valve to SG E-089 failed to close. On October 18, 2007, during surveillance testing, the Main Steam Isolation Valve on SG E-089 failed to stroke closed when the train B Hydraulic Dump Valve (HDV) solenoids were de-energized (the valve stroked satisfactorily on the train A HDV). On October 20, 2007 (date of discovery), SCE determined the failure mechanism to be internal corrosion of the HDV solenoid valves due to moisture contamination at the HDV vendor. Consequently, SCE concluded the affected valves had been inoperable for longer than allowed by their applicable specification and is reporting these events under 10 CFR 50.73(a)(2)(i)(B) and 10CFR50.73(a)(2)(vii). SCE shutdown the operating unit (Unit 2) and tested other similar valves in both units and determined the remaining similar valves were operable. SCE replaced all of the contaminated solenoids in both Units.
3642007001 | Farley 2 | 10/03/2007 | 11/19/2007 | ML07325009 | <strong>Unit 2 Reactor Trip During Unit 1 Main Generator Differential Lockout Relay Testing</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2007 at 1410, with the reactor at 100% power, Unit 2 automatically tripped due to a loss of power to the Unit 2 8-train electrical distribution system [EA]. This occurred during a Unit 1 refueling outage while performing testing on Unit 1 Main Generator Differential Lockout relay. As a result, the supply breaker to 2B Startup Transformer was inadvertently tripped. The loss of Unit 2 B-train 4160V power ultimately led to a loss of power to Reactor Coolant Pump (RCP) Breaker Indication (1 out of 3 coincidence). The reactor tripped per design. All safety systems functioned as designed. This event was caused by a testing procedure that lacked a step to block the High Voltage Switchyard (HVSY) breaker failure sequence relays. The failure to block resulted in the breaker failure sequence relays actuating. The breaker failure sequence relays tripped the associated HVSY breakers, which then deenergized the 2B Startup Transformer. Loss of the 2B Startup Transformer ultimately led to loss of RCP Breaker Indication relay, resulting in Unit 2 reactor trip. The subject procedure has been revised.
3662007001 | Hatch 2 | 02/12/2007 | 04/11/2007 | ML07102049 | <strong>Main Steam Isolation Valves Fail Local Leak Rate Testing Due to Out of Specification Internal Tolerances</strong><br /><i>Abstract:&nbsp;</i>On February 12, 2007 Hatch Unit 2 was in the refueling mode with fuel in the vessel and the reactor cavity flooded for refueling operations. Personnel were performing local leak rate testing (LLRT) on the Main Steam Isolation Valves (MSIVs), These tests determined, for both the B penetration (2B21-F022B (inboard) and 2B21-F028B (outboard)) and the C penetration (2B21-F022C (inboard) and 2B21-F028C (outboard)), that the minimum pathway leakage for each of these penetrations exceeded the values specified in the plants Technical Specifications. The maximum leakage rate allowed for all of the main steam lines is 250 standard cubic feet per hour (scfh). The as-found measured LLRT minimum pathway leakage for the B penetration was 294 scfh, and for the C penetration was 280 scfh. The total minimum pathway leakage through all four main steam lines was 574 scfh. The most likely direct causes of the MSIV minimum pathway leakages exceeding the values specified in theTechnical Specifications were out-of-specification internal valve tolerances and dimensions. It was determined that the probability of the MSIVs seating leak-tight will be reduced if the clearances between the in-body valve guides and the main disc are too large, or if anomalies in the seating areas for these valves exist, such as incorrect seating angle, width of the seating surface, or high or low spots in the seating surfaces. Internal inspection of the MSIVs determined that one or more of these conditions existed in each of the four referenced MSIVs. Each of the anomalies identified were corrected by machining or by installing an oversize disc that reduced the clearances in the valve. Review of the plants maintenance practices determined that checking these clearances was not part of the plants normal maintenance activities. The applicable plant procedure has been revised to address this issue.
3662007002 | Hatch 2 | 02/18/2007 | 04/18/2007 | ML07110047 | <strong>Excessive Feedwater Check Valve Leakage due to Valve Internal Clearances Being out of Tolerance</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2007 Hatch Unit 2 was in the refueling mode with fuel in the vessel and the reactor cavity flooded for refueling operations. Personnel were performing Local Leak Rate Testing (LLRT) on the Feedwater Check Valves. These tests determined that leakage from two of the three valves (2B21-F010A and 2B21-F077A) that comprise the 'A' Feedwater penetration pathway exceeded the acceptance criteria specified in the plant's LLRT procedure. Analysis was performed that determined the most likely direct cause of the failure of the 2B21-F010A valve is attributed to the as-found clearances being out of tolerance. The cause of the failure of the 2B21-F077A valve is attributed to normal wear. Corrective actions for the 2B21-F010A Included fabricating a new anti-extrusion ring to tighten the clearances for both sides of the disc to within required tolerance. Corrective actions for the 2B21-F077A included Lars-lapping of the in-body seat and disc, hinge pin replacement, and clean-up of the stuffing box.
3662007003 | Hatch 2 | 03/01/2007 | 04/30/2007 | ML07121013 | <strong>Excessive Leakage on Secondary Containment Bypass Valves Due to Foreign Material</strong><br /><i>Abstract:&nbsp;</i>On 3/1/2007, Unit 2 was in the Refuel mode with fuel in the reactor vessel. Personnel were performing local leak rate testing (LLRT) on the drywell floor drain sump isolation valves. These tests determined that the minimum pathway leakage associated with containment penetration isolation valves 2G11-F003 and 2G11-F004 had exceeded the associated LLRT acceptance criteria.The valves are classified as secondary containment bypass valves since the drain piping is routed to the Radwaste Building which is outside the secondary containment boundary and is, consequently, not served by the standby gas treatment system. The cause of the valve test failures was foreign material intrusion. Corrective actions for this event included removing the foreign material, cleaning and inspecting the valves, adjusting the pneumatic operator on 2G11-F003, and re-testing the valves. Cleaning and inspection of the drywell floor drain sumps was conducted to provide further assurance that measures taken for foreign material exclusion were effective. An outage repetitive task was also created to ensure cleaning and inspection of the drywell floor drain sumps is performed during each refueling outage.
3662007004 | Hatch 2 | 03/09/2007 | 05/03/2007 | ML07123040 | <strong>Leak in Reactor Pressure Boundary Due To Failure of a Socket Weld</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2007, at 1230 EST, Unit 2 was in the Cold Shutdown mode. At that time, a leak was identified in a one-inch socket weld elbow, located below the condensing chamber on the "D" Main Steam Line. The Technical Specification (TS) definition of pressure boundary leakage is "leakage through a non-insoluble fault in the reactor coolant system." Due to its location, the leak met this definition. Based upon inspection of the weld and adjacent area, it was determined that the leak existed when the Unit was in mode 1. the TS allows no pressure boundary leakage in mode 1. The cause of the leak is failure of the socket weld due to high cycle fatigue. Corrective actions for this event included replacing the failed weld and adjacent welds with high cycle fatigue resistant welds and inspection of similar piping to confirm no other leaks.
3662007005 | Hatch 2 | 03/15/2007 | 05/14/2007 | ML07134031 | <strong>High Pressure Coolant Injection System Inoperable due to Water Intrusion into the Oil System</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2007 at approximately 1532 EDT, Unit 2 was in the start-up mode at a reactor pressure of approximately 155 psi and estimated power level of one percent. The low pressure start-up testing of the High Pressure Coolant Injection (HPCI) system was in progress when the system failed to perform as required. Operations personnel entered the applicable Technical Specification for HPCI inoperable. Troubleshooting was performed to determine the cause of the failure and the system was repaired. Specifically the Electronic Governor Remote (EGR), Reduction Gear Unit, and the Duplex Filters were all replaced. The oil in the HPCI turbine was also replaced. The low pressure start-up testing of the HPCI system was re-performed successfully and the HPCI system was returned to service at 1435 EDT on March 16, 2007. This event was caused by corrosion of the EGR Actuator internals. The corrosion of the EGR internals is attributed to an event that occurred earlier in the refueling outage. During that event, water was introduced into the HPCI bearing oil system through a path created by a tagout. The root cause associated with the tagout event is that the drafter and reviewer of the tagout did not adequately address the system or functional impact associated with the components that were tagged or removed from service.
3662007006 | Hatch 2 | 04/17/2007 | 06/13/2007 | ML07165009 | <strong>Corrosion Induced Bonding Results in Safety Relief Valve Lift Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2007, Unit 2 was at 100 percent power. On that day it was identified during bench testing that two Safety Relief Valves (SRVs) experienced setpoint drift that exceeded the allowable plant Technical Specifications (TS) limit. At the conclusion of bench testing, a total of five of the eleven SRVs were identified as having setpoint drift in excess of the TS limit. The root cause of the SRV setpoint drift is corrosion-induced bonding between the pilot disc and seating surface. Immediate corrective actions for this event included replacement of all of the eleven valves with refurbished pilot valves. In addition, the pilot discs on all of the eleven valves that were removed for testing will be replaced with pilot discs made from Stellite 21, which is more resistant to corrosion bonding in this application. Evaluation of additional actions to further improve SRV performance will be tracked under the plant's corrective action program.
3662007007 | Hatch 2 | 05/18/2007 | 07/13/2007 | ML07197018 | <strong>High Pressure Coolant Injection System Inoperable due to Clogged Valve Causing Water Intrusion into the Oil System</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2007 at 17:45 EDT, Unit 2 was in Mode 1 at 2804 CMWT, 100 percent power. While investigating the source of oil on top of the Unit 2 High Pressure Coolant Injection (HPCI) Turbine Skid, Maintenance personnel found water in the HPCI lube oil system. Operations personnel entered the applicable Technical Specification for HPCI inoperable. The water intrusion was attributed to a clogged bracket drain valve which caused water to accumulate in the mechanical seal cavity. The water came from a small leak in the mechanical seal, and apparently entered the oil system by flowing past the thrust bearing oil deflector. The deflector forms one of the seal cavity walls and is not designed to keep standing water out of the bearing housing. The HPCI oil system was drained and flushed; the duplex filter and the Electronic Governor (EGR) were replaced. In addition, the drain valve was removed from the system to prevent future water accumulation. Testing of the HPCI system was performed on May 19, 2007, and the system was declared operable at 19:49 EDT. This event was caused when water backed up in the mechanical seal cavity due to a clogged drain valve, and then migrated into the oil system. The root causes of the water intrusion are: 1) a less than optimal component functional design; 2) an approved modification proposal to remove the valves had not been implemented as of the time of this event; and 3) a corrective action to periodically clean the drain line in order to keep the drain valves from clogging was unsuccessful.
3662007008 | Hatch 2 | 08/07/2007 | 10/05/2007 | ML07278018 | <strong>Reactor Scram on Low Reactor Water Level due to Partial Loss of Condensate System</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2007 at 15:06 EDT, Unit 2 was at 100 percent power in Mode 1 at 2804 CMWT. At this time a partial loss of the Condensate System caused low Feedwater flow resulting in a Reactor Protection System (RPS) actuation on Low Reactor Water Level and a Group 2 Primary Containment Isolation System (PCIS) isolation. The investigation determined that the loss of condensate system was caused by the loss of the 2D 4160V switchgear. The 2D bus provides power to the 2A and 2B Condensate and Condensate Booster Pumps. The loss of the 2D 4160V bus was the result of the inadvertent actuation of the over-current relay protecting one of the three phases of the normal supply breaker. This relay had been removed from services as part of a routine I&C periodic relay calibration. During reinstallation of the relay cover following completion of the calibration, the relay actuated tripping the normal supply breaker for the 2D 4160 switchgear and de-energizing the bus providing power to the pumps. All systems functioned per their design given the water level transient. The root cause of this event was determined to be ineffective execution of a screening procedure written to determine scram/transient potential of I&C activities. The screening procedure was executed for the calibration of the overcurrent relay and errantly determined that there was no reactor trip potential when performing the procedure on-line and did not include a precaution for installation of relay cover. The procedure has been revised to correct these inadequacies and all I&C procedures previously screened will be re-evaluated.
3682007001 | Arkansas 2 | 01/25/2007 | 03/26/2007 | ML07093041 | <strong>Completion of a Plant Shutdown Required by Technical Specifications Because a Control Element Assembly Dropped into the Core as a Result of a Failed Upper Gripper Coil</strong><br /><i>Abstract:&nbsp;</i>At 1717 CST, on January 25, 2007, Arkansas Nuclear One, Unit 2 (ANO-2), initiated a plant shutdown as required by Technical Specifications because a Control Element Assembly (CEA) had dropped into the core and could not be returned to within seven inches of the other CEAs in its group. At 1821, the reactor was manually tripped in accordance with the plant shutdown procedure. All CEAs inserted into the core, as designed. CEA 35 dropped into the core at 1109 on January 25, during maintenance activities associated with an abnormal voltage indication on the subject CEA. CEA 35 fell into the core as a result of the failure of its upper gripper coil which caused the circuit breakers that feed the CEA to trip. Repairs were completed on the affected CEA and the plant was returned to power operation at 0200 CST, on February 2, 2007. The preliminary root cause of the coil failure was determined to be thermal degradation of the coil insulation over its twenty year service life that resulted in electrical shorting within the coil. It is believed that periods of elevated voltage on the coil in the 1992-1993 time frame may have accelerated the degradation. During the next refueling outage, additional gripper coils will be removed and examined to finalize the root cause.
3692007001 | McGuire 1, McGuire 2 | 01/17/2007 | 03/16/2007 | ML07086076 | <strong>The Completion Time of Technical Specification 3.8.4 Condition A was Exceeded on May 12, 2005</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time this historical condition was identified, Unit 1 and Unit 2 were in Mode 1 (Power Operation) at 100 percent power. Event Description: On January 17, 2007, Engineering identified that a value recorded during performance of Technical Specification (TS) Surveillance Requirement (SR) 3.8.4.5 on May 12, 2005 for vital battery EVCC did not meet the acceptance criteria of the SR. Corrective actions for the failed TS SR were not performed within the COMPLETION TIME allowed by TS 3.8.4 CONDITION A. This historical event, which constitutes a condition prohibited by Technical Specifications, is reportable per 10 CFR 50.73 (a)(2)(i)(B). This event was determined to be of no significance to the health and safety of the public. Event Cause: The cause for the failure to recognize and report not meeting the TS SR acceptance criteria was human error. The in-plant investigation determined that the value was recorded in error and was not truly outside the TS SR acceptance criteria. Corrective Actions: The importance of reporting any data that does not met an acceptance criteria has been conveyed to Maintenance personnel. Affected procedures will be reviewed and enhanced to clearly delineate that the procedure affects TS or Selected Licensee Commitments (SLC) and require a signature certifying acceptance criteria are met.
3692007002 | McGuire 1 | 03/22/2007 | 05/18/2007 | ML07150019 | <strong>Failure of Containment Floor and Equipment (CFAE) Sump Discharge Outside Containment Isolation Valve (CIV) to Fully Close.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of discovery, Unit 1 was in No Mode (Shut Down) at 0 percent power and Unit 2 was in Mode 1 at 100 percent power. Event Description: On March 22, 2007, 1WL-65B CFAE sump discharge outside CIV failed the Isolation Valve Leak Rate Test (LRT) conducted during the Unit 1 end of cycle 18 refueling outage. Follow-up investigation and testing determined CIV 1WL-65B leakage exceeded acceptance criteria for total reactor building bypass leakage and was inoperable during Unit 1 Cycle 18 Operation. In addition, there was 88.15 hours during the cycle when the redundant inside CIV 1WL-64A did not have an operable emergency power source; therefore, both containment isolation valves for penetration M-374 were simultaneously inoperable for that 88.15 hour period. Since these conditions existed during a Technical Specification Mode of applicability, the event is reportable as a condition prohibited by Technical Specifications and a condition that could have prevented fulfillment of a safety function. Safety Analysis has concluded that this condition was not significant with respect to the health and safety of the public. Event Cause: 1WL-65B was over rotated during manual operation causing the overload clutch to slip past limit switch settings. When this occurs, the open and closed limit switch settings are shifted. Consequently, the open limit actuates later in the open direction and the closed limit switch actuates earlier in the closed direction which results in leakage past the seat. Human Error resulted in the condition going undetected when the requirement to LRT the valve following manual operation was waived. Corrective Action: Corrective actions will place more stringent control on manual operation of Rotork operated diaphragm valves.
3692007003 | McGuire 1 | 04/15/2007 | 06/14/2007 | ML07180031 | <strong>Inoperable Source Range Neutron Flux Monitors During Mode 6 and Core Alterations.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Unit 1 was in Mode 6 (Refueling) at 0% power, and Unit 2 in Mode1 (Power Operation) at 100% power. Event Description: On April 15, 2007, while Unit 1 was in Mode 6, core alterations occurred with only one of the two required source range neutron flux monitors operable. Operators were unaware that only one of the source range neutron flux monitors was able to generate an audible high flux at shutdown alarm. Requirement two source range neutron flux monitors to provide visual count rate indication was met during this period. This event, which constitutes an operation prohibited by Technical Specifications, was determined to be of no significance to the health and safety of the public. Event Cause: The cause of this event was the failure to ensure that the operability requirements of the Gamma-Metrics shutdown monitors were adequately captured in theapplicable surveillances and operating procedures when these monitors were credited in Technical Specifications as redundant monitors. Corrective Actions: Revise applicable procedures with the appropriate operability requirements including the function of the Gamma-Metrics shutdown monitor alarm switch, and place a warning label near each Gamma-Metrics shutdown monitor alarm switching both Units.
3692007004 | McGuire 1, McGuire 2 | 08/06/2007 | 10/05/2007 | ML07289008 | <strong>Procedure Deficiency Identified for Performing a Manual Backwash of Nuclear Service Water (RN) Strainers due to Reliance on Non-Safety Instrument Air</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2007, the "A" Train of the Nuclear Service Water (RN) System was declared inoperable due to deficient procedure guidance for manually backwashing RN strainers during Design Basis Accidents (DBA). The Station Instrument Air (VI) System is non-safety-related and cannot be relied upon to manually backwash the RN strainers during or following design basis accidents. At the time of discovery, both units 1 and 2 were in Mode 1 (power operation) and operating at approximately 100 percent power. It was determined there were two periods during the past three years when macro-fouling impacted A Train RN operability. The duration of macro-fouling in 2004 exceeded the 72 hour completion time allowed by Technical Specifications (TS) and is reported as a condition prohibited by plant TS. In addition, scheduled surveillances performed during the 2004 macro-fouling period rendered "B" Train System, Structure, and Components (SSC) inoperable resulting in two trains being simultaneous inoperable and is reportable as an event or condition that could have prevented the fulfillment of a safety function. The root cause of this event was historical modifications to the RN Strainers were completed without an adequate evaluation of the safety-related to non-safety-related system interactions. Immediate actions were taken to restore the ability to manually backwash RN during accident conditions without VI and a root cause evaluation was completed.
3872007001 | Susquehanna 1, Susquehanna 2 | 05/24/2007 | 07/19/2007 | ML07212060 | <strong>Automatic Actuation of 'C' Emergency Service Water Pump due to Improper Alignment During Emergency Diesel Generator Testing</strong><br /><i>Abstract:&nbsp;</i>At 1125 on May 24, 2007, with Unit 1 in Mode 1 at 100% power and Unit 2 in Mode 1 at 100% power, the Emergency service water (ESW) pump automatically started when the 'E' emergency diesel generator (EDG) was manually started to perform testing. At the time of the event, the 'E' EDG was aligned as a substitute for the 'C' EDG and the 'A' and 'B' ESW pumps were running. The 'C' ESW pump started, as designed, and all plant equipment, including the 'C' ESW pump, operated as expected. Plant procedures specify ensuring proper ESW system alignment when an EDG is started. The 'C' ESW pump should have been manually started prior to the 'E' EDG start to prevent the automatic pump start; however, the operator performing the testing failed to recognize that the ESW alignment that existed at the time of the event would result in a pump automatic start. This event is attributed to a human performance error in that a procedure prerequisite for ensuring proper ESW alignment was marked complete but not implemented as intended. Causal factors included failure to perform a formal pre-job brief, failure to utilize peer checking, and less than adequate management oversight. Corrective actions taken included coaching and counseling the operators involved in the event and issuing a communication to on-shift Operations personnel that discussed the event and reinforced expectations for procedure compliance. In addition, training will be provided to appropriate Operations personnel regarding this event and will include emphasis on the expectations that were not met. This event is reportable as an event that resulted in an unplanned automatic actuation of an ESW system per 10 CFR 50.73(a)(2)(iv)(A). There were no consequences to the health and safety of the public as a result of this event since the event does not represent a degraded condition and all station equipment responded as designed during the event.
3872007002 | Susquehanna 1, Susquehanna 2 | 06/20/2007 | 08/15/2007 | ML07240034 | <strong>ESSW Pump House Ventilation Inoperable Following Modification</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2007, with Susquehanna Unit 1 in Mode 1 at 100% power, it was determined that an unrecognized condition had existed at the Engineered Safeguard Service Water (ESSW) pump house that, administratively, rendered a single loop of Residual Heat Removal inoperable for the suppression pool cooling mode of operation. This condition was created in August 2002 when, for security related purposes, an access door to the pump house was permanently sealed with concrete block. Because the door was being relied upon in station procedures to provide an air circulation path necessary to mitigate the effects of a divisional HVAC failure in the ESSW pump house, this modification placed the station outside of its design basis relative to single failure requirements for the pump house ventilation system. Both an inadequate implementation of the corrective action process and process weaknesses associated with the handling of a complex modification implemented in 1985 contributed to this situation. In response to this event, PPL has "gagged" two pump house dampers to the open position. This measure will ensure circulation cooling in the event of a divisional HVAC failure until a permanent corrective measure can be implemented to address this single failure issue. Susquehanna's FSAR will be revised to address and recognize any design features or operator actions associated with this final resolution when implemented. Additionally, Susquehanna's modification program now requires performance of a failure modes and effects analysis that would have identified the latent, adverse consequences created through implementation of the 1985 modification. The program now also incorporates a formal impact evaluation process that makes it more difficult to implement a change like the 2002 modification without recognizing potential impacts on operational and design basis requirements. Finally, Susquehanna's corrective action program is significantly more robust than it was in the 1990's when actions to update the FSAR were not properly incorporated and taken to completion. This situation is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. There were no safety consequences or compromises to public health and safety as a result of this event.
3882007001 | Susquehanna 2 | 03/09/2007 | 05/08/2007 | ML07142004 | <strong>U2 Secondary Containment Bypass Leakage Exceeded</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2007 at 1345 hours, with Susquehanna Unit 2 in Mode 5 (Refueling) at 0% power, it was determined that the as-found minimum pathway Secondary Containment Bypass Leakage (SCBL) Technical Specification (TS) limit had been exceeded during regularly scheduled Local Leakage Rate Testing (LLRT). At the time the limit was surpassed, the station was testing the Unit 2 ‘A’ Residual Heat Removal Containment Spray penetration. Despite work history that suggested leak rate failures at this penetration were not usually attributable to the isolation valve being tested (HV251F016A) but were often caused by a leaking test boundary valve (HV251F021A), PPL lubricated and stroked the tested isolation valve before boundary valve repairs could be made. This action required PPL to accept the higher than desired as found LLRT results. Analysis has concluded that the boundary valve was, in fact, primarily responsible for the unsatisfactory LLRT results and that the event was caused by PPLs failure to rework the boundary valve and perform a second as-found leak rate test. In response to this event, PPL intends to dearly identify those leak rate tests that contribute to SCBL in procedures, maintenance work plans, and station schedules. Troubleshooting plans will be pre-staged for SCBL related LLRT activities. This situation is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(A) because the total as-found minimum pathway SCBL leakage rate exceeded the Technical Specification limit. There were no safety consequences or compromises to public health and safety as a result of the additional SCBL leakage since the dose consequences from the additional leakage would not have exceeded 10CFR100 or 10CFR50 Appendix A, GDC 19 limits.
3892007001 | St. Lucie 2 | 08/18/2007 | 10/16/2007 | ML07297052 | <strong>Reactor Shutdown due to Unidentified RCS Leakage</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2007, St. Lucie Unit 2 was in Mode 1 at 100 percent reactor power when a planned manual reactor trip was initiated. The planned trip was a result of a known reactor coolant system (RCS) unidentified leak exceeding a plant management imposed administrative leakage limit. Technical Specification operational leakage limits were never exceeded. The subsequent containment walkdown identified the leak source as non-isolable RCS pressure boundary leakage from a cracked socket weld on the 3/4 inch Class 1 2B1 Reactor Coolant Pump (RCP) seal injection piping. The cause for the socket weld failure was low stress high cycle fatigue resulting from RCP vibration and the susceptibility of socket welds to high cycle fatigue failure. During the forced outage, the failed weld was removed and the seal injection piping was isolated, with the configuration controlled under a temporary system alteration. Corrective actions include replacement of the most vulnerable Unit 2 RCP seal injection piping socket welds with a more robust weld design, permanent removal of insulation from sockets welds within the Unit 2 RCP shrouds to facilitate future inspections, replacement of the 2B1 RCP motor, and evaluation of the St. Lucie Unit 1 seal injection piping.
3892007002 | St. Lucie 2 | 12/21/2007 | 02/18/2008 | ML08058031 | <strong>2B2 Reactor Coolant Pump (RCP) Seal Housing Leakage</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2007, St. Lucie Unit 2 was in Mode 3 returning from a refueling outage, when Maintenance identified the 3/4 inch diameter seal injection piping weld connection at the seal cartridge of the 2B2 reactor coolant pump (RCP) [EIIS:AB:P] was leaking. This was determined to be pressure boundary leakage and the Unit entered a short notice outage (SNO) to investigate the leak. Visual and liquid penetrant examinations identified the presence of a linear indication at the pipe side toe of the weld on the pump seal package. This suggests the failure mechanism was outside diameter-initiated fatigue. During disassembly of the piping, significant cold-spring was also noted. Corrective actions taken to date include replacement of the seal package containing the degraded weld, preliminary destructive metallurgical examination of the weld and removal of the piping cold-spring. Extent of condition inspections included performing liquid penetrant tests on all other Unit 2 RCP seal package nozzle connections (upper, middle, lower, controlled bleed-off, and vapor seal leak-off) and verifying there was no cold spring present on any of the other lower seal cavity lines on the other three RCPs. Upon completion of forensic metallurgical testing of the failed pipe, a root cause evaluation will be completed and results communicated in a revision to this LER.
3892007003 | St. Lucie 2 | 12/29/2007 | 02/27/2008 | ML08066007 | <strong>Manual Reactor Trip following Misalignment of Five (5) Control Element Assemblies (CEAs) During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>On December 29, 2007, St. Lucie Unit 2 was in Mode 3 returning from a scheduled refueling outage when a manual reactor trip was initiated. The control element drive mechanism (CEDM) system was not able to maintain five (5) control element assemblies (CEAs) in the withdrawn and aligned position. All control systems responded as required. The most probable cause of the event was determined to be the aging Maintenance Hold Bus power supplies with a contributing factor being a voltage isolation card fault. Corrective actions included procedure precautions on the use of the Maintenance Hold Bus and the replacement of the voltage isolation card. A successful Post Maintenance test was performed on the control rod system. To evaluate the extent of condition, the input and output voltages of the Maintenance Hold Bus power supplies and the voltage isolation card associated with the CEA were measured. All measurements were evaluated and considered to be normal. There was no adverse impact on the health and safety of the public.
3952007001 | Summer 1 | 02/05/2007 | 07/26/2007 | ML07215005 | <strong>Manual Reactor Shutdown due to Steam Leak at Feedwater Booster Pump Recirculation Header</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2007, while returning the "D" feedwater booster pump to service, a steam leak developed in the Turbine Building. Investigation revealed a steam leak had developed in the vicinity of the "D" feedwater booster pump recirculation header. Since the exact location could not be readily identifiable, the shift supervisor conservatively directed a manual reactor trip at 0307. All systems responded as expected on the reactor trip. The emergency feedwater pumps automatically started on Lo-Lo Steam Generator Level. The cause of the steam leak was determined to be a failure of the gasket for the "D" feedwater booster pump recirculation header orifice. The cause of the gasket failure was attributed to normal aging and pipe movement during the startup of the "D" feedwater booster pump. For corrective action, the gaskets and orifice plate were replaced, and the plant was returned to power operation on 2/06/2007. The feedwater system operating operating procedure has been revised to direct operators to ensure certain system conditions are met prior to starting a feedwater booster pump.
3952007002 | Summer 1 | 10/05/2007 | 03/06/2008 | ML08070023 | <strong>Failure to Follow Administrative Controls Results in LCO 3.6.4 Violation</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2007, while troubleshooting IFS1900A, Reactor Building Cooling Unit (RBCU) drain flow switch, the administrative controls for establishing demineralized water to the Reactor Building while in Mode 1 were not implemented as required by Limiting Condition for Operation (LCO) 3.6.4. The original plan to test IFS1900A included establishing demineralized water to the Reactor Building by opening normally locked closed containment isolation valves at penetration XRP0231. The administrative controls included stationing operators at the penetration isolation valves to administratively maintain containment isolation valve operability. During the implementation of the plan, the operators erroneously assumed that since penetration XRP0231 was declared inoperable because it was not in its drained condition, the administrative controls were not necessary. Subsequently, the operators stationed at the isolation valves were allowed to vacate their positions effectively terminating administrative control of containment isolation valve operability and violating LCO 3.6.4. The root cause has been determined to be establishing demineralized water to the reactor building without a formal procedure. Immediate corrective action was to drain and isolate XRP0231 and return the penetration to operability. In addition, a procedure will be developed for establishing demineralized water to the reactor building in Modes 1 through 4.
3952007003 | Summer 1 | 10/04/2007 | 03/06/2008 | ML08070023 | <strong>Clogged Reactor Building Cooling Unit Drain Line Results in Violation of LCO 3.4.6.1</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2007, during an as-found functional flow test of Reactor Building Cooling Unit (RBCU) drain flow switch, IFS01900A, the required alarm failed to initiate. RBCU drain flow switch IFS01900A was declared inoperable. IFS01900B was assumed to be in the same condition as IFS01900A and was declared inoperable also. Boroscope investigation of the bottom of the 6 inch P-trap of the RBCU drain line revealed debris plugging the 1 inch line tapping off the P-trap. IFS01900A was cleared of the blockage via a 6 inch blind flange downstream of the P-trap and was declared operable on October 11, 2007. Preliminary investigation has determined that this condition existed for a significant period of time. An evaluation was conducted to determine if the condition existed for a time longer than permitted by Technical Specifications. An engineering review of plant operating records completed on November 14, 2007, found multiple occasions over the last three years where the more restrictive six hour portion of Technical Specification 3.4.6.1 Action Statement should have been entered due to other leakage detection systems being declared inoperable. The cause of the inoperable RBCU drain flow switches and subsequent technical specification violation was foreign material introduced through the drain piping during RBCU cleaning, and an inadequate Surveillance Test Procedure (STP). Corrective actions will be developed to ensure foreign material will not affect the P-trap and associated piping for IFS01900A and IFS01900B. In addition, the test method in the surveillance test procedure for the RBCU drain flow switches will be revised to ensure the RCS leakage detection function is met.
3972007001 | Columbia | 03/21/2007 | 05/15/2007 | ML07142004 | <strong>Automatic Depressurization System Logic Signal Instrument Inadvertantly Disabled</strong><br /><i>Abstract:&nbsp;</i>On March 21st, 2007, at approximately 0214, it was determined that a pressure sensing instrument had been isolated and out of service during the time it was required to be operable by plant Technical Specifications. The instrument provides a low pressure Emergency Core Cooling System (ECCS) pump running permissive signal for initiation of the Automatic Depressurization System (ADS). The instrument was discovered isolated during surveillance testing and maintenance records indicate it had potentially been isolated for as long as 32 days. This is longer than the 8-day Completion Time allowed for Required Action G.2 of Technical Specifications Limiting Condition for Operation (LCO) 3.3.5.1 to restore the channel to operable status. This event meets the criteria for reporting pursuant to 50.73(a)(2)(i)(B). During the entire time the instrument was out of service, redundant instruments were operable to maintain initiation capability of both ADS subsystems. No safety consequences are associated with this event.
3972007002 | Columbia | 04/04/2007 | 05/31/2007 | ML07163024 | <strong>Discrepancy in Special Nuclear Material Inventory</strong><br /><i>Abstract:&nbsp;</i>During preparations for an NRC inspection of Columbia's SNM Control and Accounting Program (April 16-19, 2007), documentation concerning the recovery of two pieces of a broken fuel rod was obtained.The documentation revealed the existence of potential fuel particles estimated to be less than 1 gram, in aggregate, located in the spent fuel pool. The exact location of these particles cannot be confirmed at this time. The particles were created during a 1990 refueling outage when a fuel rod broke during an inspection.Following the recovery of the broken rod, a survey was performed that revealed a small dark particle of material surrounded by smaller black particles in a stainless steel bucket which had been positioned under the broken fuel rod pieces. The bucket was suspended off of the spent fuel pool wall where it is believed to have been later dislodged and its contents spilled into the pool. The location of these particles is most likely in the spent fuel pool or buried at a site licensed to receive radioactive material.Given the disposition of the material, no threat to the health and safety of the public exists. Energy Northwest is pursuing corrective actions to both address the missing fuel particles and to prevent future recurrence of a loss of control and accountability of licensed material. There have been no other events associated with the loss of control and accounting of loose SNM at Columbia.
3972007003 | Columbia | 04/08/2007 | 06/07/2007 | ML07166018 | <strong>Technical Specification Required Shutdown due to Inoperable AC Electrical Power Subsystem</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2007 at approximately 0930 PST, Energy Northwest was replacing inoperable transformer E-TR-IN/2 when the ground reference for critical instrument power panel E-PP-8AA was unknowingly removed. The ensuing power fluctuations resulted in the panel being declared inoperable, entering Technical Specification 3.8.7, Condition A. Prior to exceeding the 8 hour completion time of Condition A, management decided to initiate a controlled reactor shutdown to address the issue. The root cause of this event was a less than optimal design that introduced a vulnerability via the unnecessary routing of the grounded neutral wire for E-PP-8AA through E-TR-IN/2. Corrective actions have been initiated to pursue a design change to facilitate maintenance and eliminate, as practical, vulnerabilities in neutral/ground paths supporting critical equipment. There have been no other documented instances at Columbia involving the inadvertent removal of a neutral ground path leading to an event.
3972007004 | Columbia | 06/28/2007 | 08/21/2007 | ML07241039 | <strong>Reactor Scram due to Tripped Condensate Booster Pump</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2007 at 1717 PDT Columbia Generating Station experienced an unexpected trip of Condensate Booster Pump (CBP) 2B (COND-P-2B). The trip occurred while operators were manually transferring the COND-P-2B duplex oil filter to the standby filter. The trip of COND-P-2B resulted in a low suction pressure trip of the reactor feedwater pumps and a reactor scram on low water level. The cause of this event was a latent equipment condition involving the incorrect configuration of the COND-P-2B lube oil filter valves combined with the operational decision to transfer filters with COND-P-2B required to be in service. Corrective actions have been initiated to properly configure the COND-P-2B lube oil transfer valves and enhance plant documentation to ensure the proper configuration is maintained following future maintenance activities. Furthermore, Energy Northwest will enhance the operational directives governing future on-line oil filter transfers. There are no documented previous instances at Columbia involving the inadvertent removal of CBP lube oil filters from service.
3972007005 | Columbia | 12/10/2007 | 02/07/2008 | ML08051053 | <strong>Inoperable Diesel Generator due to Inadequate Procedure That Caused Potential Transformer Fuses to Clear During Shut Down of the Diesel</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2007, it was discovered that an unidentified failure of the Emergency Diesel Generator (DG) that supports the High Pressure Core Spray system resulted in a failure to comply with the required actions of three separate conditions of Technical Specification 3.8.1, AC Operating Sources on two separate occasions. The cause of the DG failures was the performance of inadequate procedures on May 3, 2005 and October 19, 2007 that resulted in clearing of the fuses on the primary side of the metering and relaying potential transformers during shut down of the DG. The potential transformers provide power to the electronic governor as well as the local and remote indications rendering the electronic governor inoperable while the fuses were cleared. The DG was inoperable from May 3, 2005 to June 7, 2005 and again from October 19, 2007 until November 10, 2007. The root cause of the inadequate procedures was a lack of knowledge of the DG shut down logic by licensee Operations and Engineering personnel. Corrective actions include revising the affected procedures and providing training for the appropriate Operations and Engineering personnel. This event did not adversely affect the health and safety of the public because the DG remained available and no loss of off-site power occurred during the time frames the fuses were cleared.
4002007001 | Harris | 03/09/2007 | 05/08/2007 | ML07136009 | <strong>Control Rod Shutdown Bank Anomaly Causes Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>At 07:40 a.m. on March 9, 2007, with the reactor at approximately 100 percent power, surveillance test OST-1005 "Control Rod and Rod Position Indicator Exercise Quarterly Interval Mode 1-3," was being performed to satisfy Technical Specification (TS) 4.1.3.1.2 where each operable shutdown and control rod not fully inserted into the core is determined to be operable by movement of at least 10 steps in any one direction at least once per 92 days. During this test, Shutdown Bank A stopped at approximately 220 steps causing a rod control urgent alarm rendering the affected rods inoperable and initiating an entry into TS 3.0.3. However, throughout this event, all rods were capable of manually or automatically tripping into the core to shutdown the reactor. The cause was determined to be a failed Slave Cycler Logic Card in the Westinghouse Rod Control System [AA] (card model 3359C80G01 s/n 0210). This card was replaced with a logic card from stock. Operators exited TS 3.0.3 at 10:33 a.m. The plant was in TS 3.0.3 for 2 hours and 53 minutes. The most likely mechanism for the Slave Cycler Logic Card failure is aging of a Z4 chip. A planned corrective action is to establish a structured program of card replacements. This action is being tracked through the corrective action program.
4002007002 | Harris | 06/12/2007 | 08/13/2007 | ML07233012 | <strong>Control Rod Shutdown Bank Anomaly Causes Entry into Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>At 13:10 EDT on June 12, 2007, with the reactor at approximately 100 percent power, surveillance test OST-1005, "Control Rod and Rod Position Indicator Exercise Quarterly Interval Mode 1-3," was being performed to satisfy Technical Specification (TS) 4.1.3.1.2 where each operable shutdown and control rod not fully inserted into the core is determined to be operable by movement of at least 10 steps in any one direction at least once per 92 days. During this test, while inserting Shutdown Bank A rods, a Rod Control Urgent Alarm activated, rendering the affected rods inoperable and initiating entry into TS 3.0.3. However, throughout this event, all rods were capable of manually or automatically tripping into the core to shutdown the reactor. The cause was determined to be a failed Master Cycler Counter Card in the Westinghouse Rod Control System [AA] (Printed Wiring Assembly part number 3360C94G01, s/n WSN0595). TS 3.0.3 was exited at 16:41 EDT. The plant was in TS 3.0.3 for 3 hours and 31 minutes. The most likely mechanism for the Master Cycler Counter Card failure is aging of Z13 and Z15 logic chips. In addition to the completed corrective action of replacing the Counter Card, a planned corrective action is the establishment of a structured program of card replacements, to be tracked through the corrective action program.
4002007003 | Harris | 09/28/2007 | 11/19/2007 | ML07332017 | <strong>Automatic Reactor Trip following Actuation of a Sudden Pressure Relay and Lockout of the 1A StartupTransformer (SUT)</strong><br /><i>Abstract:&nbsp;</i>At 22:32 on September 28, 2007, while reducing power for Refueling Outage (RFO) 14, a fault pressure trip on "1A" Startup Transformer (SUT) caused a reactor trip/turbine trip with a loss of all Reactor Coolant Pumps (RCP) and a subsequent Auxiliary Feedwater (AFW) actuation. There was no inoperable equipment at the start of this event that contributed to this event. Safety systems functioned as required and operators responded in accordance with approved procedures. Post trip discovery found that the data to determine the available margin to the "1A" SUT sudden pressure trip setpoint was not available at the time of the design and installation of the Qualitrol 930 series sudden pressure relays. Additionally, it was determined that that the relay was out of calibration in the more sensitive direction. Completed corrective actions include replacing the Qualitrol 930 series relay with the Qualitrol 900 series relay and conducting testing to validate that the "1A" SUT was not damaged. Additional corrective actions are to use a temporary modification to gather data on the "1A" SUT to determine operating margin and implement appropriate design changes to the sudden pressure relays on the SUTs.
4002007004 | Harris | 10/19/2007 | 12/17/2007 | ML07362037 | <strong>Bare Conductors on 'B' Steam Generator Wide Range Level Barton Transmitter as Identified via 10 CFR Part 21 Process</strong><br /><i>Abstract:&nbsp;</i>At 18:00 on October 19, 2007, while replacing connector assemblies in response to a 10 CFR Part 21 Nuclear Industry Advisory (NIA) issued by PRIME Measurements and Nuclear Regulatory Commission (NRC) Information Notice (IN) 2006-14, Harris Nuclear Plant (HNP) personnel identified bare conductors on the field side pigtail at the epoxy interface of the connector assembly of Barton transmitter LT-487 (Steam Generator 'B' wide range level indication). The connector assembly associated with LT-487 is required to provide a moisture tight seal between the electrical enclosure and the postulated harsh post-accident environmental conditions. Moisture present at the pigtail conductors could short or result in spurious operation of the transmitter. The wire insulation at this interface should have been embedded into the epoxy, preventing the exposure of any bare conductor. The root cause of this issue is a defect in the manufacturing process of the transmitter connector assembly. Actions taken at the HNP to date to mitigate the impact of the faulty manufacturing process included replacing fourteen of the eighteen affected connectors. The four remaining connectors will be replaced at the next opportunity. The affected connectors were installed at the time of plant construction, and the defect was identified on only one of the fourteen connectors replaced. There was no other inoperable equipment that contributed to this event, and the connectors were never subjected to the postulated harsh, post-accident environment.
4002007005 | Harris | 11/05/2007 | 01/04/2008 | ML08011007 | <strong>'B' Train of Essential Services Chilled Water Was Inoperable for a Period Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 01:44 on 11/5/07, while performing a safety train equipment realignment to 'B' train, the 'B' Essential Services Chilled Water (ESCW) chiller tripped due to low refrigerant pressure. The root cause of this event was that post-maintenance testing was inadequate in detecting leakage from the chiller to the receiver tank, resulting in a loss of refrigerant. This leakage occurred as a result of valve 1CY-7 not being fully shut following maintenance that required evacuating all refrigerant. Full evacuation of 'B' chiller is an infrequent evolution that has been conducted less than five times since placing the Harris plant online in 1987. The post-maintenance testing that was performed on the chiller consisted of external leak checks and a series of tests to verify functionality and operability of the chiller following maintenance. The tests performed were unable to detect the presence of leakage internal to the system from the turbopak to the receiver tank. Not achieving tight shut-off through 1CY-7 resulted in leakage of refrigerant to the transfer tank after the chiller had been declared operable following completion of maintenance and testing. This leakage ultimately caused the inoperability of the 'B' ESCW chiller. Planned corrective actions to prevent recurrence include revising two procedures to require evacuation of the receiver tank following refrigerant transfer to ensure an internal leak path to the receiver does not exist.
4132007002 | Catawba 1, Catawba 2 | 06/09/2007 | 08/08/2007 | ML11053034 | <strong>Technical Specification Violations Associated with Divider Barrier Integrity</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2007, at 2155 hours, with Unit 2 in Mode 1 at 73% power, the Unit 2 divider barrier submarine hatch was discovered to be in an unsecured position. The discovery was made by a non-licensed operator while making rounds. Subsequently, on June 10, 2007, at 0125 hours, with Unit 1 in Mode 1 at 100% power, the Unit 1 divider barrier submarine hatch was also discovered to be in an unsecured position. The discovery was made by a non-licensed operator while making rounds. Both submarine hatches were closed at the time of discovery; however, they were not secured. Therefore, the requirements of Technical Specification 3.6.14, Divider Barrier Integrity, were not met for these hatches. The root cause of these Technical Specification violations was determined to be general deficiencies in the hatch design that make them susceptible to inadvertently becoming unsecured. Corrective actions to be taken in response to these events include re-designing the hatches. During the time periods that Technical Specification 3.6.14 was violated for these hatches, both units remained in an analyzed condition; therefore, all required safety systems would have been able to perform their accident mitigation functions had they been called upon to do so. As a result, there was no safety significance to these events.
4132007003 | Catawba 1, Catawba 2 | 08/25/2007 | 10/24/2007 | ML07303003 | <strong>Undervoltage Condition Resulted in the Actuation of the Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On August 25, 2007 at approximately 10:58 am, both Unit 1 and Unit 2 experienced a voltage dip of approximately 0.462 second duration when a transformer at a merchant plant connected to Duke's grid faulted. The electrical grid disturbance caused all four Emergency Diesel Generators (EDGs) to actuate. The EDGs ran unloaded because the condition existed for less than the 8.5 seconds required for separation from offsite power. At 12:28, the Transmission Control Center (TCC) notified plant operations that the faulted busline was isolated, and by 12:36, all EDGs were secured and restored to standby. The response of plant equipment to this electrical grid disturbance was as expected. A Duke Energy team was chartered to provide further investigation to verify that the Catawba switchyard is as secure as-possible from similar external conditions. The health and safety of the public were not adversely affected by this event.
4132007004 | Catawba 1, Catawba 2 | 10/30/2007 | 12/19/2007 | ML07358018 | <strong>Control Room Area Chilled Water System Inoperable in Excess of Technical Specification Requirements due to Unanticipated Component Interactions</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2007 with Unit 1 operating in Mode 1 at 100% power and with Unit 2 operating in Mode 5 (Cold Shutdown), it was discovered that both trains of the Control Room Area Chilled Water System (CRACWS) were inoperable. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 was immediately entered. During Engineered Safety Features (ESF) Blackout and Loss of Coolant Accident (LOCA) testing, Train B Chiller of the CRACWS failed to restart. After troubleshooting this condition, it was determined that the failure of the chiller to restart was the result of the thrust bearing module reset value being set below the normal bearing oil operating temperature. The resistance of the redundant fuse FU-4 installed in the bearing temperature monitoring circuit changed the bearing module reset value. Train A CRACWS Chiller has identical bearing temperature monitoring circuitry. This condition has existed on both trains since April 10, 2007. In consequence, both CRACWS chillers were inoperable for a period of time in excess of TS requirements. The apparent cause of this event is attributed to unanticipated interaction of fuse FU-4 with the thrust bearing module circuitry. Corrective actions included removing the redundant fuses from the bearing module circuitry. This event did not adversely affect the health and safety of the public. This report does not involve a safety system functional failure.
4142007001 | Catawba 2 | 05/11/2007 | 07/10/2007 | ML07199009 | <strong>Failure to Comply with Action Statement in Technical Specification (TS) 3.3.1 for Loss of a Channel of the Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>At 2149 on May 10, 2007 during maintenance on the Solid State Protection System B-train 48VDC power supply, the channel 4 over temperature delta temperature (OTDT) trip setpoint became inoperable due to a failure of the axial flux imbalance circuit card. However, for the plant conditions that existed at that time, the OTDT channel was not recognized as being inoperable using normal control room board indications. Therefore, the inoperable channel was not placed in the trip condition within 6 hours (or be in Mode 3 within 12 hours) as required by Technical Specifications 3.3.1. The channel was placed in the trip condition after approximately 13 hours and 1 minute. The safety significance of this event is minimal. The OTDT trip function is not credited in the current safety analysis or fuel design; the existing plant conditions did not challenge the OTDT trip setpoint, and the remaining 3 operable OTDT channels would have generated an OTDT trip signal for all appropriate plant conditions. This event does not involve a safety system functional failure.
4142007002 | Catawba 2 | 11/05/2007 | 01/03/2008 | ML08009020 | <strong>Technical Specification Violation Associated with Containment Valve Injection Water System</strong><br /><i>Abstract:&nbsp;</i>On 10/07/07 at 1629 hours, during the End-of-Cycle 15 Refueling Outage, calibration of Containment Valve Injection Water System (CVIWS) surge chamber 2A level transmitter 2NWLT5020 was being performed. It was observed that the transmitter's loop output began to drop steadily after the transmitter was returned to service following its calibration. Investigation revealed that CVIWS surge chamber 2A narrow range level high pressure root isolation valve 2NWIV5020 was closed. Investigation concluded that the valve was most likely closed during the End-of-Cycle 14 Refueling Outage. This rendered the associated CVIWS train inoperable for longer than allowed by Technical Specifications. During the time period that valve 2NWIV5020 was closed, there were two instances during which the unit was unknowingly in Technical Specification Limiting Condition for Operation 3.0.3 for a time period longer than allowed. This event was determined to be inconsequential from a plant risk perspective based on the fact that the affected containment penetrations are not considered to be likely pathways for radiation release. Therefore, the health and safety of the public were not adversely affected by this event.
4162007001 | Grand Gulf 1 | 04/11/2007 | 06/05/2007 | ML07157020 | <strong>Failure to Comply with Technical Specification 3.3.8.1- Function 1.b Loss of Voltage Time Delay</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2007 at 1221, it was discovered during Technical Specification surveillance testing that the Division 2 Emergency Bus 16AB (4.16 kV) feeder breaker 152-1611 from ESF (Engineered Safety Feature) Transformer 12 would open at a 0.35 second time delay upon receipt of a loss of voltage signal. This was contrary to its required Technical Specification3.3.8.1 Function 1.b allowable value of >/=0.4 and </=1.0 seconds for a loss of voltage time delay. Investigation revealed that the 4.16 kV Emergency Bus 15AA (Division 1) and 16AB (Division 2) loss of voltage protective time delay relays (15AA-162-1, 15AA-162-2, 16AB-162-1, and 16AB-162-2) were set such that their time delay (0.3 seconds) did not allow adequate surveillance testing of the Technical Specification 3.3.8.1 Function 1.b. Loss of Voltage - Time Delay Load Shedding and Sequencing System (LSSS) credited time delay devices (XA22-TD1 and XA22-TD2). The cause has been determined to be a failure to recognize in the original design documents for the ESF Division 1 (15AA) and Division 2 (16AB) Emergency Bus switchgear that the standard protective bus under-voltage device time delay (set at 0.3 second) relays could react faster than the Technical Specification 3.3.8.1 credited LSSS time delay devices.
4162007002 | Grand Gulf 1 | 05/19/2007 | 07/16/2007 | ML07198014 | <strong>Reactor Scram due to Turbine Trip Caused by Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2007 at 1127, a Reactor SCRAM from 78% Core Thermal Power (CTP) occurred due to a Main Turbine trip on low Condenser vacuum. Reactor power had been lowered from 100% to 78%, per Loss of Condenser Vacuum Off-Normal-Event Procedure (ONEP), just prior to the automatic actuation of the Reactor Protection System (RPS). Failure of a High Pressure (HP) Condenser expansion joint resulted in degrading Condenser vacuum and subsequent turbine trip over an approximately three minute period. Pressure control was initially maintained with Turbine Bypass Control valves until vacuum decreased to the point that bypass was no longer available. Then Reactor pressure was controlled using a Safety Relief Valve (SRV). Reactor water level continued to be maintained with Condensate system. This report is being submitted pursuant to10CFR50.73(a)(2)(iv)(A). The cause of the event was the failure of the HP Condenser expansion joint between the Main Turbine and Condenser. Failure of the expansion joint resulted in low condenser vacuum. All Control Rods inserted fully and Reactor level did not decrease below the automatic Emergency Core Cooling System (ECCS) actuation set point (Level 2, -41.6 inches). The Reactor vessel level 3 isolation setpoint of + 11.4 inches was reached for Shutdown Cooling which was already isolated. The expansion joint was replaced to correct the condition.
4162007003 | Grand Gulf 1 | 08/21/2007 | 10/15/2007 | ML07291038 | <strong>Reactor Scram due to Decreasing Reactor Vessel Water Level</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2007 at 1415 hours Grand Gulf Nuclear Station experienced an actuation of the Reactor Protection System (RPS) which resulted in an automatic reactor shutdown (SCRAM) from 100 percent power due to decreasing reactor water level. The initiation of RPS resulting in an automatic reactor SCRAM is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A). At the time of the SCRAM technicians were securing from routine maintenance in the Bailey INFI-90 digital Feed Water control panel for the "A" Feed Pump when an unexpected Power Failure Interrupt (PFI) signal was received. This unexpected signal drove the "A" Feed Pump governor control valve to minimum position which lead to a reactor scram on Level 3 (+11.4 inches) low reactor water level. The reactor water level did not reach the Level 2 set point (-41.6 inches) for initiation of Emergency Core Cooling Systems (ECCS), therefore no ECCS initiation occurred. All control rods were fully inserted into the core and all other system performed as designed. The normal heat sink (main condenser) remained available therefore no Safety Relief Valve actuations occurred. The Feed Water panel was inspected and as a precaution, the bus monitor, auto transfer, power supply, and power entry panel were replaced.
4232007001 | Millstone 3 | 04/05/2007 | 05/23/2007 | ML07151008 | <strong>Failure of Two Main Steam Safety Valves to Lift Within the Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>With the plant in MODE 1 at 100% power on April 5, 2007 set pressure "simmer" testing of Unit 3 (MPS 3) Main Steam Safety Valves (MSSVs) was conducted per plant procedures. This testing was conducted just prior to the recent refueling outage. During the conduct of testing, two MSSVs failed to lift within the (+/- 3%) acceptance criteria. Valve 3MSS*RV22B lifted at 1221.3 psig. (1.3 psig above the set pressure range, approximately 3.1%),and 3MS*SRV22D lifted at 1232.8 psig. (12.8 psig above the set pressure range, approximately 3.8%). 3MSS*RV22B supports the B Steam Generator (SG) and valve 3MSS*RV22D supports the D SG. Both valves were subsequently adjusted/retested with the results within the required range of +/- 1%. Based on information provided by Electric Power Research Institute Report report TR-113560 (Investigation of MSSV High First Lift Phenomenon in Dresser 3700 Series MSSVs, Sept. 2000), industry experience, MSSV test history at Millstone, and engineering judgment, the failure of the MSSVs to lift within the required set pressure range is attributed to a corrosive oxide locking action between surface layer materials of the disc-seat interface sometimes referred to as "oxide locking" or "micro bonding". This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) "Any operation or condition prohibited by the plants Technical Specifications."
4232007002 | Millstone 3 | 04/25/2007 | 06/11/2007 | ML07173005 | <strong>Loss of Offsite Power Caused by Transmission System Operator While Defueled</strong><br /><i>Abstract:&nbsp;</i>At 1047 on April 25, 2007 with the plant shutdown (0% power) and in a defueled condition, a loss of offsite power (LOP) caused by a switching error on the part of the offsite transmission system operator (TSO) occurred at Millstone Power Station Unit 3 (MPS3). Millstone Power Station Unit 2 remained at 100% power and connected to the grid throughout the event. The MPS3 "A" emergency diesel generator started automatically and supplied power to the "A" train 4160 volt AC emergency bus. At the time of the event, the applicable plant technical specifications (TS) such as Reactor Coolant System Pressure / Temperature Limits (TS 3.4.9.1), Spent Fuel Pool Reactivity (TS 3.9.13) and Water Level - Storage Pool (TS 3.4.9.11) were not challenged by the event. Operators restored power to spent fuel pool cooling at 1054 in accordance with plant procedures. The shift manager declared an Unusual Event (UE) at 1101 based on the Emergency Action Level criteria for a loss of offsite power. The UE was terminated at 1427. When the LOP occurred, the plant response was as expected except as described in the event description section of this LER. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv) as an event or condition that resulted in the manual or automatic actuation of emergency AC electric power systems including emergency diesel generators. The offsite TSO has initiated corrective actions to address the human performance aspects of this event. Additional corrective actions are being taken in accordance with the station's corrective action program.
4232007003 | Millstone 3 | 09/27/2007 | 11/21/2007 | ML07338121 | <strong>Reactor Head Vent Valve Circuits Not Isolated from Control Room During Fire Scenario</strong><br /><i>Abstract:&nbsp;</i>On September 27, 2007 at 1730 hours while operating at 100% power, Millstone Power Station Unit 3 (MPS3) entered a Technical Specification (TS) Action Statement 3.3.3.5 for Remote Shutdown Instrumentation when a vulnerability in the fire safe shutdown strategy was identified affecting reactor vessel head vent valve transfer switches covered by TS 3.3.3.5. During an engineering review, it was discovered the control circuits for two reactor vessel head vent valves (3RCS*SV8095A, 3RCS*SV8096A) would not be properly isolated from the control room during certain fire scenarios. Specifically, for catastrophic fires in the control room, cable spreading area or instrument rack room, operators evacuate the control room and control the plant from the Auxiliary Shutdown Panel (ASP) located in the east switchgear room. During the review, it was discovered control circuit relays for 3RCS*SV8095A and 3RCS*SV8096A are located in the main control board. After the transfer switches on the Fire Transfer Switch Panel (FTSP) are repositioned to "Local," these control circuit relays, which are within the fire area, remain in the control circuit. Since these relays are located within the fire area, it must be assumed the fire can affect their function and thus could affect the transfer of control from the main control room to the ASP for 3RCS*SV8095A and 3RCS*SV8096A. Therefore, the transfer switches associated with these valves were declared inoperable. This condition is being reported under 10CFR50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications," and under 10CFR50.73(a)(2)(ii)(B), "Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety."
4232007004 | Millstone 3 | 10/05/2007 | 12/03/2007 | ML07345081 | <strong>Fire Scenario Results in Unanalyzed Condition - Potential Loss of Charging</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2007 and October 11, 2007 while operating at 100% power, Millstone Power Station Unit 3 (MPS3) identified a vulnerability in the fire safe shutdown strategy in which a fire could disable both the train A and train B charging pumps. In the event of a fire affecting one train of charging with the opposite train charging pump in service, a fire induced circuit failure could produce spurious closure of the Volume Control Tank (VCT) outlet valve, resulting in damage to the operating charging pump. As a result, neither charging pump would be available to provide reactor coolant system inventory control and reactor coolant pump seal injection. Since the station's design basis following a fire in a specific area is that one train of required systems remain free of fire damage, these scenarios result in an unanalyzed condition. The analyses for fire areas, prepared in the 1980s, reviewed spurious equipment operation. However, the report failed to consider the unique interaction between the spurious closure of the VCT outlet valve and the operating charging pump in the redundant train. Compensatory measures have been implemented and will remain in place until a permanent resolution is identified and implemented. The condition resulted in no adverse safety consequences. It is of regulatory significance because it represents an unanalyzed condition. This condition is being reported under 10CFR50.73(a)(2)(ii)(B), "Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety."
4242007001 | Vogtle 1, Vogtle 2 | 02/19/2007 | 04/27/2007 | ML07117053 | <strong>Auxiliary Contact Blocks on Motor Starter Not Being Secured Resulted in the Inability to Meet Their Seismic Qualifications</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2007 at 1330, a top-mounted auxiliary contact block for the Unit 1 `B' Train SI Pump Mini-flow Isolation valve motor starter assembly was found not completely engaged. This component was assumed inoperable for longer than allowed by Technical Specifications (TS) as a result of not meeting seismic qualifications. This condition was discovered during a broadness inspection performed on both Unit 1 and Unit 2 as a corrective action to an earlier event on October 14, 2006, where the Unit 2 'A' Train Containment Spray Suction Isolation Valve failed to close as a result of a bound top-mounted auxiliary contact. Upon finding the auxiliary contact block locking tab not engaged during the February 19, 2007 inspection, the seismic qualification of any auxiliary contact block that is not fully seated was called into question, including the Unit 2 'A' Train Containment Spray Suction Isolation Valve, which was found on October 14, 2006. Over 250 motor starter assemblies on both units (including all safety related) have been inspected as a result of the broadness inspection. A total of eight top mounted auxiliary contact blocks on the motor starter assemblies were not completely engaged. Six were determined to be reportable. Investigation of the February 19 event concluded that the original installation of the top-mounted auxiliary contact blocks did not have adequate procedural guidance to ensure they were properly engaged via a locking tab. Maintenance procedures have been revised after the October 14 event to require independent verification of auxiliary contact block engagement after installation.
4252007001 | Vogtle 2 | 01/01/2007 | 02/27/2007 | ML07058054 | <strong>Sludge Mixing Valves was Determined to be in a Condition which was Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On January 1, 2007 at 1310 EDT, while at 100% power, Unit 2 Refueling Water Storage Tank (RWST) sludge mixing valves 2HV-10957 and 2HV-10958 were discovered to have been inoperable for 24 days, placing them in a condition prohibited by Technical Specification (TS). The subject valves were placed in the jack open position and tagged using a clearance to facilitate maintenance on another component. The clearance was returned to the control room, and signed off as removed. Operability was determined by stating that the tag out had been released and the LCO was exited. This determination of operability was incorrect and left the valves inoperable for 24 days. The primary cause of this event was no procedural guidance was given to verify the valves were operable following being placed on the manual jack. A contributing factor was inadequate use of human performance tools. The operator removing the clearance and the independent verifier did not have a clear understanding of how the jack worked for these valves and made an incorrect assumption of how these valves operated. Other contributing causes included the pre-job brief was not held prior to the release of the tag out, and the discussion about the valves in the clearance concerning their current position or the required position had little detail and was unclear to the operators.
4252007002 | Vogtle 2 | 04/23/2007 | 06/15/2007 | ML07169020 | <strong>Unit 2 Main Generator Tripped, Resulting in an Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On April 23,2007, at 1024 EDT, Unit 2 experienced an automatic reactor trip from approximately 54% power during power ascension following completion of refueling outage 2R12. The main generator neutral overcurrent relay actuated resulting in a Generator/Turbine/Reactor trip. The post-trip investigation revealed that a ground fault had occurred on the main generator 'A' phase bushing. The bushing fault was a result of stator water leaking out of the tang area of the main generator 'A' phase bushing and saturating the bushing insulation. The wet insulation provided the ground fault path that caused the main generator neutral overcurrent relay to actuate. Investigation determined that the primary cause of this event was the design of the main generator bushing tang assembly due to it being a cast copper component utilizing a braze material that is susceptible to crevice corrosion. Prior to restart, the leak was repaired in the main generator 'A' phase bushing tang assembly, a helium tracer gas test was performed on all three main generator tang assemblies, and the Generator Gas System operating procedure was revised to ensure main generator hydrogen pressure is maintained at a higher pressure than stator water.
4402007001 | Perry | 05/15/2007 | 07/16/2007 | ML07205032 | <strong>Automatic Reactor Protection System Actuation due to Reactor Coolant Level Decrease</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2007, at approximately 0058 hours, the Reactor Protection System (RPS) automatically actuated in response to decreasing reactor pressure vessel (RPV) coolant level. At the time of the event, Reactor Feedwater System test/tuning activities were in progress with the reactor operating at approximately 31 percent of rated thermal power. All control rods fully inserted into the core and RPV coolant level was restored with no actuation of emergency core cooling systems. The cause of the event was attributed to a decrease in RPV coolant level resulting from a design logic error not detected during modification pre-operational review or test activities. A contributing cause included a weak conduct of testing process. The design logic error was corrected. The testing instruction was revised. Existing procedures are being revised, and enhanced procedural guidance will be implemented to improve temporary instruction control, conduct of testing, implementation of engineering changes, and infrequently performed tests and evolutions. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of the RPS.
4402007002 | Perry | 07/11/2007 | 09/07/2007 | ML07256001 | <strong>Shutdown Cooling Pump Trip Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 11, 2007, at approximately 2313 hours, the Residual Heat Removal pump (RHR) B Tripped off. At the time of the event, the plant was in Mode 4 (Cold Shutdown). With RHR B Subsystem inoperable, an alternate method of decay heat removal for the RHR B subsystem could not be verified within one hour as required by Technical Specification Limiting Condition for Operation 3.4.10, Required Action A.1. Required Action A.1 was completed on July 12, 2007, at 0559 hours when the tripped RHR B pump was returned to standby. The RHR B pump trip occurred when an Instrument and Control Technician performing Reactor Core Isolation Cooling (RCIC) surveillance testing unnecessarily loosened a wire connection from an electrical terminal, inducing a current from the RCIC circuitry into the electrically independent RHR B trip system. Modifications to separate the wiring and to install noise suppression diodes are being prepared for installation. Personnel actions were taken per the FENOC Performance Management Process. This event was determined to be reportable as an operation or condition prohibited by Technical Specifications, 10CFR50.73(a)(2)(i)B).
4402007003 | Perry | 08/27/2007 | 10/29/2008 | ML08324022 | <strong>Improper Containment Floor Grating Installation Results in an Unanalyzed Condition, Supplement</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2007, a three by seven foot section of grating located in the reactor containment building was found to be missing the required hold down fasteners. The grating had been removed in July 2007, to support a reactor recirculation system pump motor replacement. An engineering review determined that this grating could become dislodged, during a postulated Loss of Coolant Accident. The grating could impact the emergency core cooling system suction strainer resulting in one or more of the following systems becoming inoperable: residual heat removal (RHR) B, C and high pressure core spray. The grating was subsequently restored to design configuration. The cause of the error was determined to be inadequate detail in the work order, inadequate turnover of the work, and inadequate training for configuration control. Corrective actions include: revision of the "Post Maintenance Test Manual" to include verification of the restoration of structural steel components, review of work order content requirements by the work planners, lessons-learned presentations for work turnover requirements between work groups and lessons-learned presentations for configuration control. Further review of this event identified that RHR A and the division 1 emergency diesel generator had been inoperable for short periods while the grating condition existed. This event is being reported in accordance with 10CFR50.73(a)(2)(ii)(B), an unanalyzed condition, 10CFR50.73(a)(2)(v)(D), prevention of a safety function of a system necessary to mitigate consequences of an accident and 10CFR50.73(a)(2)(i)(B), any operation or condition prohibited by Technical Specifications.
4402007004 | Perry | 11/28/2007 | 02/15/2008 | ML08053039 | <strong>Automatic Reactor Protection System Actuation due to Feedwater Control Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On November 28, 2007, at 0732 hours, the Reactor Protection System (RPS) automatically actuated due to receipt of a turbine control valve fast closure signal. At the time of the event, the plant was operating at 100 percent rated thermal power. All control rods fully inserted. The High Pressure Core Spray (HPCS) system automatically started and was used to maintain reactor water level. The Reactor Core Isolation Cooling (RCIC) system started but tripped 13 seconds later. The RPS actuation signal was caused by a failure of the power supplies in the Digital Feedwater Control System. The power supplies were replaced with a different model. Failure of the RCIC system to continue operating was due to improper tuning of the flow controller in January 2006. The RCIC flow controller settings were restored to known acceptable values. Further investigation revealed that the RCIC system was inoperable since that time and, as a result, Technical Specifications for RCIC and HPCS were not met. The safety significance of this event is considered to be very low. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(a), 10CFR50.73(a)(2)(i)(B), and Operational Requirements Manual section 7.6.2.1, which requires a Special Report submittal following an Emergency Core Cooling System actuation and injection into the reactor coolant system.
4402007005 | Perry | 12/12/2007 | 02/11/2008 | ML08051053 | <strong>Plant Startup With Inoperable Reactor Core Isolation Cooling System</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2007, at 2110 hours, the Reactor Core Isolation Cooling (RCIC) system was declared inoperable after Engineering concluded that RCIC testing results were not acceptable. The system computer point traces showed that flow controller settings could challenge stable flow control during system operation. Engineering could not confirm that the RCIC system was able to perform its design function. When RCIC was declared inoperable, the reactor was operating in Mode 1 at 89 percent rated thermal power. During restart from a forced outage, two Mode changes were made while the RCIC system was inoperable. This event is reported in accordance with 10CFR50.73(a)(2)(i)(B) as an operation prohibited by Technical Specifications. Safety significance for this event is very low. The causes of this event were failure to recognize the effects of tuning parameters on RCIC system performance, knowledge deficiencies for system tuning practices, and lack of configuration control over RCIC flow controller settings. Corrective actions include RCIC flow controller setting restoration to acceptable values and the system being acceptably retested. The RCIC flow controller settings will be placed under formal configuration management controls, instructions will be revised to adjust and set RCIC flow control modules, and appropriate training will be determined for engineering and instrumentation and control personnel.
4402007006 | Perry | 12/21/2007 | 02/19/2008 | ML08058019 | <strong>Loss of Safety Function and Condition Prohibited by Technical Specifications due to Annulus Exhaust Gas Treatment System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2007, at approximately 0825 hours, with the plant operating in Mode 1 (Power Operation), at approximately 100 percent power, low flow occurred in the Annulus Exhaust Gas Treatment System (AEGTS) train "B" while train "A" was out of service. The low flow resulted in less than the minimum allowed secondary containment annulus differential pressure. This Condition was determined to be reportable in accordance with 10CFR50.73(a)(2)(v)(C) and (D), Loss of Safety Function. Additionally, this condition resulted in entry into Technical Specification Limiting Condition for Operation 3.0.3. Failure to correct this condition within one hour is reportable in accordance with 10CFR50.73(a)(2)(i)(B), a Condition Prohibited by Technical Specifications. The cause of the low flow was the failure of the discharge damper on the "B" Train. The discharge damper failure was due to side-load wear induced binding of the shaft and shaft extension of the associated Hydramotor actuator. Both the discharge and the recirculation damper actuators were replaced. Maintenance instructions will be revised to ensure proper alignment of the shaft and shaft extension and proper return spring seating. Causal analysis will be performed on any future critical Hydramotor failures. Since AEGTS is not a core damage mitigation system and does not mitigate Large and Early Containment releases, the unavailability of the AEGTS was determined to be of very low safety significance.
4402007007 | Perry | 06/22/2007 | 05/14/2008 | ML08142036 | <strong>Reactor Recirculation Pump Failure Results in Manual Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2007, at approximately 0100 during a planned shutdown, reactor recirculation (RRC) pump B failed to transfer to slow speed and subsequently tripped. On June 22, 2007, at approximately 0329 hours, with the reactor operating at approximately 23 percent of rated thermal power, shutdown of the plant was completed by a manual actuation of the Reactor Protection System (RPS). The cause of the RRC pump B failure to transfer to slow speed was a malfunction of the low-frequency motor-generator set control and interlock circuit Agastat time-delay relay. This was due to the auxiliary contact failing to open as a result of less than adequate programmatic controls for relay checkout and calibration. A contributing cause of the event was less than adequate implementation of testing controls for installing relays. The failed Agastat time-delay relay was replaced with a newly calibrated Agastat time-delay relay. The timing relay checkout and calibration process was revised to include visual inspection of switch contact alignment and testing requirements. A training qualification card was developed for the calibration and testing of relays. Lessons learned will be added to maintenance training programs. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) for events resulting in actuation of the RPS.
4402007008 | Perry | 06/29/2007 | 05/14/2008 | ML08142049 | <strong>Single Recirculation Loop Operation Results in Planned Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2007, at approximately 1426 hours, with the plant in Mode 1 (i.e., Power Operation), the plant operating in single loop, and the reactor operating at approximately 58 percent rated thermal power, shutdown of the plant was initiated by a manual actuation of the Reactor Protection System. The purpose of the shutdown was to repair, or replace reactor recirculation system (RRC) pump motor A which tripped from fast speed operation on June 27, 2007. The cause of the RRC Pump Motor A trip was an electrical fault in the motor. The motor was past due for replacement at the time of failure. The work management preventative maintenance process for RRC motors had not yet been initiated. A contributing cause of the event was the plant accepting a less than adequate risk assessment for the large motors maintenance program. The RRC pump motor A was replaced with a refurbished motor. PM tasks were initiated for motors to meet refurbishment frequency recommendations as stated on the motor templates. Critical motors not having spares available were identified. An assessment will determine the effectiveness of the PM template implementation process. Critical large motors exceeding template rewind intervals will be identified and scheduled. This is a Voluntary Report submitted as a condition of generic interest to the industry.
4432007001 | Seabrook | 02/14/2007 | 04/12/2007 | ML07103033 | <strong>Noncompliance with the Requirements of Technical Specification 3.6.3</strong><br /><i>Abstract:&nbsp;</i>On February 14, 2007 at 1725, with the plant in Mode 1 at 100% power, Operations personnel identified a failure to comply with the actions of Technical Specification (TS) 3.6.3,Containment Isolation Valves. Preventative maintenance on a 120-volt circuit breaker, which commenced on February 13, 2007, de-energized and, consequently, rendered inoperable two containment isolation valves, RC-V2840 and RC-V2876. In preparation for the work, the containment penetration with RC-FV-2840 was isolated by deactivated automatic valves secure din the isolation position as required by TS 3.6.3. However, personnel failed to recognize that maintenance on the circuit breaker also rendered inoperable a second valve, RC-FV2876. As a result, the containment penetration associated with RC-FV-2876 was not isolated within 4 hours as stipulated by TS 3.6.3. Following discovery of this condition on February 14, 2007, Operations personnel promptly isolated the containment penetration containing RC-FV2876 to meet the action of TS 3.6.3. The direct cause of the event was inadequate preparation and review of the clearance order for work on the 120-volt circuit breaker. RC-FV-2876 remained closed for the duration of the event and no safety consequences resulted from the condition. However, this event is of regulatory significance because it resulted in a condition prohibited by the TS.
4432007002 | Seabrook | 04/05/2007 | 05/24/2007 | ML07149050 | <strong>Incorrect Valve Stroke Time Renders Emergency Feedwater Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2007 with the unit in Mode 1 at 100% power, Seabrook Station declared the turbine-driven emergency feedwater pump (TDEFWP) inoperable because the turbine steam supply valve stroke time was outside its acceptable limit. The design basis stroke time for the steam supply valve is five to 15 seconds; however, a review of past surveillance tests revealed that the actual stroke time was less than five seconds. This condition, which rendered the TDEFWP inoperable, existed on three occasions because the surveillance test for measuring the valve's stroke time incorrectly specified a minimum stroke time of four seconds rather than five seconds. The valve stroke time was adjusted and restored to an acceptable value. The cause of the even the was a human error in 1989 that failed to identify that a design change inserted an incorrect minimum stroke time in station documents. While the technical specifications require a plant shutdown if an emergency feedwater pump is inoperable for greater than 72 hours, the plant continued to operate in Mode 1 for more than 72 hours on three occasions with the TDEFWP inoperable. Consequently, this event resulted in a condition prohibited by the technical specifications. The TDEFW pump remained functional and no adverse consequences resulted from this event.
4452007001 | Comanche Peak 1 | 11/21/2007 | 01/17/2008 | ML08024025 | <strong>Emergency Diesel Generator Inoperable for Longer Than Allowed by TS due to Paint on Metering Rod</strong><br /><i>Abstract:&nbsp;</i>On November 21, 2007, at 1020 hours Comanche Peak Nuclear Power Plant (CPNPP) Unit 1 was in Mode 1 operating at 100% power. During a monthly surveillance test on the Unit 1 Train B Emergency Diesel Generator (EDG), the EDG failed to start as required. During troubleshooting activities, a technician identified what appeared to be paint residue from a small drop of paint on one of the fuel pump control racks. The residue was removed and at 2132 the EDG was successfully started, declared operable, and returned to service. The most probable cause for this event was determined to be a paint drop that was not cleaned off of the 6L fuel pump control rack following painting activities on the EDG. This paint drop is believed to have prevented the operation of the control rack, which subsequently prevented the entire mechanical linkage from rotating. The lack of movement precluded sufficient fuel from being admitted to all of the cylinders which prevented the engine from starting. Corrective actions include procedure revisions to require a post maintenance "pull test" of the fuel pump control rack mechanisms and to require "as you go" inspection and cleanup when painting around sensitive components, and enhancement of prejob briefings for painters to heighten their sensitivity to this type of event. All times in this report are approximate and Central Time unless noted otherwise.
4542007002 | Byron 1, Byron 2 | 10/19/2007 | 03/05/2008 | ML08066054 | <strong>Technical Specification Required Shutdown of Unit 1 and Unit 2 due to an Ultimate Heat Sink Pipe Leak Common to Both Units</strong><br /><i>Abstract:&nbsp;</i>The Ultimate Heat Sink is a common system to Unit 1 and Unit 2 and consists of two mechanical draft cooling towers and basins (i.e., 0A and 0B) and a water makeup system. Each tower consists of four separate cooling cells. The station was in the process of assessing pipe wall thickness on the riser piping of each cell. On October 19, 2007 at 1730 hours, the riser piping of the C cell in the 0A tower was being cleaned of corrosion buildup in order to obtain accurate ultrasonic wall thickness examinations. During the course of this cleaning effort, a small hole was created in the pipe and it started to spray water. The leak was estimated as 10 gpm. The pipe was declared inoperable. This section of pipe cannot be isolated from the other cells on the 0A tower, consequently the 0A tower (i.e., four cells) was also declared inoperable. Technical Specification Limiting Condition for Operations 3.7.9, "Ultimate Heat Sink," Condition G was entered for both Units 1 and 2. Condition G required both units to be place in Mode 3 in six hours and Mode 5 in 36 hours. Both units were brought to Mode 5 by 0001 hours, on October 21, 2007. Causes were determined to be general and pitting corrosion caused by long term exposure of the non-protected carbon steel pipe to misting air/water environment, failure to identify weaknesses in processes that led to ineffective decision-making affecting issue prioritization, and less than adequate procedural guidance related to monitoring degradation of safety related external pipe corrosion. Corrective actions include replacement of the degraded piping and upgrading identified process weaknesses.
4542007003 | Byron 1 | 10/05/2007 | 03/03/2008 | ML08064058 | <strong>Technical Specifications Non-Compliance on a Single Reactor Trip lnstrument Channel due to an lnstrument Maintenance Procedure Revision Error</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2008, during the performance of the Channel Operational Test (COT) for the 1B Reactor Coolant (RC) Delta T/T-Average protection channel, an Instrument Maintenance Department technician (non-licensed) questioned and subsequently validated that the COT procedure contained an incorrect jumper configuration on a lead/lag circuit card that provides dynamic compensation to the Delta T signal. An ensuing investigation revealed this incorrect configuration was installed on the lead/lag circuit card using this incorrect procedure during the previous execution of the 1B Delta T/T-Average channel COT on October 5, 2007. Consequently, the Technical Specification Reactor Trip functions of Overtemperature Delta Temperature and Overpower Delta Temperature for the 1B RC Delta T channel were unknowingly inoperable for approximately 80 days. During the revision development process for the 1B Delta T/T-Average channel COT procedure, the jumper positions for the lead/lag card were inadvertently transposed from another card. The subsequent procedure review and approval process did not identify this transposition error. The correct jumper configuration was determined and the 1B Delta T/T-Average procedure revised to restore the circuit card to the proper configuration. An extent of condition review was conducted with other procedure revisions involving the personnel involved in preparation and review. No similar discrepancies were discovered, such that the error was limited to the 1B Delta T/T-Average channel.
4552007001 | Byron 2 | 04/09/2007 | 06/08/2007 | ML07159021 | <strong>Reactor Pressure Vessel Head Control Rod Drive Mechanism Penetration Nozzle Weld Indication Due to an Initial Construction Weld Defect Allowing the Initiation of Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>In accordance with NRC order EA-03-009, "Issuance Of Order Establishing Interim Inspection Requirements For Reactor Pressure Vessel Heads At Pressurized Water Reactors," Byron’s Unit 2 reactor head was ranked in the low Primary Water Stress Corrosion Cracking (PWSCC) susceptibility category. This low ranking required the initial Control Rod Drive Mechanism (CRDM) penetrations volumetric examinations to be completed in the recent spring 2007 refuel outage (B2R13). During the B2R13 volumetric examination of the Unit 2 CRDM penetration nozzle 68, an ultrasonic test (UT) indication was discovered. Subsequently, bare-metal visual examination was completed, and no evidence of boric acid was identified. A boat sample from CRDM penetration 68 was obtained and analyzed. The root cause was determined to be a lack of fusion during initial construction fabrication that resulted in a weld defect. The weld defect allowed initiation of PWSCC. The indication was repaired and the reactor vessel head returned to service. Future inspections will occur in accordance with NRC Order EA-03-009. This condition had minimal safety consequences. The CRDM penetration indications were identified prior to any through-wall leakage. This condition is reportable to the NRC in accordance with 10 CFR 50.73 (a)(2)(ii), as a condition that resulted in a principal safety barrier being seriously degraded.
4562007001 | Braidwood 1 | 06/27/2007 | 08/27/2007 | ML07240007 | <strong>Unit 1 Reactor Trip Following a 345 Kv Transmission Line Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2007, at 0921 hours, Braidwood Unit 1 reactor tripped from 100% power following a grid disturbance on a 345 Kv transmission line due to a lightning strike. This disturbance caused an actuation of protective relays for the 1D reactor coolant pump. The shutdown of the reactor coolant pump (RCP) resulted in a rapid reduction of coolant flow in the 1D reactor coolant loop and subsequent Reactor Protection System actuation to trip the Unit 1 reactor. Operator response to the trip was proper and all safety related systems, structures and components operated normally during this event. The Root Cause of the Unit 1 trip was determined to be a latent design weakness in the RCP protective scheme that permitted the existence of an undetected component failure creating a grid disturbance-intolerant vulnerability. Corrective actions in response to this issue include revising identified procedures to perform monitoring of the integrity of critical fuses within trip-sensitive protective relaying circuits, and implementation of design changes to reduce or eliminate the identified vulnerability from the RCP protective relaying system, or if design changes are not appropriate, develop alternate actions to address the vulnerability. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the Reactor Protection System (Reactor Trip) and the Auxiliary Feedwater System.
4562007002 | Braidwood 1 | 09/22/2007 | 11/21/2007 | ML07325035 | <strong>Unit 1 Power Range N43 Positive Rate Trip Inoperable due to Miscalibration of Time Constant</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2007, Braidwood Unit 1 was operating at full power. At 1346 hours, Technical Specification Limiting Condition for Operation Action Requirement 3.3.1, Conditions A, D and E were entered to perform an eighteen month channel calibration of nuclear instrumentation system power range channel N43. During the calibration, the as found value for the N43 rate circuit positive rate trip time constant was found with an out-of-tolerance value of 1.68 seconds. This value was below the Technical Specification requirement of greater than or equal to 2.0 seconds. Following proper notifications, the calibration surveillance was completed, with all as left values in tolerance, and N43 was returned to an operable status. The past operability review determined that during the last 18-month calibration completed on March 8, 2006, the time constant value was inaccurately calculated. The two root causes of the March 2006 calibration error were: 1) inattention to detail on the part of the instrument Maintenance technician; and 2) failure to perform a procedurally required independent verification of calculated data. The corrective actions to prevent recurrence include counseling the involved individual for failure to properly perform the surveillance calibration, and revising the power range surveillances to clearly indicate how the time constant is to be calculated, including requirements for independent verifications for the chart trace calculations. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to10CFR50.73(a)(2)(i)(B).
4562007003 | Braidwood 1 | 10/24/2007 | 12/21/2007 | ML08009055 | <strong>Improper Installation of Insulation on the Unit 1 Main Steam Safety Valves</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2007, at 0917 hours, Braidwood Unit 1 entered Mode 3 while returning to power from a refueling outage. A Mechanical Maintenance supervisor observed that insulation was installed on the five main steam [SB] header safety valves (MSSVs) for both the 1A and 1D main steam lines. On October 26, 2007, with Unit 1 in Mode 1, the insulation was removed from the valves. Following a review by the safety valve program engineer, it was determined that the insulation posed an operability issue due to the potential impact on the MSSVs’ setpoint. Based on information from the MSSV manufacturer, and later confirmed through testing, the insulated MSSVs were considered inoperable for a period of time greater then allowed by Technical Specifications, therefore, this event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B). The cause of the installation of insulation and associated MSSV inoperability was the breakdown in the application of established engineering fundamentals in various parts of the Engineering Organization. The corrective actions included removal of the insulation on the MSSVs to restore the MSSVs to the condition in existence at the time the setpoints were established. On December 9, 2007, with Unit 1 in Mode 1, trevitesting was performed on three of the MSSVs to verify that the MSSV springs were not subjected to temperatures that permanently affected valve operability. Additional actions included testing of a spare MSSV on December 15-16, 2007, mimicking actual plant conditions, to determine the MSSV Operability impact of the installation of the insulation. There were no safety consequences impacting plant or public safety as a result of this event.
4572007001 | Braidwood 2 | 08/23/2007 | 10/22/2007 | ML07305033 | <strong>Unit 2 Manual Reactor Trip due to High Condenser Backpressure Resulting from Circulating Water Pump Trips</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2007, at 1530 hours, Braidwood Unit 2 reactor manually tripped from 100% power following the automatic trips of the 2A and 2B circulating water pumps due to sudden spiking of the inlet traveling screen water level differential. Operator response to the trip was appropriate and all safety related systems, structures and components operated normally during this event. The root cause of the Unit 2 trip was that the traveling screen instrumentation experienced a sudden and false high differential level indication brought on by a momentary plugging of the upstream bubbler tube. This momentary plugging was caused by agitated debris during a period of high winds. The corrective action to prevent recurrence will be to install a time delay to preclude trips of the circulating water pumps due to sudden and false high differential level indication. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the Reactor Protection System (Reactor Trip) and the Auxiliary Feedwater System.
4582007001 | River Bend | 02/06/2007 | 03/08/2007 | ML07074051 | <strong>Special Nuclear Material Inventory Error</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2007, at 6:15 p.m. CST, the determination was made that a non-irradiated traversing incore probe (TIP) was not in its expected storage location. According to the special nuclear material inventory records, the TIP was stored in a container in the radioactive waste building on the plant site. During an inspection of the container, the TIP could not be found. A subsequent investigation concluded that the TIP was likely shipped to the licensed disposal facility at Barnwell, SC in November 2000. A non-irradiated TIP typically contains approximately 0.75 milligrams of uranium-235, and has a contact dose reading of less than 0.5 millirem per hour. While the investigation indicates that the TIP was likely shipped to a licensed disposal facility, this condition is being conservatively reported in accordance with 10CFR20.2201(a)(1)(ii) as a loss of licensed material of a quantity greater than ten times the quantity specified in Appendix C of that part.
4582007002 | River Bend | 05/04/2007 | 06/29/2007 | ML07184016 | <strong>Unplanned Manual Reactor Scram Due to Loss of Cooling on No. 2 Main Transformer</strong><br /><i>Abstract:&nbsp;</i>At 1256 CDT on May 4, 2007, an unplanned manual reactor scram was initiated following the loss of cooling on the No. 2 main transformer. Reactor power at the time of the scram was approximately 67 percent. Following the scram, reactor water level briefly decreased below Level 3 as expected, resulting in the automatic closure of two containment isolation valves in the suppression pool cleanup system. This isolation was confirmed to have occurred as designed. Control of reactor pressure and water level was promptly established. No emergency coolant injection system actuation was required.This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as a condition that resulted in the unplanned manual actuation of the reactor protection system. The loss of cooling to the transformer resulted from an electrical fault in the cooling system control cabinet caused by rainwater intrusion. The cabinet was repaired and sealed, and preventative maintenance procedures are to be enhanced to prevent recurrence. The plant responded to the manual scram as expected, thus this event was of minimal safety significance.
4582007003 | River Bend | 05/21/2007 | 07/19/2007 | ML07211021 | <strong>Unanalyzed Condition of Emergency Diesel Generator in Post-Fire Safe Shutdown Scenario</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2007, a review of industry operating experience (OE) related to emergency diesel generators (DG) found a condition which is not consistent with the assumptions of the River Bend Station (RBS) post-fire safe shutdown analysis. That analysis assumes that the high temperature trips on the Division 1 DG would remain active following a start signal resulting from a loss of offsite power (LOP). This OE review found that when the DG starts following a LOP, non-critical trips (such as high temperature) are bypassed. With the non-critical trips bypassed, the DG will continue to run without sufficient cooling, likely resulting in damage to the engine. It appears that, during past revisions of the safe-shutdown analyses, reviewers did not adequately assess all potential failure modes resulting from multiple spurious actuations. This is being reported in accordance with 10CFR50.73(a)(2)(ii)(B) as a condition resulting in the plant being in an unanalyzed condition that significantly degrades plant safety. This condition does not cause the Division 1 DG to be inoperable with respect to its function required in the accident analysis and Technical Specifications. A pre-existing Standing Order that prohibits welding and grinding in the main control room during Modes 1, 2, and 3 was revised to specifically address this condition.
4582007004 | River Bend | 08/15/2007 | 10/11/2007 | ML07289035 | <strong>Emergency Diesel Generator Failed Surveillance Test due to Paint on Fuel Injector Control Linkage</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2007, at 9:29 PM, the Division 2 emergency diesel generator (DG) was started for a scheduled surveillance test. The plant was operating at 100 percent power at the time of the test. One acceptance criterion for the test requires generator output frequency to be stabilized between 58.8 and 61.2 hertz within 10.0 seconds of the start signal. The DG failed to meet this criterion, taking 13.1 seconds to stabilize within the required frequency range. As the DG did not meet the acceptance criterion required by Technical Specifications, it was shut down and declared inoperable. An examination of the DG found that the fuel injector metering rods were fouled with paint over spray. This was caused by inadequate planning and controls of the painting in the DG room. It was determined that this condition had existed for approximately 4 months. Since this period exceeds the allowable outage time for the DG, this event is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications. Analysis of tests performed in the interim period concluded that the DG was capable of controlling electrical load and reaching the test load range of 3000-3100 KW with paint on the fuel injection pump metering rods. There was no loss of safety function of the emergency electrical supply system as a result of this condition.
4582007005 | River Bend | 09/26/2007 | 11/14/2007 | ML07324029 | <strong>Unplanned Reactor Scram During Surveillance Testing due to Damaged Terminal Board</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2007, at 10:42 pm CDT, an unplanned automatic reactor scram occurred while the plant was operating at 100 percent power. At the time of the event, scheduled surveillance testing was in progress for a functional test of the average power range monitor (APRM) channel "A". Part of the test procedure involved the actuation of the Division 1 reactor protection system (RPS) trip circuitry. When this action was taken, 36 reactor control rods ("Group 2" rods) unexpectedly inserted into the core. As the reactor operator was taking actions to respond to this condition, an automatic reactor scram was generated by a low reactor water level (Level 3) signal. This event is being reported in accordance with 10CFR50.73(a)(2)(iv) as an automatic actuation of the reactor protection system. The investigation found that a terminal block and wiring had been damaged by overheating due to a loose terminal screw, which had caused a loss of power to the scram valve pilot solenoids on the Group 2 rods. This loss of power was not apparent to the operators, as it occurred in a part of the circuit downstream of the power status lights. The damaged components were repaired, and similar circuits were inspected for loose terminals.
4582007006 | River Bend | 11/07/2007 | 01/02/2008 | ML08008003 | <strong>Unplanned Reactor Scram due to Transformer Fault</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2007, at 3:06 a.m. CST, an unplanned manual reactor scram was initiated following the loss of the operating condensate pumps. The plant was operating at 75 percent power at the time. The main condensate pumps tripped when power was lost on the "A" non-safety 13.8kv bus, in addition to numerous 480v load centers supplied by that bus. The loss of that 13.8kv bus occurred when a rodent inside a transformer enclosure supplied by that bus caused arcing across phases and to ground. The slow action of the circuit breaker feeding the faulted transformer caused the main feeder breaker to the "A" 13.8kv bus to trip. Following the scram, reactor water level decreased below the actuation setpoint of the high pressure core spray (HPCS) system and the reactor core isolation cooling (RCIC) system, both of which started automatically as designed. Due to the loss of electrical power, the normal service water system was being supplied by only one 50 percent capacity pump, resulting in an abnormally low header pressure. The standby service water system was being placed into service to raise header pressure when the "C" standby service water pump started automatically due to the low pressure condition (this response was as designed, considering the configuration of the system at the time). The Level 2 signal also caused actuation of the primary containment isolation valves in numerous systems, which were confirmed to have responded as designed. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an unplanned manual actuation of the reactor protection system, as well as the automatic actuations of the HPCS, RCIC, standby service water, and primary containment isolation systems.
4612007001 | Clinton 1 | 02/07/2007 | 08/16/2007 | ML07235007 | <strong>Inadequate Consideration of Vortexing in Design Calculations</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2007, the Nuclear Regulatory Commission (NRC) issued a White Finding and Notice of Violation, for failure to select an appropriate method for calculating the minimum elevation (i.e., the analytical level) of water above the high pressure core spray (HPCS) pump suction line to preclude vortex formation and subsequent air entrainment in the pumps suction. The finding identified that prior to August 12, 2006, the initiation of suction transfer from the reactor core isolation cooling (RCIC) water storage tank to the suppression pool, as derived by calculation, may not prevent significant air entrainment in the suction of the HPCS pump and subsequent loss of function of the HPCS pump. As a result, the analytical level could have resulted in significant air entrainment potentially causing the HPCS system to be incapable of completing its safety function. A root cause evaluation determined that the cause of this event was the failure to adequately evaluate the uncertainties and associated margins in the calculation used to determine the suction transfer point. Corrective action for this event includes installation of a plant modification to increase the submergence of the suction piping in the RCIC water storage tank to preclude possible vortex formation and air entrainment. This modification was installed August 12, 2006.
4612007002 | Clinton 1 | 03/15/2007 | 05/10/2007 | ML07141018 | <strong>Improper Installation of Stanchions in Containment Pool Swell Zone</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2007, it was observed that four stanchions, used to post a radiologically contaminated are in the containment building, were improperly installed. The stanchions, used for holding a nylon rope boundary around the contamination zone, were not secured to the grating in accordance with procedure requirements. Plastic tie wraps were used to hold the stanchions in place rather than grating clips withhold-down bolts. An engineering analysis determined that the stanchions were within the suppression pool swell zone subject to hydrodynamic loads following a loss of coolant accident (LOCA), and had the potential to become dislodged and damage plant equipment. The analysis determined that a stanchion striking a nearby containment isolation valve during a concurrent LOCA and Loss of Offsite Power (LOOP) event could affect containment isolation capability. Since it was determined that these stanchions had been installed during periods of diesel generator inoperability, the containment isolation function could have been affected. The root cause determined that radiation protection technicians had a knowledge gap on the requirements of the procedure used for stanchion placement in containment. This event will be emphasized in initial and continuing training for radiation protection technicians.
4612007003 | Clinton 1 | 06/18/2007 | 08/16/2007 | ML07235007 | <strong>IGSCC Causes Pressure Boundary Leak and Reactor Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 6/18/07, at 0433 hours, the Main Control Room (MCR) received alarms indicating a steam leak in the Drywell (DW). At 1241 hours, Operators decided to perform a plant shut down in order to assess the DW to identify and repair the steam leak. At 0635 hours on 6/19/07, with reactor power at about 1 percent, Maintenance personnel entered the DW and found pressure boundary leakage on a one-inch diameter ASME Section III Class II stainless steel braided, flexible hose assembly on the "C" Main Steam Line flow elbow low-pressure instrumentation tap. On this basis, operators entered the actions of Technical Specification 3.4.5, which required a plant shutdown due to reactor coolant pressure boundary leakage. The cause of this event was Intergranular Stress Corrosion Cracking (IGSCC). Corrective action for this event is to replace in-service flexible hose assemblies installed in IGSCC susceptible locations. Susceptible flexible hose assemblies not currently in service will be cut out and the lines will be capped. Preventive maintenance will be established to periodically replace susceptible flexible hose assemblies installed in IGSCC susceptible locations.
4822007001 | Wolf Creek | 07/08/2007 | 09/06/2007 | ML07255049 | <strong>Emergency Diesel Generator Out of Service Longer than Technical Specification Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2007, the Emergency Diesel Generator A (EDG A) was declared inoperable to perform a scheduled surveillance. During the surveillance test, increased leakage was detected on the engine-driven inter cooler pump shaft seal in excess of the leakage limit of 9.1 ml/min. During repairs to the intercooler pump shaft seal, the pump impeller, wear rings and shaft bearing were replaced. Post maintenance checks discovered a leak on the jacket water pump seal and that the gear box that drives both the intercooler and engine-driven jacket water pumps was abnormally hot. After the pump was disassembled, it was found that the sleeve bearing and shaft were damaged and needed to be replaced. Maintenance to repair the sleeve bearings and the shaft and required post-maintenance testing would result in exceeding the 72 hour allowed outage time (AOT) of Technical Specification 3.8.1, Action B.4.1. On July 8, 2007, Wolf Creek Nuclear Operating Corporation requested a Notice of Enforcement Discretion (NOED) to extend the AOT for EDG A an additional 48 hours to allow completion of the necessary repair and testing to restore EDG A operability. The NRC granted the NOED on July 8, 2007. EDG A was repaired, tested, and declared operable on July 9, 2007.
4832007001 | Callaway | 02/28/2007 | 04/12/2007 | ML07109016 | <strong>Single Train Inoperability in the Essential Service Water System due to Inadequate Valve Closure Setup</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2007, during a preventive maintenance activity excessive valve seat leakage was identified on one of two isolation valves between the Service Water system and the A train of the Essential Service Water system. The affected valve was a 30 inch butterfly valve without a hard seat.Troubleshooting activities determined there was no evidence of degradation, correction of the leakage required only an adjustment of the valve operator closure limits to ensure the valve disk and valve seat were properly mated when the valve operator reached the closed position. A review of work history on the valve revealed that work performed in July, 2006, could have impacted the valve closure limits. Post Maintenance Testing included Motor Operated Valve diagnostics testing to verify the closure limits instead of a more definitive leakage test. Since the diagnostics may not have established the proper closure limits, the leakage was assumed to have existed since restoration of the valve to service on July 28, 2006. Based on the technical specification surveillance requirements for the valve, the excessive leakage rendered the A Essential Service Water train inoperable during the period of excessive leakage.The specified safety functions of the train, however, would have been completed by the redundant isolation valve. A root cause analysis team identified root causes predominantly related to inadequate written instructions for post maintenance testing of this type of valve.
4832007002 | Callaway | 03/09/2007 | 05/08/2007 | ML07135025 | <strong>Manual Reactor Trip at Reduced Power due to Inadequate Feedwater Control</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2007, while operating at 100 percent power, Callaway Plant experienced a main condenser tube leak. At 0824, high sodium levels were indicated in the main steam condenser, requiring power reduction to less than five percent power until all Action Levels for condenser sodium were exited. The on-shift Operations crew began reducing power to enter MODE 3 in accordance with procedural guidance. During the transition from the Main Feedwater Regulation Valves (MFRV) to the Main Feedwater Regulation Bypass Valves(MFRBV), problems were experienced controlling water level in the "C" steam generator (S/G). At 1043, with both the MFRV and MFRBV indicating closed and the "C" S/G level still increasing, the reactor was manually tripped. The level control problem was attributed to a failed 1/P positioner on the MFRV. The controller was replaced with a like kind controller. Digital rod position indication for control rod K10 failed during the event. The control rod was fully inserted. This failure was attributed to a bent connector pin in the digital rod position indication system. The connector pin was repaired and tested satisfactorily.
4832007003 | Callaway | 06/09/2007 | 08/30/2007 | ML07254062 | <strong>1 OTDT Channel Inoperable for Greater than TS Allowable Time</strong><br /><i>Abstract:&nbsp;</i>During calibration of Reactor Coolant System (RCS) Temperature Loop 3 on June 30, 2007, problems were identified which called into question the validity of a previous calibration on Loop 2. On June 30/July 1, 2007, Reactor Coolant System (RCS) Temperature Loop 2 calibration surveillance was performed to verify the results from the last loop calibration performed on June 9, 2007. It was determined that the Lower Flux input to the Over Temperature Delta Temperature (OTDT) setpoint circuit was Out of Tolerance (OOT). This condition was determined to have been sufficient to cause the OTDT setpoint to exceed its Technical Specification Allowable Value. The Loop 2 OTDT setpoint was inoperable for 21 days. The Temperature Loop 2 setpoint was returned to the correct value on July 1, 2007. When RCS Temperature Loop 2 was calibrated on June 9, 2007 a wrong test configuration was used when making connections to simulate the Lower Flux input to the flux imbalance penalty circuitry in the Westinghouse 7300 system. The negative power supply lead must be grounded to properly simulate the input from the Nuclear Instrumentation System (NIS) cabinets; during the June 9, 2007 calibration this was not established. The calibration was performed on July 1, 2007 using the proper configuration. The loop calibration procedures have been revised to ensure the basis for this ground connection is clear.
4982007001 | South Texas 1 | 12/12/2006 | 08/07/2007 | ML07227008 | <strong>Turbine-Driven Auxiliary Feedwater Pump Failed to Start During Surveillance Testing (Supplement 1)</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2006, the Unit 1 turbine-driven auxiliary feedwater pump failed to start during a surveillance test. It had previously passed surveillance testing on November 16, 2006. A motor-operated valve controlling steam flow to the turbine did not open. Subsequent review determined that the cause of the failure to start originated during the previous surveillance test. As a result, the pump is considered to have been inoperable from November 16, 2006, to December 14, 2006. Technical Specification 3.7.1.2.b requires that, with the turbine-driven auxiliary feedwater pump inoperable, it is to be restored to operability within 72 hours or the unit is to be in hot standby within the next 6 hours and in hot shutdown in the following 6 hours. Because this pump was inoperable longer than allowed under the Technical Specifications without entering the appropriate action statements, this event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The closed motor-operated steam inlet valve was found with the valve actuator in the open position. Subsequent review determined that the latching mechanism had not been fully engaged. The root causes were determined to be inadequate maintenance instructions and a latching mechanism that was not easily set correctly. For corrective actions, maintenance instructions have been revised and determination will be made if modification of the latching mechanism is feasible. Only Unit 1 was affected. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
4982007002 | South Texas 1 | 05/17/2007 | 07/16/2007 | ML07205033 | <strong>Entry into TS 3.0.3 for Greater Than 1 Hour due to Inoperable Degraded Voltage Relays</strong><br /><i>Abstract:&nbsp;</i>At 0800 on May 17, 2007, with Unit 1 at 100% power, surveillance testing was commenced on the Train B 4160 V ESF Bus Degraded Voltage Relays. Shortly thereafter, a broken lug was discovered in the Train B 4160 V ESF Bus relay protection and metering cabinet, which affected DC control power to all four Train B degraded voltage relays, and would have prevented the relays from actuating. At 0839, all four Train B degraded voltage relays were declared inoperable and TS 3.0.3 was entered. At 0939 hours, Operations personnel entered the plant shutdown procedure (no power reduction occurred) in accordance with TS 3.0.3, and at 1041 hours TS 3.0.3 was exited following successful replacement of the lug, which restored DC power to the four degraded voltage relays. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment. The root cause of the lug failure was determined to be low cycle fatigue failure induced by the opening and closing of the associated cubicle door. Corrective actions include replacement of the failed lug and inspection of the other Unit 1 and 2 4160 V ESF Buses for similar wiring conditions. Additionally, the Unit 1 Train B 4160 V ESF switchgear cubicle 2 wire bundle between the door and cubicle will be replaced and a support bracket will be installed during the next refueling outage.
4982007003 | South Texas 1 | 04/13/2007 | 12/04/2007 | ML07345032 | <strong>Incorrect Count Rate Board Installed in Extended Range Nuclear Instrumentation Channel</strong><br /><i>Abstract:&nbsp;</i>At 1900 on April 6, 2007, with Unit 1 at 100% power, Extended Range Nuclear Instrumentation Channel NI-46 was declared inoperable due to erratic indication. Subsequent troubleshooting identified that the "A4" Log Count & Rate circuit board was defective and needed to be replaced. Based on available replacement boards whose design would permit installation in either an A2 or A4 card slot, in addition to an incorrect decision to use the wrong type replacement board, an "A2" model card was used as a replacement and Channel NI-46 was declared operable at 0456 on April 7, 2007. Subsequently, on April 14, 2007, while troubleshooting erratic / unexpected count rate and start-up rate indications on NI-46 it was identified that the A2 board installed in the A4 slot on April 7, 2007 was the wrong type of board which caused the startup rate indication to read higher than it should in addition to the shutdown monitor reading lower than expected. Therefore, Extended Range Channel NI-46 had been inoperable since April 6, 2007. Following replacement of the A2 board with the correct A4 board, NI-46 was successfully returned to service and declared operable at 2310 on April 14, 2007. However, the total time that NI-46 was inoperable had exceeded the 7-day Allowed Outage Time permitted by TS 3.3.3.6, therefore resulting in a 10 CFR 50.73 reportable occurrence as a condition prohibited by TS. The causes of the event were (1) The Extended Range Nuclear Instrumentation vendor (Gamma Metrics) made a change to the A2 and A4 circuit boards that removed the slot interchangeability design without notification to STPNOC; and (2) the decision to use the A2 board as a replacement part instead of the A4 board based on outdated information from Training material and the use of stock code information rather than manufacturer's part number information from the Master Parts List. Corrective actions include the addition of a QC inspection hold point to the Master Equipment Database / Master Parts List to confirm all incoming A2 and A4 boards have only one key on each board (specific to its respective signal processing assembly slot), and all A2 and A4 boards in the warehouse will be inspected and any double-keyed board will be disposed of. This event did not have an adverse affect on the health and safety of the public.
4992007001 | South Texas 2 | 03/14/2007 | 05/10/2007 | ML07135041 | <strong>Auxiliary Feedwater Pump Inoperable Longer Than Allowed under Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2007, Unit 2 Auxiliary Feedwater Pump 23 was started for a post maintenance test. During the test, it was noted that the pump discharge flow was not as expected. Investigation determined that the closed Long Path Recirculation Isolation Valve 2-AF-0092 was leaking by its seat. It was determined that there was no lubrication of the portion of the valve stem just below the actuator. When the valve actuator was disassembled, the stem nut was found broken into two pieces. The valve was repaired and lubricated on March 9, 2007. The operational impact of this condition was that the design bases flow to the steam generator was not achieved for this condition such that Auxiliary Feedwater Pump 23 and its associated flow path were inoperable. On March,14, 2007 it was determined that this condition existed for a period of time longer than the allowed outage time of the Technical Specifications. The cause of the stem nut failing is that no periodic preventive maintenance existed to lubricate the stem. Corrective actions include (1) repair and lubrication of 2-AF-0092, (2) verification of the functionality of the long path recirculation isolation valves for each AFW System train in both units, (3) cleaning, lubrication and inspection of auxiliary feedwater system long path recirculation isolation valves in both units, (4) review of the adequacy of current preventive maintenance scope and frequencies of risk-significant valves in the auxiliary feedwater system and (5) revision of surveillance procedures to include testing to verify that the auxiliary feedwater flow path long path recirculation isolation valves do not have seat leakage. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment. The event was of very low safety significance.
5282007001 | Palo Verde 1 | 07/05/2007 | 09/07/2007 | ML07262015 | <strong>Technical Specification Prohibited Condition due to Check Valve Not Fully Seated</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2007, with Unit 1 in MODE 3, Hot Standby, a containment isolation check valve failed to fully seat as indicated by surveillance testing. Containment Isolation check valve 1PSIEV123 (SI-123) was not in its fully seated position at the time of entry into a condition that required the valve to be OPERABLE. The check valve is a Borg-Warner (B-W), 3 inch, ASME Class 2, bonnet hung, swing check valve, located on the high pressure safety injection system (HPSI) cold-leg injection piping inside containment. This check valve functions as a containment isolation valve that is open during certain accident conditions. The valve internals were replaced and surveillance testing was successfully performed. Preliminary investigation results indicate the valve failure is attributable to binding in the spherical bearing resulting from excessive wear between the spherical bearing and the swing arm. A similar event was reported in LER 1-2006-005-00 for a failure of a B-W Low Pressure Safety Injection (LPSI) valve in November 2006.
5282007002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 07/10/2007 | 09/07/2007 | ML07262015 | <strong>Train B Class 1 E Pressurizer Backup Heater Control Circuit Would Not Be Properly Isolated for a Control Room Fire Event</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2007, during a 10 CFR 50 Appendix R review by Fire Protection Engineering, it was determined the control room circuit of the Train B class-1E pressurizer backup heaters would not be properly isolated for a control room fire event. During a control room fire event, procedures provide instruction to transfer all the Local/Remote (L/R) transfer switches to the local position. This action isolates the control room circuits associated with components required to shutdown the unit for a control room fire event. When the L/R switch associated with the Train B Class-1E pressurizer backup heaters is in the local position, a postulated line to ground fault on the conductor (wire 51 - positive line) in conjunction with a negative line to ground fault from the same battery system could cause a 10 amp fuse to fail open. This would prevent the breaker from closing from the remote shutdown panel resulting in the loss of Train B Class-1E Pressurizer backup heater local control. Palo Verde has revised the Control Room Fire procedure to add instructions to close the local manual breaker in the Train B switchgear room. In the past three years, Palo Verde has not identified a similar Appendix R issue.
5282007003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 07/13/2007 | 09/11/2007 | ML07262012 | <strong>Inadequate Surveillance Test Procedure Resulting in Failure to Meet TS Requirements</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2007, with Unit 1 in Operating MODE 3, and Units 2 and 3 both in Operating MODE 1 at approximately 100 percent rated thermal power, during performance of a Component Design Basis Review (CDBR), station personnel determined that Surveillance Test Procedure (STP), 40ST-9AF07, "Auxiliary Feedwater Pump AFA-P01 Monthly Valve Alignment," did not adequately meet its intent to satisfy Technical Specifications (TS) Surveillance Requirement (SR) 3.7.5.1 for position verification of the steam admission bypass valves to Auxiliary Feedwater Pump AFA-P01. Specifically, the STP did not provide adequate verification of the position of valves SGA-UV-134A and SGA-UV-138A. The STP was revised to include the affected valve position verification and was subsequently successfully performed. The root cause investigation is in progress. LER 50-528/2004-011 reported a failure to adequately meet a TS SR due to a failure to include required steps in an STP. The actions taken as a result of that event would not have prevented this event from occurring.
5282007004 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 08/11/2007 | 10/10/2007 | ML07291022 | <strong>Inadequate Surveillance Test Procedure Resulted in Failure to Meet Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2007, Palo Verde Units 1, 2 and 3 were in Operating Mode 1 (Power Operations), at approximately 100 percent rated thermal power, when a void was discovered in the Unit 1 Containment Spray (CS) "B" header, which was not in compliance with Technical Specification (TS) Surveillance Requirement (SR) 3.6.6.2. The direct cause of the void in the CS header was that the Unit 1 "B" CS Header was not properly vented during the fill and vent process on July 1, 2007. The root cause of this condition was ineffective use of operating fundamentals during the pre-job briefing, resulting in failure to identify the potential for air entrapment during the fill and vent process on July 1, 2007. Subsequent investigation determined that the Surveillance Test Procedure (STP) for all three units did not adequately satisfy the requirements of the TS SR to demonstrate that the CS headers were full of water. The direct cause for the identified failure to properly meet the TS SR to verify the CS header is full was a procedural deficiency in that STP 40ST-9SI13, "LPSI and CS System Alignment Verification" did not adequately demonstrate compliance with TS SR 3.6.6.2. Ultrasonic Testing (UT) was performed on all CS headers in all three units to verify that they were full of water, and a small void in Unit 3 "B" header was detected and filled and vented. UT was subsequently added to the affected STP to ensure compliance with TS SR 3.6.6.2. LER 1-2004-009-01 reported a condition in Units 1, 2 and 3 where there were voids in the Emergency Core Cooling System containment sump piping due to a failure to translate the design intent to have the line filled with water into start-up, surveillance, and operating procedures.
5282007005 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 08/21/2007 | 07/21/2010 | ML10210003 | <strong>Inadequate Surveillance Test Procedure Resulted in Failure to Meet Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2007, with Palo Verde Units 1, 2 and 3 in Operating Mode 1 (Power Operations), at approximately 100 percent rated thermal power, during performance of a Component Design Basis Review of the Auxiliary Feedwater (AF) System, station personnel determined that the existing Surveillance Test Procedures (STP) did not verify that Technical Specification (TS) Surveillance Requirement (SR) 3.3.5.4 was met for certain AF valves. TS SR 3.3.5.4 requires that the Engineered Safety Feature response time be verified every 18 months. The existing STPs did not include the response times of certain valve actuation relays and did not account for full valve stroke time. Subsequent investigation for extent of condition identified similar issues with response time testing STPs for the Main Steam Isolation Valves (MSIV), the Feedwater Isolation Valves (FWIV) and the steam admission valves to the AF System turbine driven pump. All affected valves were assessed and, when the expected additional time associated with all relay actuations and the full valve stroke were accounted for, the total response time did not exceed the TS SR limits for any of the valves. Control Room personnel entered TS SR 3.0.3 to allow a delay in the requirement for declaring the LCO not met. The cause of this event was inadequate oversight of TS required testing where testing requirements are satisfied by sequential or overlapping STPs. STPs have been revised to test the actuation and buffer relays for the affected valves. A review of TS SRs that are met through the performance of more than one test has been conducted to ensure that the TS SRs were met. There have been two previously reported conditions within the last three years where existing STPs did not verify that existing TS SRs were met.
5282007006 | Palo Verde 1 | 10/22/2007 | 12/21/2007 | ML08002000 | <strong>Required Shutdown due to Inoperable Steam Admission Bypass Supply Valve to Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2007, while performing testing per procedure 73ST-9AF02, "AFA-P01 RECIRC FLOW-INSERVICE TEST," an Auxiliary Feedwater pump turbine steam admission bypass valve, SGA-UV-138A failed to close. The valve was declared inoperable, quarantined, and a troubleshooting game plan was developed and implemented. Troubleshooting and corrective maintenance efforts were unsuccessful in restoring the valve to an operable status within the Technical Specification (TS) required action time of 7 days; therefore a reactor shutdown was initiated at 03:11 hours and completed at 05:04 hours (upon entry to Operating Mode 3), on October 22, 2007 to comply with TS Limiting Condition for Operation (LCO) 3.7.5, Condition C. The direct cause of the failure of SGA-UV-138A was the accumulation of iron oxide on the internal plunger assembly, causing excessive frictional forces between the plunger and the interior surfaces of the bonnet assembly. The root cause of the resultant reactor shutdown was ineffective implementation of the station event response and troubleshooting processes. Subsequent to the shutdown, the valve body and internals were replaced for valve SGA-UV-138A, the improper line slope upstream of the valve was corrected, and the valve was successfully retested utilizing procedure 73ST-9AF02. There has been one previous LER submitted in the past 4 years reporting the failure to complete troubleshooting and repair of a similar valve due to similar causes, resulting in a unit shutdown required by TS.
5282007007 | Palo Verde 1 | 11/22/2007 | 01/22/2008 | ML08030055 | <strong>Engineered Safety Feature Actuation and Required Shutdown due to Failed Diode in Actuation Circuitry</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2007, at approximately 19:18 hours, the "BOP ESFAS A IN TEST" alarm was received in the Unit 1 Control Room. Shortly after this unexpected alarm, other unexpected alarms were received and the essential spray pond pump started automatically. The Balance of Plant (BOP) Engineered Safety Feature Actuation System (ESFAS) Train "A" load sequencer was declared inoperable, and troubleshooting to identify the cause of the event commenced. Troubleshooting and corrective maintenance were not completed in time to restore the train to operability within the 24 hours permitted by TS Limiting Condition for Operation (LCO) 3.8.1, Condition F, and Unit 1 was shut down as required by TS LCO 3.8.1, Condition H. The direct cause of the BOP ESFAS failure was the failure of a relay coil suppression diode. The failed diode was replaced and no failures of other noise suppression diodes were identified. Following corrective maintenance and successful retest of the Train "A" BOP ESFAS load sequencer, the affected equipment was declared operable on November 25, 2007. There has been one previous Licensee Event Report submitted in the past four years reporting an Engineered Safety Feature actuation and the subsequent unit shutdown required by TS; however, the cause of that event was distinctly different from this event.
5292007001 | Palo Verde 2 | 02/19/2007 | 04/20/2007 | ML07122007 | <strong>Completion of a Shutdown Required by Technical Specification 3.5.3, Condition C</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2007, Unit 2 was In Mode 1 at approximately 100 percent rated thermal power, running the High Pressure Safety Injection (HPSI) 2A pump in support of activities to determine the leak rate of oil from the pump bearings. The oil leak rate was found to be greater than acceptable and at approximately 13:01 Mountain Standard Time (MST), Operations personnel declared the HPSI 2A pump inoperable and entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.3, Condition B, placing the plant in a 72 hour action. Corrective actions could not restore the pump to an operable status within the TSLCO allowed time. On February 19, 2007, at approximately 14:56 MST, Operations commenced a plant shutdown and at 16:45 MST, the reactor was manually tripped from approximately 20 percent power and the unit entered Mode 3. No TS LCO allowed action times were exceeded. The oil leaks were corrected and on February 22, 2007, at approximately 05:02 MST Unit 2 declared HPSI2A operable. The corrective actions were also implemented in the other five HPSI pumps on site. In the past three years, there were two events reported for a TS shutdown that became necessary when attempted repairs could not be performed within the completion time for the TS LCO required action.
5292007002 | Palo Verde 2 | 02/03/2007 | 04/04/2007 | ML07103012 | <strong>Condition Prohibited by Technical Specification - CEA Insertion Limit Exceeded</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2007, Unit 2 was in Mode 1 at approximately 100 percent power performing a surveillance test (ST) to demonstrate the operability of full strength Control Element Assemblies (CEA) by moving each CEA five inches. While performing this test, Shutdown Group B, Subgroup 6 failed to withdraw after it was successfully inserted five inches. This left the CEA Subgroup at 144 inches, which is below the limit as required by Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.6. Unit 2 entered TSLCO 3.1.6, condition A and TLCO 3.1.204 condition A at approximately 12:32 Mountain Standard Time (MST). At approximately 13:15 (MST), Unit 2 Operators entered LCO 3.0.3 due to more than one CEA inserted beyond the TS limit. At approximately 16:16 (MST) on February 3, 2007, following corrective maintenance to replace a phase synchronization card, CEA Subgroup 6 was restored above the TS 3.1.6 insertion limit and Unit 2 exited LCO 3.0.3. The cause of the failed phase synchronization card was determined to be the random failure of a ceramic capacitor. In the past three years, there were no similar events reported for multiple CEAs being inserted beyond TS Limits.
5292007003 | Palo Verde 2 | 10/06/2007 | 12/05/2007 | ML07348012 | <strong>Manual Reactor Trip due to Increased Steam Generator Sodium Levels from Failed Heat Exchanger Plug</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2007, at approximately 10:39 MST, Chemistry personnel notified Operations personnel in the Unit 2 control room that main condenser sodium levels were increasing. At approximately 10:59 MST, Chemistry personnel determined and reported that steam generator (SG) sodium levels had increased to above 1 ppm, which is the reactor trip criterion specified by procedure. Unit 2 was manually tripped at 10:59 MST from 100 % power and Operations personnel implemented standard post trip actions. The NRC Resident Inspectors were notified of the reactor trip and the NRC Headquarters was notified via the ENS at 12:32 MST (ENS #43687). The direct cause of this event was sodium ingress into the Unit 2 condenser hotwell and steam generators due to a corroded and failed tube plug in the "D" condenser air removal (AR) system seal water cooler. The root cause of the event was an error in the tube plug selection process made in January of 2001 resulting from an inadequate assessment of the tube plug material by engineering personnel. To prevent recurrence, the Unit 2 Condenser AR "D" cooler and tubes were cleaned and the tube plugs were replaced. PVNGS Maintenance Engineering personnel will determine an alternate tube plug type for the condenser AR system seal water coolers which will not be subject to corrosion or galvanic interaction with the titanium tube sheets and tubes. The existing AR system seal water cooler plugs will be replaced with the alternate plug. One LER has been reported in the past 4 years identifying a manually initiated reactor trip resulting from secondary system contaminant ingress due to a different cause.
5292007004 | Palo Verde 2 | 10/26/2007 | 12/26/2007 | ML08008042 | <strong>Inoperable Main Steam Isolation Valve Actuator Train "A" due to Inadequate Post Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>On October 26, 2007, Palo Verde Unit 2 was in Operating Mode 1 (Power Operations), at approximately 100 percent rated thermal power, when a failure occurred during Main Steam Isolation Valve (MSIV) air reservoir check valve inservice testing. The MSIV actuator train "A" was declared inoperable and troubleshooting activities were undertaken to determine the cause of the failure. Technical Specification (TS) 3.7.2, Limiting Condition for Operation (LCO) Condition A, requires restoration of the inoperable MSIV actuator train within 7 days. Troubleshooting, repair, and retest activities were completed on October 27, 2007, in accordance with an approved engineering troubleshooting, repair, and test plan. MSIV 181 was declared operable and TS 3.7.2, Condition A was exited. The direct cause of the MSIV failure was air leakage between a four-way valve and the MSIV actuator due to a missing O-ring. The subsequent root cause investigation determined that this condition resulted from inadequate post maintenance testing following the July 31, 2007, maintenance activities conducted on the four-way valve. As such, the as-found condition rendered the Unit 2 MSIV 181 (number two steam generator, steam line number two) actuator train "A" inoperable from July 31, 2007, (date of last maintenance) to October 27, 2007, (date of restored operability). This resulted in operation in a condition prohibited by TS in that the total inoperable time of the MSIV actuator train exceeded the permitted 7-day LCO action time. LER 50-529/2006-004-00 describes a failure of a four-way valve in a Unit 2 Main Feedwater Isolation Valve that resulted in a condition prohibited by TS.
5302007001 | Palo Verde 3 | 04/21/2007 | 04/07/2008 | ML08112011 | <strong>Condition Prohibited by Technical Specification Resulting from Containment Spray Nozzle Blockage</strong><br /><i>Abstract:&nbsp;</i>During an extent of condition review for events that could have led to the obstruction of the Containment Spray (CS) system, Arizona Public Service (APS) identified an April 21, 2007, event where nozzles in the Unit 3 CS system may have become obstructed. On December 5, 2007, while performing a Surveillance Test of the Unit 3 CS spray nozzles, APS personnel discovered one obstructed nozzle on each of two separate Containment Spray (CS) train 'A' lines. The evaporation of borated water from a header overfill event caused boric acid residue to accumulate and obstruct the two CS nozzles for a period greater than allowed by Technical Specification 3.6.6 limiting condition for operation. The nozzles were cleaned and restored to service on December 18, 2007. The cause of the CS overfill event was determined to be leakage by the containment spray train 'A' discharge valve seat. The cause of the Unit 3 CS system nozzles blockage was from inadequate consideration of the consequences of overfilling the CS system with borated water. There have been no previous similar events in the past three years that had a similar failure mechanism or that should have prevented this event as a result of previously implemented corrective actions.