## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192009001 | Oyster Creek | 02/01/2009 | 03/31/2009 | ML09097073 | <strong>Automatic Reactor Shutdown Caused by Main Transformer Failure</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2009 the Oyster Creek Generating Station was operating at 100% reactor power, 661 Megawatts Electric (MWE). Oyster Creek had been online for 56 days following the 1F17 Forced Outage due to the MIA transformer failure on November 28, 2008. At 2156 hours, Oyster Creek's main generator tripped due to the actuation of the 230kV bus section differential relay due to the failure of the MIA main power transformer. This caused a load reject SCRAM that automatically shut down the reactor. The transformer failure led to the declaration of an Unusual Event at 2211 hours, based on a fire lasting greater than 15 minutes affecting the M1A transformer. The fire was extinguished at 2227 hours and the Unusual Event was terminated at 2337 hours on February 1, 2009. There were no nuclear safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to the automatic reactor protection system actuation.
2192009002 | Oyster Creek | 02/02/2009 | 03/31/2009 | ML09100029 | <strong>Failure to Take the Appropriate Tech Spec Action When Primary Containment Isolation Valve Became Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0955 on February 2, 2009, a Reactor Water Cleanup System heat exchanger outlet high temperature alarm and isolation signal was received. The Reactor Water Cleanup System inlet isolation valve (V-16-1), did isolate but the heat exchanger inlet isolation valve (V-16-14), failed to close in response to the system high temperature signal. The heat exchanger outlet high temperature isolation function was not a safety function and not a Tech Spec requirement. Later troubleshooting determined that a malfunctioning relay prevented V-16-14 isolation from the heat exchanger outlet high temperature signal. During troubleshooting on February 3, 2009, Operations determined that since V-16-14 was a primary containment isolation valve, this same malfunctioning relay would have also prevented that safety function and Tech Spec 3.5.A.3 applies. The Tech Spec required actions within four hours if a primary containment isolation valve became inoperable. The relay problem was corrected and V-16-14 was returned to operable status at 1712 on February 3, 2009. Based on the above, the four-hour Tech Spec requirement was not achieved and this is being reported under 10 CFR 50.73(a)(2)(i)(B).
2192009003 | Oyster Creek | 04/25/2009 | 06/10/2009 | ML09167009 | <strong>Manual Reactor Shutdown Caused by Loss of Cooling to the Main Transformer</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2009, with the unit at 100% power, loss of cooling to the Main Power Transformer M1A resulted in a manual plant scram. The loss of cooling was caused by a faulted cooling bank motor starter, resulting in the failure of the MIA auxiliary control power transformer and subsequent loss of control power for the remaining cooling bank motor starters. A reactor load reduction was commenced in accordance with the alarm response procedure to maintain MIA temperatures below the alarm set points. While reactor power was being reduced, transformer operation was limited to 30 minutes without forced cooling. Operations secured the power reduction and manually scrammed the reactor from 74% power in accordance with plant procedures. The post scram response was normal and the required notifications were made. All safety systems operated as expected following the reactor scram. There were no safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to manual actuation of the reactor protection system.
2192009004 | Oyster Creek | 10/25/2008 | 11/12/2009 | ML09324008 | <strong>Establishment of Secondary Containment Boundary Contrary to Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>During the 1 R22 Refueling Outage (Fall 2008), a Temporary Modification was made to the secondary containment so that the trunnion room door could be left open to support maintenance activities. The Temporary Modification moved the barrier for secondary containment from the outer walls and door of the trunnion room to the inner walls, ceiling, floor, and associated penetrations in the trunnion room. A 10 CFR 50.59 Evaluation supported the Temporary Modification based on the determination that secondary containment integrity could be maintained separate from the trunnion room door and concluded that a Technical Specification change was not needed. During the NRC Plant:Modification Inspection (May 4 through 15, 2009), the determination was made that the Temporary Modification. to open the trunnion room door for extended periods of time during 1 R22 was in noncompliance with Oyster Creek's Technical Specifications. The supporting 10 CFR 50.59 Evaluation inappropriately determined that prior approval from the NRC was not needed in that the secondary containment integrity required by Technical Specification Limiting Condition of Operation (TS LCO) 3.5.B was maintained.
2192009005 | Oyster Creek | 07/12/2009 | 02/05/2010 | ML10054161 | <strong>Reactor Scram Following a Transmission Line Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2009 with the Unit at 100% power in the "Power Operation" mode, a severe electrical storm resulted in multiple lightning strikes on an interconnected 34.5 kV offsite transmission line. These lightning strikes in conjunction with a failure of a line breaker to open caused grid disturbances, a main generator trip on over-excitation, an automatic reactor scram due to the load rejection, and a loss of offsite power to the Startup Transformers. When the plant experienced the loss of offsite power to the Startup Transformers, both Emergency Diesel Generators (EDGs) started and energized their associated safety related buses. During the event, EDG #1 was slow to tie onto its safety-related bus and the erratic "B" Isolation Condenser (IC) level indication resulted in operators declaring the IC inoperable. An Unusual Event was declared for the loss of power to the Startup Transformers for greater than 15 minutes. All declarations and notifications were made correctly and in a timely manner. This event is being reported pursuant to: 10CFR50.73(a)(2)(iv)(A) due to automatic actuation of the reactor protection system, isolation condensers, and emergency diesel generators; and 10CFR50.73(a)(2)(v)(D) due to loss of offsite power to the Startup Transformers.
2192009006 | Oyster Creek | 08/03/2009 | 02/08/2010 | ML10054159 | <strong>EDG #1 Inoperable due to Failure of its Output Breaker to Close</strong><br /><i>Abstract:&nbsp;</i>On August 3, 2009, the output breaker for the Emergency Diesel Generator #1 (EDG #1) failed to close during its bi-weekly surveillance load test. EDG #1 started and came up to speed, but the output breaker did not close automatically, as expected. The cause of the EDG #1 output breaker failure to close was a failed GBC relay. EDG #1 was declared inoperable since it did not automatically load onto its bus ("C" 4160V bus). This event is being reported pursuant to 10CFR50.73(a)(2)(i)(B) due to a condition prohibited by the plant's Technical Specifications. This report also constitutes a Part 21 notification.
2202009001 | Nine Mile Point 1 | 01/26/2009 | 03/25/2009 | ML09090051 | <strong>Failure to Implement Required Technical Specification Actions Associated with Failed Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>At 0033 on January 26, 2009, at Nine Mile Point Unit 1 (NMP1), Main Steam Isolation Valve (MSIV) 01-01 failed a Technical Specification (TS) required surveillance test when it failed to re-open following a partial closure test. The failure of MSIV 01-01 to re-open was not immediately recognized as a failure to meet the TS surveillance requirement, therefore MSIV 01-01 was not declared inoperable. As a result, the required action statements to either isolate the main steam line within 4 hours, or commence a shutdown within 1 hour and be in cold shutdown within 10 hours were not implemented. The cause for the delay in declaring MSIV 01-01 inoperable was the Shift Manager became focused on assessing the safety function of the MSIV to close and did not fully evaluate the relevant TS surveillance requirement. In addition, the leadership team and the operating crew failed to provide the appropriate backup in validating the Shift Manager's decision regarding the operability of MSIV 01-01. Corrective actions in response to this event include communication of lessons learned, enhanced training for licensed operators and Shift Technical Advisors on application of TS surveillance requirements - and operability assessments, and procedure enhancements.
2202009002 | Nine Mile Point 1 | 04/10/2009 | 06/08/2009 | ML09167010 | <strong>High Pressure Coolant Injection System Initiation Following a Manual Turbine Trip Due to High Turbine Bearing Vibrations</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2009, at 0538 hours, with Nine Mile Point Unit 1 (NMP1) operating at 28 percent Rated Thermal Power (RTP), operators manually tripped the turbine in response to rising turbine bearing vibrations. Following the turbine trip, the High Pressure Coolant Injection (HPCI) System automatically initiated as designed, The HPCI System initiation signal was immediately reset. Reactor water level was maintained in the normal operating range throughout the transient. There was no reactor scram since the turbine was tripped at a power level that is below the generator load rejection scram setpoint. After determining and addressing the cause of the vibration, the turbine was restarted and the generator was synchronized to the grid at 11:39 on the same day without any complications. The HPCI System is a mode of operation that uses selected equipment of the Condensate and Feedwater System to perform its function. The HPCI System is not an Emergency Core Cooling System (ECCS). The apparent cause of the turbine trip was failure to follow an operating procedure for placing the second stage reheaters in service. To prevent recurrence, the applicable procedure has been revised to include better guidance on placing second stage reheaters in service. In addition, pre-outage Just-In-Time training material will be revised to include the proper method for placing second stage reheaters in service and to review this event as an internal operating experience event.
2202009003 | Nine Mile Point 1 | 10/05/2009 | 12/04/2009 | ML09344006 | <strong>Manual Scram and High Pressure Coolant Injection Following a Loss of Feedwater Level Control due to Firmware Deficiency</strong><br /><i>Abstract:&nbsp;</i>At 1158 on October 5, 2009, Nine Mile Point Unit One (NMP 1) was manually scrammed from approximately 100 percent rated power due to loss of control of the shaft-driven feedwater pump flow control valve (FCV), which resulted in an increasing feedwater flow rate and rising reactor pressure vessel (RPV) water level. Following the manual scram, the High Pressure Coolant Injection (HPCI) system automatically initiated on low RPV water level as designed. At 1159, RPV water level was restored above the HPCI low level actuation setpoint and the HPCI system initiation signal was reset. The root cause of the event was a programming error in the vendor-supplied firmware logic that prevented the proper operation of the transfer function of the FCV positioner when the operating positioner became mechanically bound. Instead, the FCV continued to open and raise reactor water level despite operator attempts to manually control the FCV. Immediate actions taken to prevent recurrence were to enable the FCV controller software setting for indication of a positioner spool piece binding and to increase the Position Excess alarm sensitivity. This will provide the operators with an early indication of feedwater FCV positioner degradation. The operations procedures were also improved to give direction to the operators on how to swap positioners if certain positioner alarms come in. The firmware for the FCV controller will be upgraded to ensure that conditions that indicate potential degradation in the performance of the positioner will result in a transfer to the redundant positioner.
2372009001 | Dresden 2, Dresden 3 | 10/09/2008 | 04/07/2009 | ML09106074 | <strong>Common Mode Failure of Reactor Building Isolation Dampers</strong><br /><i>Abstract:&nbsp;</i>On February 6, 2009, a review of the recent failures of Dresden Nuclear Power Station (DNPS) Unit 2 Reactor Building Ventilation (RBV) isolation dampers found that the potential existed that those failures were potentially reportable. In 2005 through 2007, several RBV isolation dampers failed the required closure time both at DNPS and another Exelon plant. Failure analyses by Exelon and the solenoid vendor identified a potential common mode failure mechanism of solenoid valve sticking due to ihadequate lubrication of the internal parts. Subsequently, in October 2008 and January 2009, failures of the Unit 2 RBV isolation dampers Occurred. The previously identified RBV damper potential common mode failure mechanism of solenoid valve sticking due to inadequate lubrication of the internal parts could have prevented the fulfillment of the safety function. All RBV isolation dampers rely on the same model solenoid valve to close and perform their safety related function to control the release of radioactive material and mitigate the consequences of an accident. For all solenoid damper failure events, at least one in-series isolation damper closed per design. Therefore, secondary containment integrity was maintained. Replacement of all RBV isolation damper solenoid valves with an upgraded model was completed in January 2009.
2372009002 | Dresden 2 | 03/15/2009 | 03/31/2010 | ML10103012 | <strong>Unit 2 High Pressure Coolant Injection Suction Valve Fails to Close</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2009, at approximately 2025 hours (CDT), with Unit 2 at approximately 100 percent power, Dresden Nuclear Power Station Operations personnel discovered during a maintenance activity that motor operated valve 2-2301-6, Unit 2 High Pressure Coolant Injection Suction Valve, would not close. The valve is a normally open valve and is required to close during the transfer of High Pressure Coolant Injection System pump suction from the Condensate Storage Tanks to the Torus to prevent high Torus water level. Troubleshooting and diagnostic testing identified that the valve's failure to close was attributed to valve internal binding. The Root Cause of this event was that when the valve was in the full open position, the center of gravity of the solid gate valve disc extends past the end of the in-body valve guides, which caused the disc to tip and bind with the in-body guides. A contributing cause to this event is increased stem friction. The higher than normal thrust associated with the binding caused a loss of stem lubricant through extrusion, which increased the friction at the stem and stem nut interface. The in-body valve guides were lengthened into bonnet to ensure the valve disc's center of gravity is supported by guides when the valve is in the Open position. Preventative maintenance activities for motor operated valve stem lubrication were revised, as needed, to ensure that the frequency does not exceed two-years for the motor operated valve program valves with horizontal disc/stem orientation that exhibit internal binding. The safety significance of the event is minimal. An evaluation concluded that HPCI would have operated long enough to fulfill its safety function. A review of the actual Torus water levels during this time frame identified that the Torus would not have exceed its structural design values during a postulated accident. Therefore, the consequences of this event had minimal impact on the health and safety of the public and reactor safety.
2372009003 | Dresden 2, Dresden 3 | 06/02/2009 | 08/03/2009 | ML09217014 | <strong>Emergency Diesel Generator Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2009, during performance of the monthly surveillance on the Unit 2/3 Emergency Diesel Generator (EDG), an oil leak of approximately one-half gallon per minute was identified at the threaded pipe plug in the center of the turbocharger lube oil system "Y" strainer end cap. Following identification of the leak, the EDG was unloaded and shut down normally. The threaded plug was then replaced and was found to be a black 3/8 inch plastic shipping plug typically installed for Foreign Material Exclusion (FME) purposes. The Unit 2/3 EDG was considered to be inoperable from April 16, 2009 to June 2, 2009, with associated actions required by the plant's Technical Specifications not being completed. Also, concurrently with the inoperability of the Unit 2/3 EDG, scheduled maintenance was performed on each of the redundant Unit 2 and Unit 3 EDGs. This minimally impacted the ability of onsite emergency power to fulfill its safety function. The Root Cause of this event was determined to be inadequate purchase order description. The corrective actions to prevent recurrence include revision of the purchase order description of the "Y" strainer to specify a pressure retaining pipe plug of appropriate material.
2372009004 | Dresden 2 | 11/02/2009 | 12/22/2009 | ML10014141 | <strong>Unit 2 Shutdown Cooling System Isolation During Cooldown due to Temperature Instrumentation Failure</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2009, during shutdown for the Dresden Unit 2 Fall 2009 refueling outage, the Shutdown Cooling (SDC) System high temperature isolation logic actuated causing the SDC isolation valves to shut, resulting in a loss of cooling to the Reactor Vessel. Troubleshooting determined that Temperature Element 2-0261-8B, a thermocouple (TC), failed. The Resistance Temperature Detector (RTD), 2-0261-8F, housed in the same assembly, had previously failed and was out of service since December 2008. The presence of an open signal from both instruments in the same recirculation loop caused the isolation logic to activate, as designed. The apparent cause was failure at the soldered TC Junction and the RTD element-to-lead solder joint attributed to corrosion and oxidation at the solder connection. A replacement switch was installed during the refueling outage. The safety significance of this event is minimal as cooling flow was restored to the vessel in approximately 40 minutes. Plant response and operator actions were consistent with plant procedures. The protection of public health and safety and personnel safety were not compromised at anytime during this event.
2372009005 | Dresden 2 | 11/03/2009 | 12/22/2009 | ML10019179 | <strong>Unit 2 Reactor Recirculation Drain Line Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2009 during a walkdown of the Unit 2 Drywell, plant personnel identified leakage from the above seat drain line for the 2B Reactor Recirculation Pump discharge valve. The water was flowing from a weld in a 3/4 inch line between a coupling and a socket-welded elbow. The diameter of the steady stream was approximately the size of a toothpick. The plant had been shutdown and the reactor vessel had been depressurized to commence refueling activities at the time of the discovery. Prior to the discovery of this condition, there was no abnormal indication in drywell leakage. This condition represents degradation to a principal safety barrier of the Nuclear Power plant. The through-wall leak was caused by fatigue cracking resulting from cyclic torsional loads of the cantilever connection most likely due to increased reactor recirculation pump vibrations. The leaking drain line was cut and capped. The plant's emergency core cooling systems were available during this condition. Therefore the safety significance of this event is minimal due to the health and safety of the public not being compromised.
2372009006 | Dresden 2, Dresden 3 | 11/12/2009 | 12/17/2010 | ML10364013 | <strong>Failure of Main Control Room Ventilation Due to Breaker Malfunction</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2009, Dresden performed a technical specification surveillance to functionally test the Unit 2 Emergency Diesel Generator under-voltage and Emergency Core Cooling integrated function capabilities. The Under-Voltage / Emergency Core Cooling System logic is designed to shed and sequence selected electrical loads onto the associated Emergency Diesel Generator (EDG) in the event of a loss of offsite power to prevent overloading the EDG. During the testing, the logic appropriately tripped the feeder breaker to motor control center 29-8, which supplies electrical power to the emergency ventilation system for the main control room. However during an attempt to reestablish the load, the feeder breaker failed to reclose. The lack of emergency power to the ventilation system rendered it incapable of performing its intended safety function. Therefore this condition is being reported as an event that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The failed breaker was replaced. The failed breaker was sent to a vendor for analysis. Based on the troubleshooting and failure analysis, the most likely cause is a buildup of lubricant and oxidation on the secondary contact slides in the breaker cubicle. The four-year preventative maintenance activity for these types of cubicles was revised to include an activity to clean the secondary contact slides with an abrasive pad to remove the buildup of baked on lubricant and oxidation. The safety significance of this event is minimal due to the health and safety of the public not being compromised. The capability to shut the plant down and maintain it in a safe condition was not compromised. Offsite power was available during the course of this event.
2372009007 | Dresden 2, Dresden 3 | 11/27/2009 | 01/22/2010 | ML10033029 | <strong>Reactor Protection System Nonconformance to a Design Standard</strong><br /><i>Abstract:&nbsp;</i>During a field walkdown while DNPS Unit 2 was in its fall 2009 refueling outage, it was identified that Reactor Protection System (RPS) Pressure Switches (PS) 2-0504-A, B, C, and D all share a common sensing line with a single isolation valve (2-0504-A/D-HV). A subsequent review found a similar configuration existed on Unit 3. After further review, it was concluded that Technical Specification RPS functions 8 and 9, 'Turbine Stop Valve - Closure' and 'Turbine Control Valve Fast Closure, Trip Oil Pressure - Low' are susceptible to single point vulnerability due to a nonconformance to design standard IEEE 279 -1968. Specifically, failure of the common sensing line would bypass these RPS scram functions when reactor power is greater than 38.5 percent. Based on this single point vulnerability, these RPS scram functions could have been disabled if the sensing line failed and therefore this event is reportable per 10 CFR 50.73(a)(2)(v)(A), "Any event or condition that could have prevented the fulfillment of a safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition." For Unit 2, DNPS took actions to restore compliance to the referenced design standard prior to the return to service. For Unit 3, DNPS has performed an operability determination, and the safety function remains operable. Actions to restore compliance for DNPS Unit 3 are scheduled for the next refueling outage.
2372009008 | Dresden 2 | 11/03/2009 | 02/05/2010 | ML10054012 | <strong>Unit 2 Core Spray Break Detection Instrument Line Not Seismically Supported</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2009, during a refueling outage walk down of the drywell, plant personnel discovered that a small bore pipe was not connected to two of its supports and the piping appeared to be bent downward away from the supports. Additionally, there was one pipe support that was determined to be missing. The three-quarter inch line was connected to the Core Spray injection line near the Reactor Vessel wall. The unsupported line was identified to be the Core Spray system line break detection for the 2B Core Spray pump injection line. This line is connected to the Core Spray injection line between the Core Spray injection manual isolation valve and the reactor vessel nozzle. Following an engineering evaluation, it was determined that in the event of a design basis earthquake, there was a potential for the instrument line to fail, which may have resulted in an unisolable three-quarter inch piping leak from the reactor vessel. This condition represents serious degradation to a principal safety barrier of the Nuclear Power plant and is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(A). Based on the investigation, it is believed that this condition is historical in nature. Therefore, no definitive cause could be determined. However, it is believed that the piping supports may have been stepped on which resulted in the instrument line becoming disconnected from the supports. Additionally, based on an inspection of the drywell wall, it was evident that the missing pipe support had been broken off the wall. The plant's emergency core cooling systems were available to provide inventory control in the event that an instrument line failure occurred. Therefore the safety significance of this event is minimal due to the health and safety of the public not being compromised.
2442009001 | Ginna | 09/16/2009 | 11/13/2009 | ML09323011 | <strong>Control Room Emergency Air Treatment System Inoperable Due to Design Deficiency</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2009, Diesel Generator Load and Safeguard Sequence Testing was completed. Testing included placing the Control Room Emergency Air Treatment System (CREATS) in service followed by initiation of a simulated Safety Injection signal concurrent with a Loss of Offsite Power condition. A design deficiency utilizing AC power relays created a situation where motor starter contactor arc re-strikes resulted in transient recovery voltages (TRV) up to several times the nominal 480 Volt power source. The elevated TRV created a re-strike phenomenon causing both trains of GREATS fan breakers to trip on over current. Operator action was required to restore CREATS to operation. Ginna identified numerous previous occurrences since 10/11/2006 when both CREATS fans were operating concurrently. Five of these occurrences created a condition prohibited by Technical Specifications due to a design flaw where both trains of CREATS were inoperable. Limiting Condition for Operation 3.7.9.F, "Two CREATS trains inoperable in MODE 1, 2, 3, or 4 for reasons other than Condition B" was exceeded. A cause investigation identified an unsuitable design in the use of AC powered relays in this type of application. A plant modification was performed which changed the relays from AC power to DC power. Analysis confirmed that consequences of a design bases event, with timely operator action, were still within the acceptance criteria for Control Room Envelope (CRE) design.
2442009002 | Ginna | 12/30/2009 | 02/26/2010 | ML10063041 | <strong>Plant Trip due to Loss of Electro-Hydraulic Control System Pressure</strong><br /><i>Abstract:&nbsp;</i>On December 30, 2009, the R.E. Ginna Nuclear Plant experienced an automatic plant trip from full power. The trip was initiated upon a signal of two out of two turbine stop valves being fully closed. The two stop valves closed when the electro-hydraulic control system (EHC) could not maintain adequate EHC system pressure to keep the stop valves in the fully open position. The control room operators performed the appropriate actions of procedures E-0, Reactor Trip or Safety Injection and ES-0.1, Reactor Trip Response. Following the reactor trip, all safety systems operated as designed. The reactor was stabilized in Mode 3. The cause of the EHC pressure loss was a common mode failure of both EHC pumps caused by the incorrect seal material being used during vendor refurbishment of the pumps that were installed during the 2009 refueling outage (RFO). The specified material was Viton, however evaluation identified that Buna-N was provided which is incompatible with the EH fluid. Corrective actions to prevent recurrence are summarized in Section IV.B.
2472009001 | Indian Point 2 | 02/25/2009 | 04/27/2009 | ML09133020 | <strong>Technical Specification Prohibited Condition Due to a Surveillance Requirement Never Performed for the Atmospheric Steam Dump Valve Local Nitrogen Controls</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2009, post work testing (PWT) of a modification installing additional backup nitrogen supply capacity at local control stations for atmospheric dump valve (ADV) operation, discovered that two of four ADVs failed to stroke on nitrogen. All four ADVs tested satisfactorily using the normal instrument air (IA) supply. Troubleshooting discovered that nitrogen valve supplies and output hoses were reversed on two ADVs. The review also determined the last time maintenance was performed on the two nitrogen control valves was 2004 using an existing surveillance test for the PWT which only used IA to verify valve operation. Technical Specification (TS) Surveillance Requirement (SR) 3.3.4.2 requires verification of each required remote shutdown function to ensure it performs its intended function. A review of past operation discovered there was no surveillance test for testing the ADVs using the local nitrogen system. An NRC regulatory position on reporting TS SR never performed was identified on February 25, 2009. The apparent cause of not having a surveillance test for testing the ADVs using the local nitrogen system was inadequate use of human performance tools to ensure testing was established to meet new SRs during the review to address a 2004 adverse trend condition report. Corrective actions included; Performance of an extent of condition to ensure all remote shutdown TS SRs have test procedures. A testing procedure will be prepared for testing the ADVs using nitrogen, and a review will be performed to verify that all other TS SRs have test procedures. The event had no significant effect on public health and safety.
2472009002 | Indian Point 2 | 04/03/2009 | 05/26/2009 | ML09156003 | <strong>Manual Reactor Trip due to Decreasing Steam Generator Levels Caused by a Loss of Main Feedwater Pump 21 and Failure of the Main Turbine to Automatically Runback</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2009, Control Room Operators initiated a manual reactor trip as a result of observing decreasing steam generator (SG) levels following loss of the 21 Main Boiler Feedwater Pump (MBFP), a large steam flow to feedwater flow mismatch, and failure of the main turbine to automatically runback. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser which was subsequently shifted to the atmospheric dump valves. The direct cause of the decreasing SG levels was the trip of MBFP 21 due to a autostop oil tubing/fitting failure on the MBFP Autostop oil header. The root cause was improper tubing installation due to poor worker practices. A straight tubing installation with no bends to allow for expansion and contraction or to allow for motion under load resulted in vibration induced stress failure. The cause of the turbine runback failure was indeterminate but most likely an intermittent failure of the digital speed tachometer assembly. Corrective actions included replacement of the tubing for both MBFPs reconfigured to meet established installation requirements, performance of an independent equipment failure evaluation of the failed fitting, and implementation of a troubleshooting plan on the runback feature to confirm functionality. Five year maintenance requalification training for Swagelok fitting installation will be established and supplemental worker training for Swagelok fitting installation will be developed. The event had no effect on public health and safety.
2472009003 | Indian Point 2 | 05/28/2009 | 07/27/2009 | ML09233012 | <strong>Loss of Single Train 21 Pressurizer Backup Heater Required for Remote Shutdown from the Control Room due to an Inoperable Breaker</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2009, after completion of quarterly surveillance 2-PT-Q54,"Pressurizer Level Bistable Test," and return of the Pressurizer Level Defeat switch (L-460A) to its original position, control room (CR) alarm (Pressurizer Low Level 18% and 5%) came in and cleared, and (Pressurizer Heater Group Tripped) alarmed due to the trip of Pressurizer Heater Group 21 and the Modulating Heater Group. The breakers for these components opened and Operators attempted to reclose the breakers but were unable to re-close the breaker for the 21 pressurizer backup (B/U) heater. Operators were able to close the breaker for the 22 pressurizer B/U heater and re-close the breaker for the modulating heaters. Technical Specification (TS) 3.3.4.A (Remote Shutdown) was entered for an inoperable 21 pressurizer backup (B/U) heater. Troubleshooting was initiated and the anti pump lever for the 21 pressurizer B/U heater breaker was manually reset and the breaker closed. The apparent cause of the trip of the pressurizer heaters was a degraded switch (L-460A) where a dead spot caused an intermittent interruption of continuity when the switch was rotated to the Defeat 3 position. The interruption disrupted the input to pressurizer level bistables and momentarily actuated the bistables causing the alarm and trip of the breakers for the pressurizer heaters. The inability to reset and re-close the breaker for the 21 pressurizer B/U heater was due to a misaligned control relay trip (anti-pump) lever. Corrective actions included troubleshooting breaker 52/PBU1, realignment of the anti pump lever, testing, breaker cycling and closure. Switch L-460A and the control relay will be replaced and the cubicle rail for the breaker (52/PBU1) will be repaired. The event had no effect on public health and safety.
2472009004 | Indian Point 2 | 06/23/2009 | 08/07/2009 | ML09225037 | <strong>Loss of Single Train 23 Charging Pump Required for Remote Plant Shutdown from the Control Room due to a Failure of a Pump Internal Check Valve</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2009, the 23 Charging Pump was removed from service after operators observed decreased pressureizer level and degraded output flow. The 21 charging pump was placed in service and the 23 Charging Pump was declared inoperable and Technical Specification (TS) 3.3.4 (Remote Shutdown) Condition A was entered. The 23 Charging Pump is a function specified in TS Basis Table 3.3.4-1 for reactor coolant system (RCS) inventory control. The inoperable 23 Charging Pump resulted in failure to meet the specified safety function of TS 3.3.4. The apparent cause of the degraded pump flow was a failure of one of ten internal check valves.The cause of the valve failure was a random event. This failure and previous failures were not confined to a specific location within the pump; are independent of service life; and independent of different specified valve materials. Corrective actions included replacement of the failed internal check valve and remaining pump internal check valves. The event had no significant effect on public health and safety.
2472009005 | Indian Point 2 | 11/02/2009 | 01/04/2010 | ML10012045 | <strong>Automatic Reactor Trip due to a Turbine-Generator Exciter Protective Trip Caused by a Loss of the Generrex Power Supply Monitored Voltage due to a High Resistance Ground Connection</strong><br /><i>Abstract:&nbsp;</i>On November 02, 2009, an automatic reactor trip (RT) was initiated as a result of a turbine-generator protective trip (86P Lockout Relay). All control rods fully inserted and all required safety systems functioned properly. The Main Steam Isolation Valves (MSIVs) were closed after reports that one of the four turbine stop valves did not indicate fully closed. The plant was stabilized in hot standby with decay heat being removed by the Steam Generators (SG) via the Atmospheric Steam Dump Valves. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. The direct cause was a high resistance connection on the common ground terminal between the Generrex power supplies and alarm cards. The cause of the event was a poor Original Equipment Manufacturer (OEM) design of the common ground wiring connections on the Generrex power supply distribution block. Corrective actions included repairs to the Generrex power supply connection and installation of a second ground connection in the exciter cabinet. A Generrex system upgrade is planned for the refueling outage 19 in the spring of 2010 which includes upgrading to solid state power supplies and testing the ground wire. The event had no effect on public health and safety.
2492009001 | Dresden 3 | 10/03/2009 | 12/01/2009 | ML09344006 | <strong>Unit 3 Group I Isolation and Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On 10/03/2009 at approximately 1735 hours while at full power, Unit 3 experienced an automatic reactor scram and Group I primary containment isolation signal. Due to the Group I isolation signal, the inboard and outboard main steam isolation valves closed as designed. Prior to the reactor scram, operators were restoring the reactor water clean-up (RWCU) system per the applicable station procedure. The Probable Cause for the Group I isolation signal and reactor scram is attributed to a hydraulic pressure transient when restarting the RWCU system due to a latent procedure deficiency. The procedure for restarting the RWCU has been revised. During the reactor scram, the shared Unit 2/3 emergency diesel generator automatically started when auxiliary power transferred from the main to the reserve power source. The safety significance of this event is minimal as plant response and operator actions were consistent with the protection of public health and safety and personnel safety.
2502009001 | Turkey Point 3 | 04/01/2009 | 05/29/2009 | ML09162008 | <strong>Procedure Inadequacy Causes Control Room Ventilation Isolation Technical Specification Noncompliance</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2009, with Unit 3 in Mode 6 and core alteration and irradiated fuel movement in containment in progress, Operations personnel identified a noncompliance with Technical Specification (TS) Limiting Condition for Operation 3.3.2, Table 3.3-2, Functional Unit 9.a, Control Room Ventilation Isolation. TS Table 3.3-2, Functional Unit 9.a, requires both actuation logic channels to be operable during core alteration. One channel of actuation logic was rendered inoperable by procedure for the Engineered Safeguards Integrated Test (ESIT) which was being performed concurrently with core alteration. With one actuation logic channel inoperable, the actions of TS 3.9.13 are to be taken. TS 3.9.13, Action b, requires the Control Room Emergency Ventilation System (CREVS) to be isolated and placed in the recirculation mode of operation. Upon identification of this TS noncompliance, Operations personnel isolated the CREVS and placed it in the recirculation mode of operation. The apparent cause is attributed to inadequate governing procedures that focused on operability of the containment radiation monitors, not the actuating circuitry for the CREVS. Corrective action is to revise the governing procedures to ensure that TS 3.9.13, Action b, is followed when one containment ventilation isolation rack is de-energized for ESIT and core alteration is in progress. Safety significance is considered to be very low since there was no loss of safety function as one channel of CREVS actuation logic was operable.
2502009002 | Turkey Point 3 | 05/04/2009 | 10/01/2009 | ML09287037 | <strong>MSIV Drain Line Leak Causes Technical Specification Required Shutdown; Failure to Perform PMT Causes Inoperable MSIV</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2009 at approximately 2000 hours with Unit 3 in Mode 2 at approximately 2% reactor power during restart from a refueling outage, plant personnel found steam leaking from the bottom of the 3C Main Steam Isolation Valve (MSIV) in the area where the weld boss joins the valve body. Technical Specifications (TS) 3.4.10 and 3.0.3 were entered and a unit shutdown was initiated at approximately 0330 on May 5, 2009, upon confirmation that the leak was from a weld and structural integrity was impacted. At approximately 0348 hours, operators closed the 3A and 3B MSIVs. The 3C MSIV did not close on demand, was declared inoperable and TS 3.7.1.5 was entered. At approximately 0437, the 3C MSIV closed. The reactor was tripped and Mode 3 was entered at approximately 0438. Mode 4 was entered at approximately 0847 on May 5, 2009 and Mode 5 was entered at approximately 1431 the same day whereupon Unit 3 exited TS 3.0.3. The root cause of the drain line leak was determined to be poor welding workmanship due to limited accessibility. The root cause of the 3C MSIV failure to close on demand is attributed to inadequate guidance for verification of post maintenance tests (PMT) for returning equipment to service. Corrective actions include repairing the 3C and 3B MSIV drain lines, and revision to work package PMT identification and review practices.
2512009001 | Turkey Point 4 | 08/11/2009 | 10/13/2009 | ML09295034 | <strong>4B Emergency Diesel Generator Inoperable Due to Air-bound Main Fuel Pump</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2009 during a surveillance test, erratic fuel pressure indications were observed by an operator at the 4B Emergency Diesel Generator (EDG). The DC priming pump remained running beyond the point when it normally would shut off. The diesel was secured for troubleshooting and repairs. Subsequent investigation determined that the 4B EDG was inoperable for about 14.3 days, in excess of the allowed outage time of 14 days. The cause of the inoperability was an air bound engine driven fuel pump due to air in-leakage at a suction strainer. Corrective actions include replacement of the suction strainer, and revision of the maintenance procedure to ensure proper installation and gasket seating during fuel suction strainer housing reassembly. The DC priming pump would have been able to provide sufficient fuel for the 4B EDG to respond to loss of offsite power and loss of coolant accident loads while load management would have been necessary for station blackout loads. The risk impact associated with the approximate 14.3 days the 4B EDG was considered inoperable results in an ICCDP (Incremental Conditional Core Damage Probability) of 5.4E-08 and an ICLERP (Incremental Conditional Large Early Release Probability) of 2.6E-10, well below NRC thresholds. Therefore, safety significance is considered to be very low.
2542009001 | Quad Cities 1 | 04/28/2009 | 06/26/2009 | ML09187042 | <strong>Magnesium Rotor Degradation Causes Failure of Unit 1 Reactor Recirculation Pump Discharge Motor Operated Valve to Close and Results in Loss of LPCI When in Loop Select Function</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2009 while in refueling outage Q1R20, and while performing surveillance testing to stroke reactor recirculation system [AD] valves [V], the Unit 1 reactor recirculation pump [P] discharge motor operated valve [20] (MOV) 1-0202-5B, did not close when the control switch [HS] was taken to close. Operations reported the control switch was taken to stop after approximately 100 seconds. Shortly afterwards, remote (control panel) light indication [IL] for 1-0202-5B was lost. Operators reported the breaker [BKR] was not tripped, and that local (MCC) light indication was also out. MOV 1-0202-5B and the Low Pressure Coolant Injection (LPCI) [BO] mode of Residual Head Removal (RHR) [BO] were declared inoperable as of the time of discovery. Since the Unit was in Mode 5 for refueling outage Q1R20, LPCI was not required to be operable. Tech Spec 3.5.2, ECCS-Shutdown, was satisfied by two (2) operable core spray [BM] subsystems. Initial troubleshooting indicated the supply breaker thermal overload had tripped, and the valve motor [MO] windings were shorted. MOV 1-202-5B was manually closed, which restored the LPCI system to operable status. The valve was being assessed for repairs when it was discovered the motor had been damaged, due to magnesium oxidation of the rotor assembly. The magnesium rotor motor for the valve operator [84] was subsequently replaced during Q1R20 and the valve was returned to operable status prior to Unit startup. This issue was determined to be an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident, and is therefore reportable per 10CFR50.73(a)(2)(v)(D).
2542009002 | Quad Cities 1 | 05/24/2009 | 07/23/2009 | ML09217031 | <strong>Inoperable RCIC Primary Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2009, during the Reactor Core Isolation Cooling (RCIC) [BN] pump [P] operability surveillance test following refueling outage Q1 R20, the RCIC system tripped on high turbine [TRB] exhaust discharge pressure when the disc on the RCIC Turbine Exhaust primary containment (torus) [NH] outboard isolation swing check valve [V] 1-1301-41, became separated from the hinge arm. The disc separation was caused by the disc stud fracturing as a result of high cycle fatigue. Once the failure occurred, the disc stud with the retaining nut still attached migrated downstream to the RCIC Turbine Exhaust primary containment (torus) inboard isolation stop check valve 1-1301-64 and became caught between the disc and the seat on the stop check. This prevented the stop check valve 1-1301-64 from closing fully. The disc failure of the swing check valve 1-1301-41, combined with the stuck open condition on the stop check valve 1-1301-64, resulted in both primary containment isolation valves (PCIVs) being inoperable, thus impacting primary containment integrity. Other redundant safety systems, such as High Pressure Coolant Injection (HPCI) [E3J], were available at the time RCIC was declared inoperable, and Unit 1 was subsequently shut down so that repairs to the disabled check valves could be performed. The inboard and outboard containment isolation valves in the RCIC turbine exhaust line were subsequently repaired prior to Unit 1 restart. The failure of the PCIVs, although impacting the containment integrity safety function, did not create any actual plant or safety consequences, since Unit 1 was not in an accident condition requiring containment integrity for the RCIC steam exhaust line during this event. This issue was determined to be reportable per 10CFR50.73(a)(2)(v)(D), since it resulted in an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2542009003 | Quad Cities 1 | 05/30/2009 | 08/03/2009 | ML09223033 | <strong>Failure of RHR Torus Spray Isolation Valve to Open due to Declutch Mechanism Problems</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2009 (Discovery Date) at 2010 hours, while in Mode 1 at 100% power after startup from Forced Outage Q1F59, the MO 1-1001-37B, torus [NH] spray shutoff valve [SHV] was found inoperable, in that it would not open while using the control switch [HS] during the performance of the Residual Heat Removal (RHR) [BO] Power Operated Valve Test surveillance procedure. Investigation into the event determined that the valve motor actuator [84] declutch lever had been inadvertently bumped into the manual mode of operation during previous outage related work activities in the vicinity of the valve. When given the open signal from the control room the valve actuator did not return to the motor mode of operation from the manual mode of operation due to increased friction caused by degraded lubricant/grease in the area of the clutch return spring and clutch keys, and possible degradation/wear of the clutch keys. The failure of the MO 1-1001-37B valve to open, although impacting the ability to achieve flow for RHR suppression pool spray, did not create any actual plant or safety consequences, since Unit 1 was not in an accident condition requiring RHR suppression pool spray during this event. Furthermore, the containment spray [NH] function (which consists of drywell spray and suppression chamber spray) is not required for proper performance of the containment pressure suppression system. This issue was, however, determined to have resulted in a past operation or condition prohibited by the plant Technical Specifications (TS), and is reportable per 10CFR 50.73(a)(2)(i)(B), because on May 30, 2009 (Event Date) while in Mode 2, at 0225 hours during startup from Q1F59, the activity of having changed modes to enter Mode 2 resulted in not meeting TS LCO 3.6.2.4 for two required operable RHR suppression pool spray subsystems while in Modes 1, 2 and 3.
2542009004 | Quad Cities 1 | 09/08/2009 | 11/06/2009 | ML09317020 | <strong>Pinhole Leak in Core Spray Piping Results in Loss of Containment Integrity and Plant Shutdown for Repairs</strong><br /><i>Abstract:&nbsp;</i>On September 8, 2009, during the performance of a quarterly 1A Core Spray (CS) system [BM] flow test, a pinhole leak was identified in the 1B CS minimum flow line just downstream of MO 1-1402-38B (1B CS minimum flow valve [V]). The leaking pipe [PSP] could not be isolated from primary containment [NH]. As a result, primary containment was declared inoperable at 1935 hrs and Technical Specification (TS) 3.6.1.1, Required Action B.1, was entered requiring a plant shutdown in 12 hours. Unit 1 was shut down on September 9, 2009 at 0638 hrs. This event is therefore reportable under 10 CFR 50.73(a)(2)(i)(A), "The completion of any nuclear plant shutdown required by the plant's Technical Specifications." After Unit 1 was shutdown the affected CS piping (5 inches long by 1-1/2 inches in diameter) was removed and an inspection was performed. The inspection confirmed that an area of the pipe had severely thinned. The thinned area had indications consistent with cavitation erosion. The 1B CS piping downstream of 1-1402-38B was replaced on September 10, 2009, and a section of the 1B CS piping upstream of 1-1402-38B was also replaced on September 10, 2009. Unit 1 was synchronized to the grid at 0822 hrs on September 12, 2009.
2592009001 | Browns Ferry 1 | 02/18/2009 | 04/20/2009 | ML09114025 | <strong>Turbine Trip and Reactor Scram Due To Power Load Unbalance Signal On Main Generator</strong><br /><i>Abstract:&nbsp;</i>February 18, 2009, at 0351 hours Central Standard Time (CST), following a scheduled preventative maintenance activity, Unit 1 reactor automatically scrammed from a turbine trip due to a power load unbalance signal on the main generator. Specifically, at 0349 hours CST, Operations swapped the Unit 1 Main Generator Isophase Bus Duct System cooling fan from the running to the alternate fan. When the alternate fan started, water entrapped in the fan housing was expelled into the bus provided a path to ground inside the bus duct. This resulted in actuation of the generator protective relays and a turbine trip and automatic reactor scram, which resulted in the automatic actuation of the reactor protection system. Water that had settled in the idle bus duct cooling fan housing was expelled into the main generator isophase bus duct upon fan startup providing a conductive path to ground. The root cause of this event was less than adequate design process guidance for consideration of seasonal variations in the operating conditions for heating ventilation and air conditioning (HVAC) system design. The design process does not consider full range of operation of HVAC systems using raw cooling water as a cooling medium during the winter months. BFN inspected the Unit 1 isophase bus for damage. No damage was identified. BFN installed a drain with a site glass on each Unit 1 bus duct cooling fan housing. General Operating Instruction, Operations Round Logs, was revised requiring verification that there is no water in the idle fan and to drain any water that may have accumulated prior to placing it into service. BFN will modify the design change technical considerations checklist to provide design process guidance for consideration of seasonal variations in operating conditions for HVAC design.
2592009002 | Browns Ferry 1 | 03/21/2009 | 09/27/2013 | ML13273A26 | <strong>Unexpected Logic Lockout of the Loop II Residual Heat Removal System Pumps</strong><br /><i>Abstract:&nbsp;</i>On March 20, 2009, in preparation for testing, Operations declared Residual Heat Removal (RHR) pumps 1A and 1C inoperable, entering Technical Specification (TS) Limiting Condition for Operation (LCO) 3.5.1 Condition A and Required Action A.1. <br /><br /> On March 21, 2009, while placing a jumper in accordance with the surveillance, Unit 1 received an RHR Pump Initiate Lockout signal for Loop II RHR Pumps 1B and 1D. With the lockout signal in place, the automatic start function of RHR Pumps 1B and 1D is inhibited. Unit 1 entered TS LCO 3.5.1 Condition H, Action H.1, with two or more low pressure ECCS injection/spray subsystems inoperable for reasons other than Condition A, and entered TS LCO 3.0.3. Operations restored the automatic start function of RHR Pumps 1 B and 1D, and exited TS LCO 3.5.1 Condition H and TS LCO 3.0.3. However, because the concurrent condition of RHR Loop II and Loop 1 RHR pump 1C were unknown at the time, Unit 1 was not placed in LCO 3.0.3 as required by TS 3.5.1, Required Action H.1. <br /><br /> A walkdown recognized that the jumper was being installed in one panel and removed from another. However, when the revision was made, the wrong surveillance step was revised. The action to place and remove a jumper took place in the incorrect cabinet. Corrective actions included a technical review of procedures and re-indoctrinated on adequate independent qualified review techniques.
2592009003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 06/19/2009 | 08/17/2009 | ML09233010 | <strong>A Train Standby Gas Treatment System Inoperable Longer Than Allowed by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2009, at approximately 1330 hours Central Daylight Time (CDT) plant Engineering notified Operations that the A-Train of Standby Gas Treatment (SGT-A) relative humidity (RH) heater 37C relay had failed. Consequently, the C-phase heating element was not functioning. Operations immediately declared SGT-A inoperable in accordance with the Plant's Technical Specifications (TSs) and entered a seven day Limiting Condition for Operation (LCO) 3.6.4.3, Action A1 for Units 1, and 3: With one SGT subsystem inoperable, restore SGT subsystem to operable status in seven days. At the time of the event Unit 2 was in Mode 4 and SGT was not required to be operable. On June 19, 2009, TVA replaced the 37C relay. On June 20, 2009, at approximately 0138 hours CDT, following post maintenance testing, SGT-A was declared operable and the TS LCO for an inoperable SGT subsystem was exited. TVA's investigation into this event also found that on November 11, 2008, a work order was generated to trouble shoot and correct main control room annunciator indicating loss of power on the RH heating element. Trouble shooting performed on January 22, 2009, found the RH heater relay coil circuit was open and relay coil failed. On June 19, 2009, when plant engineering notified operations that the C-phase relative humidity heaters were not functional, operations determined SGT-A was inoperable. Units 1, 2, and 3 were in a condition prohibited by the plant's TSs. Therefore, TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications.
2592009004 | Browns Ferry 1 | 07/24/2009 | 09/27/2013 | ML13273A26 | <strong>High Pressure Core Injection Found Inoperable During Compensate Header Level Switch Calibration and Functional Test</strong><br /><i>Abstract:&nbsp;</i>At 1415 Central Daylight Time (CDT) on July 24, 2009, with Unit 1 in Mode 1, at approximately 100 percent of rated thermal power, Operations was conducting a surveillance on the High Pressure Coolant Injection System (HPCI), 1-SR-3.5.1.7, "HPCI Main and Booster Pump Set Development Head and Flow Rate Test at Rated Reactor Pressure." At approximately 1415 CDT, during the prerequisite steps 1-PCV-073-0018C, the HPCI Turbine Stop Valve Mechanical Trip Hold Valve developed a tear in the diaphragm. This tear caused oil from the HPCI control oil system to spill at a rate of approximately 0.25 to 0.5 gallons per minute (gpm). The pressurization of the control oil system is the motive force required to open the HPCI stop valve. If the oil system could not be pressurized the HPCI Stop Valve could not be opened which would render HPCI inoperable. <br /><br /> The root cause was a material defect in the diaphragm of 1-PCV-073-0018C, HPCI Turbine Stop Valve Mechanical Trip Hold Valve, allowed the diaphragm to tear under normal system pressure and operating conditions. <br /><br /> Corrective actions to prevent recurrence include the quarantine of spare diaphragms determined to be from same lot as the diaphragm that failed and verifying that diaphragms from the same lot as the failed diaphragm are not currently installed.
2592009006 | Browns Ferry 1 | 09/01/2009 | 09/27/2013 | ML13274A34 | <strong>Inoperable High Pressure Coolant Injection Pump due to Emergency Core Cooling System Inverter Failure</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2009, at 1614 hours Central Daylight Time (CDT), Operations personnel received indications that the Unit 1 Emergency Core Cooling Systems (ECCS) Division II 250V DC Inverter had tripped. The trip resulted in the inoperability of the Unit 1 High Pressure Coolant Injection (HPCI) System. The Unit 1 Core Spray (CS) System Loop II had previously been declared inoperable due to the inoperability of the associated air handling unit and TS 3.5.1 Condition A had been entered. The combination resulted in TS 3.5.1 Condition D being entered. Condition D requires either restoration of the low pressure ECCS injection/spray subsystem or the HPCI System within 72 hours. On September 2, 2009, at 1741 hours CDT, following restoration activities, Operations declared CS Loop II operable and exited TS 3.5.1 Condition D. Following restoration activities on the Division II ECCS Inverter, the HPCI System was declared operable and TS 3.5.1 Condition C was exited on September 3, 2009, at 0500 hours CDT.<br /><br /> The cause for this event was a catastrophic failure of the metal oxide varistor installed between the positive and negative legs of the power supply. Corrective actions to prevent recurrence include performing an evaluation of the design of the surge suppression features and, if necessary, pursue a design change to prevent a shorted varistor from tripping the ECCS 250V inverter input.
2602009001 | Browns Ferry 2 | 02/16/2009 | 04/20/2009 | ML09114025 | <strong>Manual Reactor Scram Following Stator Cooling Water Equipment Failure</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2009, at 0513:47 hours Central Standard Time (CST), the Unit 2 reactor was manually scrammed and the turbine tripped in response to excessive stator cooling water temperature and initiation of the automatic turbine trip timer. At 0506 hours CST, operations received a stator cooling water abnormal alarm. Operations dispatched an auxiliary unit operator to the stator cooling water skid to investigate the alarm. At approximately 0512 hours CST, the idle stator cooling water pump was started. At 0513 hours, operations received alarms indicating the stator cooling water outlet temperature had exceeded the high temperature setpoint of 174 degrees F and the automatic turbine trip timer started. As required by Alarm Response Procedure, ARP-9-8A, Operations manually scrammed the reactor and tripped the turbine at 0513:47 hours CST. The root cause of this event was inadequate design of the stator cooling water system. In this event, the temperature controller and TCV-35-54 is a single point failure that led to the manual scram. The stator cooling water temperature control valve, TCV-35-54, is a proportioning valve that directs water flow through the stator cooling water heat exchangers. When the TCV is in the open position, flow bypasses the stator cooling water heat exchangers. In contrast, when the TCV is in the closed position, water flows through the stator cooling water heat exchangers. When the temperature controller failed, TCV-35-54 repositioned to the open position bypassing the heat exchangers. To prevent recurrence of this event, TVA's plans include design and install a temperature controlled solenoid that will vent the actuator air supply to TCV-35-54. Also, install a hand wheel to allow manual control of TCV-35-54.
2602009002 | Browns Ferry 2 | 05/31/2009 | 01/04/2010 | ML10006079 | <strong>Leak in an ASME Class I Code Reactor Pressure Boundary Pipe</strong><br /><i>Abstract:&nbsp;</i>On May 31, 2009, at approximately 1210 hours Central Daylight Time (CDT), during the performance of the Unit 2, ASME Section XI System Leakage Test of the Reactor Pressure Vessel and Associated Piping, 2-SI-3.3.1.A, TVA identified a leak on the Residual Heat Removal Shutdown Cooling root valve that could not be isolated. Following the confirmation that the through-wall leak was associated with an ASME Class I pressure boundary the test was terminated. Operations maintained the reactor in Mode 4 in accordance with the Technical Requirements Manual Action Statement 3.4.3.A.1. A weld performed in February of 1992, on the valve body and the tapered plug contained a defect. The root pass was made using the gas-tungsten process. This process was the industry standard in 1992. TVA postulates that a small amount of moisture present during the weld operation caused a defect in the weld. The defect slowly propagated and failed.
2602009003 | Browns Ferry 2 | 06/08/2009 | 07/28/2011 | ML11213A20 | <strong>Safety/Relief Valve As-Found Setpoint Exceeded Technical Specification Lift Pressure</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2009, the Tennessee Valley Authority (TVA) determined, as a result of laboratory surveillance testing, 7 of 13 Browns Ferry Nuclear Plant Unit 2 Safety/Relief Valves (S/RVs) mechanically actuated at pressures greater than 3 percent above their Technical Specifications (TS) setpoint. The S/RVs were thus inoperable for an indeterminate period during Cycle 15 period of operation. Unit 2 TS Limiting Condition for Operation 3.4.3 requires the safety function of twelve (12) S/RVs to be operable in reactor modes 1, 2, and 3. With one or more required S/RVs inoperable, the unit is required to be placed in Mode 3 (Hot Shutdown) within 12 hours and in Mode 4 (Cold Shutdown) within 36 hours. Since 7 of 13 S/RVs actuated above their TS setpoint plus the 3 percent allowance, it is probable that Unit 2 operated longer than allowed by the TS. Therefore, NA is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications.
2602009004 | Browns Ferry 2 | 06/11/2009 | 02/12/2010 | ML10049108 | <strong>Technical Specifications Shutdown due to Rise in Unidentified Drywell Leakage</strong><br /><i>Abstract:&nbsp;</i>At 1200 hours Central Daylight Time (CDT) on June 11, 2009, Browns Ferry Nuclear Plant Unit 2 experienced a rise in drywell leakage during reactor startup. The four-hour unidentified leak rate from 0800 to 1200 hours CDTon June 10, 2009, was 0 gallons per minute (GPM), while the four-hour unidentified leak rate from 0800 to 1200 hours CDT on June 11, 2009 was 3.88 GPM. This increase in leakage exceeded the Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.4.4 limit of a 2 GPM increase in unidentified leakage in a 24 hour period. At 1555 hours CDT on June 11, 2009, Unit 2 initiated a reactor shutdown via a manual reactor SCRAM to comply with TS LCO 3.4.4 Condition C to be in Mode 3 in 12 hours and to be in Mode 4 within 36 hours. Following verification that the procedure, 2-AOl-100-1, Reactor Scram, actions were completed, the reactor mode switch was placed in Shutdown. The increase in unidentified leakage was due to failure of a Main Steam Line B Safety Relief Valve (SRV) to fully close. As a result of this steam leakage, two main steam SRV tail pipe vacuum breakers, 2.5 inch and 10 inch, were cycling. This SRV failure and vacuum breaker cycling allowed steam to enter the drywell instead of going to the torus. Additionally, upon reset of the manual reactor scram, Reactor Protection System (RPS) 'B' scram channel did not reset as expected. At 1609 hours CDT on June 11, 2009, RPS Channel 'A' actuated a full reactor scram due to Intermediate Range Monitor 'C' spiking high and the inability to reset RPS 'B' scram channel. This automatic scram was found to be the result of a loose scram relay/contactor terminal connection.
2602009005 | Browns Ferry 2 | 07/18/2009 | 09/16/2009 | ML09264011 | <strong>Reactor Motor Operated Valve Board and Residual Heat Removal Subsystem Inoperable Longer than Allowed by the Plant's Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On July 18, 2009, at approximately 1425 hours Central Daylight Time (CDT) during scheduled performance of General Operating Instruction, Monthly Emergency Control Switch Verification - Unit 2 (0-GOI-300-1 Attachment - 15.13) Operators found the Manual/Auto Transfer Switch on 480 V Reactor Motor Operated Valve (RMOV) Board 2D in the incorrect, manual, position. Operators immediately declared 480 V RMOV Board 2D and associated Loop I of Residual Heat Removal (RHR) [BO] System inoperable and entered Technical Specifications (TS) 3.8.7 Actions, Condition C, and TS 3.5.1 Actions, Condition A. TS 3.8.7 Actions, Condition C, Required Action C.1 requires, with Unit 2 480 V RMOV Board 2D inoperable, that the affected RHR subsystem be immediately declared inoperable. With Loop I of the RHR System inoperable (i.e., one low pressure Emergency Core Cooling System (ECCS) injection/spray subsystem inoperable), TS 3.5.1 Actions, Condition A, Required Action A.1 requires the low pressure ECCS injection/spray subsystem be restored to operable status within 7 days. By 1509 hours CDT on July 18, 2009, Operators returned the switch to the auto position and exited the associated TSs Actions. BFN assumed the switch had been out of position since the restart from the Unit 2 refueling outage on June 19, 2009. Therefore, Unit 2 was in a condition prohibited by the plant's TSs (i.e., one low pressure EECS injection/spray subsystem was inoperable for longer than the 7 day Completion Time of TS 3.5.1 Actions, Condition A, Required Action A.1). Hence, TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications.
2602009006 | Browns Ferry 2 | 05/24/2009 | 02/16/2010 | ML10056003 | <strong>Automatic Reactor Protection System Scram While Shutdown</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2009, at approximately 0232 hours Central Daylight Time (CDT), with Unit 2 in a refueling outage and all rods fully inserted Operations personnel inserted a "B" channel half scram to support a contactor maintenance work activity. At approximately 0247 hours CDT, Operations received an "A" Channel half scram and a Reactor Protection System (RPS) actuation (full scram). The RPS actuation occurred when a fuse was removed from the circuit that supplied power to the contact that bypassed a high level scram signal from the scram discharge volume (SDV). At the time of the occurrence, the SDV had been isolated and was full of water due to previously hydrolazing the Scram Discharge Volume Instrument Tank and Headers. As a result, with the bypass removed, a reactor scram signal was generated, which lead to an RPS actuation (full scram).
2602009007 | Browns Ferry 2 | 09/29/2009 | 11/20/2009 | ML09328085 | <strong>Manual Scram During Removal of a Reactor Feedwater Pump from Service</strong><br /><i>Abstract:&nbsp;</i>At 2321 hours on September 29, 2009, with Unit 2 at 100 percent power, operators were in the process of removing reactor feedwater pump 2B from service for scheduled maintenance. At the time, condensate pump 2B and condensate booster pump 2C had been previously removed from service for maintenance. When feedwater pump 2B speed was lowered to where flow was below the minimum flow setpoint, the pump 2B minimum flow valve automatically opened. This action increased total condensate flow, which lowered feedwater and condensate booster pump suction pressures. Feedwater pump 2A and condensate booster pump 2A subsequently tripped on low pump suction pressure signals. Feedwater pump 2C automatically increased speed to maintain reactor vessel level and tripped on overspeed. Operators manually scrammed the reactor due to decreasing vessel water level. Decreasing vessel level also resulted in the auto-initiation of High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC). HPCI successfully started and in combination with feedwater pump 2B restored water level to normal. RCIC started, but failed to achieve sufficient speed to inject. A separate LER is being submitted on the RCIC malfunction. The event investigation determined that the operating instructions for removing a feedwater pump from service were inadequate for the operating configuration (with less than a full complement of condensate and condensate booster pumps in operation). The subject operating instructions have been revised to require that feedwater flow be below that needed for 85 percent power prior to removing a feedwater pump from service if a condensate/condensate booster pump is not in service. A new tool for assessing the risk of online activities was implemented. The risk review process for performing online feedwater/condensate system maintenance is also being reviewed.
2602009008 | Browns Ferry 2 | 09/30/2009 | 11/24/2009 | ML09336018 | <strong>Reactor Core Isolation Cooling System Inoperable Longer Than Allowed by the Plant's Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 30, 2009, at approximately 0830 hours Central Daylight Time, Browns Ferry Nuclear Plant (BFN) Site Engineering personnel concluded that during a September 29, 2009, manual reactor scram, the Reactor Core Isolation Cooling (RCIC) system pump failed to inject into the reactor vessel in response to decreasing water level. At the time the conclusion was made, Unit 2 was in Mode 3 with reactor pressure less than 150 psig; thus, the RCIC system was not required to be operable in accordance with the Applicability of Technical Specification (TS) 3.5.3, RCIC System. Consequently, no entry into the associated TS actions was required. Previously, on September 12, 2009, BFN personnel noted that plant data indicated that since August 27, 2009, the output from the Woodward Electric Governor-Magnetic Pickup (EG-M) control box was lower than expected. On September 29, 2009, the Unit 2 RCIC system failed to properly start and inject into the reactor vessel when the Reactor Vessel Low Low, Level 2 (-45 inches) setpoint was reached following a manual reactor scram. Because the RCIC system failed to inject when needed and the governor output had been lower than expected for an extended period of time, TVA has concluded that the RCIC system had been inoperable longer than the TS 3.5.3, Required Action A.2 Completion Time of 14 days. The root cause of this event was a failure to enter a condition adverse to quality into the corrective action program. When the HPCI system was inoperable, it remained available for injection into the reactor pressure vessel except for a total of five minutes. During the time periods that the HPCI system was unavailable, the remaining emergency core cooling systems were available to perform the HPCI system function. Therefore, TVA concludes that there was no significant reduction in the protection of the public by this event.
2602009009 | Browns Ferry 2 | 11/17/2009 | 01/19/2010 | ML10022045 | <strong>Inadvertent Isolation of the High Pressure Coolant Injection System During Testing Activities</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2009, at 2034 hours Central Standard Time, the Unit 2 High Pressure Coolant Injection (HPCI) system unexpectedly received a Group 4 Primary Containment Isolation Signal, during the performance of Surveillance Procedure, HPCI Steam Line Space High Temperature Functional Test. Browns Ferry Nuclear Plant Operations personnel entered Abnormal Operating Instruction, Group 4 High Pressure Coolant Injection Isolation, AOI-64-2B. They also entered Technical Specification (TS) Limiting Condition for Operation (LCO) Action 3.5.1, Condition C. TS 3.5.1 Required Actions C.1 and C.2 required the Reactor Core Isolation Cooling (RCIC) system to be immediately verified by administrative means to be operable, and to restore the HPCI system to operable status in 14 days. Operations personnel immediately verified by administrative means the RCIC system was operable. By 2250 hours Operations personnel reset the HPCI isolation signal and using the applicable portions of Operating Instruction, High Pressure Coolant Injection, placed the HPCI system back in standby readiness, exiting AOI-64-2B, and the TS LCO actions. The root cause for HPCI inoperability was a faulty test connector on the HPCI Steam Line Space High Temperature test panel. Disassembly and inspection of the HPCI Steam Line Space High Temperature test panel connector found that the internal portion of the connector body was not insulated and the insulation on several connectors within the assembly was not sufficient to prevent inadvertent short circuit. The test connector was replaced and the surveillance procedure was successfully completed.
2612009001 | Robinson 2 | 04/20/2009 | 11/05/2010 | ML10316010 | <strong>Emergency Diesel Generator Inoperable in Excess of Technical Specifications Allowed Completion Time</strong><br /><i>Abstract:&nbsp;</i>At 1250 hours EDT on April 20, 2009, with H. B. Robinson Steam Electric Plant, Unit No. 2, operating at approximately 100% power, breaker 52/27B, Emergency Diesel Generator (EDG) 'B' output breaker, failed to close during the performance of OST-409-2, "EDG 'B' Fast Speed Start. " Technical Spetifications (TS) Limiting Condition for Operation (LCO) 3.8.1 Condition B, was entered due to EDG 'B' being inoperable. On April 21, 2009, EDG 'A' was tested satisfactorily to verify operability in accordance with OP-604, "Diesel Generators 'A' and 'B'," and TS LCO 3.8.1, Action B.3.1. Breaker 52/27B was replaced on April 21, 2009, and EDG 'B' was declared operable on April 23, 2009. The investigation for the inoperability of EDG 'B' due to breaker 52/27B failure to close determined that the cotter pin used to retain the relay's mechanical lift linkage had rotated to a position that prevented complete return of the lift linkage to its normal position. Therefore, the lift linkage maintained the control relay trip pin engaged and maintained the control circuits open preventing the breaker from closing. The investigation concluded that EDG 'B' was inoperable from March 28, 2009 to April 23, 2009. This resulted in approximately 26 days of inoperability. Additionally,the investigation determined that EDG 'B' was unable to fulfill its safety related function from March, 28, 2009 to April 21, 2009. This condition resulted in a failure to meet the required actions associated with TS Action Statement 3.8.1.B.4 and Condition C, which is a condition prohibited by the plant's Technical Specifications. Therefore, it is reportable based on 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications."
2612009002 | Robinson 2 | 06/29/2009 | 08/27/2009 | ML09244076 | <strong>Failure to Complete Technical Specifications Required Action within the Allowed Completion Time</strong><br /><i>Abstract:&nbsp;</i>At 1611 hours EDT on June 29, 2009, with H. B. Robinson Steam Electric Plant, Unit No. 2, operating at approximately 100% power, Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.0.3 was unknowingly entered based on failure to meet the required actions of TS LCO 3.3.2, "Engineered Safety Feature Actuation System (ESFAS) Instrumentation." The condition prohibited by the TS was in effect for approximately two minutes and posed no adverse effect to the health and safety of the public. The required actions in effect at the time were associated with TS LCO 3.3.2, Conditions D and E, Required Actions D.1, D.2.1, E.1, and E.2.1, which provide actions for inoperability of one containment pressure channel. The cause of this event was determined to be insufficient work instructions to describe the impact of the repair activities for the containment pressure channel. During the repair, the channel was removed from the tripped condition due to interruption of power when the comparator was removed from the circuit. The channel was returned to the tripped condition within about 2 minutes by replacement of the comparator and subsequently returned to operable status. Removing the channel from the tripped condition resulted in a failure to meet the required actions associated with TS LCO 3.3.2, which is a condition prohibited by the plant's Technical Specifications. Therefore, this condition is reportable under 10 CFR 50.73(a)(2)(i)(B), for any operation or condition which was prohibited by the plant's Technical Specifications.
2612009003 | Robinson 2 | 11/06/2009 | 01/05/2010 | ML10011021 | <strong>Manual Reactor Trip due to Failure of 'A' Steam Generator Level Module</strong><br /><i>Abstract:&nbsp;</i>At 2203 hours EST on November 6, 2009, with H. B. Robinson Steam Electric Plant, Unit No. 2, operating at approximately 100% power, control room operators responded to alarms received for steam flow greater than feed flow and level deviation on 'A' Steam Generator. Feed Regulating Valve, FCV-478, for 'A' Steam Generator indicated closed with controller demand of 0 percent. Control room operators attempted to manually open FCV-478. During this time, an increase in feed flow was noted. The 'A' Steam Generator level continued to lower to approximately 35 percent. The reactor was manually tripped at 2203 as the trip setpoint was approaching. The event was caused by a premature failure of the flow error signal summator power supply for the 'A' Feed Regulating Valve Control Loop FC-478E. The summator power supply has been replaced and the loop was calibrated successfully. The condition is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
2632009001 | Monticello | 04/02/2009 | 12/22/2010 | ML10357003 | <strong>Containment Overpressure Not Ensured in the Appendix R Analysis</strong><br /><i>Abstract:&nbsp;</i>During the review of calculations to respond to a request for additional information from the NRC in support of the station's Extended Power Uprate license amendment, station personnel discovered that although the plant credits Containment Overpressure, the Appendix R analysis does not ensure Containment Overpressure is maintained. The cause of the event was the calculation that credited the Containment Overpressure was either not reviewed by fire protection program personnel or program personnel failed to internalize the need for a revision to the Appendix R analysis. Until the issue is resolved per the guidance of Regulatory Guide 1.189, compensatory measures have been put in place to address the vulnerabilities.
2632009002 | Monticello | 04/02/2009 | 05/29/2009 | ML09152013 | <strong>Pipe Whip For High Energy Line Break</strong><br /><i>Abstract:&nbsp;</i>On April 2 and 14, 2009, with the plant shutdown and in Mode 5, plant personnel were performing a HELB pipe whip and jet impingement walk down of areas inaccessible during operations. During the walk down, two potential HELB pipe whip issues were found (RCIC HELB in the Steam Chase and Main Steam HELB in the Condenser Room). The cause of the event was a failure by station personnel to identify and correct these potential pipe whip issues during the HELB re-evaluation completed in 1986. The potential HELB conditions were corrected by a modification performed during the outage.
2632009003 | Monticello | 05/12/2009 | 07/13/2009 | ML09194054 | <strong>Main Steam Line B Flow Isolation Instrumentation Inoperable due to Leaking Equalizing manifold Valve</strong><br /><i>Abstract:&nbsp;</i>On 05/12/2009 at 21:30, while raising power from 30 to 50%, Operators entered an action statement pertaining to TS 3.3.6.1 due to the apparent failure of B' Main Steam Line Flow Isolation Sensor. The action statement was related to the loss of safety function due to the '8' MSL flow isolation indication indicating approximately 25% lower than the other three flow instruments. The cause of the event was the manifold equalizing valve failure to fully close due to galling of the valve stem threads. Immediate corrective actions were to isolate the indicator and replace the manifold equalizing valve. Planned actions are to replace all three-way Fetterolf safety related and/or risk significant instrumentation manifold equalizing valves and four ATWS three-way manifolds and two manifolds associated with risk significant instruments.
2632009004 | Monticello | 07/01/2009 | 08/28/2009 | ML09240055 | <strong>Missed Technical Specification Action for Failed Technical Specification Surveillance on Standby Gas Treatment System</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2009 during the performance of a Technical Specification Surveillance, an out of band reading was taken. This condition was not discovered until later reviews of the completed surveillance and resulted in the station not entering the required action statement. The root cause of the event was an inadequate Technical Specification program management as evidenced by several missing and weak barriers (defense in depth). Corrective actions taken or planned include: The procedure was revised and the surveillance satisfactorily re-performed; face to face meetings between the SROs and the Plant Manager will be conducted to discuss this event and to obtain a commitment for behavior change; develop and implement a new barrier in the SOMS LCO tracking process for identifying the ITS action statements to be entered during a given work week and work necessary to exit the action statement.
2632009005 | Monticello | 08/20/2009 | 05/14/2010 | ML10138066 | <strong>Failed Fusible Link on Door 18</strong><br /><i>Abstract:&nbsp;</i>During operator rounds, a High Energy Line Break (HELB) barrier door was found closed. At the time of the event it was believed this condition had the potential to result in the loss of both the upper and lower 4 kV switchgear rooms if a HELB event were to occur. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 was entered and the condition was corrected. Subsequent evaluation determined the station would have maintained one source of offsite power. An investigation determined that the root cause of the event was that the door's fusible link had failed due to cyclic overload caused by repeated door over-travel. Corrective actions taken or planned include: the failed fusible link was replaced and the door restored for operation; the site is investigating alternative HELB door configurations for modification to handle the worst case flooding loads and door 18 will be placed in a shut configuration; if this is found not to be practical, the door 18 closer will be evaluated to determine if a model less susceptible to link failure can be obtained.
2652009001 | Quad Cities 2, Quad Cities 1 | 03/25/2009 | 06/09/2009 | ML09167009 | <strong>Failure of Common Unit EDG Auxiliaries to Transfer Power Sources to Support Unit 2</strong><br /><i>Abstract:&nbsp;</i>On April 10, 2009, during a routine operating surveillance it was discovered (discovery date) that the Common Unit (Unit 1/2) Emergency Diesel Generator (EDG) [DG] auxiliaries would not automatically transfer from Unit 1 to Unit 2 power feeds as required. Troubleshooting of the Unit 1/2 EDG support equipment logic determined that a fuse [FU] had failed on March 25, 2009 (event date), causing a loss of power to the circuit. This failure occurred during routine maintenance and was not discovered for 16 days. The unidentified blown fuse resulted in the 1/2 EDG being Tech Spec "inoperable" from March 25, 2009 (1200) to April 11, 2009 (0234). This condition is prohibited by Technical Specification (TS) 3.8.1.B.4, since the 1/ 2 EDG was inoperable for greater than seven (7) days without the LCO Action Statements being met. The fuse was subsequently replaced and power to the circuit was restored by 0234 hours on April 11, 2009, restoring the Unit 1/2 EDG to an operable status. It should also be noted that, on March 31, 2009, from 0104 hours to 0144 hours, and again from 0836 hours to 1218 hours, the Unit 2 EDG was rendered inoperable to perform surveillances per Tech Spec SR 3.8.1.2 and SR 3.8.1.3, for monthly start and load testing. While in this inoperable condition, concurrent with the inoperable condition of the Unit 1/2 EDG, as noted above, Unit 2 had no Tech Spec operable EDGs. This condition is prohibited by TS 3.8.1.E, since the 1/2 EDG and the Unit 2 EDG were simultaneously inoperable for greater than 2 hours without the LCO Action Statements being met. The failure of the logic circuit did not create any actual plant or safety consequences. The Unit 1/2 EDG was fully capable of responding to a Loss of Off-site Power (LOOP) on either Unit 1 or Unit 2, concurrent with a Loss of Coolant Accident (LOCA). The affect of this condition was limited to the unlikely scenario of a LOOP/LOCA on Unit 2 with a degraded voltage condition on Unit 1. There were no degraded voltage conditions on Unit 1 during this event. This issue was determined to have resulted in a past operation or condition prohibited by the plant Tech Specs, and is reportable per 10CFR50.73(a)(2)(i)(B), since the 1/2 EDG was inoperable for greater than seven days and exceeded TS 3.8.1.B, and since the 1/2 EDG was inoperable for greater than two hours and exceeded TS 3.8.1.E.
2662009001 | Point Beach 1 | 03/09/2009 | 05/06/2009 | ML09128019 | <strong>Component Cooling Water Pump Inoperable In Excess of Technical Specification Allowed Completion Time</strong><br /><i>Abstract:&nbsp;</i>From 1724 hours on 1/1/09 to 1410 hours on 1/5/09, and from 1031 hours on 1/27/09 to 1539 hours on 1/31/09, oil from the inboard bearing oiler of component cooling water (CCW) pump, 1P-11B, leaked at a rate that could have prevented the pump from fulfilling its 30-day mission time. During the periods of oil leakage, the pump remained in service. Safety analyses credit the CCW system for 30 days of continuous operation during the post-accident recirculation phase. Reviews completed in March 2009 concluded that the pump would not have fulfilled its 30-day mission time during the referenced timeframes. Therefore, the pump was inoperable in excess of the 72-hour Completion Time allowed by Technical Specification 3.7.7.A. The event was caused by the failure to document oil additions to 1P-11B in the corrective action program (CAP) and a failure to perform an adequate operability review. Corrective actions include reinforcing the importance of documenting oil additions in the CAP and revising maintenance and operation procedures. During the periods of oil leakage, required CCW flow was maintained to safety-related equipment. The event is of low safety significance.
2692009001 | Oconee 1, Oconee 2 | 06/10/2009 | 08/06/2009 | ML09223059 | <strong>Several Prior Spent Fuel Pool Configurations Did Not Comply with TS 3.7.13</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2009, it was determined that there had been three (3) prior instances where spent fuel assemblies had not been stored in the Spent Fuel Pool (SFP) in compliance with Technical Specification (TS) 3.7.13. Each of the instances occurred in the shared Unit 1 and 2 SFP (Unit 3 has a separate SFP), during refueling outages, and in each case, the noncompliance existed from approximately one (1) week to one (1) month before the fuel was reloaded and TS compliance subsequently restored. TS LCO 3.7.13, Condition A states, [upon discovery of the noncompliance] "Initiate action to move the noncomplying fuel assembly to the correct location." The required action completion time is given as "immediately." Duke has concluded that in each of these instances, a noncompliance with the TS existed that was not corrected in a timeframe commensurate with the required action completion time. Consequently, this event is being reported pursuant to 10 CFR 50.73 (a) (2) (i) (B) as a condition prohibited by the TSs. As interim corrective actions, both Oconee current SFPs were confirmed to be in full compliance with TS 3.7.13, and applicable fuel handling procedures were revised to ensure that future storage configuration changes are validated by the subject matter expert (s) before being made. This event is considered to have no significance with respect to the health and safety of the public.
2692009002 | Oconee 1, Oconee 2, Oconee 3 | 10/21/2009 | 12/17/2009 | ML09357019 | <strong>Automatic Initiation of Emergency Feedwater upon Loss of Main Feedwater</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2009, it was determined that there had been sixteen (16) prior instances where, while in the mode of applicability, a main feedwater pump (MFDWP) had been reset but was not aligned and providing main feedwater. Had the other MFDWP tripped, the Emergency Feedwater Pumps (EFWPs) would not have initiated on loss of main feedwater. This condition was not recognized; therefore, operability was not restored immediately as required by TS. 3.7.5. This Technical Specification compliance issue involved an Electro/Mechanical signal interface which was not clearly understood and, thus, compliance not satisfied during required unit start-up activities. Design and procedure changes have been implemented to ensure compliance with Technical Specifications. This event is considered to have no significance with respect to the health and safety of the public.
2722009001 | Salem 1 | 12/05/2009 | 03/29/2010 | ML10103109 | <strong>Chillers Inoperability Exceeds TS Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On 11/29/09 at 1345 hours, the 12 Chiller was removed from service for maintenance and design change installation. With one Chiller inoperable, a 14-day Limiting Condition for Operation (LCO) was entered. On 12/02/09 at 1713 hours the 13 Chiller was found out of service and declared inoperable. With two inoperable Chillers, a 72-hour LCO was entered. On 12/04/09 at 2017 hours, the 12 Chiller was declared operable following completion of maintenance and testing of the design change installation. The 72-hour LCO was exited. However, the original 14-day LCO window remained active because of the inoperability of 13 Chiller. On 12/07/09, during the operability retest of 13 Chiller, the 12.Chiller tripped on low temperature freeze protection and a 72-hour LCO was re-entered. A detailed troubleshooting of the 12 Chiller identified that the low temperature trip switch was set 7 degrees F above its required setpoint. The 12 Chiller low temperature trip switch was promptly reset to the correct setpoint. However, because the low temperature trip switch setting that made the 12 Chiller inoperable existed during the period 12/02/09 through 12/07/09 while 13 Chiller was inoperable, two Chillers were inoperable for longer than the 72 hours allowed by TS 3.7.10 Action b.3. This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), "any operation ... prohibited by the plant's Technical Specification." '
2752009001 | Diablo Canyon 1 | 03/22/2009 | 05/19/2009 | ML09147028 | <strong>Replacement Steam Generator Support Inadequate due to Improper Washer Plate Installation</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2009, at 13:34 PDT, with Unit 1 in Mode 3 (Hot Standby) a significant condition adverse to quality was verified by plant walkdown of the Replacement Steam Generator (RSG) vertical support bolting. Plant operators entered Technical Specification (TS) 3.0.3, stabilized Unit 1 in Mode 3, and made a nonemergency event notification (EN#44927) in accordance with 10 CFR 50.72(b)(3)(ii)(B) at 17:02 PDT. RSG 1-3 was determined to be in an unanalyzed condition due to two out of sixteen washer plates not seated in the vertical support column adapter due to interfering weld metal on the interior recesses. On March 22, 2009, at 15:36 PDT, a shim was installed between the washer plate and column adapter at each nonconforming location on RSG 1-3. This brought the support columns into compliance with the full design capacity and plant operators exited TS 3.0.3. The cause of the event was determined to be human error by RSG contract personnel due to lack of attention to detail. Similar Unit 1 and 2 installations were confirmed to be adequate.
2752009002 | Diablo Canyon 1 | 06/29/2009 | 08/28/2009 | ML09247008 | <strong>Two Trains of Auxiliary Feedwater Inoperable due to Protection System Failure</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2009, at 06:47 PDT, with Unit 1 in Mode 1 (Power Operation) the Eagle 21 Protection Set II, Rack 8, alarmed in the control room due to a Loop Calculation Processor (LCP) card failure. Plant operators declared motor-driven auxiliary feedwater (AFW) Pumps 1-2 and 1-3 inoperable in accordance with TS 3.7.5 Limiting Condition for Operation (LCO). Plant operators entered Operating Procedure (OP) Abnormal Procedure AP-5, "Malfunction of Eagle 21 Protection or Control Channel," and took manual control actions in the control room. On June 29, 2009, at 07:14 PDT, Technical Specification (TS) 3.7.5, Condition C, was exited when the first level control valve (LCV) was placed in manual and a dedicated licensed plant operator was assigned to the AFW level controller. TS 3.7.5 LCO was exited when the second LCV was placed in manual at 07:17 PDT. The cause of the TS 3.7.5 entry was determined to be the result of intended design response to an Eagle 21 LCP failure, i.e., to lockup the control output in a "fail-as-is" status to minimize a plant transient as a result of a single failure. On June 30, 2009, at 08:26 PDT, the failed Eagle 21 LCP card was replaced and the LCVs returned to automatic level control.
2772009001 | Peach Bottom 2 | 02/12/2000 | 03/24/2009 | ML09086077 | <strong>Clearance Performance Error Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 2/13/09, Operations personnel discovered that a non-compliance existed with Technical Specifications (TS) when a TS Required Action for an inoperable Control Rod (Control Rod 10- 51) was found to be not implemented. Control Rod 10-51 was inoperable since 2/11/09, yet the Control Rod Hydraulic Control Unit directional control valves were discovered to be energized at 0933 hours on 2/13/09. This condition was due to an operator error associated with the performance of a safety clearance that occurred on 2/12/09. Qualifications of individuals involved with this event were removed pending remediation. The lessons learned from this human performance issue will be shared with other personnel. Other management interventions were performed to strengthen administrative programs. There were no actual safety consequences associated with this event. There were no previous similar LERs identified.
2772009002 | Peach Bottom 2, Peach Bottom 3 | 08/19/2009 | 10/09/2009 | ML09286061 | <strong>Pneumatic Supply Degraded for Containment Isolation Valves due to Mis-Positioned Valve</strong><br /><i>Abstract:&nbsp;</i>On 8/24/09, it was determined that certain valves associated with the Primary Containment and Containment Atmospheric Diltuion (CAD) systems were inoperable. This determination was the result of the discovery by maintenance personnel that a 1.5" manual isolation valve (HV-0-07C-10) was in the closed position. HV-0-07C-10 isolates gaseous nitrogen flow from the vapor space of the CAD liquid nitrogen storage tank to the Safety Grade Instrument Gas (SGIG) system. The SGIG system provides pneumatic supply to operate certain valves associated with Primary Containment isolation / vacuum relief and the CAD system. Once discovered closed on 8/24/09, HV-0-07C-10 was promptly re-opened and the affected valves were restored to an operable status by 1445 hours on 8/24/09. This condition resulted in a condition prohibited by Technical Specfications and a loss of safety function of the Unit 2 and 3 Primary Containment isolation capability. The event was due to personnel error. HV-0-07C-10 was locked open and added to the locked valve program. This event has been evaluated to not be risk significant.
2782009001 | Peach Bottom 3 | 01/21/2009 | 03/06/2009 | ML09071025 | <strong>Control Rods Inoperable During Mode 2 Operations as a Result of Interferences</strong><br /><i>Abstract:&nbsp;</i>As a result of control rod interference monitoring testing performed by Operations personnel on 1/28/09, it was determined that three control rods were inoperable during the unit shutdown that was performed on 1/21/09. This testing determined that Control Rods 14-55, 18-55 and 42-55 could be inoperable for operational conditions involving time periods when reactor pressure is below 850 psig (Mode 2 operations). This occurrence is considered reportable as a common cause that resulted in the inoperability of three control rods for approximately 4.75 hours on 1/21/09 during Mode 2 unit operations. The common cause is related to control rod blade interferences with the fuel channel. There were no actual safety consequences associated with this event. Appropriate shutdown margin was maintained during this event. A control rod interference monitoring / testing program was established. Extent-of-condition testing was performed on Units 2 and 3. There were no previous similar LERs identified.
2782009002 | Peach Bottom 3 | 01/26/2009 | 03/24/2009 | ML09086077 | <strong>Inoperable 'A' Wide Range Neutron Monitor Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>A condition prohibited by Technical Specifications (TS) occurred when Unit 3 entered Mode 2 operations for plant startup on 1/26/09 at 0900 hours. Specifically, the TS 3.0.4 requirements were not met to allow for an entry into a mode of applicability with the 'A' Wide Range Neutron Monitor inoperable. The cause of the inoperable 'A' WRNM was a result of inadequate human performance regarding a technical decision made during the outage (prior to 1/26/09 startup). The technical decision allowed for entry into Mode 2 after an adjustment was was to the mean square voltage (MSV) component of the WRNM function resulting in the MSV being inaccurate for a small range of neutron flux while in Mode 2. Individuals involved with the event have been counseled regarding the importance of rigorous technical evaluations when making decisions that could affect TS equipment performance. WRNM adjustment procedures are also being upgraded. There were no actual safety consequences associated with this event. There were no previous similar LERs identified.
2782009003 | Peach Bottom 3 | 03/26/2009 | 05/12/2009 | ML09135004 | <strong>Inoperable Containment Isolation Valve Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 3/26/09, it was discovered that the 3D Residual Heat Removal Pump Suppression Pool Suction Isolation Valve (MO-3-10-013D) was degraded due to a greasing deficiency identified during performance of extent-of-condition testing associated with grease deficiencies previously discovered on motor-operated valves (MOVs). It was determined that this condition was prohibited by Technical Specifications (TS) since this valve is a Primary Containment Isolation Valve (PCIV) and was inoperable for containment isolation purposes for a time period longer than allowed by TS. The cause of the greasing deficiency was due to grease hardening primarily due to inadequate preventive maintenance. The valve was repaired and returned to serivce on 3/27/09. Appropriate upgrades to the MOV lubrication program are being made. There were no previous similar LERs identified involving MOV grease deficiencies.
2782009004 | Peach Bottom 3 | 04/20/2009 | 08/31/2009 | ML09244080 | <strong>Inoperable Ventilation Fan Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 8/17/09, Engineering personnel determined that one Unit 3 High Pressure Service Water (HPSW) / Emergency Service Water (ESW) ventilation subsystem was rendered inoperable as a result of preventive maintenance performed on 4/13/09 for the motor control center breaker assembly for the 3B HPSW/ESW Pump Room Ventilation Supply Fan. This condition existed until 7/5/09 when repairs were made to a motor starter contactor / thermal overload relay connection. This occurrence was considered as a condition prohibited by Technical Specifications (TS) since the inoperable HPSW/ESW ventilation subsystem resulted in one Unit 3 HPSW subsystem being considered to be inoperable for a time period greater than allowed by TS. The underlying cause of this condition was that the associated maintenance procedure for preventive maintenance performed on 4/13/09 did not provide clear direction for torquing the connection. The motor starter mechanism / thermal overload relay was repaired on 7/5/09. The associated maintenance procedure is being revised. There were no actual safety consequences associated with this condition.
2782009005 | Peach Bottom 3 | 08/10/2009 | 10/07/2009 | ML09282048 | <strong>Common Cause Failure of 'C' and 'E' Wide Range Neutron Monitors</strong><br /><i>Abstract:&nbsp;</i>As a result of a cause evaluation completed on 9/15/09 involving Wide Range Neutron Monitors (WRNMs) failures, it was identified that the 'C' and 'E' WRNMs had failed as a result of an apparent common cause. The cause evaluation determined that both of these WRNMs failures were likely the result of a suspected degraded connection between the upper cable and the WRNM detector element. There were no actual safety consequences associated with this event. The 'A' Reactor Protection System trip system was placed in trip prior to entering Mode 2 on 9/13/09. Therefore, the safety function of the 'C' and 'E' were ensured to be met prior to entering the mode of applicability for the WRNMs for the recent refueling outage. The 'C' and 'E' WRNMs were replaced in September 2009 during the P3R17 refueling outage. The vendor manufacturing process is being reviewed for potential improvements. There were no previous similar LERs identified.
2782009006 | Peach Bottom 3 | 09/13/2009 | 10/23/2009 | ML09301012 | <strong>Unplanned Manual Scram due to Shortening Reactor Period During Scheduled Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 9/13/09, at approximately 2244 hours, Operations personnel manually scrammed the Unit 3 reactor from 0.2% power as a result of an observed shortening reactor period. The reactor was manually scrammed by placing the mode switch in the shutdown position. There were no actual safety consequences associated with this event. The scram function operated as designed and there were no complications as a result of the manual scram. The event was considered not to be risk significant. The cause of the manual scram was due to a shortening reactor period during a planned soft shutdown using control rods. The manual scram was required due to a small amount of feedwater being added to the reactor during a time period when control rods were not being inserted. This resulted in a decrease in the reactor period. Plant shutdown procedures for Units 2 and 3 will be revised to provide additional control of operational activities to minimize the likelihood of a short period when performing a soft shutdown. There were no previous similar LERs identified.
2782009007 | Peach Bottom 3 | 09/14/2009 | 11/04/2009 | ML09313006 | <strong>Oil Leak from Main Steam Isolation Valve Dashpot Results in Short Valve Stroke Time</strong><br /><i>Abstract:&nbsp;</i>On 9/18/09, an Engineering evaluation determined that the ouboard Main Steam Isolation Valve (MSIV) A0-3-01A-086A did not meet its required Technical Specification (TS) minimum closure time of >/. 3 seconds. This determination was based on MSIV stroke time testing performed on 9/14/09 when entering a refueling outage. This condition was considered as a condition prohibted by TS since there was evidence that the condition had existed during plant operations. The cause of the event was due to not requiring preventive maintenance for the MSIV oil dashpot needle control valve. Based on troubleshooting during the refueling outage, it was determined that when the oil dashpot stroked, a small amount of oil would leak from the o-ring seal around the stem of the 34" needle control valve. Over time, this resulted in insufficient oil in the dashpot causing inadequate dampening of the MSIV motion. The leaking MSIV oil dashpot needle control valve was replaced. The preventive maintenance program will be upgraded to ensure that the Units 2 and 3 MSIV needle control valves receive appropriate preventive maintenance in future outages. There were no actual safety consequences associated with this event. There were no previous similar LERs identified.
2802009001 | Surry 1, Surry 2 | 05/30/2009 | 07/29/2009 | ML09217016 | <strong>Inoperable Emergency Service Water Pump Caused by Inadequate Design Change</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2009, with Units 1 and 2 at 100% reactor power, diesel engine driven Emergency Service Water Pump "A" (ESWP A) failed to start due to water intrusion into exhaust piping. The exhaust piping was recently modified to add missile protection and the applied sealant failed. Following engine repairs and change of the sealant material type, the pump was declared operable on June 3, 2009. During operator rounds on June 6, 2009, water was discovered leaking around the exhaust pipe for ESWP A and the pump was again declared inoperable. The pump was returned to pre-modification Configuration and declared operable on June 9, 2009. The direct cause of both events was water intrusion into the ESWP diesel exhaust. The root cause was the failure of the design change to account for a full range of design inputs. A new modification will be developed and the design change process will be strengthened to prevent recurrence. The ESWP A failures did not affect the health and safety of the public. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B), any operation or condition that was prohibited by the plant's Technical Specification, and 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2802009002 | Surry 1, Surry 2 | 09/24/2009 | 11/23/2009 | ML09335053 | <strong>Emergency Service Water Pumps Potential Flooding due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On September 24, 2009, with Units 1 and 2 at 100% reactor power, it was discovered that the three emergency service water (ESW) pump oil cooler outlet lines, which penetrate the pump base plates, were not sealed to prevent pump house water intrusion. The ESW pump house is designed to withstand flooding from hurricane driven tidal surges of 22.7 feet. With the pump base plates at approximately 18 feet above sea level, potential pump inoperability would occur if the water level rises above 18 feet. The cause evaluation identified that in the 1990's, the threaded interface seals on the outlet lines were no longer utilized. The evaluation also found the apparent cause to be inadequate procedural guidance for sealing the outlet lines. Following discovery, seals were installed. The maintenance procedure has been strengthened to prevent recurrence. An evaluation determined this issue to be of very low risk significance, therefore, the health and safety of the public was not affected. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B), any event or condition which was prohibited by Technical Specifications.
2812009001 | Surry 2 | 11/29/2009 | 01/28/2010 | ML11208197 | <strong>Manual Reactor Trip Initiated to Replace a Rod Control Data Logging Card</strong><br /><i>Abstract:&nbsp;</i>On November 29, 2009 at 0808 hours, with Unit 2 reactor critical, operators identified a discrepancy between Control Bank 'B' (CBB) Group 1 and Group 2 step demand counters (SDC) during startup physics testing. At 1045 hours, the decision was made to manually trip Unit 2 to replace a Supervisory Data Logging Card in the Rod Control System Logic Cabinet. Replacing the card would disable multiple group SDCs. The card was replaced, rod control system tested, and the system returned to service. At 2150 hours, Unit 2 reactor achieved criticality and startup physics testing continued. When the reactor was manually tripped, the control rods promptly inserted and all systems responded as expected. The Supervisory Data Logging Card will be tested and results reviewed to determine the cause of the discrepancy. Based upon the test results, options will be reviewed to reduce future failures. The reactor trip resulted in no significant safety consequences or implications and the health and safety of the public were not affected. This report is being submitted pursuant to 10 CFR 50.73(a)(2)(iv)(A), manual actuation of the reactor protection system (RPS).
2822009001 | Prairie Island 1, Prairie Island 2 | 01/14/2009 | 03/16/2009 | ML09076050 | <strong>Unanalyzed Condition due to Manual Actions That Do Not Comply with 10 CFR 50, Appendix R</strong><br /><i>Abstract:&nbsp;</i>On January 14, 2009 during a review of Prairie Island Nuclear Generating Plant's (PINGP) safe shutdown compliance assessment, it was discovered that a fire in either fire area 31 or 32 could cause the loss of the instrument air system which is credited with providing compressed air to the safeguards chilled water system. The safeguards chilled water system is required in order to achieve and maintain hot shutdown for compliance with 10 CFR 50 Appendix R. This condition is of low safety significance because in the event of a loss of instrument air, the safeguards chillers have compressed air cylinders which provide a minimum of 8 hours of backup air. Operators validate on every shift that there is at least a 12 hour supply of backup air in the cylinders and have instructions that direct replacement of the compressed air cylinders if less than a 12 hour supply of air is available. The discovery of this condition is being reported as an unanalyzed condition in accordance with 10 CFR 50.73(a)(2)(ii)(B) due to the clarification in Regulatory Issue Summary (RIS) 2006-10 that Appendix R, Paragraph III.G.2 does not allow the use of operator manual actions to satisfy the requirements of Appendix R. Replacement of the air cylinders is considered an operator manual action.
2822009002 | Prairie Island 1 | 03/19/2009 | 05/18/2009 | ML09139039 | <strong>Unplanned Safety Related Actuation of 121 Water Cooling Pump</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2009, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was operating in mode 1 at 100% power. The 121 Motor Driven Cooling Water Pump (MDCLP) was aligned as a safeguard replacement pump per procedure for planned maintenance of the 12 Diesel Driven Cooling Water Pump (DDCLP). Maintenance steps were completed to a point allowing restoration and post maintenance testing (PMT) of 12 DDCLP in accordance with a maintenance procedures. However, required steps in the operation's procedure to align the 121 MDCLP to its normal non-safeguards alignment prior to starting post maintenance testing were not performed. When aligned as a safeguard pump, any unplanned actuation is reportable under 10 CFR 50.73(a)(2)(iv). 121 MDCLP operated normally and there were no adverse plant effects from the transient.
2822009003 | Prairie Island 1 | 03/23/2009 | 05/22/2009 | ML09142057 | <strong>Component Cooling System Vulnerability to Tornado Missile Hazard</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2009, at approximately 1200 CDT, Northern States Power Company – a Minnesota corporation (NSPM) design engineering personnel discovered a potential vulnerability with Prairie Island Nuclear Generating Plant (PINGP) Unit 1 component cooling (CC) piping. The potential exists for a tornado missile hazard to impact the CC piping that supplies the 122 spent fuel pool (SFP) heat exchanger (HX). In the normal configuration, a missile impact to this piping would affect both trains of PINGP Unit 1 component cooling thus rendering the CC system inoperable. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degrades plant safety and 10 CFR 50.73(a)(2)(v)(A) as a condition that could have prevented the fulfillment of a safety function of a system that is needed to maintain the reactor in a safe shutdown condition. The condition was caused by a design change that added the 122 SFP HX prior to initial plant startup. The 122 SFP HX is currently isolated to protect the CC system function from a tornado missile hazard.
2822009004 | Prairie Island 1, Prairie Island 2 | 04/06/2009 | 01/07/2011 | ML11010024 | <strong>Residual Heat Removal System Inoperability While in Mode 4 due to Potential Steam Voiding</strong><br /><i>Abstract:&nbsp;</i>During scoping for Generic Letter 2008-01, a concern with the Residual Heat Removal System (RHR) was identified. High temperature water had the potential to flash to steam during a Loss of Coolant Accident (LOCA) scenario while in Mode 4. Subsequent analysis determined that, while in Mode 4, the temperature of the fluid at the RHR pump suction header exceeded 226 degrees Fahrenheit (F) which, under LOCA conditions, could have resulted in a void being entrained into the common RHR pump suction. This condition rendered both trains of RHR inoperable. This condition was allowed to occur because operating procedures failed to address voiding due to hot fluid in the RHR piping. An additional contributor to the condition was the failure to adequately address Westinghouse Nuclear Safety Advisory Letter (NSAL) 93-004. Current corrective actions have been issued to modify operating procedures to manage RHR void formation. The LER supplement documents the licensee's subsequent additional engineering analysis that determined that if a (LOCA) occurred in Mode 4, it cannot be assured that the RHR pumps operating for shutdown cooling would have also functioned for the Emergency Core Cooling Systems (ECCS). This did not align with Technical Specifications 3.5.3, Note 1, that allowed a RHR pump to be considered Operable for ECCS while it was aligned and operating for shutdown cooling.
2822009005 | Prairie Island 1 | 05/18/2009 | 07/17/2009 | ML09198053 | <strong>Reactor Trip Due to 12 Circulating Water Pump Trip Caused by Electrical Ground Fault</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2009 at 1305 hours, the site experienced a lockout of the 12 Circulating Water pump due to a ground fault in the power supply cable. This resulted in a turbine trip and associated reactor trip of Unit 1. Corrective actions taken or planned include repair of the faulted cable and improvements in the implementation of the cable monitoring program.
2822009006 | Prairie Island 1, Prairie Island 2 | 10/20/2009 | 03/31/2011 | ML11091015 | <strong>Unanalyzed Condition Due to Potential Safety System Susceptibility to Turbine Building Flooding Due to a Postulated High Energy Line Break, Supplement 2</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2009, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was in Mode 5 during a refueling outage. Unit 2 was in Mode 1 operating at full power. PINGP staff determined that in the event of flooding in the Turbine Building, due to a postulated high energy line break (HELB), operability of the Unit 1 Emergency Diesel Generators (D1 and D2) may not be assured. The as-found condition was an original design issue that was determined to be reportable during preparation of an analysis of flooding due to a postulated HELB in the Turbine Building. Physical and procedural changes have been made to minimize challenges to plant equipment and personnel in combating potential flooding events. The causal evaluation determined that an incorrect mindset was developed that large internal flooding events in the Turbine Building could be mitigated by operator action. It was also determined that management oversight and resolution of identified Turbine Building HELB and flooding issues were lacking.
2822009007 | Prairie Island 1 | 09/13/2009 | 03/19/2010 | ML10078045 | <strong>Unanalyzed Condition due to a Breached Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2009, Northern States Power Company, a Minnesota corporation (NSPM), doing business as Xcel Energy, documented an apparent breach between the Prairie Island Nuclear Generating Plant (PINGP) 11 and 12 Battery Rooms. The two Battery Rooms are separated by an eight inch concrete block wall that contains a penetration seal. The penetration seal of consists a five-inch and one-inch conduit filled and sealed to form a fire barrier. The five-inch conduit was breached to run temporary cable for maintenance work. An evaluation completed on October 28, 2009, concluded that the as-found condition was a breached fire barrier, such that the required degree of separation for redundant safe shutdown trains was lacking. Thus, this event is belng reported In accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition. The causal evaluation concluded that the site does not have a Fire Barrier Impairment Permit form so it was not included In the work package as required by fleet procedures. In addition, the pre-maintenance walkdown failed to identify shortcomings in the planning process with respect to the temporary cable routing.
2822009008 | Prairie Island 1 | 12/14/2009 | 02/11/2010 | ML10047075 | <strong>Unanalyzed Condition due to an Inadequate Fire Barrier</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2009, Northern States Power Company, a Minnesota corporation (NSPM), doing business as Xcel Energy, identified that the power source to Safeguards Bus 16 was not protected per 10 CFR 50 Appendlx R requirements in Fire Area (FA) 32. For a fire that occurs in FA32, fire induced damage to cable 1C-333 could cause a spurious lockout of the 1RY transformer source to Bus 16. Another source, the D2 Emergency Generator, was available to power Bus 16. However, cables affecting the operation of the D2 Emergency Generator exited a fire-protected cable tray and ran unprotected for a short distance before they exited Fire Area 32. This condition was previously reported to the NRC as an unanalyzed condition (10 CFR 50 72(b)(3)(ii)(B)) on December 14, 2009 due to the missing fire barrier. The causal evaluation for this event determined that the apparent cause was inattention to detail and the lack of a detailed procedure to perform R Appendix circuit analysis. An hourly fire watch was previously in place for Fire Area 32 as a compensatory measure and will continue until the cable protection issue has been resolved. Cables for the credited power source to Safeguards Bus 16 will be provided the required fire protection to meet the safe shutdown requirements in National Fire Protection Association (NFPA) 805.
2822009009 | Prairie Island 1, Prairie Island 2 | 12/18/2009 | 02/16/2010 | ML10048031 | <strong>Radioactive Source Inventory Discrepancy</strong><br /><i>Abstract:&nbsp;</i>During the 2009 radioactive source inventory at Prairie Island Nuclear Generating Plant (PINGP), station personnel determined that two sources were missing that are greater than 10 times the quantity specified in 10 CFR 20 Appendix C. These two sources included a 0.07 microcurie (uCi) U-234 source installed in a radiation monitor detector and a 2 uCi mixed gamma standard that contains 0.09 uCi of Am-241. A search for the sources was performed. The 2 uCi mixed gamma standard containing 0.09 uCi of Am-241 was found. The cause of the issue was that the significance assigned to the source control program did not align with the potential impact associated with loss of control of radioactive sources. Procedure upgrades, increased supervisory oversight, and accountability for program ownership will improve administration of the radioactive source control program.
2852009001 | Fort Calhoun | 01/12/2009 | 03/13/2009 | ML09082008 | <strong>Failure to Monitor Waste Gas Transfer Due to Operator Error</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2009, at 1513 Central Standard Time, Waste Gas was pumped from the Vent Header to Waste Gas Decay Tank, WD-29B. The Waste Gas Analyzer was aligned to sample Waste Gas Decay Tank, WD-29D. The Waste Gas was not transferred to the tank that was being sampled. This was a violation of the Technical Specifications (TSs). After the operator had completed the Waste Gas Transfer he realized that he had pumped to the wrong tank. The Waste Gas Analyzer was aligned to sample Waste Gas Decay Tank WD-29B. The sample confirmed that the concentrations of hydrogen and oxygen were below the flammability limits of the gases. A root cause analysis determined that the reason for not complying with the TS was the inappropriate use of turnover logs as the sole method to track long term off-normal plant status information. This resulted in insufficient System status information barriers (labels, tags, etc.) being present to remind operators of the off-normal alignment of the Waste Gas System. Criteria have been developed for weekly reviews of turnover sheets to ensure sufficient status control barriers for components (labels, tags, etc.) are in place.
2852009002 | Fort Calhoun | 04/14/2009 | 08/03/2009 | ML09223034 | <strong>Technical Specification Violation due to Installation of an Unqualified Part in a Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>A non-qualified relay was mistakenly installed in the pump control unit of a process radiation monitor on November 21, 2008. This condition was discovered on April 13, 2009, during review of work to replace a pump control relay for a different monitor. In response to this discovery, the non-qualified relay was replaced with a qualified K1 relay on April 14, 2009. During the time that the non-qualified relay was installed, RM-062 (Auxiliary Building Vent Stack Radiation Monitor) and RM-051 (Containment Noble Gas Radiation Detector) were inoperable at the same time in violation of TS 2.15, Instrumentation and Control Systems. The root cause was determined to be that management expectations are not clearly established to verify the safety classification of replacement components as required by the station's maintenance work control procedure. Appropriate station documents will be revised to clearly establish management expectations to verify the safety classification of replacement components. This will be completed by November 1, 2009.
2852009003 | Fort Calhoun | 04/30/2009 | 08/10/2009 | ML09230023 | <strong>Void in Safety Injection Piping During Operation due to Inadequate Procedural Guidance</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2009, during the first performance of QC-ST-HPSI-0001, "High Pressure Safety Injection Gas Accumulation Detection," a void was discovered on the cooled suction line to high pressure safety injection (HPSI) pump SI-2B. Technical Specification (TS) 2.3(2)e, a 24-hour limiting condition for operation (LCO), was entered. Actions were successfully taken to vent the void. Follow-up ultrasonic testing was done to confirm the location was water filled. The TS LCO was exited approximately 1 hour later. The frequency of the surveillance test was temporarily shortened from quarterly to monthly to allow for increased monitoring of the void. On May 28, 2009, the location was retested and confirmed to be water filled. The root cause was determined to be the incomplete review and identification of SI system high point vents during the development of SI system drain/refill plans. A review of operating instructions, in combination with the system elevation drawings, will be conducted to ensure adequate procedural guidance is provided for filling and venting of piping at the high point vents. The review will include those systems covered under Generic Letter 2008-01. The review will be completed by September 30, 2009. Procedural revisions to provide guidance for proper fill and venting of the HPSI cooled suction piping will be developed and issued by September 30, 2009.
2852009004 | Fort Calhoun | 11/26/2006 | 04/23/2010 | ML10125014 | <strong>Containment Integrity Unknowingly Violated During Performance of a Leak Test</strong><br /><i>Abstract:&nbsp;</i>Containment integrity was unknowingly violated on October 26, 2003, and November 26, 2006, as a result of opening manual containment isolation valve SI-410 (Safety injection Tanks Fill/Drain Valve). This occurred during a surveillance test (ST), when containment integrity was required and administrative controls (dedicated operator) were not implemented. In preparation for performing a leak check of the safety injection tanks leakoff piping, a procedural step in the ST opened manual containment isolation valve SI-410, as well as re-aligning other valves. The procedure prerequisites require the reactor coolant system be pressurized above 600 psig, which results in the reactor coolant system being greater than 210 deg F; thus, containment integrity is required. Prior to the subsequent performance of the ST on November 1, 2009, it was recognized that the opening of SI-410 needed to be administratively controlled. The ST was revised to require administrative controls be in place prior to opening containment isolation valve SI-410. The root cause analysis for this event is the reviewer of the change to QC-ST-SI-3006 failed to identify the conflict between required test conditions (i.e., RCS temperature greater than 210 deg F and containment integrity is required) and opening SI-410 (i.e., manual containment isolation valve).
2852009005 | Fort Calhoun | 11/06/2009 | 05/03/2010 | ML10134012 | <strong>Inoperable Auxiliary Feedwater Train Due to an Inoperable Injection Valve</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2009, during performance of air operated valve diagnostic testing of HCV-1107A (Steam Generator 'A' auxiliary feedwater (AFW) inlet valve), the air regulator setting was found to be 23.6 pounds per square inch gauge (psig). The regulator pressure setting of 23.6 psig is contrary to the required nominal setting of 35 psig credited in calculation FC06904, "Category 1 Air-Operated Valve (AOV) Operator Margin Analysis." (HCV-1107A is an air-to-close valve.) The root causes of this event were determined to be: The most probable root cause of this event is that in 2006 a technician, who knew the standard practice was to set the regulator a minimum of 5 psig greater than the highest benchset, set the regulator at the wrong pressure. The technician noted the benchset flowscan on October 27, 2006, was 17.91 psig and set the regulator to 22.91 psig (nearly 23 psig). This adjustment was not covered by a written instruction. The latent root cause of this event was the adjustment would have been an action not covered by any existing retrievable written instructions. The fundamental flawed assumptions and weak work practice reflected the cultural norms and values that existed in the Instrumentation and Control maintenance organization in 2006. The air regulator for HCV-1107A was reset from 23.6 psig to 35 psig.
2862009001 | Indian Point 3 | 01/02/2009 | 10/30/2009 | ML09314025 | <strong>Automatic Actuation of an Emergency Diesel Generator and Two Auxiliary Feedwater Pumps During Surveillance Testing due to Inadvertent De-Energization of the Normal Supply Breaker to 480 Volt Safeguards Bus 6A</strong><br /><i>Abstract:&nbsp;</i>On January 2, 2009, Instrumentation & Control (I&C) Technicians were performing surveillance testing, when the normal supply breaker for 480 Volt AC safeguards bus 6A inadvertently opened, causing the bus to de-energize. The bus undervoltage control circuitry caused an automatic actuation of emergency diesel generator (EDG) 32 which started and re-energized the bus. In accordance with design, loads on bus 6A were stripped and then re-loaded back onto the bus including actuation of motor driven auxiliary feedwater (AFW) pump (AFWP) 33 and steam driven AFWP 32. All systems performed as designed. AFW was injected into the steam generators (SG) that resulted in an approximate 1-2% change in SG level, a 0.1% increase in reactor power and no control rod movement while in AUTO. The initial root cause analysis (RCA) did not identify a cause but determined the bus 6A breaker trip was caused by energizing its shut trip coil. A subsequent troubleshooting plan and testing did not identify a cause. A revised RCA failed to identify a specific cause but identified a probable cause as a meter lead short between terminals of degraded grid time delay relay (62-1/6A). The relay (62-1/6A) being tested at.the time of the event was replaced and the surveillance test satisfactorily re-performed. Corrective actions included revision of the surveillance test to require the use of different test meter leads and brief of personal on potential that meter leads probes have the potential of a short circuit during meter readings. The event had no effect on public health and safety.
2862009002 | Indian Point 3 | 03/10/2009 | 05/11/2009 | ML09139029 | <strong>Technical Specification Prohibited Condition Caused by Two Main Steam Safety Valves Outside Their As-Found Lift Setpoint Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2009, during the performance of surveillance procedure 3-PT-R006A, main steam safety valves (MSSV) MS-45-1 and MS-48-3 failed their As-Found lift set point test. In accordance with the test, these valves must lift at +/- 3% of their required setting. Valve MS-45-1 lifted at 1112.7 psig outside its acceptance range of 1034 to 1096 psig. Valve MS-48-3 lifted at 1165.1 psig outside its acceptance range of 1077 to 1143 psig. All other MSSVs tested passed their As-Found test criteria and were left within +/- 1% of their required setting in accordance with the test procedure. Technical Specification (TS) 3.7.1,"Main Steam Safety Valves," requires the MSSVs to be operable in accordance with TS Table 3.7.1-1 and Table 3.7.1.-2. TS Surveillance Requirement (SR) 3.7.1.1 requires each MSSV be verified to lift per Table 3.7.1-2 in accordance with the Inservice Testing Program. Operability of the MSSVs includes the ability to open within the setpoint tolerances. As these two valves were found outside their limit they failed their As-Found testing. In accordance with NUREG-1022, Section 3.2.2, reporting guidelines, the existence of similar discrepancies in multiple valves is an indication that the discrepancy may have arose over a period of time, and therefore existed during plant operation and is reportable. The apparent cause of the two MSSVs lifting greater than 3% of their nominal setpoint is indeterminate but most likely caused by setpoint drift. Corrective actions included adjusting the valves, subsequent maintenance during the refueling outage, and re-testing with an As-Left setting within the +/- 1% As-Left set point criteria. The event had no effect on public health and safety.
2862009003 | Indian Point 3 | 05/15/2009 | 07/06/2009 | ML09195032 | <strong>Manual Reactor Trip Due to Steam Generator 33 High Water Level Caused by a Failed 33 Main Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On May 15; 2009, Control Room operators initiated a manual reactor trip for high steam generator (SG) 33 water level which could not be corrected due to a failed open 33 main feedwater (FW) regulating valve (FCV-437) . All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main. condenser. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. In response to the event main FW isolated and the Auxiliary Feedwater System automatically started. The direct cause of the high SG level was the positioner feedback linkage on FCV-437 became disconnected causing the valve to open. The cause of the positioner feedback link disconnection was inadequate procedure direction and written instructions. The valve maintenance procedure did not contain steps to "perform wrench tightness of the rod jam nuts after positioner linkage was disconnected, and then reconnected during valve overhaul. There were also no steps in the diagnostic test procedure that directed workers to verify wrench tightness of the jam nuts. A contributing cause was ineffective use of Human Performance (HP) tools. Corrective actions included repair of the valve positioner linkage and verification of other position linkage assemblies. The valve Overhaul. procedure and diagnostics procedure will be revised to ensure direction to wrench tighten jam nuts and verify installation of lock washers on jam nuts, wrench tighten connection of linkage to the valve yoke and positioner, wrench tighten connection of the turnbuckle to yoke and verify mifiimum thread engagement of the rod to turnbuckle. The event had no effect on public health and safety.
2862009004 | Indian Point 3 | 05/28/2009 | 04/21/2010 | ML10118006 | <strong>Generator Water Level Caused by Inadequate 31 Main Feedwater Pump Governor Valve Setting</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2009, the Control Room received 32 MBFP vibration alarms and reduced power to approximately 65% and removed the 32 MBFP from service. The 31 MBFP was unable to supply sufficient feedwater (FW) flow to maintain Steam Generator (SG) levels which resulted in all four main FW regulating valves (FRV) opening. SG-31, 33, 34 water levels recovered but the SG-32 water level increased and continued increasing after the 32 FRV was placed in manual. The 32 SG level reached the high level trip initiating a turbine trip that resulted in a reactor trip (RT) All required safety systems functioned properly including the Auxiliary Feedwater System which automatically started as expected. The root causes for the RT were 1) Ineffective problem solving, and 2) Poor vendor oversight. Contributing causes included 1) an inadequate procedure, 2) procedure adherence, 3) low FW flow in the 32 MBFP feed line and FRV controller short reset time, 4) Ineffective corrective actions. Significant corrective actions included: adjustment of the 31 MBFP governor, trained engineering personnel on Kepner-Tregoe problem solving technique, coached Maintenance personnel on requirements for contractor oversight and included the event in maintenance training, revised procedure 0-TUR-402-MFW to require stroke measurement of governor valves and linkage clearance check, new SG Water Level Controller settings under evaluation for implementation, Maintenance, Operations, Engineering and Outage Management were briefed on the root cause and lessons learned, and Maintenance and Engineering were briefed on expectations for effective problem solving. The event had no effect on public health and safety.
2862009005 | Indian Point 3 | 06/09/2009 | 08/07/2009 | ML09233010 | <strong>Technical Specification Prohibited Condition due to Exceeding the Allowed Completion Time for an Inoperable 480 Volt Undervoltage/Degraded Grid Relay Caused by Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2009, the inoperability during past operation of a 480 volt time delay relay was identified during an NRC Problem Identification and Resolution (PI&R) inspection. The inspection identified that a relay (62-1/3A) for 480 volt bus 3A had been documented in November 2007 for failing its As-Found acceptance tolerance including its Technical Specification (TS), required value during performance of a surveillance test. The previous months test also showed it failed these test criteria. The relay in each test was calibrated to within tolerance within the TS allowed outage time. In accordance with reporting guidelines the failure is assumed to occur at the time of discovery unless there is firm evidence, based on review of relevant information, to indicate the discrepancy existed previously. A corrective action (CA) was initiated for the November 2007 event and evaluated by engineering for past operability. The engineer incorrectly concluded the relay had been performing satisfactorily and failed to recognize the significant drift as a degraded component. The significant drift and repeat failures would indicate the relay was inoperable during past operation and exceeded the TS allowed outage time. The relay was replaced in November 2007. The apparent cause was personnel error due to inadequate knowledge of the drift monitoring program and component drift performance. CAs included reinforcement of management expectation for initiating CRs for as-found failures; development of expectations and guidance for evaluation and disposition of as-found surveillance failures, and re-evaluation of the functional failure determination for failed components. The event had no effect on public health and safety.
2862009006 | Indian Point 3 | 08/10/2009 | 06/21/2012 | ML12185001 | <strong>Automatic Reactor Trip due to a Turbine-Generator Trip Caused by Actuation of the Generator Protection System Lockout Relay During a Severe Storm with Heavy Lightning</strong><br /><i>Abstract:&nbsp;</i>On August 10, 2009, during a severe thunderstorm, the Control Room received indication of a Turbine Trip and Reactor Trip initiated by the Generator Primary Lockout Relay (86P). All control rods fully inserted and all required safety systems functioned properly. 6.9 kV Bus 2 failed to auto transfer to 6.9 kV bus 5 resulting in the trip of the 34 Reactor Coolant Pump and de-energization of 480 volt safeguards Bus 2A. Emergency Diesel Generator (EDG) 31 automatically started and re-energized 480 volt bus 2A. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. EDG-32 and 33 remained in standby as offsite power remained available. The Auxiliary Feedwater (AFW) System automatically started as expected due to Steam Generator low level from shrink effect. 6.9kV Bus 2 was energized from 6.9 kV bus 5 via closure of 6.9 kV bus 2-5 tie Breaker. The direct cause was actuation of the Generator Primary Lockout Relay (86P) due to misoperation of relay 85L1/345 due to extraneous voltage induced on ground during a lightning strike. The root cause was the 345 kV Primary Pilot Wire System is susceptible to the maximum ground potential rise (GPR) based on the original design. The susceptibility to GPR is due to 1) the calculated worst case GPR is higher than the insulating rating of the pilot wires, 2) The pilot wire system was not provided with equipment to protect against GPR. Corrective actions included inspection of 345 kV output feeder W96, testing of pilot wire cables, calibration and testing of applicable protection system relays. Enhancements will be implemented to the Station Grounding Plan, and the 138 kV and 345 kV pilot wire systems replaced. The event had no effect on public health and safety.
2862009007 | Indian Point 3 | 08/27/2009 | 10/21/2009 | ML09302011 | <strong>Automatic Reactor Trip Due to a Turbine Trip As a Result of Turbine Autostop Oil Actuation Caused by a Failed Autostop Oil Fitting</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2009, a Turbine Trip and Reactor Trip were initiated by main turbine control oil Autostop turbine trip. All control rods fully inserted and-all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. There was no radiation release. No Emergency Diesel Generator actuated as offsite power remained available. The Auxiliary Feedwater (AFW) System automatically started as expected due to Steam Generator low level from shrink effect. The cause of the trip was a loss of Turbine Autostop oil pressure below the trip setpoint due to a failed pipe adaptor fitting on the line connecting the Turbine Autostop oil to the Turbine solenoid trip device. The pipe adaptor fitting failed due to high cyclic fatigue caused by the improper installation of the Autostop,oil line fitting in the Turbine pedestal bulkhead wall. The cause of the event was the as-found configuration did not meet the Original Equipment Manufacturer (OEM) design expectation. This condition resulted in a configuration where the threaded fitting bottoms out in the threaded hole which induced additional stress on the fitting threads. The additional stress combined with normal stress caused a premature failure. Corrective actions included replacement of the failed fitting, inspection of Autostop oil lines, and monitoring vibrations on turbine bearing No. 1. An engineering change will be developed to redesign the turbine pedestal piping wall penetration for the autostop oil turbine protection solenoid valve. The event had no effect on public health and safety.
2862009008 | Indian Point 3 | 10/06/2009 | 12/02/2009 | ML09344013 | <strong>Technical Specification Prohibited Condition due to Exceeding the Allowed Completion Time for an Inoperable Over Power Delta Temperature (OPDT) Bistable</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2009, during performance of surveillance 3-PT-Q87D (Channel Functional Test of Reactor Coolant Temperature Channel 441) bistable 3TC-441C/D As-Found test readings were identified as out of specification for the Over Power Delta Temperature (OPDT) reactor trip function. The bistable was adjusted in accordance with the procedure and all readings were left in specification. An assessment of the condition determined that bistable 3TC-441C/D had been found out of specification on the previous quarterly surveillance on June 26, 2009. Technical Specification 3.3.1 (Reactor Protection Instrumentation), Table 3.3.1-1, Function 6 has an Allowable Value per Note 2 of 1.8% of delta Temperature span, which for bistable TC-441C/D correlates to a 0.144 Volts DC (Vdc) deviation from the nominal value. The OPDT Trip test criteria is 6.60 (6.56 to 6.64) Vdc. The As-Found OPDT value was 6.86 Vdc which exceeded the TS allowed value. On October 6, 2009, engineering concluded the second failure can not be assumed to have occurred at the time of discovery and represented an inoperable condition during past operation. The apparent cause was a discrepancy between the maintenance and test equipment (M&TE) output and reference value seen by the bistable. The discrepancy can be attributed to a deficiency with the test points used to input the reference value. The failure mechanism was concluded to have been a faulty reference value that was sensed by the bistable. The OPDT bistable (3TC-441C/D) was replaced. Surveillance procedures 3-PT-Q87 A through D where revised to require recording voltages that are inputted into the instrument loop. Troubleshooting will be performed on the bistable circuit for possible test point deficiencies. The event had no effect on public health and safety.
2862009009 | Indian Point 3 | 10/14/2009 | 11/03/2010 | ML10313004 | <strong>Loss of Single Train Neutron Flux Detector N-38 Required for Plant Shutdown Remote from the Control Room due to a Power Supply Failure</strong><br /><i>Abstract:&nbsp;</i>On September 24, 2009, during performance of IC-SI-18 (Full Power Alignment for the Gamma-Metrics Excore Nuclear Instrumentation System) channel N-38 could not be aligned and the power range was declared inoperable and Technical Specification (TS) 3.3.3 (Post Accident Monitors) entered. Subsequent engineering review of signal data determined the signal for N-38 started to degrade on September 15, 2009. Because the power supply was common over the full operating range including the source range, TS 3.3.4 (Remote Shutdown) was applicable. The neutron flux detector N-38 (source range) is a function specified in TS Basis Table 3.3.4-1 Function 1, Reactivity Control (and credited in Technical Requirements Manual (TRM) 3.3.D, Appendix R Alternate Safe Shutdown Monitoring). The inoperable N-38 failed to meet the specified safety function of TS 3.3.4. The apparent cause was a lack of a recurring preventive maintenance (PM) action to replace the power supplies because N-38 was not included in the Indian Point Energy Center (IPEC) Power Supply PM Program or the IPEC Capacitor Replacement Program. N-38 was classified low critical using guidance of Entergy procedure EN-DC-153, "Preventive Maintenance Component Classification." N-38 should have screened out as high critical. Corrective actions included replacement of the failed power supply with the operable power supply from redundant detector N-39. New power supplies were provided for N-39 and N-38, N-38 was reclassified as high critical, and a new PM was initiated to periodically replace the power supplies of N-38 and N-39. Procedure 3-PT-M100 (Monthly Post Accident Monitor Channel Checks) will be enhanced. The event had no effect on public health and safety.
2872009001 | Oconee 3 | 12/12/2008 | 02/10/2009 | ML09048008 | <strong>Two PALS CIVs Inoperable due to Use of Unqualified Seat Material</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2008 two containment isolation valves in a Post Accident Liquid Sampling line in Unit 3 were declared inoperable. Technical Specification Limiting Condition for Operation (LCO) 3.6.3 Conditions A and B were entered immediately and power was removed from two normally-closed solenoid-operated valves in the same line to meet the required actions of the LCO. However, the unit has been operated since the valves were installed in 1996 until discovery of the inoperable condition. Consequently, the appropriate Technical Specification required actions were not met within the allowed outage time permitted, and the unit was operated in a condition prohibited by Technical Specifications. The inoperable condition was caused by the use of soft seat materials which are not qualified for the elevated pressure and temperatures they could be exposed to in post-accident sampling service. The planned corrective action is to replace the soft-seated valves with a hard-seated design. This event is considered to have no significance with respect to the health and safety of the public.
2872009002 | Oconee 3 | 05/21/2009 | 07/20/2009 | ML09203039 | <strong>Unit 3 Trip Due to Generator Phase Differential Lockout</strong><br /><i>Abstract:&nbsp;</i>At 2014 on May 21, 2009, Oconee Nuclear Station Unit 3 experienced a reactor trip as a result of a generator lockout while escalating power following a refueling outage. The X phase differential relay (device 87U) actuated because a relay tap setting was configured incorrectly due to personnel error. This generator lockout resulted in a Reactor Protection System (RPS) actuation due to an anticipatory trip. The RPS received a Loss of Main Turbine Anticipatory Trip Signal and tripped the Control Rod Drive (CRD) breakers. The unit responded as expected. The Emergency Operating Procedure (EOP) was entered, subsequent actions completed, and a transfer to the unit shutdown procedure was made without complication. There were no significant equipment failures. Appropriate post-trip reviews were performed and recovery actions completed per station procedures. The Unit 3 87U differential relays' tap block settings were corrected on all three phases. Unit 3 reached criticality on May 22, 2009, and power escalation resumed. This event is considered to have no significance with respect to the health and safety of the public.
2892009001 | Three Mile Island 1 | 10/23/2009 | 10/07/2010 | ML10286013 | <strong>Multiple Main Steam Safety Valve Test Failures</strong><br /><i>Abstract:&nbsp;</i>During testing prior to refueling outage 1R18 (October 2009), six TMI-1 Main Steam Safety Valves (MS-V-19A, 17C, 18C, 19C, 21B and 19D) failed "as-found" setpoint testing. These valves are Dresser 3700 series steam safety valves. Valve lift pressures were more than 3% above setpoint during performance of surveillance test 1303-11.3. The valves were declared inoperable, and reactor power was reduced to comply with Technical Specification 3.4.1 until operability was restored. Many industry event reports, broader Exelon experience, TMI experience, and EPRI studies associated with this problem with Dresser 3700 series steam safety valves were reviewed to develop the cause and corrective actions. The primary root cause is a design deficiency, in that the design does not prevent the formation of an oxide bond between the valve disc and seat, which results in unacceptable valve performance. Material changes and process control improvements will be established, which have been shown to be the most effective means for preventing unacceptable Main Steam Safety Valve (MSSV) lift pressures. This problem applies to Dresser series 3700 relief valves. At TMI-1, these valves are only used in Main Steam Safety Valve applications. These valves are required to limit system pressures to within design limits. The condition of the affected MSSVs during cycle 17 would not have prevented the performance of MSSV safety functions credited in the safety analysis. The submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73 (a)(2)(i)(B), "a condition prohibited by Technical Specifications."
2932009002 | Pilgrim | 12/22/2009 | 02/19/2010 | ML10056002 | <strong>Failure to Meet Technical Specification Requirements for Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2009, at 0845 hours, with the reactor at 100% core thermal power and steady state conditions, Pilgrim Nuclear Power Station (PNPS) declared Secondary Containment inoperable due to the loss of a water seal on two 14 inch drain lines in the Torus Compartment designed to mitigate the consequences of a flood in the Reactor Auxiliary Bay. There are two troughs that are designed to provide a floodable volume (the torus room) in the event of a significant water leak in the auxiliary bay, while maintaining secondary containment integrity by ensuring a given water level is maintained in the troughs. The initial assessment of the condition indicated that the cross-sectional area of pipes, as found, have the potential to exceed the analytical value of allowable Secondary Containment leakage pathway size documented in the design calculations. The Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.7.C.2.a, was immediately entered at 0845 until the condition was corrected. Immediate corrective actions taken were to refill the trough to the correct level, initiate repairs to the level switch, which was found to be defective, and to enhance the weekly tour requirement of the Torus Compartment performed by plant operations. The TS LCO was subsequently exited at 0945 hours, one hour into the allowed 4 hour time frame, at which time Secondary Containment was declared operable. The event posed no threat to public health and safety.
2962009001 | Browns Ferry 3 | 08/24/2009 | 10/23/2009 | ML09301012 | <strong>Reactor Scram Due to Loss of Condensate Booster Pumps</strong><br /><i>Abstract:&nbsp;</i>At 1850 Central Standard Time (CST), on August 24, 2009, Unit 3 operators inserted a manual scram due to lowering reactor vessel water level. Prior to the manual scram, Condensate Booster Pump 3A tripped on low suction pressure followed by a trip of Condensate Booster Pump 3B. The Reactor Feedwater Pump Turbine (RFPT) suction header experienced low suction pressure, but feedwater pump 3A did not trip as expected. Feedwater pump 3B tripped as expected. The condensate flow path through the demineralizers is the only path with sufficient capacity to provide an adequate source of feedwater to the reactor vessel at 100 percent power. Loss of the flowpath through the condensate demineralizers caused lowering reactor water level which resulted in a control room operator inserting a manual reactor scram. Reactor vessel water level decreased to -47 inches and was recovered by High Pressure Coolant Injection (HPCI) system and Reactor Core Isolation Cooling (RCIC) system initiation. The communication adapter for Condensate Demineralizer Programmable Logic Controller Remote Chassis 10 (which is associated with condensate demineralizer;vessel 3H) was found with status lights indicating a communications failure had occurred, This failure caused an apparent loss of communication with the remote chassis associated with the other condensate demineralizer vessels. The root cause of this event was determined to be less than adequate functional testing of the condensate demineralizer system valve lock-up devices. TVA is developing a more robust testing methodology and frequency (preventative maintenance work orders) for ensuring the condensate demineralizers effluent lockup devices work properly.
2962009002 | Browns Ferry 3 | 11/12/2009 | 07/28/2010 | ML10211004 | <strong>Inoperable High Pressure Coolant Injection System due to Excessive Water in the Steam Line Drain</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2009, at approximately 1235 hours Central Standard Time (CST), while securing the High Pressure Coolant Injection (HPCI) turbine following the performance of Surveillance Procedure, Unit 3 HPCI Main and Booster Pump Set Developed Head and Flow Rate Test at Rated Reactor Pressure, Browns Ferry Nuclear Plant (BFN) Operations personnel received an alarm indicating high water level in the HPCI turbine exhaust steam drain pot. In accordance with the applicable Alarm Response Procedure, Operations personnel opened the HPCI condensate level control valve and subsequently dispatched personnel to the HPCI pump to drain the condensate from the drain pot through the drain pot level switch instrument test drain. Operations personnel removed in excess of 80 gallons of condensate from the HPCI turbine exhaust drain pot to clear the alarm. At 1711 hours CST, because Operations personnel could not verify the HPCI system exhaust line was fully drained the system was declared inoperable. The immediate cause of HPCI inoperability was high water level in the HPCI turbine exhaust drain pot. BFN has determined that the cause for the HPCI system inoperability was siphoning of water from the suppression pool. Immediate corrective actions included isolating the HPCI turbine exhaust drain line from the suppression pool. BFN is planning to permanently remove the HPCI turbine exhaust drain line from service. On November 14, 2009, prior to returning HPCI to operable status, the Reactor Core Isolation Cooling system was declared inoperable. This condition existed for approximately 2 hours due to loss of power to the flow controller.
2962009003 | Browns Ferry 3 | 03/22/2006 | 07/29/2011 | ML11214A10 | <strong>Reactor Core Isolation Cooling System Inoperable Longer Than Allowed by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2007, and again on August 26, 2009, during post-scram reviews, Browns Ferry Nuclear Plant personnel identified an unexpected level of instability in the Reactor Core Isolation Cooling (RCIC) system flow and turbine response following reactor scrams that occurred on February 9, 2007, and on August 24, 2009. Following each event, site engineering personnel reviewed the RCIC response and concluded the RCIC system was capable of performing its design function and Operations determined that RCIC was operable. On February 12, 2007, and again on August 26, 2009, Unit 3 entered Mode 2, commencing startup operations. Following the second event on August 24, 2009, Unit 3 was returned to service and remained at power until September 12, 2009, when Unit 3 was removed from service for scheduled maintenance activities. During the September 2009 outage, the RCIC Electric Governor-Remote (EG-R) was replaced and successfully tested. On March 25, 2010, in response to questions from the Nuclear Regulatory Commission (NRC), the Tennessee Valley Authority notified the NRC via a conference telephone call that Unit 3 RCIC was inoperable since March 22, 2006, after the EG-R had been installed and when Unit 3 exceeded 150 psig while in Mode 2. This reflected RCIC inoperability longer than allowed by Technical Specification 3.5.3 and mode changes not allowed by LCO 3.0.4. A failure analysis, conducted by Engine Systems Incorporated, determined the oscillations were caused by a missing buffer piston and springs within the EG-R.
2982009001 | Cooper Station | 11/01/2009 | 12/29/2009 | ML10005007 | <strong>Disarmed Control Rod Technical Specification Requirements Not Met</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2009 at 0746 Central Standard Time, Operations personnel determined the requirements of Technical Specifications (TS) Limiting Condition for Operation 3.10.4, Single Control Rod Withdrawal-Cold Shutdown, were not met when it was discovered the control rods in the five by five (5x5) array around control rod 50-19 had been rearmed and the clearance order released. Cooper Nuclear Station was in day 37 of refueling outage RE25, Mode 4, Cold Shutdown operation. Control rod 50-19 was being returned to service after replacement of its control rod drive mechanism (CRDM) O-ring seal with the control rod still withdrawn and uncoupled from its CRDM at the time of discovery. The cause of the error is attributed to inadequate programmatic controls for maintaining configuration control of the 5x5 array. Immediate actions were taken to restore compliance with TS until control rod 50-19 was restored to operability. Actions to preclude recurrence include revising appropriate procedures and communicating management expectations for clearance order activities. This event is considered to have negligible safety significance.
2982009002 | Cooper Station | 11/06/2009 | 12/30/2009 | ML10005006 | <strong>Manual Scram on Low Water Level Caused by Turbine Trip from Hydraulic Fluid Leak</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2009, at 19:30 Central Standard Time, Cooper Nuclear Station (CNS) control room operators inserted a manual reactor scram when vessel water level lowered quickly after a turbine trip. The turbine had been tripped after a hydraulic fluid leak developed in the digital electro-hydraulic (DEH) turbine control system that could not be isolated and repaired with the turbine on-line. After the scram, all control rods inserted and automatic systems responded as expected. A Group 2 isolation occurred due to reactor low water level conditions. Vessel water level was subsequently recovered and the Group 2 isolation was reset. The leak was caused by higher than normal vibration of the DEH supply line for governor valve #3 (GV-3) at low power. CNS repaired the leak by replacing the swaged joint connection that had fractured with a modified fitting. Additionally, a missing stop bolt for the actuator bracket on GV-3, that would have restrained the DEH supply line, was replaced. The root cause was deficient workmanship. CNS will add a step in the applicable preventive maintenance plans for the governor valves to ensure that the support bolting for the valve actuator bracket is installed. This event was not risk significant.
2982009003 | Cooper Station | 11/07/2009 | 01/04/2010 | ML10007009 | <strong>Isolation of Residual Heat Removal Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>At approximately 21:08, Central Standard Time, on November 7, 2009, isolation signals from pressure switches in the Recirculation System caused Shutdown Cooling suction isolation valves to close, which initiated a trip of the operating Residual Heat Removal (RHR) Pump D. Cooper Nuclear Station was in Mode 4, Cold Shutdown, with reactor temperature at 167 degrees Fahrenheit. The closure of RHR suction isolation valves was a result of deficient operational procedures. The procedures do not contain statements to ensure mechanical vacuum pumps are secured, with steam lines open to the condenser and reactor pressure near or below 0 psig with RHR suction isolation valves open. The operating crew did not demonstrate sufficient control of reactor pressure while Shutdown Cooling was in operation. Reactor pressure decreased to a negative value resulting in flashing of water to steam while in Shutdown Cooling. This event is not risk significant.
2982009004 | Cooper Station | 11/11/2009 | 01/08/2010 | ML10013021 | <strong>Manual Reactor Scram for Digital Electro-Hydraulic Fluid Leak</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2009, at 17:43 Central Standard Time, Cooper Nuclear Station (CNS) control room operators inserted a manual reactor scram after a non-isolable digital electro-hydraulic (DEH) fluid leak developed. This was the same governor valve (GV) and fitting location that had leaked November 6, 2009, and required a forced plant shutdown. After the scram, all control rods inserted and automatic systems responded as expected. Inspection of the governor valve fitting found that the face O-ring installed five days earlier was not the correct size for the application and did not seal appropriately. This O-ring was acquired from a turbine generator tool box and was not added to the work order to document its use. CNS maintenance replaced the O-rings on all electro-hydraulic fittings for GVs with new ones from warehouse inventory. The root causes were a failure to follow the material control and warehouse issuing processes and ineffective management of the initial repair to the DEH fluid leak five days prior. CNS will use management processes to reinforce expectations for procedure compliance and will implement case study training on this event. CNS will also inventory the turbine generator tool box and remove any materials that are not in compliance with the procedure for in-process material control. This event was not risk significant.
2982009005 | Cooper Station | 12/21/2009 | 07/27/2010 | ML10215042 | <strong>High Pressure Coolant Injection Governor Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2009, Cooper Nuclear Station (CNS) Control Room Operators started the High Pressure Coolant Injection (HPCI) auxiliary oil pump to obtain an oil sample for the predictive maintenance oil analysis program. Following the start of the auxiliary oil pump, the HPCI governor valve did not respond as expected. The HPCI auxiliary oil pump was operated a second time and the governor valve did not operate at all. HPCI was declared inoperable at 13:37, Central Standard Time (CST), resulting in entry into Technical Specification Limiting Condition of Operation (LCO) 3.5.1 Condition C, and LCO 3.3.3.2 Condition A. Offsite analysis found corrosion on internals of the electro-hydraulic governor (EG-R). This bound the EG-R and prohibited positioning the HPCI governor valve. The corrosion originated from particulate introduced during filter change out activities, which induced corrosion in the EG-R internals during standby conditions. CNS replaced the EG-R, flushed the oil system, and revised procedures for HPCI filter change out activities. CNS will identify preventative maintenance and/or design changes to prohibit corrosion. This event was determined to be reportable as a loss of safety function. Actual nuclear safety significance is minimal as no events occurred which required HPCI to be initiated. HPCI was declared operable at 16:45 CST on December 24, 2009.
3022009001 | Crystal River 3 | 01/27/2009 | 03/20/2009 | ML09083072 | <strong>Manual Reactor Trip Due To Loss of A 4160V Unit Bus Loads Caused By Incorrectly Connected Test Leads</strong><br /><i>Abstract:&nbsp;</i>At 10:17, on January 27, 2009, Progress Energy Florida, Inc. (PEF), Crystal River Unit 3 (CR-3), was operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER when the Reactor Coolant System pressure was observed rising toward the automatic reactor trip setpoint and the reactor was manually tripped. Prior to this event, technicians were performing preventive maintenance on the 'A' 4160 volt Unit Bus indication located in the Main Control Board. Doble Relay Test Set leads were incorrectly connected in place of the Fluke MultiMeter leads during a voltage check. This resulted in a path to ground that blew the 'A' and 'B' Secondary Side potential transformer fuses, resulting in a loss of voltage indication on the 'A' 4160 volt Unit Bus and tripping loads. The Reactor Protection System responded as expected to the manual trip signal, control rods fully inserted and safety systems functioned' as required. No reduction in the public health and safety was created. The causes for the manual reactor trip were improper use of human performance tools and inadequate closure of corrective actions for a previous similar event. All relay work was immediately stopped and a Human Performance Review Board Meeting was held. This report is submitted pursuant to 10CFR50.73(a)(2)(iv)(A). A previous similar occurrence was documented in Nuclear Condition Report (NCR) 133661.
3022009002 | Crystal River 3 | 04/30/2009 | 06/22/2009 | ML09181011 | <strong>In Technical Specification 3.0.3 Greater Than One Hour due to Loss of Motor Control Center During Testing</strong><br /><i>Abstract:&nbsp;</i>At 10:40, on April 30, 2009, Progress Energy Florida, Inc., Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER when Engineered Safeguards (ES) Motor Control Center (MCC) 3B1 de-energized while connecting test equipment to a molded case circuit breaker. Prior to this event, a clearance was in effect to perform preventive maintenance on High Pressure Injection System valve MUV-26. This clearance placed CR-3 into Improved Technical Specification (ITS) 3.5.2 for one train of Emergency Core Cooling Systems inoperable. Loss of ES MCC-3B1 caused loss of the main lube oil pump for MUP-1C, resulting in ITS 3.0.3 entry. The clearance on MUV-26 was lifted after one hour and 24 minutes, allowing exit from ITS 3.0.3. The backup lube oil pump for MUP-1C remained in operation during the time ITS 3.0.3 was in effect. MUP-1C would have performed its safety function during a design basis event. This event did not represent a reduction in the public health and safety. The causes for this event were allowing work on energized equipment instead of taking the equipment out of service and deviating from work order instructions without having them revised. Load testing was immediately stopped. This report is submitted pursuant to 10CFR50.73(a)(2)(i)(B). No previous similar occurrences have been reported to the NRC.
3022009003 | Crystal River 3 | 08/24/2009 | 10/21/2009 | ML09296023 | <strong>Manual Reactor Trip Due To Group 7 Control Rods Insertion Caused By Inadequately Protected Test Jumper</strong><br /><i>Abstract:&nbsp;</i>At 11:00, on August 24, 2009, Progress Energy Florida, Inc. (PEF), Crystal River Unit 3 (CR-3) was operating in MODE 1 (POWER OPERATION) at 100 percent RATED THERMAL POWER when the Control Room staff received multiple alarms and observed the Group 7 control rods fully insert into the reactor core. The reactor was manually tripped prior to automatic actuation of the Reactor Protection System (RPS). Prior to this event, electricians were implementing Preventive Maintenance procedure PM-126, "Electrical Checks of CRD [Control Rod Drive] Power Train." When the Integrated Control System was placed in Automatic, the output driver within the Group 7 programmer caused an erroneous phase sequence to the control rod drive stators, culminating in inadequate magnetic force to restrain the rods from dropping during movement. The RPS responded as expected to the manual trip signal, control rods fully inserted and safety systems functioned as required. No reduction in the public health and safety was created. The programmer failure was caused by inadvertent test jumper contact while using an improperly fused test jumper. This caused an over-current failure of the output driver within the programmer. The programmer was replaced and PM-126 was placed on administrative hold. This report is submitted under 10CFR50.73(a)(2)(iv)(A). No previous similar occurrence has been reported to the NRC.
3022009004 | Crystal River 3 | 09/22/2009 | 12/17/2009 | ML09356007 | <strong>Main Steam Safety Valve Lift Setpoints Outside Required Tolerance Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2009, Progress Energy Florida, Inc., (PEF) Crystal River Unit 3 (CR-3) was in MODE 1 (POWER OPERATION) at approximately 100% RATED THERMAL POWER. While performing surveillance procedure SP-650, "ASME Code Safety Valves Test," on the 'A' Once Through Steam Generator, the lift setpoint for Main Steam Safety Valve (MSSV) MSV-34 was found above its maximum allowable tolerance. Subsequently, three of ten tested MSSVs were found to have lift setpoints above/below their maximum allowable tolerance. Improved Technical Specification (ITS) 3.7.1 states that the MSSVs shall be operable as specified in Table 3.7.1-1 in MODES 1, 2 and 3. To be operable, the MSSV lift setpoints must be within the maximum allowable tolerance of ± 3%. The existence of similar discrepancies in multiple relief valves is an indication that the discrepancies may have developed over a period of time. Therefore, PEF concludes that multiple MSSVs were inoperable during plant operation for a period longer than allowed by ITS and the condition is reportable under 10CFR50.73(a)(2)(i)(B). This condition does not represent a reduction in the public health and safety. The selected cause is possible failure to provide critical information to the vendor for valve rebuild. The three MSSVs were adjusted and retested satisfactorily. Similar occurrences were reported to the NRC in Licensee Event Reports 50-302/2001-002-00 and 50-302/2003-002-00.
3052009001 | Kewaunee | 01/23/2009 | 03/24/2009 | ML09090051 | <strong>Emergency Diesel Generators Inoperable Requiring Notice of Enforcement Discretion</strong><br /><i>Abstract:&nbsp;</i>On January 23, 2009 at 13:58 CST with the station at 100 percent power, Dominion Energy Kewaunee, Inc. was informed by the Nuclear Regulatory Commission that the station was not complying with Technical Specification 3.7.a.7. The Technical Specification requires the availability Of 35,000 gallons of fuel oil for either diesel generator from two underground storage tanks. A siphon line connecting the two tanks was nonfunctional and the station was relying on a temporary transfer pump to move fuel oil between the underground tanks. The function of the siphon line had been removed from the licensing basis in 1993. This required the station to declare both emergency diesel generators inoperable and enter Technical Specification 3.0.c, "Standard Shutdown Sequence." The station made a request for a Notice of Enforcement Discretion for Technical Specification 3.7.a.7 while an exigent Technical Specification License Amendment was being processed. At 15:42 CST on January 23, 2009, the NRC granted the station a 14-day Notice of Enforcement Discretion. Although preparations were made to shutdown, no reactivity manipulations were performed. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications.
3052009002 | Kewaunee | 01/28/2009 | 03/30/2009 | ML09099042 | <strong>Steam Exclusion Door Blocked Open During Maintenance Activities</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2009 with the station at 100 percent power, mechanical maintenance notified the control room that two doors would be opened per procedure to perform dry testing of carbon dioxide hose reel Stations. Upon checking at 08:34 CST, Operations found Door 3 open with a person stationed at the door and Door 5 open with the installed door chock down and a person stationed at the door. Per the barrier control procedure, doors shall only be held open by an individual without the use of mechanical aids (e.g. chocks or cords). Door 5 was in this condition approximately 15 minutes. A postulated high energy line break in the turbine building would communicate with the carbon dioxide tank room where Door 5 is located to provide a steam exclusion boundary with both trains of 480 volt engineered safeguards feature busses. This would result in both trains Of engineered safeguards feature equipment being inoperable. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B), as a condition that resulted in the nuclear power plant being in an unanalyzed condition. Additionally, since both trains of emergency safeguards equipment were inoperable, this condition is being reported under 10 CFR 50.73(a)(2)(v), for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident.
3052009003 | Kewaunee | 01/31/2009 | 04/01/2009 | ML09097027 | <strong>Containment Spray Pump A Inoperable At Degraded Voltage Protection Setpoint</strong><br /><i>Abstract:&nbsp;</i>On January 31, 2009, a Dominion Energy Kewaunee (DEK) engineering evaluation determined that at the allowed setpoint of the degraded voltage protection relay, the 1A containment spray pump could potentially trip. A postulated starting of the motor during the lowest voltage conditions possible at the relay setting could result in starting currents that are sufficiently high and last long enough to trip the motor's protective device. Consequently, automatic containment spray pump start to mitigate a design basis accident in accordance with the plant's safety analyses is not assured under all postulated conditions. Based on the potential to trip, the pump was declared inoperable. The containment spray pump breaker settings were adjusted and pump operability was restored. Kewaunee Power Station (KPS) Technical Specifications (TS) 3.3, "Engineered Safety Features and Auxiliary Systems", requires that two containment spray trains be OPERABLE. The IS allows one containment spray train to be out of service for 72 hours provided the opposite containment spray train remains OPERABLE. Since the settings were nonconservative since initial installation of the second. level undervoltage relays, the' 1A containment spray pump was inoperable for longer than the time allowed by TS. Therefore, this condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), as any operation or condition which was prohibited by the plant's TS.
3052009004 | Kewaunee | 03/23/2009 | 05/21/2009 | ML09148026 | <strong>Failed Backdraft Damper Renders Containment Fan Coil Unit Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2009 21:00 Central Daylight Time with the station at 100 percent power, inoperability of the containment fan coil unit 'A' was identified. While preparing to remove the fan motor during maintenance, workers saw that the fan was spinning backward and an excessive amount of air was blowing through gaps in the ventilation ductwork. Investigation found the containment fan coil unit backdraft damper not fully closed. The fan had been in an off/auto condition since November 14, 2008. This condition allowed backflow from the operating containment fan coil unit 'B'. With the fan spinning backward, it is postulated that the fan would trip on overcurrent when started. Following review of the operability of required containment cooling systems since November 14, it was determined that Technical Specifications had been violated numerous times due to inoperability of various combinations of containment cooling system components and the postulated inoperable containment fan coil unit 'A'. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), as a condition which was prohibited by the plant's Technical Specifications, 10 CFR 50.73(a)(2)(ii)(B), as a condition that resulted in the nuclear power plant being in an unanalyzed condition, and since both trains of containment cooling systems were inoperable, this condition is being reported under 10 CFR 50.73(a)(2)(v), for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (C) Control the release of radioactive material; or (D) Mitigate the consequences of an accident.
3052009005 | Kewaunee | 03/26/2009 | 05/21/2009 | ML09148026 | <strong>Nonfunctional Steam Exclusion Door Results in Postulated Inoperability of Safety Systems</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2009, during performance of a comprehensive design reconstitution of hazard barriers, Dominion Energy Kewaunee (DEK) identified that a steel-covered glass window contained in Steam Exclusion Door 140 was not capable of withstanding the pressures that would be generated by a postulated high energy line break (HELB). Consequently, Door 140 was nonfunctional as a hazard barrier. Kewaunee Power Station (KPS) Technical Requirements Manual (TRM) 3.0.9, "Steam Exclusion System", directs that all equipment supported by a nonfunctional steam exclusion barrier be declared inoperable immediately. Door 140 supports multiple trains of emergency core cooling systems (ECCS) and other equipment required by Technical Specifications (TS). With Door 140 nonfunctional, TRM 3.0.9 required all equipment supported by that door to be declared inoperable. A power reduction to 1663 MWTh was performed in accordance with TS 3.4.b.3. Since multiple out of service trains is technically an unanalyzed condition, this condition is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B), as a condition that resulted in the nuclear power plant being in an unanalyzed condition. Additionally, since both trains of emergency core cooling were declared inoperable, this condition would also meet the reporting criteria of 10 CFR 50.73 (a)(2)(v)(B), any event or condition that could have prevented the fulfillment of a safety function.
3052009006 | Kewaunee | 04/16/2009 | 02/03/2011 | ML11046027 | <strong>Protection Instruments Not Calibrated to Individual Technical Specification Set Point Limits</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2009, during review of an instrumentation calibration procedure, Dominion Energy Kewaunee (DEK) staff identified that the procedure for calibrating low steam line pressure safety injection lead/lag circuitry units was not adequate to ensure that Technical Specification (TS) setpoint requirements were met. Calibration methodology used a vendor supplied calibration graph of a composite output from the lead and lag circuit module to determine acceptance criteria. However, Kewaunee Power Station (KPS) TS specified individual setting limits for the lead and lag time constants. A review of this condition determined that, while the composite output met acceptance criteria per the calibration procedure, the individual lag time constants did not meet TS acceptance criteria. Consequently, all six channels of the Low Steam Pressure/Line Safety Injection signal were declared inoperable. TS required the plant to be placed in Hot Shutdown as soon as practicable for this condition, which was achieved at 2356 CDT. While the plant was shutdown, an extent of condition review identified that the lead/lag circuitry units on the Overtemperature AT instruments similarly did not meet TS acceptance criteria. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A), for a TS required shutdown; 10 CFR 50.73(a)(2)(i)(B), for a condition prohibited by the plant's TS; and 10 CFR 50.73(a)(2)(vii), for two independent inoperable channels required to shutdown the reactor or for accident mitigation.
3052009007 | Kewaunee | 04/21/2009 | 06/22/2009 | ML09180040 | <strong>Inadequate Station Procedures for Testing Containment Vacuum Breaker System Leads to a Violation of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 21, 2009 during review of Kewaunee Power Station (KPS) Technical Specifications (TS) as they relate to containment isolation, Dominion Energy Kewaunee (DEK) staff identified that the procedures for testing containment vacuum relief valves were not adequate to ensure that TS requirements were met, leading to a violation of TS requirements. The containment vacuum relief valves perform both a vacuum relief function and a containment isolation function. Both of these are safety related functions that must be performed per the design basis for the facility. When coupled with a postulated equipment failure on the same containment penetration, a lack of specific detail regarding the minimum degree of redundancy has led to the failure to apply TS 3.0, Limiting Conditions for Operation. On October 1, 2008 at 1111 hours, during performance of a KPS surveillance procedure, a vacuum relief valve did not reposition when the control room switch was activated. This led to deactivation of vacuum relief valve VB-10B, rendering the vacuum relief function on the "B" train inoperable for approximately five days. KPS operators should have commenced a reactor shutdown per TS 3.0.c based on the duration of VB-10B inoperability. This event is being reported pursuant to 10 CFR 50.73 (a)(2)(i)(B), any operation or condition which was prohibited by TS.
3052009008 | Kewaunee | 10/10/2009 | 12/04/2009 | ML09349099 | <strong>Inadequately Controlled Reactor Coolant System Dilution Results in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 10, 2009, while the reactor was in refueling shutdown mode, the boron concentration of the reactor coolant system was inadvertently reduced below the 2500 ppm limit required by Kewaunee Power Station (KPS) Technical Specifications (TS), resulting in a violation of TS requirements. At the start of the event, the reactor vessel head was removed, the reactor was defueled, and the refueling cavity was flooded. Operators had begun diluting reactor coolant system (RCS) water in the residual heat removal (RHR) flow path to reduce the boron concentration in the refueling cavity. This activity inadvertently reduced the reactor coolant boron concentration in the RHR system below the minimum value required by TS. With RCS boron below the minimum TS limit, operators began transferring fuel assemblies from the spent fuel pool into the reactor. A sample of RCS water obtained from the RHR system shortly after commencement of refueling activities showed a boron concentration of about 2300 ppm. Upon confirmation of the boron concentration, fuel handling was suspended and boron concentration of the RCS was restored to required limits. This event is being reported pursuant to 10 CFR 50.73 (a)(2)(i)(B), any operation or condition which was prohibited by TS.
3052009009 | Kewaunee | 10/15/2009 | 12/09/2009 | ML09351001 | <strong>Automatic Start of Emergency Diesel Generator due to Safeguards Bus Power Supply Transformer Trip</strong><br /><i>Abstract:&nbsp;</i>At 1204 on October 15, 2009, with the reactor in cold shutdown mode, power was lost to Safeguards Bus 5. Loss of power to the bus resulted in automatic actuation of emergency diesel generator (EDG) A to re-energize the bus. The power loss was caused by tripping and lockout of the Tertiary Auxiliary Transformer, which supplies the bus, due to an incorrectly set transformer relay input parameter. The single operating residual heat removal (RHR) pump was being powered by Safeguards Bus 5 when it lost power. Operators restored RHR flow by starting the opposite train RHR pump, which had been in standby. The unaffected safeguards bus was being powered from an alternate power supply at the time of this event. Therefore, based on the unavailability of offsite power via the normally aligned electrical supply transformers, operators conservatively declared Technical Specification (TS) 3.1.a.2.B not met for both trains of RHR. This event is being reported pursuant to 10 CFR 50.73 (a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the listed systems. It is also being conservatively reported pursuant to 10 CFR 50.73 (a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications.
3062009001 | Prairie Island 2 | 02/16/2009 | 04/20/2009 | ML09110021 | <strong>LER 2-09-01, Clearance Order Renders Opposite train Emergency Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2009 at 0129 CST, while train A emergency diesel generator (EDG) was out of service for planned maintenance, the train B EDG for Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was rendered inoperable. This had the effect of making both EDGs for PINGP Unit 2 inoperable concurrently. This event was due to an improperly planned electrical isolation that inadvertently disabled both of the train A fuel oil transfer pumps. One of these two pumps is necessary to meet the fuel oil requirements specified in the technical specifications (TS). This condition was discovered the following day at approximately 1100 CST. Operations personnel took actions immediately to restore the isolated fuel oil transfer pump and by 1145 CST, the pump and subsequently the train B EDG were returned to operable status. Thus, this condition existed for a period of approximately 34 hours which is reportable as a condition prohibited by TS. TS require that if both EDGs are inoperable, then that Unit must be in MODE 3 within 8 hours. PINGP licensing basis requires that three of the four fuel oil storage tanks (FOST) for Unit 2 be available in order to provide up to 14 days of fuel in the event of a design basis flood and loss of offsite power (LOOP) scenario. The 14 days is deemed sufficient to allow the PINGP fuel oil supply to be replenished from offsite sources. To meet this requirement, at least one of the fuel oil transfer pumps and FOSTs in the opposite train are relied upon in order to consider the EDG operable.
3112009002 | Salem 2 | 10/17/2009 | 12/15/2009 | ML09358009 | <strong>22 Component Cooling Heat Exchanger Inoperable for Greater Than Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2009 at 0538 hours, control room operators noted an abnormal increase in reactor coolant system (RCS) temperature following performance of section 5.3 of procedure S2.OP-ST.SSP-0002, "SEC MODE OPS TESTING 2A VITAL BUS." The control room supervisor (CRS) directed a walk down of the residual heat removal (RHR) and component cooling (CC) system which identified that the 22 CC Heat Exchanger (HX) service water outlet valve 22SW356 gearbox had rotated causing the valve to go partially closed. At 0603, the CRS entered the abnormal operating procedure for component cooling. Technical Specification 3.9.8.2 was entered at 0603 hours for less than 2 trains of RHR operable and water level less than 23 feet above the reactor flange. At 0658 hours, the 22SW356 valve was secured in position to prevent the valve from going closed any further. At 0753 hours, operators verified the ability of the 22 CC HX to provide adequate core cooling by adjusting the RHR HX outlet control valve. RCS temperature reduced from 125.6 °F to 124.5 °F. At 0818 hours, 3000 gpm of service water flow was established to the 21 CC HX and a RCS temperature decrease was observed. At 1004 hours, 9000 gpm of flow was established to the 21 CC HX. At 1017 hours, TS 3.9.8.2 was exited. The causes of this event were installation of the wrong material mounting bolt and incorrect torque values. Corrective actions consist of replacement of the valve and gearbox using proper mounting bolts, procedure changes, roll-outs to appropriate personnel, and generation of preventive maintenance tasks. This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), "any operation ... prohibited by the plant's Technical Specification."
3132009001 | Arkansas 1 | 02/05/2009 | 04/03/2009 | ML09093054 | <strong>Manual Reactor Trip From Power in Response to a Loss of Control Rod Drive Cooling Water Flow Due to a Gasket Failure Which Resulted in Air Intrusion Into the Intermediate Cooling Water System</strong><br /><i>Abstract:&nbsp;</i>On Thursday, February 5, 2009, at approximately 1524 CST, Arkansas Nuclear One, Unit 1 was manually tripped from 61 percent power due to increasing temperatures of the Control Rod Drive (CRD) Motors resulting from a loss of CRD cooling water flow. The CRD Motors share cooling water flow from the Non-Nuclear Intermediate Cooling Water (ICW) system with Service Air Compressors and other non-nuclear loads. A failed head gasket on the C-3A Service Air Compressor resulted in the introduction of large quantities of air into the ICW system which resulted in cavitation of P-33A ICW pump and both P-79A and P-79B CRD Motor cooling pumps. This loss of CRD cooling flow caused CRD temperatures to approach 180F which is the reactor trip criteria for OP-1203.003, CRD Malfunction Actions procedure. Post trip responses were normal with all plant systems functioning as expected and with no safety system actuations. The ICW supply and return lines to the Service Air Compressors were isolated restoring ICW and CRD Motor cooling flow. An alternate source of Service Air was provided, and the unit was returned to power on February 6, 2009, at 2219 CST. The root causes of this event were inadequate original design and inadequate maintenance instruction. Corrective actions include providing an alternate source of Service Air, evaluating the equipment for upgrade, and evaluating similar equipment for the same failure scenario.
3132009002 | Arkansas 1 | 02/07/2009 | 04/01/2009 | ML09092026 | <strong>Manual Reactor Trip From Power in Response to a Fire at the Main Generator Hydrogen Addition Station Caused by a Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On February 7, 2009, at approximately 1046 CST, the reactor was manually tripped from 90 percent power in response to a report of a fire at the main generator hydrogen addition station. Prior to the occurrence of the fire, Operations personnel were preparing to add hydrogen to the main generator. The Inside Auxiliary Operator (IAO) who was to perform the task conducted a pre job brief with the Shift Technical Advisor, who was also a qualified Shift Manager. The IAO then proceeded to the hydrogen addition station to perform the task. The procedure requires that the hydrogen station to generator inlet isolation valve, which is a normally open valve, be verified open. The IAO first attempted to open the valve with no success, then unsuccessfully attempted to close the valve. Assuming the valve was stuck on its closed seat; the operator obtained a pipe wrench and proceeded to rotate the valve handle in the open direction. Suddenly, the bonnet, hand wheel, and valve internals assembly ejected from the valve body, releasing hydrogen under pressure to the atmosphere. The operator immediately exited the area and the hydrogen quickly ignited. Operations personnel expeditiously initiated action to isolate the hydrogen leak. As a conservative action, the reactor was manually tripped at 1046 CST. The cause of this event was personnel error. The involved individual will receive remedial training and go through a requalification process.
3132009003 | Arkansas 1 | 09/22/2009 | 12/17/2009 | ML09351081 | <strong>Unanalyzed Condition That Significantly Degraded Plant Safety Existed Intermittently Due to an Unlatched Door Serving as a High Energy Line Break Barrier</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2009, at approximately 1329 CDT, with the plant operating at 100% power, it was discovered during the review of an Arkansas Nuclear One Unit 1 past operability evaluation that an unanalyzed condition may have existed for a short period of time in which a door that serves as a High Energy Line Break (HELB) barrier may have been unlatched. With the door unlatched, an engineering evaluation concluded that a critical crack in the Main Feedwater pipe traversing the south penetration room would force the door (DR-19) open, creating a harsh environment in the adjoining Emergency Feedwater (EFW) pump room. Because the EFW [BA] pump room is not evaluated for harsh conditions, it must be conservatively assumed that both pumps may fail to operate following this HELB event. Investigation revealed that the most probable cause of the latch failure was due to wear of the latch bolt hole.
3162009001 | Cook 2 | 07/26/2009 | 02/18/2010 | ML10054008 | <strong>Manual Reactor Trip due to RCP Seal Degradation Caused by Accumulation of Corrosion Products</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2009, at 1506 hours, Donald C. Cook Nuclear Plant (CNP) Unit 2 Control Room Operators performed a manual reactor trip in response to a malfunctioning reactor coolant pump (RCP) seal. All control rods fully inserted and the auxiliary feedwater system (AFW) started and performed as designed. The reactor trip was uncomplicated and all major plant components functioned as designed; as such, there were no safety system functional failures. The reactor trip was reported in accordance with 10 CFR 50.72 (b) (2) (iv) (B) and the AFW actuation was reported in accordance with 10 CFR 50.72(b) (3) (iv) (A). The reactor trip and AFW actuation are reportable as a Licensee Event Report in accordance with 10 CFR 50.73 (a) (2) (iv) (A). As Control Room Operators were responding to indications of a malfunctioning RCP seal, they were procedurally directed to perform a manual reactor trip and then remove the RCP from service. The immediate cause of the trip was manual actuation due to a malfunctioning RCP seal. The root cause was a failure by the station to recognize that a buildup of corrosion products had the potential to enter the seal, causing failure. The seal assemblies in RCP 21 and RCP 22 were replaced. A plan has been developed and will be implemented for flushing the RCP seal components.
3172009001 | Calvert Cliffs 1 | 03/06/2009 | 05/04/2009 | ML09124050 | <strong>Reactor Coolant Pump Starts not in Accordance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 6, 2009, Calvert Cliffs Nuclear Power Plant discovered that procedural requirements for starting a Reactor Coolant Pump (RCP) were not consistent with the pump start requirements contained in Technical Specifications 3.4.5, Note 2, 3.4.6, Note 2, and 3.4.7, Note 3. These notes provide Reactor Coolant System (RCS) criteria, such as pressure, level, and secondary water temperature acceptable for starting any RCP when the RCS temperature is less than 365 degrees F. Contrary to these pump start requirements, RCPs were started on April 6, 2006, December 20, 2006, and March 11, 2008 without meeting the RCS pressure requirement of Technical Specification 3.4.5, Note 2. This condition was prohibited by Technical Specifications. No adverse conditions resulted during these RCP starts. This event appears to be caused by a failure to recognize that when Improved Technical Specifications were adopted at Calvert Cliffs in 1998 a change was made that affected the applicability of the start criteria for this function. The corresponding operating procedure was not adequately updated to match the Improved Technical Specifications. The affected operating procedures are being revised to incorporate Technical Specification requirements for RCP starts. This condition does not apply to Unit 2 because the start conditions for RCPs are different than those on Unit 1 and have been met.
3212009001 | Hatch 1 | 03/09/2009 | 05/04/2009 | ML09124024 | <strong>Pump Suction Swap for HPCI and RCIC Non-Conservative With Respect To Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On March 9 at 1200 EDT, Unit 1 was in Mode 1 at 2798 CMWT, 99.8 percent power. Based on instrument elevation survey data taken on March 6, 2009, and subsequent evaluation on March 9, 2009, a determination was made that a level switch for the High Pressure Coolant Injection (HPCI) and a level switch for the Reactor Core Isolation Cooling (RCIC) suction swap from the Condensate Storage Tank (CST) to the suppression pool had an actual setpoint that was less conservative than that specified in the Technical Specifications. During further evaluation on March 17, 2009 it was determined that the current setpoint for the CST level suction swap to the suppression pool does not take into account the necessary reduced voltage assumption for certain DC motor operated valves. This has the effect of requiring a higher level switch setpoint to prevent vortexing at the suction from the CST. Finally, on March 30, 2009 it was determined that the level switch for the suppression pool high level suction swap for RCIC pump suction had an actual setpoint that was less conservative than that specified in the Technical Specifications. The above items are related to HPCI / RCIC pump suction swap setpoints. This event was caused by calculation, design and configuration control weaknesses related to HPCI / RCIC CST and Suppression Pool level switches and inadequate verification of elevation during installation. A design change has been implemented to correct the errors in the instrumentation system designs and resulting setpoint errors, and a work order has been implemented to adjust the height of the remaining instrument.
3212009002 | Hatch 1 | 05/04/2009 | 06/18/2009 | ML09173014 | <strong>MSIV Closed Outside of the Allowable Time due to Loss of Oil in Actuator</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2009 at 851 EDT, Unit 1 was in hot shutdown, Mode 3. Stroke time testing of the inboard Main Steam Line Isolation Valve (MSIV), 1B21-F022B, failed to meet both the procedural minimum limit, and the Technical Specification minimum limit of greater than or equal to three seconds. The valve closed in 1.53 seconds. A Work Order was generated to determine the cause of the failure. Upon investigation, it was found there was no oil in the actuator due to a leak at a fitting on the actuator. The oil provides a dampening effect for the valve closure and the absence of oil allowed the valve to close faster than desired. The oil leak originated from a 3/4 inch NPT port on the dashpot cylinder. The cause of the leak is attributed to degradation of the Teflon tape applied as a thread sealant. Corrective actions consist of removing, cleaning and reassembling fittings to the port using Loctite 5772 in place of the Teflon tape. In addition, the procedure for actuator dash pot reassembly has been revised to require use of the Loctite 5772 sealant. In addition to improve reliability of all threaded fittings for the MSIV actuators the procedure has been revised to require cleaning and the application of new Loctite 5772 sealant any time threaded connections are removed from the actuator.
3212009003 | Hatch 1 | 05/08/2009 | 06/19/2009 | ML09170063 | <strong>Work Activities On The Main Turbine Cause An Unexpected Turbine Reset Resulting In A Group I Isolation</strong><br /><i>Abstract:&nbsp;</i>On May 8, at 1515 EDT, Unit I was in Mode 3, hot shutdown, when a Group 1 isolation signal was received. All eight Main Steam Isolation Valves (MSIV) and appropriate small bore valves closed as designed. The signals received were a valid main condenser low vacuum signal coincident with a main turbine reset signal which opened a turbine stop valve. The reset of the turbine was an unanticipated result of ongoing mark VI turbine control system processor repair work. The reactor was in hot shutdown for nuclear instrument repair. The condition causing the turbine reset was cleared and the turbine was tripped with all valves closed. The Group 1 trip was reset and MSIV's were opened. Inadequate information on the Mark VI logic concerning the fact that a turbine trip reset occurs when the S1 core processor is rebooted caused this event. This reboot resets the turbine trip, opens the turbine stop valves, and causes Group 1 valve isolation when a low condenser vacuum condition exists. In addition, procedure 57GMMIC- 005-1 was not active when this evolution took place. This procedure prevents a turbine reset by providing a hard turbine trip logic seal-in. A new procedure will be developed that addresses actions to be taken and potential consequences when a reboot of the Si processor is to be performed.
3212009004 | Hatch 1 | 05/10/2009 | 06/19/2009 | ML09173018 | <strong>IRM Signal Spike Caused by Electrical Noise Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On May 10 at 1041 EDT, Unit 1 was in run at 224 CMWT, 8 percent power. At this time a reactor startup from a planned maintenance outage was in progress. Upon placing the reactor mode switch to the run mode as part of normal startup activities, a full reactor scram was initiated. Intermediate Range Neutron Monitoring (IRM) upscale trips were received in each of the two Reactor Protection System (RPS) scram channels. Investigation revealed that the ‘1A’ IRM (Bus A) and the ‘1 H’ IRM (Bus B) had spiked upscale when the mode switch was taken to run. The cause of the scram was an electrical noise spike transmitted into the IRM’s. The noise signal was sufficient to cause IRM “A” and “H” to trip on "high-high" neutron flux level. Replacing degraded cables, and connections, as well as improving grounding of the neutron monitoring system improved noise levels in the system. In addition ferrite beads were installed on each cable entering and/or exiting the preamplifier NEMA enclosures on each of the eight IRM channels.
3212009005 | Hatch 1 | 05/15/2009 | 07/13/2009 | ML09194053 | <strong>Inadequate Procedure results in a Group 1 Isolation and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On May 15, 2009 at 05:19 EDT, Unit I was in the cold shutdown mode with reactor power at 0 CMWT. At that time, a Group 1 isolation signal on actual low condenser vacuum was generated when Operations personnel moved the reactor mode switch to the run position per subsection 7.1 of special purpose procedure 42SP-05-12- 09-PI-1-1, "Test of Nuclear Instrumentation Response to Diverse Logic System Actuations." Because the Main Steam Isolation Valves (MSIVs) were open at the time the Group 1 isolation signal was generated, they closed per design resulting in a reactor scram trip signal on MSIVs less than 90 percent open with the mode switch in the run position. Since the unit was in the cold shutdown condition at the time of the event, all controls rods were already inserted fully and therefore no rod motion occurred. However, the Main Steam Line Drain and Reactor Water Sample Line isolation valves also closed per design on the Group 1 isolation signal. Operations personnel returned the reactor mode switch to the shutdown position and reset the isolation and scram signals. Operations personnel left the MSIVs in the closed position. This event was caused by a personnel error resulting in the development of an inadequate procedure. The procedure was reviewed, revised, and successfully performed. The initial procedure writer was coached.
3212009006 | Hatch 1, Hatch 2 | 12/15/2009 | 01/18/2011 | ML11019060 | <strong>Main Control Room Air Conditioner Inoperable due to Inoperable Solenoid Valve</strong><br /><i>Abstract:&nbsp;</i>On 12/15/2009, the cooling water for some of the MCR air conditioning was identified as no longer being "single failure proof". This placed the plant in a condition prohibited by the Tech Specs (TS). Further investigation revealed that on January 6, 2006 valve 1P41-F123A was identified as not having any stem travel. This valve is in the Plant Service Water (PSW) cooling line for an air conditioner located outside the MCR boundary and outside of the area serviced by the MCR air conditioner. This valve is one of two valves that are designed to isolate in the event of a pipe rupture to ensure adequate flow is maintained for MCR air conditioners cooled by Division I PSW. Following isolation of the cooling line, the second isolation valve was found to be inoperable on 12/17/2009. Since the valves would not automatically isolate, this portion of the line would no longer be considered single failure proof, which should have resulted in entry into the condition required by the TS. This event was caused most recently by less than adequate implementation of a design change in 1982 that impacted the ability of licensed operators to recognize the significance of the failure of the isolation valves. Corrective actions included isolating the non-safety cooling water line, confirming existing design change procedures require impact reviews of licensing documents; establishment of administrative controls to maintain isolation boundaries, and reviewing lessons learned in operability training for licensed personnel.
3232009001 | Diablo Canyon 2 | 03/17/2009 | 08/17/2009 | ML09238014 | <strong>Technical Specification 3.0.3 One Hour Exceeded due to Failure of Group Step Counters</strong><br /><i>Abstract:&nbsp;</i>On March 17, 2009, at 09:25 PDT, with Unit 2 in Mode 1 (Power Operation) at approximately 100 percent reactor power, the 1-hour time allowed by Technical Specification (TS) 3.0.3, to correct one of two reactor shutdown rod group step counters was exceeded. On February 18, 2009, plant operators identified a Bank "B" group step counter digital display that began to blink indicating degraded battery voltage. On March 8, 2009, the group step counter failed. On March 17, 2009, at 08:25 PDT, plant operators entered TS 3.0.3, following identification of a second group step counter failure for shutdown Bank "B," a condition not allowed by TS 3.1.7. On March 17, 2009, at 10:18 PDT, one group step counter was replaced and TS 3.0.3 was exited, and TS 3.1.7, Action D was reentered. Plant operators exited TS 3.1.7 at 11:11 PDT following the installation of fresh batteries in the second group demand counter for shutdown Bank "B." The cause of the event was inappropriate maintenance schedule and priority to replace the group demand counter batteries prior to failure.
3232009002 | Diablo Canyon 2 | 08/26/2009 | 01/19/2010 | ML10027022 | <strong>Technical Specification 3.7.1 Violation due to Cracked Valve Spring</strong><br /><i>Abstract:&nbsp;</i>On August 26, 2009, at 12:45 PDT, with Unit 2 in Mode 1 (Power Operation) plant operators declared the main steam safety valve (MSSV) RV-224 inoperable in accordance with Technical Specification (TS) 3.7.1 Limiting Condition for Operation, and reduced power. On August 26, 2009, at 16:06 PDT, Technical Maintenance personnel completed resetting the power range high flux reactor trip setpoints from 109 percent to 87 percent reactor power completing TS Action 3.7.1.A.1. This event was the result of a cracked MSSV spring. Based upon the final assessment Pacific Gas and Electric Company presumes the valve was outside the TS allowable setpoint prior to discovery. Immediate corrective actions included gagging the MSSV to preclude inappropriate opening during power operation. The MSSV RV-224 spring was removed during the Unit 2 fifteenth refueling outage. Additional failure analysis supports that the cause of the failure was environmentally induced corrosion initiated cracking with subsequent spring fracture.
3232009003 | Diablo Canyon 2 | 10/23/2009 | 12/23/2009 | ML09363008 | <strong>Containment Sump Recirculation Valve Position Interlock Failure Due to Inadequate Testing</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2009, with Unit 2 in Mode 6 (Refueling) and the reactor core offloaded to the spent fuel pool, plant operators identified failures of containment sump recirculation valves to activate their open interlock. This.condition would have prevented the residual heat removal (RHR) flow from reaching the containment spray, high head and intermediate head safety injection pumps following alignment to long term recirculation in accordance with Emergency Operating Procedures (EOP) via the control room manual remote switches. On October 23, 2009, the Unit 1 sump valves interlock condition was satisfactorily verified based upon a review of testing previously performed. Plant operators made a non-emergency notification in accordance with 10 CFR 50.72(b)(3)(ii)(B) at 14:44 PDT (EN45461). This event was the result of inappropriate maintenance and testing performed during the Unit 2 fourteenth refueling outage (2R14) that resulted in the valve position interlock switches for the containment sump unable to perform their safety function without local manual operator action. Unit 2 Cycle 15 specific analysis performed for a range of loss of coolant conditions found that the time to perform local manual operator actions was available. The analysis also verified that radiological conditions at the local manual actuation locations would allow operator action.
3242009001 | Brunswick 2 | 01/27/2009 | 03/29/2009 | ML09097027 | <strong>High Pressure Coolant Injection (HPCI) System Inoperable Due to Water in the HPCI Turbine Casing</strong><br /><i>Abstract:&nbsp;</i>On January 27, 2009, at 2007 hours Eastern Standard Time (EST), the Unit 2 High Pressure Coolant Injection (HPCI) system was declared inoperable due to a sustained high water level in the HPCI exhaust line drain pot. The inability to reduce level in the exhaust line drain pot resulted in backup of water into the HPCI turbine casing which rendered the system unavailable to perform its safety function. This sustained high level was caused by a failure of the HPCI barometric condenser condensate pump and difficulties in establishing an alternate drain path from the barometric condenser. The HPCI system was declared operable, following repair of the HPCI barometric condenser condensate pump, on January 28, 2009, at 2050 hours EST. There are two root causes associated with this event. The HPCI barometric condenser condensate pump failed because no Preventive Maintenance (PM) activities had been established for the pump and motor. The difficulties in establishing an alternate drain path were a result of an incorrect annunciator response procedure. Corrective actions to prevent recurrence include establishment of PM activities for the HPCI barometric condenser condensate pump and motor and correction of the annunciator response procedure.
3252009001 | Brunswick 1, Brunswick 2 | 01/21/2009 | 03/22/2009 | ML09090051 | <strong>Loss of Control Room Air Conditioning and Emergency Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2009, at approximately 1300 hours Eastern Standard Time (EST), a loss of Control Building Heating, Ventilation and Air Conditioning (HVAC) control air Occurred. As a result, the two Control Room Emergency Ventilation subsystems required by Technical Specification (TS) 3.7.3, "Control Room Emergency Ventilation (CREV) System," and the three Control Room Air Conditioning subsystems required by TS 3.7.4, "Control Room Air Conditioning (AC) System," became inoperable. Because BSEP has a shared control room (CR), Unit 1 and Unit 2 entered TS 3.7.3 Required Action'C.1 (i.e., be in Mode 3 within 12 hours) and TS 3.7.4 Required Action E.1 (i.e., enter Limiting Condition for Operation (LCO) 3.0.3 immediately). Operability of the Control Room AC subsystems and CREV subsystems was restored and related LCOs, including LCO 3.0.3 were exited at 1429 hours following the restoration of control air to the CREV system. No reactor power reduction took place on either unit as a result of the LCO 3.0.3 entry. The direct cause of the loss of control air to the control room ventilation system was blockage of air flow through the Control Building instrument air dryer due to freezing of condensate within the cooling coil. The freezing was due to the failure to incorporate system operating parameters for temperature into the operating procedures associated with the Control Building HVAC system. Corrective actions to prevent recurrence include revising appropriate procedures to include guidance for low temperature operation.
3252009002 | Brunswick 1, Brunswick 2 | 07/08/2009 | 09/08/2009 | ML09258038 | <strong>Valid System Actuations due to Loss of Power to Emergency Bus E2</strong><br /><i>Abstract:&nbsp;</i>On July 8, 2009, at 1013 hours Eastern Daylight Time (EDT), during planned preventive maintenance activities, electrical power was lost to the 4160V emergency bus E2. Emergency Diesel Generator 2 automatically started and re-energized the E2 bus. The loss of power to E2 resulted in Unit 1 Primary Containment Isolation System Groups 2, 3, 6, and 10 isolations. Per design, no Unit 2 safety system group isolations or actuations occurred. Other Unit 1 actuations included the Reactor Building Ventilation System isolation (i.e., Secondary Containment isolation), automatic start of both trains of the Standby Gas Treatment System and automatic start of both trains of the Control Room Emergency Ventilation System. The affected equipment responded as designed. This event occurred during activities associated with instrument calibration of an emergency bus E2 voltage transducer. Technicians performing the activity opened the wrong test switch. As a result, arcing occurred when test equipment was connected to an energized circuit. This caused the blown fuse in the C phase of emergency bus E2, which in turn caused a loss of power to the emergency bus and the E2 master/slave breaker to trip. The root cause of this event is inadequacies associated with procedure 0PIC-CNV023 and the associated work order used to perform the preventive maintenance task. Corrective actions to prevent recurrence will correct identified problems with these documents.
3252009003 | Brunswick 1 | 08/14/2009 | 10/13/2009 | ML09292035 | <strong>High Pressure Coolant Injection (HPCI) Inoperable due to Automatic Closure of Inboard Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2009, at approximately 19:58 Eastern Daylight Time (EDT), the High Pressure Coolant Injection (HPCI) system inboard isolation valve automatically isolated. Inboard isolation was caused by an inadvertent high ambient temperature signal from the HPCI steam leak detection monitor. Local temperatures were confirmed to be normal and no steam leak was identified. With the HPCI system steam supply isolated, the HPCI system was declared inoperable in accordance with Technical Specification 3.5.1. The safety consequences of this event were minimal. The Emergency Core Cooling Systems (ECCS), with the exception of "A" loop of the Low Pressure Coolant Injection (LPCI) system, along with the Reactor Core Isolation Cooling (RCIC) system and Automatic Depressurization (ADS) system were operable and available to provide adequate core cooling if needed. The select cause of this event was determined to be early failure of a ceramic capacitor on a thermocouple input board on the isolated thermocouple signal conditioner. The corrective action for this event was to replace the failed thermocouple input module.
3252009004 | Brunswick 1, Brunswick 2 | 09/20/2009 | 11/19/2009 | ML09341021 | <strong>Technical Specification Required Shutdown Due To Emergency Diesel Generator 4 Inoperability</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2009, at 1950 hours Eastern Daylight Time (EDT), Emergency Diesel Generator (EDG) 4 was removed from service for routine maintenance and surveillance testing and both units entered Technical Specification (TS) 3.8.1, Required Action D.4, which required the inoperable EDG to be restored to operable status within 7 days (i.e., on September 20, 2009, at 1950 hours). On September 19, 2009 during post-maintenance testing of EDG 4, the diesel failed to start. As a result, it was evident that EDG 4 would not be restored to operable status within the Completion time of TS 3.8.1, Required Action D.4 and the decision was made to shutdown the units. Unit 1 entered Mode 3 at 2222 hours EDT on September 20, 2009, and Unit 2 entered Mode 3 at 0421 hours EDT on September 21, 2009. Subsequent investigation and testing determined that failure of EDG 4 was due to binding of the mechanical governor control (i.e., EGB) due to presence of foreign material. The select cause of this event is the failure to prevent intrusion of foreign material into the mechanical governor control during vendor performed maintenance. A contributing cause was BSEP maintenance controls. Lack of specificity in procedures for EGB maintenance created the potential for undetected foreign material to be introduced. Corrective actions include the establishment of purchase order requirements for foreign material exclusion (FME) and revising site procedures associated with EGB maintenance and governor oil addition or removal to include FME control and cleanliness requirements.
3272009001 | Sequoyah 1, Sequoyah 2 | 01/28/2009 | 03/27/2009 | ML09090031 | <strong>Appendix R Unanalyzed Condition Affecting Safety Related Shutdown Boards</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2009, during an audit of the Fire Protection Program, a postulated Appendix R fire scenario was identified that could potentially cause a loss of power to fire safe shutdown equipment in two areas of the Auxiliary Building. As part of the Appendix R common power supply analysis, coordination between load breakers and feeder breakers is required to protect the power supply because of a fire generated fault on the load power cable. The fire scenario identifies how this coordination could be defeated on the 6900-volt shutdown boards. The scenario occurs when the load breaker's 125 volt direct current (DC) control circuit is damaged in the fire and could potentially open the control circuit fuses, subsequently disabling the breaker's trip circuit containing the overcurrent relay protection. The same fire could damage the 6900-volt power cables, causing a phase-to- phase fault. The load breaker cannot clear the fault with the trip circuit control power fuses blown. Opening the feeder breaker causes a loss of the 6900 volt shutdown board and associated electrical loads. The two fire areas have operable detection and suppression systems. Compensatory measures (fire watches) have been initiated in the two fire areas. A modification has been initiated to remove the local control switch portion of the circuit to resolve this potential fire related failure.
3272009002 | Sequoyah 1, Sequoyah 2 | 02/11/2009 | 04/10/2009 | ML09103019 | <strong>Lower Containment Gaseous Radiation Monitor Channel Inoperable, a Resultant of Lekage Detection Capabilities</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2008, NRC verbally informed SQN that the lower containment atmosphere gaseous radioactivity monitors were considered inoperable. SQN subsequently declared the lower containment atmosphere gaseous radioactivity monitor channels inoperable and complied with the associated technical specification (TS) actions of Limiting Condition for Operation 3.4.6.1. On November 12, 2008, SQN submitted a license amendment request (LAR) to remove the lower containment atmosphere gaseous radioactivity monitor channels from the SQN TSs. NRC approved the SQN LAR on December 4, 2008. On February 11, 2009, NRC documented a violation of Units 1 and 2 TS 3.4.6.1, “Leakage Detection Instrumentation,” for the SQN failure to maintain the gaseous lower containment atmosphere radioactivity monitors of the reactor coolant system (RCS) leakage detection instrumentation operable. NRC concluded that the Unit 1 and 2 monitors had been inoperable since June 1987 as a result of not being able to perform their safety function of detecting a RCS pressure boundary leak of 1 gallon per minute in one hour because of improvements in reactor fuel quality. In addition, NRC exercised enforcement discretion and did not issue enforcement action for this violation in accordance with Enforcement Guidance Memorandum 09-001, “Dispositioning Violations of NRC Requirements for Operability of Gaseous Monitors for Reactor Coolant System Leakage Detection.”
3272009003 | Sequoyah 1, Sequoyah 2 | 03/26/2009 | 12/21/2009 | ML09363004 | <strong>Units 1 and 2 Reactor Trip on Reactor Coolant Pump (RCP) Buses Undervoltage</strong><br /><i>Abstract:&nbsp;</i>The enclosed LER is being revised to indicate a condition where SQN failed to perform a technical specification (TS) action within the required timeframe. The enclosed LER is being revised to indicate that the condition resulted in an unplanned scram with complications. On March 26, 2009 at 0452 Eastern daylight time (EDT), Sequoyah Units 1 and 2 received an automatic reactor trip on reactor coolant pump (RCP) buses undervoltage. A loss of Common Station Service Transformer (CSST) C caused a loss of power to two unit boards on each unit that feed RCPs. CSST B continued to supply offsite power to the Train B safety-related shutdown boards for both units. The emergency diesel generators started and powered the Train A safety-related shutdown boards for both units. Both units were stabilized in hot standby (Mode 3). CSST C was isolated from CSST D and reenergized from the switchyard PCBs. Offsite power was then restored to the Train A safety-related shutdown boards for both units. The cause of the bus fault was determined to be degraded bus bar insulation and water intrusion into the CSST D secondary bus duct: Corrective actions include replacement of a section of the CSST D bus and inspection of the other CSSTs and cooling tower transformers (CTT). Repairs to degraded insulation of CSST C, CTT A, and CTT B were made as a result of the inspections. After the dual unit trip, with one offsite power source inoperable, the remaining offsite power source was not demonstrated operable within one hour as specified by TS 3.8.1.1 Action a. The TS action was subsequently completed.
3272009004 | Sequoyah 1 | 04/28/2009 | 06/29/2009 | ML09180045 | <strong>Unit 1 Manual Reactor Trip Following Isolation of Two Intermediate Pressure Feedwater Heater Strings</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2009, at 2159 Eastern daylight time, SQN Unit 1 reactor was manually tripped following automatic isolation of two intermediate pressure feedwater heater strings. Prior to the reactor trip, the control room was notified that a moisture separator relief valve (MSR) had lifted. Upon notification of the condition of the valve, Operations personnel entered applicable abnormal operating procedures. Unit power was reduced from 27 percent to approximately 18 percent in an attempt to close the MSR relief valve. Since the reduced power level did not close the valve, the turbine was manually tripped. Following the turbine trip, two intermediate pressure feedwater heater strings automatically isolated. Operations manually tripped the reactor and entered the applicable emergency procedures. The plant safety systems responded as designed. The cause of the MSR valve lifting was determined to be failure of a gland sealing steam check valve to isolate because of foreign material. The cause of the isolation of the intermediate heater strings was determined to be the backflow of inventory from Heater Drain Tank (HDT) No. 3 into the No. 2 heater, which interfered with the ability of No. 2 heater to maintain proper level. As an interim action applicable plant operating procedures have been revised to ensure that when the plant is operating below 50 percent RTP, HDT No. 3 is maintained in full bypass to the condenser. The corrective action will perform a study of the necessary design change options and implement a solution.
3272009005 | Sequoyah 1 | 05/06/2009 | 07/06/2009 | ML09187102 | <strong>Manual Reactor Trip Following a Loss of Flow through Loop 1 Feedwater Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On May 6, 2009, at 2256 Eastern daylight time with Unit 1 operating at 100 percent reactor power, the reactor was manually tripped because of imminent loss of steam generator level induced by the closure of the Loop 1 main feedwater regulating valve. During normal power operations, the control room received a steam flow/feedwater flow mismatch alarm. Operations placed the Loop 1 main feedwater regulating valve in manual and attempted to open the valve. Operations observed that there was still no flow to the Loop 1 steam generator. Operators took action to manually trip the reactor. The Loop 1 main feedwater regulating valve actuator diaphragm was found to be ruptured. The diaphragm failure is attributed to an improper clamping force of the diaphragm to the actuator stem. This insufficient clamping force was a result of insufficient torque applied to the fastening screw. The insufficient clamping force allowed stress concentrations at the diaphragm hole, which caused an initial tear in the diaphragm composite material and led to an instantaneous failure of the diaphragm.
3272009006 | Sequoyah 1, Sequoyah 2 | 05/27/2009 | 08/28/2009 | ML09243033 | <strong>Units 1 and 2 Inoperability of Auxiliary Building Gas Treatment System Because of Inadequate Surveillance</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2009, at 2100 Eastern daylight time, on SQN Units 1 and 2 it was determined that the auxiliary building gas treatment system (ABGTS) pressure test surveillance instruction (SI) was not being performed adequately on safety-related auxiliary building secondary containment enclosure (ABSCE) dampers. This is a result of closed in-series nonsafety-related dampers beyond the test boundary could mask leakage through the safety-related dampers. SQN Units 1 and 2 invoked the provisions of Surveillance Requirements (SR) 4.0.3. Subsequently, the ABGTS safety-related dampers were retested and both trains were verified as operable. The ABGTS pressure test SI has historically been performed in an alignment that allows the nonsafety-related dampers that isolate in series with safety-related ABSCE dampers to be closed. Based on further review, it was determined that the application of the provisions of SR 4.0.3 was not appropriate for this situation. As such, the event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B).
3272009007 | Sequoyah 1, Sequoyah 2 | 09/23/2009 | 11/20/2009 | ML09328017 | <strong>Failure to Perform a Technical Specification (TS) Action within the Required Timeframe</strong><br /><i>Abstract:&nbsp;</i>On September 23, 2009, at 0346 Eastern daylight time (EDT), Diesel Generator (DG) set 2B-B was declared inoperable because of scheduled surveillance testing. SQN Units 1 and 2 entered Technical Specification (TS) 3.8.1.1, Action b. With one DG set inoperable, TS 3.8.1.1 Action b requires the remaining AC electrical power sources to be demonstrated operable. Specifically for the offsite circuits required to be operable by TS Limiting Condition for Operation (LCO) 3.8.1.1.a, Action b requires, within one hour, that each of the two independent circuits between the offsite transmission network and the Class 1E distribution system be demonstrated operable by verifying correct breaker alignment and indicated power availability. At 0630 EDT, it was discovered that the required action for offsite circuits had not been performed. The TS action was performed and demonstrated the offsite circuits were operable. The cause of this event has been determined to be inadequate oversight by the Operations unit supervisor for the assignment, performance, and verification of the TS action. Corrective actions include Operations procedure revisions to enhance verification and ownership of implementation of TS actions and counseling of the Operations personnel involved.
3272009008 | Sequoyah 1, Sequoyah 2 | 10/28/2009 | 01/27/2010 | ML10032005 | <strong>Fuel Assemblies in Spent Fuel Pool not Stored in Conformance with Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to include the results of the root cause evaluation for this event. On October 28, 2009, at 1708 Eastern daylight time, it was discovered that four fuel assemblies in the SQN spent fuel pool (SFP) were not in conformance with criticality control requirements of Technical Specifications (TS) 5.6.1.1.c. These configuration errors occurred during the October 2009 SFP reconfiguration campaign to maintain conformance with the SFP decay heat dispersion requirements. The fuel assembly transfer forms (FATFs) prepared for this reconfiguration campaign did not correctly incorporate the TS 5.6.1.1.c criticality requirements and erroneously specified unacceptable SFP locations for the four fuel assemblies. The fuel assemblies were moved in accordance with the FATFs which resulted in the SFP nonconformance. Once the nonconformance was discovered, corrective actions were initiated to move the four assemblies within the SFP to a TS compliant configuration. The cause of the mis-configuration was insufficient procedural guidance in designing a SFP arrangement and creation of the FATFs.
3272009009 | Sequoyah 1, Sequoyah 2 | 12/30/2009 | 04/14/2010 | ML10109001 | <strong>Unanalyzed Condition Affecting 'Probable Maximum Flood (PMF) Level</strong><br /><i>Abstract:&nbsp;</i>This LER is being revised to include the results of the root cause evaluation for this event. On December 30,-2009, the issuance of an updated calculation titled "PMF Determination for Tennessee I River Watershed" increased the SQN design basis PMF level from Elevation 719.6 feet to Elevation 722.0 feet. This increase in calculated .PMF elevation resulted from several calculational changes including updated dam rating curves using model data and changes in reservoir operating policy. A previous change had decreased the SQN PMF elevation from 722.6 feet to 719.6 feet. However, SQN remains designed for a flood elevation of 722.6 feet with the current exception of the diesel generator sets and spent fuel pool cooling pumps. Because of the unanalyzed condition, the potential existed for SQN to exceed its PMF design bas,is and adversely affect plant safety. No actual flooding occurred. The root causes of this event were determined to be the failure to establish a PMF procedure or process that could be used to train personnel to perform, revise, and maintain accurate PMF calculations and inadequate communication between organizations. Contingency measures were put into place to protect the diesel generator sets and spent fuel pool cooling pumps. Applicable plant procedures are being revised to incorporate these contingency measures to protect plant equipment during a PMF event.
3282009001 | Sequoyah 2 | 05/27/2009 | 07/20/2009 | ML09201045 | <strong>Unit 2 Automatic Reactor Trip Following a Power Range Negative Rate Trip</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2009, at 1904 Eastern daylight time, SQN Unit 2 reactor automatically tripped following a power range negative rate trip. An investigation revealed that one out of five rod control power cabinets had lost power as a result of lightning strikes onsite that induced a voltage on the electrical cables between the power cabinets and the reactor head. The Unit 2 power supplies in the rod control system contain a circuit that will sense a high voltage condition and will trip the power supply. When the high voltage condition occurred, the control rods (10) supplied from the affected cabinet inserted into the core causing the negative rate trip. The plant safety systems responded as designed. The root cause of this event has been determined to be the power supplies are susceptible to lightning induced overvoltage conditions because of a lack of a filter in the overvoltage protection circuit for the control rod drive system. The corrective actions include replacement of the existing overvoltage circuits with those less susceptible to voltage induced occurrences. An evaluation of lightning protection issues for the site is being conducted.
3282009002 | Sequoyah 2 | 11/26/2009 | 01/25/2010 | ML10027003 | <strong>Manual Reactor Trip Because of Degrading Main Feedwater Pump Turbine Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On November 26, 2009, at 0242 Eastern standard time (EST), SQN Unit 2 reactor was manually tripped following indication of degrading main feedwater pump turbine (MFPT) condenser vacuum. At approximately 0239 EST, the shift manager was notified of a degrading vacuum in the 2A MFPT condenser. Operations manually tripped the reactor and entered the applicable emergency procedures. The cause of this event was determined to be the closure of two isolation valves for a level switch on the gland seal steam system that trapped water in the level switch and indicated a high gland steam level. With the level switch actuated, two associated gland seal steam drain valves failed open and allowed gland seal steam to be directly routed to the drain lines of the MFPT condenser. This allowed steam to be injected into the drain flow from the 2A MFPT and created a restricted flow condition because of the steam bound environment and subsequently challenged the drain capability of the 2A MFPT condenser. The root cause of this event was determined to be a deficiency in enforcing proper standards for status control during work development and execution. Corrective actions include revising the work control process procedure to strengthen status control requirements and additional training regarding status control for selected plant personnel.
3312009001 | Duane Arnold | 02/01/2009 | 04/02/2009 | ML09096031 | <strong>Manual Reactor Scram Due to Loss of Condenser Cooling</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2009, with the plant operating at 53% power, during plant shutdown evolutions in preparations for Refuel Outage (RFO) 21, operators were in the process of securing the 'A' cooling tower in accordance with Operating Instruction 442, Circulating Water System. While throttling the 'A' cooling tower riser isolation valves in preparations for securing the 'A' circulating water pump, a rupture of the '13' cooling tower west riser occurred. In anticipation of a loss of circ water pit level, a manual scram was inserted at 1800. Following the manual scram, the plant was stabilized per abnormal operating procedures. Containment isolation signals operated as designed with Groups 2, 3, and 4 received. The cause of this event was an inadequate procedure. Operating Instruction 442 was inadequate to prevent an inappropriate operational configuration that resulted in the failure of the cooling tower riser. A design change restored the failed riser with a more robust design, and enhanced the design of the remaining risers on both cooling towers. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312009002 | Duane Arnold | 02/03/2009 | 03/05/2009 | ML09068003 | <strong>Outdoor Liquid Radwaste Storage Tank Radioactive Concentration Limit Exceeded</strong><br /><i>Abstract:&nbsp;</i>Following a manual scram that occurred on February 1, 2009, water was directed from the reactor to the radwaste system in order to adjust reactor water level. The water was directed to the radwaste tanks via the Reactor Water Clean Up (RWCU) and Residual Heat Removal (RHR) systems. Some of the RWCU water went to the normal radwaste tanks (1T-070 and 1T-072) for processing, however, most of the RHR water was directed into the radwaste surge tank, 1T-088. At 1332, on February 2, 2009, Surveillance Test Procedure (STP) NS490002, Low Pressure Coolant Injection (LPCI) Inject Check Valve Full Flow Test, was started as previously planned. This test resulted in an additional source of reactor vessel water to 1T-088 from the RHR Shutdown Cooling System. The RHR Shutdown Cooling system is an unfiltered source of reactor water. At 0130 on February 3, 2009, a radwaste operator discovered elevated dose rates in the vicinity of 1T-088. A subsequent sample of 1T-088 determined that the tank contained approximately 88 Curies of total radioactivity. This exceeded the Technical Specification administrative limit and Operational Dose Assessment (ODAM) limit of 50 Curies. Therefore, this event is reportable per 10 CFR 20.2203(a)(3)(i).
3312009003 | Duane Arnold | 04/03/2009 | 06/02/2009 | ML09154024 | <strong>Unplanned Manual Scram due to Increasing Reactor Water Level</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2009, while operating at 100% power, with no Technical Specification (TS) Required Actions in affect, instrument and controls (I&C) technicians were performing Surveillance Test Procedure (STP) 3.3.3.2-09, Reactor Water Level and Pressure Instruments Calibration. This STP was performed for the first time since the recorder had been replaced during Refueling Outage (RFO) 21 in February 2009. Step 7.1.20 directed lifting a lead on the positive terminal of channel 2 on Level Recorder Switch (LRS) 4559/4560. When the lead was lifted, the control loop for reactor vessel level control was opened, and indicated vessel level pegged low. The plant response, as designed, was to increase feed water flow to the reactor to compensate for the indicated lowering vessel level. This caused actual reactor vessel level to increase. As a result of the increasing reactor water level, operators inserted a manual scram at 0028. All safety systems responded as designed. Containment isolations signals were received for groups 2, 3, and 4 due to reactor level dropping below 170 inches. All isolations went to completion. This reactor level response is normal following a reactor scram. The cause of this event was an inadequate procedure change. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312009004 | Duane Arnold | 10/08/2009 | 12/07/2009 | ML09344006 | <strong>Unplanned Automatic Reactor Scram due to an Invalid Reactor Protection Signal</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2009, while operating at 100% power, during the performance of Surveillance Test Procedure (STP) 3.3.3.2-09B, Reactor Water Level and Pressure Instruments (Loop B) Calibration, an automatic reactor shutdown occurred. The shutdown was caused by the failure to close an instrument isolation valve for a Reactor Vessel Pressure Transmitter. The failure to close this valve resulted in creating a sensed low reactor water level on Reactor Protection System (RPS) channels A2 and B2, and thus resulted in the automatic reactor shutdown. Primary Containment Isolation System (PCIS) Groups 2, 3 and 4 were received due to reactor water level dropping below 170 inches due to the expected level shrink immediately following the reactor scram. All isolations went to completion. Reactor water level was subsequently returned to normal as expected under post scram conditions. The cause of this event was that defenses in depth were inadequate to prevent the plant transient during the performance of STP 3.3.3.2-09B. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3332009001 | FitzPatrick | 11/12/2008 | 01/12/2009 | ML09021027 | <strong>Inadequate Engineering Calculation Results in Insufficient Inventory in EDG Fuel Oil Storage Tanks</strong><br /><i>Abstract:&nbsp;</i>On 11/12/2008, while operating at 100% power (Mode 1), it was determined that a condition originally identified in July 2007 should have been reported under 10 CFR 50.73. Details are provided in the attached narrative. In summary, on several occasions between July 2004 and July 2007, an Emergency Diesel Generator (EDG) Fuel Oil Storage Tank (FOST) may not have had sufficient inventory to ensure seven (7) days of continuous EDG operation under full load conditions, resulting in being outside the Technical Specification (TS) Requirements. The apparent cause of the condition was failure to include all appropriate conservatisms when establishing the TS requirement. Corrective actions included increasing the FOST minimum available inventory requirement and submitting a TS Amendment. When discovered in July 2007, the FOST(s) inventories were between the calculated 7 day and 6 day requirements and were restored to greater than the 7 day requirement within the TS allowable time. During the three (3) years preceding the discovery, (July 2004 to July 2007), the combined inventories of Fuel Oil Storage Tanks and their associated Fuel Oil Day Tanks were sufficient to ensure seven (7) days of continuous EDG operation. Therefore, the EDG systems were available to perform their required safety function and there was no reduction in the margin of safety as a result of this condition.
3332009002 | FitzPatrick | 01/28/2009 | 04/09/2009 | ML09106074 | <strong>Subsystem Inoperable In Excess Of Technical Specifications Allowed Out-Of-Service Time</strong><br /><i>Abstract:&nbsp;</i>During the initial construction of the James A. FitzPatrick Nuclear Power Plant (JAF) a change was made to the design of the Battery Room Ventilation (BRV) System that changed the size of the BRV Air Handling Units (AHU) from 12,000 CFM to 6,000 CFM. This change was not addressed during the preparation of a Custom Technical Specification Interpretation regarding operability of the BRV System and its impact on the Batteries, Battery Charger's, and 125VDC Distribution System. The resulting error was carried forward into the Technical Requirements Manual (TRM) when JAF converted to Improved Technical Specifications (TS). This was discovered during preparation for a planned. maintenance activity in January 2009. The error allowed the BRV System to be considered operable with .a single AHU in service. It was determined that this may not have provided adequate ventilation under all design conditions. Therefore, an appropriate TS LCO should have been entered when an AHU was taken out of service (00S).. The most restricting LCO, '3.8.4 Condition B (8 hOurs to restore) followed by Condition C (be in mode 3 in 12 hours) was used to review past operability. It was determined on two occasions in the past 3 years this allowed 00S time would have been exceeded during planned maintenance. Therefore, this report is being submitted in accordance with 10CFR 50.73(a)(2)(i)(B).
3332009004 | FitzPatrick | 03/24/2009 | 05/26/2009 | ML09149017 | <strong>Subsystem Inoperable in Excess of Technical Specifications Allowed Out-of-Service Time</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2009, the control room envelope (CRE) boundary door, between the Control Room Chiller Room and the Control and Relay Room Fan Room, was found unlatched. The door was relatched and Technical Specification LCO 3.7.3 Condition B was entered. This was the third occurrence in a five day period. The cause was a worn latching mechanism that allowed the door to become unlatched due to vibration and pressure changes in the room. With this boundary door unlatched, the CRE boundary is not operable and the availability of the CRE to perform its accident mitigating function cannot be assured. Based on the identified cause, LCO 3.7.3 Condition B should have been entered on March 19, 2009, the first occurrence, and remained in effect until the degraded latch was repaired. Because the door could become unlatched at any time, the Technical Specifications requirement to maintain the CRE OPERABLE or take required actions was not met from March 19 until LCO 3.7.3 Condition B was entered on March 24. Therefore, this condition is reportable under 10 CFR 50.73(a)(2)(i)(B) (Violation of Technical Specifications) and 10 CFR 50.73(a)(2)(v)(D) (Loss of Safety Function).
3332009005 | FitzPatrick | 04/20/2009 | 06/22/2009 | ML09176010 | <strong>Safety Relief Valve Setpoints Outside of Allowable Tolerances</strong><br /><i>Abstract:&nbsp;</i>Review of the as-found test results for 11 Safety / Relief Valve (S/RV) [SB] pilot assemblies removed and replaced in September 2008, determined that 5 S/RVs were,outside the allowable as-found tolerance of 1145 psig +/- 3% (+/- 34.3 psig) required by Technical Specification (TS) Surveillance Requirement SR 3.4.3.1. The effect of these S/RVs being out of tolerance was analyzed and the results of this analysis show that Reactor Pressure Vessel (RPV) overpressure protection and nuclear plant safety were not adversely affected. Consequently, the safety significance of this event was minimal. The most probable cause for the failure of four of the S/RVs was determined to be corrosion bonding between the S/RV pilot disc and seat, a recognized industry generic problem with two-stage Target Rock relief valves. The fifth failure was determined to be due to significant pilot valve seat leakage which would have required additional steam pressure to overcome the leakage and lift this S/RV.
3332009006 | FitzPatrick | 04/22/2009 | 06/22/2009 | ML09176009 | <strong>Inoperable High Pressure Coolant Injection System</strong><br /><i>Abstract:&nbsp;</i>On 04/22/09, during the initial startup sequence of ST-4N, "HPCI Quick-Start, lnservice, and Transient Monitoring Test (1ST)", HPCI steam line isolation valves 23M0V-15, 23M0V-16, and 23M0V-60 closed on an invalid high steam flow isolation signal. The High Pressure Coolant Injection (HPC1)[EllS=BJ] turbine tripped due to the HPCI isolation signal. This invalid HPCI steam line isolation temporarily rendered the HPCI system inoperable and thus, this condition was reported within 8 hours per 10 CFR 50.72(b)(3)(v)(D). LCO 3.5.1 Condition C, HPCI System inoperable, was entered until the cause of the isolation was determined, required adjustments were made, and SR 3.5.1.9 was satisfied. The cause of the invalid isolation was a rapid opening of the HPCI Turbine Stop Valve 23H0V-1[EllS=V] that caused a surge in steam flow, which exceeded the High 'Steam Flow isolation trip setpoint.
3332009007 | FitzPatrick | 07/07/2009 | 09/08/2009 | ML09254022 | <strong>Inoperable Emergency Diesel Generators due to Degraded Voltage Timers</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2009, with the plant operating at 100% power, surveillance testing of the 4.16 KV Emergency Bus Degraded Voltage Time Delay Relays revealed that the "as-found" delay time for three of the four relays exceeded the Technical Specification (TS) allowable value for both channels of the Emergency Onsite Power System Loss Of Power (LOP) Instrumentation. The relays were marginally out of specification high. As a result, the LOP instrumentation was inoperable during the surveillance interval. The LOP instrumentation is required to maintain operability of the emergency diesel generators (EDG). The failure of both channels of the Emergency Onsite Power System LOP instrumentation caused both trains of EDG's to be inoperable for longer than the TS allowed completion time. The cause of failure is attributed to setpoint drift characteristics that are applicable to all four of the Agastat E7012 relays used as degraded voltage timers. TS 3.8.1 requires the plant to be in MODE 3 within 14 hours if both trains of EDG's are inoperable. Although the EDG's were technically inoperable, they were available and would have performed their safety function. This condition is reportable per 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS and per 10 CFR 50.73(a)(2)(vii) as a single condition that caused two independent trains to become inoperable. Immediate corrective actions were to replace the relays with solid state relays using an approved modification on July 8 and 9, 2009.
3332009008 | FitzPatrick | 09/17/2009 | 01/11/2010 | ML10055067 | <strong>High Pressure Coolant Injection System Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2009, a root cause analysis of the High Pressure Coolant Injection (HPCI) TURBINE STEAM SUPPLY STOP VALVE (23HOV-1) failure in January 2009 discovered that a previous change to the In-service Testing (IST) opening stroke time reference value had been incorrectly raised from 19.45 seconds to 22.12 seconds. The change, which was made on August 10, 2005, was not properly evaluated and did not contain adequate technical justification in accordance with the ASME OM Code. The cause of this event is attributed to personnel error in the implementation of the IST Program. Specifically, the opening stroke time reference value was revised without the appropriate technical justification. The change masked a degrading trend in the 23HOV-1 opening stroke time and resulted in the inoperability of the HPCI system. The condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications..." because during the time period described, the HPCI system was inoperable longer than allowed by the TS completion times. Although the HPCI system was technically inoperable prior to the maintenance activity, the HPCI system would have started and injected to the core, if required, within the required system initiation time of 60 seconds, and would have been able to perform its safety function during the eight hour mission time assumed in the JAF accident analyses.
3342009001 | Beaver Valley 1 | 03/26/2009 | 05/22/2009 | ML09163046 | <strong>Surveillance Test Inadvertently Violates Technical Specification 3.6.1 for Containment Operability</strong><br /><i>Abstract:&nbsp;</i>Beaver Valley Power Station (BVPS) Unit 1 commenced the performance of a Recirculation Spray System (RSS) flow test surveillance on one of the two outside RSS pumps. To perform this test while in Mode 1, the suction and discharge containment isolation valves (CIVs) on this RSS train of piping were closed (but not de-energized) and the RSS pump piping and casing was filled with water through the pump's casing manual drain valve since the RSS train is normally maintained dry. After successfully running the pump on recirculation flow, it was recognized during the pump draining operation that the CIVs on this RSS train's piping needed to be de-energized in order to maintain containment operability. These CIVs receive an 'open' signal following a containment isolation-Phase B signal, and not the typical 'close' signal. Thus, if a design basis accident was postulated to have occurred when the pump casing's manual valves were open, containment Operability would be compromised with the CIVs going open and pressurizing the pump casing. This is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications (TS). The cause of this event was determined to be less than adequate change management in revising the performance mode of the test without adequate evaluation of the impact on Technical Specification requirements. Narrow focus by procedure preparers, review organizations and end users on the most obvious TS requirement (Recirculation Spray System) resulted in a failure to identify that a more limiting TS requirement (Containment operability) was impacted by the test. This event is considered to have very low safety significance.
3342009002 | Beaver Valley 1 | 04/20/2009 | 06/18/2009 | ML09174005 | <strong>Feedwater Isolation Initiates Auxiliary Feedwater System During Refueling Shutdown</strong><br /><i>Abstract:&nbsp;</i>During a plant shutdown on April 20, 2009, a feedwater isolation occurred at the Beaver Valley Power Station (BVPS) Unit 1 as a result of two of three narrow range water level transmitters in the 'B' steam generator reaching the Hi-Hi setpoint. There was not sufficient time for Operator manual attempts to reduce the excessive feedwater flow rate prior to reaching the high water level. An automatic Feedwater Isolation Signal was initiated on the Hi-Hi steam generator water condition in the 'B' steam generator, with safety-related plant systems responding as designed. Both motor-driven auxiliary feedwater pumps started, as designed, in response to all main feedwater pumps being tripped by the Feedwater Isolation Signal. This was a valid actuation of the Auxiliary Feedwater System, which is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) The root cause of this event was determined to be foreign material found within the bypass feedwater regulating valve positioner, causing the valve to fail to close during the event. The foreign material was manufacturing induced and did not represent internal organizational or process weakness related to the procurement and use of this valve. The safety significance of the Feedwater Isolation event on April 20, 2009 was very low.
3342009003 | Beaver Valley 1 | 04/23/2009 | 06/18/2009 | ML09174005 | <strong>Containment Liner Through Wall Defect Due to Corrosion</strong><br /><i>Abstract:&nbsp;</i>During the Beaver Valley Power Station (BVPS) Unit 119th Refueling Outage, an ASME XI IWE general visual examination of the Reactor Containment Building (RCB) steel liner was conducted. The BVPS Unit 1 containment design consists of an internal steel liner that is surrounded by reinforced concrete. A suspect area was identified on the steel liner at the 746 feet elevation of the BVPS Unit 1 RCB during this inspection. This area was approximately 3 inches in diameter and exhibited blistered paint. The paint blister was intact at the time of discovery. Collapse of the blister during further inspection revealed protruding rust product underneath. This area was then cleaned to allow further evaluation. The cleaning activity uncovered a rectangular area of approximately 1 inch (horizontal) x 3/8 inch (vertical) that penetrated through the entire liner plate thickness. The liner plate at this location has a nominal thickness of 0.375 inches. The liner opening was enlarged and a piece of wood, which was approximately 2 inches x 4 inches x 6 inches, was removed. The resulting void was then filled with grout, a replacement plate was installed, and the area tested. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(A). The cause of the through wall liner corrosion was pitting type corrosion (rust) originating from the concrete side caused by foreign material (wood) that was in contact with the carbon containment steel liner. The wood was left behind as a result of inadequate housekeeping practices during the original construction of the containment wall. This event is considered to have very low safety significance.
3342009004 | Beaver Valley 1 | 04/26/2009 | 11/25/2009 | ML09336018 | <strong>Two Ultrasonic Indications Found in Reactor Coolant System Drain Pipe</strong><br /><i>Abstract:&nbsp;</i>During the Beaver Valley refueling outage, while performing planned ultrasonic examination of reactor coolant piping in accordance with Materials Reliability Project document MRP-146 "Materials Reliability Program: Management of Thermal Fatigue in Normally Stagnant Non-Isolable Reactor Coolant System Branch Lines", two relevant indications were found in a Reactor Coolant System 2-inch pipe segment which is a stainless steel drain/sample line off of the "A" hot leg on April 26, 2009. This is reportable pursuant to 10 CFR 50.73(a)(2)(ii)(A). There was no indication of through-wall leakage. This pipe segment was replaced. The most primary cause of the two identified cracks was determined to be fatigue. This event is considered to have very low risk significance.
3352009001 | St. Lucie 1 | 02/19/2009 | 04/20/2009 | ML09118039 | <strong>Unit 1 Verbatim Technical Specification Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2009, St. Lucie Unit 1 was operating in Mode 1 at 100% power when it was determined that the completed surveillance for the Unit 1 fuel oil transfer pumps was not in verbatim compliance with the technical specification (TS) and therefore operation of the facility is in a condition prohibited by TS, and reportable in accordance with 10 CFR 50.73 (a) (2) (i) (A). Both Unit 1 emergency diesel generators (EDGs) are operable and within their surveillance requirements based on the performance of post maintenance testing (PMT) which was in verbatim compliance. An evaluation determined this to be a legacy process issue due to interpretation of the TS regarding the acceptability of overlap testing. The design of the system in which the Unit 1 diesel oil transfer pumps do not auto start during normal operations, and the day tanks are gravity fed, is a design that is not conducive to verbatim compliance and is considered a contributing cause. Corrective actions taken include a change to surveillance procedures to eliminate any "overlap" testing.
3352009002 | St. Lucie 1, St. Lucie 2 | 02/18/2009 | 04/20/2009 | ML09118039 | <strong>Use of Unprotected Network to Transmit Safeguards Information</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2009, St. Lucie Unit 1 was operating in Mode 1 at 100% power when it was discovered that electronic information, designated as Safeguards Information (SGI), was transferred from a St. Lucie SGI computer (protected) to a non-SGI device (unprotected). The SGI was then emailed from the acting PSL Security Manager to a Security Director at another utility and then entered into a public folder on the Site local area network (LAN). The root cause of the event was determined to be a lack of formal guidance for declassifying electronic SGI prior to transferring from a protected environment to a non-protected environment. Contributing factors included formatting of information being transmitted, time pressure issues and human performance. Corrective actions included deletion of the SGI files from the unprotected Local Area Network (LAN), affected workstation computers were removed from service and re-imaged, and back-up systems purged. Similar actions were also taken at the other utility.
3352009003 | St. Lucie 1, St. Lucie 2 | 02/18/2009 | 04/20/2009 | ML09120006 | <strong>Radioactive Ni-63 Source Not Located During Semi-Annual Source Inventory</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2009, St. Lucie Unit 1 and Unit 2 were operating in Mode 1 at 100% power when a semi-annual radioactive source inventory conducted by Radiation Protection (RP) was unable to locate a source. The source was a 15 mCi Ni-63 sealed source generally licensed in accordance with 10 CFR 31. A search for the source was performed, but was unsuccessful. The loss of the source requires notification to the NRC and is reportable in accordance with 10 CFR 20.2201(b). The foil-like radioactive material is contained in a sealed housing requiring a tool for removal. Contact with the source poses no external or internal dose hazard to the health and safety of the public. The probability for personal contact and/or ingestion of the source is considered low. The evaluation determined the cause of this event to be a lack of a proper source control and process for Generally Licensed Devices. Corrective actions included revisions in the area of physical controls of the source and appropriate procedure changes.
3362009001 | Millstone 2 | 07/03/2009 | 08/19/2009 | ML09239004 | <strong>Reactor Trip due to High Pressurizer Pressure</strong><br /><i>Abstract:&nbsp;</i>At 1304 on July 3, 2009, with the Millstone Power Station Unit 2 at 100% power in Mode 1, the reactor automatically tripped due to a high pressurizer pressure reactor trip signal. There was a grid disturbance coincident with the time of the trip. Approximately 5 seconds prior to the trip, the four main turbine stop valves and four intermediate stop valves went fully closed. With the main turbine stop valves closed, the reactor coolant system (RCS) pressure increased to the high trip setpoint. The reactor automatically tripped and both pressurizer power operated relief valves (PORVs) lifted to relieve pressure as designed. The reactor trip generated a turbine trip signal. The most probable cause of this event is that the 24VDC power supply to the electro-hydraulic control (EHC) of the turbine valves did not tolerate the July 3, 2009 grid disturbance. As a result of the grid disturbance, the master trip solenoid valves (MTSVs) provided fluctuating emergency trip system (ETS) hydraulic pressure to the turbine valves. This fluctuating hydraulic pressure caused the turbine stop and intermediate stop valves to close unexpectedly. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
3362009002 | Millstone 2 | 07/13/2009 | 09/08/2009 | ML09259007 | <strong>Reactor Coolant System Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2009 prior to start-up from a forced shutdown with Millstone Power Station Unit 2 (MPS2) in mode 3 (hot standby) at 0% reactor power, a reactor coolant system (RCS) pressure boundary leak in the MPS2 'A' reactor coolant pump (RCP) seal cooler region was identified by a technician conducting a system walk-down at normal operating pressure/normal operating temperature (NOP/NOT). Chemical analysis of the fluid emitting from the leak conclusively identified the fluid to be reactor coolant. In accordance with Technical Specification 3.4.6.2 action b, MPS2 immediately commenced a cool down to mode 5 (cold shutdown). The pressure boundary leakage was determined to be the result of a weld defect from original fabrication of the 'A' RCP seal cooler. The weld was repaired and the unit was started up and returned to service. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by Technical Specifications, and 10CFR50.73(a)(2)(ii)(A) as a degraded or unanalyzed condition.
3362009003 | Millstone 2 | 10/07/2009 | 06/07/2010 | ML10201029 | <strong>Two Independent Diesel Gererators Rendered Inoperable due to Cornmon Cause</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2009, while Millstone Power Station Unit 2 was in Mode 5 at 0% power, operators conducting a control board walk-down at turnover noted that the "inhibit" keys for under voltage protection were in place and the sensor channels for both vital buses were bypassed. It was determined that the channels were bypassed earlier in the day while Millstone Power Station Unit 2 was in Mode 4. This condition existed for approximately seven hours and rendered both emergency diesel generators inoperable, however the emergency diesel generators were available to be remotely started. The cause of the event was less than adequate written instructions for performing the task by instrument and controls technicians. Upon discovery, the channels were taken Out of "inhibit", restoring under voltage protection and operability of the emergency diesel generators. A new procedure to govern bypassing/inhibiting protective system sensor channels has been written and is in the review process. This event is being reported in accordance with 10CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(v)(D) and 10 CFR 50.73(a)(2)(vii). This is a supplement to LER 2009-003-00 to report this condition in accordance with 10 CFR 50.73(a)(2)(v)(D).
3362009004 | Millstone 2 | 11/11/2009 | 01/11/2010 | ML10025028 | <strong>Overdue ASME Code Required Inservice Test Did Not Meet Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On November 11, 2009, while Millstone Power Station Unit 2 was in Mode 5 at 0% power, the operators discovered a thermal relief valve was not tested or replaced within the allowed time interval as required by the ASME OM Code Mandatory Appendix 1, paragraph I-1390, and when subsequently tested the valve failed its acceptance criteria. The relief valve is on the inlet to the 'B' containment spray pump seal cooler and was replaced with a fully operational valve approximately seven and a half months beyond the end of the current ten year test interval. This condition was determined to be of low safety significance because at no time during the period when the relief valve was considered 'failed' were plant systems configured such that the relief valve would have been required to provide its relief function, and therefore no safety systems or components were inoperable and incapable of performing their safety functions. The cause was determined to be failure to follow procedures. The planners were briefed on the event and counseled on the need to follow station procedure requirements. The relief valve was replaced with an operational valve. This event is reportable as an operation or condition prohibited by Technical Specification per 10 CFR 50.73 (a)(2)(i)(B).
3362009005 | Millstone 2 | 12/02/2009 | 01/29/2010 | ML10056035 | <strong>Both Containment Air Lock Doors Open in Mode 1</strong><br /><i>Abstract:&nbsp;</i>On November 13, 2009, with Millstone Power Station Unit 2 exiting a refueling outage and preparing to go from Mode 5 to Mode 4, both the inner and outer containment personnel hatch air lock doors were closed, verified closed and successfully pressure tested. On December 2, 2009, while in Mode 1 at 100% power, personnel entered the containment for a planned entry. Subsequently, while in the process of entering the containment, a second entry team opened the outer air lock door and observed the inner door ajar. This condition should have been prevented by a design interlock which prevents opening the outer air lock door if the inner air lock door is not closed. The interlock failed to perform its design function because it was not properly reset during the refueling outage due to inadequate procedures. The outer air lock door was immediately closed. The time both air lock doors were open was less than one minute. The procedures that restore and verify the containment air lock door interlock have been revised. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) as any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
3382009001 | North Anna 1, North Anna 2 | 10/13/2009 | 12/14/2009 | ML09352039 | <strong>Missile Shield Door Design Function Not Met Due To Improper Configuration</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2009, with Units 1 and 2 operating at 100 percent power (Mode 1), an engineering evaluation confirmed the east missile shield door for the Service Water Valve House (SWVH) would not have performed its design function during a design basis tornado event. The east missile shield door locking pins were not engaged and the security hasp and lock would not be capable of meeting the design loading. Station procedure O-AP-41, Severe Weather Conditions, did not ensure the SWVH missile shield doors were properly secured in the event of a tornado or hurricane event. This could result in the east missile shield door swinging outward in a tornado missile event and a tornado missile could have entered the SWVH and disabled the electric power supply to the Service Water (SW) motor operated valves (MOV). This could have prevented the SW System from being able to mitigate the consequences of an accident and is reportable pursuant to 10 CFR 50.73 (a)(2)(v)(D). This event posed no significant safety implications since the SW spray arrays were verified to be in operation during each entry into the severe weather condition and capable of mitigating the consequences of an accident. Therefore, the health and safety of the public were not affected by this event.
3382009002 | North Anna 1 | 10/23/2009 | 12/15/2009 | ML09356085 | <strong>Completion of Unit Shutdown Required By Technical Specifications Due to RCS Leakage</strong><br /><i>Abstract:&nbsp;</i>At 1718 hours on October 23, 2009, with Unit 1 operating at 100 percent power (Mode 1), a unit shutdown commenced in accordance with Technical Specification 3.6.1, Containment Integrity, due to a small unquantifiable through wall leak on the normal letdown line upstream of outside containment isolation valve 1-CH-TV-1204B. At 1353 hours on October 24, 2009, Unit 1 entered Mode 5 cold shutdown. The normal letdown line leak was determined to be in the weld between the valve body and the special end connection. Subsequently, repairs were completed and the letdown system was returned to service. Unit 1 returned to 100 percent power (Mode 1) on October 30, 2009. This event is reportable per 10 CFR 50.73 (a)(2)(i)(A) for completion of a nuclear plant shutdown required by the plant's Technical Specifications. No significant safety. consequences resulted from this event since there was no release of radioactive material. Therefore, the health and safety of the public were not affected by this event.
3382009003 | North Anna 1 | 11/15/2009 | 01/14/2010 | ML10020020 | <strong>Inoperable Reserve Station Service Transformer due to Improper Load Tap Changer Setting</strong><br /><i>Abstract:&nbsp;</i>At 1434 hours on November 15, 2009, a Technical Specification limiting action was entered for an inoperable offsite circuit in order to troubleshoot the load tap changer (LTC) setting on the "A" Reserve Station Service Transformer (RSST) 1-EP-ST-2A. At 1445 hours it was determined that the undervoltage blocking setting for the "A" RSST LTC controller was set at 110 volts (~3850 VAC on the transfer bus) with a required voltage setting for operability of 105 volts (~3675 VAC on the transfer bus) or less. As a result the "A" RSST was notable to meet the GDC-17 preferred source requirement and was declared inoperable. This condition had existed since December 2008 when the LTC controller was installed. As such a condition prohibited by Technical Specification 3.8.1 existed and is reportable per 10 CFR 50.73(a)(2)(i)(B). At 1602 hours the 1J Emergency Bus was transferred to the Unit 2 "B" Station Service bus clearing the limiting action. No significant safety consequences resulted from this event since the condition would not have prohibited the 1J Emergency Diesel Generator from starting and providing electrical load on a loss of offsite power. Therefore, the health and safety of the public were not affected by this event.
3382009004 | North Anna 1, North Anna 2 | 12/09/2009 | 02/03/2010 | ML10048004 | <strong>Automatic Reactor Trip and ESF Actuation due to Human Performance Error During Testing</strong><br /><i>Abstract:&nbsp;</i>At 1423 hours on 12/9/09, electrical supply breaker L102 was inadvertently opened, which caused the "C" Reserve Station Service Transformer (RSST) to de-energize. This caused a loss of power to the 1H and 2J Emergency Buses and an automatic start of the 1H and 2J Emergency Diesel Generators (EDGs); both EDGs operated as designed. The Unit 1 "B" and Unit 2 "A" Charging pumps automatically started, as designed, due to the loss of power. The Unit 2 "G" Bus did not automatically transfer from the "C" RSST to the "B" RSST prior to undervoltage relay lockout operation resulting in the loss of the Unit 2 Circulating Water pumps. This resulted in a loss of condenser vacuum and a subsequent Unit 2 turbine and reactor trip. The Unit 2 Auxiliary Feedwater (AFW) pumps automatically started and operated as designed. The Unit 2 "C" Station Service Bus was also de-energized following the trip, as expected with the "C" RSST de-energized. This resulted in the loss of the Unit 2 "C" Reactor Coolant Pump (RCP). The "A" and "B" RCPs operated as designed. This event is reportable per 10 CFR 50.73 (a)(2)(iv)(A) for the automatic actuation of the Reactor Protection System, EDGs, AFW System, and Charging Systems. No significant safety consequences resulted from this event since all Engineered Safety Feature equipment responded as designed. Therefore, the health and safety of the public were not affected by this event.
3392009001 | North Anna 2 | 04/28/2009 | 06/22/2009 | ML09181010 | <strong>Automatic Start of 2H EDG due to Loss of "B" Reserve Station Service Transformer</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2009, at 0953 hours, with North Anna Unit 2 operating at 100% power (Mode 1), Control Room Operations personnel received several annunciators simultaneously that indicated that the "B" Reserve Station Service Transformer (RSST) tripped and locked out. The Unit 2 "H" Emergency Diesel Generator (EDG) automatically started on a Degraded Voltage/Under Voltage signal due to the loss of the "B" RSST. The Unit 2 "H" EDG automatically picked up the load of the Unit 2 "H" emergency bus as designed. The "B" Charging/SI pump and "B" Component Cooling pump auto started due to the loss of power. Operations personnel entered appropriate abnormal procedures and stabilized the plant. An 8-hour Non-Emergency Report was made to the NRC at 1200 hours, in accordance with 10 CFR 50.72 (b)(3)(iv)(A), for an event that resulted in the automatic actuation of an EDG and Charging/SI pump. This event posed no significant safety implications since the Unit 2 "H" EDG started as designed and re-energized the emergency bus. The health and safety of the public were not affected by this event.
3412009001 | Fermi 2 | 03/28/2009 | 05/22/2009 | ML09148025 | <strong>Manual Reactor Scram in Response to High Turbine Vibration</strong><br /><i>Abstract:&nbsp;</i>At 0146 hours EDT March 28, 2009, the reactor mode switch was taken to shutdown in response to high vibration levels on the Main Turbine number 1 bearing. Reactor power had been reduced in preparation for a manual scram from below 25 percent power to enter into a unit refueling outage (RF13). The reactor protection system (RPS) performed as expected, and all rods were fully inserted into the core. Reactor water level reached a low of approximately 162 inches above top of active fuel and recovered to normal automatically without operator intervention. Reactor water level was maintained in the normal band with the Control Rod Drive System Supply. Reactor water Level 3 isolations occurred as expected. There was no maintenance or testing in progress that would affect high turbine vibration levels. Safety related plant equipment responded as expected to the manual reactor scram. The manual scram was inserted when turbine vibration levels on bearing number 1 reached 15 mils during the shutdown for RF13. The high turbine vibration was determined to be due to a High Pressure Turbine rub transversing bearing number 1. Cooling of the Moisture Separator Reheaters (MSRs) occurred early in the shutdown process, and it was determined that the rub was due to the MSR cool down process. The shutdown procedures will be reviewed in conjunction with vendor information and other industry operating experience to determine potential procedure enhancement.
3412009002 | Fermi 2 | 09/30/2009 | 11/17/2009 | ML09329003 | <strong>Manual Reactor Scram due to Hydrogen Leakage into the Stator Water Cooling System</strong><br /><i>Abstract:&nbsp;</i>At 11:09 EDT on September 30, 2009, the reactor mode switch was taken to shutdown and the main turbine generator was manually tripped in response to hydrogen gas leakage into the stator water cooling system from the main generator. The reactor protection system performed as expected, and all control rods fully inserted into the core. Reactor water level reached a low of approximately 122 inches above top of active fuel and recovered to normal level automatically without operator intervention. Reactor water level was maintained above Level 2, and as expected, none of the primary containment isolations or safety injection systems initiations associated with Level 2 occurred. The main steam isolation valves remained open, and the reactor feedwater system automatically restored and maintained reactor water level. The main steam bypass valves opened and automatically controlled reactor pressure. There was no transient increase in reactor dome pressure and no safety relief valves (SRVs) actuated. All primary containment isolations and actuations for reactor water Level 3 occurred as expected. The manual scram was inserted due to hydrogen leakage from the generator hydrogen cooling system into the stator water cooling system that exceeded a predetermined maximum allowable operational leakage rate. A leak in the generator stator water cooling system was located and repaired in accordance with the generator manufacturer's recommendations.
3462009001 | Davis-Besse | 10/13/2009 | 08/26/2010 | ML10244010 | <strong>Containment Air Cooler Fans Inoperable Due to Misapplication of Potter and Brumfield Rotary Relays</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2009, with the plant in Mode 1 at approximately 100 percent power, an evaluation of the Containment Air Cooler (CAC) fan circuitry design identified a misapplication of Potter and Brumfield MDR rotary relays. The relay wiring allowed the relays to potentially stop in an intermediate position, where the normally closed and normally open contacts were open. The CACs were declared inoperable per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.6 Condition E. Because Service Water Train 2 and subsequently Containment Spray Train 2 were also inoperable at the time of discovery, TS LCO 3.6.6 Condition G was applicable requiring entry into TS LCO 3.0.3. The operating fans were shifted from their normal fast speed alignment to the slow speed alignment used for accidents, which eliminated the relay issue and allowed them to be declared operable. This issue is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation prohibited by the Technical Specifications and in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function. An engineering change was completed to modify the CAC fan circuitry to eliminate this issue and allow the fans to be restored to fast speed alignment.
3462009002 | Davis-Besse | 12/16/2009 | 02/16/2010 | ML10050096 | <strong>Vibration Induced Failure of Temperature Instrument Results in Operation above Licensed Power Limit</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2009, with the plant in Mode 1 at approximately 100 percent power, it was identified that one of the inputs to the secondary heat balance for steam temperature was indicating approximately 8 degrees F lower than the input for the opposite steam line temperature indication. Based on heat balance calculations, this 8 degree F difference resulted in an indicated power of approximately 0.45 percent full power less than actual reactor thermal power. This 8 degree F difference resulted from a failed resistance temperature detector (RTD). The RTD failed due to the vibration of the main steam lines because the RTD was not long enough to ensure proper compression of the sensing element in the thermowell. A new RTD was installed, and this RTD will be replaced every two years until an RTD of appropriate length with better resistance to vibration is installed. A review of historical plant computer data showed this temperature difference existed since April 2006, and resulted in the plant operating at a maximum 8 hour average reactor power of 100.374 percent, which exceeded the maximum analyzed power level allowed by the Technical Specifications by 0.004 percent on one occasion. This issue is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation prohibited by the Technical Specifications.
3482009001 | Farley 1 | 02/16/2009 | 04/06/2009 | ML09097021 | <strong>EDG Auto Start due to Inadvertent Relay Actuation</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2009 at 16:55, Emergency Diesel Generator (EDG) 1C received an auto start signal due to de-energization of 4160 volt emergency Bus 1H [EB]. The bus was de-energized when a material handling cart inadvertently struck a relay cabinet containing the bus protective relays. The impact on the cabinet resulted in the phase two differential relay actuating which opened the supply breaker and actuated a lockout relay. With the undervoltage signal present on Bus 1H, EDG 1C received a start signal. EDG 1C started and all equipment functioned as designed. Unit 1 remained at 100 % power during the event. Recovery actions were initiated and no damage was found on Bus 1H or in the relay cabinet. Normal equipment alignment was reestablished at 20:53 hours. The material handling cart that struck the relay cabinet was being used during a maintenance outage on EDG 1-2A. The cart was stored next to the relay cabinet which is located adjacent to the walk way into the EDG 1-2A room. As another material handling cart was being moved through the walk way, it struck the stored cart which impacted the relay cabinet. The wheels on the stored cart were not chocked to prevent movement. Work was suspended on EDG 1-2A. The area was walked down to ensure no other carts or materials were improperly stored in the area. A walkdown of other safety related areas of the plant was conducted to verify all stored carts were properly secured. Personnel involved in the EDG 1-2A outage activities were briefed on the event prior to work resuming.
3482009002 | Farley 1, Farley 2 | 03/27/2009 | 05/26/2009 | ML09146077 | <strong>Turbine Driven AFW Pump Inoperable due to Internal Flooding Concerns</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2009 SNC determined that the calculation for internal flooding did not account for a floor drain located in a pipe chase that is exposed to the Main Steam Valve Room (MSVR). This open floor drain could allow water introduced into the MSVR during a Feed Water Line Break (FWLB), to reach the Lower Equipment Room. The Lower Equipment Room houses the Turbine Driven Auxiliary Feed Water (TDAFW) Pump [BA] and associated Uninterruptible Power Supply (UPS). Review of the flooding calculations was initiated to determine the projected level of water that could be expected in the Lower Equipment Room due to a FWLB in the MSVR. As a conservative measure, in the early morning hours of March 28, 2009, the floor drains in the pipe chase for Units 1 and 2 were plugged, returning both Units to the design configuration consistent with the internal flooding calculation. The review of the design calculation for internal flooding determined that during a FWLB in the MSVR, water was not assumed to reach the Lower Equipment Room and rise to a level to negatively affect equipment. SNC determined that during a FWLB in the MSVR with the drain line unplugged, the water could reach a level in the Lower Equipment Room that could have made the TDAFW UPS inoperable thus rendering the TDAFW Pump inoperable. Current design for a FWLB event requires two of the three AFW pumps to meet the AFW flow demand. With the assumed failure of the TDAFW Pump at the initiation of a FWLB in the MSVR, the single failure criteria could not be met. With the floor drains now plugged the TDAFW Pump will not be negatively affected by a FWLB in the MSVR.
3482009003 | Farley 1, Farley 2 | 05/13/2009 | 06/29/2009 | ML09181016 | <strong>Failure to Report Arrest Results in Inappropriate Unescorted Access</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2009 with Unit 1 and Unit 2 at 100 percent power, Southern Nuclear Operating Company (SNC) was informed that an SNC employee at Joseph M. Farley Nuclear Plant (FNP) had been under custodial arrest on May 9, 2009. This information was received from an Alabama Power Company employee who noticed that the individual was listed on the police arrest report in the May 13, 2009 edition of an area newspaper. SNC determined that the employee had returned to work at FNP on May 13, 2009 and did not report the arrest to his supervisor as required by procedure. SNC confirmed that the employee was the individual identified in the newspaper and that the employee had been arrested the previous weekend. SNC revoked the individual's access authorization and removed the individual from duty. The individual was required to complete the arrest reporting procedure to supervision, required to submit to a "for cause" Fitness for Duty testing, and was escorted off site. SNC determined that the individual had entered the Protected Area (PA) as part of a work assignment that morning. Review of PA entry records indicated that the individual had entered the PA but had not entered any Vital Areas. Areas where the individual had been working were inspected and no negative effect on plant operations or equipment was identified. SNC made a one hour notification at 1655 EDT on May 13, 2009.
3522009001 | Limerick 1 | 01/16/2009 | 03/13/2009 | ML09072107 | <strong>Neutron Flux Accident Monitoring Instrumentation Inoperable</strong><br /><i>Abstract:&nbsp;</i>The required and minimum number of accident monitoring instrumentation channels for neutron flux were not maintained operable for periods that exceeded the Technical Specification 3.3.7.5 allowable outage times. The apparent cause of the event was that the Technical Specification and associated Bases do not clearly identify what instrumentation is required to satisfy the requirement for two operable neutron flux channels during operation in POWER OPERATION (OPCON 1) and STARTUP (OPCON 2) modes. Following this event the licensed operators were trained on this requirement. The Daily Surveillance Log/OPCON 1,2,3 was revised to verify that the required number of SRMs and IRMs remain operable in OPCON 1. The TS 3.3.7.5 Bases for accident monitoring instrumentation will be revised to clarify the site methods for meeting the accident monitoring instrumentation requirements. Licensed operator training will be revised to reinforce the requirements for maintaining the accident monitoring instrumentation channels operable.
3522009002 | Limerick 1, Limerick 2 | 12/09/2008 | 04/22/2009 | ML09112047 | <strong>A Control Room Emergency Fresh Air Supply System Subsystem Inoperable</strong><br /><i>Abstract:&nbsp;</i>The "A" Control Room Emergency Fresh Air Supply System Subsystem was inoperable for a period that exceeded the Technical Specification allowed outage time. This occurred due to the time from removal of the sample to the time the unsatisfactory results of the vendor analysis were obtained exceeding the 7-day Technical Specification allowed outage time for one subsystem being inoperable. The sample analysis was completed within 31 days after removal as specified by the surveillance requirement. The affected charcoal bed was replaced and the subsystem was returned to operable status within 3 days of receiving the unsatisfactory sample results. Charcoal bed age and penetration data have been added as inputs to bed performance monitoring and replacement decision making.
3522009003 | Limerick 1, Limerick 2 | 08/27/2009 | 10/26/2009 | ML09299040 | <strong>Both Isolation Actuation Instrumentation Channels Inoperable</strong><br /><i>Abstract:&nbsp;</i>A review of steam leak detection setpoint calculations identified a nonconservative isolation actuation setpoint for the high pressure coolant injection system equipment room high differential temperature isolation. The event was caused by inadequate design controls that allowed less than adequate documentation of design analysis and less than adequate transmittal of design information during a modification and Technical Specification change in 1994. This resulted in an error during the environmental qualification temperature computation for the high pressure coolant injection system equipment room. Upon issue discovery a temporary configuration change was implemented to lower the high pressure coolant injection system equipment room high differential temperature setpoints. This issue is historical. Technical rigor of calculation issues have been addressed by implementation of the post-merger Exelon configuration change process procedures in 2002 and technical task risk/rigor assessments that were implemented in 2004. A license amendment request will be submitted to lower the Technical Specification 3.3.2 high pressure coolant injection system equipment room high differential temperature setpoint.
3532009001 | Limerick 2 | 03/31/2009 | 06/01/2009 | ML09152053 | <strong>Valid Actuation of the D23 Emergency Diesel Generator Bus Undervoltage Logic</strong><br /><i>Abstract:&nbsp;</i>A valid actuation of the D23 Emergency Diesel Generator bus undervoltage minimum actuation logic occurred following manual operator action to mitigate a bus overvoltage condition during emergency diesel generator testing. The event was caused by a failure of the emergency diesel generator voltage regulator due to an intermittent failure of the #1 rectifier bank. The emergency diesel generator voltage regulator was swapped to the #2 rectifier bank and the emergency diesel generator testing was successfully completed. The #1 rectifier bank is scheduled for replacement. Testing will be performed on the rectifier to confirm the cause of the failure was due to excessive forward voltage drop across the flyback diode.
3532009002 | Limerick 2 | 05/24/2008 | 07/07/2009 | ML09188025 | <strong>Inoperable Main Turbine Bypass System</strong><br /><i>Abstract:&nbsp;</i>A condition prohibited by Technical Specifications was identified during a review of main turbine valve testing activities. In 2008 there were three occasions when the main turbine bypass system was rendered inoperable. The action to verify the minimum critical power ratio above the limit specified in the Core Operating Limits Report was not completed within one hour as required by Technical Specifications. The condition prohibited by Technical Specifications was caused by inadequate site documentation for a critical design basis function. The Design Basis Document will be revised to include the design basis function of the stop valve load limit logic.
3542009001 | Hope Creek | 01/17/2009 | 03/16/2009 | ML09085043 | <strong>Reactor Manual Scram due to Turbine Runback</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2009 at 0432, a manual reactor scram was initiated by the operator at the controls by locking the mode switch in the SHUTDOWN position in response to a runback of the turbine generator caused by the current/flow comparator circuit of the stator water cooling (SWC) system. The runback was in response to a loss of the Turbine Auxiliary Cooling System (TAGS) loads due to (1) a solenoid valve failure of one of the TACS supply isolation valves (EG-HV-2522C) which caused the isolation valve to close and the system to transfer to the alternate TAGS supply; and (2) automatic isolation of the alternate TACS water supply due to a LO-LO-LO expansion tank level during the automatic transfer. The loss of cooling to the TAGS loads caused the SWC temperatures to increase, activating the runback circuitry for the turbine generator and the recirculation motor generators. The manually-initiated scram was In anticipation of a turbine generator trip and subsequent load reject that would have been caused by the high SWC temperatures after a time delay. The reactor was at 100% power at the beginning of the event and was approximately 73% power when the manual scram was initiated. Two control rods near the periphery of the core inserted past position "00" ("Full ln"} and did not settle to position "00". The control rods were subsequently tested for channel distortion and were determined to be operable. An ENS notification was made (event number 44784) at 0725 on January 17, 2009, in accordance with 10 CFR 50.72(b)(2)(iv)(6). All other safety systems functioned as required.
3542009002 | Hope Creek | 04/18/2009 | 08/18/2009 | ML09245059 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specification Allowable</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2009, PSEG received the initial results for the safety relief valve (SRV) pilot valve 'as-found' setpoint testing. The results indicated that two SRV pilot valve setpoint drifts exceeded Technical Specification (TS) allowable tolerance specified in TS 3.4.2.1. This specification requires SRV setpoint limits to be within +/- 3% of the specified value. The valves failing to meet limits were Target Rock Model 7567F two-stage SRVs. As-found testing was performed at an offsite test facility following Hope Creek fuel cycle fifteen. Additional SRVs were selected for testing, and subsequent results led to all 14 SRV pilot valves being removed as part of the expanded sample population. In all, a total of six of the fourteen SRV pilot valves experienced setpoint drift outside of the TS 3.4.2.1 limit. The apparent cause for the SRV setpoint failures has been completed. Immediate corrective action was to replace all of the pilot assemblies with tested and certified spare pilot assemblies. Since the number of SRVs outside the setpoint tolerance limit (six) was greater than the number of SRVs allowed to be inoperable by TS 3.4.2.1 (one), this condition is reportable under 10CFR50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant Technical Specifications.
3542009003 | Hope Creek | 05/06/2009 | 07/01/2009 | ML09189077 | <strong>Traversing In-core Probe (TIP) Containment Isolation Valves Found Open</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2009, four of the five traversing in-core probe (TIP) isolation valves were found in the open position with the associated machines de-energized. The plant was at 100% core thermal power (CTP) and the required position for the valves when the machines are de-energized is closed. Upon investigation it was discovered that the associated TIP detectors were located inside the primary containment at the indexers instead of being stored inside their shielded containers. This condition had existed since the machines were secured on May 6, 2009. The TIP isolation valves would not have isolated the containment upon receipt of a valid signal because the detector cables would have prevented full closure of the valves. Since there was no automatic function that would have provided a containment isolation for these penetrations and compensatory measures had not been taken as required by the Technical Specifications (TSs), this event is reportable as a condition not allowed by TS 3.6.3 under 50.73(a)(2)(i)(B). The event occurred due to a human performance error while operating the TIP machines and was not noted by operators due to their reliance on the Reactor Engineers (REs) in maintaining the TIP system configuration. The TIP machines were energized and the detectors were retracted into their respective shielded containers and the isolation valves were closed on May 8, 2009.
3542009004 | Hope Creek | 05/17/2009 | 07/14/2009 | ML09202025 | <strong>Multiple Control Rod Drifts Resulting in a Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2009, at approximately 0335, an automatic scram signal was received due to a low RPV water level condition when multiple control rod drives (CRDs) inserted into the reactor core causing lower reactor power and the collapse of voids in the core. The multiple CRD motion was caused by an air leak on the scram air header at hydraulic control unit (HCU) 22-11 (corrective action program (CAP) number: 20415621). The leak was from the separation of a copper solder connection which had been previously identified as having an air leak, but which was not entered into the corrective action process for resolution due to an oversight while reviewing diagnostic test data. The root cause investigation (RCE) determined that there were inconsistent expectations for the supplemental personnel's reporting of test or inspection results that led to the degraded condition not being correctly identified in the CAP to initiate timely repair. An ENS notification (number 45074) was made in accordance with 10CFR50.72(b)(2)(iv)(B) -- an event or condition that results in actuation of the reactor protection system when the reactor is critical. This event is also reportable under 50.73(a)(2)(iv)(A) for actuation of a system listed in 50.73(a)(2)(iv)(B)(1) -- reactor protection system (RPS).
3542009005 | Hope Creek | 05/26/2009 | 07/23/2009 | ML09211063 | <strong>Missed EDG Surveillance Check</strong><br /><i>Abstract:&nbsp;</i>At 0800 on May 26, 2009, the A emergency diesel generator (EDG) was declared inoperable for installation of a design change to the EDG rectifier section. At 0823, in accordance with Technical Specification (TS) 3.8.1.1 action b, the control room crew performed verification of off-site power sources to satisfy the limiting condition for operation (LCO) requirement to perform surveillance requirement (SR) 4.8.1.1.1.a "within one hour and at least once per 8 hours thereafter". The next performance of the SR was due at 1623 on May 26, 2009. Due to a human performance error and emergent plant events, the control room crew did not perform SR 4.8.1.1.1.a within the required 8 hours. The SR was performed successfully at 2014 on May 26, 2009, after the oncoming control room crew determined that the SR had not been performed by the previous control room crew as required by TS 3.8.1.1 Action Statement b. This placed the plant in a condition not allowed by the TSs which is reportable under 10 CFR 50.73(a)(2)(i)(B).
3542009006 | Hope Creek | 12/02/2009 | 01/29/2010 | ML10049075 | <strong>Post-fire Safe Shutdown Analysis Error</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2009, during a review of the post-fire safe shutdown analysis, it was noted that conditions existed whereby the requirements of the Hope Creek (HC) fire protection program (BTP CMEB 9.5-1) for the required degree of separation for redundant safe shutdown trains were not met. Contrary to the Updated Final Safety Analysis Report (UFSAR) Section 9A, a postulated fire in either of the reactor building fire areas (RB1 or RB2) could have tripped, and prevented the start of both chilled water pumps, thus causing a loss of HVAC to several areas. The loss of the HVAC system is due to a logic system interrelationship that the post-fire safe shutdown analysis does not specifically address. This is a condition that has existed since the initial post-fire safe shutdown analysis was performed. In accordance with the example provided in NUREG 1022 (Rev. 2), this event is reportable under 10CFR50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. An 8-hour NRC ENS notification was made in accordance with 10CFR50.72(b)(3)(ii)(B) on 12/02/09 (event number 45536). At the time, HC was at 100% power. Corrective actions were initiated to establish immediate compensatory fire watches until the fire response procedures were revised. The post-fire safe shutdown analysis is being revised to identify the manual actions needed to address the logic interrelationships.
3612009001 | San Onofre 2 | 09/13/2009 | 11/12/2009 | ML09317014 | <strong>Unit Trip on Low Vacuum Caused by Intake Circulating Water Gate</strong><br /><i>Abstract:&nbsp;</i>On 9/13/09 (Event Date) at approximately 12:42 PDT, Unit 2 automatically tripped from 94 percent power on low condenser vacuum [JC] caused when a Circulating Water [NN] intake structure recirculation gate stopped in mid-position. Heat treatment of the intake water tunnels is periodically performed to control marine growth. Intake structure recirculation gates allow reversal of the normal flow path, directing heated water from the condenser discharge through the inlet tunnel, and seawater through the outlet tunnel to the condenser inlet. Operators performing the heat treatment were in the process of reversing the circulating water tunnel flow when the gate stopped 45% open, allowing heated water to enter the condenser inlet. Although actions were taken to reduce power and restore the gate alignment, the continued loss of condenser vacuum caused an automatic turbine trip and reactor trip. All post-trip equipment functioned as required and the event has a low safety significance. The gate misaligned when it operated on 9/5/09; a loose stem stop nut was found. The gate was operated on 9/9/09 after maintenance; the misalignment was not corrected and the gate failed to move into position on 9/13/09. Unit 2 was restarted on 9/16/09. Corrective action was taken to improve the procedural guidance for gate maintenance and to implement a rapid response recovery for gate operations.
3612009002 | San Onofre 2, San Onofre 3 | 03/28/2009 | 05/27/2009 | ML09148017 | <strong>Inoperable 1E Breaker Causes Containment Chiller to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2009 at 2228 PST, the Containment Emergency Cooling Unit (ECU) Class 1E supply breaker 2B0410 failed to close upon demand from the control room in preparation for a routine surveillance test. Based on the failure analysis, SCE concluded that breaker 2B0410 was not functional for Design Basis Accidents between March 11 and April 1, 2009 and not seismically qualified. Because the Class lE powered ECU was inoperable for greater than the 7 days allowed by Technical Specification (TS) 3.6.6.1, this report is being submitted in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the TS. The breaker failure to close was caused by the combined effects of misalignment and interferences between the breaker and the cubicle. SCE modified the cubicle by replacing the "hex" head bolt with a round head bolt to eliminate the interference with the breaker causing the misalignment. Additional actions included inspection of other similar breaker/cubicles on Units 2 and 3, cycling the breakers to verify operability, and modifying the cubicles, as necessary. Since the ECU was unavailable for 21 days and other breakers remained operable to all but seismic events throughout the duration of this occurrence, the safety significance of this event was low.
3612009003 | San Onofre 2 | 09/29/2009 | 11/25/2009 | ML09331043 | <strong>Pressurizer Auxiliary Spray Failed Inservice Test</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2009, with Unit 2 in Mode 4 for the Cycle 16 refueling outage, the Inservice Test (IST) determined that back leakage through Pressurizer [AB] Spray check Valve (MU-977) potentially prevented the Pressurizer Auxiliary Spray from meeting the residual heat removal licensing basis described in the UFSAR. The licensing basis conservatively assumes depressurization of the RCS within one hour for an initiating event with a Loss of Offsite Power (LOOP), a seismic event, and the single failure of an Emergency Diesel Generator (EDG). The failure to meet the depressurization rate criteria under conservative assumptions does not affect the system response or results for analyzed Design Basis Accidents. The event has a low safety significance as other means are available to accomplish depressurization of the RCS for accident mitigation. The cause of the check valve failure was a manufacturing defect. The swing arm hinge bushings were found backed out of the valve body and prevented free movement of disc swing arm assembly. The manufacturer had knurled the metal to fit the bushings into the body when an interference fit was required. MU-977 was repaired; the other similar valve on Unit 2 will be inspected prior to start up from the Cycle 16 refueling outage. Bushings on Unit 3 valves were previously replaced and the valves have continued to pass IST performance tests.
3612009004 | San Onofre 2 | 12/23/2009 | 02/19/2010 | ML10061056 | <strong>Both Trains of Spent Fuel Pool Cooling Inoperable Results in a Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On 12/23/2009 at about 0957 PST with Unit 2 defueled for a refueling outage, Train A Salt Water Cooling (SWC) low flow and Component Cooling Water (CCW) Heat Exchanger high differential pressure alarms were received in the control room. The reduction in SWC flow was suspected to be caused by debris in the CCW heat exchanger. To clear the debris, Operators stopped the Train A SWC pump at approximately 1014 PST, realigned the system for reverse flow, and restarted the SWC pump at 1116 PST. While the Train A SWC pump was stopped, the temperature in the Spent Fuel Pool (SFP) increased from about 74 to 78 degrees F. Train B CCW System was previously removed from service for scheduled maintenance. With both trains of the CCW system out of service, SFP cooling was suspended for approximately 62 minutes while the Train A SWC pump was off. Based on guidance from the NRC, this event is being reported under 10 CFR 50.73(a)(2)(v)(B) as a loss of safety function of systems that are needed to remove residual heat. Investigation subsequently found the flow decrease was the result of a damaged SWC pump suction strainer that allowed ocean debris to enter the CCW heat exchangers. The safety significance of this event was low since the temperature of the SFP remained below the maximum allowed 160 degrees F and all other applicable licensing controlled specifications were met.
3612009005 | San Onofre 2 | 02/03/2009 | 09/03/2010 | ML10250029 | <strong>Wiring Error in Diesel Generator Circuit Results in Loss of Fire Isolation Capability</strong><br /><i>Abstract:&nbsp;</i>On 2/3/2009, with Unit 2 in Mode 5, plant personnel were performing planned maintenance on the Unit 2 Train A Emergency Diesel Generator (EDG) control panel. During this testing, it was discovered that a fire isolation fuse was mis-wired and bypassed the fuse protection for the local EDG control circuitry. In this condition, a hot-short on the remote (control room) wiring would open circuit the control power fuse to the EDG excitation circuitry and cause a loss of EDG function. SCE is reporting this occurrence in accordance with 10CFR50.73(a)(2)(ii)(B). On 2/3/2009, SCE corrected the wiring error to match to restore Unit 2 to the credited Appendix R configuration. SCE initiated hourly fire-watches at designated cable locations in Unit 3 until July 2009 when the Unit 3 Train A EDG excitation circuit was confirmed to be wired properly. Train B EDGs for Units 2 and 3 are not credited in the Appendix R analysis. They do not have fire isolation fuses in the circuit design and are not susceptible to this failure mode. SCE has determined that the EDG Train A wiring error has a very low safety significance.
3622009001 | San Onofre 3 | 09/14/2009 | 11/16/2009 | ML09321013 | <strong>Component Declared Inoperable After LCO Time Limit</strong><br /><i>Abstract:&nbsp;</i>On 9/15/09 (Event Date) at 0030 PDT, with Unit 3 at 100 percent power, operators determined Limiting Condition of Operation (LCO) 3.8.1 B.2 for the Emergency Diesel Generators (EDG) was not met. Post-Accident Monitoring Instrumentation (PAMI) is required by TS 3.3.11 and is supported by the EDGs because the mission time exceeds the battery capacity. Some of the PAMI indications are displayed to the operators by the Qualified Safety Parameter Display System (QSPDS). LCO 3.8.1 B.2 requires declaring EDG supported features inoperable within four hours. On 9/14/09 at 1200 EDG Train B failed a surveillance test; however, it was not identified that QSPDS Train A had been previously removed from service to repair a display monitor. Both trains of QSPDS were returned to service at 1728. At 0030 on 9/15 it was discovered QSPDS Train B had not been declared inoperable by 1600 as required, and a late log entry was made. The apparent causes were an inadequate procedure, a failure to adequately assess the emergent equipment failure for cross-train impact, and failure to recognize QSPDS as integral to PAMI. Corrective actions revised the EDG surveillance procedure to emphasize QSPDS is part of PAMI, and issued a required reading on preventing an inadvertent loss of safety function. There was no safety significance as components were restored to service within the allowable time limits.
3622009002 | San Onofre 3 | 12/12/2009 | 02/10/2010 | ML10047068 | <strong>Emergency Diesel Start Failure Results in Unusual Event</strong><br /><i>Abstract:&nbsp;</i>On 12/11/09 the Train B Emergency Diesel Generator (EDG) was declared inoperable when a technician grounded a wire, opening a fuse, and causing alarms in the control room. Technical Specification (TS) 3.8.1 Action B required a common cause evaluation or starting the alternate train EDG within 24 hours. On 12/12/09 at 00:25 PST, TS Condition 3.8.1.F was entered when the 24 hour period expired. At 01:05 PST Train A EDG 3G002 failed to start to comply with Condition B.3.2. Unit 3 entered a TS required shutdown from 96% power at 01:26 PST and declared an Unusual Event as required by the SONGS Emergency Plan. The condition exited at 05:11 and 40% power when the Train B EDG became operable. The Train A EDG failure was caused by an open capacitor in a power supply. The resulting voltage spikes caused a speed switch malfunction, locking out the start signal to the air motors. The Train B EDG had a pre-existing ground on one side of the circuit that caused the fuse to open when the other side was grounded, actuating the control room annunciators. Corrective actions included troubleshooting, which located the pre-existing ground, and installing new power supplies with recently manufactured capacitors. The safety significance was low as the Train B EDG was fully functional during the event for either manual or automatic start.
3642009001 | Farley 2 | 10/06/2009 | 03/01/2010 | ML10061009 | <strong>Service Water Pump Seismic Supports Degraded</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2009 after completing repairs to the Unit 2 B-Train Service Water System (SVV) Pump [BI] Seismic Supports, Southern Nuclear (SNC) identified that the Unit 2 A-Train SW Pump Seismic Supports did not meet the design requirements to support operability of the SW pumps during a seismic event. Efforts to replace seismic supports for the five Unit 2 SW Pumps were completed on October 10, 2009. New seismic supports and mounting bolts were installed for each pump. A corrective action from the Root Cause Evaluation to inspect the seismic supports for Unit 1 and Unit 2 SW Pumps, on an established frequency, has been entered into the sites Corrective Action Program. As an extent of condition review, Unit 1 SW Pump seismic supports were also inspected. Results demonstrated that the Unit 1 supports met the design requirements to support operability of the Unit 1 SW Pumps. A corrective action from the Root Cause Evaluation to replace the seismic supports has been entered into the sites Corrective Action Program. Further analysis of the service water pumps and the need for seismic rings to withstand a design basis earthquake were performed. This analysis determined that the pump would not have been adversely affected by seismic activity and thus the pumps would have remained operable.
3662009001 | Hatch 2 | 03/12/2009 | 05/04/2009 | ML09124026 | <strong>Safety Relief Valves Allowable Test Range Exceeded Due to Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2009 at approximately 4:00 pm EDT, Unit 2 was in refuel mode at 0 percent power. On that day, it was determined that during bench testing at an independent testing facility five Safety Relief Valves (SRVs) experienced setpoint drift that exceeded the allowable plant Technical Specifications (TS) limit above the setpoint value. The initially identified cause of the SRV setpoint drift above the setpoint value is corrosioninduced bonding between the pilot disc and seating surface. Immediate corrective actions for this event included replacement of the SRVs with refurbished pilot valves with discs made from stellite 21 that have been certified to actuate within 11.5 psi of the setpoint. Each of the pilot discs from the valves removed for testing have been replaced with a pilot disc made from Stellite 21 material. Evaluation of additional actions to further improve SRV performance will be tracked under the plant's corrective action program.
3662009002 | Hatch 2 | 03/13/2009 | 05/04/2009 | ML09124025 | <strong>Primary Containment Allowable Bypass Leakage Rate Exceeded Due To Failure of Feedwater Check Valve(s)</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2009, Unit 2 was in the Refuel mode with fuel in the reactor vessel. Personnel were evaluating local leak rate testing (LLRT) on the valves and penetrations which comprise the primary containment bypass leakage isolation valves. The valves are classified as secondary containment bypass valves since the piping is routed outside the secondary containment boundary. It was determined that the "A" feedwater line, which is considered to be a water filled line, had a tested leakage value that would result in the line losing its water seal prior to thirty days after the initiation of a design basis accident, and thus the leakage should be considered as part of the bypass leakage. As part of the bypass leakage the measured value when converted to an equivalent air leakage value exceeds the allowable bypass leakage criteria. The cause of the feedwater valve test failures was misalignment caused by internal wear and missing bearing cover lock pins for the outboard valve and misalignment caused by excessive clearance between the hinge pin and the disc, and the hinge pin adjustment had changed over the operating cycle. Corrective actions for this event included rebuilding the valves with new parts, replacing the missing parts, and performing a modification to account for the incorrect hinge pin length.
3662009003 | Hatch 2 | 06/20/2009 | 08/10/2009 | ML09223014 | <strong>Main Generator Runback due to High Stator Water Cooling Water Temperature Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On June 20, 2009 at 14:17 EDT, Unit 2 was in mode 1 with an approximate reactor power of 2804 CMWTh. At this time protective circuitry initiated a main generator runback due to a high Stator Water Cooling (SWC) outlet temperature. The electro-hydraulic control (EHC) Mark VI cores processor began reducing turbine load by closing the turbine control valves (TCV) and subsequently opening the turbine bypass valves (TBV). Operations personnel began reducing reactor load in response to the main generator runback by reducing recirculation flow. The reactor power was reduced to approximately 66 percent reactor thermal power and could not be reduced any lower without the insertion of control rods. Due to turbine load reducing faster than the manual actions taken to reduce reactor load, reactor pressure began to increase. Pressure had reached the setpoint to actuate the Reactor Protection System, and a reactor scram was initiated due to high reactor pressure. This event was caused by the improper set-up of the SWC temperature control instrument loop during 2R20 outage. Corrective actions consist of: set-up of SWC valve 2N43F100 was corrected and the control system was calibrated, review of other work during the refueling outage was performed to ensure a similar condition does not exist on other equipment, and review of the Unit 1 SWC system was performed to confirm operation.
3662009004 | Hatch 2 | 06/23/2009 | 08/10/2009 | ML09223015 | <strong>Turbine Trip on High Reactor Water Level due to Failed Circuit Board Results in Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On June 23, 2009 at 03:51 EDT, Unit 2 was in mode 1 with an approximate reactor power of 1710 CMWTh. At this time an automatic reactor scram occurred as a result of a turbine trip due to high reactor water level. Prior to the event the reactor was increasing in power during startup from a recent outage. An instrument which controls reactor water level failed resulting in an increase in reactor water level. The water level increased to a point where the turbine control valve fast closure trip signal was initiated due to high reactor water level. All control rods fully inserted and Reactor Feed pumps tripped. Reactor water level initially decreased to approximately negative 25 inches, due to void collapse. The Primary Containment isolation Valve Group 2 isolation setpoint was reached, and the Group 2 valves isolated. Both the 'A' and 'B' Reactor Feed Pumps initially tripped, and the 'A' feed pump was restarted and used to restore and maintain reactor water level. Reactor pressure reached an upper value of approximately 964 psig. No Safety Relief Valves opened, nor were they required to open, based on the maximum pressure reached. Reactor water level increased to a maximum value of approximately 60 inches above instrument zero, but was restored to normal range. The cause of this event was the failure of an internal power supply electrolytic capacitor which caused a failure of the DC power supply for the Yokogawa level controller 2C32-K648. The failed power supply card containing the capacitor was replaced following the event and repetitive tasks have been created to replace this and similar power supply cards at a prescribed interval.
3682009001 | Arkansas 2 | 03/13/2009 | 05/12/2009 | ML09133022 | <strong>Manual Reactor Trip from Power In Response To Feedwater Regulating Valve Failing Closed</strong><br /><i>Abstract:&nbsp;</i>On Friday, March 13, 2009, at approximately 21:51 CDT, Arkansas Nuclear One, Unit 2 was manually tripped from 84% power due to decreasing level in the “B” Steam Generator caused by the “B” Main Feedwater Regulating Valve moving in the closed direction without input demand to close. The trip was manually initiated at approximately the 25% Steam Generator water level. Due to the valve malfunction the system was unable to restore the Steam Generator water level before the 22.2% Emergency Feedwater System Control actuation set point was reached. The Emergency Feedwater System actuated, as designed, restoring Steam Generator water levels to normal. Post trip responses were normal with all plant safety systems functioning as expected. Investigation revealed that the most probable root cause of the event was a foreign substance in the clearance area of the armature, internal to a current-to-pressure (I/P) converter in the “B” Main Feedwater Regulating Valve positioner. The positioner was replaced and tested, and Unit 2 returned to 100% power operation, Mode 1, at 17:01 CDT on March 17, 2009.
3682009002 | Arkansas 2 | 09/07/2009 | 11/06/2009 | ML09309068 | <strong>Containment Building Penetration Isolation Valves Open During Core Alterations without Application of Administrative Controls Required by Technical Specifications due to Inadequate Procedure Instructions.</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2009 at approximately 1400 hours, with Unit 2 in mode 6 for refueling, operators discovered that containment penetration isolation valves located on the return line of the Containment Atmosphere Monitoring System were configured such that a direct path existed between the containment atmosphere and the auxiliary building atmosphere and the resulting containment breach was not being administratively controlled as required by Unit 2 Technical Specifications. During the plant shutdown, in preparation for refueling, the system was initially placed in the correct configuration in accordance with the plant cool down procedure. However, subsequent local leak rate testing evolutions required system valve position manipulations and, following the second test affecting this system, the valve alignment was not restored to the required configuration. Core alterations commenced shortly thereafter, placing the unit in a condition prohibited by Technical Specifications. It was determined that the failure to apply proper containment closure controls was caused by inadequate procedure instructions for restoration of the affected system following local leak rate testing. Upon discovery, the system configuration was immediately re-established to comply with the Technical Specification Limiting Condition for Operation and the procedure requirements governing containment closure controls.
3682009003 | Arkansas 2 | 09/08/2009 | 11/05/2009 | ML09309068 | <strong>Steam Generator Tube Exceeding Technical Specification Plugging Criteria Remained in Service During Previous Cycles as a Result of the Failure to Use Proper Independent Verification</strong><br /><i>Abstract:&nbsp;</i>On September 8, 2009, at approximately 0452 CDT, with the plant shutdown in Mode 6, it was discovered during the 2R20 Arkansas Nuclear One Unit 2, "B" Steam Generator (SG) inspection, that a wrong SG tube was plugged during a previous outage. During the Spring 2005 refueling outage (2R17), a SG tube with an identified flaw was plugged correctly on the cold leg end, but the wrong SG tube was plugged on the hot leg end. This condition resulted in Unit 2 operating at power since April 2005 with a SG tube characterized with an approximate 43% through wall defect in violation of the Unit 2 Technical Specification SG tube plugging limit of > 40% through wall. Investigation revealed that the error in plugging was caused by a failure to use proper independent verification. Both the SG tube with the identified flaw and the inadvertently plugged SG tube were removed from service.
3682009004 | Arkansas 2 | 09/20/2009 | 11/19/2009 | ML09324003 | <strong>Emergency Diesel Generator Automatic Actuation While Performing Offsite Power Transfer Testing Due to a High Resistance Contact Supplying Voltage to a Synchronizing Check Relay.</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2009, at approximately 0511 Central Daylight Time, during the performance of planned surveillance testing, the 2K-4A Emergency Diesel Generator automatically started due to an undervoltage signal. An Offsite Power Transfer Test was being performed to test the automatic transfer from the Startup 3 Offsite Transformer (SU3) to the Startup 2 Offsite Transformer (SU2). When the test was initiated, a slow transfer of the Red Train 4160 Volt Electrical Bus 2A1 from SU3 to SU2 occurred instead of the expected fast transfer. The slow transfer of the 2A1 Bus resulted in a momentary loss of power, for approximately two seconds, to the Red Train 4160 Volt Safety Electrical Bus 2A3 which is powered from the 2A1 Bus. The undervoltage condition on the 2A3 Bus caused the 2K-4A Emergency Diesel Generator to auto start as designed, but did not power the 2A3 Bus, since the 2A3 Bus was successfully powered from the 2A1 Bus after the slow transfer completed. The cause of this event was attributed to a high resistance contact on a contact block located in the SU2 to 2A1 Bus Feeder Breaker. This high resistance contact interfered with the voltage supply to the 2A1 Bus Synchronizing Relay, resulting in the slow transfer of the 2A1 Bus. The wiring located on the high resistance contact was subsequently moved to an alternate available contact on the subject contact block with appropriate resistance.
3682009005 | Arkansas 2 | 12/08/2009 | 02/02/2010 | ML10033117 | <strong>Manual Reactor Scram and Emergency Feedwater Automatic Actuation due to an Unexpected Plant Response following the Loss of a Main Feedwater Pump at Full Power</strong><br /><i>Abstract:&nbsp;</i>On December 08, 2009, at 0837 Central Standard Time (CST), Arkansas Nuclear One, Unit 2 (ANO-2) was operating near 100 percent power when the 'A' Main Feedwater Pump (MFWP) was manually tripped in response to high thrust bearing temperature. The Loss of MFWP Abnormal Operating Procedure (AOP) was executed. A manual Reactor trip was initiated when the 'A' Steam Generator (SG) water level decreased to approximately 27 percent. The Emergency Feedwater (EFW) system automatically actuated at the designed setpoint of 22.2 percent to restore SG levels. The Loss of MFWP AOP contained instructions which limited the Main Turbine load reduction rate (plant power reduction rate) that was necessary to recover SG water levels prior to reaching the EFW automatic actuation setpoint. The ANO-2 plant simulator response had previously indicated that SG levels could be recovered following the loss of a MFWP from full power without requiring a Reactor trip. Following the subject event, the plant simulator software was revised to incorporate observed plant data. The Loss of MFWP AOP was revised to provide a mitigation strategy based on actual plant response data, and was validated using the revised ANO-2 plant simulator model. After replacement of the 'A' MFWP thrust bearing, ANO-2 returned to near full power on December 13, 2009, at approximately 1813 CST.
3692009001 | McGuire 1, McGuire 2 | 04/27/2009 | 06/24/2009 | ML09182032 | <strong>Nuclear Service Water System (NSWS) "A" Trains Past Inoperable When Aligned to the Standby Nuclear Service Water Pond (SNSWP) due to Corrosion</strong><br /><i>Abstract:&nbsp;</i>Unit Status: Unit 1 and Unit 2 were in Mode 1 at 100% power. Event Description: On April 27, 2009, the Unit 1 "A" (1A) and Unit 2 "A" (2A) NSWS Trains suctions were realigned to the SNSWP, the automatic backwash function of the strainers upstream of the pumps was disabled and the pumps were declared inoperable as prerequisites to perform testing. During the test, unexpected fouling of the 2A NSWS Strainer was caused by corrosion products which collected on the strainer and resulted in reduced 2A RN train flow rate. A subsequent evaluation of this condition determined operator actions specified for strainer fouling were not considered time critical and would not have assured previous "A" Train NSWS pump operability for loss of Instrument Air events and "A" Trains pump suction are also manually realigned to the SNSWP. Event Cause: Corrosion products accumulated on the surface of the "A" Trains SNSWP pump suction header piping due to an inadequate frequency, duration and flow rate specified in the periodic flush procedure. Corrective Actions: Immediate action was taken to assure "A" Trains NSWS operability if "A" Train is required to be manually aligned to the SNSWP. Action will be taken to revise the flush procedure.
3702009001 | McGuire 2 | 09/29/2009 | 11/24/2009 | ML09335052 | <strong>Failure to Comply with the Requirements of TS 3.4.12, LTOP System, due to a Safety Injection Pump Not Double Isolated from the RCS During ESF Test Alignment</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event Unit 2 was in Mode 6 at 0% power and Unit 1 was in Mode 1 at 100% power. Event Description: On September 29, 2009, while aligning for the Unit 2B Train Engineered Safety Features (ESF) Actuation test, Technical Specification 3.4.12, "Low Temperature Overpressure Protection System (LTOP)," was violated by having two Safety Injection pumps and one Charging pump capable of injecting into the Reactor Coolant System (one Safety Injection pump was not double isolated from the Reactor Coolant System). Sequencing of tasks was not controlled such that the breaker for 2B Safety Injection pump was racked in prior to having the pump double valve isolated as required by the Technical Specification. Event Cause: The Removal and Restoration Lift for Test document developed for the ESF test alignment failed to specify the correct sequence for racking in the 2B Safety Injection pump breaker, contrary to the direction provided in the Engineered Safety Features Actuation Test procedure. Corrective Actions: Revise the Safety Tagging process to ensure compliance with the LTOP Technical Specification 3.4.12 prior to racking in the LTOP pump breakers and that manipulations shall be directed by procedure. In addition, develop signage to place on the LTOP pump breakers stating manipulation shall be directed by procedure.
3732009001 | LaSalle 1, LaSalle 2 | 05/21/2009 | 07/20/2009 | ML09202017 | <strong>Automatic Reactor Scram Due to Failure of Main Power Transformer Surge Arrestor</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2009, at 1635 CDT, LaSalle Unit 1 automatically scrammed from 100% power. The scram was due to a generator lockout signal caused by a failure of the surge arrester on the 'A' phase of the Unit 1 West Main Power Transformer (1W MPT). The safety significance of this event was minimal. All control rods fully inserted, all systems responded as expected to the scram, and Emergency Core Cooling Systems were not challenged. The voltage transient caused by the arrestor failure resulted in a number of invalid alarms and isolations on both Units. The cause of the surge arrester failure was determined to be a manufacturing defect. Corrective actions included verifying that the 1W MPT had not been damaged by the event, and replacing the failed surge arrester. Additionally, future procurements of station surge arresters will require that the vendor supply the test data.
3732009002 | LaSalle 1 | 07/20/2009 | 09/18/2009 | ML09272086 | <strong>Loss of Shutdown Cooling due to Spurious Closure of the Shutdown Cooling Suction Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2009, LaSalle Unit 1 was in Mode 4 Cold Shutdown. At 1448 CDT the inboard shutdown cooling suction isolation valve (1E12-F009) unexpectedly closed, causing a trip of both the 1A and 1B Residual Heat Removal (RHR) pumps and a loss of shutdown cooling. Control room operators entered the appropriate abnormal procedures, reopened 1E12-F009, and restarted the 1A RHR pump at 1500 CDT thereby restoring shutdown cooling. The safety consequences of this event were minimal. Shutdown cooling was restored within 12 minutes and reactor coolant temperature rose 12 degrees F. Both Reactor Recirculation (RR) pumps were running during the event, so forced coolant circulation was maintained. The root cause analysis determined that the cause of the spurious closure of the shutdown cooling isolation valve was high contact resistance on Agastat relay 1B21H-K77 in the shutdown cooling suction high flow isolation logic. Corrective actions included replacing the faulty relay, and scheduling other relays of this model in the shutdown cooling isolation logic for replacement.
3742009001 | LaSalle 2 | 08/15/2009 | 10/14/2009 | ML09294071 | <strong>Main Turbine Trip and Reactor Scram due to Digital Electro-hydraulic Control Circuit Card Failure</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2009, at 1606 hours (CDT), Unit 2 was at 100% power performing weekly. Main Turbine overspeed surveillance testing. During the surveillance, the Main Turbine unexpectedly tripped on an overspeed signal from the Digital. Electro-Hydraulic Control (DEHC) system, causing a reactor scram, The safety significance of the event was minimal. The speed of the Main Turbine was confirmed to have been normal at the time of the trip. All control rods fully inserted, and all systems responded as expected to the scram. The cause of the Main Turbine trip was a failed communication chip on the VCMI card in the DEHC system. The root cause of the event was the failure to adequately understand the impact of a diagnostic alarm from the VCMI card, due to a lack of Vendor information. The failed card was replaced. Other corrective actions include a review of all DEHC alarms to determine their potential impact on plant operations, and revising the DEHC alarm procedures appropriately.
3742009002 | LaSalle 2 | 10/12/2009 | 12/11/2009 | ML09356084 | <strong>Completed Plant Shutdown Due to Unidentified Leakage in Excess of Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2009, at 2333 CDT, unidentified leakage on LaSalle Unit 2 exceeded the Technical Specification (TS) Limiting Condition for Operation 3.4.5.d limit of less than or equal to a two gallon per minute increase in the previous 24 hour period while in Mode 1. Required Action (RA) B.1 requires that the increase in unidentified leakage be reduced below the limit within four hours. If RA B.1 can not be met, RA C.1 and C.2 require that the unit be in Mode 3 within 12 hours and Mode 4 within 36 hours. A plant shutdown was commenced at 0300 hours on October 12, 2009, and Mode 4 was reached at 0005 hours on October 13, 2009. The unidentified leakage was determined to be from a packing leak on the Inboard Main Steam Isolation Valve Drain Line Isolation Valve (2B21-F016). The packing leak was repaired and the unit was restarted on October 14, 2009. Corrective actions to prevent recurrence include training maintenance personnel on the different types of gaskets used on pressure seal valves, and revisions to the subject maintenance procedures.
3822009001 | Waterford 3 | 05/30/2008 | 04/27/2009 | ML09119030 | <strong>3.0.4 Violation: Mode Change with an Inoperable Emergency Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>This LER reports a condition prohibited by Technical Specification when a mode change was made with one of three required Emergency Feedwater (EFW) Pumps unknowingly inoperable. On May 30, 2008, at 0824, Waterford 3 entered MODE 3 with Emergency Feedwater Pump AB inoperable due to a lifted lead on the EFW pump governor valve control system. The mode change was not in conformance with LCO 3.0.4 which precludes entry in a mode or other specified condition in the Applicability statement when an LCO is not met and the ACTION requires a plant shutdown if the LCO is not met within a specified interval. LCO 3.7.1.2 requires three Emergency Feedwater Pumps to be OPERABLE in Modes 1, 2, and 3. Emergency Feedwater Pump AB has a 72 hours Allowed Outage Time (AOT) with a required plant shutdown per Technical Specification 3.7.1.2 ACTION d. There have been no previous similar licensee events reported in the last three years.
3822009002 | Waterford 3 | 05/22/2008 | 10/20/2009 | ML09295033 | <strong>Voluntary Report: Shortened Service Life of Station Battery 'B' due to Manufacturing Impurities</strong><br /><i>Abstract:&nbsp;</i>This is a voluntary LER to report an issue of generic interest. During Refuel 15, Station Battery 'B' [EJ] was disconnected from the bus to perform testing. On 5/16/2008, at approximately 20:00 hours, a performance test on the battery showed that battery capacity was at 86.25% of the manufacturer rating. Since the average of previous performance tests was 103.7%, a degraded battery was indicated based on the capacity dropping more than 10% from its average. Station Battery 'B' was manufactured by C&D Battery and was installed in . October 1992. The rated service life of the battery is 20 years. The battery had been in-service, for 15.6 years prior to the performance test on 5/16/08. A confirmatory performance discharge test on 5/22/2008 revealed the battery. had prematurely aged and required replacement. Measured capacity on 5/22/2008 was 71.67%. Although not applicable in modes 5 or 6, Technical Specification Surveillance Requirement (SR) 4.8.2.1.e requires battery capacity be at least 80% of the manufacturer's rating. The plant was in Mode 6 with the Station Battery 'B' disconnected from the plant from 5/16/2008 until replaced with new LCR-33 cells manufaCtured by C&D Battery on 5/24/2008. A Root Cause Evaluation could not determine the cause for the Station Battery 'B' prematurely aging because the Battery Cells were disposed of prior to analysis.
3822009003 | Waterford 3 | 02/22/2010 | 04/29/2010 | ML10123032 | <strong>Multiple Tyco Relay Failures</strong><br /><i>Abstract:&nbsp;</i>This is a Licensing Event Report (LER) to identify a 10CFR21 issue of generic interest. There have been two additional failures of Tyco relay model E7024PB with date codes that had not previously failed since LER 2009-003-00 was submitted. Waterford 3 has observed a higher than expected failure rate of normally energized Tyco model E7024PB electro-pneumatic time delay relays produced since 2007. Seven of the eight failures were observed on 2007 or newer date code relays and one was observed on a 2004 date code relay. The early-in-life failures have been observed on Tyco model E7024PB relays designed as an Off-Delay, 4 pole double throw, 125VDC operating coil, with a time delay range of 0.5 to 5 seconds. All failed relays were replaced. Post failure bench testing at Waterford 3, Tyco, or independent Failure Analysis has not consistently repeated the failures.
3822009004 | Waterford 3 | 07/05/2009 | 12/11/2009 | ML09348049 | <strong>Condition prohibited by Technical Specification with Log Power Channel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 10/15/09, Waterford 3 discovered Technical Specification (TS) 3.3.1 requirements of Table 3.3-1, note C, were not met with logarithmic power inoperable. The Reactor Protection System (RPS) trip channel bistable for Reactor Coolant System (RCS) Flow Low was not bypassed or placed in tripped condition within one hour when the associated RPS channel Logarithmic (Log) Power Excore Nuclear Instrumentation (ENI) was rendered INOPERABLE. This condition is reportable under 10 CFR 50.73(a)(2)(i)(B), resulting from the operation or condition prohibited by Technical Specification which exceeded the Limiting Condition for Operation (LCO) allowed outage time. The cause was determined to be inadequate interpretation and wording of the TS requirements associated with TS Table 3.3.-1.
3822009005 | Waterford 3 | 10/19/2009 | 05/13/2010 | ML10137022 | <strong>Spurious Moisture Separator Reheater Relief Valve Opening Resulting in a Manual Reactor Trip and an Engineering Safety Feature Actuation (Emergency Feedwater Actuation)</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2009, at approximately 09:44 with the plant operating at 100% power (Mode 1), Waterford 3 manually tripped the reactor due to lowering condenser hotwell level caused by a stuck open moisture separator reheater relief valve. The Plant Protection System (PPS) responded as designed, resulting in an uncomplicated reactor trip. Subsequently, Emergency Feedwater Actuation Signals (EFAS-1 and EFAS-2) were received due to low Steam Generator (SG) levels which is an anticipated response to the reactor trip with the plant at or near full power. The emergency feedwater system did not receive a signal to send water to the steam generators. The plant was then maintained in Mode 3 with both steam generators being fed from the main feedwater system with steam generator levels in the normal operational band for Mode 3. Failure Mode Analysis (FMA) identified a broken pilot valve spring on the stuck open moisture separator heater relief valve. The pilot valve spring was replaced on all six moisture separator heater relief valves prior to unit restart. Adequate water level was maintained in the steam generators to ensure decay heat removal from the Reactor Coolant System (RCS). The event is not considered a safety system functional failure. The event did not compromise the health and safety of the general public.
3822009006 | Waterford 3 | 10/22/2009 | 02/25/2010 | ML10057041 | <strong>Degraded Hydraulic Fluid Causes Both Main Feedwater Isolation Valves to Fail Inservice Test Stroke</strong><br /><i>Abstract:&nbsp;</i>On 12/28/2009, it was established that inservice test (IST) failures that occurred on 10/22/2009 on both Main Feedwater Isolation Valves (MFIVs) had a common cause and could have prevented the fulfillment of the MFIVs safety function needed to mitigate the consequences of an accident. The plant operated in a condition prohibited by Technical Specification 3.7.1.6, which requires both MFIVs to be operable in Modes 1 through 4. Surveillance requirement 4.7.1.6 requires the closure time of less than or equal to 5 seconds. Both MFIVs use hydraulic actuators, and each contains two separate hydraulic trains. An actuation signal results in both trains closing the valve. While in Mode 5 with Reactor Coolant System temperature and pressure at approximately 170 degrees F and 350 psia, IST testing using one of their hydraulic trains resulted in MFIV A closing in 12.6 seconds, and MFIV B failing to close. The maximum allowed stroke time for the IST is 7.56 seconds. The MFIV tests using their other hydraulic trains were satisfactory. The Apparent Cause Evaluation determined that moisture intrusion during a previous plant shutdown likely caused gel to form, restricting flow in the affected four way valves. Corrective action included replacing the hydraulic fluid. Planned corrective action is to replace the hydraulic fluid prior to plant startup in which moisture could exist in the fluid.
3872009001 | Susquehanna 1 | 08/18/2009 | 10/16/2009 | ML09302011 | <strong>High Pressure Coolant Injection System Inoperable due to Turbine Stop Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2009, the Unit 1 High Pressure Coolant Injection (HPCI) turbine stop valve FV-15612 showed dual position indication following the performance of the weekly HPCI lube oil system preventive maintenance functional test. The stop valve should have indicated full closed at this time. Investigation confirmed that the valve stem was not in the full closed position. This is significant because the HPCI ramp generator will not reset if the stop valve is not fully closed. Without a functioning ramp generator, the HPCI system would likely experience 1 or 2 overspeed trips before the governor could successfully control turbine speed. At 0920 on August 18, 2009, the Unit 1 HPCI system was declared inoperable. The NRC was notified (via ENS 45273) in accordance with 10 CFR 50.72(b)(3)(v)(D) for an event or condition that could have prevented the fulfillment of a safety function required to mitigate the consequence of an accident. The cause for the failure of the stop valve to fully close was due to general corrosion of the actuator piston bushing. This resulted in mechanical interference which inhibited stop valve movement. The cause of the accelerated corrosion in the area of the stop valve actuator piston was due to chronic through-seat leakage from the HPCI steam supply admission valve. The stop valve was subsequently repaired and the Unit 1 HPCI system was declared operable on August 24, 2009. The seat leak on Unit 1 HPCI steam admission valve HV-155F001' will be repaired during the next Unit refueling outage. During the next scheduled Unit 2 HPCI system outage, the corroded parts on the Unit 2 HPCI stop valve will be replaced. There were no actual adverse consequences to the health and safety of the public as a result of this event.
3882009001 | Susquehanna 2 | 04/29/2009 | 10/12/2009 | ML09296027 | <strong>Multiple Test Failures of Main Steam Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>During the Susquehanna Unit 2 14th Refueling and Inspection Outage, three (3) Main Steam Safety Relief Valves (SRVs) failed to meet the setpoint criteria of +/- 3% set forth in Technical Specification 3.4.3. All three SRVs actuated at a setpoint less than the -3% criteria. The cause of the lower setpoint actuation is attributed to drift. This event was determined to be a Common-Cause Inoperability of Independent Trains or Channels and reportable under 10 CFR 50.73(a)(2)(vii). The SRVs remained functional and the Technical Specification required number of SRVs (12) remained operable. There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
3882009002 | Susquehanna 2 | 04/28/2009 | 10/26/2009 | ML09308013 | <strong>Emergency Service Water Cooling Valves Found Closed Resulting in the Unit 2 'C' Residual Heat Removal Pump being Inoperable for Approximately 4 Months</strong><br /><i>Abstract:&nbsp;</i>On August 25, 2009, while performing pre-start checks to place Unit 2 Residual Heat Removal (RHR) loop in Suppression Pool Cooling, a field operator identified that Unit 2 Emergency Service Water (ESW) cooling valves 211193 and 211194 were unlocked and in the closed position. These valves, which supply ESW cooling water from the 'B' ESW loop to Unit 2 'C' RHR pump unit cooler and motor oil cooler, are required to be locked open. Investigation revealed that ESW cooling valves 211193 and 211194 were closed on April 28, 2009, following restoration of a clearance order associated with a modification to install new stainless steel and cross-tie piping from the 2C motor cooler to the 'A' loop of ESW. 'Because the valves had been closed since April 28, 2009, the Unit 2 'C' RHR pump was rendered inoperable for approximately 4 months. As such, TS LCO 3.5.1, action statements were not met. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), for a condition prohibited by Technical Specifications. The cause of the event was human performance error by station personnel for failure to follow the guidance in procedure NDAP-QA-0302. This resulted in a loss of status control for ESW cooling valves 211193 and 211194 for a period of 4 months. Corrective actions taken included verification that all Unit 1 and 2 locked open ESW valves going to any ECCS equipment were in the correct position. A written communication was provided to all operators regarding this event. Planned corrective actions include incorporating procedure NDAP-QA-0302 into annual pre-outage training for all operators. The actual consequence of this event is the Unit 2 'C' RHR pump was inoperable for approximately 4 months, which resulted in TS LCO 3.5.1 action statement not being met. The potential consequences, given the worst case single failure for the ESW and RHR Service Water (SW) systems is that with no cooling water to the Unit 2 'C' RHR pump unit cooler and motor cooler, the pump would be expected to eventually fail resulting in SSES not having the minimum ECCS equipment required for long term cooling of Unit 2.
3892009001 | St. Lucie 2 | 03/19/2009 | 04/08/2009 | ML09110039 | <strong>Unit 2 Main Feedwater Isolation Valves Stroke Time Potentially Affected by Temperature</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2009, St. Lucie Unit 2 was operating in Mode 1 at 100% power when the Onsite Review Group (ORG) concluded the Seabrook Station' s Operating Experience Report "Adverse Effect On Feed Water Isolation Valve Stroke Test Due To Unusual Conditions Encountered During A Forced Outage," identified on December 18, 2008, was a reportable condition for St Lucie Unit 2. A review of available plant data and documents determined that St. Lucie Unit 2 main feedwater isolation valves (MFIVS) stroke times could potentially not meet plant technical specification (TS) of 5.15 seconds if the temperature of the hydraulic fluid in these valve actuators falls below 60 ° F. An evaluation of available vendor data concluded the inability to meet TS closure times could result from increased hydraulic fluid viscosity caused by low ambient teinperatures . Contributing factors included inadequate design specification, operating procedures, and latent design weaknesses .. Immediate corrective actions included monitoring ambient temperature in the steam trestle. Longer term corrective actions included MFIV replacement and shiftly temperature checks.
3892009002 | St. Lucie 2 | 04/01/2009 | 06/01/2009 | ML09160036 | <strong>Ingress of Algae Results in Manual Trip of St. Lucie Unit 2</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2009, St. Lucie Unit 2 was operating in Mode 1 at 94% power when Unit 2 experienced a continuing reduction of condenser vacuum and an increase in the debris filter system (DES) differential pressure resulting from the ingress of algae from the Atlantic Ocean into the intake canal. Previous attempts to control the debris were unsuccessful and Unit 2 was manually tripped at 92% power at 18:05 in accordance with Off-Normal Operating Procedure 2-0620030, "Circulating Water System". All systems functioned normally, and the plant was stabilized at normal operating temperature and pressure. A non-emergency notification was made to the NRC at 20:51, April 1, 2009. There was no impact on Unit 1. The loss of vacuum was caused by a greater than expected influx of a unique strain of algae which challenged the debris filter screening system and current design of the weir pit which allows recirculation of debris back into the intake canal. Corrective actions taken include a daily Staff Biologists' analysis of biota entering the intake canal with reports provided to the Shift Manager, actions to review weir design, preventive maintenance and cleaning of the weir pit, and development of a new procedure for Intake Intrusion Mitigation.
3892009003 | St. Lucie 2 | 07/13/2009 | 03/22/2011 | ML11095036 | <strong>RCP 2B2 Lower Seal Cavity Line Leak</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2009 at 21:32, St. Lucie Unit 2 was in Mode 1 at 100% power when the reactor was down powered and manually tripped (on July 13 at 00:38), in accordance with plant rapid down power procedures, due to an increasing trend in reactor coolant system (RCS) unidentified leakage rate. The RCS leak source was identified as a cracked weld where lower cavity seal line I-3/4"-RC-228 connects to the 2B2 RCP seal cartridge. The J- weld was cut from the RCP seal housing and metallurgical failure analysis was performed. The analysis concluded the failure mechanism was outside diameter (OD) initiated, low stress high cycle fatigue caused by resonance vibration. The analysis did not identify any original welding or material deficiencies as contributors to the failure. Corrective actions include replacing cracked seal housing; cutting and capping the RCP seal lines susceptible to resonance vibration, including seal injection on all four RCPs and the upper seal cavity lines on two RCPs; installation of additional vibration monitoring equipment on seal piping on three of the four St. Lucie Unit 2 RCPs; and as a long term corrective action, eliminate RCP seal injection and remove the vibration-vulnerable piping.
3892009004 | St. Lucie 2 | 09/21/2009 | 11/19/2009 | ML09328085 | <strong>Unit 2 Unplanned Manual Reactor Trip During Reactor Startup</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2009, St. Lucie Unit 2 was performing a plant startup following a 2B2 Reactor Coolant Pump maintenance outage. St. Lucie Unit 2 was entering Mode 2 at 1325 EDT when a Control Room Operator noted that primary safety valve (PSV) V1202 had indications of seat leakage based on increasing tailpipe temperatures. At 1333 on 9/21/09, the Control Room operators observed V1202 tailpipe temperature increase to approximately 224 °F coincident with a quench tank pressure increase from 4.0 psig to 4.4 psig. Subsequently, the Unit Supervisor ordered a manual reactor trip in accordance with plant procedures. Note that the reactor had not yet achieved criticality. The PSV's seat leakage was a result of the valve not achieving thermal stability early enough to resist the increasing pressure loading. Contributing causes included gas management during the startup process, missing pressurizer nozzle insulation, and procedure deficiencies. Corrective actions included configuration changes to the PSV discharge piping, and procedure revisions to address start up rates and PSV thermal stability.
3902009001 | Watts Bar 1 | 05/27/2009 | 07/27/2009 | ML09210068 | <strong>Inoperability of Aux Bldg Gas Treatment System due to Inadequate Surveillance and Breach of ABSCE Boundary</strong><br /><i>Abstract:&nbsp;</i>On 5/27/09, TVA identified that the Watts Bar Nuclear Plant (WBN) Unit 1 Auxiliary Building (AB) Gas Treatment System (ABGTS) pressure test surveillance instruction was inadequate, as closed nonsafety related dampers could mask leakage through credited safety related dampers in the AB Secondary Containment Enclosure (ABSCE). AB General Ventilation manipulation to place WBN in a known tested condition created a pressure differential that caused failure of temporary ABSCE boundary doors installed to facilitate Unit 2 construction. WBN entered LCO 3.7.12 Condition B for 2 trains of ABGTS inoperable. TVA repaired the boundary, and the LCO Condition was exited in approximately 3.5 hours. Subsequently, TVA retested ABGTS, and both trains were verified as operable. From initial licensing until 5/27/09, WBN operated in noncompliance with TS because of the inadequate surveillance instruction. On 6/27/09, another AB General Ventilation manipulation created a pressure differential that caused the temporary doors to fail once again. One temporary door and a permanent steel door are now closed to ensure boundary operability. Failures of the temporary doors were due to an inadequate design and insufficient interim actions after the first event to prevent another failure. This event is reported in accordance with 10 CFR 50.73 (a)(2)(i)(B) and (a)(2)(v)(C) and (D).
3902009002 | Watts Bar 1 | 07/17/2009 | 09/15/2009 | ML09259026 | <strong>Emergency Diesel Generator Actuation due to Loss of Power to 6.9 kV Shutdown Board</strong><br /><i>Abstract:&nbsp;</i>The event in this LER occurred on July 17, 2009, while the unit was at 100% power. The plant was in Technical Specification (TS) 3.8.1, "AC Sources - Operating," Condition A for one offsite circuit being inoperable. The Common Station Service Transformer (CSST) D had been removed from service to perform corrective maintenance. In support of this maintenance the 2B-B Shutdown Board had been aligned to the alternate power supply. While returning the alignment to normal configuration, a start signal was sent to the diesel generators. This signal was caused by a misalignment of the alternate supply breaker's actuation arm and microswitch. The cause for the installation with misalignment of the actuation arm was a lack of vendor manual criteria and thus site maintenance procedures to perform adjustment of the actuation arm in relation to the breaker's microswitch. Extent of condition reviews identified one additional breaker to have this misalignment. Both breaker's were replaced with verified spares. All four diesel generators started as expected, and load for the 2B-B Shutdown Board was assumed by the 2B-B Diesel Generator. All safety systems functioned as designed. This condition did not adversely affect the safe operation of the plant or health and safety of the public. This event is reported in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3952009001 | Summer 1 | 08/12/2009 | 10/12/2009 | ML09286061 | <strong>Inadequate Procedure Results In EDG Not Obtaining Maximum Load Required By Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2009 the "B" Emergency Diesel Generator (EDG) could not be operated at maximum load within the Technical Specification (TS) range of 4600-4700 kilowatts (kW). The 18 month surveillance was being performed to operate the "B" EDG continuously for 24 hours with 2 hours required at maximum load. The "as found" loading was determined to be 4575 kW which was just below the TS range. The fuel rack stop had been adjusted during maintenance on March 30, 2008. Since the two hour loading requirement could not be met and may have existed since the adjustment in 2008, this is a violation of the Limiting Condition for Operation for TS 3.8.1.1. The root cause was determined to be inadequate procedural guidance for setting the fuel rack stop. During previous maintenance, the fuel rack stop had been set too low which did not allow the "B" EDG to be loaded high enough to achieve the required TS range. The low fuel rack stop setting was the result of a prior maintenance procedure revision which did not specify proper indication, did not have a target value and had a non-conservative loading range. The maintenance procedure has been revised to correct the problems and verify proper fuel rack stop setting.
3952009002 | Summer 1 | 10/02/2009 | 08/17/2010 | ML10232021 | <strong>Automatic Reactor Trip due to a Main Generator Output Breaker Fault</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2009, at approximately 0649 hours, the plant was operating in Mode 1 at 100% power when the reactor automatically tripped due to a main turbine trip. The turbine trip was initiated by a main generator stator ground. All systems responded as required. The emergency feedwater pumps automatically started on low-low steam generator level as expected. The plant stabilized in Mode 3 and remained in Mode 3 until repairs were complete. The cause of the stator ground was determined to be a failure in the 'B' phase of the main generator output breaker. The 'B' phase contact was found to be damaged. Damaged parts were sequestered for investigation and further analysis. After an extensive analysis by the root cause team and the breaker vendor, the root cause of the 'B' phase failure could not be conclusively determined. An independent assessment by external consultants was also inconclusive. Due to obsolescence of the main generator output breaker and difficulties experienced while procuring replacement parts during the breaker repair effort, the main generator breakers are scheduled to be replaced in the next refueling outage.
3952009003 | Summer 1 | 11/20/2009 | 01/19/2010 | ML10021019 | <strong>Potential Loss of Residual Heat Removal System Safety Function in Mode 4 due to an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On 11/20/09, VCSNS determined that there was a potential for operating in an unanalyzed condition due to loss of the safety function of the Residual Heat Removal (RHR) system. VCSNS determined that under certain conditions flashing could occur in the RHR system while in Mode 4. The resulting steam voids could prevent the RHR system from fulfilling its safety function during the injection and recirculation phase of a Loss Of Cooling Accident (LOCA). The condition represents a safety system common cause failure that would affect both trains of RHR in Mode 4 only and is reportable under 10 CFR 50.73(a)(2)(ii)(B), 10 CFR 50.73(a)(2)(v)(B), and 10 CFR 50.73(a)(2)(vii)(B). The apparent cause of this condition was the failure to consider the most limiting boundary conditions when calculating the temperature limit to preclude flashing of the RHR system. Corrective actions consisted of the reanalysis of the limiting temperature to manage system flashing and the revision of operating procedures.
3952009004 | Summer 1 | 12/16/2009 | 02/11/2010 | ML10048012 | <strong>Manual Reactor Trip due to Main steam Dump System Fault</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2009, VC Summer Nuclear Station (VCSNS) was undergoing a planned downpower to repair main turbine control valve #4. As power was being reduced, the main turbine was manually tripped at approximately 46% reactor power due to elevated turbine vibration. Following the turbine trip, the main steam (MS) dump system failed to operate resulting in actuation of MS power operated relief valves (PORVs) and MS safety valves. Due to increased reactor coolant system (RCS) and main steam pressures, a manual reactor trip was initiated at 1415 hours. The plant was stabilized in Mode 3 and remained in Mode 3 until repairs were completed. The cause of the fault in the MS dump system was determined to be a failed circuit card. Upon replacement of the failed circuit card and repair of the main turbine control valve, the plant returned to power operation on December 17, 2009 at 2002 hours.
3972009001 | Columbia | 02/08/2009 | 03/16/2010 | ML10083008 | <strong>Reactor Scram due to Turbine Control System Trip Header Depressurization</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2009 at 1125 hours, an automatic reactor scram occurred while Columbia was operating in Mode 1 at 75% power. The Digital Electro-Hydraulic (DEH) Control System emergency trip header momentarily depressurized during testing following on-line quadvoter valve assembly replacement. A Turbine Governor Valve Fast Closure trip signal was generated and a reactor scram occurred. The direct cause of the event was the introduction of air into the DEH system during quadvoter valve replacement and subsequent compression of the unvented, entrapped air during post maintenance testing. The compression resulted in backflow and excursion of the trip header pressure below the trip setpoint. The root cause is design deficiencies in the on-line serviceable quadvoter assembly which allowed system conditions that resulted in a reactor trip following performance of on-line maintenance activities. Both quadvoter valve assemblies in the affected channel were replaced. Prior to reactor startup, the DEH system was vented and tested to ensure removal of all air. Corrective actions to address quadvoter design deficiencies and to improve quadvoter performance have been pursued. This event did not adversely affect the health and safety of the public. Since the installation of a new DEH system at Columbia in 2007, one similar event was reported by Energy Northwest in LER 2008-001-00.
3972009002 | Columbia | 05/08/2009 | 03/17/2010 | ML10083008 | <strong>Manual Reactor Scram due to Loss of Hydrogen Pressure in the Main Generator</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2009 at 1046 hours, a manual reactor scram was inserted while Columbia was operating in Mode 1 at 87% power. Loss of air side seal oil pressure and consequential loss of hydrogen pressure in the main generator occurred during testing of the seal oil system backup regulator and air side seal oil back up pump. When the backup system was activated, a crud burst of corrosion products from the back up oil supply line and biological growth from the heat exchanger plugged the single in-line filter. This caused a loss of air side seal oil pressure, allowed hydrogen to escape from the generator, and necessitated the manual scram. The process for addressing compensatory measures for the single point vulnerability of the Cuno filter (SO-F-1) was inadequate (Root Cause 1). An ineffective and untimely repair of Seal Steam flange leaks contributed to increased levels of moisture in the air side seal oil system. This resulted in formation of corrosion products and biodegradable material in the seal oil system (Root Cause 2). Interim risk mitigation actions to monitor the in-line filter continuously during backup system operation and seal oil system startup and take actions as necessary are being established in plant operating procedures. The seal oil filter upgrade is scheduled to be implemented during the next refueling outage (R-20). No similar events have been reported by Energy Northwest.
3972009003 | Columbia | 06/26/2009 | 03/16/2010 | ML10083009 | <strong>Manual Reactor Scram due to a Fire Stemming from a Turbine Lube Oil Leak</strong><br /><i>Abstract:&nbsp;</i>At 1949 on June 26, 2009, with Columbia operating at approximately 75% power, a small fire near the #2 high pressure turbine bearing was reported to the main control room. As directed by procedure, a manual scram was inserted at 1952. The in-service turbine lube oil vapor extractor system did not provide enough differential pressure to prevent lube oil from leaking out of the bearing pedestal. The fire occurred when the leaking lube oil came into contact with a hot pipe causing the oil to flash. The root causes were an out of calibration pressure switch and the integrated system knowledge of the main turbine lube oil exhauster system by Operations and Engineering was weak. The pressure switch has been replaced. Additional corrective actions taken to prevent recurrence include revisions to station procedures to ensure that the turbine lube oil vapor extractor system pressure is monitored via independent instruments during routine operator rounds as well as after any system manipulation. In addition, improvements in training for Operations and Engineering are planned to increase overall system knowledge. No similar events have been reported by Energy Northwest.
3972009004 | Columbia | 08/05/2009 | 05/02/2011 | ML11145A11 | <strong>6.9 kV Non-Segregated Electrical Bus Failure</strong><br /><i>Abstract:&nbsp;</i>At 0750 on August 5, 2009, while Columbia was operating at 100% power, an electrical fault on a 6.9 kilovolt (kV) non-segregated bus resulted in a turbine trip and automatic reactor scram. During the scram recovery, the turbine bypass valves remained in the full open position and did not automatically modulate to maintain reactor pressure as expected. The most probably cause of the bus failure is a relaxation of bolted connections on the center phase flexible link(s) caused by repeated thermal cycles over time. The root cause identified for this event was the non-performance of preventive maintenance (PM) tasks for torque checks of the non-segregated bus links. The damaged bus has been repaired, and changes to the controls for PMs will be made to ensure proper performance to prevent this type of failure from recurring. The failure of the bypass valves to control pressure resulted from an error introduced during a design change of the Digital Electric Hydraulic (DEH) system implemented in 2007. As a result, the bypass valves transferred to manual pressure control mode when the pressure transient exceeded the main steam throttle inlet pressure input signal limit for all three channels. The DEH system has been modified to correct the erroneous signal limit, and to retain automatic control of the bypass valves during similar high throttle pressure events. No previous similar events have been reported by Columbia.
3972009005 | Columbia | 11/07/2009 | 01/04/2010 | ML10012045 | <strong>Manual Reactor Scram due to Main Turbine DEH Control System Fluid Leak</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2009, the control room staff had completed a scheduled downpower of Columbia Generating Station to perform maintenance activities. After reaching the targeted power level, a rapid loss of hydraulic fluid from the main turbine digital electro-hydraulic control (DEH) system occurred. This resulted in the initiation of a manual scram of the reactor as directed by plant procedures at 0725. This event meets the reporting requirements of 10 CFR 50.73(a)(2)(iv)(A) for manual actuation of a system described in 10 CFR 50.73(a)(2)(iv)(B)(1). The direct cause for the loss of hydraulic fluid was the failure of an o-ring at the lower mounting block flange of accumulator DEH-TK-1D. This flange was determined to be incorrectly assembled following preventive maintenance performed during the previous refueling outage. The root cause was determined to be that the administrative requirements associated with maintenance on the DEH Accumulators did not impose special verifications, controls, or personal accountability measures to ensure that maintenance is performed appropriately. The affected flange was reassembled with a new o-ring and bolts torqued to recommended values. This event did not adversely affect the health and safety of the public.
4002009001 | Harris | 03/18/2009 | 05/18/2009 | ML09147028 | <strong>Emergency Bus 1A-SA Undervoltage Relay As Found Dropout Voltage Did Not Meet TS Allowable Values</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2009, while Harris Nuclear Plant was operating at full power, a channel calibration was performed on the 6.9 kV Emergency Bus 1A-SA undervoltage relays. During the calibration, two Model 12NGV13 relays did not meet the Technical Specification Allowable Value requirement for dropout voltage. Plant Technical Specification (TS) Table 3.3-3, Loss-of-Offsite Power functional unit, requires a minimum of two operable channels per bus for that channel to be considered operable. If the minimum number of channels is not restored within one hour, the affected diesel generator is declared inoperable. On March 18, 2009, a Reportability Evaluation concluded that the improper setting of the primary undervoltage relays resulted in operation outside TS parameters, a condition prohibited by TS and a reportable event per 10 CFR 50.73. The root cause of this event was determined to be an unavailability of information concerning the effect of relay coil voltage level on dropout setting. A review of procedure and calibration history indicated that prior to mid-1998, relay calibrations were performed with a starting input voltage of ˜120 V applied to the relay coil. From mid-1998 through the 2007 channel calibration, a starting input voltage of 95 V, enough of a voltage level to "reset" the dropout contacts, was applied to the relay coil. However, for the 2009 calibration, the starting input voltage was returned to 120 V applied to the relay coil, reflecting normal plant condition. This link between the relay coil voltage level and dropout setting was confirmed through bench testing after the 2009 calibration. Corrective actions taken were calibration of the affected 1A-SA relays using the correct starting input voltage, verification that the same model 1B-SB relays were calibrated properly and planned testing of the same model relays in other applications with a nominal 120 V starting point. There were no safety consequences impacting plant or public safety as a result of this event. The Emergency Bus 1A-SA undervoltage relay would have performed its required actions upon loss of electrical power, although it would have experienced a delay of approximately 1 millisecond (ms). This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications.
4002009002 | Harris | 10/16/2009 | 12/15/2009 | ML09358002 | <strong>Potential for Residual Heat Removal Trains to be Inoperable During Mode Change</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2009, during a review of Wolf Creek LER 2008-008-002 which addressed potential void formation, a concern with the Harris Nuclear Plant (HNP) Residual Heat Removal (RHR) system during Mode 3 and Mode 4 was identified. During shutdown conditions, HNP typically lines up one or both of the RHR trains to the Reactor Coolant System (RCS) for shutdown cooling and switches them to RHR injection mode of operation prior to entering Mode 3 from Mode 4. During the switchover, system procedures require the RHR system to be cooled down using the mini-flow line through the RHR heat exchanger. The physical location where the mini-flow piping returns to the suction of the RHR system prevents cooling approximately 90 feet of the RHR suction line. The stagnant water in the RHR suction line cools by ambient losses only and can remain high (maximum 350 degrees F) for several hours. The condition with hot water in the RHR suction piping can also occur shortly after initiating RHR Shutdown cooling mode of operation during the cooldown and would exist until RCS temperatures are reduced sufficiently to preclude a concern. Further review of the plant conditions during the last three years show that the RHR system Limiting Condition for Operation (LCO) has not been met eleven times in Modes 4 through Mode 1. The root cause is the original RHR system design and system operating guidance provided by Westinghouse were deficient and have allowed conditions to exist where steam flashing can occur in the RHR shutdown cooling piping and pump suction if the RHR system had to be transitioned to the Emergency Core Cooling System (ECCS) mode for injection and recirculation from the shutdown cooling mode in Mode 4 or soon after transitioning to Mode 3. Immediate corrective actions were to revise plant procedures such that steam void formation in the RHR system would not occur.
4102009001 | Nine Mile Point 2 | 08/23/2009 | 10/22/2009 | ML09302011 | <strong>Momentary Loss of Control Power to High Pressure Core Spray Pump Due to Degraded Fuse Block Connection</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2009, at 0915 hours, the Nine Mile Point Unit 2 (NMP2) control room received a High Pressure Core Spray (HPCS) Inoperable annunciator and a Division 3 Diesel Direct Current Control Power Failure annunciator for one second, after which both annunciators cleared. An operator was immediately dispatched to the Division 3 switchgear room, but did not find any obvious failure. During troubleshooting, a degraded connection was found between the removable and stationary parts of the HPCS breaker CLOSE fuse block. The contact gap for one of the receiver connections internal to the stationary section of the CLOSE fuse block was wider than the other 3 receiver connections. At that point, HPCS was declared inoperable per Technical Specification 3.5.1. The degraded receiver connection was adjusted and the CLOSE fuse block was reassembled. The HPCS pump was run and subsequently declared operable at 2046 hours. Throughout the event, NMP2 continued to operate at 100% power. There were no other inoperable components impacting this event. The apparent cause of this event was failure to incorporate a GE Service Advisory Letter (SAL) 322.1 recommendation for checking the fuse block contact wipe or contact gap settings as part of the 4.16 kV breaker Preventive Maintenance (PM). To prevent reoccurrence, the procedures for the 4.16kV and 13.8 kV breaker PMs will be revised to include the fuse block contact gap adjustment.
4122009001 | Beaver Valley 2 | 08/19/2009 | 10/15/2009 | ML09295034 | <strong>Equipment Operability for Steam Generator Tube Rupture Safety Analysis Not Met</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2009, Beaver Valley Power Station (BVPS) Unit 2 discovered that a combination of two inoperable same-train components could invalidate the design basis accident safety analysis, even though applicable Technical Specification Required Actions are being met. Specifically, if one Emergency. Diesel Generator and one of the four Atmospheric Steam Dump Valves are not available with no other postulated single failures, Engineering has determined that the time frame for Reactor Coolant System depressurization would be extended during a postulated Steam Generator Tube Rupture design basis accident. As a result, the ruptured steam generator could overfill. Maintaining a steam bubble in the secondary side of a ruptured steam generator ensures that a large portion of any radioactive iodine will be partitioned (i.e., contained) within the secondary water and not released to the environment when secondary steam is released. This partitioning is a safety function credited in the licensing basis safety analysis. This specific plant configuration occurred within the last 3 years, which could have prevented the fulfillment of the safety function of a structure or system that is needed to control the release of radioactive material; or mitigate the consequences of an accident. This is reportable per 10 CFR 50.73(a)(2)(v)(C) and 10 CFR 50.73(a)(2)(v)(D). The root cause of this event was an inadequate design basis review during original plant design (legacy item) which resulted in minimal design capacity with respect to Steam Generator Tube Rupture overfill. Subsequently identified issues made it necessary to rely on cross-train components to meet safety analyses assumptions. The safety significance of these plant configurations is very low.
4122009002 | Beaver Valley 2 | 10/23/2009 | 12/21/2009 | ML09364005 | <strong>Unacceptable Indications Identified During Reactor Vessel Head Inspection</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2009, during the Beaver Valley Power Station (BVPS) Unit No. 2 refueling outage (2R14), it was determined that the results of planned ultrasonic (UT) examinations performed on two penetrations of the reactor vessel head would not meet the applicable acceptance criteria. The indications are not through wall and there was no evidence of leakage based on inspections performed on top of the reactor vessel head. The reactor vessel head examinations were being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) for reactor vessel head inspections to find potential flaws/indications well before they grow to a size that could potentially jeopardize the structural integrity of the reactor vessel head pressure boundary. Pursuant to NUREG 1022, Rev. 2, indications that cannot be dispositioned as acceptable per ASME Code Section XI in a Reactor Coolant System pressure boundary are reportable under 10 CFR 50.72(b)(3)(ii)(A) / 50.73(a)(2)(ii)(A) as a condition of the nuclear power plant, including its principal safety barriers, being degraded. Primary Water Stress Corrosion Cracking (PWSCC) of the Alloy 600 J groove weld is the basic cause of the identified failure. Reactor head penetrations No. 49 and 57 were repaired in accordance with the applicable embedded flaw repair methodology which was approved by the Nuclear Regulatory Commission. The safety significance of these indications was very low.
4132009001 | Catawba 1 | 01/30/2009 | 04/01/2009 | ML09096030 | <strong>Both Trains of Chemical and Volume Control, Auxiliary Feedwater and Containment Spray Systems were Inoperable Due to a Component Failure</strong><br /><i>Abstract:&nbsp;</i>On January 30, 2009, with Unit 1 operating in Mode 1.at 100% power, 1RN-291 (Component Cooling System (KC) Heat Exchanger 1A Nuclear Service Water System (RN) Control Valve) failed to control flow to lA KC Heat Exchanger. The Valve was indicating open on the Operator Aid Computer (OAC); however, the expected increase in flow through the.heat exchanger was not obtained when the operational mode of the valve was changed. Train lA of KC was declared inoperable. A review of OAC data revealed that valve 1RN-291 had failed on January 28, 2009. During this timeframe, Train lA of KC was unable to provide a heat sink- for various systems that are essential to the mitigation of design basis events. Additionally, between January 28 and January 30, Train 1B of Chemical and Volume Control, Containment Spray, and Auxiliary Feedwater Systems were taken out of service to perform maintenance activities; therefore, both trains of these systems were inoperable at some point during this time period. The event is attributed to the failure of the Rod End Bearing Assembly of valve 1RN-291. The valve was repaired and Train lA KC was declared operable. This event did not adversely affect the health and safety of the public. This report involves a safety system functional failure.
4162009001 | Grand Gulf 1 | 02/25/2009 | 04/23/2009 | ML09114033 | <strong>Containment Isolation Valves Placed in Service after Maintenance without Administrative Controls Due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2009 maintenance was completed on two Residual Heat Removal Primary Containment Isolation Valves (PCIVs). The PCIVs were returned to service before the required Technical Specification (TS) 5.5.6 Inservice Testing Program stroke time tests were performed to confirm operability. The PCIVs should have been placed under administrative controls or isolated per TS 3.6.1.3 Required Action (RA) A.1 within 4 hours. TS 3.6.1.3 RA E.1 requires entry into Mode 3 within 12 hours if A.1 is not met. Neither PCIV was tested within the combined 16 hour RA completion times of TS 3.6.1.3. A condition prohibited by TS existed for both valves. The cause of this event was failure to correctly follow procedure and inadequate work order verification. Control Room personnel did not follow station procedure for entering separate Limiting Conditions for Operation when prepared for multiple components within the same TS. One LCO was entered for both PCIVs and the RHR A system. Both Control Room and Outage Control Center personnel misinterpreted the work order tasks as cancelled resulting in the retest being marked not applicable. There is no safety consequence associated with this event. Operations management initiated a standing order to ensure retest and TS / LCO requirements are reviewed by additional crew Senior Reactor Operators during LCO and tagging activities.
4162009002 | Grand Gulf 1 | 05/05/2009 | 07/02/2009 | ML09183126 | <strong>Emergency Diesel Generator Actuation Caused by a Degraded DC Control Battery</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2009 at 2327 hours Central Daylight Time, Grand Gulf Nuclear Station was in Mode 1 operating at approximately 100 percent power when a valid Engineered Safety Feature (ESF) actuation of the Division 1 Emergency Diesel Generator and Standby Service Water A occurred. The actuation occurred due to a degraded voltage condition on ESF Transformer 12 which initiated a Load Shed and Sequence on the 15AA bus, which required the EDG to start and supply AC power to the bus. The cause of the ESF actuation was a 90% bus undervoltage condition that lasted for greater than nine seconds due to feeder breaker 5X01 and main breaker 5X22 failing to open and clear a fault on over current in the required 3 to 5 cycles. The feeder breaker and main breaker did not open due to low DC control voltage which was caused by a degraded 48 VDC battery bank. The battery bank (24 cells) was inspected and found to have visual cell damage in one cell. Additional cell testing was performed on the battery bank and two of the tested cells were found to have unsatisfactory results. The degraded 48 VDC battery bank was replaced with a new 48 VDC battery bank on May 11, 2009 and the new battery is working properly. Additionally, breaker maintenance and testing was performed on breakers 5X01 and 5X22.
4162009003 | Grand Gulf 1 | 07/22/2009 | 08/21/2009 | ML09233068 | <strong>Special Nuclear Material Inventory Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On July 22, 2009, at 1733 hours Central Daylight Time (CDT), the determination was made that an unirradiated local power range monitor (LPRM) detector was not in its expected storage location. The LPRM detector contained an estimated maximum quantity of 5.84 microcuries of Uranium-234 (U-234) and Uranium-235 (U-235) combined, thus meeting the reporting criteria in 10 CFR 20.2201(a)(1)(ii) as a loss of licensed material of a quantity greater than ten times that specified in Appendix C to 10 CFR Part 20. According to special nuclear material (SNM) inventory sheets, the LPRM detector was expected to be stored in a canister in a Spent Fuel Pool (SFP) drum. However, during performance of the annual physical inventory of SNM, the LPRM detector could not be located. Subsequent investigation concluded that the LPRM was disposed of as an SNM discard and shipped to the licensed facility at Barnwell, South Carolina, in February 2005 for burial as radioactive waste.
4162009004 | Grand Gulf 1 | 07/24/2009 | 12/14/2009 | ML09349036 | <strong>Condition Prohibited by Technical Specifications due to Control Room Air Conditioning Subsystem 'B' Inoperability Not Recognized</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2009, at 2254 hours Central Daylight Time, Grand Gulf Nuclear Station (GGNS) was in Mode 1 operating at approximately 100 percent power, when a past operability concern related to Control Room Air Conditioning (CRAC) subsystem B was discovered. On May 13, 2009, a surveillance test had been performed per Technical Specification (TS) Surveillance Requirement 3.7.4.1, with questionable test results. Based on the event investigation, the questionable test results were due to a deficiency introduced during previous maintenance. Subsequent evaluation of the test data determined that the CRAC B unit would not maintain a control room temperature of less than or equal to 90 degrees F under design basis accident heat loads. Therefore, the surveillance acceptance criteria were not met for verifying the CRAC subsystem is capable of removing the assumed heat load. Based on this evidence, CRAC B had been inoperable from March 28, 2009, to June 25, 2009, when the surveillance retest was completed satisfactorily. Since a Condition Prohibited by Technical Specifications had existed but was not recognized, the required 30-day action completion time for TS Limiting Condition for Operation 3.7.4 for one inoperable CRAC subsystem was exceeded. This condition is reportable under 10 CFR 73(a)(2)(i)(B). This event did not prevent the fulfillment of the safety function of the CRAC system.
4232009002 | Millstone 3 | 12/19/2009 | 02/15/2010 | ML10054185 | <strong>Millstone Unit 3 Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 19, 2009 an automatic reactor trip occurred on Millstone Power Station Unit 3 while the unit was in Mode 1, at 100 % power, due to a turbine trip caused by a generator output electrical fault. All control rods fully inserted into the reactor. The auxiliary feedwater pump started as designed and maintained steam generator level. All other post trip actions were standard and all systems operated as expected. A post trip walk-down identified damage to 'C' phase main generator breaker and isophase ducting. There were no radiological challenges as a result of the event. The most probable cause of the ground fault, which resulted in the turbine trip, was determined to be a manufacturing defect in the main generator breaker, 15G-3U-2, 'C' pole contacts. The 'C' pole of the main generator breaker was repaired. All three poles of the breaker will be inspected during the next refueling outage (3R13) to verify the proper geometry of the contacts as well as the security of the fasteners holding the moving contact piston flange in place. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
4242009001 | Vogtle 1 | 09/16/2009 | 11/09/2009 | ML09314029 | <strong>Ultimate Heat Sink Inoperable Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>In preparation for Vogtle Electric Generating Plant (VEGP) refueling outage ( IRIS), on Wednesday, September 16 at approximately 1357 hours Eastern Daylight Time (EDT), Nuclear Service Cooling Water (NSCW) flow to the B train auxiliary containment and reactor cavity cooler was isolated. The isolation valves were closed to install expansion joints between the safety related NSCW piping and the non safety related normal chilled water piping. During installation of the expansion joints it was noted that there was significant leakage past the manual valves that had been closed to isolate the NSCW system. At the time of installation of the expansion joints, the potential consequences the leakage could have on the Operability of the Ultimate Heat Sink (UHS), was not recognized. Subsequently, on Saturday, September 19, at 0306 hours EDT, it was determined that leakage past the NSCW manual isolation valves was in excess of analyzed limits and Technical Specification Required Action Statement 3.7.9A was entered. Unit 1 was subsequently shutdown for the scheduled refueling outage on Sunday, September 20, 2009. However, since there was firm evidence that there was excessive, leakage past the manual isolation valves at the time the expansion joints were installed, Unit 1 operated in a condition longer than allowed by the Technical Specifications.
4242009002 | Vogtle 1 | 12/07/2009 | 02/02/2010 | ML10043034 | <strong>Inadvertent Contact with Handswitch Results in an Automatic Reactor Trip of Unit 1</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2009, at approximately 18:01 hours Eastern Standard Time (EST) with Unit 1 operating at 100 percent rated thermal power, an automatic turbine trip occurred due to low main condenser vacuum. In response to the turbine trip, the Reactor Protection System (RPS) actuated and automatically opened the reactor trip breakers. All control rods fully inserted into the core and all safety systems responded per design. Both Motor Driven Auxiliary Feedwater pumps and the Turbine Driven Auxiliary Feedwater pump started in accordance with plant design due to lo-lo steam generator water level in two steam generators. The unit was stabilized in Mode 3. The cause of the low condenser vacuum was determined to be inadvertent operation of a control room handswitch that resulted in a de-energization of a non-lE 480 volt switchgear. The loss of power to the non-lE 480 volt switchgear resulted in the defeat of an interlock on the loop seal drain valve for the standby Steam Jet Air Ejector (SJAE) which allowed the valve to open. Once the water in the loop seal had drained to the main condenser, a path between the condenser and the atmosphere was established and the main condenser vacuum started to decline. Approximately nine minutes elapsed from the time the handswitch was inadvertently opened until the low main condenser vacuum turbine trip setpoint was reached which resulted in the automatic turbine trip and subsequent automatic reactor trip.
4242009003 | Vogtle 1 | 12/09/2009 | 02/02/2010 | ML10043034 | <strong>High Main Turbine Vibration Results in a Manual Reactor Trip of Unit 1</strong><br /><i>Abstract:&nbsp;</i>On December 09, 2009 at approximately 23:10 hours Eastern Standard Time (EST), during power ascension from an unplanned shutdown, with the unit operating at approximately 24 percent rated thermal power, the reactor was manually tripped. As preparations were being made to synchronize the main generator to the grid, high vibrations were experienced on the high pressure turbine. Due to the high vibrations on the turbine, the turbine was manually tripped. As the turbine was coasting down vibration levels continued to increase. Therefore condenser vacuum was broken to slow the turbine to minimize any potential damage. Prior to breaking condenser vacuum and in anticipation of the trip of the operating main feedwater pump due to low condenser vacuum, the control room operators manually tripped the reactor. Once condenser vacuum had decreased below the main feedwater pump trip setpoint, the main feedwater pump tripped and the motor driven auxiliary feedwater (AFW) pumps automatically started. All control rods fully inserted and all safety systems responded in accordance with plant design. The plant was stabilized in Mode 3.
4252009001 | Vogtle 2 | 12/23/2009 | 02/12/2010 | ML10061052 | <strong>Instrument Air Isolation Results in a Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On December 23, 2009 at approximately 15:25 hours Eastern Standard Time (EST), Vogtle Electric Generating Plant (VEGP), Unit 2 was manually tripped from 100% power due to a loss of instrument air to the turbine building. Instrument air low pressure alarms were received in the control room and secondary side valves responded to the loss of instrument air. Due to the loss of air pressure, several secondary side valves positioned to their fail safe position. This ultimately led to a decrease in suction pressure to one of the main feedwater pumps causing the main feedwater pump to trip on low suction pressure. In anticipation of loss of feedwater flow to the steam generators, the control room operators manually tripped the reactor in accordance with the Abnormal Operating Procedure (AOP) for a main feedwater malfunction. All control rods fully inserted and the motor driven auxiliary feedwater pumps automatically started on low steam generator water level in one of the steam generators in accordance with plant design. All of the control rods fully inserted and the plant was stabilized in Mode 3.
4402009001 | Perry | 06/21/2009 | 08/20/2009 | ML09238014 | <strong>MSR High Level Signal Causes Turbine Trip and Reactor Protection System Actuation</strong><br /><i>Abstract:&nbsp;</i>On June 21, 2009, at 1750 hours, the reactor protection system (RPS) automatically actuated due to receipt of a turbine control valve fast closure signal. All control rods fully inserted and there were no complications during the shutdown. Reactor coolant pressure and level were maintained within expected parameters. The event was caused by receipt of an invalid high water level signal from moisture separator reheater (MSR) 1B instrumentation, which resulted in a main turbine trip, fast closure of the turbine control valves, and activation of the RPS. Incorrect adjustment of the MSR level switches following maintenance in the recent refueling outage was the direct cause for their actuation. Failure to evaluate industry operating experience, not documenting as-found deficiencies in the corrective action program, not considering non-safety equipment as important, and improper work package/procedure use and adherence contributed to this event. The MSR level switches were subsequently adjusted and calibrated satisfactorily to assure proper operation. Maintenance procedures and templates will be revised to prevent recurrence of incorrect level switch adjustment. The safety significance of this event is considered to be low. This event is reported in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as an event or condition that resulted in a manual or automatic actuation of the reactor protection system including reactor scram or reactor trip.
4402009002 | Perry | 06/22/2009 | 08/20/2009 | ML09238014 | <strong>Diesel Generator CO2 Fire Suppression Control Panel Miswiring Results in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2009, it was discovered that a wiring error in a fire protection carbon dioxide (CO2) panel resulted in a condition in which a fire protection CO2 actuation signal for the Division 3 diesel generator room would cause the Division 2 diesel generator room ventilation supply fans to isolate. Additionally, a fire protection CO2 actuation signal for the Division 2 diesel generator room would cause the Division 3 diesel generator room ventilation supply fans to isolate. The condition existed from January 15, 2009, to June 23, 2009, when the wiring error was corrected. The root cause was determined to be an inadequate post modification test which failed to identify the miswiring of two output wires from the diesel generator CO2 Fire Suppression System control panel. The two Division 2 and Division 3 CO2 Fire Suppression System control panel wiring label errors were corrected and the wires relanded to their correct terminals. Procedure guidance will be revised to provide more detailed expectations concerning the scope and rigor of post maintenance/modification testing requirements and enhancing the cable tag/wire mark configuration control process. The safety significance of this condition is considered to be low. This condition is reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety.
4402009003 | Perry | 10/16/2009 | 12/14/2009 | ML09358002 | <strong>Completion of Technical Specifications Required Shutdown due to Division 2 Emergency Service Water (ESW) Inoperability</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2009, at 0718 hours the Division 2 Emergency Service Water (ESVV) pump B tripped after 77 minutes of operation. Testing confirmed initial breaker indications that there was an electrical problem with power to the associated pump motor. A controlled plant shutdown was commenced due to the anticipated investigation and expected repair time exceeding the Technical Specification (TS) Required Action completion time. On October 16, 2009, at 0048 hours, shutdown of the plant was completed by manual actuation of the Reactor Protection System. The plant remained in Mode 3 until 0429 hours on October 19, 2009, when the plant entered Mode 4. Following repairs and testing, on October 28, 2009, the Division 2 ESW pump B was restored to service at 0515 and declared operable at 1358 hours. The cause of the Division 2 ESW pump B trip was determined to be a manufacturing defect in the power supply cable based on cable failure analysis. A contributing cause was attributed to the effects of the predictive maintenance testing methodology. The failed cable section was replaced with a Unit 2 installed spare. Corrective actions were initiated to replace similar safety-related cables and to revise cable replacement frequency and procedures to incorporate lessons learned. The safety significance of this event is considered to be low. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) for completion of any nuclear plant shutdown required by the plant's TS and in accordance with 10CFR50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's TS.
4432009001 | Seabrook | 10/01/2009 | 11/30/2009 | ML09343024 | <strong>Reactor Protection System Actuation on Steam Generator Low Water Level</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2009 at approximately 2241 EDT with the plant in Mode 4 at approximately 260 degrees, actuation of the reactor protection system (RPS) resulted from low water levels in steam generators (SG) A and C. Inadequate monitoring and control of SG levels while performing a plant cooldown resulted in SG levels decreasing below the reactor trip setpoint of 20% narrow range level, which caused an actuation of the RPS. By 2307, the operators restored levels in the affected SGs to greater than 20%. This valid actuation of the RPS did not actuate any plant components because the reactor trip breakers were already open and the emergency feedwater system was removed from service. No adverse consequences resulted from this event. The root cause of the event was attributed to liberal expectations and standards for implementing procedures that direct major plant evolutions, which led to the operating crew's failure to assess potential risks associated with performing a plant cooldown without placing the residual heat removal system in service. The planned corrective actions include remediation for the operator and revising the standards for implementing procedures for major plant evolutions.
4462009001 | Comanche Peak 2 | 12/14/2009 | 02/11/2010 | ML10054158 | <strong>Unit 2 Gamma-Metrics Calibration Impact on Containment Pressure and RCS Tcold</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2009, at 0800 hours, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 at 100% power. A channel calibration on Unit 2 Train B Neutron Flux Monitoring System (Gamma-Metrics) resulted in the inoperability of channels in different systems: Unit 2 containment pressure channel 4, and Channel 4 of the Overtemperature N-16 and Overpower N-16 reactor trips. When the test equipment being used for the channel calibration was disconnected from the Gamma- Metrics system, the affected control room indications returned to normal. The cause of this event was grounding the Gamma-Metrics system to current paths and ground loops which served to couple a voltage potential through the plant grounding system to the affected plant parameters. Completed corrective actions include: 1) A Maintenance Standing Order was issued to control the use of test equipment that has the ability to ground a floating circuit, and (2) The shield cable ground was corrected for the Unit 2 containment pressure channel 3 and 4 main control board indicators. Planned corrective actions include procedure changes to improve the control and use of test equipment. All times in this report are approximate and Central Standard Time unless noted otherwise.
4542009001 | Byron 1, Byron 2 | 10/28/2009 | 06/09/2010 | ML10160039 | <strong>Drain Procedure for ECCS Suction Line Creates an Unanalyzed Condition due to Inadequate Configuration Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2009, an on-line planned work window began for the Unit 1 Train B Residual Heat Removal (RH) suction line to replace the water as a dose reduction effort and to perform required valve stroke tests on the Sump Isolation Valve (i.e., 1SI8811B). The 1SI8811B valve receives an automatic open signal during a Loss of Coolant Accident (LOCA) to switch the Train B Emergency Core Cooling System pumps' suction to the sump. Byron Operating Procedure (BOP) RH-4, "Draining of the RH System," was initiated to drain the Unit 1 Train B RH suction line. The BOP RH-4 requires the 1SI8811B valve to be closed but it does not require it to be de- energized. On October 28, 2009, at 0027, the drain and vent valves were opened to start the draining evolution. During the draining, a Reactor Operator identified a concern that with the 1SI8811B not de-energized it was still capable of opening in response to a LOCA. This would create a leak path of radioactive sump water outside of Containment into the Auxiliary Building while the drain and vent valves were open. The cause was determined to be an inadequate drain procedure in that it did not require the 1SI8811B to be de-energized while the RH suction line was breached. Corrective actions include revising the procedure and performing an extent of condition assessment. This condition was subsequently determined to be an unanalyzed condition; however, there were no actual safety consequences since at no time was an SI8811 valve open when the suction line was breached.
4552009001 | Byron 2 | 06/24/2009 | 02/10/2010 | ML10043084 | <strong>Late Entry into Technical Specification Condition Associated with Reactor Coolant System Leakage Characterization Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2009, at approximately 1:00 pm, a small pinhole leak was identified in a coupling weld connection of a 3/8 inch diameter Process Sampling (PS) tube which is connected to the Unit 2 Reactor Coolant System (RCS). The leak rate was characterized as less than one drop in five minutes which is estimated to be approximately 0.005 gallons per day. This pinhole leak was in a non-ASME code line and was isolated from the RCS via an ASME Class 2 closed sample control air operated valve. After a review of the appropriate Technical Specifications (TS), Shift Management concluded this small leak was considered RCS "identified" leakage and not RCS "pressure boundary" leakage. Therefore, no TS actions were deemed to be necessary for this condition. The NRC Senior Resident Inspector challenged the characterization of the leak as RCS "identified" leakage versus RCS "pressure boundary" leakage. The NRC's basis for this position was that the leak was not isolated because some leak by was occurring past the isolation valve's seat out through the fault. After continued discussions with the NRC, the licensee acknowledged the NRC position and immediately entered TS 3.4.13 Condition B on Unit 2 for exceeding the RCS "pressure boundary" leakage limit at 4:30 pm on June 26, 2009. Condition B requires Unit 2 to be placed in Mode 3 in six hours and Mode 5 in 36 hours. In addition, an expedited repair effort of the PS line had been initiated earlier in the day. The repair to the line was successfully performed and tested by 8:07 pm, and TS 3.4.13 Condition B was exited prior to a power reduction. Shift Management incorrectly characterized the RCS leakage as identified leakage. Shift Management personnel will be trained on how to correctly characterize RCS leakage of this nature. This event had very low safety significance due to the extremely small nature of the leakage past the seat of the closed isolation valve.
4562009001 | Braidwood 1 | 04/08/2009 | 06/08/2009 | ML09156051 | <strong>Steam Generator Tube Exceeding Plugging Criteria Remained in Service During Previous Cycle</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2009, eddy current testing (ECT) of the 1B steam generator detected a distorted indication and identified the indication as requiring additional ECT in order to resolve. On April 8, 2009, additional testing determined the indication to be secondary side foreign object wear that was sized at a depth of 73 percent through wall. Technical Specification 5.5.9 c.1 requires plugging of tubes containing flaws with a depth equal to or exceeding 40 percent of the nominal wall thickness. The tube was subsequently plugged. A review of the results from historical test data determined that the distorted indication had been identified by the computer data screening system during the previous two Unit 1 refueling outages (spring 2006 and fall 2007), but was not retained by the manual eddy current data analyst(s) in either outage, and subsequently not reported in prior outages. The indication from the spring 2006 outage has been determined to be less than the 40 percent TS 5.5.9.c.1 plugging criteria. The indication from the fall 2007 outage was consistent with the indication from the April 2009 outage, and therefore, it is concluded that the flaw exceeded the Technical Specification 5.5.9.c.1 plugging limit of 40 percent in the fall 2007 outage and was not plugged. The cause of this event was determined to be a historic human performance issue related to the amount of technical rigor applied during the review of the distorted eddy current as identified by the computer screening system in the fall 2007 outage. Corrective actions include: revising the eddy current analysis guidelines to emphasize the requirement to manually review available frequencies associated with distorted top of tubesheet indications prior to determining if an indication requires additional analysis, and incorporating results of this issue into the site specific performance demonstration training and testing program in order to ensure all data analysts and screening systems are capable of properly identifying the signal as requiring additional eddy current inspection. There were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B).
4562009002 | Braidwood 1 | 06/24/2009 | 08/02/2010 | ML10224009 | <strong>Safety Injection System Containment Sump Isolation Valve 1SI8811B Failed to Stroke Full Open due to Torque Switch Assembly Corrosion</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2009, safety injection system containment sump isolation valve 1SI8811B was stroked open for surveillance testing. The 1SI8811B control board indication went dual, but never indicated full open. Locally 1SI8811B was observed approximately 30 to 40 percent open. Investigation found water in the actuator limit switch (LS) compartment, and it was determined the actuator torque switch (TS) for the 1SI8811B was corroded and non functional. The cause of the corrosion was determined to be water intrusion into the LS compartment through the conduit connector from a leaking overhead area roof removable slab. The TS and LS finger bases were replaced. On June 26, 2009 at 02:42 hours, the valve was restored to operable status. The root cause was determined to be that station personnel did not fully understand that the area design configuration did not incorporate water tight electrical components to prevent water intrusion, resulting in a lack of sensitivity to the effects of water spills, sprays or leaks in the area. Corrective actions include replacing the TS and LS finger bases, cleaning and drying the wires and LS compartment on 1SI8811B, and repair of the area roof removable concrete slab area in accordance with design drawings. Corrective actions to prevent recurrence include providing training to applicable personnel on the general design configurations and the need to ensure proper controls involving water within specific equipment qualification zones, and developing and implementing processes and controls to evaluate electrical components affected by potential water intrusion in safety related areas. There were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(v)(B). Failure of 1SI8811B to fully open prevented 1SI8804B, Residual Heat Removal to Safety Injection, and 1CS009B Containment Spray Pump 1B Sump Suction Valve from opening.
4572009001 | Braidwood 2 | 04/24/2009 | 06/23/2009 | ML09174032 | <strong>Reactor Trip on Over Temperature Delta Temperature due to a Signal Spike on One Channe lWith Another Channel Placed in theTripped Condition for SurveillanceTesting</strong><br /><i>Abstract:&nbsp;</i>On April 24, 2009, a Technical Specification calibration of the 2B pressurizer pressure loop was being performed. In support of this surveillance, the 2B over temperature delta temperature (OTDT) bistable was placed in the tripped condition. At 1141 hours, while the 2B pressurizer pressure channel calibration was in progress, a momentary/spurious signal spike occurred on the 2D OTDT channel. With the 2B OTDT bistable already placed in the tripped condition, the spike on the 2D OTDT channel satisfied the 2 of 4 trip coincidence, and initiated an automatic reactor trip. The investigation for this event found no issues with human performance, equipment failure, or plant activities that could have caused the signal spike. The root cause of the Unit 2 reactor trip is determined to be the design of the Reactor Trip System and Engineered Safety Features Actuation System, which places a loop in a tripped condition for testing, increases vulnerability during testing conditions. The corrective action to prevent recurrence is to pursue a modification which bypasses a tested channel rather than placing it in the tripped state during surveillances. There were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
4572009002 | Braidwood 2 | 07/30/2009 | 09/28/2009 | ML09271019 | <strong>Unit 2 Loss of Offsite Power Coincident with a Reactor Trip due to Loss of 2C Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2009 at 20:59 hours, Unit 2 experienced an automatic reactor trip from full power. The 2C reactor coolant pump (RCP) tripped on overcurrent following the initial loss of system auxiliary transformer (SAT) 242-1 on a sudden pressure relay actuation and subsequent bus 258 transfer. This resulted in an automatic reactor trip from full power due to less than four RCPs in operation above 30% power. The root causes of the Unit 2 reactor trip were determined to be: 1) the 2C RCP breaker tripped inappropriately due to a combination of an overcurrent trip setpoint time delay shorter than minimum acceptable, and an overcurrent drop out reset value too low; and 2) the procedure for the calibration of overcurrent protective relays does not contain guidance to take an as-found reading / calibration and functional check of the overcurrent drop out reset value. The corrective actions include: 1) perform a functional check, and calibration of the overcurrent protective relays for the 2C RCP, and on pumps with the same overcurrent protective relay; and 2) revise the procedure for the calibration of overcurrent protective relays to include procedure steps for functional check and calibration, as required, for the high drop out instantaneous values associated with overcurrent time delay relays. There were no actual safety consequences impacting plant or public safety as a result of this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B) including any event or condition that results in actuation of the reactor protection system (RPS) when the reactor is critical, actuation of the emergency AC electrical power system, and actuation of the PWR auxiliary feedwater system.
4572009003 | Braidwood 2 | 11/10/2009 | 06/15/2010 | ML10167032 | <strong>Drain Procedure for ECCS Suction Line Creates an Unanalyzed Condition due to Inadequate Configuration Requirements</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2009, during an applicability investigation of a reportable event at another station, Braidwood Unit 2 identified two occurrences in which residual heat removal (RH) suction vent and drain valves were open while the containment sump isolation valve (SI8811) was capable of automatically opening during Operating Modes 1 through 4. These occurrences were Unit 2 RH Train B (2S1881113) on December 7, 2006, and Unit 2 RH Train A (2S18811A) on September 30, 2009. The events occurred during on-line planned work windows for the RH suction lines to replace the water as a dose reduction effort and to perform required valve stroke tests on the SI8811 valve for the respective train. The SI8811 valve receives an automatic open signal during a loss of coolant accident (LOCA) to switch the train-specific emergency core cooling system pumps' suction to the sump. Braidwood Operating Procedure (BwOP) RH-4, "Draining of the RH System," was initiated to drain the RH suction line. BwOP RH-4 requires the SI8811 valve to be closed, but it does not require it to be de-energized. Therefore, during the draining evolution, the SI8811 valve was still capable of opening in response to a LOCA. This would create a leak path of radioactive sump water outside of containment into the auxiliary building while the drain and vent valves were open. The cause was determined to be an inadequate drain procedure in that it did not require the SI8811 to be de-energized while the RH suction line was breached. Corrective actions include revising the procedure and perfomling an extent of condition assessment. This condition was subsequently determined to be an unanalyzed condition; however there were no actual safety consequences since at no time was an SI8811 valve open when the suction line was breached.
4582009001 | River Bend | 01/14/2009 | 03/11/2009 | ML09076098 | <strong>Standby Liquid Control System Inoperable Greater than Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On January 14, 2009, an investigation of operational practices related to the standby liquid control (SLC) system concluded that for the period of March 14, 2003, to October 28, 2008, a seismic event could have rendered the system incapable of performing one of its design safety functions as credited in the station's accident analysis. This condition resulted from an inadequately evaluated change made to a surveillance test procedure that allowed water to remain in the system's test tank. The test tank is not seismically analyzed when full of water. Administrative controls have been put in place concerning draining of the tank following future tests. Test procedure revisions are being developed. The safety significance of this event is negligible. This event is reportable in accordance with 10CFR50.73 as operations prohibited by Technical Specifications and a loss of the safety function of the SLC system.
4582009002 | River Bend | 09/20/2009 | 11/17/2009 | ML09328017 | <strong>Unplanned Manual Reactor Scram Following Trip of Both Reactor Recirculation Pumps</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2009, at 5:47 p.m. CDT, an unplanned manual reactor scram was initiated while reactor power was at approximately 23 percent of rated thermal power. A plant shutdown for a refueling outage was in progress at the time. At approximately 5:33 p.m., with reactor power at 37 percent, the operators had attempted to shift the reactor recirculation pumps from fast speed to slow in accordance with the plant shutdown procedure. RCS pump "A" shifted to slow speed, but approximately nine seconds later, it tripped off. RCS pump "B" did not complete the transfer to slow speed, but tripped off from high speed. Following the trip of the RCS pumps, the thermal-hydraulic conditions in the reactor remained within operational limits of plant Technical Specifications. The response procedures for the trip of both RCS pumps did not specify the actuation of the manual scram. The conservative decision was made to initiate the scram. After the scram signal was initiated, operators stabilized reactor pressure and temperature. All systems responded as designed. No safety systems were out of service at the onset of the event. A controlled reactor cooldown was commenced in preparation for the outage. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as a condition that resulted in the unplanned manual actuation of the reactor protection system while the reactor was critical.
4582009003 | River Bend | 09/29/2009 | 11/23/2009 | ML09334006 | <strong>Low Pressure Coolant Injection Actuation Following Loss of Water from Upper Reactor Cavity Pool</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2009, at approximately 11:27 a.m. CDT, the main control room operators manually started the low pressure coolant injection function of the residual heat removal (RHR) system in response to a decrease in upper reactor cavity water level. At the time of the event, the plant was in a refueling outage. No handling of irradiated fuel or control blades was in progress. A Division 1 integrated emergency core cooling system surveillance test was in progress. One of the expected responses was the actuation of the Division 1 primary containment isolation logic. That actuation caused the closure of primary containment isolation valves in various systems, one of which was the service air system. Among the components being served by the service air system was the main steam line (MSL) plugs in the reactor pressure vessel. The investigation of this event found that the MSL plug in the "A" main steam line was not installed correctly. The mechanical seal had not been completely engaged. In this condition, the backup inflatable seal pressurized by the service air system was the only barrier keeping water out of that main steam line. When the service air header in the primary containment was depressurized, the seal deflated and began to leak. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as a condition involving the unplanned actuation of an ECCS system.
4612009001 | Clinton 1 | 07/02/2009 | 08/28/2009 | ML09252035 | <strong>Safety Function Lost due to Capacitor Failure on Circuit Card</strong><br /><i>Abstract:&nbsp;</i>On 7/02/09, the Nuclear System Protection System (NSPS) Self-Test System identified a failure of the Division 3 High Pressure Core Spray (HPCS) logic circuit card (HPCS-1). This failure resulted in the output initiation signals from this card being blocked, preventing the safety function of automatic HPCS initiation and automatic start of the Division 3 emergency diesel generator (DG) and the Division 3 Shutdown Service Water System pump. Operators declared the HPCS, the DG, and the SX systems inoperable but available and entered the applicable Technical Specification action requirements. The Reactor Core Isolation System was verified to be operable as required by Technical Specifications. The cause of the Division 3 logic circuit card failure was a knit-line delamination and associated cracks on a ceramic capacitor in the Power On Initialization circuit due to a manufacturing anomaly that limited the expected lifetime of this capacitor. The defective ceramic capacitor caused the output initiation signals from this card to be blocked, preventing automatic HPCS initiation signals. Corrective actions for this event include repairing the Division 3 logic circuit card that failed, obtaining a spare Division 3 logic circuit card and creating a Performance Centered Maintenance template and evaluating strategies for performing preventive maintenance activities on NSPS circuit cards.
4612009002 | Clinton 1 | 09/18/2009 | 10/23/2009 | ML09308001 | <strong>Contractor Falsified Information for Unescorted Access Authorization</strong><br /><i>Abstract:&nbsp;</i>A contractor was given unescorted security access on 9/14/09 as a reinstatement background investigation based on the contractor having previous unescorted access at another nuclear facility greater than 30 days earlier, but less than 365 days. The access was authorized prior to completion of the background investigation as allowed by NRC. On 9/18/09 during conduct of the background investigation of the contractor, an issue was identified with the Personal History Questionnaire (PHQ) completed by the contractor for unescorted security access. The issue was a previous employer identified derogatory information that the contractor did not disclose on the PHQ at the time of processing on 9/14/09. If Exelon had known the derogatory information at the time of initial access processing, unescorted access would have been denied to the contractor. On the basis of this information, the contractor was located and removed from the Protected Area (PA) and unescorted security access was immediately terminated. The contractor had been in the PA for a total of 14 hours and 27 minutes, and in the vital area for a total of 31 minutes during the period of authorized access. Areas in the plant that the contractor accessed were walked down for any indications of degradation of safety systems and none were found. This event is reportable under the provisions of 10 CFR 73.71(b)(2).
4612009003 | Clinton 1 | 09/24/2007 | 11/20/2009 | ML09336018 | <strong>Safety Function Loss due to No Like for Like Verification of Swapped Relays</strong><br /><i>Abstract:&nbsp;</i>While the Division 3 Emergency Diesel Generator (DG) was inoperable and unavailable for scheduled maintenance, technicians discovered two time delay relays in the Division 3 DG control panel were in swapped locations. The Division 3 DG is analyzed to automatically start and load, energize the High Pressure Core Spray (HPCS) system pump motor, and provide electrical power necessary to initiate opening of the HPCS injection valve in less than 23 seconds after the Loss of Offsite Power (LOOP) / Loss of Coolant Accident (LOCA) initiation signal. Swapping the relays had two negative effects, the most significant of which resulted in the Division 3 DG being incapable of starting for 45 seconds during a LOOP/LOCA immediately following manual shutdown of the engine while one of the two relays timed out. Additionally, the HPCS injection valve would not have opened, and the HPCS pump would not have achieved design flow in less than 47 seconds as analyzed after a LOOP/LOCA initiation signal. This condition existed from 9/24/07 to 9/23/09. The cause of this event was inadequate attention to detail and failure to comply with written instructions. Corrective actions include revising the model work order instructions to ensure correct relays are installed, briefing Electrical Maintenance personnel on this event, and providing training on parts verification activities.
4612009004 | Clinton 1 | 09/30/2009 | 11/20/2009 | ML09335052 | <strong>Steam Leak due to Valve Packing Torque Results in Required Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 9/29/09, at 1544 hours, with reactor power at 96.9%, operators began noting indications of a steam leak in the Drywell. By 1616 hours, Drywell floor drain leakage rate had increased from 0.25 gallons per minute (gpm) to 3.4 gpm, exceeding the limit of 2 gpm increase in the previous 24 hour period while in Mode 1 specified in Technical Specification (TS) 3.4.5, Reactor Coolant System (RCS) Operational Leakage. In response to the increased leakage, operators entered the TS 3.4.5 Required Action to verify within 4 hours the source of the unidentified leakage source is not service sensitive type 304 or type 316 austenitic stainless steel. At 1850 hours, the station was unable to determine that the source of the increase in unidentified leakage was not service sensitive type 304 or type 316 austenitic stainless steel; operators entered the TS 3.4.5 Required Actions to bring the unit to cold shutdown, and cold shutdown was achieved at 1834 hours on 9/30/09. Investigation identified a valve stem packing leak in the Drywell. The causes of this event were the valve stem is off-center with the stuffing box and work instructions did not require the packing to be torqued to the as-left value from the original installation. Corrective actions for this event include replacing the packing, investigating the cause of the off-center valve stem, and verifying packing torque for other valves.
4612009005 | Clinton 1 | 10/15/2009 | 03/23/2011 | ML11095016 | <strong>Manual Scram on High Water Level due to Reactor Recirc Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On 10/15/09 the 'B' Reactor Recirculation (RR) Pump unexpectedly tripped from fast speed to off. Reactor Pressure Vessel (RPV) water level increased and operators placed the Reactor Mode Switch in Shutdown at a predetermined level prior to the high reactor vessel water level automatic scram setpoint. All control rods fully inserted. When RPV water level decreased below the low RPV water level setpoint, operators entered Emergency Operating Procedure (EOP) 1, RPV Level Control. The cause of this event is attributed to failure of the 'B' RR pump motor. Vendor failure analysis concluded that the failure in the RR pump motor was a B-Phase turn-to-turn fault located at a connection end coil knuckle. The failure was limited to a single coil end turn knuckle of the winding and was located in a position that is not susceptible to air flow or foreign material. The apparent cause of the failure was a random insulation breakdown of the original winding that resulted in a turn-to-turn failure. The pump motor that failed has been replaced by a spare pump motor and the motor that failed was shipped to a vendor for failure analysis and repair.
4822009001 | Wolf Creek | 04/28/2009 | 06/24/2009 | ML09181070 | <strong>Reactor Protection System Actuation and Reactor Trip due to Main Feedwater Regulating Valve Failing Closed</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2009 at 3:27 p.m. Central Daylight Time, Wolf Creek experienced an automatic actuation of the Reactor Protection System (RPS) including an automatic reactor trip due to low water level in the "B" steam generator (SG). The RPS actuation occurred after the "B" SG Main Feedwater Regulating Valve (MFRV) closed in response to failures of the primary and secondary fuses for the Westinghouse 7300 control card frame that contained the associated control cards for the MFRV. When the "B" MFRV closed, "B" SG level decreased below the reactor trip setpoint initiating a reactor trip. The unit received a feedwater isolation and auxiliary feedwater actuation (both motor-driven and turbine-driven) because of the low SG level. All control rods inserted fully and the RPS and the Engineered Safety Features (ESF) Systems performed as expected. The cause of the "B" MFRV closure was the failure of the primary and secondary fuses for the Westinghouse 7300 card frames. All of the 7300 card frame fuse holders were inspected using thermography and 14 fuse holders and fuses were replaced. The degraded fuse holders and associated fuses were replaced before reactor start-up commenced on April 30, 2009. The safety significance of this event is low. This event is bounded by analyses as reported in the Wolf Creek Generating Station (WCGS) Updated Safety Analysis Report (USAR) section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
4822009002 | Wolf Creek | 08/19/2009 | 10/17/2009 | ML09300015 | <strong>Loss of Offsite power due to Lightning</strong><br /><i>Abstract:&nbsp;</i>On 08/19/2009 Wolf Creek Generating Station (WCGS) was operating at approximately 100% power. At approximately 1549 hours, WCGS experienced an unplanned automatic shutdown. The turbine and reactor trip occurred due to the momentary loss of offsite power (LOOP) to the onsite buses. Operations personnel and safety equipment responded appropriately to place the plant in a stable condition in Mode 3. All control rods inserted fully and the Reactor Protection System and the Engineered Safety Features System performed as expected. A lightning strike on LaCygne 345 kV line caused the loss of the LaCygne line. The Rose Hill 345 kV line was lost due to a loss of carrier function, causing line operation (opening of switchyard breakers), and subsequent loss of the Benton 345 kV line as a result of the unit heading toward instability. The safety significance of this event is low. Both emergency diesel generators started and supplied power to the safety related buses. There were no adverse effects on the health and safety of the public.
4822009004 | Wolf Creek | 08/21/2009 | 10/18/2009 | ML09300015 | <strong>Feedwater Isolation on High Water Level in 'A' Steam Generator</strong><br /><i>Abstract:&nbsp;</i>On 8/21/2009, at approximately 0648 CDT, Wolf Creek Generating Station experienced a turbine trip and Feedwater Isolation Signal (FWIS) generated as result of high water level in 'A' Steam Generator. The water level in the 'A' Steam Generator exceeded the initiation setpoint of 78%. Steam generator water level returned below the initiation setpoint at approximately 0656 CDT. (EN # 45281) At the time of the event, the turbine was in the tripped condition and main feedwater Isolation valves, feedwater regulating valves and feedwater regulating bypass valves were closed due to a plant trip that occurred at 1549 CDT on 8/19/2009 (Reference LER 2009-002-00). The event had no impact on plant conditions. The cause of the event was a human performance error due to inadequate monitoring of critical operating parameters by the on-duty operating crew. There were no component failures or functional failures of equipment. The safety significance of the event was very low. All systems functioned as designed. Plant conditions and configuration were such that the turbine trip and FWIS had no effect other than alarm annunciation and signal generation.
4822009005 | Wolf Creek | 10/22/2009 | 06/26/2013 | ML13190A00 | <strong>Loss of both Diesel Generators with all fuel in the Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>At 1206 CDT on 10/22/2009, with Wolf Creek Generating Station in Refueling Outage 17, Control Room annunciators 20D and 20B for the "A" Diesel Generator (DG) actuated. At 1208 CDT the "A" DG was taken out of service for troubleshooting of abnormal alarm indications. At 1739 CDT on 10/22/2009, a Notification of Unusual Event (NUE) was declared due to the loss of the "A" DG with the "B" DG out of service for refueling outage maintenance. At the time of the event, the reactor vessel was defueled with all fuel located in the Spent Fuel Pool. Power to the safety related busses was being supplied by offsite power. <br><br> The root cause of the false speed switch actuation was a wiring error of the speed switch. The control cabinet supplier did not wire the speed switch per the recommendation of the speed switch manufacturer. As a result the speed switch signal wire was not protected from ambient electromagnetic interference. The speed switches were rewired per the manufacturer's recommendation. <br><br> The "A" DG was returned to service at 0738 CDT on 10/23/2009. The NUE was exited at 0740 CDT on 10/23/2009.
4822009006 | Wolf Creek | 06/30/2009 | 01/06/2010 | ML10015007 | <strong>Inadequate Common Cause Failure Determination Results in Condition Prohibited by Technical</strong><br /><i>Abstract:&nbsp;</i>At 1115 CDT on June 30, 2009, a through wall leak on Essential Service Water (ESW) System piping just upstream of valve EF HV-038 was identified by shift crew personnel during building watch rounds. The "B" ESW train was declared inoperable per Technical Requirement (TR) 3.4.17, "Structural Integrity," and Condition A of LCO 3.7.8, "Essential Service Water (ESW) System," was entered. This resulted in the "B" diesel generator (DG) being declared inoperable and entering Condition B of LCO 3.8.1. Required Action B.3.1 for TS 3.8.1 is to determine if the operable DG is inoperable due to a common cause failure. Control room personnel utilized procedure SYS KJ-200, "Inoperable Emergency Diesel," when the DG was declared inoperable and determined that a common cause failure did not exist. At 1202 CDT Required Action B.3.1 was exited. At 2140 CDT, a structural integrity evaluation utilizing Code Case N-513-2 demonstrated that adequate structural integrity of the "B" ESW train existed. The "B" ESW train and "B" DG were declared operable. Subsequently, the NRC Resident Inspector challenged the adequacy of the common cause failure determination. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TSs based on the NRC Inspection Report 2009004 characterization of the issue as a violation of TSs.
4822009007 | Wolf Creek | 03/24/2009 | 01/11/2010 | ML10020027 | <strong>Removal of Equipment from Service Required by Technical Specifications and NRC Safety Evaluation</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2009 at 0600 Central Standard Time (CST), Limiting Condition for Operation (LCO) 3.8.1 was declared not met and Condition B entered when the "B" diesel generator (DG) was taken out of service for voluntary planned maintenance activities. Required Action B.4.2.2 with a Completion Time of 7 days was applied when the DG was declared or rendered inoperable for the performance of voluntary planned maintenance. At 1552 hours, a partial performance of STS IC-208B, "4kV Loss of Voltage and Degraded Voltage TADOT NB02 Bus - Separation Group 4," was commenced to take as-found data prior to the replacement of the 48 VDC power supply (EGL0002DA). At 1620 hours, Condition A.1 of LCO 3.3.5 was entered when the Channel 4 degraded voltage circuitry was removed from service for the partial performance of STS IC-208B. Channel 4 was returned to service at 1630 hours and the partial performance of STS IC-208B completed satisfactorily. At 1654 hours, the Channel 4 degraded voltage circuitry was removed from service for replacing the 48 VDC power supply and Condition A.1 of LCO 3.3.5 entered with 6 hours to place the channel in trip. At 2109 hours, Condition A of LCO 3.3.5 was exited when the Channel 4 degraded voltage circuitry was returned to service after replacement of the power supply and completion of STS IC-208B. The "B" DG was returned to service on March 28, 2009 at 0323 hours. The Condition B, Required Action B.4.2.2, of LCO 3.8.1 was completed well within (3 days 21 hours and 23 minutes) the 7 day Completion Time as required by the Technical Specifications.
4822009008 | Wolf Creek | 04/02/2008 | 01/11/2010 | ML10020020 | <strong>Potential for Containment Fan Coolers to Not Have Automatically Started in Slow Speed</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2008, as a result of operating experience from another plant, it was identified that with the containment fan coolers running in fast speed, certain small break loss-of-coolant accidents (SBLOCA) harsh environment scenarios may result in the fan coolers not starting in slow speed on an safety injection (SI) signal. On April 10, 2008, this event was reported in accordance with 10 CFR 50.72(b)(3)(ii)(B) as an event or condition that results in the nuclear power plant being in an unanalyzed condition that significantly degrades plant safety (Event Number 44131). An analysis was performed for a spectrum of SBLOCA scenarios and limiting main steam line break (MSLB) scenarios with the assumption that the fan coolers were not available to perform their specified function. In addition to the analysis, a review of plant data for the period January 1, 2005 through June 10, 2008 was performed to identify those periods of time when the fan coolers were in high speed operation concurrent with containment and cooling water conditions conducive to high loading that could potentially cause the fast speed thermal overloads to trip. The event notification was retracted on June 20, 2008 based on the evaluation determining that an unanalyzed condition did not exist.
4822009009 | Wolf Creek | 08/22/2009 | 03/22/2010 | ML10089042 | <strong>Defeating Feedwater Isolation on Low Tavg Coincident with P-4 Function Results in Missed Mode Change</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2009, at 0540 hours Central Daylight Time (CDT), with the plant in Mode 3, Control Room staff defeated the feedwater isolation on low Tavg coincident with P-4 Function using procedure SYS SB-122, "Enabling/Disabling P-4/Lo Tavg FWIS." This procedure was performed for restoring main feedwater flow through the main feedwater isolation valves (MFIVs) to supply water to the steam generators. On August 23, 2009, at 0125 hours the jumpers installed for defeating the feedwater isolation on low Tavg coincident with P-4 function were removed and procedure SYS SB-122 completed at 0140 hours. The Nuclear Regulatory Commission (NRC) Resident questioned the defeating of the feedwater isolation on low Tavg coincident with P-4 function while in Mode 3. Technical Specification (TS) 3.3.2, Table 3.3.2-1 specifies the applicable Mode for Function 8.a. (Reactor Trip, P-4) as Modes 1, 2, 3. Defeating the feedwater isolation on low Tavg coincident with P-4 function using procedure SYS SB-122 results in both channels being defeated. There is no TS Condition for two inoperable trains. Limiting Condition for Operation (LCO) 3.0.3 specifies that when an associated Action is not provided, action shall be initiated within 1 hour to place the plant in Mode 4 in 13 hours. Action was not taken as required by the TSs.
4822009010 | Wolf Creek | 11/18/2009 | 07/13/2010 | ML10201038 | <strong>Failure to Meet LCO 3.0.4b During Transition from Mode 4 to Mode 3</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2009, at 2353 hours Central Standard Time (CST), Control Room personnel authorized the transition from Mode 4, Hot Shutdown, to Mode 3, Hot Standby, in accordance with Limiting Condition for Operation (LCO) 3.0.4b. with the turbine driven auxiliary feedwater (AFW) pump inoperable. Heat-up activities were in progress to return the plant to service following a refueling outage with the plant ready to transition from Mode 4 to Mode 3 with the exception of completing some work activities and post maintenance testing to restore the turbine driven AFW pump to a functional status. A risk assessment was completed as required by LCO 3.0.4b. and identified that protected train signs may be posted as deemed necessary. On November 18, 2009, at 0024 hours, the plant transitioned from Mode 4 to Mode 3 under the provisions of LCO 3.0.4b. for the turbine driven AFW pump with no protected equipment signs posted for the motor driven AFW pump rooms. On December 17, 2009, at a weekly meeting with the NRC Resident Inspector, the inspector identified a potential violation of LCO 3.0.4b. for not establishing risk management actions prior to transitioning from Mode 4 to Mode 3 as required by the technical specification. The risk management action not established was protected equipment signage for the motor driven AFW pump rooms.
4822009011 | Wolf Creek | 12/16/2009 | 02/15/2010 | ML10055088 | <strong>Intermediate Range Detector NI-36 Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2009 the NRC Senior Resident Inspector proposed a violation of Technical Specification Table 3.3.1-1 Function 18.a. A Problem Identification and Resolution (PI&R) inspection sample was performed on Intermediate Range Detector NI-36 and identified that during Refueling Outages 14 and 15 the detector repeatedly failed non-Technical Specification procedure STN IC-236. In one case, the detector failed to go below the intermediate range neutron flux interlock (P-6). This resulted in the detector being inoperable in Cycles 15 and 16. Events are reportable if they occurred within a timeframe of the previous three years. The last four months of Cycle 16 are in the three-year timeframe for reportability. This condition is of low safety significance. The detector was replaced on April 10, 2008 during Refueling Outage 16.
4832009001 | Callaway | 02/19/2009 | 02/04/2010 | ML10035066 | <strong>Technical Specification Required Shutdown due to Loss of Power Supply</strong><br /><i>Abstract:&nbsp;</i>At 0228 on 2/19/2009, while operating at 100-percent reactor power, multiple control room annunciators actuated in response to a power supply failure in the Balance of Plant Engineered Safety Features Actuation System (ESFAS) channel 1 logic cabinet. Due to the number of isolation and actuation instrumentation functions affected, numerous Technical Specification (TS) Conditions and Required Actions were entered. TS 3.3.2.0 required the plant to be in MODE 3 in 6 hours and MODE 4 in 12 hours. Although the power supply was replaced in a timely manner, it was not able to be replaced before plant shutdown was required per TS 3.3.2.0. Hence, load reduction began at 0530, with MODE 3 being reached at 0817. The power supply was replaced and the system was restored to Operable at 1009. Root Causes for this event include inadequate trending of condition monitoring data, no preventive maintenance strategy for critical power supplies, and failure to identify generic power supply failure issues and implement corrective actions. The Corrective Action to Prevent Recurrence for this event is to generate new preventive maintenance tasks in order to implement a time-based replacement and refurbishment program for critical power supplies.
4832009002 | Callaway | 05/25/2009 | 11/05/2009 | ML09310010 | <strong>TDAFP Failed to Start During Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>At 1141 on 25 May 2009, while operating at 100% power, the Turbine-Driven Auxiliary Feedwater Pump (TDAFP) failed to start during surveillance testing. The failure occurred due to excessive frictional loading from the cumulative effects of a lack of lubrication effectiveness coupled with an incorrectly installed thrust washer for the TDAFP Trip & Throttle Valve (TTV). The TTV Preventative Maintenance (PM) lubrication frequency was determined to be inadequate for the operating conditions. In addition, the last scheduled TTV lubrication was found to have not been performed, and an error was found to have occurred during TTV assembly. All surveillance tests between the refueling outage and the May 25 failure had been successful. The TDAFP became inoperable between the failed surveillance and the previous successful surveillance. The exact time the TDAFP became inoperable is unknown, but it is assumed the TDAFP was inoperable longer than permitted by the Technical Specifications. In addition, a second Auxiliary Feedwater Pump was rendered inoperable for surveillance within the period that the TDAFP is assumed to have been inoperable. The TTV was lubricated, and the TDAFP was returned to service at 2256, 25 May 2009. Corrective actions include revising the PM frequency and revising the TTV installation procedure to incorporate valve lubrication requirements as a critical step.
4832009003 | Callaway | 11/04/2008 | 08/31/2009 | ML09244017 | <strong>Turbine-Driven Auxiliary Feedwater Pump Inoperable During MODE change from 4 to 3</strong><br /><i>Abstract:&nbsp;</i>On 7/1/09, Plant Engineering reviewed Turbine-Driven Auxiliary Feedwater (TDAFP) test data that was recorded on 11/3/08 during plant restart from Refuel 16. From review of this data, it was noted that the recorded position indication of the remote servo for the TDAFP governor flow valve was below the minimum expected value. The TDAFP was declared inoperable on 11/5/08 after entry into MODE 3 due to erratic TDAFP governor valve position indication observed during surveillance testing, and Condition C of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.5 was entered at that time. However, the 7/1/09 review showed the TDAFP had become inoperable prior to entering MODE 3 on 11/4/08 due to the faulty remote servo that was installed during Refuel 16. Entry into MODE 3 without TS LCO 3.7.5 being met constituted a violation of TS LCO 3.0.4. The Root Cause for this event is that the procedure did not meet the requirements of the Callaway Procedure Writing Manual in regards to acceptance criteria. The Corrective Action to Prevent Recurrence is to revise the procedure to include acceptance criteria. Other causes include a defective remote servo being installed and the lack of thorough consideration of servo failure following an unexpected overspeed trip while running the TDAFP turbine on auxiliary steam.
4832009004 | Callaway | 07/04/2009 | 08/27/2009 | ML09244017 | <strong>Failure to Comply with Technical Specification 3.8.1 Required Action A.1 for One Offsite Circuit Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0927 on 4 July 2009, while operating at 100% power, an unlabeled indication light on breaker NB0112 was found unlit. The unlit light indicated a failure of a synchronizing circuit for safety-related bus NB01 which rendered the normal offsite power source inoperable. As a result of this circuit failure, the Emergency Diesel Generator (EDG) associated with NB01 would not have been able to synchronize to the normal offsite source. The EDG remained capable of powering NB01 and could still support a synchronized load transfer to the alternate source. With one offsite source inoperable, Technical Specification (TS) 3.8.1 Required Action A.1 required verification of the remaining offsite source within one hour and once every eight hours thereafter. The synchronizing circuit failure was not identified until 1820 on July 6 due to incorrect assumptions made during initial investigation of the unlit light. As a result, the Completion Time of Required Action A.1 was not met. Compliance to TS 3.8.1 was restored at 1850 on July 6. The event was caused by a combination of the lack of written instructions, training, component identification and field labels related to the unlabeled indication light. Corrective actions include development of written instructions and training, installation of local information tags, issuance of component identifiers and enhancement of operating technician logs.
4832009005 | Callaway | 12/08/2009 | 09/29/2010 | ML10273017 | <strong>Inoperability of Atmospheric Steam Dump Valves</strong><br /><i>Abstract:&nbsp;</i>On 12/8/2009, atmospheric steam dump (ASD) valve ABPV0003 was taken out of service for calibration of a pressure transmitter and controller. Post-maintenance testing revealed the valve would not stroke fully open nor control in manual. A manual/auto (M/A) station was replaced and the positioner diaphragm pressure gauge port was blown out to ensure it was not blocked. After post-maintenance testing, the valve was declared operable at 0132 on 12/11/2009. The other three ASDs were stroke tested as an extent-of-condition test. Two of them performed satisfactorily. However, ABPV0002 did not stroke fully open as required, and was declared inoperable. Troubleshooting for ABPV0002 revealed the current-to-pressure transducer (I/P) output to be erratic and actuator leakage to be in excess of the allowable rate. The I/P transducer and a diaphragm were replaced, and after completing post-maintenance testing the valve was declared operable at 0442 on 12/13/2009. Erratic output from the ABPV0002 transducer was caused by vibration. It was concluded that ABPV0002 was inoperable for a time longer than permitted by Technical Specification (TS) 3.7.4. It was further concluded that the period of time ABPV0002 was inoperable overlapped the period of time ABPV0003 was removed from service. Therefore, this condition is reportable as a condition prohibited by the TS and as an event or condition that could have prevented fulfillment of a safety function. Corrective actions include implementing a time based replacement strategy for M/A stations and relocating I/P transducers to eliminate the vibration failure mechanism.
4982009001 | South Texas 1 | 02/24/2009 | 07/30/2009 | ML09222004 | <strong>Oil Reservoir for Essential Chiller 12B Below Required Temperature</strong><br /><i>Abstract:&nbsp;</i>On 02/24/2009 Unit 1 was in Mode 1. Essential Chiller 12C was out of service for planned maintenance. Essential Chiller 12B was running and was secured in preparation for chiller train rotation at 13:51. At 22:28, Essential Chiller 12B oil reservoir temperature was found to be 108F which is below the required minimum temperature of 120F. Essential Chiller 12B was found to be inoperable from the time it was secured at 13:51 due to inadequate calibration of the oil heater thermostat completed on 2/17/09. Operability of Essential Chiller 12C was restored at 2126 on 02/24/09. This condition resulted in two Essential Chillers being inoperable for 7 hours 35 minutes without initiating a unit shutdown. This event is reportable under 10CFR 50.73(a)(2)(i)(B) because the two trains were inoperable longer than allowed by Technical Specification 3.7.14 without taking appropriate action. The root cause of the low oil temperature condition on Essential Chiller 12B was the lack of an oil heater thermostat calibration procedure that was specific to the Essential Chillers. Corrective actions include revision of the calibration procedure and planning model. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety related equipment.
4982009002 | South Texas 1 | 09/17/2009 | 03/25/2010 | ML10092005 | <strong>Main Steam Isolation Valve Blocked from Closing</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2009, Unit 1 Main Steam Isolation Valve (MSIV) 1D (MS-FSV-7444) was discovered to be inoperable due to restricted movement that kept it from being closed completely. Erection of a work platform around MSIV 1D began on September 14 with decking that was later found to interfere with valve movement. Operability was restored at 14:57 on September 17, 2009, when the interference was removed. Technical Specification 3.7.1.5 requires that each MSIV be operable in Modes 1, 2; and 3. If one MSIV is inoperable but open, power operation may continue provided that operability is restored within four hours, or the requirements of the Configuration Risk Management Program are met. Otherwise, the unit is to be in at least hot standby within six hours. Because the MSIV was inoperable longer than allowed under the Technical Specifications without taking the appropriate action, this event is reportable under 10 CFR 50.73(a)(2)(i)(B). The event is also reportable under 10 CFR ,50.73(a)(2)(v)(C) as a safety system functional failure because MSIV 1D would not have been able to fully isolate a faulted steam generator to mitigate a radioactive release. The root cause of the event was inadequate procedures for scaffold installation. The procedures did not ensure an adequate review of the impact of the scaffold installation on operation of the plant. Procedures have been revised to improve control over installation of scaffolding. Only MSIV 1D was affected by this condition. There were no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
4992009001 | South Texas 2 | 07/09/2009 | 09/14/2009 | ML09265018 | <strong>Essential Chiller 22A Trip on Low Oil Pressure</strong><br /><i>Abstract:&nbsp;</i>At 11:21 on July 9, 2009, Unit 2 Essential Chiller 22A tripped due to low oil pressure approximately 105 seconds into its startup sequence. Technical Specification 3.7.14 requires that if one train of Essential Chilled Water is inoperable in Modes 1, 2, 3, and 4, it is to be restored to operability within seven days, or apply the requirements of the Configuration Risk Management Program, or the unit is to be in at least hot standby within the following six hours. An operability evaluation concluded that Essential Chiller 22A had been inoperable for greater than allowed under the Technical Specifications without taking the appropriate action, therefore this event is reportable under 10 CFR 50.73(a)(2)(i)(B). The root cause of the Essential Chiller 22A low oil pressure trip was refrigerant saturation in the lube oil due to a long idle period prior to the attempted start. Refrigerant saturation reduced oil viscosity and the ability to develop normal oil pressure, which led to low pressure trip setpoint being reached. Subsequent to the trip, Essential Chiller 22A was successfully started at 11:53. The B and C trains of Essential Chilled Water remained operable during this event. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
5282009001 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 02/18/2009 | 04/20/2009 | ML09121011 | <strong>Safety Injection System Recirculation Alignment Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2009, station personnel identified that certain pump and valve alignments of the Safety Injection (SI) system used for periodic surveillance testing and recirculation of the Refueling Water Tank (RVVT) could, in conjunction with specific accident scenarios, jeopardize both trains of SI pump minimum flow recirculation capability and affect the operability of SI pumps. Further, these alignments could have resulted in the bypass of Containment sump water to the RVVT and adversely impacted the available net positive suction pressure for the SI pumps after a Recirculation Actuation Signal (RAS). Even though these alignments have been performed for many years, the infrequent nature of these alignments and the unlikely occurrence of the specific accident scenarios resulted in very low risk to the plant. The root causes were determined to be inadequate review and approval of procedure changes and the inadequate review of operating experience. Corrective actions included changes to the procedure change process to include validation of the design configuration bases. A prior event with similar causes was reported in LER 05-00528/2004-009-01. Due to the timing of both events the corrective actions from this LER could not have prevented the condition being reported now.
5282009003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/13/2009 | 07/13/2009 | ML09209019 | <strong>Surveillance Test Procedure Inadequate to Meet the Requirements of TS</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2009, Palo Verde engineers discovered Surveillance Requirement (SR) 3.8.9.1 was not completely implemented in Surveillance Test (ST) procedure 40ST-9ZZ05, "Weekly Electrical Distribution Checks." The procedure did not verify the supply breaker alignment for the Class 1E 125 VDC distribution panels (PKA-D21, PKB-D22, PKC-D23 and PKD-D24) as required by Technical Specification (TS) Bases Table 3.8.9-1. As a result, all three Palo Verde units entered SR 3.0.3. Procedure 40ST-9ZZ05 was revised later the same day to include verification of the breaker position for the Class 1E 125 VDC distribution panels. The revised procedure was performed in all three units satisfying SR 3.8.9.1 and each unit exited SR 3.0.3. Investigation of this event determined the condition has existed since the implementation of the Palo Verde Improved Technical Specifications (ITS) on August 13, 1998, when the Class 1E distribution panels were added to TS Bases Table 3.8.9-1. The cause of the event was a lack of technical rigor when implementing the ITS. One similar event was reported by PVNGS in the past three years in LER 50-528/2007-003 where a monthly valve alignment did not adequately meet its intent to satisfy TS SR.
5292009001 | Palo Verde 2 | 04/22/2009 | 07/21/2009 | ML09216040 | <strong>Emergency Diesel Generator Fuel Oil Transfer Pump Failure</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2009, at approximately 10:05 Mountain Standard Time (MST), while performing Surveillance Test 73ST-9DF01, "Diesel Fuel Oil Pump - Inservice Test," the diesel fuel oil transfer pump for Emergency Diesel Generator 2B (EDG-2B) failed. Control Room Operators declared EDG-2B inoperable and entered TS Limiting Condition for Operation (LCO) 3.8.1. The breaker for the transfer pump was found opened in the trip free position. Troubleshooting identified an electrical short to ground between a terminal and the associated cable connection box. The faulty terminal was repaired and the transfer pump was retested with acceptable results. Control Room Operators declared EDG-2B Operable on April 23, 2009, at 08:58 MST. The failure was determined to be caused by moisture in the cable connection box that initiated a corrosion process that eventually caused an electrical short to ground. As an immediate corrective action, all the other site EDG (five) cable connection boxes were examined and were found to be dry. Cable megger readings were all greater than 100 Mega-ohms. The investigation also concluded that the failure would likely have prevented EDG-2B from meeting its mission time of seven days for a period of time that was in violation of TS 3.8.1 (AC Sources - Operating) and TS 3.8.2 (AC Sources - Shutdown). No similar events have been reported by PVNGS in the past three years where an EDG fuel oil pump failed causing the EDG to become Inoperable.
5292009002 | Palo Verde 2 | 08/21/2009 | 12/23/2009 | ML09365015 | <strong>Condition Prohibited by Technical Specification 3.6.3 for Inoperable Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2009, the Unit 2 steam generator (SG) blowdown sample solenoid-operated containment isolation valve (CIV) 2SGAUV211 failed to close during a scheduled surveillance test. The mode of the failure was the control relay failed to de-energize the valve solenoid when the control room hand switch was taken to the "close" position. Between that date and October 5, 2009, four additional Unit 2 SG blowdown CIVs failed to close in the same manner as valve 2SGAUV211. In each of the cases, the control relay had been replaced during preventive maintenance and the observed failures occurred during the first closure demand following successful completion the post-maintenance retest in which the normally open valves closed upon demand. The common mode failures of the CIVs to close represented a condition in which each of the CIVs was inoperable for durations longer than the action completion times of Technical Specification Limiting Conditions for Operation. The root cause of the control relay failures has not been identified and the investigation is on-going. Similar events have not been reported by the station in the previous 3 years.
5302009001 | Palo Verde 3 | 12/03/2009 | 02/01/2010 | ML10049074 | <strong>Manual Reactor Trip due to a Loss of Instrument Air to the Containment Building</strong><br /><i>Abstract:&nbsp;</i>On December 3, 2009, at approximately 04:31, Mountain Standard Time, Unit 3 control room operators initiated a manual reactor trip from approximately 100 percent rated thermal power in response to a loss of instrument air (IA) to the containment building. The loss of IA caused a closure of the reactor coolant pump (RCP) seal bleed off isolation valve, redirecting RCP seal bleed off from the volume control tank (VCT) to the reactor drain tank (RDT). To prevent overfilling and breaching the RDT rupture disc, plant operators initiated a manual reactor trip. After tripping the reactor, all four RCPs were tripped and RCP seal bleed off was secured. Forced circulation was restored at 10:58 when a temporary modification was installed which aligned nitrogen to the IA system. No automatic engineered safety feature (ESF) actuations occurred during the event and none were required. All safety related buses remained energized from normal offsite power during and following the reactor trip. A solenoid coil failure on instrument air containment isolation valve (3JIAAUV0002) caused a loss of IA to the containment building. Consequently, the RCP seal bleed off isolation valve to the VCT closed which redirected RCP seal bleed off to the RDT and led plant operators to the decision to manually trip the reactor. The failed solenoid valve coil was replaced prior to restarting Unit 3 on December 5, 2009. Palo Verde Nuclear Generating Station reported a manual reactor trip of unit 2 in LER 529-2003-001-00 where instrument air was lost. The failure mechanism of the previous event was not similar to this event, and as such, the corrective actions for that event would not have prevented this event.