## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
1332010001 | Humboldt Bay 3 | 06/24/2010 | 07/14/2011 | ML11196005 | <strong>Lost Radioactive Calibration Standard</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2010, while conducting the quarterly inventory of radioactive sources in accordance with Humboldt Bay Power Plant (HBPP) Unit 3 Radiation Control Procedure (RCP) -6D, "Inventory and Controls for Radioactive Sources," it was discovered that source number HBS-498 was missing from the count room. HBS-498 is a mixed gamma source with an activity of 0.35 micro-curies as of August 9, 2010, and is used for the calibration of gamma detectors. The calibration source radionuclide composition yields an aggregate quantity of missing licensed material of 53 times the quantity specified in 10 CFR 20 Appendix C, which exceeds the reporting criterion of 10 times the quantity specified in Appendix C. At the time Revision 0 to this LER was submitted, it was reported that an extensive search had not been successful in locating the source to date (i.e., as of August 20, 2010); however, the missing source was located in Unit 3 on February 1, 2011. The root cause for this event has been determined to be inadequate Radiation Protection procedures to ensure control of radioactive sources. Procedure RCP-6D was revised to strengthen the source control process.
2192010001 | Oyster Creek | 10/07/2010 | 12/17/2010 | ML10362010 | <strong>Automatic Start of Emergency Diesel Generator due to Unexpected Trip of the ID Bus Normal Feed Breaker</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2010, the No. 2 Emergency Diesel Generator (EDG) automatically started and loaded onto the 'D' 4160V Safety-Related Bus (`D' Bus) due to a valid undervoltage start signal resulting from deenergization of the 'D' Bus. The "D" Bus main breaker opened during test equipment installation while performing a grid undervoltage channel functional test. The cause of the trip of the `D' Bus main breaker was test equipment failure from chemical attack on the plastic test jacks. Further investigation found that the timer connection jack showed signs of electrical pitting and arcing and was internally shorted to ground. After the test equipment was installed and prior to opening the test switch, the voltage on two of the undervoltage relays decreased below the set points for degraded voltage conditions, opening the normal feed breaker resulting in a valid undervoltage start signal for the No. 2 EDG. Due to the event, the procedure for test equipment installation will be revised to include pre-use testing of the timer to ensure that the battery of the digital timer is acceptable for use and that the terminals are not shorted or grounded. Additionally, a placard will be installed on the timers stating, "Caution - Do not use cleaners or solvents to clean terminals on this unit. Avoid contact with oil on terminals. This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) as an automatic ESF system actuation.
2192010002 | Oyster Creek | 12/23/2010 | 02/21/2011 | ML11060130 | <strong>Automatic Reactor Scram During Startup due to Low Main Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On December 23, 2010, with the reactor critical high in the Intermediate Range in the "Startup" mode, the reactor automatically scrammed on low main condenser vacuum. The cause was due to exceeding the 600 psig bypass reset enabling the low condenser vacuum trip prior to establishing the required vacuum. This bypass allows operation at reduced power below 600 psig during startup until adequate vacuum can be established in the main condenser. The main condenser low vacuum reactor protection scram signal processed when reactor pressure was raised above the 600 psig bypass function during reactor startup. A procedure requirement for confirming all main condenser low vacuum alarms and trips are reset prior to exceeding 500 psig ensures that a scram signal is not present. The direct cause of the event was determined to be inadequate procedure compliance by the Unit Reactor Operator (URO) in not verifying that all requirements were met prior to proceeding above 500 psig reactor pressure. Corrective actions include enhancement of operating procedures to clearly define key milestones requiring supervisor concurrence prior to continuing with reactor startup or shutdown. This event is being reported pursuant to: 10CFR50.73(a)(2)(iv)(A) due to an automatic actuation of the Reactor Protection System (RPS).
2202010001 | Nine Mile Point 1 | 11/10/2010 | 01/07/2011 | ML11019023 | <strong>Reactor Scram due to Inadequate Post Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>At 1056 on November 10, 2010, Nine Mile Point Unit 1 scrammed from full power operation due to closure of outboard Main Steam Isolation Valves (MSIVs) 01-03 and 01-04. Valves 01-03 and 01-04 closed following receipt of an invalid low-low reactor water level signal. The scram was the result of a combination of two latent preexisting plant conditions and performance of a quarterly instrument channel surveillance test. The first preexisting condition was misaligned connector pins on Grayboot splice connectors for outboard MSIV Channel 11 solenoid operated valves. The cause of the misalignment was determined to be insufficient rigor in the behaviors and knowledge (training) used in identifying appropriate post maintenance testing (PMT) requirements. The second preexisting condition was a misaligned contact spring in isolation logic Channel 12 relay 12K74 (General Electric (GE) Model CR305). The cause of this failure was excess material (plastic) left during fabrication of the relay's movable contact holder. Immediate actions were to repair the Channel 11 Grayboot splice connectors and replace Channel 12 relay 12K74. Training will be provided to planning personnel to ensure an adequate understanding of complex/redundant circuits for the proper determination of PMT requirements. Procedure/manuals governing Grayboot connector maintenance activities will be revised to include additional post assembly inspections and testing.
2442010001 | Ginna | 01/07/2010 | 03/05/2010 | ML10068012 | <strong>Two Fuel Assemblies Identified In Incorrect Spent Fuel Pool Locations Following Database Upgrade</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2010, during review of fuel moves in the Spent Fuel Pool (SFP) in preparation for a fuel assembly canister sipping evolution, Reactor Engineering personnel identified that two fuel assemblies were misclassified per Technical Specifications (TS) Limiting Condition for Operations (LCO) 3.7.13 and stored in incorrect locations. Event investigation identified that both assemblies, utilizing the 2001 methodology, had been placed in their correct storage location when last positioned in 2001. In 2005, the fuel database was migrated, updated and minor assembly burnup adjustments were made utilizing specific weights for each fuel assembly, resulting in a small (< 1%) change in the burnup of several early regions of fuel assemblies. At the time of the change, this was considered insignificant and was not evaluated against TS 3.7.13 figures. The upgraded database shifted the assemblies' burnups from slightly above the fuel classification line, to slightly below. The two fuel assemblies were relocated to assure compliance with LCO 3.7.13 on January 8, 2010. An additional corrective action includes completion of fuel burnup validation and reconciliation calculations. Based on the multiple conservatisms in the criticality analysis, the minor change in the calculated burnup, and the considerable margin in the soluble boron concentration in the spent fuel pool, there was no nuclear safety consequence caused by this event.
2442010002 | Ginna | 09/09/2010 | 12/03/2010 | ML10342029 | <strong>Unanalyzed Condition due to Leakage of Residual Heat Removal Pump Suction Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2010, after isolation of Residual Heat Removal (RHR) pump suction relief valves for maintenance, the shift operating crew identified that the rate of level rise in the Auxiliary Building (AB) sump tank had slowed. Prior to the isolation, leakage into the AB sump tank was estimated to be approximately 6 gph. The source of the elevated leakage was attributed to the RHR pump suction relief valves. The Technical Specification program for primary coolant leakage outside of containment has a limit of 2 gph and the current site dose calculation assumes Emergency Core Cooling System leakage of 4 gph. During certain accident conditions, with the continued leakage of RHR suction relief valves, the plant would have been in an unanalyzed condition for dose. An evaluation was performed upon identification of the condition and concluded that the safety system would have been able to perform its required function and no regulatory dose limits would have been exceeded. The cause of the leakage is attributed to damage of the valve seats due to excessive cycling. Excessive cycling was caused by a surveillance test alignment which subjected these valves to pressures in excess of the lift setpoint. Corrective Actions are described in section IV.
2472010001 | Indian Point 2 | 01/11/2010 | 03/09/2010 | ML10075025 | <strong>Automatic Reactor Trip as a Result of a Turbine-Generator Trip due to a Loss of Generator Field Excitation Caused by a Failed Exciter Rectifier</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2010, an automatic reactor trip (RT) was initiated as a result of turbine trip due to a loss of main generator excitation. The plant was stabilized in hot standby with decay heat being removed by the main condenser {SG}. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. Prior to the RT one of four rectifiers (#24) of the main generator excitation system was believed to be electrically isolated and its cooling was isolated to stop an existing cooling leak. Investigations determined the rectifier disconnect switch that was believed to be open remained in a closed condition. This condition allowed current to continue to flow through the 24 rectifier diodes and because there was no cooling water the diodes failed resulting in a loss of field voltage to the exciter actuating a trip signal. The direct cause of the RT was loss of generator field excitation due to loss of two diodes within the # 24 Generrex rectifier cabinet. The root cause was failure of management to implement critical decision making. A significant contributing cause was an improper lubricant used on disconnect switch contact surfaces. Corrective actions included a brief of station personnel on the event and lessons learned. A Generrex upgrade modification will be implemented including new disconnect switches in the spring 2010 refueling outage, case study training will be completed, computer based training (CBT) from the case study will be prepared and included in training curriculum, Alarm Response Procedure (2-ARP-SJF) and System Operating Procedure (2-SOP-24.4) will be revised for operation of the new disconnect switches, and maintenance personnel will be instructed on appropriate application of greases. The event had no effect on public health and safety.
2472010002 | Indian Point 2 | 03/09/2010 | 04/30/2010 | ML10131022 | <strong>Technical Specification Prohibited Condition Caused by Two Main Steam Safety Valves Outside As-Found Lift Setpoint Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2010, during surveillance testing, main steam safety valves (MSSV) MS-45C and MS-48C failed their As-Found lift set point test. Per the test, these valves must lift at +/- 3% of their required setting. Valve MS-45C lifted at 1108.6 psig, 12.6 psig outside its acceptance range of 1034 to 1096 psig. Valve MS-48C lifted at 1147.4 psig, 4.4 psig outside its acceptance range of 1077 to 1143 psig. All other MSSVs tested passed their test criteria and left within +/- 1% per test procedure. Technical Specification (TS) 3.7.1,"Main Steam Safety Valves," requires the MSSVs to be operable in accordance with TS Table 3.7.1-1 and Table 3.7.1-2 TS Surveillance Requirement (SR) 3.7.1.1 requires each MSSV be verified to lift per Table 3.7.1-2 in accordance with the In-service Testing Program. Operability of the MSSVs is defined as the ability to open within the set point tolerances. As these two valves were found outside their limit they were inoperable. The most likely cause of MS-45C outside its acceptance range was set point drift. The most likely cause of MS-48C outside its acceptance range was valve spring skew. The valves are subject to material property changes due to temperature, pressure and vibration which can affect set point accuracy and repeatability. Valve spring skew causes the spindle and internals to not remain perpendicular to the centerline of the valve producing frictional forces affecting the set point. Corrective actions included performing maintenance on both valves, adjusting as required, re-testing and left within the +/- 1% As-Left set point criteria. The MSSV maintenance procedure will be revised to provide more specific guidance on increasing valve guide bearing diameter. The event had no effect on public health and safety.
2472010003 | Indian Point 2 | 03/13/2010 | 05/10/2010 | ML10141029 | <strong>Inoperable Emergency Diesel Generators During Refueling Shutdown due to Inadvertent Isolation of Service Water Cooling Caused by Failure to Properly Verify the In-Service Cooling Header</strong><br /><i>Abstract:&nbsp;</i>On March 13, 2010, during a refueling outage work window protective tagout (PTO) of a service water (SW) header valve, the Balance of Plant (BOP) work window manager approved a PTO which authorized closure of a SW valve isolating SW to all three emergency diesel generators (EDG) from the SW 1-2-3 header. Upon closure of the SW valve, the control room (CR) received a EDG SW low flow alarm and directed the field operator to remove the PTO and un-isolate the header. The apparent cause was improper verification techniques by the BOP work window manager to determine current plant conditions. A contributing cause was the field operator did not verify that the actual valve line-up supported the expectation for current plant conditions. Prior to authorizing work, the BOP window manager checked the unit log for the scheduled swap of SW to header 4-5-6 and then authorized the PTO. Prior to SW isolation from the 1-2-3 header the field operator failed to verify that the SW 4-5-6 header was in-service. Corrective actions included coaching the BOP window manager on use of reliable sources for determining plant condition and the need for good communications with watch personnel, an operations stand down was performed to re-enforce management expectations on properly verifying plant conditions required for PTOs and understanding their impacts prior to implementation. An Outage Lessons Learned will be prepared to establish a method for implementation during outages that requires peer checking initial conditions for PTO's prepared for specific plant conditions. A review will be performed to determine if changes to tagging procedures or fleet practices are warranted. The event had no significant effect on public health and safety.
2472010004 | Indian Point 2 | 03/18/2010 | 05/14/2010 | ML10145011 | <strong>Plant Operation Outside Technical Specifications due to a Leak in the Reactor Coolant Pressure Boundary</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2010, at approximately 11:14 hours, while shutdown for refueling, boron accumulation was noted on the reactor coolant pump No, 1 seal bypass three quarter inch line 76 upstream of valve 256B. Based on the amount of boron, a conclusion was reached on April 5, 2010 that this condition could have existed during plant operation and therefore the plant could have been operating contrary to Technical Specification (TS) TS 3.4.13. The cause of the through wall indication was a five-sixteenths inch rounded weld defect introduced at the time of system construction which propagated through wall as a result of the system loading conditions during plant operations. There was no extent of condition since boric acid inspections of other locations did not identify any other instances of similar through wall defects. Corrective action was taken to repair the indication. There was no significant effect on public health and safety.
2472010005 | Indian Point 2 | 04/23/2010 | 06/22/2010 | ML10180026 | <strong>Technical Specification Prohibited Condition due to an Inoperable Control Room Ventilation System Caused by a Closed Normally Open Damper</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2010, during scheduled testing of the Control Room Ventilation System (CRVS), results showed less than required flow rates. An investigation and troubleshooting discovered the normally open "B" damper (CCRB1) on the suction duct for the carbon/HEPA filter and CRVS booster fans was closed preventing design flow rates. The damper was re-opened and secured in position and the CRVS re-tested satisfactorily. The bar used for maintaining the damper blocked open was found off and without a securing device on its attachment point. A review of past work history determined that on June 4, 2009, periodic testing was performed satisfactorily verifying the damper was open at that time. A review of work activities performed in proximity to damper (CCRB1) determined that during the spring refueling outage 2010, the "A" (CCRA1) damper and a ventilation duct section were replaced. The "A" damper is in very close proximity to the "B" damper. Maintenance concluded the "B" damper blocking bar was most likely contacted during damper "A" work activities. The apparent cause was Human Performance tools were not applied to ensure work activities did not affect other equipment in the area. Contributing cause was damper "B" had no blocking bar positive locking device. Corrective actions include reopening the "B" damper, re-testing to verify CRVS fully functional, and installation of a new cotter pin to secure the damper blocking bar. Coaching and a brief will be provided to applicable personnel on lessons learned and management expectations on use of human performance tools. The damper will be added to a check of list (COL) The event had no significant effect on public health and safety.
2472010006 | Indian Point 2 | 09/01/2010 | 10/30/2010 | ML10313003 | <strong>Safety System Functional Failure due to Inoperable Reactor Coolant Loop 21 and 22 Wide Range Hot Leg Temperature Indicators Credited for Remote Shutdown per Technical Specification 3.3.4</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2010, during performance of 2-PT-Q017C (Alternate Safe Shutdown Supply Verification to 23 CCP), the Reactor Coolant System (RCS) Wide Range Hot Leg Temperature Instruments TI-5139 (Loop 21) and TI-5141 (Loop 22) test readings were found out of specification. Technical Specification Basis 3.3.4 (Remote Shutdown), Table 3.3.4-1, Function 3.b Decay Heat Removal via Steam Generators, RCS Hot Leg (HL) Temperature requires one operable function. The RCS HL Temperature is also credited in Technical Requirements Manual (TRM) 3.3.D (Appendix R Alternate Safe Shutdown Instrumentation). After verification of proper performance of the test, Operations concluded the function for RCS HL Temperature was inoperable and entered TS 3.3.4 Action Statement A.1. The apparent cause was indeterminate. A Failure Modes and Effect Analysis identified two possible causes: PC-1) A test process failure. The test has had historical problems with the test sequence where the instruments are powered prior to start of the 23 CCP and starting currents impacted instrument readout. Also the instruments and circuit is required to warm up and stabilize after establishing power. To mitigate these effects the test was revised. PC-2) Component failure. A complete failure of the R/I converter (TM) could cause the condition but a successful re-test and calibration ruled out a complete failure. Corrective actions include re-performing test 2-PT-Q017C with engineering review, and evaluating re-test results and identifying any additional actions. The event had no effect on public health and safety.
2472010007 | Indian Point 2 | 09/03/2010 | 11/02/2010 | ML10313004 | <strong>Automatic Reactor Trip due to a Turbine Trip as a Result of a High Steam Generator Level Trip after Transition to Single Feedwater Pump Operation</strong><br /><i>Abstract:&nbsp;</i>On September 3, 2010, during a scheduled plant shutdown, an automatic reactor trip (RT) was initiated as a result of a turbine trip due to a high steam generator (SG) water level. All control rods did not indicate fully inserted as the Individual Rod Position Indicator (IRPI) for rod H-8 indicated 38 steps withdrawn and its rod bottom light failed to light. Rod H-8 was verified to be fully inserted by alternate means. All primary systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as designed due to automatic trip of the MBFPs as a result of closure of the MBFP discharge valves from the SG high level trip. The direct cause of the RT was a turbine trip on a high SG level. The root cause was inadequate design control of the proportional band and reset tuning settings for critical plant controllers. There was less than optimum controller settings on the MBFP speed controller, Feed Regulatory Valve (FRV) flow controllers, and the SG level controllers for low power operation. Significant corrective actions include: I&C procedures developed from I&C Preventive Maintenance documents have been reviewed to ensure that the instrument calibration requirements have been transferred into the I&C procedures, a list of critical controllers was generated and the Equipment Data Base (EDB) updated with known existing settings, I&C procedures will be reviewed to identify changes to ensure controller calibrations maintain required settings and procedures will be revised to incorporate testing of critical parameters, an engineering evaluation will be issued and the EDB updated in the work control program with findings on controller settings. The event had no effect on public health and safety.
2472010008 | Indian Point 2 | 09/13/2010 | 09/15/2011 | ML11265A22 | <strong>Safety System Functional Failure Due to Inoperable Refueling Water Storage Tank Low-Low Level Alarms</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2010, during performance of alarm checks, Panels SA-SC did not illuminate. The Refueling Water Storage Tank (RWST) low-low level alarms, required by Technical Specification 3.5.4, were rendered inoperable as a result of the loss of power. Operations entered procedure AOP-ANNUN-1 for failure of flight or supervisory panel annunciators and replaced a fuse found to be blown. Since the RWST low-low level alarms are required by Technical specifications, this was considered a safety system functional failure. Over current condition is the direct cause of the fuse blowing. The apparent cause of the fuse failure was fuse fatigue. The contributing cause was the 10 amp fuse for the annunciator circuit was marginally sized for its design load. Corrective actions include; performance of an evaluation of the fuse size for the Control Room (CR) Supervisory Panels which determined they were marginally sized and the 10 amp fuses should be replaced with 15 amp fuses, the annunciator panel fuses in the Control Room Supervisory Panels SAF, SAF-1, SBF-1, SBF-2 and SCF were replaced with 15 amp fuses. As an extent of condition the unit 3 annunciator circuit design will be evaluated. The event had no effect on public health and safety.
2472010009 | Indian Point 2 | 11/07/2010 | 06/21/2012 | ML12185001 | <strong>Automatic Reactor Trip due to a Turbine-Generator Trip Caused by a Fault of the 21 Main Transformer Phase B High Voltage Bushing</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2010, an automatic reactor trip (RT) was initiated as a result of a turbine-generator trip due to actuation of the main generator primary and back-up lockout relays. All control rods fully inserted and all primary systems functioned per design except for the 138 kV Station Auxiliary Transformer tap changer. The plant was stabilized in hot standby with decay heat being removed by the main condenser {SG}. Based on reports of two explosions an Alert was declared in accordance with the emergency plan which was terminated at 22:18 hours. There was no radiation release. The Emergency Diesel Generators did not start as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. The direct cause of the RT was due to actuation of the 86P and 86BU relays that sensed a fault from the failure of 21 main transformer (MT) as a result of a low impedance fault of the 345 kV Phase B bushing. The root cause was an internal failure of the phase B bushing due to a vendor design/manufacturing deficiency. Corrective actions include replacement and acceptance testing of the 21 MT, external visual inspections of the 22 MT HV bushings, Unit Auxiliary Transformer (UAT), Iso-phase bus and 345 kV feeder W95, testing of the 22 MT, UAT, Iso-phase bus and HV components. Damaged HV components were replaced. The bushings for the 21 and 22 MT were replaced with another manufacturers bushing. The event had no effect on public health and safety.
2492010001 | Dresden 3 | 10/11/2010 | 12/10/2010 | ML10355025 | <strong>OPRM Power Supply Failure During Maintenance Results in Unit 3 Automatic Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>During preparation for planned maintenance to perform testing of the Electrical Protection Assembly breakers, plant personnel transferred the Reactor Protection System from its normal power supply to its reserve power supply in accordance with approved plant procedures. While transferring from the normal to reserve power supply, the main control room received an expected half-scram signal due to the 3A RPS bus undergoing a dead-bus transfer. The breaker for the reserve power supply was closed which provided power to the 3A RPS bus. However, prior to the half-scram being reset, a power supply failure occurred in the Oscillation Power Range Monitoring System on the opposite RPS division. The concurrent half-scram signals resulted in a full RPS actuation. All control rods fully inserted. Reactor water level was maintained using the Condensate and Feedwater Systems. Reactor pressure was controlled using the Main Turbine Bypass Valves to the Main Condenser. Following the scram, the Auxiliary Power System transferred from its main power source to the reserve power source, as designed. During this transfer, the Unit 2/3 Emergency Diesel Generator automatically started. This automatic start occurred as the result of the EDG start logic momentarily sensing both the main power source breaker and the reserve power source breaker contacts being open concurrently. Since there was no undervoltage signal received, the automatic start of the EDG is considered invalid. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A), Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).
2492010002 | Dresden 3 | 11/01/2010 | 12/16/2011 | ML11362A39 | <strong>MSIV Leakage Exceeds Technical Specifications Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2010, plant personnel performed local leak rate testing of the Main Steam Line Isolation Valves (MSIVs). During the testing, it was identified that the valves' combined leakage exceeded the limits allowed by the plant's Technical Specifications. Based on the subsequent investigation, it is concluded that the primary contributor to MSIV leakage is seat ring wear. Seat ring wear is a normal occurrence in valves. Seats are hardfaced with Stellite or other hard materials to minimize the wear that occurs each time the plug closes onto the valve seat. The wear is associated with the high friction that develops between the plug and the seat as initial contact occurs, followed by sliding action as the plug centers itself in the seat. Seat wear results in misalignment between the plug and the seat ring due to a non-optimal valve design. The MSIVs that exhibited excessive leakage were internally inspected and machined. The as-left leakage rates were verified to be within Technical Specifications leakage limits. Discussions were held with the vendor regarding modification to the valve internals. Currently, a change to the valve design is being pursued through the plant modification process to modify the angle of the plug and the valve seat which should increase valve reliability. The safety significance of this condition is low. Three MSIVs exceeded the allowed limits for leakage as specified by the plant's Technical Specifications. The combined leakage of all main steam lines was within the limits allowed for overall primary containment leakage. The health and safety of the public was not compromised as a result of this condition.
2492010003 | Dresden 3 | 11/26/2010 | 01/25/2011 | ML11034019 | <strong>Steam Leak Results in HPCI Inoperability</strong><br /><i>Abstract:&nbsp;</i>On November 26, 2010, during plant startup from a refueling outage, High Pressure Coolant Injection (HPCI) system was being tested in accordance with the plant's technical specifications. Testing was commenced at approximately 1700 hours CST. The HPCI pump was started as indicated by rising pump discharge pressure and flow. During the test, the Main Control Room received fire detection system alarms for the HPCI pump room. The HPCI turbine had developed a steam leak from the turbine steam chest. The HPCI turbine was manually tripped and the testing secured until repairs were made. The cause of the steam leak is less than adequate torque on four studs/nuts. There are three potential factors that could have resulted in the torque values being less that required. These factors are: 1) the bolting relaxing during heat up and cool down between the low pressure and high pressure surveillance tests; 2) improper use of the hydraulic torque wrench; and 3) no additional torque was applied to bolts following the first pass. None of the above items could be confirmed. Following the shutdown of the system, maintenance personnel re-torqued the turbine steam chest. The system was re-started and the high pressure HPCI test was successfully completed. No leaks were identified. The safety significance of this condition is low. Automatic Depressurization and Low Pressure Emergency Core Cooling System were available and capable of providing makeup to the reactor vessel inventory. The health and safety of the public was not compromised as a result of this condition.
2502010001 | Turkey Point 3, Turkey Point 4 | 03/09/2010 | 06/07/2011 | ML11174A04 | <strong>Spent Fuel Storage Design Feature Assumptions are Exceeded</strong><br /><i>Abstract:&nbsp;</i>A condition prohibited by the Technical Specifications (TS 5.5.1.1.a) occurred in 2001 when the areal density of portions of the west panel in Unit 3 Region II Spent Fuel Pool (SFP) storage cell M-16 was determined to be less than the licensing basis analysis assumed minimum areal density of 0.006 gm-B10/cm2. The cause of the noncompliance with TS is Boraflex degradation. Interim measures were subsequently implemented to compensate for Boraflex degradation using empty storage spaces or rod cluster control assemblies to offset the Boraflex loss. A new licensing basis has been implemented that no longer relies on Boraflex as a neutron absorber in both Unit 3 and 4 SFPs. As a result of an extent of condition review, flow-damaged storage cells in both Unit 3 and 4 SFPs have been determined to not meet TS 5.5.1.1.c, which requires a nominal center-to-center spacing of 9.0 inches. The top of the cell walls in four Unit 3 and two Unit 4 SFP storage cells were discovered to be damaged in 2005. The cause is attributed to high cycle fatigue due to flow-induced vibration from the SFP cooling system discharge piping located above the affected cells. These cells have never been used to store fuel since they are inaccessible due to interference from the discharge piping. The affected and adjacent cells have been administratively removed from service. A license amendment request has been submitted to revise TS 5.5.3 regarding licensed fuel storage capacity.
2502010002 | Turkey Point 3 | 06/07/2010 | 08/05/2010 | ML10230038 | <strong>Fuel Transfer Pump Failure Renders 3B Emergency Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>During testing of the 3B Emergency Diesel Generator (EDG) on June 7, 2010, the 3B Fuel Transfer Pump (FTP) failed to start with a low level in the 3B fuel oil day tank. The test was terminated and the 3B EDG was shut down. The cause of the failure was due to binding of the FTP. The apparent cause of binding was lack of bearing lubrication. There was no preventive maintenance (PM) activity in place to ensure adequate bearing lubrication. Corrective actions include: 1) The 3B EDG FTP was replaced, 2) the 3A EDG FTP bearings were lubricated and the pump was run to verify functionality, 3) the 3A EDG FTP will be replaced, and 4) a PM activity will be developed to lubricate the Unit 3 EDG FTP bearings. A past operability assessment concluded that the 3B FTP and thus the 3B EDG were inoperable in accordance with the Technical Specifications (TS) for a period of about 1.5 months, which exceeds the allowed outage time of 14 days. This is a condition prohibited by the TS and reportable. The 3B EDG fuel oil day tank is equipped with a low level alarm that annunciates in the control room. The fuel available in the day tank at the low level alarm setpoint is sufficient for the 3B EDG to operate at design basis loads for at least 18 hours. Operators are directed to transfer fuel with an alternate transfer pump in accordance with an existing procedure in the event of failure of the 3B FTP. Thus, operators are notified and have sufficient time to take manual action to ensure the 3B EDG can perform its safety function. Therefore, while the 3B EDG was not operable in accordance with TS during the period of concern, it was functional, and thus this event has low safety significance.
2502010003 | Turkey Point 3 | 09/23/2010 | 11/19/2010 | ML10334051 | <strong>Reactor Trip due to Fault on 230kV Side of Generator Step-Up Transformer</strong><br /><i>Abstract:&nbsp;</i>On September 23, 2010, with Unit 3 operating at 100% power, an unplanned automatic reactor trip occurred at approximately 17:14:40 when an electrical flashover on the high side of the Unit 3 Generator Step Up (GSU) transformer occurred. All systems responded as designed. At 17:52, a notification (EN# 46274) was made to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) due to actuation of the Reactor Protection System with the reactor critical and 10 CFR 50.72(b)(3)(iv)(A) due to Auxiliary Feedwater System actuation. The Unit 3 reactor and turbine tripped due to a generator differential protection relay trip. This event was entered into the Corrective Action Program as AR 582206. All systems functioned as normal with the exception of Control Rod G5 in Control Bank A which indicated 18 steps. The unit entered and exited E-0 "Reactor Trip" and ES-0.1 "Reactor Trip Response." All 4kV buses had power from the Unit 3 Start Up Transformer. Heavy weather (rain and wind) conditions existed at the time of the reactor trip. The root cause was an external flashover to ground of the "C" phase high voltage (HV) bushing. The Unit 3 GSU Transformer High Voltage Bushings (all phases) were replaced with longer bushings. Transformer Surge Arresters, Stand Off Insulators, Conductors, and Generator Radial Lead Seals were replaced.
2502010004 | Turkey Point 3, Turkey Point 4 | 10/01/2010 | 04/04/2011 | ML11109A03 | <strong>Inoperable Main Steam Line Accident Monitoring Instrumentation-Supplement</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2010, Turkey Point Unit 3 was in Mode 6 due to refueling outage, and Turkey Point Unit 4 was operating in Mode 1. Radiation Monitor RAD-6426, with Eberline Data Acquisition Monitor (DAM-1) and High Range Noble Gas Detector Assembly SA-9, common to Turkey Point Units 3 and 4, is required to be OPERABLE in Modes 1 through 3, in accordance with Technical Specification (TS) 3.3.3.3. During the process of researching the design basis for a replacement monitor, it was identified that insufficient levels of noble gases are transported to the RAD-6426 detector to provide a detectable concentration of noble gases. On October 1, 2010, it was determined that RAD-6426 was unable to be restored to an OPERABLE status within 7 days as specified by the TS. The sampling transport system does not deliver a representative sample of noble gases released at the main steam line safety valves and/or atmospheric dump valves and has not since the original installation of the monitor in 1981, and as such it has not met the intent of the TS requirements. The latent design deficiency associated with the sample transport system is due to inadequate DAM-1 design, design verification, and functional testing. This condition is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) due to any operation or condition which is prohibited by the plant's TSs. Turkey Point complied with the TS action requirements by initiating the preplanned alternate monitoring method of appropriate parameters and by submitting a Special Report within the required TS action time. Corrective actions include actions to replace this monitor.
2502010005 | Turkey Point 3, Turkey Point 4 | 10/25/2010 | 12/22/2010 | ML10362011 | <strong>Containment Liner Through Wall Defect Due to Corrosion</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2010, during the Unit 3 Cycle 25 Refueling Outage, containment liner plate degradation in the reactor pit area was detected during the ASME XI, IWE inspection. Augmented visual and ultrasonic examinations were performed. Thinning of the liner and twelve through wall holes (all in close proximity) were discovered. Design Features Technical Specification 5.2.1f requires a nominal thickness of the containment steel liner of 0.25 inches. This condition was reported to the NRC October 25, 2010 (Event number 46362) as a condition resulting in a serious degradation of the containment liner. A liner plate section was replaced and inspected in accordance with the ASME Code. A root cause analysis was performed, including a metallurgical failure analysis. The root cause was determined to be failure of the coating system which was not designed for periodic immersion service. In order to prevent recurrence, the lower region of the reactor pit will have a coating system suitable for immersion applied. Previous boric acid inspections, ASME XI, subsection IWE, and Appendix J visual inspections did not detect this degradation. Actions have been identified to improve the liner inspection programs. The root cause extent of condition analysis for this condition revealed that Unit 4 has had similar issues. A through wall hole about 1/16" in diameter was discovered November 25, 2006 in the Unit 4 reactor sump pit. The hole was evaluated as non-significant and repaired.
2502010006 | Turkey Point 3 | 11/15/2010 | 01/13/2011 | ML11027010 | <strong>Manual Reactor Trip and Auxiliary Feedwater Actuation in Response to Loss of Circulating Water Pump</strong><br /><i>Abstract:&nbsp;</i>With Unit 3 at 100% power, at approximately 0604 on November 15, 2010, the reactor was manually tripped when the 3A2 Circulating Water Pump was stopped due to an overheated packing gland. The manual trip was in anticipation of an automatic turbine/reactor trip on low condenser vacuum. While Auxiliary Feedwater automatically actuated, a train of normal feedwater remained available to feed the steam generators. During the reactor trip, the 3B Steam Dump to Atmosphere valve opened automatically, as designed, but failed to close on operator demand as required by procedure. It was locally isolated with a manual isolation valve stopping the cooldown. The reactor coolant system (RCS) temperature was stabilized at 487F and borated as required by procedure. The RCS returned to normal operating temperature and pressure and the unit was stabilized in Mode 3. Two root causes were identified: 1) There were inadequate administrative controls for pump packing consolidation for applicable non-nuclear safety (NNS) related pumps, and 2) A healthy skepticism and recognition of risk was not adequately considered or communicated. Corrective actions include: 1) Incorporate information on packing consolidation break-in period, system perturbation information, temperature bands, and minimum/maximum levels for packing leak-off for NNS pumps into the post maintenance testing procedure, 2) implement plan for Recommendation 1 of SOER 10-2: Engaged, Thinking Organizations, 3) inspect Unit 3 and 4 pumps that utilize packing, 4) replace 3A2 CWP pump shaft packing and packing follower, and 5) repair 3B Steam Dump to Atmosphere valve.
2512010001 | Turkey Point 4 | 11/26/2009 | 01/25/2010 | ML10035039 | <strong>Two Shutdown Bank Rods Were Dropped from Fully Withdrawn Position</strong><br /><i>Abstract:&nbsp;</i>On November 26, 2009 at approximately 2018 hours, during performance of Rod Position Indication System Replacement Testing (in Mode 3) and while withdrawing A and B control rod banks, the New Analog Rod Position Indication (NARPI) System indicated rods H6 and H10 dropped from fully withdrawn Shutdown Bank B (Group 2). Annunciator B-9/3 "Shutdown Rod Off Top" annunciated and the associated "Rod Bottom Lights" illuminated. The NARPI Testing was stopped. Troubleshooting began to determine whether the problem was with NARPI or the Rod Control System. Instrumentation and Control personnel checked voltages, recorded current traces, and reported that both rods dropped. ONOP-028.3, "Dropped RCC" was entered and the reactor was manually tripped at 2340 inserting all rods. At the time of the trip, the reactor was in mode 3 (Keff less than 0.99). A 10 CFR 50.72 8-hour report (EN# 45522) was made to the NRC. The RCS boron concentration was maintained at or above the Minimum Shutdown Boron Concentration specified in the NARPI test procedure (4-PTP-028.2). The apparent cause of the failure was a high resistance connection. This event is considered to be reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), due to manual actuation of the Reactor Protection System to trip the reactor, inserting all rods.
2512010002 | Turkey Point 4 | 01/11/2010 | 03/11/2010 | ML10083009 | <strong>Reactor Trip Resulting from Steam Generator Feedwater Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2010, at approximately 1058 an unplanned manual reactor trip on Unit 4 was initiated due to Steam Generator (SG) level being greater than 75%. The unit was stabilized in Mode 3 on off-site power with main feed for decay heat removal. The unit trip was precipitated by the manual stop of the 4A SG feedwater pump (SGFP) due to a degrading oil inventory. Plant response to the loss of the 4A SGFP and the subsequent reactor trip was as expected. The root cause of the loss of the 4P1A SGFP lube oil level was determined to be unresponsive seal water injection controls to the pump outboard bearings which resulted in inadequate seal water injection flow to the 4P1A SGFP outboard seal coincident with SGFP bearing cavity drain blockage. Corrective actions include: 1) Replace obsolete Unit 3 and 4 SGFP seal water hand controller stations with more responsive controller stations. 2) A preventive maintenance activity will be established to verify the bearing seal cavity drains are clear on a periodic basis, after completion of maintenance and prior to SGFP start following an outage.
2512010003 | Turkey Point 4 | 05/10/2010 | 07/09/2010 | ML10203025 | <strong>Damaged Speed Sensor Caused the 4A Emergency Diesel Generator to be Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2010, during a normal start for local parallel operation of the 4A Emergency Diesel Generator (EDG) for a test, frequency unexpectedly increased to approximately 63 Hz. Consequently, a normal shutdown of the 4A EDG was initiated. While shutting down, the 4A EDG locked out due to "Piston Cooling Oil Low Pressure." The apparent cause of the 4A EDG's uncontrolled speed/frequency increase and subsequent lock-out is a failure of the speed sensing magnetic pickup due to being set too close to the engine flywheel. A change to the maintenance procedure will be made to ensure that the run-out of the engine flywheel gear teeth is checked and that the magnetic pickups are set with adequate clearance from the top of the highest gear tooth. The other three EDGs were assessed and determined not to be affected. Since the magnetic pickup was set during a maintenance activity, the 4A EDG was considered inoperable from the start of maintenance until the magnetic pickup was repaired. This resulted in a period of inoperability of approximately 16.9 days. The risk impact associated with the approximate 16.9 days the 4A EDG was considered inoperable results in an ICCDP (Incremental Conditional Core Damage Probability) of 5.6E-08 and an ICLERP (Incremental Conditional Large Early Release Probability) of 9.8E-11, well below NRC thresholds. Therefore, safety significance is considered to be very low.
2512010004 | Turkey Point 4 | 09/08/2010 | 11/05/2010 | ML10333018 | <strong>Reactor Trip During Replacement of Degraded Relay in the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On September 8, 2010, with Unit 4 operating at 100% power, an unplanned automatic reactor trip occurred at approximately 13:45 during replacement of the 4B Reactor Protection System (RPS) Left Turbine Stop Valve Closure Logic Relay 4-SL-X-B [JC:RLY]. All rods fully inserted and all systems responded as designed and the unit was stabilized in Mode 3. At 15:52, an 4-hour report (EN# 46235) was made to the NRC Operations Center in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) due to an automatic reactor trip and actuation of the Auxiliary Feedwater System. The reactor trip was caused by the opening of the 4B RPS trip breaker due to the de-energizing of reactor trip relays RT-9 and RT-10 when the two leads were lifted off terminal 1 of relay 4-SL-X-B during the replacement evolution. Deficiencies in the work order package and guiding procedure failed to establish and/or verify the plant conditions required to successfully complete the evolution. Corrective actions included replacement of the degraded relay 4-SL-X-B and revisions to the work order package and guiding procedures to ensure the Reactor Trip Bypass Breaker shall be in the closed position when replacing any reactor protection relay while the unit is in operational Modes 1 or 2.
2512010005 | Turkey Point 4 | 09/09/2010 | 10/12/2010 | ML10288004 | <strong>Failure of Group Step Counter with Valid Manual Actuation of the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2010 at approximately 16:34 hours, the unit entered Technical Specification (TS) 3.1.3.3 Action as a result of the Control Bank C Group 1 Step Counter failing to increment. The reactor was subcritical in Mode 3 progressing to reactor startup. The reactor trip breakers were opened as required by the Action of TS 3.1.3.3. The TS requires that the reactor trip breakers be opened if the Bank demand counters (group 1 and group 2) are not within +/- 2 steps of each other. All rods fully inserted. The unit remained in Mode 3. This was a manual actuation of the Reactor Protection System. Therefore, an 8-hour report (EN# 46246) was made in accordance with 10 CFR 50.72(b)(3)(iv) to the NRC Operations Center. The apparent cause of the event was failure of a Step Counter Battery. The Group Step Counters are driven by lithium ion batteries. The failure of the battery was unpredictable, with minimal consequences. There was no reason to expect early failure. The failed battery was replaced, along with the remainder of the Step Counter Batteries. A five year search of the plant, INPO, and NRC databases was performed and did not reveal any previous similar occurrences. Therefore, no further actions have been recommended.
2512010006 | Turkey Point 4 | 09/21/2010 | 11/19/2010 | ML10333018 | <strong>Automatic Reactor Trip due to Spurious High Pressurizer Pressure Trip Signal</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2010, at approximately 2017, with Turkey Point Unit 4 operating at 100% power, an unplanned automatic reactor trip occurred while the quarterly surveillance for the Channel II High Pressurizer Pressure Protection Loop (P-4-456) was in progress. The cause of the trip was attributed to Channel I spurious trip signal of the High Pressurizer Pressure Protection Loop (P-4-455) coincident with Channel II being already tripped due to the surveillance procedure. All rods fully inserted and all systems responded as designed and the unit was stabilized in Mode 3. At 2228, a report (EN#46265) was made to the NRC per 10 CFR 50.72(b)(2)(iv)(B) for actuation of Reactor Protection System with the reactor critical and per 10 CFR 50.72(b)(3)(iv)(A) for actuation of the Auxiliary Feedwater System. Excessive separation found in the electrical bifurcated pins of the ELCO connectors of the NUS instrument Comparator (PC-4-455A) module caused the Channel I spurious trip signal. Corrective actions include replacement of Comparator PC-4-455A, providing formal training for Maintenance personnel to properly inspect NUS modules with ELCO connectors, adding quantitative criteria in site procedures to perform connector inspection, and inspecting other NUS module connectors installed at the plant that could have electrical pins with excessive separation.
2512010007 | Turkey Point 4 | 10/01/2010 | 11/24/2010 | ML10342010 | <strong>Unplanned Entry into TS 3.0.3 due to Misalignment of Unit 3 HHSI Pump Discharge Valves</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2010, with Unit 3 in Mode 6 and Unit 4 in Mode 1 operating at 100% power, an unplanned entry into Technical Specification 3.0.3 occurred at approximately 09:51 when the Unit 4 Head Safety Injection (HHSI) system was at a reduced capability due to a misalignment of the Unit 3 HHSI pump discharge valves creating a flow path from the Unit 4 Refueling Water Storage Tank (RWST) through the HHSI pumps to the Unit 3 cold leg injection lines, which were open to the refueling cavity. The Unit 4 HHSI system was at a reduced capability rendering it inoperable from approximately 09:51 until 10:27 (36-minutes) when the HHSI isolation valve 3-867 was closed. The event was discovered at approximately 10:05. An 8-hour report (EN# 46303) was made to the NRC Operations Center in accordance with 10 CFR 50.72(b)(3)(v)(D). The causes of the event include: 1) no administrative control of the operating unit Safety Injection flowpath with one unit shutdown, and 2) poor organizational processes resulted in failure to recognize the requirements to maintain Emergency Core Cooling System (ECCS) flowpath integrity, during periods when the opposite unit is in a low pressure condition. Corrective actions include revision of processes and procedures that control ECCS flowpath integrity during periods when the opposite unit is in a low pressure condition.
2512010008 | Turkey Point 4 | 12/09/2010 | 10/20/2011 | ML11297A01 | <strong>Manual Reactor Trip due to Condenser Tube Leak</strong><br /><i>Abstract:&nbsp;</i>At 22:00 on December 9, 2010, Unit 4 had indication (high sodium) of a condenser tube leak. A rapid power reduction to less then 5% was commenced in accordance with plant procedures as the sodium levels increased to greater than 250 ppb (action level 3). Chemistry confirmed that the high sodium level was due to salt water intrusion from the 4BN Main Condenser tube bundle. A management decision was made to shutdown the reactor in accordance with plant procedures by manually opening the reactor trip breakers at about 22:58:13 from approximately 17.5% power. All systems functioned as designed and there was no impact on the health and safety of the public. The NRC was notified (Event Number 46471) at approximately 01:25 (EST) on December 10, 2010. Corrective actions involved plugging the failed tube and four other tubes with minimal indications. The failed tube was removed during the next refueling outage (RFO PT4-26) and sent for analysis. The analysis indicated the root cause to be axial cracking caused by high cycle fatigue. Eddy Current Testing was performed during RFO PT4-26 with conservative plugging criteria to plug all tubes with indications of greater than 50% wall-loss. Long term, the Unit 3 and Unit 4 condenser tube bundles are currently planned for replacement under the Extended Power Uprate Project.
2542010001 | Quad Cities 1 | 01/28/2010 | 03/29/2010 | ML10097002 | <strong>Electromatic Relief Valve Main Disc Failure</strong><br /><i>Abstract:&nbsp;</i>On January 28, 2010 while performing refurbishment activities on Electromatic Relief Valve (ERV) [RV] 3C, recently removed from Unit 1, it was discovered that the valve main disc would not open during its inspection. During disassembly of the valve a slight gap was found between the disc retainer and the main disc guide. In addition, circumferential grooves were found worn into the main valve disc guide. This condition had allowed the main disc seal rings to slip into a groove in the disc guide which effectively locked the main disc in the closed position. With the ERV main disc locked in the closed position, the valve would not have operated in manual, automatic overpressure protection, or the Automatic Depressurization System (ADS) mode of operation. Upon further investigation, the ERV disc retainer was determined to have been improperly torqued during manufacturing valve assembly, which allowed the gap, between the disc retainer and the main disc guide to cause the main valve disc guide to be loosely seated in the valve cavity, allowing the fretting wear to occur over time. The ERV was in service from April 2005 to April 2009. Although the exact time of failure of the ERV cannot be determined, the 3C ERV was estimated to be inoperable for greater than 14 days and likely caused the Required Actions and associated Completion Times to not be met for Technical Specifications (TS) 3.4.3 Action B (Safety and Relief Valves), TS 3.5.1 Action I (ECCS-Operating), and TS 3.6.1.6 Action B (Low Set Relief Valves). This event is therefore, a past operation or condition prohibited by the plant Technical Specifications, and is therefore reportable per 10 CFR 50.73(a)(2)(i)(B).
2542010002 | Quad Cities 1 | 08/12/2010 | 10/06/2010 | ML10286182 | <strong>Unit 1 Reactor Scram Due to Turbine Trip from Low Condenser Vacuum During Main Condenser Flow Reversal</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2010, Quad Cities Unit 1 performed a scheduled reversal of the direction of flow through the main condenser [KE]. During the flow reversal, two valves [ISV] failed to operate, resulting in low condenser vacuum. In response to the low condenser vacuum, the main turbine [TRB] tripped and the reactor [RCT] scrammed. There were no complications during the turbine trip and reactor scram, and all systems functioned as required. The root cause for this event was determined to be foreign material from the manufacturing process in an auxiliary contact unit [29] for the breaker [BKR] of one of the valves involved in the main condenser flow reversal process. This caused the valve to fail to open. A contributing cause to the event was the setpoint of a thermal overload [TS] for a separate main condenser flow reversing valve that did not anticipate the specific conditions of this event and caused this valve to trip at mid-position. The reactor and turbine responded as designed to the low condenser vacuum. Although the turbine trip occurred prior to the expected vacuum level, it was determined that this is due to the location of the instrument taps in the condenser for the turbine trip being at a higher elevation than the location of the instrument taps for the reactor protection system (RPS) [JD] and main control room [NA] indication. Corrective actions included auxiliary contact and thermal overload replacement and testing, procedure changes, and reviews for potential setpoint and design changes. The safety significance of this event was minimal. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram or reactor trip.
2552010001 | Palisades | 01/19/2010 | 03/19/2010 | ML10081040 | <strong>Potential Loss of Safety Function due to Service Water Pump Shaft Coupling Failure</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2009, at 0908 hours, with the plant in Mode 1 at 100% power, service water system (SWS) pump, P-7C, failed to deliver discharge pressure. Investigation into the failure revealed a broken coupling between the top line shaft and the packing shaft. As a result, a 72-hour limiting condition for operation (LCO) was entered in accordance with Technical Specification (TS) 3.7.8, due to one SWS train being inoperable. The TS 72-hour LCO was exited after approximately 71 hours on October 2, 2009, at 0822 hours when repairs to P-7C had been completed. Subsequent metallurgical analysis determined that the coupling failed due to intergranular stress corrosion cracking (IGSCC) that was caused by the coupling being too hard. On January 19, 2010, an Entergy Nuclear Operations Inc. evaluation concluded that, based on the failure mechanism of the coupling, P-7C would have been unable to operate satisfactorily for the required 30-day mission time. Therefore, it was inoperable. This 30-day period of inoperability corresponds to 720 hours of runtime, starting on August 23, 2009, and the failure of the coupling on September 29, 2009. Additionally, during the period P-7C was inoperable, the redundant SWS train was inoperable for a period of approximately six hours on September 2, 2009, due to routine maintenance activities on P-7B. Therefore, both SWS trains were simultaneously inoperable for a period of time not allowed by TS 3.7.8. This occurrence is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(v)(B) and 10 CFR 21.21(c).
2552010002 | Palisades | 08/23/2010 | 10/18/2010 | ML10292010 | <strong>Condition that Could Have Prevented the Fulfillment of a Safety Function</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2010, at approximately 2210 EDT, with the plant in Mode 1 at 100% power, the control room received a turbine protection and bleeder trip circuits undervoltage alarm. Upon investigation, 125 VDC datalogger distribution panel ED-205 was found to be de-energized, causing turbine protection trip relays RELAY-305-L and RELAY-305-R to become inoperable. These two inoperable relays disabled the reactor trip function of the Reactor Protective System upon a loss of turbine generator load. The control room operators determined, after consulting with other plant staff, that the inoperable loss of load reactor trip function required entry into Technical Specification (TS) Limiting Condition for Operation (LCO) 3.3.1 Condition C. The NRC resident inspector questioned whether the entry into TS LCO 3.3.1 Condition C was a non-conservative TS entry. The inspector believed that TS LCO 3.3.1 Condition E should also have been entered because at least two loss of load trip channels were inoperable and that TS LCO 3.0.3 should have been entered because TS LCO 3.3.1 provided no Required Action when more than two loss of load trip channels are inoperable. Follow-up review by plant staff concluded that TS LCO 3.3.1 Condition E and TS LCO 3.0.3 should have been entered when the loss of load reactor trip was found inoperable. This occurrence is reportable under 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(v)(A).
2552010003 | Palisades | 10/01/2010 | 11/22/2010 | ML10326046 | <strong>Unanalyzed Condition Discovered due to Non-Compliance with 10 CFR 50 Appendix R</strong><br /><i>Abstract:&nbsp;</i>On October 1, 2010, during a corrective action program extent of condition review, a postulated Appendix R fire scenario was identified in three fire areas that could potentially result in the loss of safety-related 2400 volt alternating current (VAC) bus 1C and/or bus 1 D, with subsequent loss of equipment credited for Appendix R compliance to support safe shutdown in the event of such a fire. As part of the Appendix R common power supply analysis, coordination between load breakers and feeder breakers is required to protect the power supply because of a fire-generated fault on the load power cable. The fire scenario identifies how this coordination could be defeated on the safety-related 2400 VAC buses. The scenario occurs when the load breaker's control circuit is damaged by a fire which could potentially open the control circuit fuses and disable the breaker's trip circuit containing the over-current relay protection. The same fire could subsequently damage the 2400 VAC power cables, causing a cable fault. The load breaker cannot clear the fault with the trip circuit control power disabled. The clearing of the cable fault would propagate upstream to the next coordinated breaker, which would result in the bus feeder breaker opening, causing a loss of the 2400 VAC buses and associated electrical loads. Compensatory actions taken include hourly fire watch tours and a standing order to immediately sound the site fire alarm and call out the fire brigade for a control room alarm that indicates a fire in any of the affected three fire areas.
2552010004 | Palisades | 11/09/2010 | 01/07/2011 | ML11007045 | <strong>Cracks Discovered in Emergency Diesel Generator Turbocharger Support Plates</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2010, Palisades' plant personnel discovered two cracks in the turbocharger vertical support plates of the 1-1 emergency diesel generator (EDG). Probable causes for the cracks in the support plates are high-cycle vibration and thermal cycling during engine runs. With two cracks in the turbocharger vertical support plate, an operability evaluation determined the 1-1 EDG was operable-DNC. Operable-DNC is a condition where a Technical Specification (TS) system structure or component is operable, but a degraded or nonconforming condition exists that does not require compensatory measures. On November 4, 2010, during repair of the two previously identified cracks, a third crack in a vertical support plate was discovered. Weld repairs were completed on all three cracks on November 4, 2010. Due to the discovery of the third crack, on November 9, 2010, Entergy Nuclear Operations, Inc. (ENO) and Fairbanks Morse, supplier of the 1-1 EDG, concluded additional detailed evaluations were required to maintain reasonable assurance the 1-1 EDG would have been able to operate satisfactorily for the required 30-day mission time. Therefore, without reasonable assurance of past operability, this situation is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Due to the ongoing evaluation of the condition, ENO may request a cancellation of this LER, or a supplement will be submitted to provide additional details.
2592010001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 08/09/2010 | 12/26/2012 | ML13002A05 | <strong>Units 1, 2, and 3 Appendix R Safe Shutdown Instruction Procedures Contain Incorrect Operator Manual Actions</strong><br /><i>Abstract:&nbsp;</i>On August 9, 2010, during a review of design input calculations in support of the NFPA 805 transition from the 10 CFR 50 Appendix R licensing basis, it was discovered that two 4kV breakers that should be tripped and/or tripped and isolated during certain Appendix R fires were not identified in the calculation summary. Specifically, for a postulated fire in Fire Zone 01-03, Breaker 14 on 4kV Shutdown Board B should be tripped. Also, for a postulated fire in Fire Zone 02-03, Breaker 19 on 4kV Shutdown Board A should be isolated and tripped in lieu of Breaker 10. Therefore, the Safe Shutdown Instructions (SSIs) for certain Appendix R fires do not contain two required operator manual actions (OMAs) to trip and/or trip and isolate these breakers. These OMAs are necessary to prevent spurious load additions on the credited Emergency Diesel Generator (EDG) during certain Appendix R fires. Without operator action to trip these breakers, spurious actuations could add loads on the credited EDG beyond what has been analyzed. The cause of the omissions was that certain 4kV electrical loads identified in the appendices and attachments of the calculation were not transposed correctly to the main body of the calculation and subsequently were not identified in successor calculations and operating procedures.
2592010002 | Browns Ferry 1 | 09/16/2010 | 05/20/2011 | ML11144A28 | <strong>Drywell Pressure Instrument Channel Inoperability due to Improper Instrument Tubing Slope</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2010, it was determined that a condition initially identified on December 8, 2008, reflected inoperability of a drywell pressure channel for longer than allowed by Technical Specifications. Subsequent review for extent of this condition identified that the inoperable condition existed from October 2, 2008, until corrected on December 9, 2008. Additionally, a subsequent occurrence of an inoperable drywell pressure channel between May 25, 2010, and October 6, 2010, was discovered. Corrective actions taken on December 9, 2008, and October 6, 2010, involved purging trapped water in the instrumentation sensing line. The immediate cause was improperly sloped instrument sensing lines that allowed water to condense and collect in the sensing lines, resulting in non-conservatively biased instrumentation output signals. The instrument sensing lines were modified during the Cycle 8 refueling outage (Fall 2010) to eliminate water traps and provide proper slope to assure no accumulation of condensed water. The condition resulted from modifications in 2005 which did not assure adherence to the design specifications for proper instrument sensing line slope. The cause for improper instrument slope is attributed to human error and unclear procedural guidance. The Browns Ferry procedures and processes have been revised to clearly require the verifications for proper slope.
2592010003 | Browns Ferry 1 | 10/23/2010 | 09/30/2013 | ML13275A13 | <strong>Failure of a Low Pressure Coolant Injection Flow Control Valve</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2010, during a refueling outage for Browns Ferry Nuclear Plant (BFN) Unit 1, the Tennessee Valley Authority (TVA) discovered that a Residual Heat Removal (RHR) Loop II low pressure coolant injection (LPCI) flow control valve failed to open while attempting to establish shutdown cooling (SDC) while in Mode 3. Operations personnel declared RHR Loop II inoperable for ECCS and placed RHR Loop I in service for SDC. <br /><br /> Unit 1 Technical Specification (TS) limiting condition for operation (LCO) 3.5.1, Emergency Core Cooling System (ECCS) - Operating, requires both RHR loops of LPCI to be operable in reactor Modes 1, 2, and 3. Investigation of the valve failure to open determined that the root cause was a manufacturer's defect resulting in undersized disc skirt threads at disc connection. Based on causal analysis information, the stem-to-disc separation occurred sometime before November 2008. Thus, RHR Loop II was inoperable for a period longer than the 7 days allowed by TS 3.5.1. This condition is reportable as both operations prohibited by TS and as an event or condition that could have prevented fulfillment of a safety function. <br /><br /> This report constitutes a Part 21 notification.
2592010004 | Browns Ferry 1 | 10/27/2010 | 09/30/2013 | ML13275A14 | <strong>Residual Heat Removal System Pump Motor Failure</strong><br /><i>Abstract:&nbsp;</i>On October 27, 2010, at approximately 1240 hours Central Daylight Time (CDT), the 1C Residual Heat Removal (RHR) pump motor tripped while in shutdown cooling (SDC). Operations personnel received reports of smoke coming from the 1C RHR pump room and responded in accordance with Emergency Plan Implementing Procedure (EPIP) - 17, "Fire Response Procedure," and Abnormal Operating Instruction (A01) 0-A01-26-1, "Fire Response." By approximately 1245 hours CDT, Operations personnel declared the 1C RHR pump inoperable, and re-established SDC by placing the 1A RHR pump in SDC. Because there was no fire, Operations personnel exited 0-A01-26-1 and EPIP-17. <br /><br /> Investigation results indicate that the failure to correct a degraded condition of the pump motor caused the motor to trip, which rendered the pump inoperable for greater than Technical Specifications allowed outage times. <br /><br /> The immediate cause of this event was a dynamic physical rotor/shaft bow that caused internal rubbing that led to the mechanical failure of the motor. The root cause was a dynamic rotor bow that was misdiagnosed and treated as a rotor unbalance condition during motor refurbishment.<br /><br /> The 1C RHR pump motor was replaced and tested successfully.
2592010005 | Browns Ferry 1 | 12/06/2010 | 04/01/2011 | ML11096074 | <strong>Safety/Relief Valves As-Found Setpoints Exceeded Technical Specification Lift Pressure Values</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2010, the Tennessee Valley Authority (TVA) determined, as a result of offsite laboratory surveillance testing, 3 of 13 Browns Ferry Nuclear Plant - Unit 1 Safety/Relief Valves (S/RVs) mechanically actuated at pressures greater than the allowed 3 percent above their Technical Specification (TS) setpoint. Therefore, the S/RVs were inoperable for an indeterminate period during the previous Cycle 8 period of operation. Unit 1 TS Limiting Condition for Operation 3.4.3 requires the safety function of twelve (12) S/RVs to be operable in reactor modes 1, 2, and 3. With one or more required S/RVs inoperable, the unit is required to be placed in Mode 3 (hot shutdown) within 12 hours and in Mode 4 (cold shutdown) within 36 hours. Since 3 of 13 S/RVs actuated above their TS setpoint plus the 3 percent allowance, it is probable that Unit 1 operated longer than allowed by the TS. There are two causes of the S/RVs exceeding the setpoint lift tolerance: (1) corrosion bonding between the disc and seat while the valve is in service, and (2) the thermal heat-up conditions used in the laboratory testing were not consistent among all 13 S/RVs. TVA has revised administrative controls to ensure that the test facility provides a consistent heat-up rate for all 13 S/RVs tested pursuant to TS surveillance requirement 3.4.3.1. TVA will continue the application of the platinum coating to address corrosion bonding between the seat and disc.
2602010001 | Browns Ferry 2 | 02/25/2010 | 04/26/2010 | ML10118025 | <strong>Condition Prohibited By Technical Specifications When Two Emergency Core Cooling Systems, Loops I and II of the Residual Heat Removal System Low Pressure Coolant Injection System, Became Inoperable</strong><br /><i>Abstract:&nbsp;</i>Back leakage through Emergency Core Cooling System (ECCS) Residual Heat Removal (RHR) Loop II low pressure coolant injection (LPCI) valves resulted in the water in the pipe upstream of the inboard valve to be at an elevated temperature with respect to ambient conditions. To prevent voiding in the piping, monitoring with trigger points/actions were established. RHR Loop I was inoperable for scheduled maintenance. On February 25, 2010, at 1840 hours Central Standard Time, a trigger point was met, and Operations personnel entered Technical Specifications (TS) Limiting Condition for Operation (LCO),3.0.3 based on entry into TS LCO 3.5.1 Condition H when RHR Loops I and II were inoperable. Operations personnel began lowering reactor power at 1935 hours because the conditions requiring entry into TS LCO 3.0.3 could not be corrected within an hour. TS LCOs were exited at 2000 hours when RHR Loop II system pressure was restored to ensure that the piping would remain filled. At 2320 hours, reactor power was returned to 100 percent. The cause of this event is aged components and lack of preventive maintenance activities on valve internals. The Tennessee Valley Authority is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications.
2602010002 | Browns Ferry 2 | 04/26/2010 | 06/25/2010 | ML10181007 | <strong>Failure to Meet the Requirements of Technical Specifications Limiting Condition for Operation due to Inoperable Primary Containment Isolation Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2010, from 0218 hours Central Daylight Time (CDT) to 0500 hours CDT, Maintenance personnel performed Surveillance Procedure 2-SR-3.3.6.1.6(4), Reactor Core Isolation Cooling (RCIC) Time Delay Relay Calibration. On April 26, 2010, at approximately 1115 hours CDT, contact boots were discovered on relay 2-RLY-071-13A-K32, RCIC High Steam Flow Relay. Operations immediately declared the B Channel of the RCIC Steam Line Flow - High Isolation Function inoperable and entered Technical Specification (TS) 3.3.6.1 Action A, which requires that with one or more required channels inoperable, within 24 hours, place the channel in trip. On April 26, 2010, at approximately 1140 hours CDT, after verifying there was no testing or maintenance activities in progress that required the contact boots to be in place, Operations personnel removed the contact boots from contacts of relay 2-RLY-071-13A-K32 and declared the B Channel of the RCIC Steam Line Flow - High Isolation Function operable, exiting TS 3.3.6.1 Action A. Operations personnel verified that the A Channel remained operable during the time the B Channel was inoperable, which would have isolated RCIC on a valid Steam Flow - High signal. TVA will review and revise applicable procedures to incorporate independent verification requirements for the steps associated with restoring the correct configuration when removing contact boots.
2602010003 | Browns Ferry 2 | 06/09/2010 | 08/09/2010 | ML10224025 | <strong>Reactor Scram due to Closure of the Main Steam Isolation Valves and Subsequent Invalid RPS Scram from the Intermediate Range Monitoring System</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2010, at approximately 0330 hours Central Daylight Time (CDT), outboard Main Steam Isolation Valve (MSIV) A closed while transferring the Reactor Protection System (RPS) 120 V-AC power from the normal to the alternate power supply in preparation for a planned activity. At approximately 0331 hours CDT Unit 2 received a Primary Containment Isolation Signal (PCIS) Group 1 isolation signal resulting in the closure of all of the MSIVs and automatic reactor scram. During the scram, all automatic functions occurred as expected. All control rods inserted. Operations personnel briefly entered Emergency Operating Instruction, 2-EOI-001, "Reactor Pressure Vessel Control," controlling both reactor vessel pressure and reactor vessel water level. At approximately 0335 hours CDT, Operations personnel reset the PCIS Group 1 Isolation Signal, and by approximately 0341 hours the reactor scram was reset. The root cause for the MSIV closure event is indeterminate. TVA's analysis identified two possible causes: 1) Debris from the control air system in the Direct Current (DC) solenoid plunger area or, 2) DC power system electrical circuitry issues. TVA plans to install a filter in the control air system upstream of the outboard MSIV control air header. TVA also plans to install transient monitoring equipment on the DC solenoid circuit and evaluate the results. If the results of the monitoring change the root cause and corrective actions, TVA will provide a revised report.
2602010004 | Browns Ferry 2 | 06/16/2010 | 08/06/2010 | ML10231004 | <strong>HPCI Isolation During Time Delay Relay Calibration</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2010, at 1258 Central Daylight Time (CDT), the High Pressure Coolant Injection (HPCI) system received an isolation signal during the performance of procedure 2-SR-3.3.6.1.6(3), the surveillance for the HPCI time delay relay calibration. At 1320 hours CDT, operations personnel discovered 2-FCV-73-2 (HPCI steam line inboard isolation valve) and 2-FCV-73-3 (HPCI steam line outboard isolation valve) were isolated. Operations personnel entered Abnormal Operating Instruction, Group 4 HPCI Isolation, 2-AOI-64-2B. HPCI Auto Isolation Logic was reset at 1807 hours CDT. The surveillance was re-performed without incident at 2034 hours CDT. Subsequent investigation determined that contacts 1 and 2 of relay 2-RLY-073-23A-K9 made contact during the testing of this relay. The cause is relay contact protective boots failed to prevent a contact pair from making contact during testing that resulted in the HPCI isolation. The contact boots that are used during the surveillance are made by cutting off the fingers of a heavy rubber glove. TVA has determined that depending on this type of boot used for circuit isolation during testing is a weak maintenance practice. The corrective action is to survey other sites and utilities to determine what alternative "booting" methods are available, and implement use of the appropriate alternative method at BFN to improve boot effectiveness and reliability.
2602010005 | Browns Ferry 2 | 07/12/2010 | 09/10/2010 | ML10265004 | <strong>High Pressure Coolant Injection System Isolation Experienced During Performance of High Pressure Coolant Isolation Steam Supply Low Pressure Functional Test</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2010, at approximately 1230 Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN) maintenance personnel commenced a scheduled performance of Surveillance Procedure, 2-SR-3.3.6.1.2(3B), High Pressure Coolant Injection (HPCI) Steam Line Supply Low Pressure Functional Test on the Unit 2 HPCI system. At 1310 CDT, the Unit 2 HPCI system unexpectedly received a Unit 2 Group 4 HPCI Primary Containment Isolation Signal (PCIS). Also, at 1310 hours CDT, Operations personnel declared the HPCI system inoperable and entered Technical Specification (TS) Limiting Condition for Operation 3.5.1 Action C, which requires verifying by administrative means that the Unit 2 Reactor Core Isolation Cooling (RCIC) system is operable, and restoring the Unit 2 HPCI system to operable status within 14 days. Operations verified that the RCIC system was operable. Operations entered Abnormal Operating Instruction, 2-AOI-64-2B, Group 4 High Pressure Coolant Isolation. By 1325 hours CDT, Operations personnel reset the HPCI system isolation using the applicable portions of 2-AOI-64-2B, and Operating Instruction, 2-OI-73, High Pressure Coolant Injection, and placed the Unit 2 HPCI system in standby readiness, exiting the TS Action. The immediate cause for the HPCI system isolation was the installation of multiple volt ohm meters (VOMs) on the associated circuits during performance of the surveillance. The apparent cause of the event is a lack of clear procedural guidance allowing the performer to interpret the requirements in the procedure and inappropriately place multiple VOMs on the associated circuit. The HPCI Low Steam Header Isolation Switch Functional test was revised to eliminate the need for performer interpretation. The procedure revisions included steps to connect and disconnect each VOM during checks for voltage.
2612010001 | Robinson 2 | 02/22/2010 | 06/10/2010 | ML10159022 | <strong>Emergency Diesel Generator Inoperable in Excess of Technical Specifications Allowed Completion Time</strong><br /><i>Abstract:&nbsp;</i>This revision corrects editorial errors in the labels of blocks 5 and 6 in LER 2010-001-00 and reflects the revised Refueling Outage 26 completion date. At 0455 hours EST on February 22, 2010, with H. B. Robinson Steam Electric Plant, Unit No. 2, operating at approximately 99% power, Emergency Diesel Generator (EDG) 'B' was removed from service for scheduled maintenance. Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.8.1 Condition B, was entered due one EDG inoperable. During the post maintenance testing in accordance with procedure OP-604, "Diesel Generators 'A' and 'B', " breaker 52/27B, EDG 'B' output breaker failed to close. The investigation for the inoperability of EDG 'B' breaker 52/27B determined that the Shunt Trip Attachment (STA) had internal binding that prevented the STA from releasing the trip bar, resulting in the trip bar remaining in the "trip condition" and preventing the breaker from closing. EDG 'B' was inoperable from January 28, 2010 to February 24, 2010, approximately 27 days. This resulted in a failure to meet the required actions associated with TS Action Statement 3.8.1.B.4 and Condition C. This is reportable under 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by the plant's Technical Specifications." Additionally, EDG 'A' was declared inoperable on February 8, 2010 for approximately 6 hours and 53 minutes for scheduled maintenance. The combined inoperability of EDG 'A' and 'B' could have prevented the fulfillment of a safety function. This is reportable under 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident."
2612010002 | Robinson 2 | 03/28/2010 | 05/27/2010 | ML10153050 | <strong>Plant Trip due to Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>At 18:52 EDT on March 28, 2010, with the H. B. Robinson Steam Electric Plant, Unit No. 2, operating in Mode 1 at approximately 99.5% power, a feeder cable failure to 4kV non-vital Bus 5 caused an arc flash and fire. Four kV Bus 5 failed to isolate from non-vital 4kV Bus 4 due to a failure of circuit breaker 52/24 to open, which resulted in reduced power to 'B' Reactor Coolant Pump (RCP) and a subsequent reactor trip on Reactor Coolant System (RCS) loop low flow. Subsequent to the reactor trip, an automatic safety injection occurred due to RCS cooldown. Plant response was complicated by equipment malfunctions and failure of the operating crew to diagnose plant conditions and properly control the plant. During plant restoration a relay was reset, which re-initiated the electrical fault and caused a second fire. The root cause of the event was failure of circuit breaker 52/24 to open due to incorrect evaluation of trip circuit indication. Lack of monitoring of key plant parameters by the operating crew is an additional root cause that contributed to the event. The event described in this Licensee Event Report is reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
2612010003 | Robinson 2 | 04/29/2010 | 06/28/2010 | ML10183027 | <strong>Potential Loss of Residual Heat Removal System Safety Function in Modes 3 and 4 due to Void Formation</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2010, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, shutdown in Mode 6 during Refueling Outage 26, it was determined that there was a potential for operating in an unanalyzed condition due to a loss of the safety function of the Residual Heat Removal (RHR) system. HBRSEP, Unit No. 2, determined that under certain conditions flashing or water hammer could occur in the RHR system during Modes 3 and 4. The resulting steam voids could prevent the RHR system from fulfilling its safety function during the injection and recirculation phase of a Loss of Coolant Accident (LOCA). This condition could have prevented the fulfillment of the safety function that is needed to remove residual heat in Modes 3 and 4 and is reportable under 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(ii)(B), and 10 CFR 50.73(a)(2)(v)(B). The cause of this condition has been determined to be deficiencies in the original plant design and system operating guidance provided by Westinghouse. A contributing cause identified that HBRSEP, Unit. No. 2, did not perform an adequate review of Westinghouse Nuclear Safety Advisory Letter NSAL-93-004. Corrective actions are in progress to revise the applicable operating procedures to maintain the Technical Specifications required operability of RHR and ECCS functions. These revisions are expected to be completed prior to entry into Mode 4, during restart from the current refueling outage (RO-26).
2612010004 | Robinson 2 | 04/26/2010 | 06/24/2010 | ML10180026 | <strong>Clearance Error Results in the 'A' Emergency Diesel Generator Becoming Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2010, with H. B. Robinson, Unit No. 2, shutdown in Mode 6 during Refueling Outage 26, it was determined that a condition existed that could have prevented the fulfillment of the safety function needed to mitigate the consequences of an accident. From April 18 to April 26, 2010, an equipment clearance inadvertently made Emergency Diesel Generator (EDG) 'A' inoperable. During this time period, on April 24, 2010, EDG 'B' was taken out of service for required surveillance testing in accordance with OST-401-2, "EDG B Slow Speed Start." Technical Specification (TS) 3.8.2 requires one diesel generator capable of supplying one train of the onsite AC electric power distribution subsystem(s) when in Mode 6. TS 3.8.2, Condition B, states if one required EDG is inoperable initiate actions to restore an EDG to operable status immediately. The condition where EDG 'B' was out of service for surveillance testing while EDG 'A' was inadvertently inoperable resulted in a failure to meet the required action associated with TS Action Statement 3.8.2.B.4. The root cause of this event was determined to be insufficient procedural guidance. Guidance was not available to provide a risk assessment or an additional supervisory review of a clearance following the completion of the pre-outage clearance window. The planned corrective action to prevent recurrence is to revise a procedure to include requirements for additional reviews for clearances.
2612010005 | Robinson 2 | 06/24/2010 | 05/18/2011 | ML11147A07 | <strong>Emergency Diesel Generator Inoperable due to Inverter Failure</strong><br /><i>Abstract:&nbsp;</i>This revision contains additional information regarding reactor coolant system temperature described in LER 2010-005-00 and reflects revised corrective actions. At 1433 hours EDT on June 24, 2010, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, shutdown in Mode 5 during Refueling Outage 26, a loss of Instrument Bus 3 (IB-3) and Instrument Bus 8 occurred during performance of OST-163, "Safety Injection Test and Emergency Diesel Generator Auto Start on Loss of Power and Safety Injection." The loss of IB-3 resulted in the loss of Residual Heat Removal (RHR) temperature control and resulted in inoperability of the required Emergency Diesel Generator due to loss of the automatic load sequencer. Both trains of RHR continued to operate and reactor coolant system temperature remained in the range of approximately 93 to 97 degrees Fahrenheit. This condition could have prevented the fulfillment of a safety function that is needed to mitigate the consequences of an accident and is reportable under 10 CFR 50.73(a)(2)(v)(D). The cause of this event has been determined to be the age related failure of an inverter component resulting from the inappropriate closure of a partially completed Preventive Maintenance associated work order. The corrective actions to prevent recurrence include a revision to a procedure to clarify guidance for partial Preventive Maintenance work order completion. In addition, guidance will be provided to maintenance personnel regarding the completion and coding of partially performed or not performed Preventive Maintenance work orders.
2612010006 | Robinson 2 | 08/04/2010 | 10/04/2010 | ML10281049 | <strong>Pressurizer Heaters Inoperable Longer Than Allowed Due to Inadequate Procedure</strong><br /><i>Abstract:&nbsp;</i>On August 4, 2010, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, operating in Mode 1, it was determined that if Emergency Diesel Generator (EDG) 'A' is inoperable, the required emergency power supply to the pressurizer heaters could not have been provided if required. Technical Specification (TS) 3.4.9, "Pressurizer," requires pressurizer heaters to be capable of being powered from an emergency power supply. The TS requires that if emergency power capability is not available, it is restored within 72 hours or a plant shutdown initiated. There have been periods when EDG "A" was inoperable for greater than 72 hours and a plant shutdown was not initiated. This condition is prohibited by the plant's Technical Specifications and is reportable under 10 CFR 50.73(a)(2)(i)(B). The cause of this event was inadequate verification of plant changes during the implementation of TMI lessons learned. The corrective actions to prevent recurrence include implementing a plant modification and associated procedure changes.
2612010007 | Robinson 2 | 09/09/2010 | 01/17/2011 | ML11021099 | <strong>Reactor Trip due to a Degraded Connection on a Circuit Board in the Electro-Hydraulic Control Cabinet</strong><br /><i>Abstract:&nbsp;</i>At 1437 hours EDT on September 9, 2010, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at approximately 100% power, an automatic reactor trip occurred. The reactor trip signal was based on the Overtemperature DeltaT (OTDeltaT) reactor protection function. Due to the plant transient condition, the three steam generator Power Operated Relief Valves (PORVs) opened and one pressurizer PORV cycled momentarily. This event is being investigated using the HBRSEP, Unit No. 2, Corrective Action Program (CAP) and is being documented in Nuclear Condition Report (NCR) 420936. During investigation of the cause of the transient, a degraded connection on a circuit board (1A08H2) in the electro-hydraulic (EH) control cabinet was found. It has been concluded that this condition caused the loss of the governor valve common signal to the four turbine governor valves. Closure of the governor valves caused pressure and temperature in the Reactor Coolant System (RCS) to change. This resulted in the opening of a pressurizer PORV and the OTDeltaT reactor protection function initiating a reactor trip. The completed corrective action was replacement of the circuit board (1A08H2) found with the degraded connection. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
2612010008 | Robinson 2 | 10/05/2010 | 12/06/2010 | ML10343030 | <strong>Emergency Core Cooling System Inoperable in Mode 4 due to Technical Specification Misinterpretation</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2010, with H. B. Robinson Steam Electric Plant, Unit No. 2, in Mode 1 at 100% power, it was determined that during past Mode 4 operation, the Residual Heat Removal (RHR) System, was not operable per Technical Specification (TS) requirements for the Emergency Core Cooling System (ECCS) function for safety injection. Corrective actions related to gas voiding issues resulted in procedure changes that precluded the use of RHR for low-head safety injection to mitigate a Mode 4 Loss of Coolant Accident (LOCA). The changes were justified based on a technical conclusion that during the injection phase, one Safety Injection (SI) pump provided sufficient flow to mitigate a Mode 4 LOCA, and an interpretation that the TS did not specifically require both ECCS subsystems (RHR and SI) to be operable for both the injection and recirculation phases. Based on subsequent information, it was concluded on October 5, 2010, that the TS do require the RHR System to be operable for the ECCS injection phase and therefore the procedure changes resulted in a condition prohibited by Technical Specifications, which is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The root cause was determined to be unclear requirements in the TS and an inadequate 10 CFR 50.59 evaluation. The TS Bases will be revised to provide clear operability requirements and 10 CFR 50.59 guidance will be improved. Procedures have been revised to ensure RHR operability in Mode 4.
2612010009 | Robinson 2 | 10/07/2010 | 12/06/2010 | ML10343030 | <strong>Reactor Trip due to Motor Fault on the 'C' Reactor Coolant Pump and Actuation of Auxiliary Feedwater Signal and Override of Feedwater Isolation Function due to Inadequate Post-trip Procedure Guidance</strong><br /><i>Abstract:&nbsp;</i>At 0013 hours EDT on October 7, 2010, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at 100% power, an automatic reactor trip occurred. A motor fault on Reactor Coolant Pump (RCP) 'C' resulted in the Single Loop Low Flow reactor protection function and a subsequent reactor trip. The root cause for the reactor trip was determined to be inadequate end winding bracing of RCP 'C' motor. The failed RCP was replaced with the motor that had been recently removed from 'A' RCP. The removed motor will be rewound using an improved design, followed by the current motor. At approximately 0405 hours EDT on October 7, 2010, the Auxiliary Feedwater (AFW) system actuated due to a trip of Main Feedwater (MFW) Pump 'A' while attempting to start the pump. At approximately 1315 hours EDT on October 7, 2010, the operating crew recognized that action taken at about 1018 hours to place the feedwater isolation key switches in the Override/Reset position in order to start MFW Pump 'A' resulted in the inadvertent disabling of the feedwater isolation function and entry into Technical Specifications Limiting Condition for Operation (LCO) 3.0.3. The root cause for the automatic AFW initiation signal and the inadvertent entry into LCO 3.0.3 was determined to be an inadequate procedure. The procedure was revised to include appropriate guidance for resetting the Feedwater Isolation signal. The conditions described in this Licensee Event Report are reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(iv)(A), and 10 CFR 50.73(a)(2)(v)(D).
2632010001 | Monticello | 04/20/2010 | 06/18/2010 | ML10169037 | <strong>Missed Safety Relief Valve Lift Test Surveillance Interval</strong><br /><i>Abstract:&nbsp;</i>While performing a review of operating experience station personnel identified that the plant may have exceeded the American Society of Mechanical Engineers (ASME) Code required testing interval for five of eight of the Safety Relief Valves (SRVs) [RV]. The apparent noncompliance with the ASME Code was validated by the engineering staff on 4/20/2010 and the Shift Manager subsequently declared a missed surveillance and entered SR 3.0.3. A risk assessment was performed as required by SR 3.0.3, which determined that the risk significance was minimal. The cause of the event was an interpretation of the test interval requirements that resulted in the plant utilizing an install to test interval vice a test to test interval for new and refurbished valves. Corrective actions taken or planned are: a one-time relief request to go beyond the 5 year testing interval has been submitted, revise the Corporate Directive regarding the testing of SRVs and to develop guidance regarding the process to use and evaluate code interpretations.
2632010002 | Monticello | 06/03/2010 | 08/08/2011 | ML11220145 | <strong>Secondary Containment Briefly Degraded</strong><br /><i>Abstract:&nbsp;</i>At 1050, June 3, 2010, with the plant operating in Mode 1 at 100% power, DOOR-72 and DOOR-82 for airlock 413 (985' Pump Room) were inadvertently opened simultaneously, breaching the Secondary Containment (SCT) boundary. Personnel immediately identified the situation and closed both doors within four to five seconds (estimated) and Shift supervision was notified. With both doors open, the station's Technical Specification (TS) surveillance requirement 3.6.4.1.3 (verify one Secondary Containment access door in each access opening is closed) was not met. The TS LCO statement 3.6.4.1 was declared not met and Action A, (Restore secondary containment to Operable status) entered. The doors were verified closed. With SCT restored, TS 3.6.4.1 was met at 1110. The cause of the event was the design of the interlock between the doors in the 985' Pump Room which does not prevent a simultaneous entry. Corrective actions taken: the doors were closed and the interlock mechanism was verified to operate per design.
2632010003 | Monticello | 08/05/2010 | 06/13/2011 | ML11165040 | <strong>Secondary Containment Briefly Degraded</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2010, at approximately 1145 hours, with the plant operating in Mode 1 at 100% power, DOOR-72 and DOOR-82 for airlock 413 (985 foot Pump Room) were inadvertently opened simultaneously, breaching the Secondary Containment (SCT) boundary. Personnel immediately identified the situation and closed both doors within about five seconds (estimated). Shift supervision was notified. With both doors open, the station's Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.3 (verify one Secondary Containment access door in each access opening is closed) was not met. TS Limiting Condition for Operation (LCO) 3.6.4.1 was declared not met and Action A, (Restore secondary containment to Operable status) entered. The doors were verified closed. With SCT restored, TS 3.6.4.1 was met at 1219. The cause of the event was the design of the interlock between the doors in the 985 foot Pump Room which allows simultaneous entry under specific timing conditions (i.e., the doors are opened at exactly the same time - otherwise, the interlock prevents one door from opening if the other is open) and for this occurrence the site failed to take adequate corrective actions for an earlier failure. Corrective actions taken: the doors were closed and administrative controls were placed on the 985 foot Pump Room doors and also the 985 foot Plenum Room doors (which have the same design interlock).
2632010004 | Monticello | 11/04/2010 | 12/22/2010 | ML10357002 | <strong>Secondary Containment Briefly Inoperable Due to Simultaneous Opening of Airlock Doors</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2010, at approximately 1125, with the plant operating in Mode 1 at 93% power, DOOR-62 and DOOR-63 for Airlock 124 from Main Access were inadvertently opened simultaneously, breaching the Secondary Containment (SCT) boundary. This occurred when personnel attempted to enter the airlock from Secondary Containment before the outboard door fully closed. The local alarm sounded for approximately one to two seconds, and the plant employees noticed DOOR-62 was not fully closed. Plant personnel immediately closed the doors and notified the Control Room that SCT was momentarily breached (for approximately 5 seconds). While both doors were open simultaneously, Surveillance Requirement (SR) 3.6.4.1.3, verify one Secondary Containment access door in each access opening is closed every 31 days, was not met. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.4.1 was declared not met and Condition A was entered at 1125. The required action, A.1, is to restore secondary containment to Operable status, which was completed at 1125 and TS LCO 3.6.4.1 was met. This is a different interlock type than the one reported under LER submittals 2010-002-00 and 2010-003-00.
2632010005 | Monticello | 11/04/2010 | 12/22/2010 | ML10357002 | <strong>Average Power Range Monitor Indication Outside Allowable Range</strong><br /><i>Abstract:&nbsp;</i>On 4 November 2010, the site reduced power to 50% Rated Thermal Power (RTP) to isolate and repair the 15B Feedwater Heater. Upon isolation, calculated Core Thermal Power (CTP) rose approximately 3% RTP while Average Power Range Monitors (APRM) rose approximately ½% RTP. Surveillance Requirement 3.3.1.1.2 requires a difference between APRM channels and calculated power of ±2% RTP while operating at = 25% RTP. Since the readings between the two indications were now >2%, all APRMs were declared inoperable and Technical Specification 3.3.1.1 Limiting Condition for Operation (LCO) was declared not met. APRM gains were adjusted upward to restore compliance with the LCO. On 6 November, operators noted Turbine electrical power output lower than expected for calculated CTP. Investigation revealed calculated CTP was indicating high due to noise at very low dP/flow values causing a feed flow signal in the isolated 15B Feedwater Heater. A hand validation of thermal power verified an actual thermal power of approximately 50 MWth lower than calculated CTP. The error was corrected and APRM gains were lowered to match calculated CTP and meet the LCO. The APRM readings were >2% higher than CTP for approximately 60 hours. At no time during this event was the safety function of the APRM system lost.
2632010006 | Monticello | 11/22/2010 | 12/22/2010 | ML10357003 | <strong>Mode Change Made with PClVs Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2010 the plant was in Mode 4 with preparations for startup in progress. The duty crew transferred the reactor vent path to the path through Main Steam Line Drain valves MO-2373 (Main Steam Line Drain - Inboard), MO-2374 (Main Steam Line Drain - Outboard), and MO-2565 (Steam Line Drain Orifice Bypass). The valves were opened and their associated breakers were tagged open. At 1647, the change from Mode 4 to Mode 2 was completed. At 1700, a page announcement was made that Reactor Startup was commencing. The oncoming Operations Work Control Manager recalled helping tag open MO-2373 and MO-2374, which are Primary Containment Isolation Valves (PCIV), on the previous night shift. He called the control room to verify the valves had been restored prior to the mode change. He immediately notified the duty crew and Operations Management of the Technical Specification violation when he was informed they had not been restored. Startup activities were halted pending investigation and resolution of the issue. PCIV operability was restored. Startup activities were recommenced later in the shift after prerequisites had been verified and a stand down conducted.
2652010001 | Quad Cities 2 | 04/14/2010 | 06/11/2010 | ML10169008 | <strong>Main Condenser Low Vacuum Scram RPS Switch Inoperable and Exceeded Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During Startup of Unit 2 from refueling outage Q2R20, anomalous condenser [CDU] backpressure indications were noted by the control room staff. While investigation into the indication issue was in progress the operators placed the Unit into Mode 1. Approximately 12 hours later the anomalous indication was determined to be caused by a partially closed isolation valve [ISV] which isolates the turbine [TRB] condenser low vacuum pressure switch [PS] which inputs into the Reactor Protection System (RPS) [JD]. The valve was subsequently re-opened. This pressure switch is required to be operable in Mode 1 by plant Technical Specifications (TS). Since the pressure switch was determined to be inoperable, the Unit had entered Mode 1 without meeting TS 3.0.4 for the required minimum number of operable channels per TS 3.3.1.1, Function 10. The apparent cause of this event was failure of the Station to place sufficient importance on the anomalous Control Room indications. Contributing to the cause was the improperly positioned isolation valve that was potentially caused by personnel inadvertently bumping the isolation valve during outage activities. Condenser pressure plots during shutdown prior to the outage indicated pressure channels were tracking uniformly, however upon outage completion, the startup condenser pressure plots indicated anomalous readings, therefore the isolation valve had been inadvertently repositioned during the outage. Corrective actions include procedure changes to require investigations into abnormal plant indications to verify there are no impacts on TS required equipment prior to entering Modes 1 and 2, and reviews of work practices and configuration controls associated with instrument isolation valves in high traffic areas. The safety significance of this event was minimal. Although the required instrument was not operable for a short period of time, sufficient redundant condenser backpressure instrumentation was operable to maintain scram capability. This event is therefore, a past operation or condition which was prohibited by the plant Technical Specifications, and is therefore reportable per 10 CFR 50.73(a)(2)(i)(B).
2652010002 | Quad Cities 2 | 08/17/2010 | 10/18/2010 | ML10299031 | <strong>Unit 2 Manual Reactor Scram due to 2B Recirculation Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2010, Quad Cities Unit 2 performed a scheduled adjustable speed drive [DRIV] (ASD) programmable logic controller [DCC] (PLC) restoration activity. During the evolution, the ASD was unable to control the reactor [RCT] recirculation (recirc) pump [P] speed and resulted in a trip of the 2B recirc pump. The 2B feedwater [SJ] regulating valve [FCV] (FRV) was also in manual control mode at this time, and reactor pressure vessel (RPV) water level increased. Operators transferred the 2B FRV controls from manual to automatic, RPV water level continued to rise, manual scram criteria was met at 44 inches RPV water level, and subsequently Operators were required to manually scram the reactor via the reactor protection system [JD] (RPS). There were no complications during the reactor scram, and all systems functioned as required. Forced outage, Q2F65, was initiated to investigate and performs repairs. The reactor and all systems responded as designed. When in automatic operation the 2B FRV responded unexpectedly to Operators, however, the FRV operated as designed. Operators had not been informed of the valve position recovery time delay involved when transferring the 2B FRV from manual to automatic position control in this scenario. The root cause of this event is management's failure to recognize and effectively challenge critical assumptions used in authorizing work activities for performing the ASD resynchronization, and for determining risk in controlling the 2B FRV. Both process reviews failed to adequately assess and manage risk prior to performing these activities. Corrective actions include enhancements in technical rigor used in the identification and evaluation of plant decisions involving risk, associated operating procedure revisions, enhanced training, and additional considerations to perform simulator testing. The safety significance of this event was minimal. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram or reactor trip.
2662010001 | Point Beach 1 | 03/03/2010 | 01/20/2011 | ML11021008 | <strong>Engineered Safety Features Steam Line Pressure Dynamics Modules Discovered Outside of Technical Specification Values</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2010, procedure 1ICP 04.001E, Reactor Protection and Safeguards Analog Racks Steam Pressure Refueling Calibration, was performed to satisfy Point Beach Nuclear Plant (PBNP) Technical Specification (TS) Table 3.3.2-1 Function 1e, Surveillance Requirement (SR) 3.3.2.8. The testing determined that the as-found values for five out of six Unit 1 engineered safety features (ESF) steam line pressure (SLP) dynamic compensation module lead time constants were slightly below the TS required time constant limit of greater than or equal to 12.0 seconds (the TS requirement is >/=12). The basis calculation for module drift addressed static settings only and did not address dynamic settings. As a result of not addressing the dynamic settings, the tolerances for as-left settings were too restrictive and did not sufficiently account for instrument drift. Corrective actions included performing an on-line calibration check and adjusting the modules to within the allowable as-left tolerances. The Unit 2 SLP module tolerances were confirmed to be within TS-required values. The out of specification lead time constants would not have prevented the associated channels from being able to perform their required safety-related functions in the event of a main steam line break (MSLB) accident. Pursuant to 10 CFR 50.73(a)(2)(i)(B), the event is reportable as a condition prohibited by TS and 10 CFR 50.73(a)(2)(vii), as a common cause inoperability of independent trains or channels.
2662010002 | Point Beach 1 | 07/26/2010 | 09/21/2010 | ML10266011 | <strong>Manual Reactor Trip due to Lowering Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On 7/26/2010 at 2001 CDT, operations personnel initiated a manual reactor trip of Unit 1 from approximately 19% reactor power. Unit 1 was off-line to support main generator repair. The generator breaker had just been opened and steam load was transferred to the condenser steam dumps when condenser vacuum lowered. The reactor was manually tripped in accordance with plant procedures due to a lowering of main condenser vacuum prior to an automatic trip of the reactor. All safety systems functioned as expected. All control rods fully inserted. The lowering of condenser vacuum and subsequent manual reactor trip was caused by the improper application and adherence to human performance (HU) tool standards for self-checking. The failure to perform the self-check resulted in an incorrect status report for the turbine crossover steam dump motor operated valves, 1MOV-1 and 1MOV-2.
2662010003 | Point Beach 1, Point Beach 2 | 09/13/2010 | 11/11/2010 | ML10316015 | <strong>Potential for Residual Heat Removal Trains to be Inoperable During Mode Change</strong><br /><i>Abstract:&nbsp;</i>During review of NRC Information Notice 2010-0011, a concern with the operation of the emergency core cooling system (ECCS) at shutdown conditions was identified. It was determined that in MODE 4, the temperature of the fluid in the residual heat removal (RHR) pump suction header exceeded the temperature which, under postulated shutdown loss of coolant accident (LOCA) conditions, could have resulted in steam voiding and potentially damaging condensation induced water hammer. This condition could have rendered the low head safety injection (LHSI) subsystem (which includes the RHR pump and common piping) for the required single train of ECCS inoperable. Operations procedure changes are in progress and are being tracked in the site's corrective action program to ensure that administrative controls are in place to maintain one train of RHR isolated and cool while in MODE 4 so that it can be used for LOCA mitigation. This 60-day licensee event report is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(ii)(B), 50.73(a)(2)(v)(B), and 50.73(a)(2)(vii).
2662010004 | Point Beach 1, Point Beach 2 | 06/25/2010 | 02/18/2011 | ML11053014 | <strong>Improper Controls for Breach of HELB Barrier</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2010, the lock on the north control room door was replaced. This door is the normal access door to the control room and is a safe shutdown, security and high energy line break (HELB) barrier. The door was blocked open for 24 minutes during lock replacement. If a HELB had occurred in the turbine building during that time, it may have resulted in control room equipment being inoperable. The site administrative procedure in place at the time of the event allowed a control room HELB door to be open for no more than 12 hours. The 12-hour time limit was not appropriate for a HELB barrier. The procedure was in the process of being revised so the door would be allowed to stay open for no more than one hour and could not be blocked open. An Operations Notebook entry was written that established interim guidance for HELB barriers pending issuance of the revised procedure. The interim action was not adequate to prevent the event. Corrective actions are complete. This 60-day licensee event report is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(ii)(B), as an unanalyzed condition, and 10 CFR 50.73(a)(2)(v)(A), and (D) as a Condition that could have prevented fulfillment of the safety function of systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition or mitigate the consequences of an accident.
2662010005 | Point Beach 1, Point Beach 2 | 08/27/2010 | 04/25/2011 | ML11115050 | <strong>Improper Administrative Controls for HELB Barriers</strong><br /><i>Abstract:&nbsp;</i>During the spring of 2010, NextEra identified several past instances where high energy line break (HELB) barriers were not being properly controlled during maintenance and modification activities. Consequently, a HELB in certain areas coincident with the barriers being open could have adversely affected the equipment within the adjacent room. A three-year review was conducted to determine the extent of condition of the potential barrier breaches. The results revealed additional instances where HELB barriers had been improperly controlled and the barrier had been rendered inoperable. A causal evaluation determined that the administrative procedure governing HELB barriers was not consistent with industry standards and did not contain applicable regulatory guidance. An analysis for safety significance is in progress. This report supplements the 60-day licensee event report submitted on February 18, 2011, in accordance with the requirements of 10 CFR 50.73(a)(2)(ii)(B), as an unanalyzed condition and 10 CFR 50.73(a)(2)(v)(A) and (D) as a condition that could have prevented fulfillment of the safety function of systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition or mitigate the consequences of an accident. The event constitutes a safety system functional failure.
2692010001 | Oconee 1, Oconee 2, Oconee 3 | 02/20/2010 | 12/13/2010 | ML10351002 | <strong>Standby Shutdown Facility Letdown Line Orifice Strainer Blocked by Valve Gasket Material</strong><br /><i>Abstract:&nbsp;</i>On 10/11/2009, while Unit 1 was in Mode 5, the Standby Shutdown Facility (SSF) Reactor Coolant Make-Up (RCMU) system letdown flow path failed a flow test. Troubleshooting inspections found foreign material (FM), i.e., Grafoil FM from a Flowserve Model 1878 valve backseat gasket and "legacy" FM (particles of epoxy, austenitic stainless steel shavings, and a paint chip), upstream of an orifice strainer (strainer). The strainer and gasket were removed. Based on inspection of similar valves, vendor assurance of no recorded similar gasket failures, and prior flow tests, the equivalent lines on Unit 2 and 3 were initially considered Operable. On 2/18/2010 at 2250, while operating at 100% in Mode 1, Unit 2 SSF RCMU was declared inoperable due to recognition that the strainer could be partially blocked and might collapse during an event. Power was reduced to access the strainer. FM, including Grafoil, was found; the strainer was removed. On 2/23/2010, Unit 3 power was reduced to access the strainer. FM, including Grafoil, was found; the strainer was removed. The root causes of this event are an inadequately selected strainer and a vendor valve design deficiency which released FM from the backseat gasket. The backseat gasket failure is reported as a Part 21 defect. The significance determination process concluded that the issue had substantial safety significance.
2692010002 | Oconee 1 | 08/07/2010 | 12/06/2011 | ML11341A11 | <strong>Manual Reactor Trip due to 1A1 and 1A2 Reactor Coolant Pump High Vibration Indication</strong><br /><i>Abstract:&nbsp;</i>On August 7, 2010, at 1130 hours, while operating at 100%, Oconee Nuclear Station (ONS) Unit 1 received statalarm 1SA-9-D2 (Reactor Coolant Pump Vibration High). Operators entered the applicable response procedure to reduce Unit 1 power. Vibration readings continued to increase. At 1451 hours, with power at 17%, Control Room Operators manually tripped Unit 1 when the indicated vibration readings reached procedural limits. The post-trip response was normal, with all major operating parameters remaining within expected limits. Operators took appropriate action to stabilize the unit in Mode 3 (hot standby). While the operators were controlling Pressurizer and Letdown Storage Tank Level per procedure, the standby 1B High Pressure Injection (HPI) pump auto started due to low Reactor Coolant Pump Seal Flow. Investigation revealed that a false high Reactor Coolant Pump (RCP) vibration indication occurred because the active power supply (Power Supply No. 2) had failed within the control module. Corrective Actions included replacement of the Unit 1 control module (Indikon 500-IM22) and positioning the RCP vibration equipment Power Supply Selector switches to "Auto". This event is considered to have no significance with respect to the health and safety of the public.
2692010003 | Oconee 1 | 10/27/2010 | 09/26/2011 | ML11272A16 | <strong>Inoperable Emergency Feedwater Flowpath Results in a Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>While conducting a stroke test for EFW Valve 1FDW-315, the valve unexpectedly opened after both of its normal air supply sources (i.e., Instrument Air and Auxiliary Instrument Air) had been secured. The nitrogen bottle gas emergency backup system for 1FDW-315 was unable to prevent the valve from failing open after isolation of the two normal air sources. Troubleshooting focused on the 'B'-train nitrogen regulator (1N-328) for 1FDW-315 since the 'B'-train emergency backup nitrogen supply was aligned to 1FDW-315 at the time of the stroke test. Regulator 1N-328 was discovered fully backed-out which isolated the 'B'-train nitrogen bottle to 1FDW-315. This condition rendered 1FDW-315 and its associated EFW flow path inoperable. Investigation into maintenance performed on 1N-328 determined that on September 5, 2010, the regulator had been adjusted in an attempt to reduce the regulator pressure (by procedure) to within the desired pressure band but resulted in a zero (0) actual downstream pressure although the regulator gauge continued to read ~100 psig. (lt was later revealed that the high pressure was attributed to leak-by from failed downstream check valve 1NIV0072.) Unknowingly,1N-328 was left fully backed-out, which isolated the nitrogen bottle to 1FDW-315. As such, the EFW flow path to the 1A steam generator was inoperable for approximately 54 days, which exceeded the 72-hour competion time for Technical Specification 3.7.5 Condition 'B.' The root cause of this event was determined to be due to an inadequate procedure used to perform the nitrogen regulator adjustment. The applicable procedure has since been revised.
2702010001 | Oconee 2 | 07/02/2010 | 08/02/2011 | ML11215A19 | <strong>Operation Prohibited by TS due to Removal of West Penetration Room Brick Wall Support Girts</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2010, Oconee Nuclear Station (ONS) discovered that workers had removedsupport girts from the Unit 2 West Penetration Room brick wall that were required to maintain seismic adequacy of the wall. Failure of this wall could damage Standby Shutdown Facility (SSF) cables. Damage to these cables could have caused the SSF Reactor Coolant Makeup and Auxiliary Service Water functions to be inoperable for a seismically-induced Turbine Building Flood Event. Technical Specification (TS) Limiting Condition for Operation (LCO) 3.10.1 was not met in this condition. This condition existed for approximately fourteen days, which exceeded the seven-day required action time of the LCO. Consequently, ONS Unit 2 operated in a condition prohibited by TS for approximately seven days as a result of this condition. Prompt corrective action was taken to re-install the required support girts. This work was completed on July 16, 2010. The cause of this event was determined to be that critical information was not transferred from the complex activity plan to the work order task document and subsequently, to the craft in the field. The completed corrective actions have addressed this process weakness. This event is of no significance with respect to public health and safety.
2712010001 | Vermont Yankee | 05/26/2010 | 07/26/2010 | ML10214040 | <strong>Automatic Reactor Trip due to Switchyard Current Transformer Problem</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2010, at approximately 1526 hours, a generator lockout and automatic reactor trip occurred on differential current between a current transformer (CT) installed in the newly commissioned switchyard and a CT installed in the plant. During startup, when the plant reached 72% power, both channels of the reactor protection system (RPS) actuated and all control rods inserted. Following the reactor trip reactor vessel level decreased causing primary containment isolation system (PCIS) actuation for groups 2, 3, 4, and 5. All associated valves functioned correctly. Additionally, both trains of standby gas treatment system actuated. Immediate plant actions included entering appropriate trip response procedures. The operators stabilized the plant and reset both RPS and PCIS. During RFO 28, Vermont Yankee (VY) and the Vermont Electric Power Company (VELCO) commissioned a new 345kV switchyard. The direct cause of the trip was that VELCO changed the CT ratio settings within the 345kV Switchyard and failed to communicate the new ratio setting to VY. As power was increased, the differential current caused by the difference in CT ratio settings resulted in the generator lockout. Corrective actions include adjustment of the VY CT to the correct settings and establishment of the necessary programmatic controls to preclude recurrence. This event is reportable as a licensee event report (LER) per 10CFR50.73(a)(2)(iv)(A) as an event or condition that resulted in actuation of the any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B), which includes RPS and PCIS.
2712010002 | Vermont Yankee | 10/25/2010 | 03/01/2011 | ML11066029 | <strong>Inoperability of Main Steam Safety Relief Valves due to Degraded Thread Seals</strong><br /><i>Abstract:&nbsp;</i>During the 2010 refueling outage, the pneumatic actuators for the four main steam safety relief valves (RV), RV-2-71-A, B, C & D, were tested and leakage was identified through the shaft to piston thread seal on three of the four RVs. This leakage, when combined with the RV accumulator leakage, caused two of the four RVs to not meet design actuation requirements and therefore be considered inoperable. Technical Specification (TS) 3.6.D requires at least three of the four RVs to be operable for overpressure protection of the Reactor Coolant System and TS 3.5.F requires all four RVs to be operable to support the Automatic Depressurization System (ADS) function of the Core Standby Cooling System. Since inoperability of two valves could constitute an operation or condition prohibited by TS, a cause analysis was performed. On October 25, 2010, based on a review of the analysis, it was determined that there was firm evidence that the condition may have existed for a period of time greater than allowed by the TS. Therefore, this event is reportable in accordance with 10CFR50.73(a)(2)(i)(B) as an operation or condition prohibited by TS. Subsequent material testing of a seal from the same batch lot determined that the apparent cause of the thread seal condition was thermal degradation. The thread seals were replaced and tested on all four RVs prior to start up from the 2010 outage with new seals and will be disassembled for inspection, modified and tested during the next refueling outage. This event did not affect the automatic function of the RVs to provide overpressure protection and due to redundancy in the RV design and available nitrogen supplies, adequate relief capacity for ADS existed at all times. Therefore, this event did not pose a threat to public health and safety.
2722010001 | Salem 1 | 04/16/2010 | 06/14/2010 | ML10174007 | <strong>Automatic Start of the 1C Emergency Diesel Generator (EDG)</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2010, at 1641 hours, the 1C 4160 volt vital bus lost power. Surveillance testing was being performed to demonstrate the transfer of the 1C 4160 volt vital bus from one offsite power infeed to the second offsite power infeed. The 1C Emergency Diesel Generator (EDG) automatically started but the EDG output breaker did not close per design. Abnormal operating procedure S1.OP-AB.4KV-0003 was entered for loss of power to the 1C 4160 volt vital bus. Fuel movement was in progress at the time of the event and was suspended. The unexpected start of the 1C EDG was the result of the failure of the 13CSD breaker auxiliary position switch (52STA switch). The failure of the 52STA switch was the result of binding caused by misadjustment of the gap between the breaker and the 52STA switch assembly. The misadjustment was the result of unclear procedural guidance for measuring the breaker plunger gap. Corrective actions consist of replacement of the 13CSD 52STA switch, proper adjustment of the breaker plunger gap, inspection of other 4160 volt infeed breaker plunger gaps, and procedure revisions to improve the guidance for measuring breaker plunger gaps. This report is made in accordance with 10CFR50.73 (a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
2722010002 | Salem 1 | 07/07/2010 | 09/02/2010 | ML10278050 | <strong>Automatic Reactor Trip Due to Main Power Transformer Bushing Failure</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2010, at approximately 1118, an automatic reactor trip was initiated due to a turbine trip above 50% reactor power. The turbine trip was the result of the actuation of the regular and back-up phase B-C differential relays in the main generator protection scheme. This actuation was the result of an arc flash across the "B" phase main power transformer bushing following an inadvertent actuation of the transformer fire protection deluge system. The deluge system was actuated by one of the 18 air-pilot sprinkler heads that fused due to the transformer's heat, unusually high ambient temperatures, direct sunlight and restricted ventilation caused by concrete walls that surround three sides of the main power transformer "B" phase. Mist from the deluge system actuation rose above the main power transformer "B" phase bushing, driven by the transformer operating fans, heat rising from the transformer and the close proximity of the concrete wall enclosure, which resulted in the observed arc flash and bushing failure. Corrective actions included replacing the main power transformer deluge system air-pilot sprinkler heads with sprinkler heads that have a higher temperature setpoint. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)….”
2722010003 | Salem 1 | 07/23/2010 | 09/15/2010 | ML10265022 | <strong>Failure to Comply with Technical Specification 3.0.4</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2010, at 0940 hours, an Instrument and Control (I&C) Technician identified the circuitry was disabled for the motor driven auxiliary feedwater (AFW) pump automatic start on a trip of both steam generator feedwater pumps (SGFPs). At the time of discovery Salem Unit 1 was in Mode 1. The AFW automatic start circuitry is required by Technical Specification (TS) 3.3.2.1 function 8f to be operable in Modes 1 and 2. The operating shift entered TS Action Statement (TSAS) 3.3.2.1 action 21 for function 8f. TSAS action 21 entry was considered applicable when Salem Unit 1 entered Mode 2 on July 23, 2010, at 2152 hours. At 1557 hours on July 25, 2010, the automatic start of the AFW pumps on a trip of both SGFPs was re-established and TSAS 3.3.2.1 action 21 was exited. Entry into Mode 2 with the circuitry required by TS 3.3.2.1 function 8f disabled was a condition prohibited by Technical Specification 3.0.4. The cause of the failure to re-establish the automatic start circuitry for the start of the motor driven AFW pumps on a trip of the SGFPs was due to operators performing the incorrect section of the procedure to re-establish the start circuitry during mode ascension. Corrective actions consist of training, procedure revisions and personnel accountability. This report is made in accordance with 10CFR50.73 (a)(2)(i)(B), "any operation or condition which was prohibited by the plant's Technical Specifications."
2722010004 | Salem 1 | 09/20/2010 | 11/19/2010 | ML10330021 | <strong>Technical Specification 3.0.4.b Non-Compliance</strong><br /><i>Abstract:&nbsp;</i>In September 2010, Salem Unit 1 was in the process of an initial campaign to move 'aged' irradiated fuel from the Spent Fuel Pool (SFP) to a Dry Cask Storage facility. The evening of September 19, 2010, SFP manipulations procedural reviews commenced for loading Dry Cask Number 2. All chillers were operable. On September 20 at 0407 hours, the 13 Chiller was tagged out of service for scheduled maintenance. At 2049 hours, Unit 1 Control Room supervisor authorized irradiated fuel movement from the Unit 1 spent fuel pool to support dry cask storage. Movement of irradiated fuel commenced and was completed without meeting Technical Specification (TS) 3.0.4.b requirements for a risk assessment based on an inoperable chiller. TS 3.7.10 requires all three chillers to be operable for the movement of irradiated fuel. On September 29, an independent review by Operations in preparation for the next cask loading questioned whether movement of irradiated fuel should have commenced without the performance of a TS 3.0.4.b risk assessment with the 13 chiller out of service. The TS non-compliance was identified as a result of this review. The apparent cause was a failure to recognize TS 3.0.4.b applicability when a specified condition of the TS applicability was entered and inattention to detail during the evaluation of the effects of out-of-service equipment when reviewing procedural controls for movement of irradiated fuel. Corrective actions include personnel accountability, completion of risk assessment for remaining dry cask storage activities, and procedure revisions. This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), "any operation ... prohibited by the plant's Technical Specification."
2722010005 | Salem 1 | 10/15/2010 | 12/09/2010 | ML10356060 | <strong>Automatic Reactor Trip Due to Actuation of The Generator Protection Relay</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2010, at approximately 2312, Salem Unit 1 experienced an automatic reactor trip. The automatic reactor trip was the result of a turbine trip. The cause of the turbine trip was the actuation of the loss of field relay, which provides the regular (primary) protection for loss of excitation for the main generator. The exact cause for the loss of excitation has not yet been determined; a root cause evaluation is in progress. The most likely cause for the actuation of the loss of field relay is a defective Automatic Digital Regulator computer (WDR 2000). Corrective actions included: Repairing the main generator potential transformer spring loaded detent drawer locking mechanism and replacing the fuses. Unit 1 was returned to service with the voltage regulator in manual control. The unit 1 voltage regulator will be replaced during the next scheduled refueling outage. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B).…”
2752010001 | Diablo Canyon 1, Diablo Canyon 2 | 10/13/2009 | 08/27/2010 | ML10242004 | <strong>Common Cause Control Room Ventilation Radiation Detector Failures</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2009, 11:57 PDT, the combined Diablo Canyon Power Plant (DCPP) control room ventilation system (CRVS) transferred automatically to its pressurization mode of operation (mode 4) due to a high radiation signal from a system radiation monitor. On October 13, 2009, 12:26 PDT, radiation detector 1-RM-25 was found to be trending up and indicating 3 R/hr. Plant technicians removed this monitor from service upon verification of an invalid signal from the detector. On October 13, 2009, 14:42 PDT, radiation monitor 1-RM-26 was found to be trending up and was removed from service. On October 14, 2009, 0300 PDT, radiation monitor 2-RM-25 was found to be trending up and was removed from service. On October 15, 2009, plant technicians determined the cause of the 1-RM-25 failure to be water intrusion. On December 24, 2009, plant technicians determined the cause of the 1-RM-26 failure to also be water intrusion. Water intrusion was caused by manufacturer workmanship flaws. Based on the above, it was concluded that a common mode failure had occurred and was reportable under 10 CFR 50.73(a)(2)(vii).
2752010002 | Diablo Canyon 1, Diablo Canyon 2 | 03/09/2010 | 09/24/2010 | ML10278048 | <strong>Potential Loss of Safety-Related Pumps due to Degraded Voltage During Postulated Accidents</strong><br /><i>Abstract:&nbsp;</i>On March 9, 2010, while analyzing the consequences of a postulated sustained degraded grid voltage, Pacific Gas and Electric (PG&E) concluded both Units 1 and 2 were in an unanalyzed condition. On March 9, 2010, at 23:39 (EST), PG&E reported this unanalyzed condition to the NRC in accordance with 50.72(b)(3)(ii)(B) (reference NRC Event Notification Number 45754). The postulated sustained degraded voltage condition could have resulted in multiple safety-related pump motors, tripping overcurrent relays. As a result, these pumps would not be immediately available to mitigate a postulated accident and is considered a safety system functional failure. PG&E had not considered this postulated worst case degraded voltage condition credible, and had therefore not analyzed for it. As a result, technical specification (TS) surveillance requirement (SR) 3.3.5.3 values are nonconservative, and several TS Actions were not met. The immediate compensatory measure was to raise the first level undervoltage relay setpoints on the vital buses of both Units 1 and 2, thus transferring loads to emergency diesel generators prior to tripping motors on overcurrent. PG&E will submit a license amendment request to establish conservative TS SR 3.3.5.3 undervoltage relay settings. The apparent cause was misinterpretation of the undervoltage relay design criteria in the 1970's.
2752010003 | Diablo Canyon 1, Diablo Canyon 2 | 06/07/2010 | 02/11/2011 | ML11048014 | <strong>DCPP 230 kV Historical Evaluation of Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2009, the U.S. NRC issued a letter providing an interpretation of Technical Specification (TS) 3.8.1. Based on this letter, PG&E evaluated past operation of the 230 kV offsite power system. On June 7, 2010, PG&E determined that the 230 kV system was operated in a condition prohibited by TS and reportable under 10 CFR 50.73(a)(2)(i), (a)(2)(ii), and (a)(2)(v). Specifically, the 230 kV system for Units 1 and 2 was placed in an inoperable configuration from July 16, 2007 at 0245 PDT until July 27, 2007 at 1655 PDT, September 10, 2007 at 0140 PDT until September 15, 2007 at 0440 PDT, and November 3, 2008 at 0224 PST until November 7, 2008 at 0332 PST, in each event exceeding the 72 hour allowed outage time. The cause of operating in a condition prohibited by TS 3.8.1 is a non-conservative assumption leading to misinterpretation of 230 kV licensing basis requirements in 1995, which produced incorrect operating procedures. Corrective actions for this event include revision to a station procedure and revision to licensing documents in accordance with the above referenced U.S. NRC letter of December 14, 2009. The initial report was to be supplemented for any additional events uncovered in the archived operating logs. A review of the archived operating logs was conducted for the past three years and no additional events were uncovered.
2772010001 | Peach Bottom 2 | 01/30/2010 | 03/19/2010 | ML10082008 | <strong>Multiple Slow Control Rods Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>A condition prohibited by Technical Specifications was identified as a result of the performance of a surveillance test involving control rod scram time testing. As a result of the testing, it was identified that 21 of the 185 control rods were slow from control rod notch posiiton 48 to notch position 46. Stroke timing to other notches required by Technical Specifications were acceptable for these 21 control rods. The cause of the slow control rods was due to degradation of the diaphragms associated with the Scram Solenoid Pilot Valves (SSPVs). The SSPV diaphragms were replaced and the scram times were restored to acceptable values. Performance monitoring and the preventive maintenance program will be upgraded. There were no actual safety consequences associated with this event. There were no previous similar LERs identified.
2772010002 | Peach Bottom 2, Peach Bottom 3 | 09/18/2010 | 11/15/2010 | ML10320027 | <strong>Improperly Fastened Rod Hanger Results in Inoperable Subsystem of Emergency Service Water</strong><br /><i>Abstract:&nbsp;</i>On 9/22/10, Engineering personnel determined that a rod hanger (33HB-S143) supporting the discharge pipe of the 'A' Emergency Service (ESW) Pump had not been carrying adequate pipe load prior to recent upgrades of the ESW discharge pipe support system during the week of 9/13/10. It was determined that the rod hanger condition (prior to 9/13/10) would have been unacceptable due to its degraded seismic capability. The degraded condition of rod hanger 33HB-S143 only affected the 'A' ESW subsystem during postulated seismic conditions. Since this condition was caused by inadequate original construction installation, this event is considered to be a condition prohibited by Technical Specifications (TS) due to one subsystem of ESW being inoperable for a time period longer than allowed by TS. The original installation of the rod hanger was deemed to be inadequate since jam nuts were not installed to prevent loosening of the top nut that fastens the threaded rod hanger to a nearby structural steel member. The underlying cause was determined to be due to an inadequate design drawing. The affected rod hanger was repaired. The drawing associated with this rod hanger will be upgraded to clearly require staking requirements. A sample of similar rigid restraint drawings were reviewed for staking requirements and no other concerns were identified. There were no actual safety consequences associated with this event.
2772010003 | Peach Bottom 2 | 09/27/2010 | 11/19/2010 | ML10326046 | <strong>Laboratory Analysis Identifies Safety Relief Valves and Safety Valve Set Point Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Based on information received from 9/27/10 through 9/30/10 from a laboratory performing Safety Relief Valve (SRV) / Safety Valve (SV) as-found testing, Site Engineering personnel determined that SRV / SV set point deficiencies existed with two SRVs and one SV that were in place during the Unit 2 18th operating cycle. The SRVs / SV were determined to have their as-found set points in excess of the Technical Specification allowable ± 1% tolerance. The two SRVs and one SV outside of their Technical Specification allowable range were within the ASME Code allowable of ± 3% tolerance. The cause of the SRVs / SV being outside of their allowable as-found set points is due to set point drift. The SRVs / SV were replaced with refurbished SRVs / SV for the 19th Unit 2 operating cycle. There were no actual safety consequences associated with this event. There were three previous LERs identified involving SRVs / SVs exceeding their Technical Specification ± 1% setpoint requirement. There were no actual safety consequences associated with this event.
2772010004 | Peach Bottom 2, Peach Bottom 3 | 09/29/2010 | 11/24/2010 | ML10328050 | <strong>Improper Credit for Function of Off-Site Power Source Transformer Load Tap Changer</strong><br /><i>Abstract:&nbsp;</i>Based on information provided by the Nuclear Regulatory Commission (NRC) as part of their closeout of a Task Interface Agreement associated with an NRC unresolved item, the plant management staff determined that certain plant equipment could be degraded as a result of lower voltages that may exist during a postulated design basis loss-of-coolant event coupled with certain degraded voltage conditions. Although the safety significance of this event is considered to be very low, the event is considered to be a condition prohibited by Technical Specifications (TS). The cause of the event was due to the previous assumption that credit could be taken for the operation of the load tap changers associated with the offsite power source transformers. This credit would result in higher voltages to the supplied equipment. Upgrades to most of the TS impacted equipment have been performed. Other compensatory measures have been put in place to assure operability of other components until other design upgrades can be completed. There were no actual safety consequences associated with this event. There were no previous events identified.
2802010002 | Surry 1, Surry 2 | 06/04/2010 | 08/02/2010 | ML10223042 | <strong>Use of Aluminum Conduits for Cable Penetrations Degrades Fire Barriers</strong><br /><i>Abstract:&nbsp;</i>During the June 2009 Triennial Fire Protection Inspection, the NRC requested test results for aluminum conduits used in fire barrier penetrations. The testing documentation could not be produced. The fire barriers in question were declared non-functional and a condition report was initiated. Compensatory actions involved establishing fire watches for the non-functional barriers. A vendor was selected to test representative aluminum conduit configurations in fire barriers in accordance with IEEE 634-1978. Several configurations failed the 3-hour fire test. A design change was developed to modify penetrations that did not have proven test configurations, by installing seals on both side of the barrier. Since the modified aluminum conduit penetrations did not have proven test configurations, their function of preventing a fire from affecting redundant trains of safe shutdown systems could not be assured. NRC guidance for reportability, NUREG-1022, states missing fire barriers, such that the required degree of separation for redundant safe shutdown trains is lacking, is reportable as an unanalyzed condition that significantly degraded plant safety. Therefore, this report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(B).
2802010003 | Surry 1 | 06/08/2010 | 08/03/2010 | ML10225020 | <strong>Loss of Vital Bus due to Human Error Results in Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2010 at 0948 hours, with Units 1 and 2 at 100% power, the Unit 1 120 VAC Vital Bus 1- III was lost during maintenance. Main Feedwater Recirculation Valve A opened and the Main Feedwater Regulating Valves re-aligned. The resultant feedwater flow/steam flow mismatch coincident with low steam generator (SG) water level on SG A, resulted in a reactor trip. Safety Injection initiated due to loss of Vital Bus instrumentation and a momentary RCS cool down. The reactor was placed in hot shutdown and the health and safety of the public were not affected. The cause was inadvertent contact of a lead during Uninterruptible Power Supply (UPS) maintenance due to human error. Procedures and training will be revised to prevent recurrence. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A), automatic actuation of the reactor protection system. Following the trip, a resistor-capacitor suppressor failed in the Control Room Nuclear Instrument cabinet, resulting in a small fire. The fire was quickly extinguished. Therefore, this report is also being submitted pursuant to 10CFR50.73(a)(2)(x).
2822010001 | Prairie Island 1, Prairie Island 2 | 03/05/2010 | 07/02/2010 | ML10183038 | <strong>Unanalyzed Condition due to Postulated High Energy Line Break on Cooling Water System</strong><br /><i>Abstract:&nbsp;</i>On March 5, 2010, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 and Unit 2 were at 100% power. PINGP staff determined that in the event of a postulated high energy line break (HELB) event with a concurrent loss of offsite power (LOOP) and a single active failure of a cooling water (CL) pump without a corresponding safety injection (SI) signal, the CL system might not provide sufficient water to required cooling loads until after the turbine building cooling loads were isolated. The condition was determined to be reportable while investigating licensing conditions associated with a HELB. Inadequate management of HELB analyses impaired the station's ability to discover additional potential legacy vulnerabilities in a timely manner. Procedural changes have been made to ensure that the current configuration of two OPERABLE and one additional FUNCTIONAL safeguards cooling water pumps is maintained. In addition, a design basis document will be developed for the HELB program.
2822010002 | Prairie Island 1 | 04/26/2010 | 06/25/2010 | ML10176048 | <strong>Postulated Flooding of Unit 1 Fuel Oil Transfer Pump Motor Starters Could Have Resulted in Reduced Fuel Oil Inventory</strong><br /><i>Abstract:&nbsp;</i>Historically, Prairie Island Nuclear Generating Plant's (PINGP) Unit 1 relied on the total fuel oil stored in six Fuel Oil Storage Tanks (FOSTs) to meet the required minimum Technical Specification fuel oil inventory for the Diesel Driven Cooling Water Pumps (DDCLP) and the Unit 1 Emergency Diesel Generators. The postulated loss of two FOSTs fuel oil transfer pumps' motor starters could have resulted in the total fuel oil inventory falling below the amount required by Technical Specifications LCO 3.8.3 Condition A. On April 26, 2010, it was determined that a postulated flooding event in the Plant Screenhouse affecting the two DDCLP FOSTs fuel oil transfer pump's motor starters was reportable.
2822010003 | Prairie Island 1, Prairie Island 2 | 06/09/2010 | 03/31/2011 | ML11091015 | <strong>Postulated Flooding of Battery Rooms due to Inadequate Battery Room Door Threshold Seals</strong><br /><i>Abstract:&nbsp;</i>On June 9, 2010, the Battery Room Door 225 threshold seal was removed from the Battery Room door for repair at 12:10 CDT and the repair was completed at approximately 12:30 CDT. While the door seal was removed, the Structures, Systems and Components (SSCs) located in the Battery Rooms were vulnerable to a postulated Turbine Building flood. Technical Specifications (TS) Limiting Condition For Operation (LCO) 3.0.3 was entered from 1135 to1250 for both units and an eight-hour report for Loss of Safety Function (LOSF) (Event Number:45997) was made to the NRC at 19:02 CDT on June 9, 2010 under 10 CFR 50.72(b)(3)(v)(A) requirements. This condition is also reportable as a safety system functional failure under 10 CFR50.73(a)(2)(v)(A) for both Unit 1 and Unit 2.
2822010004 | Prairie Island 1, Prairie Island 2 | 10/22/2010 | 01/28/2011 | ML11028034 | <strong>Battery Charger Inoperability due to Potential Undervoltage Conditions</strong><br /><i>Abstract:&nbsp;</i>Safety related battery chargers have the potential to stop providing an output, or "lock up", if their AC input voltage drops below their nameplate minimum voltage of 90% of 480V at the battery charger Motor Control Center. Exact voltage, duration of voltage dip, and charger loading conditions which cause lock up of chargers are unknown. If a reduction in input voltage results in a battery charger locking up, the battery charger will not be able to recharge the battery from a partially discharged state unless operator actions are taken to restore the battery charger. On October, 22, 2010, an operability determination concluded that specific Design Basis Accident scenarios may include this undervoltage condition which could cause the battery chargers to lock up. The design basis requirements of the safeguards battery are such that it can carry expected shutdown loads for the DC system for one hour. Compensatory measures in the form of new operator actions have been put in place to support restoration of the battery chargers within this timeframe.
2822010005 | Prairie Island 1 | 09/09/2010 | 11/08/2010 | ML10313008 | <strong>Surveillance Required by Technical Specifications for the Emergency Diesel Generator Not Completed</strong><br /><i>Abstract:&nbsp;</i>Prairie Island Nuclear Generating Plant (PINGP) Technical Specifications (TS) 3.8.1, "AC Sources - Operating" Surveillance Requirement (SR) 3.8.1.10(c) performs a test of the Emergency Diesel Generator (EDG) in conjunction with a safety injection (SI) signal. SR 3.8.1.10(c) verifies that on an actual or simulated loss of offsite power signal in conjunction with an actual or simulated safety injection actuation signal that the EDG auto-starts from standby condition and energizes emergency loads in less than or equal to 60 seconds. The 12 Battery Charger is required to be energized during the Surveillance Procedure (SP) 1083 but was procedurally turned off. PINGP meets the SR by satisfactorily completing SP 1083, UNIT 1, INTEGRATED SI TEST WITH A SIMULATED LOSS OF OFFSITE POWER normally before entering Mode 4 after a refueling outage. During the prior three years, SP 1083 was not performed with the 12 Battery Charger turned on as required by SR 3.8.1.10(c) during the 1R25 (March 2008) and the 1R26 (October, 2009) refueling outages. Therefore this condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) because of a condition prohibited by TS.
2852010001 | Fort Calhoun | 11/01/2009 | 08/26/2010 | ML10252037 | <strong>Containment Integrity Violated During Refueling Leak Test due to Inadequate Training</strong><br /><i>Abstract:&nbsp;</i>Containment integrity was violated on November 1, 2009. This was a result of opening manual containment isolation valve SI-410 (Safety injection Tanks Fill/Drain Valve) when containment integrity was required and inadequate administrative controls were implemented. In preparation for performing a leak check of the safety injection tanks leakoff piping, a procedural step in the surveillance test opened manual containment isolation valve SI-410, as well as re-aligning other valves. The procedure prerequisites require the reactor coolant system to be pressurized above 600 psig, which results in the reactor coolant system being greater than 210 degrees F; thus, containment integrity is required. Prior to the performance of the ST on November 1, 2009, it was recognized that the opening of SI-410 needed to be administratively controlled. The ST procedure was revised to require administrative controls be in place prior to opening containment isolation valve SI-410. A root cause analysis determined that training on containment integrity to specifically meet the intent of TS 2.6(1)a, as defined in the TS basis section, is insufficient to ensure complete understanding of the requirements. The revision of training materials, retraining of appropriate plant persormel and revisions to appropriate plant documents will be administered using the station's corrective action program.
2852010002 | Fort Calhoun | 04/08/2010 | 06/04/2010 | ML10161009 | <strong>Failed Feeder Cable due to Inadequate Procedure Causes Station Shutdown</strong><br /><i>Abstract:&nbsp;</i>At 0238 Central Daylight Time (CDT) on April 8, 2010, a ground alarm for 480 Volt Bus 1B3A was indicating intermittently. The process of isolating loads on the Motor Control Center (MCC) required securing power to main feedwater isolation valve HCV-1385. Technical Specification (TS) 2.0.1 was entered at 1622 CDT due to HCV- 1385 being inoperable. At 1740 CDT, insulation on the supply feeder cables to MCC-3A1 was found to be degraded, and the phase 2 feeder cable was shorted to ground. A plant shutdown was commenced at 1740 CDT per the normal shutdown procedure. At 2123 CDT, the reactor was manually tripped from 22 percent reactor power per the normal shutdown procedure. All systems functioned properly. At 2123 CDT, the plant entered Mode 3. At 2233 CDT, HCV-1385 was manually closed and TS 2.6.1(1) was exited. The root cause analysis determined that the guidance in procedure EM-PM-EX-1100, "480 Volt Motor Control Center Maintenance," is inadequate to ensure that MCC-3A1 feeder cable lugs are properly torqued to the cables. This led to the high resistance connection at the phase 2 cable lug, overheating and degradation of the cable, and the subsequent ground on bus 1B3A. The feeder cable to MCC-3A1 was repaired and the ground cleared.
2852010003 | Fort Calhoun | 04/06/2009 | 08/10/2010 | ML13176A04 | <strong>Inadequate Margin Renders Auxiliary Feedwater Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2009, the Steam Driven Auxiliary Feedwater (AFW) Pump (FW-10) tripped off while performing OP-ST-AFW-0004 (Auxiliary Feedwater Pump FW-10 Operability Test). The pump tripped approximately one minute after it was successfully started. FW-10 discharge pressure switch (PS-1122) white indicating light was found lit on its control panel. This light indicates the pump tripped on high discharge pressure. Following the root cause analysis, it was determined that the pump had been inoperable since February 26, 2009. The root cause of this event was that Engineering Change (EC) 45105 (FW-10 Speed Limiting Governor Setting) and FDCR 45607 (Revise the Acceptance Criteria in EC 45105) reduced the discharge pressure margin to trip setpoint resulting in FW-10 becoming more susceptible to tripping on high discharge pressure. The corrective action was to increase the setpoint for the AFW Pump FW-10 High Discharge Pressure Shutdown Switch PS-1122 from 1450 pounds per square inch gage (psig) to 1600 psig.
2852010004 | Fort Calhoun | 04/28/2010 | 08/30/2010 | ML10243036 | <strong>Acoustic Monitor Failure Due to Inadequate Barriers for Protection of Cable</strong><br /><i>Abstract:&nbsp;</i>Flow Element (FE)-142, Accelerometer for Pressurizer Safety Valve RC-142 Flow Detection, failed its monthly surveillance test on May 26, 2010. One month earlier, on April 28, 2010, FE-142 had previously failed its monthly surveillance test. The failure of FE-142 on April 28, 2010, was identified in condition report (CR) 2010-2070. During the investigation for the May 26, 2010 failure, it was discovered that the direct cause for the earlier failure on April 28, 2010, was the same and had not been corrected. As a result of this discovery, FE-142 was reclassified as inoperable from April 28, 2010, to June 2, 2010, and the technical specification action time was exceeded. On June 30, 2010, the failure of FE-142 was determined to be reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The root cause of this event was that the hardline cable for the FE-142 accelerometer was allowed to have external stress applied because there were no barriers for the protection of the hardline cable during maintenance activities in the pressurizer cubicle. This allowed stress to be applied to the sotfline cable, which weakened the center conductor of the softline cable and caused the failure. The softline cable was replaced making FE-142 operable. Other actions will be administered by the station's corrective action program.
2852010005 | Fort Calhoun | 01/06/2010 | 01/26/2011 | ML11084045 | <strong>Inoperability of the Emergency Diesel Generator Fuel Oil Transfer System</strong><br /><i>Abstract:&nbsp;</i>Diesel Fuel Oil Transfer Pump FO-37 and its credited portable back-up pump were inoperable on January 6-7, 2010. On January 6, 2010, FO-37 was rendered inoperable due to local area flooding caused by the rupture of FP-772, "Service Building Fire Sprinkler Isolation Valve". A function of FO-37 is to transfer diesel fuel between "Diesel Fuel Oil Storage Tanks" FO-10 and FO-1. On June 24, 2010, an engineering evaluation determined that the credited portable back up pump to FO-37 was not the correct pump for the application and would not transfer diesel fuel oil from FO-10 to FO-1 as intended. Since both pumps (FO-37 and the credited portable back-up pump) were inoperable this is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). A root cause analysis determined there was a failure to perform an appropriate design change evaluation for maintaining diesel fuel oil transfer system capability as required by Technical Specification Amendment 162, dated March 29, 1994. The originally credited portable back-up pump was replaced with a new portable pump that has the capability to transfer diesel fuel oil between tanks FO-10 and FO-1. The appropriate procedures were revised to address the pump replacement.
2852010006 | Fort Calhoun | 12/23/2010 | 04/29/2011 | ML11122007 | <strong>Reactor Trip Due to Erroneous Moisture Separator Trip Signal</strong><br /><i>Abstract:&nbsp;</i>Fort Calhoun Station was operating at full power (nominal 100 percent). The station was preparing a scaffolding for an upcoming outage when on December 23, 2010, at 1050 Central Standard Time (CST), a reactor trip occurred. The operators entered Emergency Operating Procedure (EOP) 00, "Standard Post Trip Actions." The main steam and feedwater systems operated normally. All control rods inserted fully. The apparent cause of the turbine and subsequent reactor trip was the inadvertent actuation, caused by bumping, and sticking of one of four turbine moisture separator high water level turbine trip switches while reactor power was above 15 percent. The root cause was insufficient performance monitoring of the moisture separator high level trip mercury switches which resulted in degraded performance and increased risk for susceptibility to binding. Following the initial determination of the erroneous moisture separator high level trip signal, immediate actions included: halting all work near the moisture separator sensing lines and level switches, posting the affected areas as "Protected Equipment," and initiating a stop work action for all ongoing scaffold work within the turbine building. The Ioisture separator level switches and logic will be replaced during the 2011 refueling outage.
2862010001 | Indian Point 3 | 03/02/2010 | 04/30/2010 | ML10130006 | <strong>SSFF and TS Violation for an Inoperable RCS Wide Range Temperature Cold Leg Instrument TE-413B Credited for TS 3.3.4 Remote Shutdown</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2010, at approximately 19:18 hours, an engineering evaluation determined that there were instances of past performance that may have affected the operability of the Reactor Coolant System 31 wide range cold leg temperature loop T-413B required by Technical Specification (TS) 3.3.4, Remote Shutdown. The review concluded that the remote cabinet electro switch instrumentation switch used to transfer the circuit from the Control Room to the remote shutdown cabinet had evidence of high resistance on the contacts. This is a resistance measuring circuit and changes in resistance can affect the accuracy of the instrument. This was evaluated and a conclusion was reached that the plant had been in a condition outside TS and that constituted a safety system functional failure due to repeat surveillance failures. The cause was transfer switch high resistance. This was not identified due to poor change management and lack of proper program implementation. Completed corrective actions were a surveillance to demonstrate the current operability of the instrument successfully performed on March 2, 2010 when past inoperability was identified, revised the calibration procedure to provide adequate steps for performing R/I calibrations and proper as found criteria, and the current set point drift review process now provides a more timely review of as found calibration results for potential impacts on set point drift. Scheduled corrective action is to revise the calibration procedure to ensure CR and remote shutdown indications are consistent. This condition had no significant effect on public health and safety.
2862010002 | Indian Point 3 | 09/09/2010 | 11/08/2010 | ML10321030 | <strong>Manual Reactor Trip due to a Cooling Water Leak in the Main Generator Exciter Air Cooler</strong><br /><i>Abstract:&nbsp;</i>On September 9, 2010, during full power operations, a water leak in the main generator exciter housing was observed by an operator during rounds and the condition reported to the control room. Operations initiated closure of the Exciter heat exchanger inlet cooling water valve (SWT-25-2) in order to isolate the B section of the exciter cooler. Almost immediately the leak worsened confirming that the leak was in the A section of the exciter cooler. Water was observed to be pooling in the Permanent Magnet Generator section of the exciter and a manual reactor trip was initiated. All control rods fully inserted and all required safety systems functioned properly and the plant was stabilized in hot standby. There was no radiation release. No Emergency Diesel Generator actuated as offsite power remained available. The Auxiliary Feedwater System automatically started as expected due to Steam Generator low level from shrink effect. The direct cause of the event was a leak in the 31 Exciter Air Cooler due to the failure of an Admiralty Brass tube (S-1-11) from erosion and corrosion. The root cause was component monitoring was less than adequate. The current Eddy Current Testing, Tube Air Pressure Testing, and visual inspection techniques do not effectively identify degradation in the tube sheet area. Corrective actions include: Inspections and testing of both exciter coolers was performed and 194 tube end sleeves were installed in both ends of all unplugged tubes of the 31 and 32 Exciter Air Cooler (tube S-1-11 was plugged and two other tubes had previous plugging), guidance will be developed for inclusion in a procedure for high risk heat exchangers with Admiralty Brass tubes to proactively sleeve tube ends as a mitigation strategy. The event had no effect on public health and safety.
2932010001 | Pilgrim | 01/10/2010 | 03/11/2010 | ML10074034 | <strong>Single Train of Reactor Building Closed Cooling Water System Inoperable for Time Period Exceeding Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2010 during a backwash evolution on the Reactor Building Closed Cooling Water (RBCCW) System heat exchanger, plant operators discovered a broken bolt on the pipe clamp for the seismic support for the instrument line of the local pump suction pressure gauge attached to the RBCCW "A" Train pump suction pipe. The seismic support is provided to ensure instrument line integrity and is relied on to ensure that RBCCW leakage limits will not be exceeded. The broken bolt compromised the design function of the seismic support and RBCCW "A" Train was conservatively declared inoperable until a new bolt was installed. Pilgrim Station was operating at 100% power when the condition was identified. Subsequent engineering reviews could not determine the exact time that the bolt broke. Based on the condition of the bolt it was assumed that the bolt was broken for time period that exceeded the 72 hour allowable Technical Specification (TS) Limiting Condition of Operation (LCO) action statement for one RBCCW subsystem inoperable. An immediate corrective action was completed to install a new bolt on the seismic support clamp. Additional corrective actions were taken to identify extent of condition and to walkdown the Reactor Building Auxiliary Bay areas where similar conditions could exist. No other broken bolts or seismic support damage was identified.The probable apparent cause was identified to be corrosion that caused a progressive crack which eventually failed the bolt. The event posed no threat to public health and safety.
2932010002 | Pilgrim | 03/25/2010 | 05/20/2010 | ML10155044 | <strong>Standby Gas Treatment Declared Inoperable after Discovery of Open Demister Door</strong><br /><i>Abstract:&nbsp;</i>At 22:55 EDT on March 25, 2010, the normally closed Demister Door on 'B' Train of Standby Gas Treatment (SBGT) was found open. The door was opened during the performance of a scheduled surveillance and was subsequently not closed at the completion of surveillance. With this door being open the 'B' Train of SBGT was unable to perform its safety-related function. Because of the physical configuration of the SBGT system, it could not be immediately verified whether the 'A' Train would have been able to perform its safety-related function, since it could have drawn suction through the open demister door of the 'B' Train and the normally open crosstie between the trains. Upon discovery of the condition, a 36-hour LCO was entered in accordance with the Technical Specification (TS) 3.7.B.1.a, the 'B' demister door was closed, LCO was exited, and operability of both 'A' and 'B' Trains of the SBGT System was established. At the time the open demister door was discovered on March 25, 2010, the plant was operating at 100% power. Both Trains of SBGT System were declared inoperable from 16:07 hours to 22:55 hours, (approximately 6 hours) until the door was verified closed. The cause of the open demister door was a human performance error due to a failure to verify that the door was closed upon completion of the surveillance. Corrective actions taken included closing of the demister door, coaching of the affected personnel who performed the surveillance, and enhancements to the surveillance procedure to preclude recurrence. The event posed no threat to public health and safety.
2962010001 | Browns Ferry 3 | 04/20/2010 | 06/21/2010 | ML10174043 | <strong>Safety Relief Valves As-Found Setpoints Exceeded Technical Specification Lift Pressure Values</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2010, the Tennessee Valley Authority (TVA) determined that 8 of the 13 Safety Relief Valves (SRVs), removed from Unit 3 following Cycle 14 operation, mechanically actuated at pressures greater than 3 percent above their Technical Specification (TS) setpoints, and thus, were inoperable. Unit 3 TS Limiting Condition for Operation (LCO) 3.4.3 requires twelve (12) SRVs to be operable in reactor Modes 1, 2, and 3. With one or more required SRVs inoperable, TS 3.4.3 Action A requires the unit to be placed in Mode 3 (hot shutdown) within 12 hours and in Mode 4 (cold shutdown) within 36 hours. Since 8 of the 13 SRVs were found during test to have actuated above their TS setpoints, it is concluded that Unit 3 operated with inoperable SRVs longer than allowed by TS 3.4.3 Action A. The root cause of the SRV setpoint drift is corrosion-induced bonding between the pilot disc and seating surface. TVA is submitting this report in accordance with 10 CFR 50.73(a)(2)(i)(B), as any operation or condition prohibited by the plant's Technical Specifications.
2962010002 | Browns Ferry 3 | 04/20/2010 | 06/21/2010 | ML10174043 | <strong>A Subsystem of the Standby Liquid Control System was Inoperable Longer than Allowed by the Plant's Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2010, the 3B Standby Liquid Control (SLC) Pump failed to start during the performance of the quarterly SLC Pump Functional Test. For the test, Operations personnel had declared both SLC subsystems inoperable in accordance with the procedure and entered Technical Specifications (TS) Limiting Conditions for Operation (LCO) 3.1.7 Actions for both SLC subsystems inoperable (Action B, which requires restoration of one subsystem to operable status within 8 hours) and for one SLC subsystem inoperable (Action A, which requires both subsystems restored to operable status within 7 days). Operations personnel returned the 3A SLC Pump to operable status and exited Action B. Action B was re-entered to complete the testing, and, after successful testing of the 3B SLC Pump, Operations personnel declared both subsystems operable and exited TS LCO 3.1.7 Actions B and A. The cause of this event was the inoperability of the 3B SLC Pump motor breaker discovered when the pump failed to start. On March 29, 2010 during the refueling outage when racking in this breaker, the breaker's racking shaft sleeve did not fully engaged. Unit 3 entered TS LCO 3.1.7 applicability on April 6, 2010, during startup. Therefore, SLC Subsystem B was inoperable from April 6, 2010, to April 20, 2010, which is longer than the 7 day Completion Time allowed by Action A. SLC Subsystem A remained operable during this period.
2962010003 | Browns Ferry 3 | 03/26/2010 | 04/21/2011 | ML11115A09 | <strong>Multiple Test Failures of Excess Flow Check Valves</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2010, it was determined that 5 of 15 Excess Flow Check Valves (EFCVs) tested following Unit 3 Cycle 14 operation failed to meet Technical Specifications (TS) Surveillance Requirement (SR) 3.6.1.3.8, which requires verification that a representative sample of reactor instrumentation line EFCVs actuate to the isolation position on a simulated instrument line break signal. With the discovery of multiple failures during unit shutdown for refueling, multiple EFCVs may have been inoperable during Cycle 14 operation. TS Limiting Condition for Operation 3.6.1.3 requires that each Primary Containment Isolation Valve be operable in reactor Modes 1, 2, and 3, and when the associated instrumentation is required to be operable. Given the multiple failures of EFCVs, it is likely that Unit 3 did not comply with the applicable Required Actions and associated Completion Times of TS 3.6.1.3 Action C. Accordingly this situation is being reported as any operation or condition prohibited by the plant's Technical Specifications, i.e., 10 CFR 50.73(a)(2)(i)(B). The failed EFCVs were replaced. In accordance with the implementation of the Maintenance Rule (10 CFR 50.65) the Browns Ferry Nuclear Plant (BFN), Units 1, 2, and 3 EFCVs have been placed in Maintenance Rule a(1) status. The BFN Corrective Action Program has implemented actions to improve reliability of the EFCVs.
2962010004 | Browns Ferry 3 | 12/26/2010 | 02/24/2011 | ML11061033 | <strong>Manual Reactor Scram due to High Vibration on the Generator Exciter Inboard and Outboard Journal Bearings</strong><br /><i>Abstract:&nbsp;</i>On December 26, 2010, at 1615 hours Central Standard Time, an alarm for Main Turbine Vibration High 3-VA-47-15 was received in the Unit 3 control room on annunciator panel 3-XA-55-7B Window 32. Control room operators responded using Unit 3 Alarm Response Procedure (ARP) 3-ARP-9-7B. Exciter rotor inboard journal bearing vibration level indicated 8.0 mils and rising, and the outboard journal bearing indicated 5.5 mils and rising. At 1617 hours, an Upper Power Runback was initiated per the ARP. It was noted that vibration levels initially lowered then continued rising. At 1620 hours, control room operators initiated a manual reactor scram. The direct cause of this event was an exciter rotor-deflector rub resulting from a combination of high differential air exit temperatures and existing decreased clearances on the rotor. The root cause was inadequate procedural guidance for monitoring the exciter air cooling system and prescribing mitigation actions to be taken based on differential temperature limits. The rub was corrected during the forced outage. Corrective actions include installation of cooler vents for use in minimizing air binding, establishment of a cooler venting process, increased controls and documentation of manual "balancing" valve manipulation, increased system monitoring process rigor and oversight, and performance of a training analysis for inclusion of relevant aspects of this root cause into the Operations and Engineering training materials.
2982010001 | Cooper Station | 01/12/2010 | 03/05/2010 | ML10070059 | <strong>Technical Specification Prohibited Condition Due to Safety Relief Valve Test Failures</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2010, two of eight Target Rock safety relief valve (SRV) pilot valve assemblies, removed during refueling outage 25, failed to lift within Technical Specification (TS) lift setpoint requirements. Wyle Laboratories, Inc. performed this testing. The pressure setpoint for the first pilot assembly is 1100 +1- 33.0 psig; the SRV pilot assembly lifted at 1166 psig. The pressure setpoint for the second pilot assembly is 1090 +1- 32.7 psig; it lifted at 1139 psig. Two subsequent informational lifts were performed for both SRV pilot assemblies and were within the TS pressure setpoint tolerances. Cooper Nuclear Station (CNS) was in Mode 1, Power Operation, at approximately 74% power at the time of the discovery. The remaining SRV and SRV pilot valve assemblies tested satisfactory for TS lift setpoint requirements. The cause is the same as previously reported in Licensee Event-Report 2008-002-00, pilot disc-to-seat corrosion bonding. The performance of the two-stage Target Rock pilot-actuated valves in the current design application at CNS is unsuccessful in consistently meeting the as-found lift test requirements. CNS is pursuing corrective actions to evaluate and revise the as-found test requirements contained within TS. This event is reportable as a condition prohibited by TS. The event has negligible safety significance.
2982010003 | Cooper Station | 08/24/2010 | 10/21/2010 | ML10301003 | <strong>Low Voltage on Emergency Transformer Causes Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On August 24, 2010, at 08:14 Central Daylight Time, a low voltage condition occurred on the offsite power supply to the Emergency Station Service Transformer (ESST) during planned maintenance on the Station Startup Service Transformer (SSST). Subsequently, ESST secondary voltage dropped below the level where essential 4160 volt alternating current buses will automatically load onto the ESST. Cooper Nuclear Station (CNS) control room operators declared the ESST inoperable and entered the Technical Specification limiting condition for operation condition for two offsite circuits inoperable. After two minutes, ESST secondary voltage was restored to the proper level. CNS control room operators returned the ESST to operable status at 08:46. The cause of this event was that CNS' review of a revised switching order, associated with planned maintenance on the SSST, was inadequate. A change in sequence for switching activities had been made by the Nebraska Public Power District's system control center and the risk significance of the change was not recognized by CNS. To prevent recurrence of the event, CNS will revise procedures to add a precautionary note for performing offsite power source switching manipulations. CNS reported this event per Event Notification 46201. The event has negligible safety significance.
2982010004 | Cooper Station | 08/19/2010 | 11/18/2010 | ML10327004 | <strong>Loss of Safety Function for Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2010, at 10:05 Central Daylight Time, Cooper Nuclear Station Emergency Diesel Generator (EDG) Doors N103 and N104 were propped open for planned maintenance on EDG2. EDG2 was inoperable to support draining of the jacket water system. Door N103 is rated as a Steam Exclusion Barrier (SEB) door on the Turbine Building side of EDG1 room. With Door N103 propped open, if a main steam line rupture were to occur in the Turbine Building, the steam could enter EDG1 room through the propped open door, which may affect operability of EDG1. This resulted in an unanalyzed condition, as the EDG rooms had not been evaluated or analyzed for a High Energy Line Break. With EDG2 already declared inoperable for planned maintenance, having EDG1 inoperable creates a condition that could have prevented the fulfillment of the safety function of the EDGs. The root cause of this event was that impairment of Door N103 (a SEB door) for maintenance activities was evaluated using procedural guidance based upon a Probabilistic Risk Assessment (PRA) rather than performing an operability evaluation. Corrective Actions are established to develop training that explains and clarifies when PRA can be used and when PRA cannot be used. This event was not risk significant.
2982010005 | Cooper Station | 11/09/2010 | 04/28/2011 | ML11124A01 | <strong>Steam Exclusion Barrier Door Blocked Open Results in Loss of Safety Function I</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2010, a steam exclusion barrier (SEB) door in the control room corridor at Cooper Nuclear Station (CNS) was blocked open with a ladder to facilitate preventive maintenance. With this SEB door obstructed, steam from a postulated high energy line break could propagate into the control room and affect operability of systems, structures, or components necessary to safely shut down, cool down, and maintain cold shutdown conditions of the plant. During the time frame the door was blocked open for the work evolution, there were no Technical Specification required actions taken and no compensatory measures implemented. The root cause of the event is a failure to implement a comprehensive barrier control process. To prevent recurrence, CNS will develop a hazard barrier control process using appropriate fleet engineering standards or other approved industry guidance. This event was not risk significant.
3012010001 | Point Beach 2 | 06/19/2010 | 08/18/2010 | ML10230023 | <strong>Manual Reactor Trip Following Automatic Turbine Trip due to Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>On June 19, 2010 at 06:36 CDT control room personnel initiated a manual reactor trip of Unit 2 from MODE 2 at 0% power. Prior to the manual reactor trip, an automatic turbine trip occurred due to receipt of a generator lockout signal. Prior to automatic turbine trip, power reduction to 44% had been completed and the unit was being maintained in a stable condition in MODE 1. Following the trip, all safety systems and equipment operated as expected. All rods fully inserted into the core. The generator lockout was due to incorrectly calculated generator protection third harmonic stator ground trip relay setpoints. The incorrect setpoints were based on data taken during Unit 2 startup following the fall 2009 refueling outage. The installation of the relay setpoints occurred on February 24, 2010, when Unit 2 was at 100% power. The setpoints were not correct for the new plant configuration across the full range of power operation. The third harmonic function relays were removed from service on June 20, 2010, pending resolution of appropriate setpoint values. Unit 2 was returned to service on June 21, 2010. Immediate corrective actions included disabling the affected relay functions until new setpoints are calculated or the trip function is converted to an alarm function.
3012010002 | Point Beach 2 | 07/09/2010 | 09/03/2010 | ML10246011 | <strong>Manual Reactor Trip due to Failure of Feedwater Regulating Valve Positioner</strong><br /><i>Abstract:&nbsp;</i>On 7/9/10 at 06:47 CDT, control room personnel initiated a manual reactor trip of Unit 2 from approximately 64% power as a result of a failure of the range diaphragm assembly in the 'A' feedwater regulating valve (FRV) [FCV] positioner. Safety systems functioned as expected. Control rods fully inserted into the core. Unit 2 was returned to full power on 7/11/10 at 07:57. Corrective actions included rebuilding the failed 2CS-466 'A' FRV positioner and the 2CS-476 'B' FRV positioner. This 60-day licensee event report is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(iv)(A).
3012010003 | Point Beach 2 | 12/13/2010 | 02/07/2011 | ML11039008 | <strong>Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2010, at 1205 CST, preparations for a Technical Specification (TS) required shutdown were initiated on Point Beach Nuclear Plant (PBNP) Unit 2. TS Limiting Condition for Operation (LCO) 3.1.4, Rod Group Alignment Limits, was not met because Surveillance Requirement (SR) 3.1.4.2 was not met. The shutdown was subsequently completed at 1703 CST, December 13, 2010. A degraded field connection for the F-6 control rod caused control rod fuse 21 to blow, which ultimately resulted in the urgent and non-urgent alarms being received during performance of control rod exercises and the inability to complete the surveillance test. Following the shutdown, when a connection on a patch panel in containment was opened, checked and re-seated, the fault condition cleared as validated by numerous megger readings. Additional corrective actions include inspections of the connections during each unit's 2011 refueling outage. These actions are being tracked in the site's corrective action program. This 60-day licensee event report is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(i)(A), the completion of any nuclear plant shutdown required by the plant's Technical Specifications.
3012010004 | Point Beach 2 | 12/15/2010 | 02/14/2011 | ML11045068 | <strong>Manual Reactor Trip During Startup</strong><br /><i>Abstract:&nbsp;</i>On December 15, 2010, at 0148 CST, control room personnel initiated a manual reactor trip of the Unit 2 reactor to abort a startup that was in progress. At the time of the event, the reactor was subcritical. The manual reactor trip was initiated because rod control urgent and non-urgent alarms had been received with multiple control rods inserting freely, as indicated by individual rod position indicators and rod bottom lights. All systems functioned as expected following the trip, with all control rods fully inserting into the core. Troubleshooting determined that a degraded field connection for the D-10 control rod was the cause of the event. The degraded connection was repaired. Unit 2 was returned to service on December 21, 2010, at 0824 CST with no anomalies occurring during startup. Additional corrective actions include inspections of the connections during each unit's 2011 refueling outage. These actions are being tracked in the site's corrective action program. This 60-day licensee event report is being submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS).
3022010001 | Crystal River 3 | 10/13/2010 | 03/14/2011 | ML11081006 | <strong>As-Found Cycle 16 Pressurizer Code Safety Valve Setpoints Outside Improved Technical Specification Limit</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2010, and October 5, 2010, Progress Energy Florida, Inc., (PEF) Crystal River Unit 3 (CR-3) was in NO MODE (core off loaded) when Wyle Labs provided Notices of Anomaly for each of two Pressurizer Code Safety Valves (PCSVs) that had been removed during the Cycle 16 refueling outage (R16) and replaced with rotating spare PCSVs. The as-found lift setpoint for one PCSV was 5.32 percent above the Improved Technical Specification (ITS) setpoint and the other PCSV was 2.08 percent above the ITS setpoint. ITS 3.4.9 states that two PCSVs shall be operable in MODES 1, 2 and 3. To be operable, the PCSV lift setpoints must be within the maximum allowable tolerance of +/- 2 percent. The existence of similar discrepancies in these relief valves is an indication that the discrepancies may have developed over a period of time. PEF concludes that both PCSVs were inoperable during plant operation and that the condition is reportable under 10CFR50.73(a)(2)(i)(B). This condition does not represent a reduction in the public health and safety. The selected cause is failure to manage vendor quality. CR-3 plans to issue a PCSV specification to include specific repair requirements, surveillance requirements, valve settings, documentation requirements and a steam test procedure obtained from Dresser Industries. Similar occurrences have not been previously reported to the NRC.
3052010001 | Kewaunee | 09/20/2010 | 11/17/2010 | ML10328005 | <strong>Safety Injection Pump Recirculation Line Isolation Results in Violation of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2010, Dominion Energy Kewaunee (DEK) determined that both safety injection (SI) pumps had previously been rendered inoperable contrary to Technical Specifications (TS) requirements. The onsite NRC Resident staff had questioned the appropriateness of shutting the isolation valves on the common minimum flow recirculation line for both SI pumps while the reactor was in power operation mode. These valves had been routinely shut for short periods in the past to conduct required pump and valve testing. As a result of the evaluation of this condition, DEK determined that certain postulated accident scenarios could result in the SI pumps running when the recirculation line was needed for pump operability. Consequently, shutting the recirculation line isolation valves rendered both SI pumps inoperable. The recirculation valves were open and both SI pumps were in an operable status when this determination was made. DEK subsequently implemented administrative controls to preclude shutting these valves when the SI pumps were required to be operable. Kewaunee Power Station (KPS) TS do not allow both SI pumps to be inoperable concurrently, resulting in this condition being a violation of TS requirements. This event is being reported pursuant to 10 CFR 50.73 (a)(2)(i)(B), any operation or condition which was prohibited by TS; and, pursuant to 10 CFR 50.73 (a)(2)(v), any event or condition that could have prevented the fulfillment of a safety function.
3062010001 | Prairie Island 2 | 04/16/2010 | 06/15/2010 | ML10167005 | <strong>Unit 2 Turbine Trip During Reactor Shutdown Resulting in a Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2010, the Prairie Island Nuclear Generating Plant's (PINGP) Unit 2 reactor down power began in preparation for 2R26 refueling outage. At approximately 13% power the turbine automatically tripped due to a greater than 2.5 inch Hg pressure differential between the A and B condensers. The steam plant and reactor protection system responded as expected to the initial event. After the reactor trip, operators responded in accordance with procedures, recovered vacuum, and continued with the Unit 2 shutdown.
3062010002 | Prairie Island 2 | 05/25/2010 | 07/16/2010 | ML10200016 | <strong>Unit 2 Turbine Shutdown due to the Loss of a Main Feed Water Pump that Resulted in a Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2010, Prairie Island Nuclear Generating Plant's (PINGP) Unit 2 Reactor was increasing power following the 2R26 Refueling Outage. At approximately 32% power the turbine automatically tripped due to a trip of the 21 Main Feed Water Pump (FWP). The turbine trip resulted in an automatic Unit 2 Reactor trip. The 21 FWP trip was due to the failure of the FWP suction pressure switch. The steam plant and reactor protection system responded as expected to the initial event. After the reactor trip, operators responded utilizing emergency operating procedures for reactor trip and reactor trip recovery and transitioned into a normal shutdown procedure.
3062010003 | Prairie Island 2 | 05/21/2010 | 07/16/2010 | ML10200017 | <strong>Unit 2 Fuel Oil Transfer Pumps are Vulnerable to a Potential Common Mode Failure</strong><br /><i>Abstract:&nbsp;</i>Prairie Island Nuclear Generating Plant (PINGP) Unit 2 has four Fuel Oil Storage Tanks (FOSTs) to provide fuel oil to the D5 and D6 Emergency Diesel Generators (EDG). Each EDG FOST has an electric fuel oil (FO) transfer pump. The FO transfer pumps were installed as part of the installation of D5 and D6 in 1992. The Unit 2 FO transfer pumps are vulnerable to a common mode failure. On May 21, 2010, it was determined this condition was reportable. FO was transferred to meet the required mission time and an Engineering Change Request has been written to correct the common mode failure mechanism.
3112010001 | Salem 2 | 01/03/2010 | 03/03/2010 | ML10064054 | <strong>Manual Reactor Trip Due to Degraded Condenser Heat Removal</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2010, at approximately 0804, a manual reactor trip was initiated with reactor power level at approximately 80%. The manual reactor trip was initiated in response to a degraded Circulating Water (CW) system and in accordance with operating procedures. The CW system degradation was due to heavy ice loading that affected the ability of CW traveling water screens (TWS) to operate, which resulted in the loss of four out of six CW pumps. The unit was returned to service on January 4, 2010, at 1831 after ice was cleared from the screens, condenser water boxes were cleaned and demonstrated to operate properly. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)
3112010002 | Salem 2 | 01/21/2010 | 05/28/2010 | ML10162018 | <strong>Automatic Reactor Trip due to 21 Steam Generator Feedwater Pump Trip and Steam Generator Low Level</strong><br /><i>Abstract:&nbsp;</i>On January 21, 2010, at 1818 hours, the 21 Steam Generator Feedwater Pump (SGFP) tripped. A turbine runback automatically initiated as expected and steam generator level in all four Steam Generators (SG) continued to lower. The 22 SG reached the SG low level reactor trip setpoint at 1820 hours resulting in an automatic reactor trip. All control rods fully inserted on the trip. All three Auxiliary Feedwater (AFW) pumps started in response to the low SG water level and decay heat was removed by the steam dumps to the main condenser. Operators entered the emergency procedures for the plant trip and stabilized the plant in Mode 3 (HOT STANDBY). The cause of the 21 SGFP trip was an internal wiring short in the SGFP trip control circuit that resulted in a false low suction pressure trip signal. The cause for the wiring short was the result of poor work practices. The reactor tripped on low water level in the 22 SG as designed. Corrective actions consist of lug inspections, document changes, training analysis, and evaluation of the integrated plant response to a SGFP trip from full power and implementing changes as appropriate. This report is made in accordance with 10CFR50.73 (a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)."
3112010003 | Salem 2 | 10/17/2010 | 12/09/2010 | ML10356060 | <strong>Automatic Reactor Trip Due to Reactor Coolant Pump Bus Undervoltage</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2010, at approximately 0512 hours, Salem Unit 2 automatically tripped due to bus undervoltage for the 21 through 24 Reactor Coolant Pumps (RCPs). The non-safety related group buses which power the RCPs were being fed from the Unit 2 Auxiliary Power Transformer (APT). The APT is directly powered from the Unit 2 main generator. At the time of the trip the main generator voltage regulator was in manual control and was being transferred to automatic control. During the voltage regulator transfer to automatic, a loss of excitation occurred. This loss of excitation led to the undervoltage condition on the group buses. The 22 through 24 RCPs tripped following the reactor trip when their respective breakers opened on undervoltage, the 21 RCP continued to run through the event. The 21 and 22 Auxiliary Feedwater (AFW) pumps started as a result of the trip of both main feedwater pumps. The 23 AFW pump started as a result of low steam generator levels in all four steam generators. Unit 2 was stabilized in Mode 3 with a reactor coolant temperature of 547°F and a reactor coolant pressure of 2235 psig. The cause of the automatic reactor trip was an undervoltage condition on the non-safety related group buses which power the RCPs. The undervoltage condition was the result of a loss of main generator excitation during the transfer of the voltage regulator from manual to automatic. Troubleshooting determined that loss of excitation was the result of a degraded 43A transfer relay that failed to transfer excitation control from the manual voltage regulator to the automatic voltage regulator. Corrective actions included replacement of the 43A transfer relay. This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)...".
3132010001 | Arkansas 1 | 03/18/2010 | 05/14/2010 | ML10137024 | <strong>Multiple Main Steam Safety Valves Not within Limits due to Seat Bonding and Transient-Induced Drift Resulting in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On March 18-19, 2010, during setpoint testing of the main steam safety valves (MSSVs), four valves (PSV-2686, PSV-2691, PSV-2697, and PSV-2698) were discovered out-of-tolerance (OOT) with respect to the technical specification (TS) +/-3% surveillance requirement (SR) 3.7.1.1. PSV-2686 was 3.75% OOT, PSV-2691 was 3.86% OOT, PSV-2697 was -3.02% OOT, and PSV-2698 was -3.18% OOT. There were two apparent causes for these conditions. The PSV-2686 and PSV-2691 OOT condition was due to seat bonding, which is characterized by the formation of an oxide adhesion layer between metal parts. The PSV-2697 and PSV-2698 OOT condition was due to transient-induced drift, characterized by a valve lifting below the desired setpoint, which occurs when the spring is exercised due to valve actuations. The MSSVs were reset to within +/-1% tolerance. Current planned follow-up actions include retesting the affected valves after six months of operation and to continue exercising newly refurbished and installed valves within four months of installation as required by the model work order.
3132010002 | Arkansas 1 | 03/27/2010 | 05/26/2010 | ML10147024 | <strong>Reactor Coolant System Pressure Boundary Leakage due to Primary Water Stress Corrosion Cracking of Pressurizer Level Instrument Tap Resulted in Degradation of a Principal Safety Barrier</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2010, with Arkansas Nuclear One - Unit 1 (ANO-1) in Mode 6 for a refueling shutdown, visual examinations discovered indications of through wall leakage on an ANO-1 Reactor Coolant System (RCS) pressurizer level instrument tap nozzle. Leakage was indicated by a small amount of dry boron on the lower portion of the nozzle bore with rust stains on the Alloy 600 nozzle and in the vicinity surrounding the nozzle outlet. Subsequent inspections and evaluation revealed minor corrosion of the nozzle bore and concluded that the failure mechanism for the degradation was Primary Water Stress Corrosion Cracking (PWSCC) of Alloy 600 material. A planned mitigation repair method for the affected nozzle was implemented to resolve this condition. Also, in accordance with Arkansas Nuclear One's Inservice Inspection program, the remaining 8 pressurizer nozzles were visually inspected and exhibited no indications of leakage or degradation. During the refueling outage, all 9 pressurizer instrument nozzles were replaced with materials that are resistant to PWSCC. The pressurizer nozzles with dissimilar metal butt welds (surge, spray, and safety valve nozzles) had previously been mitigated by a full structural weld overlay.
3132010003 | Arkansas 1 | 04/18/2010 | 06/09/2010 | ML10160069 | <strong>Plant Startup from a Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2010, Arkansas Nuclear One-Unit 1 (ANO-1) was operating at approximately 11 percent Reactor power, nearing the completion of the twenty-second refueling outage, and preparing to connect the Main Generator to the Electrical Grid (Grid). The ANO-1 Operating Staff entered the Reactor Coolant Pump Abnormal Operating Procedure at 1346 Central Daylight Time (CDT) due to indications of a degraded third stage seal on a Reactor Coolant Pump (P-32C). The cause of the P-32C seal failure was later determined to be an inadequate tolerance between the pump coupling slinger ring and stand pipe splash shield. At 1356 CDT, an Operator stationed at the Main Turbine reported smoke and small flames at Main Turbine Governor Valve 3 (GV3). An electro-hydraulic control (EHC) fluid leak that had previously been repaired during the outage resulted in EHC fluid entrainment in the calcium silicate piping insulation at GV3, promoting an exothermic reaction between the EHC fluid and the insulation when exposed to operating temperatures. The Operating Staff manually tripped the Main Turbine and conservatively performed a manual Reactor scram at 1357 CDT. A local CO2 fire extinguisher was used to extinguish the small flames at GV3 immediately following detection by the Operator stationed at the valve. MODE 5 conditions were established, and after repairs to the Main Turbine insulation and P-32C seal replacement, ANO-1 was connected to the Grid at 1918 CDT on April 25, 2010.
3132010004 | Arkansas 1 | 04/25/2010 | 06/22/2010 | ML10175058 | <strong>Automatic Reactor Protection System Actuation that Resulted in a Reactor Trip due to Inadequate Procedure Use and Adherence and Workers Acting Independently</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2010, at approximately 2126 Central Daylight Time (CDT), with the plant operating at ~19.5% heat balance power following a refueling outage (1R22), a Reactor Protection System (RPS) actuation during Nuclear Instrument (NI) calibration resulted in a reactor trip at Arkansas Nuclear One, Unit 1. During performance of the NI calibration, a large neutron error signal developed resulting in a mismatch between selected power and indicated power which resulted in Group 7 control rods withdrawing for 38 seconds. The rod withdrawal initiated an RPS trip on 2 of the 4 channels, resulting in an automatic reactor trip. The failure to appropriately use and adhere to procedures was determined to be the major factor in this event. Procedure steps were not performed as written and not read verbatim to the operator as required by procedure guidance. As a result, immediate stand-downs with involved departments were conducted and additional control room oversight was established.
3152010001 | Cook 1 | 04/09/2010 | 06/18/2010 | ML10180026 | <strong>1lAB EDG Fuel Oil Transfer Pumps Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2010, at 2211 hours, during a scheduled surveillance of Unit 1 AB Emergency Diesel Generator (EDG), the breaker for AB EDG Fuel Oil Transfer Pump No. 1 tripped when the pump attempted to start. AB EDG Fuel Oil Transfer Pump No. 2 had been previously removed from service for maintenance. Unit 1 AB EDG had been declared inoperable on April 23, 2010, at 2047 hours to perform the surveillance, and remained inoperable due to no available fuel oil transfer pump. On April 8, 2010, the power cable for Unit 1 AB EDG Fuel Oil Transfer Pump No. 1 was mistakenly cut during maintenance that was intended to replace the cable for Fuel Oil Transfer Pump No. 2. Due to both Unit 1 AB EDG Fuel Oil Transfer Pumps being inoperable simultaneously, Unit 1 AB EDG was also inoperable. The time of unrecognized inoperability was from April 8 to April 23, 2010. During this time, several equipment configurations and plant manipulations were made that, in retrospect, were prohibited by Technical Specifications. Also, both EDGs (the required onsite emergency power sources) were simultaneously inoperable on two occasions. The cause of this event was inadequate verification techniques used to verify the correct power cable to cut. Corrective actions will include designing and implementing barriers to positively identify cables in the field before cutting or pulling. Unit 1 AB EDG was restored to operable status on April 29, 2010, at 1643 hours. The conditions prohibited by Technical Specifications are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(i)(B). Both EDGs (the onsite emergency power sources) being simultaneously unavailable to the plant is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(v)(D)
3152010002 | Cook 1 | 05/02/2010 | 06/23/2010 | ML10182029 | <strong>Manual Auxiliary Feedwater Actuation in Response to Main Feedpump Failure</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2010, at 0855 hours, following rising bearing temperatures on the Unit 1 East Main Feedwater Pump (MFP), Donald C. Cook Nuclear Plant Control Room Operators initiated the Rapid Power Reduction procedure in an effort to quickly lower power to remove the failing East MFP from service. Within 3 minutes of initiating the power reduction, Operators received Hi and Hi-Hi vibration alarms and reports of an oil leak on the East MFP. Operators then manually tripped the East MFP at approximately 98% power and entered the procedure for Loss of One Main Feed Pump, which directs manually starting Auxiliary Feedwater (AFW) pumps as required. Operators started both Motor Driven AFW Pumps and the Turbine Driven AFW Pump. Power was stabilized at approximately 48%. The cause of the East MFP bearing failure was a loss or reduction of lubrication oil supply to the bearing. An exact cause for the loss or reduction of lubrication oil supply could not be determined. Completed corrective actions involved disassembly, inspection, and repairs of the East MFP. Work included replacement of the failed bearing and bearing housing, replacement of the outboard hydraulic rubber-type hose with a corrugated metal hose, and a flush of the oil system for the pump. Manually starting the AFW Pumps in response to actual plant conditions resulting from equipment failure was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A), Event Notification 45893 was submitted on May 2, 2010. The event is also reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3152010003 | Cook 1 | 12/13/2010 | 02/09/2011 | ML11054028 | <strong>Manual Auxiliary Feedwater Actuation in Response to Manual Main Feedpump Trip</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2010, at 2117 hours, in response to decreasing condenser vacuum on the Unit 1 East Main Feedwater Pump (MFP), Donald C. Cook Nuclear Plant control room operators initiated the Rapid Power Reduction Procedure in an effort to quickly lower power to remove the East MFP from service. Within 2 minutes of initiating the power reduction, operators observed East MFP Condenser vacuum rapidly lowering toward the low vacuum trip setpoint. At 2119 hours, they entered the procedure for Loss of One Main Feed Pump, manually tripped the East MFP and manually started both Motor Driven Auxiliary Feedwater (AFW) Pumps and the Turbine Driven AFW Pump. Power was lowered and stabilized at approximately 48 percent. The cause of the East MFP vacuum lowering was fouling of the MFP Condenser cooling water side due to debris intrusion from rough lake conditions. Corrective actions were taken to open and clean the East and West MFP condensers. Manually starting the AFW Pumps in response to actual plant conditions resulting from equipment failure was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). Event Notification 46477 was submitted on December 14, 2010, at 0202 hours. This event is also reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3162010001 | Cook 2 | 10/06/2010 | 12/01/2010 | ML10351031 | <strong>Valid Actuation of Auxiliary Feedwater System in Response to Valid Steam Generator Low-Low Levels</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2010, at 0008 hours, a valid automatic actuation of the Unit 2 Turbine Driven Auxiliary Feedwater Pump (TDAFP) occurred as a result of two Steam Generator (S/G) levels reaching their low-low setpoint. Prior to the event, at 0001, the reactor was manually tripped, in accordance with the Power Reduction Procedure, to begin a scheduled refueling outage. Following the trip, operators completed their immediate actions and adjusted Auxiliary Feedwater (AFW) flow in accordance with procedure. While adjusting AFW flow, a cooldown of the Reactor Coolant System (RCS) was noted, however, the source was not immediately identified. The cooldown resulted in lowering S/G levels. Operators attempted to recover S/G levels but were not successful. The TDAFP started automatically as a result of two of four S/G levels reaching their low-low setpoint. Operators then began to restore normal S/G levels. The cause of the cooldown was two steam dump valves opening without a demand signal. The opening was due to an electro-pneumatic transducer (EPT) which was later found to be out of calibration. The EPT has been replaced. In accordance with 10 CFR 50.72(b)(3)(iv)(A), Event Notification 46311 was submitted on October 6, 2010, to report the automatic start of the TDAFP. This event is also reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3162010002 | Cook 2 | 10/15/2010 | 12/07/2010 | ML10350032 | <strong>Containment Divider Barrier Seal Mounting Bolts not Properly Installed</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2010, during performance of the surveillance of the Donald C. Cook Nuclear Plant Unit 2 containment divider barrier seal, personnel identified two divider barrier seal retaining bolts missing, one retaining bolt with a loose nut and one retaining bolt missing its nut. Investigation of the condition concluded that the nut has been missing for the duration of the recently completed operating cycle, the bolts have been presumed missing since replacement of the divider barrier seal in 1990 and the loose nut was not properly tightened following removal of a seal sample coupon during a previous outage. Although the evaluation of the condition concluded the safety function of the divider barrier would still be met, the condition described above constitutes a non-compliance with the Technical Specification (TS) surveillance requirement to ensure seal bolting is properly installed and therefore is reportable as a condition prohibited by TSs. The cause of this event has been determined to be a lack of clear and detailed guidance in the containment divider barrier seal surveillance procedure. Completed corrective actions include replacing the missing bolts, tightening the loose nut and replacing the missing nut. Planned corrective actions include changing the containment divider barrier seal surveillance procedure to improve clarity and provide detailed instruction. The failure to comply with TS 3.6.13 is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Specifications.
3162010003 | Cook 2 | 11/30/2010 | 01/28/2011 | ML11039052 | <strong>Changed Modes from Mode 5 to Mode 4 with Divider Barrier Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2010, at 1749 hours, Donald C. Cook Nuclear Plant Unit 2 Operators determined that the containment divider barrier was inoperable. This occurred approximately 5 hours after Unit 2 ascended from Mode 5 to Mode 4 at 1255 hours. A modification of the containment divider barrier seal had been completed prior to entering Mode 4, but the seal was not recognized as having been reassembled incorrectly at that time. As a result, the entry into Mode 4 was made with the Technical Specification (TS) required containment divider barrier inoperable, and without meeting Limiting Condition for Operation (LCO) 3.0.4 conditions to do so. During a walkdown of the divider barrier seal modification following ascension to Mode 4, the configuration of a portion of the divider barrier seal directly adjacent to the modification was questioned. This walkdown identified one missing nut and one nut with improper thread engagement. The divider barrier was determined to be inoperable because it did not meet TS 3.6.13 Surveillance Requirement 3.6.13.5, which specifies that the "Seal and seal mounting bolts are properly installed..." The cause was personnel exceeding written work scope by disassembling and not properly restoring a portion of the divider barrier seal adjacent to the area being modified. Corrective actions included correcting the seal plate assembly, adding a new nut and tightening the nut that had inadequate thread engagement. The surveillance was performed on the affected seal areas. The divider barrier was declared operable on November 30, 2010, at 2302 hours. Ascension to Mode 4 with the Containment Divider Barrier inoperable without meeting LCO 3.0.4 conditions to do so is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), Operation or Condition Prohibited by Technical Spedifications.
3172010001 | Calvert Cliffs 1 | 02/18/2010 | 05/27/2010 | ML10153046 | <strong>Reactor Trip due to Water Intrusion into Switchgear Protective Circuitry</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2010, at 8:24 a.m., Unit 1 experienced an automatic reactor trip from 92.8 percent power. The 12B Reactor Coolant Pump (RCP) tripped and the Reactor Protective System actuated on Reactor Coolant System low flow. The 12B RCP tripped due to a phase to ground short near one of the current transformers for the 12B RCP bus 14P differential/ground current protection. The ground fault was not isolated close to the source due to a failed ground protection relay in breaker 252-2202 the feeder breaker from Service Transformer P-13000-2 to the Unit 1 RCP buses. This resulted in Service Transformer P-13000-2 being deenergized. The loss of P-13000-2 resulted in a loss of the normal power supply to 14 4 kV bus. This caused the 1B Emergency Diesel Generator to start and supply power to 14 4 kV bus. The cause of the fault was a phase to ground short near one of the current transformers for the 12B RCP bus differential/ground current protection due to water intrusion. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation and automatic start of the 1B Emergency Diesel Generator. Corrective actions include revision to a relay test procedure and improved management of roof issues.
3172010002 | Calvert Cliffs 1 | 03/08/2010 | 05/07/2010 | ML10131020 | <strong>Pressurizer Safety Valves As-Found Settings Outside Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>During scheduled testing at the offsite testing facility, the as-found lift settings for the pressurizer safety valves (PSVs) previously installed at 1 RV200 and 1 RV201 locations were measured outside the Technical Specification allowable values (On March 8, 2010, 1RV200 lifted low and on March 9, 2010, 1RV201 lifted high). The valves had been installed during the 2008 Unit 1 refueling outage and were removed during the 2010 Unit 1 refueling outage for scheduled testing and maintenance. Spare valves were installed during the 2010 refueling outage. The failed valves were tested at the offsite facility. After resetting the compression screw, both valves were as-left certified satisfactorily. The post-test leak check was performed satisfactorily for 1 RV200, but it was not satisfactory for 1 RV201 (most likely due to main disc seat damage). The apparent cause of the as-found lift failures is normal setpoint variation. The valves will be refurbished later in 2010 to verify the cause. The testing records and maintenance history for the PSVs currently installed in the plant were reviewed. Based on that review, a reasonable expectation for continued operability was satisfied for those PSVs. A similar event is documented in Licensee Event Report 317/2008-002-01. The cause for that event was excessive drift which resulted from degradation in internal components.
3172010003 | Calvert Cliffs 1 | 05/12/2010 | 07/08/2010 | ML10193002 | <strong>Reactor Trip due to Loose Connection in Switchyard Breaker Panel Board</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2010 at 13:51, Unit 1 experienced an automatic reactor trip from 100 percent power, when the Reactor Protective System actuated on high pressurizer pressure due to a complete load rejection. At the time of the event, maintenance was being performed in the switchyard requiring two 500 kV breakers to be open with a third 500 kV breaker (552-22) closed, thus allowing Unit 1 main turbine generator output to the grid. However, due to a loose connection in the 125 VDC distribution panel board for the breaker disconnect switches, breaker 552-22 tripped open upon receiving a trip signal from its trip circuitry, resulting in the complete load rejection condition. The root cause of the event was a loose electrical connection in the 125 VDC distribution panel board. After the trip, one of the pressurizer safety valves leaked. The Unit was taken to Mode 5 to repair the leaking pressurizer safety valve. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to a valid actuation of the Reactor Protective System. Corrective actions include checking the electrical connections in the 125 VDC distribution panel for tightness, increasing the time delay to the re-trip feature of the subject type relays, replacing the disconnect bucket and revising the risk management procedure.
3182010001 | Calvert Cliffs 2 | 02/18/2010 | 05/27/2010 | ML10153045 | <strong>Reactor Trip due to Failure of Protective Relay Circuitry</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2010, at 8:24 a.m., Unit 2 experienced an automatic reactor trip from 99.5 percent power. The Unit 2 Reactor Coolant Pumps (RCPs) lost power and the Reactor Protective System actuated on Reactor Coolant System low flow. The RCPs lost power due to a loss of Service Transformer P-13000-2 and the 500 kV Switchyard Red Bus being deenergized, deenergizing the 22 13 kV RCP Bus. The loss of P-13000-2 resulted in a loss of the normal power supply to 24 4 kV bus. This caused the 2B Emergency Diesel Generator (EDG) to start. Shortly after receiving a start signal, the 2B EDG tripped due to a low lube oil pressure trip. The event was initiated when the Unit 1 12B RCP tripped due to an electrical fault in relay protective circuitry. The ground fault was not isolated close to the source due to a failed ground protection relay in breaker 252-2202, the feeder breaker from Service Transformer P-13000-2 to the Unit 1 RCP buses. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation and automatic start of the 2B EDG, 10 CFR 50.73(a)(2)(i)(B) due to the inoperable condition of the 2B EDG and 10 CFR 50.73(a)(2)(v)(D) for those periods when two EDGs were out-of-service.
3182010002 | Calvert Cliffs 2 | 02/23/2010 | 04/22/2010 | ML10116003 | <strong>Reactor Coolant System Pressure Boundary Leakage in Valve Leakoff Line Weld</strong><br /><i>Abstract:&nbsp;</i>On February 23, 2010, while Unit 2 was in Mode 5 during a forced outage, it was verified that the pinhole previously identified at the socket weld attaching the packing leakoff line to the bonnet of valve 2HVRC-220 (pressurizer spray bypass valve) constituted a Reactor Coolant System pressure boundary leak. The Technical Specifications limit Reactor Coolant System pressure boundary leakage to zero. Based on visual inspection performed during the post-trip boric acid walkdown the leak most likely existed during plant operation. A progressive non-destructive examination of the pinhole leak site was performed to further characterize the flaw in the socket weld as it was ground out for repair. That non-destructive examination concluded that the flaw was a single pore through the socket weld that caused-the leak. Based on a review of the maintenance history and discussions with Calvert Cliffs' staff, the apparent cause of the pinhole was a latent weld defect created during the original valve manufacturing process. The weld was repaired and inspected satisfactorily prior to startup from the Unit 2 forced outage.
3212010001 | Hatch 1 | 03/08/2010 | 04/16/2010 | ML10109006 | <strong>Corrosion Induced Bonding Results in Safety Relief Valve Lift Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>On March 11, at approximately 1300 EST, Unit 1 was at 0 CMWTh, which is 0.00 percent of rated thermal power (RTP). On that day it was concluded that at the completion of bench testing five Safety Relief Valves (SRVs) experienced setpoint drift that exceeded the allowable plant Technical Specifications (TS) limit. The root cause of the SRV setpoint drift is corrosion-induced bonding between the pilot disc and seating surface. Immediate corrective actions for this event included replacement of all eleven SRV pilot valves with refurbished pilot valves which have pilot discs made from Stellite 21 material. Also improvements in the insulation surrounding each SRV were made to reduce the likelihood of corrosion-induced bonding between the pilot disc and seating surface.
3212010002 | Hatch 1, Hatch 2 | 04/13/2010 | 06/11/2010 | ML10165008 | <strong>Degraded Plant Service Water Cooling to Main Control Room Air Conditioner Results in Loss of Function</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2010 Unit 1 was at 2800 CMWTh, 99.9 percent power and Unit 2 was in Mode 5, Refuel mode. On this date it was determined that the plant had previously operated in a condition prohibited by the Plant Technical Specification. The cooling water flow for the Main Control Room Air Conditioning was degraded due to internal fouling. Due to the degraded cooling flow, the operability of the Main Control Room Air Conditioning would be adversely impacted during a postulated design basis accident. Evaluation with conservatism removed showed that the function of the Main Control Room Air Conditioning was maintained during a postulated design basis accident. This event was caused by fouling of the cooling water pipe over a period of time. Corrective actions include, cleaning of associated piping. Some portions have already been cleaned and additional piping sections are planned to be cleaned. Radiography points will be evaluated based on flow modeling to provide early detection of internal pipe fouling. Sampling of the PSW supply to MCREC chillers through Unit 2 to confirm adequate chlorine is present will be performed.
3212010003 | Hatch 1, Hatch 2 | 05/11/2010 | 07/09/2010 | ML10193001 | <strong>Main Control Room Environmental Control System Boundary not Single Failure Proof due to Degraded Barrier</strong><br /><i>Abstract:&nbsp;</i>On May 11, 2010 Unit 1 was at 2800 CMWTh, 99.9 percent power, and Unit 2 was also at 2800 CMWTh, 99.9 percent power. On this date, it was determined that when procedure 42SV-Z41-003-0 was performed as required by the Technical Specification (TS) Surveillance Requirement 3.7.4.4 to test the operability of the Main Control Room Environmental Control system (MCREC, EIIS Code VI) boundary, the required pressurization of the Main Control Room could not be reached. As part of the test, a damper (1Z41F019) was failed open to simulate the condition of the boundary given a single failure of the damper. The results of the test showed that with this damper failed open, the TS required pressurization of >/= 0.1 inches water column of the Main Control Room (MCR, EIIS Code NA) could not be reached. Instead, the MCR could only be pressurized to 0.06 inches water column. Upon identification, the operating crew entered the appropriate required action statement. This event was caused by the apparent degradation of the MCR boundary. Both restroom exhaust dampers were secured in their "closed" position, and the subsequent control room boundary surveillance test was satisfactorily performed with a pressurization of 0.11 inches water column. Interim corrective actions include maintaining the related dampers in the closed position until actions to resolve the condition have been taken and performance of a cause analysis with corrective actions taken as required by the cause analysis.
3212010004 | Hatch 1 | 06/03/2010 | 07/30/2010 | ML10214016 | <strong>Emergency Diesel Generator 1A Excess Fuel Oil Return Tubing Failure</strong><br /><i>Abstract:&nbsp;</i>During operation of Emergency Diesel Generator (EDG) 1A for monthly surveillance, at 1443 EDT on June 03, 2010 with the Unit operating at full power, a section of one-quarter-inch tubing in the fuel oil system became disconnected from its fitting rendering EDG1A inoperable due to the potential for fire. Applicable requirements of the Technical Specifications were accomplished and plant operations continued. The tubing's function is to route waste fuel oil from the injectors to the fuel oil collection tank. The tubing separation occurred at the fitting to a discharge check valve which prevents backflow of waste oil to the injectors. This tubing failure occurred subsequent to an observed small amount of leakage at the same location on April 01, 2010. An attempt at that time to stop that leakage by tightening the fitting was unsuccessful. Subsequent to the attempt to stop the leakage, the potential impact on EDG operation was evaluated and judged to be acceptable for EDG operation pending future repair. The apparent cause of both the leakage and subsequent tubing separation was degradation of the tubing connection due to wear and stresses resulting from the repetitive disassembly and re-assembly during scheduled maintenance activities. Subsequent to both the noted leakage and the tubing separation, the corresponding tubing for the other four EDGs was examined for signs of leakage or cracking. None was found and those EDGs were determined to be operable.
3232010001 | Diablo Canyon 2 | 07/21/2008 | 03/17/2010 | ML10088011 | <strong>2008 Diablo Canyon Unit 2 Loss of Auxiliary Building Ventilation System Exhaust Fans</strong><br /><i>Abstract:&nbsp;</i>On July 21, 2008, 05:04 PDT, Diablo Canyon Power Plant (DCPP) Unit 2 entered Technical Specification (TS) 3.0.3 when operators secured auxiliary building exhaust fan E-1 with auxiliary building exhaust fan E-2 cleared for maintenance. The securing of auxiliary building exhaust fan E-1 resulted in a loss of all DCPP Unit.2 auxiliary building ventilation system exhaust. On July 21, 2008, 0534 PDT, DCPP Unit 2, TS 3.0.3 was exited when auxiliary building exhaust fan E-1 was restarted. On January 28, 2010, PG&E conducted a review of past events for safety system functional failures. Past events included entries into TS 3.0.3. This review was conducted utilizing recently published U.S. NRC training material on this subject. This review concluded that the simultaneous inoperability of the DCPP Unit 2 auxiliary building exhaust fans constituted a safety system functional failure and as such was reportable under 10 CFR 50.73(a)(2)(v).
3232010002 | Diablo Canyon 2 | 06/14/2010 | 08/05/2010 | ML10223002 | <strong>DCPP Unit 2 SI Test Line Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On May 14, 2010, a design deficiency was discovered during the final preparation of the Diablo Canyon Power Plant (DCPP) Unit 1 design change package (DCP) for the safety injection (SI) test line optimization modification. The DCP lacked the required flow restrictors for the reactor coolant pressure boundary isolation valves, resulting in the potential to create loss of reactor coolant system (RCS) inventory which would exceed normal charging system makeup capability. On June 14, 2010, it was determined that this design deficiency impacted the DCPP Unit 2 SI test line optimization modification package, implemented during the most recent refueling outage on Unit 2 (2R15). The Unit 2 design deficiency was only an issue during RCS check valve testing in Mode 4 operation during 2R15. The SI piping system and its associated components are fully qualified to perform their design basis functions when the test line isolation valves are in their normally-closed position above Mode 4. During the testing the valves were opened on each loop creating an unanalyzed condition which is reportable under 10 CFR 50.73(a)(2)(ii)(B).
3252010001 | Brunswick 1 | 02/27/2010 | 04/27/2010 | ML10125030 | <strong>Reactor Core Isolation Cooling (RCIC) Manually Started to Maintain RPV Level Following Pre-planned Scram</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2010, at approximately 0116 hours Eastern Standard Time (EST), Control Room Operators manually inserted a Reactor Protection System (RPS) trip to shutdown the reactor from approximately 21 percent of rated thermal power to begin a planned refuel outage. The 1B Reactor Feedwater Pump (RFP) had been removed from service at approximately 61% rated thermal power and isolated to support scheduled maintenance activities. Following the insertion of the RPS trip, the 1A RFP was shutdown due to high RFP turbine casing drain level. At 0158 hours, Unit 1 Control Room Operators manually started the Reactor Core Isolation Cooling (RCIC) system to maintain reactor pressure vessel (RPV) coolant level following the pre-planned reactor scram. The RCIC system maintained RPV coolant level until the 1B RFP could be returned to service. The RCIC system was shutdown at 0306 hours. All systems functioned as designed. The safety consequences of this event were minimal. The RPV level remained in the normal band while RCIC was being used for level control during the transient. All Emergency Core Cooling Systems (ECCS) were operable and available to provide adequate core cooling if needed. The root cause of this event was that Operators made the redundant RFP unavailable while still above the reactor pressure at which a RFP is required to feed the RPV. The corrective actions to prevent recurrence for this event are to revise operating procedures cautioning that a Reactor Feedwater Pump should not be made unavailable before reactor pressure is less than 350 psig.
3252010002 | Brunswick 1 | 04/25/2010 | 06/23/2010 | ML10180015 | <strong>Operation Prohibited by Technical Specifications - Reactor Protection System (RPS) Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On April 25, 2010, at 2100 hours Eastern Daylight Time (EDT), with the unit in Mode 2 at 900 psig, pressure transmitter 1-B21-PT-N023B was declared inoperable due to reading downscale. This transmitter is part of the instrumentation required for operability of Function 3, "Reactor Vessel Steam Dome Pressure - High," of Technical Specification 3.3.1.1, "Reactor Protection System (RPS) Instrumentation." Table 3.3.1.1-1, "Reactor Protection System Instrumentation," which requires two operable channels when in Modes 1 and 2. It was determined that the inoperability of pressure transmitter 1-B21-PT-N023B was due to valve 1-B21-IV-1384, "B21-PT-N023B Instrument Isolation Valve," being in the closed position. Unit 1 had previously entered Mode 2 at 0313 hours on April 24, 2010, during startup from the Unit 1, Cycle 18 refueling outage. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's Technical Specifications. The select cause of this event was the failure to effectively use the concurrent verification during the performance of procedure 0MST-EFCV18R, "EFCV Rx Inst Pen Sys Isol Vlv Func Test X53, X82, X49B-A." As a result, valve 1-B21-IV-1384 was left in the closed versus open position. The corrective actions to prevent recurrence will enhance concurrent verification practices through establishing new expectations for Maintenance personnel and procedure improvements.
3252010003 | Brunswick 1 | 05/05/2010 | 07/02/2010 | ML10201029 | <strong>Automatic Reactor Scram due to 1B Reactor Feed Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2010, at approximately 11:44 hours Eastern Daylight Time (EDT), an automatic reactor scram occurred on Unit 1 following a trip of the 1B Reactor Feed Pump (RFP). The Reactor Recirculation pumps did not run back as expected following the 1B RFP trip. The resulting water level shrink caused level in the Reactor Pressure Vessel (RPV) to drop to Low Level 1, causing the activation of the Reactor Protection System (RPS) and the Primary Containment Isolation System (PCIS). All control rods properly inserted. PCIS Group 2, Group 6, and Group 8 isolation signals were received on Low Level 1. Actuations of the Primary Containment Isolation Valves (PCIVs) were completed and the affected equipment responded as designed. Water level in the RPV momentarily reached Low Level 2, which initiated the High Pressure Coolant Injection (HPCI) System, the Reactor Core Isolation Cooling (RCIC) System, and a partial Group 3 (i.e., Reactor Water Cleanup (RWCU)) PCIS isolation. The HPCI and RCIC systems did not inject to the RPV. The RWCU inboard isolation valve isolated and, in accordance with plant design, 1-G31-F004 (i.e., RWCU outboard isolation) did not automatically isolate. Unit 2 was not affected by this event. The safety consequences of this event were minimal. All Emergency Core Cooling Systems (ECCS) were operable and available to provide adequate core cooling if needed. The investigation concluded that the adverse condition was a historical problem and no root cause could reasonably be determined.
3252010004 | Brunswick 1, Brunswick 2 | 09/13/2010 | 11/11/2010 | ML10327006 | <strong>Emergency Diesel Generator Inoperable for Greater than Technical Specification Completion Time</strong><br /><i>Abstract:&nbsp;</i>On September 12, 2010, at approximately 2100 hours Eastern Daylight Time (EDT), a routine monthly surveillance, 0PT-12.2D, "No. 4 Diesel Generator Monthly Load Test," was started on Emergency Diesel Generator No. 4 (EDG4). During the performance of the surveillance test, sparking was observed coming from the diesel generator inner ring brushes. The maximum sparking began approximately 45 minutes after EDG4 started, and remained for the duration of the diesel run. Following performance of the surveillance test, collector ring brush measurements identified abnormal wear on the inner ring brushes. Engineering determined that, due to the brush wear and excessive sparking, EDG4 would not have been able to run for its mission time. At 0430 hours on September 13, 2010, EDG4 was declared inoperable. This condition is being reported as an operation prohibited by Technical Specifications (TS), due to EDG4 inoperable greater than the TS completion time. The safety consequences of this event were minimal. The three remaining Emergency Diesel Generators were operable and available to provide emergency AC power if needed. The root cause was determined to be untimely implementation of corrective actions to a long-standing concern. The corrective actions include replacing the collector rings with an upgraded design that is not subject to corrosion.
3272010001 | Sequoyah 1, Sequoyah 2 | 04/05/2010 | 06/04/2010 | ML10160018 | <strong>Inoperability of Shutdown Board Because of Spent Fuel Pool Back-Up Pump Breaker Inoperability</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2010 at 1145 Eastern Daylight Time (EDT), Electrical Maintenance notified Operations that the spent fuel pool (SFP) back-up pump common spare (C-S) breaker had been installed, following repairs, without the required arc chutes and phase barriers. As a result, the breaker for the SFP back-up pump was declared inoperable and the associated Shutdown Board 2A1-A was considered inoperable. Main control room operators entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.2.1, Action a, due to the inoperability of the 480-volt Shutdown Board 2A1-A. After successfully disconnecting and racking out the SFP back-up pump C-S breaker, TS LCO 3.8.2.1, Action a, was exited. The direct cause was Electrical Maintenance personnel failed to install the SFP back-up pump C-S breaker arc chutes and phase barriers. The Electrical Maintenance technician failed to stop upon identifying inadequacies in the work order. Corrective actions included applying appropriate disciplinary actions. The root cause of the event was determined to be that a less than adequate process exists for conducting technical reviews. The steps required to return the breaker to an operable state were omitted from the work order and were not noted during the technical review of the work order. Corrective actions include revising the applicable Maintenance and Modifications Department Procedure to clarify the requirements for an independent qualified review and technical review of work orders.
3272010002 | Sequoyah 1 | 11/16/2010 | 01/18/2011 | ML11021011 | <strong>Manual Reactor Trip as a Result of a Failure of Feedwater Control to Maintain Steam Generator Levels</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2010, at 2210 Eastern Standard Time, SQN Unit 1 was manually tripped based on decreasing steam generator (SG) level in Loop 4. Prior to the reactor trip, reactor power was at 26 percent and ascending following completion of a scheduled refueling outage. A manual turbine trip was initiated, because a moisture separator reheater safety relief valve lifted and would not reseat. Following the manual turbine trip, the Loop 4 SG feedwater level controller was unable to control the feedwater level because of an inoperable main steam dump valve controller. Manual actions were taken by Operations personnel, but level could not be recovered and the reactor was tripped. The root cause was determined to be a failure to identify and perform adequate installation testing on the main steam dump valve controller. During the refueling outage that ended on 11/15/2010, a digital feedwater design change was implemented requiring relocation of the main steam dump valve controller. Relocating the controller required the power cord to be unplugged, the controller moved, and the power cord to be reinstalled. There was no installation testing identified for this controller in the design change notice or the associated work order. When the power cord was reinstalled, it was not properly latched. This resulted in the controller becoming unplugged. An immediate corrective action required components that were moved during the modification to be inspected. Corrective actions include revising the modification installation and installation testing procedures to add additional verifications and reviews.
3272010003 | Sequoyah 1 | 12/20/2010 | 02/17/2011 | ML11055015 | <strong>Manual Reactor Trip as a Result of a Fire in the Main Generator Neutral Bushing Bus Duct Housing</strong><br /><i>Abstract:&nbsp;</i>On December 20, 2010, at 0050 Eastern Standard Time, SQN, Unit 1 reactor was manually tripped as a result of a fire associated with the main generator. Site personnel reported smoke in and around the main generator of the turbine building. Operations personnel witnessed a fire in the neutral bus duct housing of the main generator and initiated an emergency alarm. Operation personnel entered into the abnormal operating procedure for plant fires. The fire brigade and the Incident Commander responded to the fire alarm and validated a fire present inside a vent/inspection opening of the neutral bus duct housing. After validation of the fire, operations personnel manually tripped the reactor and turbine to support the fire brigade actions to arrest the fire. The fire brigade extinguished the fire. The safety systems performed as designed for the reactor trip. The unit was stabilized in Mode 3. The cause of the fire on the main generator bushing was identified as a cyclic vibration induced failure of the neutral bushing porcelain, which allowed a hydrogen leak that ignited. The failed neutral bushing was replaced. Corrective actions include developing a preventive maintenance instruction to define a service life for refurbishment/replacement of SQN, Unit 1 and Unit 2 main and neutral bushings. Another action involves the visual inspection of the SQN, Unit 2 bushings during the next scheduled refueling outage.
3312010001 | Duane Arnold | 01/01/2010 | 03/02/2010 | ML10063042 | <strong>Emergency Diesel Generator Start due to Failed Arrester in Switchyard</strong><br /><i>Abstract:&nbsp;</i>On January 1, 2010, while operating at 100% power, the 'A' Emergency Diesel Generator (EDG) automatically started from a valid undervoltage condition, but did not load onto its respective 4160 VAC bus. The momentary undervoltage condition was caused by a momentary fault on the 161 kilovolt (kV) Vinton Line. The momentary fault was caused by a failed lightning arrestor on the 161 kV line in the Duane Arnold Energy Center (DAEC) switchyard. The 'A' EDG supply breaker was not required to close onto its respective bus as it remained powered from its normal power supply during and after the undervoltage event. Offsite power remained fully operable during and following the event. As designed, the 'A' Emergency Service Water (ESW) system automatically started. Additionally, in response to the momentary undervoltage condition, the 'B' Well Water Pump, the RWCU System, and the Spent Fuel Pooling Cooling System tripped. The cause of this event is a lack of coordination of the EDG automatic start logic and the DAEC switchyard protective relaying. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312010002 | Duane Arnold | 01/04/2010 | 09/22/2010 | ML10267005 | <strong>Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 4, 2010, a condition prohibited by Technical Specifications (TS) existed. Specifically, a TS violation occurred when it was not recognized that TS Limiting Condition for Operation (LCO) 3.3.1.1, Reactor Protection System (RPS) and 3.3.4.1, End Of Cycle - Recirculation Pump Trip (EOC-RPT) were not met when the Turbine Bypass Valves (TBVs) were in the open position (TS LCO 3.7.7). The LCO conditions existed for approximately 6.5 hours. LCO 3.3.1.1 requires RPS trip capability to be restored within 1 hour and LCO 3.3.4.1 requires a Minimum Critical Power Ratio (MCPR) penalty be inserted within 2 hours. If these actions are not completed, then both TS 3.3.1.1 and 3.3.4.1 require the plant to be less than 26% Rated Thermal Power (RTP) within 4 hours thereafter. Because reactor power was not reduced to less than 26% RTP within the 5 hours (total) required by LCO 3.3.1.1, a condition prohibited by TS existed for approximately 1.5 hours. A condition prohibited by TS 3.3.4.1 also existed for approximately 0.5 hours. This event also constituted an event or condition that could have prevented fulfillment of a safety function. The date of discovery for this event is January 11, 2010. The cause of this event was determined to be that the plant staff did not have a full/complete understanding of the relationship between TBVs being open and the direct impact on the Turbine First Stage Pressure (TSFP) trip/enable setpoint in determining TS compliance/Operability. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312010003 | Duane Arnold | 04/26/2010 | 06/25/2010 | ML10179006 | <strong>Unplanned Manual Reactor Scram due to Increasing Turbine Vibrations</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2010, at 0300, while in day 1 of a 31 day Limiting Condition for Operation (LCO) for inoperable Primary Containment Isolation Valves (Traversing Incore Probe Drive Ball Valves), during the process of shutting down the plant for a planned outage to investigate an increase in Drywell leakage, a manual scram was inserted. The manual scram was inserted due to elevated vibration readings on Main Turbine Bearing number 6. The reactor scram and associated turbine trip was initiated at approximately 14% power in anticipation of reaching Main Turbine vibration limit. The cause of the increase in bearing vibration was determined to be from a turbine rub. Turbine rubs can be induced in operating configurations of high turbine gland seal pressure with low main condenser back pressure. This configuration existed during the April 26, 2010 shutdown. The catalyst for inducing the rub was an excessive Low Pressure Turbine cool down rate which allowed one of the two Low Pressure Turbine casings to cool more than the other. This difference in casing temperatures created the formation of a rub which resulted in localized heating of the turbine shaft and resulting increase in vibration readings. There were no Systems, Structures, or Components inoperable at the time of the scram that contributed to the event. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312010004 | Duane Arnold | 10/29/2010 | 03/31/2011 | ML11090065 | <strong>Linear Indication Found During Examination of Safe-End to Nozzle Welds</strong><br /><i>Abstract:&nbsp;</i>Safe-end to nozzle weld RRA-F002A was scheduled in Refuel Outage (RFO) 22 as an examination under BWRVIP-75 and as a successive examination under ASME Section XI. On October 29, 2010, UT examination of the N2A reactor recirculation riser safe-end to nozzle weld, RRA-F002A, identified a circumferential flaw. The RRA-F002A circumferential weld indication was approximately 6.5" and 71% through-wall (TW), and identified as Inner Diameter (ID) surface connected. As part of the BWRVIP and ASME Section XI Inspection Programs, the inspection population was expanded to determine the extent of condition. There were three additional welds that required examination in accordance with guidance BWRVIP-75. The welds were RRG-F002A, RRF-F002A, and RRH-F002A. The UT examinations for all three welds were completed with no indications of flaws noted. RRA-F002A was subsequently overlaid following verbal approval on November 15, 2010 of the relief request dated November 10, 2010 (ML 103160155). The root cause identified was that the 1978 Safe-end replacements consisted of alloy 82/182 welding filler metal that is susceptible to IGSCC. There were no Systems, Structures, or Components inoperable at the time of the event that contributed to the event.
3312010005 | Duane Arnold | 11/10/2010 | 01/07/2011 | ML11007076 | <strong>Momentary Loss of Shutdown Cooling During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>On November 10, 2010, at approximately 0518 hours, with the plant shutdown and in Mode 5 during Refueling Outage (RFO) 22, the 'A' Residual Heat Removal (RHR) pump tripped while operating in the shutdown cooling mode resulting in an interruption of the primary means of decay heat removal for approximately 30 minutes. During this period, the maximum increase in reactor temperature was approximately 2 degrees Fahrenheit with a calculated time to boil of approximately 33.9 hours. There was no loss of decay heat removal capability due to the fact that both trains of Fuel Pool Cooling and the Reactor Water Cleanup systems remained in service. The cause of this event was due to an inadequate procedure revision process that introduced a latent procedure deficiency associated with isolating motive power to the RHR Shutdown Cooling isolation valves when removing the Reactor Protections System (RPS) from service. This event is being reported as an event or condition that at the time of discovery could have prevented fulfillment of a safety function of structures or systems that are needed to remove residual heat under 10 CFR 50.73 (a)(2)(v)(B). There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312010006 | Duane Arnold | 11/10/2010 | 01/07/2011 | ML11007076 | <strong>Standby Liquid Control Test Tank Seismic Analysis</strong><br /><i>Abstract:&nbsp;</i>As part of an Operating Experience review (Event Notification 46372), the seismic analysis for the Standby Liquid Control (SBLC) System test tank was questioned. On November 10, 2010, engineering analysis concluded that when the test tank was 3/4 full of water, as directed by SBLC surveillance test procedures (STPs), it would not withstand Design Basis Earthquake (DBE) seismic loads and would possibly have caused a failure of safety-related, seismically qualified SBLC equipment. Therefore it has been concluded that the SBLC system was not operable in the past when the test tank was 3/4 full of water. The SBLC test tank was drained of water on November 11, 2010. Corrective actions taken included revising applicable procedures to require that the SBLC test tank be drained when the SBLC system is required to be operable. The cause of this event was a latent design issue that occurred during construction. This event is being reported as an event or condition that at the time of discovery could have prevented fulfillment of a safety function under 10 CFR 50.73 (a)(2)(v)(A)/(D), a condition prohibited by Technical Specifications (TS) under 10 CFR 50.73 (a)(2)(i)(B), and a common-cause inoperability of independent trains or channels under 10 CFR 50.73 (a)(2)(vii). There were no actual safety consequences and no effect on public health and safety as a result of this event.
3332010001 | FitzPatrick | 03/22/2010 | 05/20/2010 | ML10141015 | <strong>Residual Heat Removal and Core Spray Safety Valves Fail to Meet IST Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>Safety valves in the Residual Heat Removal and Core Spray systems at the James A. FitzPatrick (JAF) Nuclear Power Plant failed to meet In-Service Testing (IST) as-found acceptance criteria during surveillance testing conducted in February and March 2010. The most probable cause of the setpoint failure was the presence of internal binding and/or disc to seat corrosion bonding. Component testing that falls outside the required action range for IST requires that the component be declared inoperable and the applicable Limiting Condition for Operation declared not met. 10 CFR 50.73(a)(2)(i)(B) allows licensees to consider the failure to have occurred at time of discovery unless there is firm evidence to indicate that the condition existed previously. Based on a review of test history, there is indication that this condition existed prior to discovery. The event is reportable per 10 CFR 50.73(a)(2)(i)(B), “Any operation or condition which was prohibited by the plant’s Technical Specifications...” because during the time period described, the Residual Heat Removal and core spray subsystems were inoperable longer than allowed by TS. This event is also reportable per 10 CFR 50.73(a)(2)(vii), “Any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains to become inoperable in a single system”.
3332010004 | FitzPatrick | 09/17/2010 | 11/16/2010 | ML10320039 | <strong>Main Steam Isolation Valve Leak Rate Exceeds Authorized Limit</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2010, following Local Leak Rate Testing (LLRT) of valves 29AOV-80C (Inboard) and 29AOV-86C (Outboard) Main Steam Isolation Valves (MSIVs), it was determined that the allowable leak rate was exceeded for 29AOV-86C. Due to the initial test being performed between the valves (reverse flow for 29AOV-80C), follow-up testing from above the valve plug was conducted on September 21, 2010, at which time 29AOV-80C was also determined to have failed the leak rate test. At the time of testing, the Mode Switch was in Refuel and the plant was conducting Refueling Outage 19. The excessive leakage on 29AOV-80C, was attributed to corrosion products found on the valve seat during inspection of the valve internals. Leakage on 29AOV-86C was attributed to flow erosion in the stellite seat between the 3 o'clock and 5 o'clock position, causing the disc to be off center and slightly off the seat. The valves were repaired and tested satisfactorily prior to plant startup, and an Apparent Cause Evaluation was completed.
3332010005 | FitzPatrick | 10/23/2010 | 11/15/2011 | ML11320042 | <strong>High Pressure Coolant Injection System Declared Inoperable due to Power Supply Degradation</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2010, at 0023, with the plant operating in Mode 1, at 100%, operators noticed an acrid odor coming from the High Pressure Coolant Injection (HPCI) Instrument Power Inverter (23INV-79) in the control room. Closer inspection revealed discoloration on the outside of the casing for 23INV-79. The HPCI system was immediately declared Inoperable and Technical Specification Limiting Condition for Operating 3.5.1, Condition C was entered. An Apparent Cause Evaluation determined that the most probable cause of the HPCI Inverter degradation was age related degradation of an internal transformer. The immediate corrective action was to replace the failed inverter with a new model. The HPCI system was restored to Operable status at 2054, on October 23, 2010. Future corrective actions include replacing similar inverters in other systems. This event is reportable pursuant to 10 CFR 50.73(a)(2)(v)(B), “Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat.” It was discovered, after this event, that the Reactor Core Isolation Cooling (RCIC) System was also Inoperable for the period October 16, 2010 to January 8, 2011; therefore, this event is being reported under 10 CFR 50.73(a)(2)(i)(B), “Any operation or condition which was prohibited by the plant's Technical Specifications.”
3342010001 | Beaver Valley 1 | 08/26/2010 | 10/21/2010 | ML10300004 | <strong>Void in Emergency Core Cooling System Pump Suction Header Results in Entry into Technical Specification LCO 3.0.3</strong><br /><i>Abstract:&nbsp;</i>The "A" High-Head Safety Injection (HHSI) Pump was being returned to service on 08/26/2010 following scheduled maintenance with Beaver Valley Power Station (BVPS) Unit No. 1 at 100 percent power. [One HHSI pump is also used for normal charging during power operation.] Ultrasonic tests (UT) were performed on the in-service Unit 1 charging pump common suction piping headers following a fill of the drained HHSI (charging) pump/piping. The UT identified an air void existed within the 8 inch suction header that was determined to exceed the void size acceptance criteria. Both trains of HHSI were declared inoperable, and Technical Specification LCO 3.0.3 was entered. Following additional venting and a subsequent verification that both suction piping were full of water, both trains of HHSI were declared operable, and Technical Specification LCO 3.0.3 was exited. The cause of this event is the charging pump suction piping layout at BVPS Unit 1 is conducive to allowing a void to migrate to the charging pump common suction header during a fill and vent procedure. Currently the only available high point vent is not sufficient because the vent is on a common header to all three charging pumps outside the clearance boundary. The charging pump fill and vent procedure introduced the void by allowing air to enter the operating charging pump suction header by opening the clearance isolation valve without removing the air on the cleared side of the valve. This event is considered to have very low risk significance based upon an Engineering best-estimate evaluation which showed that both HHSI trains could have performed their safety function during a postulated design basis accident.
3342010002 | Beaver Valley 1 | 10/02/2010 | 03/11/2011 | ML11075002 | <strong>270 Degree Circumferential Flaw Found on Residual Heat Removal System Drain Valve Socket Weld</strong><br /><i>Abstract:&nbsp;</i>Shortly after the Beaver Valley Power Station Unit No.1 (BVPS-1) shut down for a refueling outage, an active boric acid leak was identified on a drain valve (1RH-200) located on the common suction piping for the Residual Heat Removal (RHR) system. Following initial identification of the active leak, a Non-Destructive Examination (VT-1 examination) was performed on the valve and its associated piping. A circumferential flaw (crack) of 270 degrees in length with water seeping from the toe of the weld was discovered. Based on discovery of the weld crack, both trains of the RHR system were then declared inoperable. With no trains of the RHR System operable in Mode 5, this condition is reportable as an event that could have prevented the fulfillment of a safety function for systems needed to remove decay heat per 10CFR50.73(a)(2)(v)(B). Technical Specification (TS) 3.4.7 Actions were appropriately entered when the VT-1 inspection determined the presence of a weld flaw on 1RH-200. However, since the adverse condition was identified prior to the completion of the VT-1 examination and no action was immediately initiated per TS 3.4.7 for no operable RHR trains (since the significance of the noted leakage could not be recognized until the VT-1 examination was completed), this was an (inadvertent) operation/condition prohibited by plant's TS, and is also reportable per 10 CFR 50.73(a)(2)(i)(B). The direct cause was determined to be a fatigue failure of the socket weld. A metallurgical examination of the 1RH-200 socket weld failure determined that the mechanism responsible for the cracks in the pipe and socket weld is fatigue. The most probable root cause is less than adequate (LTA) consideration of vibration induced fatigue in the design process. The safety significance associated with the BVPS Unit 1 cracked weld on the RHR drain line valve is considered to be very low.
3342010003 | Beaver Valley 1 | 11/15/2010 | 02/18/2013 | ML13052A01 | <strong>Premature Lifting of ECCS Relief Valve Results in Post-Accident Outside-Containment Leakage Limits to be Exceeded</strong><br /><i>Abstract:&nbsp;</i>On 11/15/2010 during the performance of a Beaver Valley Power Station (BVPS) Unit 1 surveillance test on the 'A' Low Head Safety Injection (LHSI) Pump, discharge relief valve RV-1SI-845B lifted with approximately 20 gpm leakage rate going to the safeguards building area sump. Subsequent testing showed that this relief valve opened whenever the 'A' LHSI Pump operated. Engineering analysis determined that this outside-containment leakage rate would exceed regulatory limits for projected Exclusion Area Boundary (EAB) dose and projected Control Room Dose during a postulated Design Basis Accident since the relief valve is on a common discharge header. BVPS Unit 1 entered Technical Specification 3.5.2 for two trains of LHSI being inoperable and both BVPS Unit 1 and Unit 2 entered Technical Specification 3.7.10 for the Control Room Envelope boundary not being adequate since the units share a common control room. This condition was determined to be reportable per 10CFR50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety and per 10CFR50.73(a)(2)(v)(C) as a condition that could have prevented the safety function to control the release of radioactive material. Gas voiding on the inlet side of RV-1SI-845B and system piping was determined to be the most probable cause of this relief valve lifting during the LHSI pump surveillance testing. Also, relief valve RV-1SI-845B did not reseat after opening due to an incorrect guide ring setting, resulting in a leakage rate outside containment that exceeded regulatory limits. The safety significance of the relief valve leakage event that occurred on 11/15/2010 was very low.
3352010001 | St. Lucie 1 | 02/04/2010 | 12/16/2010 | ML10357003 | <strong>Air Intrusion From 1A Containment Instrument Air Compressor Into Unit 1 Component Cooling Water (CCW) System</strong><br /><i>Abstract:&nbsp;</i>On February 4, 2010, St. Lucie Unit 1 was operating in Mode 1 at 100% power when the Onsite Review Group (ORG) concluded that an air intrusion event on October 16, 2008, involving the containment instrument air system resulted in the CCW system becoming inoperable. Evaluation of the CCW system indicated that Operators detected and eliminated the source of the air ingress with no significant system impact during normal power operation. An evaluation of the system under design basis accident conditions determined that the CCW system was in an unanalyzed condition that could have prevented the fulfillment of a safety function and rendered the CCW system inoperable. In accordance with 10 CFR 50.73 (a) (2) (ii) (B), 10 CFR 50.73 (a) (2) (v) (D), 10 CFR 50.73 (a) (2) (i) (B) and 10 CFR 50.73 (a) (2) (vii) this event requires notification of the NRC via a License Event Report (LER). The root causes for this event concluded that organization and programmatic weaknesses existed in the areas of prompt identification, understanding of event significance, timely corrective actions and original design gaps of the containment instrument air compressor system. Corrective actions include plant hardware modifications, procedure revisions and training.
3352010002 | St. Lucie 1 | 05/04/2010 | 06/23/2010 | ML10183027 | <strong>Opened ECCS Boundary Door in Violation of Identified Compensatory Measures</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2010, St. Lucie Unit 1 was operating in Mode 1 at 100% power when the onsite review group (ORG) validated the Station analysis that on April 4, 2010, the compensatory measures for a breached emergency core cooling system (ECCS) boundary door were not fully implemented which compromised the ventilation pressure boundary. This event was determined to be reportable in accordance with NUREG 1022, Rev.2, 10 CFR 50.73(a) (2) (i) (B). For the period of time the door was opened the ECCS area ventilation system could not perform its safety related function. An evaluation determined the cause of the event to be a failure to follow procedures, inadequate use of human performance tools, and a lack of supervisory oversight. Corrective actions addressed: individual human performance and revised training for obtaining and utilizing breach permits.
3352010003 | St. Lucie 1 | 05/05/2010 | 06/18/2010 | ML10179005 | <strong>Unanalyzed Condition Resulting from Alignment of Non-Essential CCW Header under Certain Accident Scenarios</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2010, St. Lucie Units 1 and Unit 2 were operating in Mode 1 at 100 percent power when the Onsite Review Group (ORG) validated the Station analysis that the condition discovered on August 7, 2009, was reportable. During a NRC Component Design Basis Inspection (CDBI), the inspection team questioned the operating philosophy of restoring a non-essential component cooling water (CCW) header to an essential header following a safety injection actuation signal (SIAS) for the purpose of sampling of the steam generators for activity and cooling of the reactor coolant pump (RCP) seals. Re-alignment of the non-essential CCW header following a large break loss-of-coolant accident (LBLOCA) for Unit 2 results in an unanalyzed condition that significantly degraded plant safety. Realignment of the non-essential CCW header following a LBLOCA, both Units 1 and 2 could result in the failure of 2 or more trains in different systems from properly completing their safety function if a failure were to occur on the non-essential CCW header. The cause of the event was determined to be an inadequate EOP procedure review. Corrective actions included revisions to emergency operating procedures (EOPs) to preclude alignment of the non-essential CCW header (N-header) to the essential CCW header, and issuance of a Standing Order providing guidance to the operating crews.
3352010006 | St. Lucie 1 | 06/16/2010 | 08/16/2010 | ML10236017 | <strong>Unit 1 Manual Reactor Trip due to Two Dropped Control Rods</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2010, St. Lucie Unit 1 was in Mode 1 returning from a scheduled refueling outage when a manual reactor trip was initiated. Due to the control element drive mechanism (CEDM) system not being able to effectively maintain two control element assemblies (CEAs) in the withdrawn and aligned position. This event required Operations to manually trip Unit 1 due to greater than one CEA being misaligned from other CEAs greater than twenty inches. All control systems responded as required. A root cause evaluation (ROE) determined the cause to be a failure of the snubber network capacitors to perform its designed function. Contributing causes included ineffective maintenance on the cable spreading room air conditioners and a weakness in purchasing the correct capacitors for the power switches. Corrective actions included replacement of the under rated network capacitors on the upper gripper power switches which are normally energized (holding) on all CEDMs and the lower gripper, lift, and load transfer power switches for the lead group CEDM's, and reduction of the temperature and humidity within the cable spreading room.
3352010007 | St. Lucie 1 | 06/25/2010 | 08/24/2010 | ML10243016 | <strong>Latent Failure of Steam Driven AFW Pump Led to Operation Prohibited by TSs</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2010, St. Lucie Unit 1 was in Mode 3 when the steam driven 1C auxiliary feedwater (AFW) pump failed to reach rated speed during a Technical Specification surveillance. Operations locally tripped the 1C AFW pump and declared the 1C AFW pump out of service. The failure of the pump was caused by debris binding the turbine governor assembly. The debris was generated from the degrading atmospheric steam dump valve (ADV) silencers. The governor was repaired and the 1C AFW pump returned to service. Other corrective actions include steam driven AFW pump inspections post ADV operation, the erection of an interim housekeeping enclosure, procedural guidance for as-left and as-found governor condition, and scheduling the ADV silencers for replacement during the next refueling outage, SL1-24.
3362010001 | Millstone 2 | 02/26/2010 | 04/26/2010 | ML10125004 | <strong>Millstone Power Station Unit 2 Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2010, with the unit in Mode 1, at 100 % power, the Millstone Power Station Unit 2 (MPS2) reactor was manually tripped as required by procedure due to a loss of circulating water (CW) flow to one of the two sections of the main condenser. All control rods fully inserted into the reactor and all emergency systems functioned as designed. At the time of the trip, the 'D' CW pump was out of service for planned maintenance. The loss of CW flow to a main condenser section occurred when the 'C' CW pump automatically tripped due to a larger than expected influx of debris causing a high differential level across the traveling screens. Following the trip, the operators closed the main steam isolation valves to protect the condenser from overpressure. There were no radiological challenges as a result of the event. The cause was determined to be the failure of the organization's individual departments to work together as a team to clearly identify the risks associated with the work evolution. The risk assessment and mitigation control process has been reviewed and the appropriate actions are being taken in accordance with the corrective action program. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
3362010002 | Millstone 2 | 05/22/2010 | 07/20/2010 | ML11039048 | <strong>Manual Reactor Trip on High Steam-Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2010 at 1645 with the Millstone Power Station Unit 2 at 100% power in Mode 1, the reactor was manually tripped by operators due to a high water level condition in steam generator (S/G) number 2. Investigation determined that level oscillations occurred because of S/G level control problems associated with number 2 feedwater (FW) regulating valve. Safety systems functioned as expected based upon the signals received. The operators took actions as trained and in accordance with established procedures. No equipment was damaged as a result of the event. The unit was brought to a stable condition in hot-standby. The cause of the reactor trip was vibration induced wear of the number 2 FW regulating valve positioner beam screw. The degraded valve positioner was replaced and the frequency of on-line preventive maintenance was changed. Design changes are being evaluated to reduce FW regulating valve positioner beam screw wear. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10CFR50.73(a)(2)(iv)(B).
3362010003 | Millstone 2 | 11/28/2010 | 01/27/2011 | ML11039048 | <strong>Reactor Trip on Low Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On November 28, 2010, at 1515, Millstone Power Station Unit 2's (MPS2) reactor automatically tripped from 100% power MODE 1. Prior to the event, MPS2 was establishing conditions to perform a backwash of the "B" condenser [COND] waterbox. Operators pressed the stop pushbutton for the "B" circulating water (CW) pump [P] and were closing the "A" CW pump's water box outlet valve (2-CW-11A) [V] per established operating procedure OP-2325D when the "A" CW pump automatically ramped off. Upon loss of the second pump in the condenser, condenser pressure increased to the low condenser vacuum trip set point, causing an automatic turbine generator trip and a reactor trip. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B). The cause of the event was an organizational failure to properly develop and train on the procedure needed to conduct backwashing operations using Variable Frequency Driven (VFD) CW pumps. Corrective actions to prevent recurrence being implemented will ensure proper development and training on procedures are made during plant modifications.
3382010001 | North Anna 1, North Anna 2 | 05/13/2010 | 07/12/2010 | ML10202025 | <strong>Non-Functional Fire Barrier Penetrations Containing Aluminum Conduit due to Configuration</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2010, results of aluminum conduit seal penetration tests determined certain fire barrier penetration configurations would not perform their design function. The North Anna Power Station has approximately 900 fire barrier penetrations containing aluminum conduit of which approximately 300 were identified as requiring modification to meet their design function. Degraded fire barriers, such that the required degree of separation for redundant safe shutdown trains is lacking, is reportable as an unanalyzed condition that significantly degraded plant safety. Therefore, this report is being submitted pursuant to 10CFR50.73(a)(2)(ii)(B). At the time of discovery fire watches for the affected areas were already in place. This event posed no significant safety implications since fire suppression, detection and plant response along with the compensatory measures implemented provided an adequate level of protection for redundant equipment. This situation has not resulted in any significant safety consequences or implications and the health and safety of the public were not affected at any time. A fire has not occurred in the affected fire areas that has challenged these penetrations.
3382010002 | North Anna 1 | 07/14/2010 | 09/08/2010 | ML10257139 | <strong>Forced Shutdown due to Un-isolable "C" Steam Generator Surface Sample Line Leakage</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2010, at 1834 hours, North Anna Unit 1 entered the six hour action of Technical Specification (TS) 3.4.4 to be in Mode 3 due to the "C" Reactor Coolant System loop being declared inoperable. Prior to the declaration, a seventy two hour limiting action of Technical Requirements Manual TR 3.4.6.A was entered as a result of a leak discovered on the "C" Steam Generator (SG) sample line that was subsequently determined to be un-isolable. At 1934 hours on July 14, 2010, Operations personnel commenced ramping Unit 1 offline. The six hour limiting action of TS 3.4.4 was cleared at 2354 hours when Unit 1 entered Mode 3. A non-emergency 4-hour report was made to the NRC Operations Center at 1953 hours on July 14, 2010, in accordance with 10 CFR 50.72(b)(2)(i). This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(A) for the completion of a nuclear plant shutdown required by the Technical Specifications. This event posed no significant safety implications since the "C" SG surface sample line leak, of approximately .243 gallons per minute, did not impact the safe operation of the reactor. Therefore, the health and safety of the public were not affected by this event.
3382010003 | North Anna 1, North Anna 2 | 09/24/2010 | 11/22/2010 | ML10334051 | <strong>Potential for Containment Sump Strainer Blockage due to Unacceptable Insulation in Containment</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2010, with Unit 1 defueled during a scheduled refueling outage, an insulation discrepancy was noted while investigating the supplementary neutron shielding material on the Reactor Pressure Vessel nozzles. Engineering review of the modification that installed the shielding noted the original Tempmat insulation was replaced with Microtherm insulation per Design Change 79-S07. This conflicted with the GSI-191 vendor walk-down report. On September 24, 2010 subsequent inspections revealed Microtherm insulation on the Intermediate RCS Loop which is within the North Anna 1 containment GSI-191 Zone of Influence. The corresponding Unit 2 Intermediate RCS Loop insulation had been mitigated. On September 28, 2010, additional Microtherm insulation was identified on the Unit 1 Reactor Coolant Pumps. On September 28, 2010, management decided to voluntarily shutdown Unit 2 based on inconsistent documentation to perform insulation inspections in equivalent areas. The visual inspections confirmed the existence of Microtherm in Unit 2 Containment. On September 29, 2010, at 1415 hours, an Information Only notification was made to the NRC Operations Center. This event is reportable per 10 CFR 50.73(a)(2)(v)(D) for a condition that could have prevented the fulfillment of a safety function needed to mitigate the consecuences of an accident.
3382010004 | North Anna 1 | 10/22/2010 | 12/20/2010 | ML10363040 | <strong>Manual Reactor Trip due to Malfunction of the Rod Control In-Hold-Out Selector Switch</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2010, Unit 1 was in Mode 2, with the reactor critical at zero percent power, with personnel performing physics testing in accordance with periodic test (PT) procedure 1-PT-94.0, Refueling Nuclear Design Check Tests. During physics testing, the rod control in-hold-out selector switch was not functioning properly when control rods were moved in the outward direction. At 0636 hours, a conservative decision was made to manually trip the Unit 1 reactor, by opening the reactor trip breakers, in order to perform repairs on the rod control in-hold-out selector switch. The rod control in-hold-out selector switch was subsequently replaced. On October 22, 2010, at 0946 hours, a non-emergency four-hour report was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iv)(B) due to actuation of the Reactor Protection System. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in manual actuation of the Reactor Protection System. This event posed no significant safety consequences because the control rods remained capable of being tripped. Therefore, the health and safety of the public were not affected by this event.
3382010005 | North Anna 1 | 12/12/2010 | 02/03/2011 | ML11040011 | <strong>Unanalyzed Scaffolding Renders Charging Pump Inoperable due to Human Error</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2010, with Unit 1 in Mode 1, 100 percent power, the Unit 1 "A" Charging Pump was declared inoperable when scaffolding was discovered in the pump cubicle without Operations or Engineering reviews required for High Risk (seismic) scaffolding. This could have resulted in the failure of the pump if a seismic event had occurred. A review of operating logs indicated that, as a result of the scaffolding, the Unit 1 "A" Charging Pump was inoperable for a period greater than the Technical Specification allowed outage time. In addition, on November 9, 2010, with the Unit 1 "A" Charging Pump in service, the Unit 1 "B" Charging Pump was declared inoperable for approximately two hours to perform surveillance testing. This is also a condition prohibited by Technical Specifications. The cause of the event was human error in that the scaffold tracking program was inadvertently changed to indicate the scaffold had been removed. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by Technical Specifications. This event posed no significant safety implications since a seismic event did not occur while the scaffolding was in place and redundant pumps were available at all times. Therefore, the health and safety of the public were not affected by this event.
3392010001 | North Anna 2 | 04/27/2010 | 06/23/2010 | ML10180026 | <strong>Automatic Reactor Trip and ESF Actuation During Automatic Voltage Regulator Testing due to Inadequate Procedure Guidance</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2010 at 1637 hours, with Unit 2 in Mode 1 at 74% power during recovery from a refueling outage, an automatic reactor trip occurred while testing a new digital automatic voltage regulator (AVR). A turbine trip due to a generator lockout caused the automatic reactor trip. The direct cause of the generator lockout protective relay actuation was the incorrect operability curve set points derived from the voltage regulator Minimum Excitation Level (MEL) tuning software. Following the reactor trip, all control rods inserted into the core and decay heat was removed using the normal steam dump system. The Auxiliary Feedwater (AFW) Pumps received an automatic start signal due to low/low level in the steam generators following the reactor trip. Following the automatic start of the Turbine Driven AFW (TDAFW) pump, the Control Room received annunciator alarm (F-D8). This was an AFW Pump Trouble or Lube Oil Trouble alarm. An operator was dispatched and reported that oil was spraying from the pump bearings and reservoir. The TDAFW pump was secured and declared inoperable. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for the automatic actuation of the Reactor Protection System and AFW System. No significant safety consequences resulted from this event. Steam Generator inventory was restored to the normal operating level. Therefore, the health and safety of the public were not affected by this event.
3392010002 | North Anna 2 | 05/28/2010 | 07/26/2010 | ML10215034 | <strong>Automatic Reactor Trip and Engineered Safety Feature Actuation Due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2010, at 0004 hours North Anna Unit 2 experienced an automatic Reactor trip from 100 percent power following a lightning strike in the switchyard. A combination of events precluded the transfer of the "B" Station Service (SS) bus to the "B" Reserve Station Service Transformer (RSST), resulting in the "B" SS bus being de-energized and a consequential loss of power to Unit 2 reactor coolant pump 1B (2-RC-P-1 B). Unit 2 tripped on low flow in the "B" RCS loop. All available Engineered Safety Feature equipment responded as designed. A non-emergency 4-hour report was made to the NRC Operations Center at 0323 hours on May 28, 2010, in accordance with 10 CFR 50.72(b)(2)(iv)(B). An 8-hour report was also made in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System (AFW). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in automatic actuation of the reactor protection system and the AFW system. This event posed no significant safety implications since the reactor protection system functioned to trip the reactor. Therefore, the health and safety of the public were not affected by this event.
3392010003 | North Anna 2 | 05/28/2010 | 07/26/2010 | ML10215034 | <strong>Failure To Isolate Primary Grade Water To Blender Due to Operator Activities</strong><br /><i>Abstract:&nbsp;</i>On May 28, 2010, at 0004 hours North Anna Unit 2 experienced an automatic Reactor trip from 100 percent power following a lightning strike in the switchyard. At 0014 to 0027 hours a primary grade make-up to the blender was performed. Subsequently, it was determined that the surveillance requirement to ensure valves in the affected flow path are secured closed was not performed. At 0104 hours the primary grade (PG) supply valve was secured closed. However, the fifteen minute isolation requirement of Technical Specifications (TS) 3.1.8 was not met. Due to the high volume of activities associated with the automatic reactor trip and loss of power Operations personnel failed to secure the PG supply valve within the required time. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by TS. This event posed no significant safety implications since the dilution flow path was isolated. Therefore, the health and safety of the public were not affected by this event.
3392010004 | North Anna 2 | 06/16/2010 | 08/16/2010 | ML10236033 | <strong>Automatic Reactor Trip and Engineered Safety Feature Actuation due to Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On June 16, 2010, at 1920 hours North Anna Unit 2 experienced an automatic reactor trip from 98 percent power during a severe thunderstorm. A lightning strike within the Protected Area was the direct cause of this event. The lightning strike caused an Overtemperature Delta T (OTAT) reactor trip signal without an actual overtemperature condition. The control room team responded to the reactor trip in accordance with procedure 2-E-0, Reactor Trip or Safety injection. All Engineered Safety Feature equipment responded as designed. A non-emergency 4-hour report was made to the NRC Operations Center at 2108 hours on June 16, 2010, in accordance with 10 CFR 50.72(b)(2)(iv)(B). An 8-hour report was also made, in accordance with 10 CFR 50.72(b)(3)(iv)(A) due to actuation of the Auxiliary Feedwater System (AFW). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in automatic actuation of the Reactor Protection System (RPS) and the AFW system. This event posed no significant safety implications since the reactor protection systems functioned to trip the reactor. Therefore, the health and safety of the public were not affected by this event.
3412010001 | Fermi 2 | 03/25/2010 | 05/19/2010 | ML10140055 | <strong>Automatic Reactor Shutdown due to Generator Current Transformer Wiring Failure</strong><br /><i>Abstract:&nbsp;</i>At 16:27 EDT on March 25, 2010, the reactor mode switch was taken to shutdown following an automatic scram due to a main turbine trip. The Main Turbine Trip relays actuated causing a turbine control valve fast closure which initiated a scram signal. The scram was uncomplicated. The reactor protection system (RPS) performed as expected, and all control rods were fully inserted into the core. Both safety and non-safety related plant equipment responded as expected to the reactor scram. At the time of the event, all Emergency Core Cooling Systems (ECCS) and Emergency Diesel Generators (EDGs) were operable. All reactor parameters were maintained well within analyzed limits. Plant procedures were appropriately utilized to complete scram recovery actions. Investigation determined that the turbine trip relays actuated due to a generator differential current relay trip in the Main Generator Z phase protection circuit. The cause of the Z phase relay actuation was the result of a shorted current transformer wire in the Main Generator Z phase line terminal bushing enclosure. The wire was repaired and other preventive measures were implemented for similar wiring. Additional corrective actions are being considered in accordance with the corrective action program.
3412010002 | Fermi 2 | 06/06/2010 | 08/03/2010 | ML10223042 | <strong>Automatic Reactor Scram and Loss of Offsite Power due to Severe Weather</strong><br /><i>Abstract:&nbsp;</i>At 0238 hours, on June 6, 2010, the Reactor Protection System initiated an automatic reactor scram from 100% power as a result of a Turbine Control Valve (TCV) fast closure. The TCV closure was caused by a turbine trip signal initiated by the main turbine-generator protective control system upon sensing the loss of Division II offsite power. The loss of Division II offsite power occurred as a result of the severe weather and tornado in the area. All safety related systems operated as expected in response to this event. All control rods fully inserted into the reactor core. Reactor Pressure Vessel (RPV) water level decreased and the Reactor Core Isolation Cooling system was manually started to restore RPV level. Reactor Water Level 3 Primary containment isolations occurred as expected. Two Division II Emergency Diesel Generators started and energized their emergency loads as designed. At 0417 hours, on June 6, an Alert was declared due to damage to the Auxiliary Building fifth floor siding during the severe weather. At 0220 hours, on June 7, 2010, the Alert was terminated. The Main Generator was synchronized to the grid at 1921 hours, on June 16, 2010, following repairs to offsite power feeds and station structures.
3412010003 | Fermi 2 | 10/24/2010 | 12/20/2010 | ML10363043 | <strong>Automatic Reactor Scram due to Degraded Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2010 shortly after 16:00 EDT with the reactor operating at approximately 97% power, condenser pressure began an upward trend. High condenser pressure alarmed at 16:38 EDT, plant operators responded to the conditions using plant procedures, and at approximately 16:42 EDT on October 24, 2010, a second condenser high pressure relay actuated resulting in a turbine trip. Turbine control valve fast closure then initiated a reactor scram. All control rods fully inserted except control rod 10-35 which initially stopped moving at position 42. Control rod 10-35 was manually inserted from position 38 to the full in position three minutes later. Extensive troubleshooting was performed on control rod 10-35 and it has been demonstrated to be capable to perform its scram function. Other safety related systems performed as expected. Reactor water level decreased to below Level 3 to a minimum of approximately 133 inches above the top of active fuel. Reactor water level was returned to normal and controlled in the normal band using the Control Rod Drive and Reactor Feedwater systems. Reactor pressure was controlled and decay heat removed through the main turbine bypass valves to the main condenser. The event was caused by a degraded condenser vacuum which was caused by the erosion of the No. 3 Steam Jet Air Ejector steam supply first stage nozzle which resulted in a loss of ejector capacity. Inspections were performed of all four Steam Jet Air Ejectors, and repairs were made to restore expected performance before resuming operation.
3412010004 | Fermi 2 | 12/28/2010 | 02/23/2011 | ML11056022 | <strong>High Pressure Coolant Injection System Inoperable due to Inoperable Minimum Flow Valve</strong><br /><i>Abstract:&nbsp;</i>On December 28, 2010, during the HPCI turbine trip portion of a HPCI surveillance test, the HPCI minimum flow valve open and close indicating lights in the control room began blinking simultaneously. After a short duration (approximately 1 minute) the blinking faded and both indicators went out at 1220 EST. The HPCI minimum flow valve did not fully close as expected. Upon discovery of the problem and performance of minor troubleshooting, Operations determined that the ability of the HPCI minimum flow valve to perform its intended function was unreliable, and the valve was declared inoperable at 1220 EST. System troubleshooting, diagnostic testing, and analysis were performed, and components were identified that could be responsible for the problem. These components were replaced. Post maintenance testing was successfully completed on December 30, 2010 at 1027 EST. The HPCI minimum flow valve was closed, the system returned to service, and the LCO cleared December 30, 2010 at 1042 EST. Subsequent evaluation determined that the valve failure was caused by the close contactor, auxiliary contact alignment or high resistance, or high resistance connections. Those problems were corrected prior to returning HPCI to service. The safety consequences of this event were evaluated and determined to be low.
3462010001 | Davis-Besse | 03/02/2010 | 05/10/2010 | ML10133044 | <strong>Steam and Feedwater Rupture Control System Re-Energizes in a Blocked Condition On Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2010, with the plant in Mode 5, the Steam and Feedwater Rupture Control System (SFRCS) Logic Channel 4 re-energized in a blocked condition. While performing the investigation, on March 10, 2010, it was discovered SFRCS Logic Channels 3 and 4 could re-energize in a blocked condition following a main steam line break and loss of offsite power (LOOP). If an SFRCS actuation were to occur due to a main steam line break followed by a LOOP, the Logic Channels 3 and 4 could re-energize with the low steam line pressure block initiated and cause inappropriate SFRCS actuation and feedwater would feed the affected Steam Generator. This was due to power still being supplied to the logic circuits from the 28 VDC power supply, SFRCS would not recognize a short duration power loss and would not initiate a Power On Reset, which is intended to restore SFRCS to a known state when it re-energizes. SFRCS does not meet single failure criterion with this condition, therefore, this event is reportable as an unanalyzed condition in accordance with 10 CFR 50.73(a)(2)(ii)(B). The condition also represents an operation or condition prohibited by the Technical Specifications and is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). Corrective Action will be completed during the current refueling outage to change the SFRCS logic to ensure a Power On Reset occurs anytime power is lost.
3462010002 | Davis-Besse | 03/12/2010 | 09/30/2010 | ML10280041 | <strong>Control Rod Drive Nozzle PrimaryWater Stress Corrosion Cracking and Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2010, during the Davis-Besse Nuclear Power Station (DBNPS) Refueling Outage, results of planned ultrasonic examinations identified Control Rod Drive Mechanism (CRDM) nozzles that did not meet applicable acceptance criteria. Additionally, results of the planned bare metal visual examination of the outer surface of the Reactor Vessel Closure Head (RVCH) identified boric acid deposits indicative of Reactor Coolant System leakage. No discernable wastage of the RVCH was identified. These conditions are being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), operation in a condition prohibited by the Technical Specifications, and 10 CFR 50.73(a)(2)(ii)(A), condition of the plant, including its principal safety barriers, being seriously degraded. The direct cause of this event is primary water stress corrosion cracking (PWSCC) of the CRDM nozzles. A total of 24 CRDM nozzles were repaired, and these degraded CRDM nozzles were modified utilizing the inside diameter temper bead welding method to restore the pressure boundary of the degraded nozzles. The Root Cause of this event was a less than adequate perception of the risk of PWSCC susceptibility with the replacement RVCH resulting in inadequate identification, development, and implementation of interim actions to mitigate degradation prior to replacement with a PWSCC resistant Alloy 690 RVCH.
3462010003 | Davis-Besse | 07/02/2010 | 10/15/2010 | ML10293002 | <strong>Auxiliary Feedwater Control Valve Inoperable Due to Inadequate Prioritization of DC System Ground</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2010, with the Davis-Besse Nuclear Power Station in Mode 1 at approximately 100 percent power, the discharge control solenoid valve (FV6451) for Auxiliary Feedwater (AFW) Train 2 was found de-energized during surveillance testing. Evaluations completed August 16, 2010, determined the valve had been potentially de-energized and inoperable for 18 days due to a DC motor control center (MCC) ground resulting from a main transformer oil pump flow indicating switch stuck in the closed position. The ground fault induced a voltage greater than the design capacity of the position controller board for the valve. The root cause of this event was determined to be a lack of program implementation by site organizations for finding DC system grounds, resulting in a mindset to inadequately prioritize ground indications. An unacceptable ground had been identified on DC MCC 2 on April 7, 2010, and it degraded into a hard ground on July 2, 2010, resulting in the failed AFW discharge valve (FV6451). This issue is being reported per 10CFR50.73(a)(2)(i)(B) as an operation prohibited by Technical Specifications. One AFW train was affected, therefore, no loss of safety function occurred. Corrective Actions include clarifying program ownership, procedure improvements used to locate DC system grounds, and training on conservative assumptions and prioritization of DC system ground indications.
3462010004 | Davis-Besse | 08/26/2010 | 06/17/2011 | ML11172A34 | <strong>Spent Fuel Pool Rack Patterns did not Comply with Technical Specification 3.7.16</strong><br /><i>Abstract:&nbsp;</i>On August 26, 2010, an issue with Technical Specification (TS) 3.7.16, "Spent Fuel Storage," Bases was identified. TS 3.7.16 requires fuel assemblies in the Spent Fuel Pool (SFP) to be placed in racks per the criteria of TS Figure 3.7.16-1, which references the TS Bases. The TS 3.7.16 Limiting Condition for Operation (LCO) Action requires initiation of action to move non-complying assemblies to an allowable location with an Action Completion Time of "Immediately." On August 26, 2010, there were assemblies in the SFP that did not comply with TS. This condition existed since conversion to Improved Standard TS (ITS), which omitted a SFP rack storage patterns TS Bases sentence. Additionally, action to bring the assemblies into compliance with TSs was not initiated "immediately." The root cause was an inadequate assessment of risks and consequences when making changes in the guidance for describing acceptable analyzed assembly storage patterns resulting in a TS change that omitted information or deferred an LCO to administrative procedures during the SFP re-rack in 2001. Because assemblies in the SFP were in an acceptable pattern per the criticality analysis, there was no safety significance. Corrective Actions include a TS Bases change to permit fuel storage in the SFP racks as analyzed. This event is reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS.
3482010001 | Farley 1 | 01/26/2010 | 03/26/2010 | ML10088000 | <strong>Failure to Deactivate Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2010 at 04:00 Southern Nuclear Operating Company (SNC) declared Unit 1 Containment (CTMT) Purge Exhaust Penetration Number 13 [JM] inoperable due to excessive leakage during the quarterly Leakage Rate Test. The outside CTMT Mini-Purge valve was identified as leaking past the seat. Technical Specification (TS) 3.6.3, "Containment Isolation Valves," was entered and the inside CTMT Mini-Purge Valve was closed and deactivated in accordance with TS 3.6.3. The Main Purge Valves are normally maintained in a closed and deactivated position. This established the penetration boundary as the inside CTMT valves. On January 26, 2010 SNC determined that the inside CTMT Purge Valve was actually the valve that was leaking. At this point the CTMT isolation for Penetration Number 13 was shifted to the outside CTMT valves. During the time the inside CTMT isolation valves were closed and deactivated, the outside CTMT Mini-Purge valve was not deactivated. This was a failure to meet the requirements of TS 3.6.3 to isolate the affected penetration flow path by use of at least one closed and de-activated automatic valve within 24 hours of detection of excessive penetration leakage. Repairs to the CTMT Purge Valve were completed and the penetration returned to service on February 8, 2010.
3482010002 | Farley 1 | 02/02/2010 | 08/20/2010 | ML10235003 | <strong>Two Auxiliary Feedwater Pumps Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2010 at 1615, the Unit 1 Turbine Driven Auxiliary Feedwater (TDAFW) Pump was declared inoperable due to a high temperature identified on an electrical cable in the TDAFW Uninterruptible Power Supply (UPS) [UA]. The 1B Emergency Diesel Generator (EDG) had previously been removed from service for scheduled maintenance. As required by Technical Specification (TS) 3.8.1, "AC Sources - Operating," Required Action Statement, the Unit 1 B-Train Motor Driven Auxiliary Feedwater (MDAFW) Pump was declared inoperable at 2015 on February 2, 2010 due to the combination of its inoperable emergency power supply and inoperable redundant equipment. This resulted in two of three trains of Auxiliary Feed Water (AFW) being inoperable. Because two out of the three trains of AFW are required to meet flow requirements for limiting design basis accidents (DBA), this represents a condition that could have prevented the fulfillment of a safety function. Repairs to the electrical cable were immediately initiated. At 2216 on February 2, 2010 the Unit 1 TDAFW and 1B MDAFW Pumps were returned to operable status restoring the safety function. Thermography scan of Unit 2 UPS was completed with no indications of adverse wiring connections. Further analysis of the UPS cable high temperature indicates that the TDAFW UPS function would not have been adversely affected. Reporting is still necessary because repair activities removed the TDAFW UPS from service rendering two of three AFW trains inoperable for approximately 26 minutes.
3482010003 | Farley 1 | 08/15/2010 | 09/24/2010 | ML10267063 | <strong>Shutdown Time Exceeded for High Containment Air Temperature</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2010 at 0400, Unit 1 exceeded the Technical Specification (TS) time allowed to be in Mode 3 due to containment average air temperature greater than or equal to 120 degrees F. Unit 1 entered TS 3.6.5 required action for Containment Air Temperature on August 14, 2010 at 1400 due to the heating effects caused by closing Service Water (SW) from Reactor Coolant Pump (RCP) motor air cooler Motor Operated Valve (MOV) 3134. Containment isolation was required by TS 3.6.3 when during surveillance testing, MOV 3134 failed to indicate fully closed by remote indication. On August 14, 2010 at 2200, containment air temperature had not been restored and Unit 1 entered the 6 hour required action to be in Mode 3. A controlled ramp down to Mode 3 was begun on August 15, 2010 at 0045 but was halted when an 18 hour Notice of Enforcement Discretion (NOED) was granted at approximately 0057. When stroked closed, MOV 3134 exhibited dual indication from the control room; however the local indication showed the valve had actually closed. Local leak rate testing (LLRT) verified the condition of the valve to be closed and operable as a containment penetration isolation boundary. Once MOV 3134 was verified to be operable, it was unisolated and opened. Containment temperature was restored to within TS limits on August 15, 2010 at 0823 and the NOED was exited.
3482010004 | Farley 1 | 10/29/2010 | 12/14/2010 | ML10350013 | <strong>Loss of Refueling Integrity</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2010 at 14:00, it was determined that Unit 1 was not in compliance with Technical Specification (TS) 3.9.3 in that one penetration providing direct access to the outside atmosphere was not isolated while Core Alterations were in progress. Prior to commencing Core Alterations, refueling integrity was appropriately established per the site procedure on the inside of containment for this penetration. After Core Alterations commenced on October 28, 2010 at 05:35, a scheduled maintenance activity required shifting the integrity boundary to outside containment for this penetration. The governing site procedure for establishing refueling integrity was in error for this penetration and did not recognize the existence of two seal cooler vent valves, configured in series, for the B train Residual Heat Removal (RHR) pump. After the maintenance replacement of the relief valve inside containment, it was discovered that the two seal cooler vent valves were open and provided direct access from the containment atmosphere to the auxiliary building during the time the relief was not installed. It is estimated that refueling integrity was lost for about 10 minutes during the relief valve replacement on October 29, 2010 at approximately 04:30. The Unit 1 site procedure governing refueling integrity was corrected for both trains of RHR. The corresponding procedure on Unit 2 was also revised.
3522010001 | Limerick 1 | 06/23/2010 | 08/23/2010 | ML10235046 | <strong>Valid Actuation of the Reactor Protection System with the Reactor Critical</strong><br /><i>Abstract:&nbsp;</i>A valid manual actuation of the reactor protection system was initiated due to an automatic trip of both reactor recirculation pumps. The event was caused by a failure of a 13 kV cable that powered a non-safeguard 480 VAC load center, a failure of a load center control power undervoltage auxiliary relay to automatically provide control power to the adjacent load center and a failure of a reactor recirculation pump M-G set standby lube oil pump relay. The faulted 13 kV cable section has been replaced but has not been energized. The failed undervoltage auxiliary relay has been replaced. The failed reactor recirculation pump M-G set standby lube oil pump relay was replaced. The north stack ventilation exhaust wide range accident monitor also failed due to the initial electrical distribution voltage transient. The radiation monitor has been repaired and returned to service.
3522010002 | Limerick 1 | 12/12/2010 | 02/10/2011 | ML11042009 | <strong>High Pressure Coolant Injection System Overspeed Trip Mechanism Failure to Reset</strong><br /><i>Abstract:&nbsp;</i>The High Pressure Coolant Injection system was rendered inoperable due to a failure of the overspeed mechanism to reset during a periodic test. The cause of the failure to reset was most likely a temporary blockage of the overspeed trip mechanism piston drain port. The condition was corrected by flushing the overspeed trip mechanism during troubleshooting activities.
3532010001 | Limerick 2 | 04/29/2010 | 06/25/2010 | ML10176033 | <strong>Inoperable Reactor Enclosure Cooling Water Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>The Hi-Hi radiation alarm setpoint for the process radiation monitor on the reactor enclosure cooling water system was discovered to be exceeding the Technical Specification allowable value during a review of completed surveillance test documentation. The required grab samples were not collected during the affected period. The condition was caused by a less than adequate technical human performance during revision of the surveillance test procedure in 2003. The affected procedures have been revised to correct the error.
3542010001 | Hope Creek | 06/08/2010 | 02/18/2011 | ML11055015 | <strong>Technical Specification Surveillance Requirement Not Met</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2010, during a review of Technical Specification (TS) surveillance requirement (SR) 4.7.1.1.b, it was noted that existing surveillance tests for the Safety Auxiliary Cooling System (SACS) heat exchanger (HX) bypass valves (EG-HV-2457A/B and EGTV-2517A/B), did not appear to adequately test the isolation circuitry of the valves. This event is reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition which was prohibited by the plant's TS. The SACS HX bypass valves were shut, purposely failed closed, and declared inoperable while an engineering assessment was conducted to determine if the valves were required to be tested in accordance with the SR and/or whether existing surveillance tests met the requirements of the SR. The 2457A/B and 2517A/B valves have been tested under SR 4.7.1.1.b. before returning them to operation. Extent of condition reviews of other automatic SACS valves and automatic Station Service Water (SSW) valves servicing safety related equipment are being performed. If additional valves are identified as not being adequately included in the SR population, a supplement to this LER will be provided.
3542010002 | Hope Creek | 10/25/2010 | 04/07/2011 | ML11116A10 | <strong>As Found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specification Allowable</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2010, PSEG received the initial results for the safety relief valve (SRV) pilot valve 'as-found' setpoint testing. The results indicated that two SRV pilot valve setpoints exceeded Technical Specification (TS) allowable tolerance specified in TS 3.4.2.1. This specification requires SRV setpoint limits to be within +/- 3% of the specified value. The valves failing to meet limits were Target Rock Model 7567F two-stage SRVs. As planned all 14 SRV pilot valves were removed and replaced with pre-tested, certified spare pilot valves during refueling outage H1 RF16. All 14 removed SRV pilot valves were "as found" tested at an offsite I test facility. A total of six of the 14 SRV pilot valves experienced setpoint drift outside of the TS 3.4.2.1 limit. I The cause of the setpoint drift for five of six SRVs is corrosion bonding, which is consistent with industry experience. The materials combination for the pilot disc & the pilot seat has been a known industry issue since the design of the Target Rock 2 stage SRV. The cause of the setpoint drift of the sixth SRV was failure I of the pilot spring to impart an even loading causing a misalignment of parts. This condition is reportable under 10CFR50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant Technical Specifications.
3542010003 | Hope Creek | 11/01/2010 | 12/21/2010 | ML10363040 | <strong>RHR Shutdown Cooling Suction Relief Valve Missed Surveillance.</strong><br /><i>Abstract:&nbsp;</i>In December 2009 a self assessment discovered a technical error in the testing of 1 BCPSV-4425, the Residual Heat Removal (RHR) Shutdown Cooling (SDC) suction relief valve. 1 BCPSV-4425 is an ASME Class One (1) valve, but had been improperly grouped with Class Two (2) and Three (3) valves. As a result 1 BCPSV-4425 had been tested on a ten year, instead of a five year interval. The valve was last tested on October 25, 2007. Since there is no other Class One (1) valve of this type, it would be in a group by itself and therefore required to be tested every 24 months. As such, this discovery constituted a missed surveillance for 1 BCPSV-4425. This required application of Technical Specification (TS) 4.0.3. A risk evaluation was performed in accordance with TS 4.0.3 on December 17, 2009 to justify delay of the test until the Fall 2010 refueling outage. The evaluation concluded there was no significant increase in risk as a result of the delay in performance of the missed surveillance. The testing performed on November 1, 2010 was unsatisfactory as the as-found setpoint was outside the acceptable range. Therefore, this failed late surveillance is reportable per 10 CFR 50.73(a)(2)(i)(B).
3612010001 | San Onofre 2 | 01/26/2010 | 06/30/2010 | ML10183041 | <strong>Broken Manual Valve Prevents Timely Condensate Storage Tank Isolation</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2010 at about 1700 PST with Unit 2 in Mode 5 (Cold Shutdown), the handwheel actuator for manual isolation valve 2HV-5715 failed during a surveillance test; the last successful stroke test was on March 29, 2008. The failure was due to a lack of lubrication and corrosion of the handwheel stem. The surveillance test frequency had been changed from quarterly to biennial in 2004 without implementing periodic lubrication of the stem. Technical Specification (TS) 3.7.6 establishes inventory requirements for the Condensate Storage Tanks (CST). Valve 2HV-5715 is closed within 90 minutes of a seismic event to maintain the CST inventory in compliance with license commitments for Decay Heat Removal (RSB 5-1). The inability to close the valve within the committed time limit is being reported under 50.73(a)(2)(i)(B) as a failure to comply with the TS. The valve was repaired on January 27, 2010. Corrective actions were taken to lubricate this valve and add it to the preventive maintenance program. Preventive maintenance plans are being developed for the remaining affected valve population. The safety significance was minimal as sufficient water inventory would have remained within the design margins to comply with the licensed safety functions. Neither the health nor the safety of plant personnel or the public was affected by this occurrence.
3612010002 | San Onofre 2 | 05/12/2010 | 06/30/2010 | ML10183041 | <strong>Non-qualified Part in Turbine Driven Auxiliary Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On 5/12/10 at 0900 PDT with Unit 2 at 98% Power, Dresser Rand (D-R) informed SONGS the Digital Control System (DCS) installed for the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) may contain a circuit board with a missing solder joint. The seismic qualifications of the circuit board are in question with the missing solder joint. D-R filed a Part 21 report on 5/12/10 when the defect was discovered at Farley. The Unit 2 DCS was installed during the Cycle 16 refueling outage, and in service from 4/1/10 until the TDAFWP was declared inoperable at 0915 PDT on 5/12/10. TS 3.7.5 "Auxiliary Feedwater (AFW) System," requires the TDAFWP to be operable in Modes 1 - 4 when the steam generators are used for heat removal. The operation of the TDAFWP for greater than 72 hours with a potentially non-qualified component is being reported under 50.73(a)(2)(i)(B). The TDAFWP was returned to service on 5/14/10 at 2222 PDT after a qualified replacement was obtained from the vendor, installed, and tested in the plant. A supplemental LER will provide seismic qualification test results on the suspect circuit board. There was minimal safety significance as the circuit board had passed its TS required surveillances and the two motor driven AFW pumps were available, if needed. Neither the health nor safety of plant personnel or the public was affected by this occurrence.
3612010003 | San Onofre 2, San Onofre 3 | 07/15/2010 | 09/03/2010 | ML10250029 | <strong>Typographical Error Results in Conflicting TS Actions and TS Violation</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2010 [Event Date] during a review for a TS Upgrade Project, SCE discovered a conflict within TS 3.6.3. Condition A of this specification applies to penetration flow paths with two containment isolation valves and requires an inoperable valve to be isolated/closed within four hours. Because Condition A does not further specify the CIVs to which it applies, it can be inferred that Condition A applies to all CIVs. Conditions E and F apply to Groups D1 and D2, respectively, with the required action to place the inoperable valve in its ESF actuated position (open) with completion time specified as "In accordance with the applicable LCO pertaining to the system in which it is installed." A review of control room logs confirmed that during the past three years, SCE has not applied the required actions of Condition A to Section D.1 and D.2 CIVs. SCE is reporting this TS conflict in accordance with 50.73(a)(2)(i)(B). SCE issued a priority reading to control room operators instructing them to enter TS 3.6.3 Condition A (close CIV) for the LCS Group D1 or D2 valves whenever TS 3.6.3 Conditions E or F are entered. The Technical Specification Upgrade Project will correct this error.
3612010004 | San Onofre 2, San Onofre 3 | 07/12/2010 | 09/03/2010 | ML10250029 | <strong>EDG Ventilation Fan Nose Cone Corrosion Results in Fan Damage</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2010 at about 1004 PDT, the Train B Emergency Diesel Generator (EDG) was started for the monthly surveillance run. Shortly afterwards the plant equipment operator heard a loud metallic noise and stopped the engine. The control room received a low air flow alarm from the emergency ventilation fan. The fan hub 'nose cone' had been ingested by one of the two Emergency Fans which ventilate the building. The failure was due to corrosion in the marine environment. The fan was repaired and Train B EDG was returned to service on July 16, 2010. SCE is voluntarily reporting this occurrence because the findings may be of generic interest in that the potential exists for inspections to overlook the extent of corrosion that has occurred on components installed in inaccessible areas exposed to salt air environments. The safety significance of this occurrence is minor.
3612010005 | San Onofre 2, San Onofre 3 | 10/13/2010 | 12/10/2010 | ML10348010 | <strong>Refueling Water Storage Tank Alignment to Non-Seismic Piping Results in Potential Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On 10/13/10 an engineering evaluation determined that San Onofre Nuclear Generating Station (SONGS) Units 2 and 3 were periodically operated with the safety-related Seismic Category I (SC-I) Refueling Water Storage Tank (RWST) aligned to the nonsafety-related non-seismic purification loop piping in the Spent Fuel Pool Cooling and Cleanup System, potentially resulting in a loss of safety function. The isolation between the seismic and non-seismic piping is accomplished via a normally locked-closed manually-operated isolation valve S2(3)1204MU060 (MU060). If the non-seismic piping upstream of MU060 fails during a significant seismic event with the valve open, the safety-related SC-I return header to the RWST could be impacted post-accident, causing a reduction in RWST inventory and a potential diversion path from the Emergency Core Cooling System mini-flow line through the failed return piping. Since MU060 was periodically maintained in the open position during RWST purification activities in operating Modes 1 through 4, and there were no specific controls in place to close the valve following a seismic event or safety injection signal, the plant was in a condition which could have prevented the fulfillment of a safety function required for mitigation of a Design Basis Accident. Immediate corrective action was to close the valves on both Units 2 and 3 pending further evaluation.
3612010006 | San Onofre 2, San Onofre 3 | 10/13/2010 | 12/13/2010 | ML10348011 | <strong>Breakers Left in Non-Seismically Qualified Condition Result in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 10/13/10 an engineering evaluation determined that San Onofre Nuclear Generating Station Unit 2 and 3 had left electrical circuit breakers racked out in a non-seismically qualified condition that resulted in an inoperable 4kv bus, which is a condition prohibited by Technical Specifications (TS). From 09/02/10 to 09/16/10, the Unit 3 Train A Salt Water Cooling Pump breaker had not been latched in a seismically restrained position in its cubicle. Although the breaker was not in service during the time of the deficiency, a significant seismic event could cause cubicle door failure, releasing the breaker, potentially impacting relays for the bus 3A04 feeder breaker, rendering the Train A Class lE 4kV bus (3A04) inoperable. Since Unit 3 was operating in Mode 1 during the deficiency, the TS Limiting Condition for Operation action statements were not met for one required offsite circuit inoperable and one AC power distribution system inoperable. On 10/04/10 a similar event occurred with the Unit 2 Train A High Pressure Safety Injection Pump power supply breaker. Unit 2 was operating in Mode 1 and the breaker was not in service at the time of the deficiency. The condition was identified and corrected within 10 hours of the breaker being placed in a non-seismic position.
3642010001 | Farley 2 | 04/30/2010 | 06/17/2010 | ML10172012 | <strong>Unplanned LOSP During SI with LOSP Testing</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2010 at 21:00, an unplanned Loss of Off-Site Power (LOSP) on A-train 4160 volt emergency Bus 2F occurred during a scheduled outage test, Safety Injection (SI) with LOSP. The Emergency Diesel Generator (EDG) 1-2A was being shutdown following the actuation portion of the test. When the B2F Sequencer was reset, the EDG output breaker (DF08-2) unexpectedly opened to generate the LOSP signal on the 2F Bus. As a result, the B2F Sequencer functioned to automatically re-close DF08-2, and start both the 2A Motor Driven Auxiliary Feedwater (MDAFW) pump and 2A High Head Safety Injection (HHSI) pump. All systems functioned as designed for this condition and core cooling was maintained throughout by the B-train 2B Residual Heat Removal (RHR) pump. Unit 1 remained at 100 % power during the event. A recent design change was implemented to assure EDG sequencer reliability during all modes of EDG operation. Subsequent to this design change, the necessary procedure change had not been properly incorporated in the test procedure. Test guidance relied upon transitioning to the System Operating Procedure (SOP) for operating the newly installed Test Trip Override Switch (TTOS) located on the B2F Sequencer. However, the transition was not at the correct location in the test procedure. Once recognized, the SOP guidance was used and the B2F Sequencer TTOS was operated before resetting the sequencer; and the restoration section was completed without further complications.
3642010002 | Farley 2 | 05/22/2010 | 07/02/2010 | ML10187048 | <strong>Reactor Trip due to Failed Feedwater Regulating Valve Controller</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2010 at 16:34, with Unit 2 at 100% power, the reactor was manually tripped due to 2C Steam Generator (SG) Feedwater Regulating Valve (FRV) failing closed. At approximately 16:34, the control room crew received multiple alarms associated with 2C SG level and a process cabinet failure. The crew noted no feedwater flow and decreasing level in 2C SG. Manual control of the 2C SG FRV was attempted but there was no power or control capability of the main feedwater regulating valve. At approximately 40% narrow range level in the 2C SG, the crew manually tripped Unit 2 prior to the automatic trip setpoint of 28% narrow range level. All safety systems functioned as designed without complications. Investigation revealed that the controller driver (NCD) card in the 2C SG FRV controller circuitry failed causing the 2C SG FRV to close. The failed NCD card was replaced. Unit 2 was restarted and returned to Mode 1 on May 23, 2010 at 17:12.
3642010003 | Farley 2 | 08/05/2009 | 07/21/2010 | ML10203007 | <strong>Power Supply to 1-2R Load Center Unavailability</strong><br /><i>Abstract:&nbsp;</i>During the period between August 5 and August 9, 2009, the Unit 2 power supply to 1-2R 600 V load center (LC) did not meet the Unit 2 portion of Technical Specification (TS) 3.8.9 "Distribution Systems - Operating." This was discovered on August 9, 2009 when during routine surveillance for on-site AC distribution, the Unit 2 4160 V supply breaker DH08-2 to 1-2R 600 V LC was found in the open position. The 1C emergency diesel generator (EDG) was declared inoperable for Unit 2 due to the 4160 V supply breaker DH08-2 from Unit 2 being open, and the required action statement was entered on August 9, 2009 at 02:02. Subsequently, the 4160 V supply breaker DH08-2 was closed on August 9, 2009 at 03:36. The 4160 V supply breaker DH08-2 being open resulted in a failure to meet TS 3.8.9 limiting condition for operation (LCO) for maintaining two trains of AC vital bus electrical power distribution subsystems operable. The 1-2R 600 V LC did not meet its surveillance requirement of correct breaker position and voltage for longer than the allowed by TS. The 4160 V supply breaker DH08-2 was left open due to omission of relevant information in procedures and the interpretation of LCO 3.8.9 that existed at the time.
3662010001 | Hatch 2 | 03/10/2010 | 04/30/2010 | ML10120027 | <strong>Failure to Recognize PCIV as Inoperable Results in a Condition Prohibited By the Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On March 10, 2010 at 20:00 EST, Unit 2 was at approximately 2799 CMWTh, 99.8 percent power. Earlier that day Operations personnel were performing the Reactor Core Isolation Cooling (RCIC) operability procedure. During that evolution an annunciator indicated that the RCIC barometric condenser pressure was high. Subsequent investigation determined that the vacuum pump discharge check valve was stuck closed. A review of the system operability was performed and since the barometric condenser is not required for RCIC to fulfill its' design function for its' mission time it was determined that RCIC was operable. This valve performs a second function of primary containment isolation valve. The cause of the valve sticking was unknown and thus the valve must be considered inoperable and the appropriate Technical Specification should be entered for the inoperable valve. This was not identified until after the action time for the applicable Technical Specification had expired; therefore, a condition prohibited by the Technical Specification existed. The cause of this event was failure to review operability from both a system and a component level. Corrective actions are to incorporate this example into the Operations training program and the failed valve has been replaced and tested with an acceptable PCIV.
3682010001 | Arkansas 2 | 02/01/2010 | 03/25/2010 | ML10084071 | <strong>An Incorrect Core Protection Calculator Addressable Constant Induced by Personnel Error Resulted in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2010, during the performance of Channel "C" Core Protection Calculator (CPC-C) Triannual Channel Functional Test, Operations was required to reload Type 1 addressable constants into CPC-C. During the reload of the Type 1 addressable constants, a numerical value of 1.0207 for computer point (PID) 063 (Azimuthal Tilt Allowance) was obtained from the CPC-C Addressable Constant Log Book. PID 063 was manually set to a value of 1.0207 and CPC-C was then observed to successfully pass the software check sum and cross channel checks. After all CPC-C addressable constants were reloaded, the functional test was completed, and CPC-C was declared OPERABLE at 1606 Central Standard Time (CST) on February 1, 2010. On February 2, 2010, at 0430 CST, following a power reduction to approximately 70 percent for planned maintenance, CPC-C was placed in bypass to perform a linear power calibration. During this calibration, Operations identified that an incorrect value for PID 063 had been previously entered into CPC-C. The value for PID 063 in CPC-C was subsequently changed from 1.0207 to the correct value of 1.03, with no notable changes observed in the CPC-C calculations. CPC-C was removed from bypass and restored to OPERABLE status on February 02, 2010 at 0453 CST. An operability evaluation later determined that the CPC-C was inoperable with the incorrect addressable constant installed.
3682010002 | Arkansas 2 | 08/23/2010 | 10/21/2010 | ML10295006 | <strong>Completion of a Plant Shutdown Required By Technical Specifications Due to the Inability to Restore an Emergency Diesel Generator to Operable Status within the Allowed Outage Time.</strong><br /><i>Abstract:&nbsp;</i>On August 9, 2010, at 0330 CDT, Arkansas Nuclear One, Unit 2 (ANO-2) removed one Emergency Diesel Generator (EDG) from service for planned maintenance and entered the appropriate Technical Specification (TS) action statements. The TS required the EDG to be restored to operable status within 14 days. The scheduled maintenance was not completed within the allowed outage time due to unresolved issues associated with crankcase pressure anomalies. Therefore, a plant shutdown was initiated at 0252 CDT on August 23, 2010 to comply with the EDG TS action statement. The shutdown was completed by entering Mode 3 at 0443 CDT on August 23, 2010. Subsequent to the shutdown, due to deficiencies in the tracking process for TS Limiting Condition for Operation compliance, an operation prohibited by Technical Specifications occurred when entry into Mode 4 was not achieved in accordance with the most restrictive TS completion time. A root cause investigation postulated that two possible conditions involving degraded subcomponents were the most likely and most significant causes of the EDG crankcase pressure anomalies. A degraded gasket between the crankcase oil separator and bulkhead was identified, along with evidence of piston ring blow-by which was most noticeable on 4 lower pistons. Following the replacement of all piston rings on the lower pistons, repair and inspection of the oil separator gasket, plus additional desired maintenance, the EDG was successfully tested and restored to operable status on September 2, 2010. ANO-2 resumed power operation on September 4, 2010.
3692010001 | McGuire 1, McGuire 2 | 01/13/2010 | 03/11/2010 | ML10082028 | <strong>Power Reduction of Two Units due to Entry into LCO 3.0.3 Caused by the Inoperability of Both Trains of the Control Room Area Chilled Water System</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Units 1 and 2 were in Mode 1 at 100% power. Event Description: On January 12, 2010, while performing annual maintenance on the "A" Control Room Area Chilled Water System (CRACWS) chiller, the "B" CRACWS chiller developed a refrigerant leak on the hot gas bypass piping and was declared inoperable. With both trains of CRACWS inoperable, both McGuire units entered Technical Specification Limiting Condition for Operation (LCO) 3.0.3 and initiated a shutdown of both units. Following a temporary repair to the "B" chiller, McGuire requested and received a Notice of Enforcement Discretion (NOED) and terminated the two unit shutdown. Event Cause: The cause of the "B" CRACWS chiller hot gas bypass piping leak was vibration produced by normal chiller operation. Contributing to the leak was additional vibration produced by a 2007 chiller controls modification, piping corrosion, and residual piping stresses produced by a 2009 base metal weld repair. Corrective Actions: Replace the hot gas bypass piping on both CRACWS chillers. Reduce the piping vibration on the CRACWS chillers to acceptable levels. Inspect and coat the chiller piping susceptible to corrosion.
3692010002 | McGuire 1 | 05/12/2010 | 06/30/2010 | ML10188027 | <strong>Unit 1 "A" Containment Spray (NS) Pump Past Inoperable due to an Oil Leak from Pump Motor Oil Sight Glass</strong><br /><i>Abstract:&nbsp;</i>On April 29, 2010 the Unit 1 "A" Train Containment Spray (NS) pump was declared inoperable upon discovery of an oil leak on the Pump Motor Lower Bearing Sight-glass. The condition was entered into the site's corrective action program and a subsequent evaluation completed May 12, 2010, determined reasonable assurance of past operability could not be justified for a period of fourteen days. It was determined the event met 10 CFR50.73 reporting criteria as indicated in Section 11 (above). Actions taken to correct the oil leakage prior to affecting the component's mission time were not adequate due to a failure to recognize or determine the existing condition correctly. Applicable procedures will be revised to provide additional information when making oil additions via oil sight glasses based on sight glass design and sealing characteristics, list the actions required in case low oil level is discovered, and provide additional information for components bound by mission time requirements.
3692010003 | McGuire 1 | 06/12/2010 | 08/11/2010 | ML10230038 | <strong>Dropped Control Rods Resulting in Completion of a Technical Specification Required Shutdown and Actuation of the Reactor Protection Svstem and Auxiliarv Feedwater Svstem.</strong><br /><i>Abstract:&nbsp;</i>Event Description: On June 10, 2010, Unit 1 Shutdown Bank "B" Rod N7 dropped fully into the core. On June 12, 2010, Unit 1 Shutdown Bank "B" Rod J13 dropped fully into the core while Rod N7 was still dropped. As directed by procedures, Operators initiated a Unit 1 Reactor trip by manually actuating the Reactor Protection System. Subsequent to tripping Unit 1, the 1A and 1B Motor Driven Auxiliary Feedwater Pumps were manually actuated to maintain Steam Generator levels. Event Cause: A regulation card in a Rod Control System Power Cabinet experienced an intermittent connection due to a degraded solder joint. This intermittent connection caused a drop in the current supply to the Control Rod Drive Mechanisms (CDRMs) for Unit 1 Shutdown Bank "B" Rod N7 and Unit 1 Shutdown Bank "B" Rod J13. Current dropped to levels which allowed the CRDM grippers to drop Rods N7 and J13 into the core. Corrective Actions: The degraded Rod Control System Power Cabinet regulation card was replaced. Additional preventative maintenance strategies will be evaluated for identifying degraded solder joints on cards in the Rod Control System Power Cabinets. Replacement of selected cards in the Rod Control System Power Cabinets with an upgraded card will be evaluated.
3692010004 | McGuire 1, McGuire 2 | 09/27/2010 | 11/23/2010 | ML10340008 | <strong>Improper Technical Specification Application When Diesel Generator Starting Air Receivers Cross-Tied</strong><br /><i>Abstract:&nbsp;</i>The two sub-trains of the starting air system for each diesel generator had been cross-tied during maintenance activities without complying with Technical Specification (TS) Required Actions. This event was determined reportable per 10 CFR 50.73(a)(2)(i)(B) - Operations Prohibited By Technical Specifications. The root cause was an inadequate 10 CFR 50.59 Evaluation associated with a Nuclear Station Modification (NSM) in 1994. The contributing causes were deviation from Westinghouse Standard TS (NUREG-1431), misapplication of TS Condition, vague Safety Evaluation wording, and inadequate Updated Final Safety Analysis Report (UFSAR). This event is considered to have no significance with respect to the health and safety of the public. Significant corrective actions include evaluating additional NSMs and associated 10 CFR 50.59 Evaluations, revising the affected UFSAR, and submitting a License Amendment Request to revise the affected Technical Specification.
3702010001 | McGuire 2 | 01/19/2010 | 03/26/2010 | ML10097004 | <strong>Loose connection in a panel board serving a Solid State Protection System Train concurrent with redundant train maintenance could have prevented fulfillment of a safety function.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Units 1 and 2 were in Mode 1 at 100% power. Event Description: From approximately 1907 hours to 1938 hours on January 19, 2010, the Control Room received intermittent annunciators and bi-stable indications Investigation determined this was due to power cycling off and on to some loads served by 120VAC Vital I&C panel board 2EKVA. One load affected was Channel 1 of Train A of the Unit 2 Solid State Protection System (SSPS) While power was removed from this Channel, Train A would have been incapable of generating an Engineered Safety Features Actuation System signal. Concurrent with the cycling of power to Channel 1 of Train A of Unit 2 SSPS, the 2B Train of Containment Spray (NS) and the 2B Diesel Generator (DG) were inoperable for scheduled maintenance. The above conditions could have delayed initiation of the Unit 2 safety injection DG actuation and the Unit 2 NS safety functions. McGuire is reporting this as a condition that could have prevented. fulfillment of a safety function needed to mitigate the consequences of an accident. Event Cause: Fabrication deficiency caused a loose bus bar connection in panel board 2EKVA which rendered Train A of Unit 2 SSPS inoperable concurrent with maintenance on the redundant train. Corrective Actions: Moved Unit 2 SSPS Train A Channel 1 power to another 2EKVA breaker. Maintenance procedure for Unit 1 & 2 120VAC/125VDC Vital I&C panel boards was revised to ensure these panels are adequately inspected for loose bus bar connections. Inspections of panel connections are planned and, based upon results, replacement of these panel boards will be considered.
3702010002 | McGuire 2 | 10/22/2010 | 05/10/2011 | ML11138A02 | <strong>Unit 2 Nuclear Service Water System "A" Train Past Inoperable due toFailed Strainer Differential Pressure Instrument.</strong><br /><i>Abstract:&nbsp;</i>On October 22, 2010, it was determined air in-leakage past a threaded fitting on the low pressure side of the Differential Pressure (DP)loop affected the past operability of the Unit 2 "A" (2A) Train of Nuclear Service Water System (NSWS). The root causes were improper assembly of a tube fitting during preventive maintenance and inadequate post maintenance test (PMT). The fitting threads were galled during assembly which provided a leak path during vacuum conditions. The PMT required a visual leakage inspection for affected pressure boundaries at normal system pressure which was not adequate for operation at vacuum conditions. Immediate action was taken to repair the fitting and restore 2A NSWS Train to operable. Actions planned to prevent recurrence includes development of PMT at vacuum conditions (i.e., high system flows) and revising station processes to ensure the revised PMT (or functional verification) is performed after restoring disconnected field process tubing or after any suspected field process tubing leaks.
3732010001 | LaSalle 1, LaSalle 2 | 03/03/2010 | 04/28/2010 | ML10118033 | <strong>Unauthorized Individual Gained Access to the Protected Area</strong><br /><i>Abstract:&nbsp;</i>An unauthorized person gained access to the protected area. The individual's badge had been previously cancelled, but was able to access the protected area through the Main Access Facility (MAF). The individual was escorted out of the protected area by security. An ENS one hour notification was completed per 10 CFR 73.71(b)(1). This event affects both units due to the shared protected area. The safety consequences of this event were minimal. The unauthorized individual displayed no malevolent intent to gain access. The apparent cause evaluation determined that an authorized individual unlocked the turnstile, but stepped away for assistance. The authorized individual failed to perform proper human performance techniques for self-check. While the authorized individual was seeking assistance, an unauthorized individual accessed the protected area via the unlocked turnstile. Actions taken include coaching the individual on the proper human performance techniques when using vital doors or security access turnstiles. This report is being issued based on the requirements of 10 CFR 73.71(d), Reporting of Safeguards Events within 60-days of the event.
3732010002 | LaSalle 1, LaSalle 2 | 07/26/2010 | 09/24/2010 | ML10267003 | <strong>Division 1 Diesel Generator Cooling Water Pump Trip and Auto Re-Start due to Shutdown Attempt with Remote Automatic Start Signal Present</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2010, at 1819 CDST, with Unit 1 in Mode 1 (Power Operation), the Division 1 Diesel Generator Cooling Water Pump (DGCWP) unexpectedly restarted after being secured. The DGCWP provides the cooling water to its associated Diesel Generator (DG) and ECCS cubicle area coolers, and the Low Pressure Core Spray (LPCS) pump motor cooler. The Division 1 DGCWP was being shutdown following completion of required surveillances on related supported systems. The DGCWP was secured using the main control room pump control switch. When the switch was returned to the standby position, the DGCWP breaker received an automatic lock-out. The automatic lock-out occurred as a result of the circuit being designed to preclude continuous breaker cycling (anti-pumping). When the operator reset the breaker by placing the control switch momentarily to stop and back to standby, the DGCWP automatically restarted. This was because the LPCS/Reactor Core Isolation Cooling (RCIC) corner room cooling fan was still running following the completed surveillances, and when the fan is running, an automatic start signal is provided to the DGCWP. The operator was unaware that the LPCS/RCIC corner room cooling fan was still running. The cause of this event was a latent procedure error in that the steps being performed failed to require verification that all of the remote components that send start signals to the DGCWP were secured. Procedure revisions have been initiated for procedures that direct securing DGCWPs to ensure that all remote components that provide an automatic start signal to the DGCWP have been secured.
3732010003 | LaSalle 1, LaSalle 2 | 10/28/2010 | 09/08/2011 | ML11252142 | <strong>Standby Liquid Control Test Tank Seismic Analysis</strong><br /><i>Abstract:&nbsp;</i>As part of an NRC Component Design Bases Inspection, the seismic analysis of the Unit 1 and Unit 2 Standby Liquid Control (SBLC) system test tanks was challenged. On October 27, 2010, the operability determination process was initiated and Engineering began verifying design data and calculations. During this review, on October 28, 2010, Engineering determined that the historical calculation used the wrong formula in determining the test tank's natural frequency. The consequence is that if the test tank is filled with water, the possibility exists that the test tank could fall over during a seismic event and adversely affect both trains of SBLC. Calculations confirm that with the test tanks empty, the mounting is seismically qualified. The SBLC test tanks on both units had been drained of water on October 27, 2010, and thus both Unit 1 and 2 SBLC systems were fully operable upon discovery of the calculation error. This error occurred in 1981 and therefore is historical. The cause of the event was less than adequate (historical) design information and analysis. The current process for performing design analyses requires an owner review of vendor calculations. An acceptance review of the vendor calculations prior to issuing the document is procedurally required. Corrective actions included performing a Engineering evaluation to support the seismic analysis of the SBLC test tank mounting with the test tank drained, and draining of the test tank.
3742010001 | LaSalle 2 | 09/25/2010 | 11/24/2010 | ML10336004 | <strong>High Pressure Core Spray System Declared Inoperable due to Failed Room Ventilation Control Relay</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2010, at 0210 hours CDT, the Unit 2 Rounds Equipment Operator reported that the High Pressure Core Spray (HPCS) switchgear room supply fan 2VD05C and the electrically interlocked exhaust fan 2VD07C were not running. All Unit 2 Division 3 equipment was declared inoperable and unavailable. Because HPCS is a single train system, this occurrence is reportable under 10 CFR 50.72(b)(3)(v)(D) and 10 CFR 50.73(a)(2)(v)(D) as an event or condition that alone could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Troubleshooting identified that the switchgear cubicle control relay had failed. The relay was replaced, and post maintenance testing was completed satisfactorily. The cause was determined to be age-related failure due to the lack of time-based replacement preventative maintenance, which was due to improper duty cycle classification. Corrective actions include reclassifying the subject relays to high duty cycle and instituting time-based replacements.
3822010001 | Waterford 3 | 01/13/2010 | 02/23/2010 | ML10056003 | <strong>Spent Fuel Pool Cooling Single Failure</strong><br /><i>Abstract:&nbsp;</i>This licensee event report identifies an unrecognized single failure vulnerability associated with FS ILS2000 A2 (FUEL POOL WATER LOW LEVEL SWITCH). Spent Fuel Pool (SFP) Level Switch (FS ILS2000 A2) supplies the low level trip function for both Spent Fuel Pool cooling pumps and the SFP purification pump. The failure of the level switch or loss of power to the level switch will cause all three pumps to trip with no restart capabilities. A temporary modification was created that would allow operations to defeat the level switch interlock and restore SFP cooling in the unlikely event of a failure or loss of power of this switch. On January 13, 2010 as a result of continued evaluation of this condition, it was recognized that this condition is reportable under 10CFR50.73(a)(2)(ii) (Degraded or Unanalyzed Condition) and 10CFR50.73(a)(2)(vii) (Common Cause Inoperability of Independent Trains or Channels) due to one failure being able to disable the safety function of both SFP cooling pumps. The Updated Final Safety Analysis Report (UFSAR) and General Design Criteria (GDC) require the SFP cooling pumps to meet single failure independence. No actual FS ILS2000 A2 failure occurred, this design condition was identified during work preparation.
3822010002 | Waterford 3 | 02/23/2010 | 04/22/2010 | ML10116003 | <strong>Main Feedwater Isolation Valve B exceeded allowed outage time due to tubing connection failure</strong><br /><i>Abstract:&nbsp;</i>On 2/23/2010 maintenance personnel were performing a scheduled calibration of a,nitrogen accumulator pressure switch associated with Main Feedwater Isolation Valve (MFIV) B. Shortly after isolating the instrument valve, the associated instrument side tubing blew out of a tubing fitting. Subsequent examination identified that the compression fitting had not been properly installed and tightened. In addition, loose bracket mounting bolts were identified on the instrument isolation valve just upstream of the compression fitting Since the instrument line had been isolated prior to the tubing connection failure, no loss of nitrogen occurred from the associated accumulator. MFIV B remained operable with the pressure switch isolated. An evaluation of past operability determined that the degraded condition of the tubing connection while in service would have caused a past inoperable conditn that would. exceed the Technical Specification allowed outage time. Corrective actions include replacement of the compression fitting and tightening of the bracket mounting bolts.
3822010003 | Waterford 3 | 02/08/2010 | 05/20/2010 | ML10144019 | <strong>Worn Fuel Oil Line on A Train Emergency Diesel Generator Caused by Inadequate Mounting Clamp</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2010, at approximately 14:47, with the plant operating at 100% power (Mode 1), Waterford 3 commenced a post-surveillance cooldown on Emergency Diesel Generator A (EDG A) [EK]. The local Nuclear Auxiliary Operator noted the one inch main fuel oil supply line support clamp was loose and the supply line tubing had circumferential wear indication under the clamp. An engineering review of the wear indication found the wall thickness at 0.0132" remaining from a nominal wall thickness of 0.060". An Engineering calculation determined a tubing wear rate that showed a design basis 30 day run by the EDG A would not have been met since approximately August 31, 2005 without mitigating actions. Since August 2005, there were several occurrences when EDG B was also out of service. This condition represents operation not in compliance with Technical Specifications and a safety system functional failure. Additionally, Technical Specification (TS) requirements were not met when the steam driven EFW pump was periodically unavailable while EDG A was in this condition. The tubing was replaced on February 10, 2010. The event did not compromise the health and safety of the general public.
3872010001 | Susquehanna 1 | 03/15/2010 | 05/14/2010 | ML10145039 | <strong>Unit 1 Secondary Containment Bypass Leakage Exceeded</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2010 during the Susquehanna Unit 1 16th Refueling and Inspection Outage, it was determined that the as-found minimum pathway Secondary Containment Bypass Leakage (SCBL) Technical Specification (TS) limit had been exceeded during regularly scheduled Local Leak Rate Testing (LLRT). At the time the limit was surpassed, a LLRT was being performed on the Unit 1 'B' Residual Heat Removal Containment Spray penetration. The tested containment isolation valve (HV151F016B) was leaking 4,515 sccm. When the 4,515 sccm leakage through HV151F016B was added to the combined as-found minimum pathway SCBL calculation it equaled 7,977 sccm (16.9 scfh). This total as-found minimum pathway leakage exceed the Technical Specification limit of 7,079 sccm (15 scfh). This event is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(A) because the total as-found minimum pathway SCBL leakage rate exceeded the Technical Specification limit. There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event since the dose consequences from the additional leakage would not have exceeded regulatory limits.
3872010002 | Susquehanna 1 | 04/22/2010 | 02/01/2012 | ML12033A02 | <strong>Automatic Reactor Scrams Occur During Post-Modification Testing of the Digital Feedwater Integrated Control System</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2010, at 1051 hours, Susquehanna Steam Electric Station Unit 1 experienced an automatic reactor scram, from 32% power, on low reactor water level (ENS 45866). The low level condition occurred during planned testing of a new digital feedwater Integrated Control System (ICS), which included upgrades to the feedwater level control system, the reactor feed pump turbine speed controls, and the reactor recirculation speed controls. During testing at low power conditions, the second of three reactor feed pumps (RFP) was placed in automatic flow control mode for the first time with the goal of parallel automatic operation of two RFPs. A reactor water level transient occurred when the second RFP began feeding into the reactor. The resulting concurrent flow reduction of both RFPs quickly lowered water level to the low level scram setpoint. Corrective actions were taken to adjust the ICS speed controller gain and master feedwater level controller gain. At approximately 2301 hours on May 14, 2010, Unit 1 automatically scrammed from 66% power due to a main turbine trip on high reactor water level (ENS 45930). The high level condition occurred during additional planned testing of the digital ICS, which involved the trip of one of the four condensate pumps. The high reactor water level transient was attributed to a large feedwater flow/steam flow mismatch caused by insufficient gain on the ICS master feedwater level control system master water level controller in response to large transient conditions. Corrective actions were taken to increase the system gains for large transients using "gap" control on the ICS level controller and flow controller. The root cause analyses concluded the process used in the development and implementation of the ICS gains/tuning factors did not adequately use risk considerations, independent oversight, analytical tools and techniques, operating experience and appropriate resource management. Also, the station's post-event analysis of the April scram did not adequately evaluate the extent of condition or extent of cause and represents a missed opportunity to prevent the May scram. Planned corrective actions include providing guidance for developing and implementing control system tuning parameters, using the plant simulator for non-training purposes and post-event analysis. There were no actual adverse consequences to the health and safety of the public as a result of these events. The RPS responded as expected. All control rods fully inserted. These events are being reported under 10 CFR 50.73(a)(2)(iv)(A) due to the actuation of the RPS and RCIC.
3872010003 | Susquehanna 1 | 07/16/2010 | 02/28/2012 | ML12060A07 | <strong>Unit 1 Manual Reactor Scram due to Leakage from the Unit 1 Circulating Water System and Subsequent Flooding of the Unit 1 Condenser Bay</strong><br /><i>Abstract:&nbsp;</i>On July 16, 2010, at approximately 1641 EDT, the Susquehanna Steam Electric Station Unit 1 reactor was manually scrammed due to a large unisolable circulating water system leak in the main condenser area. All control rods fully inserted. Reactor water level lowered to -28 inches causing Level 3 (+13 inches) isolations. The Integrated Control System (ICS) Feedwater Level Control (FWLC) system detected the scram condition and automatically entered setpoint setdown mode, which placed the non-lead Reactor Feedpumps (RFPs) in idle mode, and initiated transition to startup level control mode. During this transition, ICS FWLC did not transfer to single element control due to a higher than expected steam flow signal, and concurrent feedwater flow oscillations resulted in an increase in reactor water level. Reactor water level reached Level 8 (+54 inches) which resulted in the trip of all three RFP turbines, the High Pressure Coolant Injection (HPCI) system, and the Reactor Core Isolation Cooling (RCIC) system to shutdown. The circulating water system was shut down and the main steam isolation valves were manually closed. Reactor water level was restored and maintained within normal operating range using the RCIC system. Pressure control was initiated using the HPCI system in the pressure control mode. All safety systems operated as expected. No steam relief valves opened. It was estimated that approximately one million gallons of water leaked into the condenser bay area. The cause of the unisolable circulating water system leak was due to the condenser waterbox manway gasket rolling out of position. Investigation concluded that the gasket reached the point where it could no longer maintain system pressure and rolled out of position due to gasket creep (i.e., inadequate gasket preload to maintain joint integrity). The gasket extrusion was the result of inadequate preload, rather than a system pressure transient or a material defect. Corrective actions taken for Unit 1 included inspection and replacement of gaskets. The root causes were determined to be less than optimal system manway and isolation valve design, less than adequate risk informed decision making resulted in the failure to adequately address previous Circulating Water (CW) system leaks, and inadequate procedure quality, use and adherence resulted in the loss of CW pressure boundary integrity and inadequate mitigation of the CW leak. Planned actions to prevent recurrence included revising procedures to address gasket installation procedure deficiencies, revising procedures to address isolating individual waterboxes, and developing revisions to processes and procedures to improve risk informed decision making. There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) due to the manual actuation of the RPS, RCIC and HPCI system.
3872010004 | Susquehanna 1 | 03/11/2010 | 08/08/2013 | ML13221A52 | <strong>"D" Outboard Main Steam Isolation Valve Leakage - 2010</strong><br /><i>Abstract:&nbsp;</i>On March 11, 2010, during local leak rate testing (LLRT) of Main Steam Line Isolation Valve (MSIV) Penetration Number X-7D, the Unit 1 "D" Main Steam Line Boundary the Unit 1 "D" Outboard Isolation Valve exceeded 71 standard liters per minute. This condition, which was considered to have existed during the previous operating cycle, was a failure to meet Technical Specification (TS) 3.6.1.3. <br><br> The cause of the event was a valve body seat with a poor contact area. This coupled with the X-7D as-left penetration leakage having minimal margin to the TS limit, contributed to the as-found testing failure in the next refueling outage. Root causes included: 1) Station Engineering management and supervision not exercising Technical Authority over the Appendix J Program, 2) the Leak Rate Test Program procedure not establishing "maintenance limits" for As-Found and As-Left MSIV LLRT test results, and 3) the station reportability procedure inappropriately stating that exceeding the MSIV 100 scfh leak rate limit is not reportable. <br><br> Key corrective actions taken include revising the Susquehanna conduct of station engineering procedure, the leak rate testing program procedure, and the station reportability procedure. <br><br> There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3892010001 | St. Lucie 2 | 01/06/2010 | 03/08/2010 | ML10075024 | <strong>Control Room Habitability Impacted by General Atomics Model RM-80 Radiation Monitoring System Firmware Anomaly</strong><br /><i>Abstract:&nbsp;</i>On January 6, 2010, St. Lucie Unit 2 was operating in Mode 1 at 100% power when the Onsite Review Group (ORG) concluded that the General Atomics 10 CFR 21 Notification - "General Atomics Model RM-80 Radiation Monitoring System", identified on June 28, 2009, resulted in a reportable condition for St. Lucie Unit 2. The Unit 2 RM-80 firmware anomaly experienced during the performance of response time testing of control room outside air intake (CROAI) radiation monitors (RIM-26-61, RIM-26-62, RIM-26-65 and RIM-26-66), could have resulted in the 10 CFR 50.67 limit of 5 rem TEDE to the operators being exceeded and is, therefore, reportable in accordance with 10 CFR 50.73(a)(2)(v). Upon determination by Engineering that the CROAI failure was related to a firmware error, General Atomics was requested to evaluate the problem and determined that the CROAI failure was due to a latent firmware error applicable to the Model RM-80 Radiation Monitoring System and subsequently, issued a 10 CFR 21 notice. Corrective actions included: (1) correction of the firmware error by General Atomics, (2) updating of CROAI installed firmware and successful testing of all four CROAI radiation monitoring channels, and (3) an extent of condition review determined no immediate operability concerns existed for the other safety-related or Technical Specification monitors.
3892010002 | St. Lucie 2 | 04/15/2010 | 06/14/2010 | ML10173055 | <strong>Unit 2 Manual Reactor Trip due to Moisture Separator Re-heater Safety Valve Lift</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2010, St. Lucie Unit 2 was operating in Mode 1 at 100% power when the Unit was manually tripped due to premature lifting of the 2B moisture separator re-heater (MSR) safety valve. The Unit initially commenced a rapid down power evolution as a result of the lifting safety valve followed by a manual reactor trip at approximately 95% power. All control element assemblies (CEA) fully inserted on the trip and all systems functioned as designed; the plant was stabilized at normal operating temperature and pressure in Mode 3. A non- emergency notification to the NRC was made due to manual reactor protection system (RPS) actuation and auxiliary feedwater (AFW) system actuation. The primary root cause of the event was determined to be less than adequate material (LTA) design for the MSR safety valve pilot spring. Corrective actions included replacement of pilot valve springs for each of the four Unit 1 and 2 MSR safety valves (MSRV) with either new (CR) alloy steel or Inconel springs prior to startup of Unit 2 and ensure that replacement of MSRVs for Unit 1 are procured with appropriate spring materials and drawings to reflect the same.
3902010001 | Watts Bar 1 | 05/21/2010 | 07/20/2010 | ML10209014 | <strong>Reactor / Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2010 at 1936 hours with Watts Bar Nuclear Plant, Unit 1 at 100 percent rated thermal power, the reactor tripped automatically in response to a turbine trip signal generated by closure of the Main Turbine Throttle/Stop Valves. Following reactor trip, main feedwater isolation occurred due to reactor trip coincident with low Reactor Coolant System TAVG, which then resulted in automatic startup of the Auxiliary Feedwater System. The most probable cause was determined to be an intermittent failure of a circuit card in the Westinghouse Mark IV Analog Electro-Hydraulic (AEH) turbine control system that caused the servo control valves for all four Main Turbine Throttle Valves to close their respective valves. TVA replaced the suspect circuit cards in the AEH control system. All safety systems performed their required functions in response to this event. This event is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv).
3902010002 | Watts Bar 1 | 08/15/2010 | 10/14/2010 | ML10292054 | <strong>Valid Auxiliary Feedwater Actuation During Power Reduction for Planned Maintenance</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2010, Watts Bar Nuclear Plant (WBN) Unit 1 was at 20% reactor power. The Main Feedwater (MFW) pump B was manually tripped as part of a power reduction in preparation for taking the Main Turbine offline to perform planned repairs. The plant operators observed an unplanned isolation of the Intermediate Pressure Heater string and responded by manually tripping the MFW pump A before it experienced a loss of suction. Additionally, Operations personnel manually started the Auxiliary Feedwater (AFW) System. Reactor power was further reduced and Mode 2 was entered. The cause of this event was a procedural inadequacy in the Operations procedure for turbine trips. The procedure did not contain information to address the time critical nature of manually placing the heater drain tank level control valves in bypass, which led to the unplanned heater string isolation. Corrective actions for this event include revising the procedure to include time constraints. This event is being reported as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A) because AFW manual actuation was valid and was not part of a pre-planned sequence during reactor operation.
3902010003 | Watts Bar 1 | 11/14/2010 | 01/13/2011 | ML11168006 | <strong>Manual Reactor Trip due to High Main Bank Transformer Temperature</strong><br /><i>Abstract:&nbsp;</i>At 06:45 Eastern Standard Time (EST) on 11/14/2010, Watts Bar Nuclear Plant, Unit 1 initiated a rapid load reduction in response to rising oil temperature in Main Bank Transformer 1A (MBT-1A). The high oil temperature in MBT-1A was attributed to a loss of forced-oil-air cooling due to a faulted motor starter which overloaded the control power transformer (CPT) that provided control power to the main bank cooling circuits. Loss of the CPT de-energized all six main bank coolers. Each main bank cooler has a circulating oil pump and four fans. The load reduction rate was not sufficient to reverse the temperature rise, so a manual reactor trip was initiated at 06:52 EST to prevent exceeding the 80oC maximum oil temperature operating limit. Following the reactor/turbine trip the plant entered the appropriate shutdown procedures to stabilize the plant at Hot Standby Conditions. No overcooling transient occurred and no safety injection signals were initiated for this event. The damaged components were replaced and additional corrective actions are being implemented to prevent recurrence. Corrective action included changes to the maintenance procedures and design changes to the main bank cooler circuits to eliminate single point vulnerabilities, to the extent practical. This event is reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv).
3952010001 | Summer 1 | 04/27/2010 | 06/28/2010 | ML10181007 | <strong>Reactor Building Cooling Units Reduced Air Flow Rate below Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2010 a past operability determination identified that the Reactor Building Cooling Units (RBCUs) air flow rate had previously been below the minimum required by the Technical Specification (TS). Although filters in the RBCU had been replaced to increase the air flow rate; the investigation of this issue determined that a non-conservative filtration area factor was used in previous calculation of the air flow rate. A re-calculation of the air flow rates using a corrected filtration area factor was performed for each RBCU. As a result, RBCUs XAA0001A and XAA0002A had air flow rates below the required Technical Specification range between Refuel 16 and 18. RBCUs XAA0001B and XAA0002B had air flow rates below the Technical Specification range between Refuel 16 and 17. This was a violation of the Limiting Condition for Operation for TS 3.6.2.3 and 3.6.3. Filters had been replaced and the air flow rates were determined to be satisfactory using the corrected filtration area factor prior to the end of Refuel 18. The cause of this event was the use of a non-conservative filtration area factor for calculation of the air flow rate.
3952010003 | Summer 1 | 09/25/2010 | 11/22/2010 | ML10330003 | <strong>Inadequate Procedural Guidance Results in Violation of Technical Specification 3.0.4 During Plant Startup</strong><br /><i>Abstract:&nbsp;</i>ABSTRACT: On September 25, 2010 at 1354, VCSNS violated Technical Specifications sections 3.0.4 and 3.7.1.6 by entering Mode 1 without ensuring operability of all three Feedwater Isolation Valves (FWIV). The feedwater system has three pneumatic actuated feedwater isolation valves. Prior to entry into Mode 1 the valves are opened one at a time to allow accumulator air pressure to increase greater than 500 psi, minimum pressure required for operability. When the third valve was opened, the operating crew did not wait until the accumulator air pressure was restored to operable prior to Mode 1. The apparent cause was identified as a failure to provide proper procedural instructions to ensure the FWIV accumulator operating pressures are verified to be greater than the minimal pressure for operation prior to Mode 1 entry. As a corrective action VCSNS will revise the General Operating Procedure (GOP) 4A, "Power Operation Mode 1 Ascending" to verify the FWIV actuator pressure is above the minimum pressure for operability prior to entering Mode 1. 10CFR50.73(a)(2)(1)(B) Condition prohibited by Technical Specification.
3972010001 | Columbia | 06/30/2010 | 08/30/2010 | ML10257139 | <strong>Failure of a Secondary Containment Isolation Valve to Fully Close</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2010, Columbia Generating Station (Columbia) discovered a condition prohibited by Technical Specifications (TS). An Air Operated Valve (AOV) diagnostic test was performed on Secondary Containment Isolation Valve (SCIV) FDR-V-219, contained in the Floor Drain Radioactive (FDR) system. Results showed that the valve was not fully closing. This valve must be capable of closing and staying closed to be considered operable. Unknowingly, Columbia has operated with this valve inoperable since 1994, a condition prohibited by LCO 3.6.4.2, Conditions A and C. Upon discovery of the inoperable status, the TS required actions for this condition were completed. Subsequently, the valve stroke has been adjusted and the valve has been declared operable. The direct cause occurred on July 4, 1994. During the replacement of the valve actuator for SCIV FDR-V-219, the actuator stroke was set with the valve not fully closed and seated. Position limit switches were set based on the incorrect stroke length and did not provide any indication of the problem to the control room operators. The root cause of the event was inadequate work instructions that failed to verify that the valve was fully closed and seated prior to setting the actuator stroke. No similar events have been reported by Columbia.
3972010002 | Columbia | 12/20/2010 | 02/18/2011 | ML11055018 | <strong>LPCS Minimum Flow Valve Failed to Open due to Premature Fuse Failure at the Solder Joint</strong><br /><i>Abstract:&nbsp;</i>This event is being reported under 10 CFR 50.73(a)(2)(v)(D). On December 20, 2010, the low pressure core spray pump was started and the minimum flow valve lost indication. An annunciator was received indicating that the valve had lost power. The three line power fuses for the starter for the motor operator were found to be cleared. The cleared fuses were Cooper/Bussman Fusetron dual-element, time-delay, current-limiting, 600 Volt, 1.25 Amp fuses (model FRS-R-1-1/4). The overload element in each fuse was failed (triggered). Troubleshooting did not reveal any binding within the valve, binding within the motor operator, or sticking or dirty contacts within the starter. An examination of the cleared fuses revealed a poor solder joint in the trigger assembly in one fuse. The cause of this event is premature failure of one of the three fuses from momentary inrush current at a current value under the fuse curve which led to overload and failure of the remaining two fuses. Corrective actions consisted of quarantine of fuses from the same lot as that of the cleared fuses and inspection of fuses in all safety-related motor operated valves in support of ECCS to ensure they were not the same brand fuse of the same 1.25 Amp size from the same lot.
4002010001 | Harris | 11/10/2009 | 01/11/2010 | ML10020027 | <strong>Clearance Error Results in Required Equipment Becoming Inoperable</strong><br /><i>Abstract:&nbsp;</i>A past operability determination completed on November 10, 2009, concluded that on October 18, 2007, during Refueling Outage 14, a clearance rendered 1SW-271, "B" Emergency Service Water (ESW) Discharge Valve unable to remain open when opened. This resulted in the "B" ESW system being non-functional during a time when "B" ESW was required to be functional. At the time of the clearance hang, the plant was shut down in Mode 5 with loops not filled. Technical Specification 3.4.1.4.2 states two Residual Heat Removal (RHR) loops shall be operable and at least one RHR loop shall be in operation. The plant transitioned to Mode 5 with loops filled and Technical Specification 3.4.1.4.1 states at least one RHR loop shall be operable and in operation. While in this mode "A" RHR was made inoperable for testing. For these plant modes, "B" ESW should have been in a functional status. The root cause of this event was determined to be that inaccurate information was communicated with regards to impacted equipment associated with opening breaker DP-1B-SB-33 (Feed to Aux Transfer Panel). Work being performed was to re-wire transfer switch 43T-28SB/822. The review of impacted equipment was focused on equipment affected by the transfer switch contacts instead of equipment impacted by the breaker. Planned corrective actions to prevent recurrence are to revise procedures to alert the clearance preparers and schedulers that due to the complexity of DC power distribution circuitry, removal of DC power within Main or Auxiliary Transfer Panels, Auxiliary Relay Panels (ARPs) or Annunciator Cabinets should not be performed on equipment that is the Protected Train.
4002010002 | Harris | 11/15/2009 | 06/07/2011 | ML11165A22 | <strong>Manual Actuation of the Reactor Protection System due to Hydrogen Seal Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2009, at 100% power, the Harris plant experienced a significant oil leak from the Hydrogen Seal Oil system. A non-licensed operator notified the Main Control Room (MCR) that the handle rotated each shift by Operations on the Air Side Seal Oil self-cleaning strainer became disconnected during manual rotation after approximately 1/4 turn, resulting in the oil leak. Based on this report and due to receipt of a "Turbine Lube Oil Reservoir Low Level" alarm, a decision was made to initiate a unit shutdown. The unit was manually tripped at 22:42 by the Main Control Room Operators. The plant promptly attained normal operation no-load temperature and pressure. Following the reactor trip, when the decision was made to break condenser vacuum, the "B" steam generator Main Steam Isolation Valve (MSIV) failed to fully close on demand from its control switch, but was closed due to field actions at 23:03 by locally isolating instrument air to the valve. The root cause of the Hydrogen Seal Oil leak was that for past maintenance performed on the Air Side Seal Oil strainer, the Graded Approach to Planning and Scheduling instructions and Decision Tree was too generic. When considering the level of planning detail, the work coordination management procedure, WCM-006 does not provide guidance on considering the vulnerabilities to the plant as a result of the work being performed on the component. As a result, the thrust collars that hold the filter handle in place were not installed during past maintenance which allowed the filter handle to eject. Immediate corrective actions were to stabilize the plant, and secure the Turbine Seal Oil/Lube Oil systems to stop the leak. Aqueous foam was sprayed on the Oil to prevent a fire hazard. The oil was cleaned up and the Air Side Seal Oil strainer replaced. Planned corrective actions to prevent recurrence are to revise and implement WCM-006 such that Level "A" work activities (Quality Critical) are classified based on Equipment Classification that could cause a plant transient or shutdown and define other criteria for Level "A" (Quality Critical).
4002010003 | Harris | 09/16/2010 | 11/15/2010 | ML10327005 | <strong>Condition Prohibited by Technical Specifications When Non-seismic System Was Aligned to Refueling Water Storage Tank</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2006, procedure OP-116.01, Fuel Pool Purification System, was revised to permit purification of the Refueling Water Storage Tank (RWST) using the non-seismic Fuel Pool Purification system in Modes 1-4 without declaring the RWST inoperable and entering the Technical Specification (TS) Limiting Condition for Operation (LCO) action statement. In 2010, the NRC Resident Inspector questioned this practice, which led to the conclusion that Harris Nuclear Plant should have obtained prior NRC approval to perform this activity. The root cause investigation concluded that ambiguous procedural guidance resulted in a misinterpretation of requirements. Corrective actions include procedure revisions to eliminate RWST purification in Modes 1-4 and clarification of guidance regarding the impact of proposed activities on the design and licensing bases.
4002010004 | Harris | 11/05/2010 | 01/04/2011 | ML11011016 | <strong>Valid Actuation of B Emergency Diesel Generator due to Loss of 'B-SB' 6.9kV Safety Bus</strong><br /><i>Abstract:&nbsp;</i>At 1:04 AM EDT on November 5, 2010, during refueling outage 16, maintenance personnel were performing Post Maintenance Testing (PMT) following replacement of the B main generator lockout relay when the 6.9 KV B-SB Emergency Bus spuriously de-energized, resulting in the automatic starting of the 1B-SB Emergency Diesel Generator (EDG). This temporary interruption in power to the bus also resulted in the loss of the B Residual Heat Removal (RHR) pump and associated shutdown cooling for approximately 3 minutes. Safety systems responded as expected during the event. The 6.9 KV 1A-SA Emergency Bus remained available from both off site power and the 1A-SA Emergency Diesel Generator throughout the event. Loss of the 6.9KV 1B-SB Emergency Bus resulted in a temporary loss of power to the B RHR pump which was the only decay heat removal system in service at the time but it was recovered manually after the B EDG re-energized the bus. The root cause of the event is the lack of guidance in plant procedure PLP-400, Post Maintenance Testing, for establishing PMT instructions for complex relay replacements. Corrective action will be to revise PLP-400 to establish guidance for PMT development when replacing complex relays such as 86 UV or 86 lock out relays and implement the use of improved test leads.
4002010005 | Harris | 11/09/2010 | 12/30/2010 | ML11005007 | <strong>Emergency Core Cooling System (ECCS) Inoperable for Greater than Time Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 9, 2010, 1RH-25, Residual Heat Removal (RHR) Header 'A' Isolation Valve to Charging Safety Injection Pump (CSIP) Suction, and 1RH-63, RHR Header 'B' Isolation Valve to CSIP Suction, were both de-energized as a result of performing Operating Procedure OP-111, Section 7.2, Restoring the RHR System to Emergency Core Cooling System (ECCS) Mode. This caused both trains of ECCS to be inoperable. The plant was in Mode 4 with one train of ECCS required to be operable. It was not recognized that both trains of ECCS were inoperable. Transition from Mode 4 to Mode 3 occurred while in this condition. In Mode 3 both Trains of ECCS were required to be operable. These conditions are prohibited by the Harris Nuclear Plant (HNP) Technical Specifications and are reportable under 10 CFR Part 50.73 (a)(2)(i)(B). They are also reportable under 10 CFR Part 50.73(a)(2)(v)(D). The root cause is that OP-111, Section 7.2.2 had incorrect steps that required the breakers for 1RH-25 and 1RH-63 be opened. The primary contributing cause is a lack of human performance tool usage by operators performing OP-111. Immediate corrective actions included promptly closing 1RH-25 and 1RH-63 circuit breakers and following operating procedure lineup checks. Additionally, OP-111, Residual Heat Removal System, was revised to correct the steps that required the breakers for 1RH-25 and 1RH-63 be open in Section 7.2.2.
4102010001 | Nine Mile Point 2 | 01/07/2010 | 05/05/2010 | ML10134012 | <strong>Reactor Scram Due to Inadvertent Actuation of the Redundant Reactivity Control System During Maintenance</strong><br /><i>Abstract:&nbsp;</i>At 0100 on January 7, 2010, Nine Mile Point Unit 2 scrammed from full power following receipt of an invalid Low-Low Reactor Pressure Vessel (RPV) level signal (Level 2). The Level 2 signal caused a Division II Redundant Reactivity Control System (RRCS) initiation signal that caused an Alternate Rod Insertion (ARI) scram initiation and a trip of the reactor recirculation pumps. The Level 2 signal also initiated Reactor Core Isolation Cooling (RCIC). The invalid RPV Level 2 signal was caused by maintenance technicians performing fill and vent activities on Residual Heat Removal (RHS) instrumentation as part of a planned maintenance window for Division II RHS. The direct cause of this event was venting of RHS instrumentation during planned maintenance. The root cause of this event is, Operations Management has not sufficiently monitored and reinforced standards associated with plant impact assessment during work planning. To address this issue, additional training will be provided to personnel performing the Operations planning functions. In addition, quarterly Management Review Meetings will be implemented for Operations planning personnel to provide continual reinforcement of the standards and provide for monitoring and feedback. The operating procedure involved in this event will be revised to provide precautions and limitations when venting.
4132010001 | Catawba 1, Catawba 2 | 02/01/2010 | 03/31/2010 | ML10092006 | <strong>Technical Specification Violation Associated with Failure to Perform Offsite Circuit Verification</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2010, Technical Specification (TS) 3.8.1, "AC Power Sources - Operating" was violated for Units 1 and 2. The violation occurred following the racking out.of a 6.9 kV bus tie breaker for preventive maintenance. Due to unclear TS Bases, plant personnel did not recognize that with the tie breaker racked out, one offsite circuit was inoperable. Licensed Operations personnel failed to adequately evaluate and perform the required actions associated with the inoperability of the offsite circuit in a timely manner. Surveillance Requirement (SR) 3.8.1.1 was not performed within one hour as required to verify that the other offsite circuit was operable. SR 3.8.1.1 was subsequently performed for both units and the tie breaker was subsequently racked back in, thereby restoring the inoperable offsite circuit to operable status. Planned corrective actions include enhancing the affected TS Bases. Throughout this event, all 4.16 kV Engineered Safety Feature buses remained energized and backed by available Diesel Generators. The health and safety of the public were not adversely affected by this event.
4132010002 | Catawba 1 | 02/18/2010 | 04/20/2010 | ML10112066 | <strong>Discovery of Reactor Coolant System Pressure Boundary Leak at Thermowell 1NCTW5850 Seal Weld.</strong><br /><i>Abstract:&nbsp;</i>Event Description: On February 18, 2010, with the unit in Mode 4, a reactor coolant pressure boundary leak was identified at the lA reactor coolant hot leg thermowell 1NCTW5850 seal weld. A cool down to Mode 5 was initiated. Unit Status: At the time of the event, Unit 1 was in Mode 4 at CA, power. Power had been reduced to perform an inspection in containment to identify the source of primary leakage Event Cause: The cause of the failed seal weld was inadequate weld control when the weld was fabricated during initial construction. The weld failure resulted from the presence of a discontinuity involving a metal removal process. Applied loads, primarily pressure loads (high strain - low cycle fatigue) to the weakened area (i.e. location metal removed) contributed to the seal weld failure. Corrective Actions: After reducing primary system pressure, additional weld passes were applied at the seal weld associated with the mechanical joint located between the weld boss and the thermowell Visual examination of the other three Unit 1 hot leg RTD thermowells concluded no sign of leakage.
4132010003 | Catawba 1 | 05/20/2010 | 07/19/2010 | ML10231050 | <strong>Technical Specification Violation due to Failure to Perform Required Actions Following Solid State Protection System Relay Latch Failure</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2010, Technical Specification (TS) 3.3.2, "Engineered Safety Feature Actuation System (ESFAS) Instrumentation" (retroactive) was violated for Unit 1. The violation occurred following the identification of SSPS Train 1A relay K625 to not latch properly when energized during quarterly Auxiliary Safeguards Testing. Plant personnel did not recognize that the latching mechanism associated with the K625 relay affected the Train 1A manual actuation feature for Phase B Containment Isolation. On May 20, 2010, it was identified that the latching mechanism affected the manual actuation feature required per TS 3.3.2, Condition B, Table 3.3.2-1 Function 3.b.1, which was not identified on April 30th. As a result of not identifying that the manual actuation feature was not capable of meeting its function as required by TS, the associated Required Actions were not completed for the Limiting Condition for Operation (LCO). Train 1A of manual Phase B Containment Isolation was subsequently declared inoperable on May 20, 2010 at 13:59. Planned corrective actions include revising the administrative procedure governing the operability process to require the originator, reviewer, and approver to ensure applicable TS Surveillance Requirements are listed and evaluated. This event only affected the operability of one train of the Manual Phase B Containment Isolation Function (Train 1A). The automatic actuation function for Phase B Containment Isolation was not affected by the failure of the K625 relay latching mechanism. The health and safety of the public were not adversely affected by this event.
4132010004 | Catawba 1 | 07/30/2010 | 09/16/2010 | ML10266003 | <strong>Technical Specification Violation Involving Notice of Enforcement Discretion due to Failure of Diesel Generator Engine-Mounted Thermocouple</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2010 at 0200 hours, Technical Specification (TS) 3.8.1, "AC Sources - Operating" and three supported system TS were violated when the 72-hour Completion Time for Diesel Generator (DG) 1A expired. TS 3.8.1, Condition B had been previously entered following the failure of an engine-mounted exhaust thermocouple. The failed thermocouple was subsequently located in the stationary vane of the right bank turbocharger. On the afternoon of July 29, 2010, the NRC granted enforcement discretion concerning TS 3.8.1, Condition B and its supported system TS. The period of enforcement discretion began on July 30, 2010 at 0200 hours and was to be effective for 24 hours. DG 1A was subsequently returned to operable status and all applicable TS Conditions were exited by July 30, 2010 at 0308 hours. This was prior to the time that Unit 1 would have had to be placed in Mode 3 absent the granting of enforcement discretion (0800 hours on July 30, 2010). The thermocouple failure was determined to be due to mechanical fatigue resulting from high-cycle, low-amplitude, cyclic stresses. Planned corrective actions include replacing all exhaust thermocouples in both DGs on Units 1 and 2. The failure of the thermocouple did not affect the ability of DG 1A to perform its safety related function following an event for which emergency AC power would have been required. Therefore, the health and safety of the public were not adversely affected by this event.
4142010001 | Catawba 2 | 01/11/2010 | 03/09/2010 | ML10071008 | <strong>Reactor Mode Change with Limiting Condition for Operation 3.6.6 Not Met in Violation of Limiting Condition for Operation 3 n 4</strong><br /><i>Abstract:&nbsp;</i>As part of an extent of condition review of an issue identified in the Fall 2009 Unit 1 refueling outage, it was discovered that during the Spring 2009 Unit 2 outage, a reactor mode change was made with Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.6 not met, as one train of the Containment Spray (NS) system was inoperable. On April 16, 2009 at 1500, with Unit 2 moving from Mode 5 to Mode 4, LCO 3.6.6 was unknowingly not met, as Surveillance Requirement (SR) 3.6.6.3 could not be met due to a valve 'incapable of automatically opening in accordance with the SR. This mode change was in violation of LCO 3.0.4. The issue was identified during the Fall 2009 Unit 1 refueling outage; however, a risk assessment was performed per LCO 3.0.4.b to allow the mode change, preventing the unit from violating TS. After further evaluation, the Unit 2 event was identified and the condition was determined to be reportable on January 11, 2010. The cause of the event was that unclear TS Bases did not address inoperability of the NS system when the valves in question were de-energized. Corrective Action was taken to make all licensed Operations personnel aware of the lessons learned from this event through an Operations Guide. The Emergency Core Cooling System Water Management License Amendment Request was previously submitted and will remove the requirement for automatic actuation of the NS system, thus allowing for the deletion of SR 3.6.6.3. This incident was determined reportable since the plant was in a condition prohibited by TS. There was no safety significance associated with the event.
4142010002 | Catawba 2 | 10/17/2010 | 12/15/2010 | ML10354009 | <strong>Technical Specification Violation Involving Mode Change with Inoperable Auxiliary Feedwater System Train Due to Closed Pump Discharge Valves</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2010 at 0209 hours, during startup following the completion of the End of Cycle 17 Refueling Outage, Unit 2 entered Mode 4 with the required motor driven train (manually-actuated) of the Auxiliary Feedwater (AFW) System inoperable. The required train's (2A or 2B) pump discharge valve was not in the correct position (open) as required by plant Technical Specifications (TS) and plant procedures. The affected valves were discovered to be in the closed position at 1330 hours. Following the discovery of this event, the affected valves were repositioned to the correct position. The root cause of this event was determined to be that the procedure for AFW System operation was not structured to provide clear guidance to the operators for the status of AFW System alignments for Mode 4 and Mode 3. The affected procedure will be revised to provide clear guidance for the determination of AFW System alignments for entering these modes. Throughout this event, the affected valves were capable of being manually positioned according to plant procedures in the unlikely event of a plant transient requiring a manual start of the AFW System in Mode 4. This event was limited to plant operation in Mode 4 only. The health and safety of the public were not adversely affected by this event.
4162010001 | Grand Gulf 1 | 03/08/2010 | 05/05/2010 | ML10125055 | <strong>Automatic Reactor Scram On Decreasing Reactor Water Level Due To Inadvertent Reactor Feed Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2010, at approximately 1635 hours Central Standard Time (CST), Grand Gulf Nuclear Station (GGNS) was in Mode 1 operating at approximately 100 percent power, when an actuation of the Reactor Protection System (RPS) occurred due to decreasing reactor water level. The cause of the event was the combination of the Reactor Feed Pump B (RFP B) minimum flow valve failing open due to an erroneous signal from flow instrumentation, and the Reactor Feed Pump Turbine A (RFPT A) tripping due to speed demand mismatch caused by control valve linkage binding. One feed pump could not support the reactor feedwater demand, resulting in a reactor scram per design on Reactor Water Level 3 (+11.4 inches narrow range). The appropriate off-normal event procedures were entered to mitigate the transient with all systems responding as designed. All control rods inserted to shut down the reactor. No loss of offsite or Engineered Safety Feature (ESF) power occurred. No emergency core cooling system (ECCS) initiation setpoint was reached and no safety relief valves (SRVs) lifted. The normal heat sink (main condenser) remained available during this event. Reactor water level was restored and maintained by the condensate and feedwater system.
4162010002 | Grand Gulf 1 | 10/14/2010 | 12/13/2010 | ML10348000 | <strong>Control Room Air Conditioning System "B" Tripped on Low Oil Pressure While the 'A' Subsystem was Inoperable for Maintenance Resulting in a Condition that Could Have Prevented the Fulfillment of the Mitigation Safety Function</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2010 at 0422 hours, the Grand Gulf Nuclear Station (GGNS) Control Room Air Conditioning (CRAC) Subsystem B tripped on low oil pressure while CRAC subsystem A was out of service for maintenance. Control Room temperature increased and actions were taken to maintain Control Room temperatures below the Technical Specification (TS) limit of 90 degrees F. Causal analysis identified three possible failure modes for this event which included the intermittent failure of the low oil differential pressure switch due to a less robust design than the original; intermittent failure of one or more loading/unloading mechanisms due to inadequate work instructions; and one or more of the temperature control valves in an open condition or in a more than desired open condition. One contributing cause was identified for inadequate Foreign Material Exclusion controls during maintenance activities on CRAC B. These three probable causes and the contributing cause are addressed in GGNS's Corrective Action Program. Control Room temperature was maintained within limits until a CRAC subsystem was restored. This event is reportable under 10 CFR 50.73(a)(2)(v)(D).
4232010002 | Millstone 3 | 05/17/2010 | 07/15/2010 | ML10334049 | <strong>Automatic Reactor Trip on Lo Lo Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2010 an automatic reactor trip occurred on Millstone Power Station Unit 3 (MPS3) while the unit was in Mode 1, at 17 % power, due to a low steam generator (S/G) water level condition in 'C' S/G caused by the inability of the feedwater regulating bypass valve (FRBV) to properly control S/G levels in automatic or manual control. All control rods fully inserted into the reactor. The auxiliary feedwater system started as designed and maintained S/G level. Safety systems functioned as expected based upon the signals received. There were no radiological challenges as a result of the event. The cause of this event was determined to be the inability of the FRBV control system to control S/G levels at low power operations. The control loop was dynamically tuned and the level controller adjusted to improve system control and performance. A design change is being evaluated to improve the performance of the SG level control system during low power operations. This event is being reported in.accordance.with10 CPR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
4232010003 | Millstone 3 | 05/27/2010 | 07/26/2010 | ML10231050 | <strong>Secondary Containment Rendered Inoperable due to Misaligned Dampers</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2010, with Millstone Power Station Unit 3 (MPS3) at 100% power in Mode 1, during a panel walkdown, operators discovered that two sets of auxiliary building tunnel exhaust dampers were misaligned and open at the same time. This configuration created a pathway from the secondary containment to the outside and rendered secondary containment inoperable. The condition was immediately corrected by placing the dampers in their correct position. The correct damper position should have been established prior to entry into Mode 4 on May 13, 2010. The cause of the misalignment was inadequate communications and instructions for existing procedure status between operating shifts. An apparent cause evaluation was conducted to provide corrective actions, such as revised procedures and log entry requirements in accordance with the corrective action program. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant technical specifications and 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
4232010004 | Millstone 3 | 08/21/2010 | 10/19/2010 | ML10307012 | <strong>Inoperable Turbine Driven Auxiliary Feedwater Pump due to Degraded Relief Valve</strong><br /><i>Abstract:&nbsp;</i>On August 21, 2010, while operating in MODE 1 at 100 percent power, Millstone Power Station Unit 3's (MPS3) Turbine Driven Auxiliary Feedwater (TDAFW) pump was declared inoperable due to leakage past its associated relief valve's seat. This condition was identified while performing Operations Surveillance Procedure SP.3622.3-001. Further investigation revealed that this condition existed on June 30, 2010. The extended period of inoperability of the TDAFW pump is a condition prohibited by the plant's Technical Specification 3.7.1.2 and is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B). The cause of the inoperability of the TDAFW pump was a failed relief valve. The relief valve failure was a consequence of minimal margin between the setpoint of TDAFW Pump Discharge Relief Valve 3FWA*RV45 and Auxiliary Feedwater system pressure while on recirculation flow. The reason the event is reportable is the organization failed to recognize that the TDAFW pump was inoperable. Interim corrective actions included repairing the leaking relief valve. As corrective action to prevent recurrence, design changes are being evaluated to modify the system configuration. To correct the failure to recognize the inoperability of the pump, SP 3622.3-001 was revised to add recirculation flow limits and acceptance criteria in other Operations Surveillance Procedures were reviewed.
4242010001 | Vogtle 1 | 09/26/2010 | 04/27/2011 | ML11118067 | <strong>Breaker Failure Results in 1B Train Containment Cooling System Being Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>During an attempted start of one of the four required I B train containment cooling fans in low speed on October 24, 2010, the fan failed to start. Subsequent troubleshooting revealed that the failure of the fan to start was due to a malfunction of the 480 volt breaker that provides power to the fan motor low speed winding. Based upon the investigation performed, it was determined the breaker had been rendered incapable of closing since September 26, 2010. This was the last time the breaker had been closed and the containment cooling fan had operated in low speed satisfactorily. Consequently, the 1B train of Containment Cooling was Inoperable for approximately 28 days from September 26, 2010 until the failure was discovered on October 24, 2010. Investigation into the breaker failure determined that the cause was due to a screw, that holds a molded plastic cover in place, being inserted too deep. This ultimately led to the screw binding the breaker closure mechanism. Corrective actions included temporarily removing this same screw on other similar breakers to ensure this type of failure could not occur. A design change is planned to provide permanent resolution to this issue.
4252010001 | Vogtle 2 | 02/18/2010 | 04/16/2010 | ML10109006 | <strong>Closure of RHR Injection Valve in Mode 1</strong><br /><i>Abstract:&nbsp;</i>On February 18, 2010 while reviewing a partially completed surveillance procedure for verifying the operability of the Train B shutdown panel transfer function, it was discovered that the motor operated valve (MOV) that isolates Residual Heat Removal (RHR) flow to loops 3 and 4 cold legs had been momentarily stroked closed twice with the unit in Mode 1, on January 5, 2010. Stroking this valve closed in Mode 1 renders both trains of RHR inoperable since the required emergency core cooling flow from the RHR pump(s) cannot be assured, and requires entry into Technical Specification LCO 3.0.3. The cause of this event was due to cognitive error by Operations department personnel applying fundamental knowledge of the Emergency Core Cooling System configuration needed to satisfy Technical Specification Limiting Condition of Operations (LCO) requirements. Also, the procedure used to perform the test was inadequate since at the time the valve was stroked, it did not contain a caution to alert the operator that the valve could not be stroked with the unit at power.
4252010002 | Vogtle 2 | 01/28/2010 | 10/12/2010 | ML10286174 | <strong>High Head Safety Injection Rendered Inoperable Due to an Inadequate Review of Scheduled Work</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2010 an Operations Superintendent was reviewing past performances of the reactor trip breaker surveillance test in preparation for an upcoming surveillance test on a reactor trip breaker. During this review it was determined that on January 28, 2010 the 2B Solid State Protection System (SSPS) Mode Selector switch was placed in Test to perform a surveillance test on the 2B reactor trip breaker. Placing the 2B SSPS Mode Selector switch in Test defeats the Engineered Safety Features (ESF) automatic actuation signal to the 2B train components. At the time 2B SSPS Mode Selector was placed in test, the 2A high head safety injection (HHSI) pump was tagged out of service for planned maintenance. In this configuration, both trains of HHSI were rendered inoperable and outside the Conditions stated in Technical Specification 3.5.2, since neither train would have automatically started on an ESF actuation signal. Although not recognized at the time of the event, this condition required entry into Technical Specification LCO 3.0.3. The cause of this event was due to an inadequate Loss of Safety Function (LOSF) determination, as described in Technical Specification 5.5.15, being performed and the work planning process not adequately identifying potential Technical Specification implications for the scheduled work.
4402010001 | Perry | 04/27/2009 | 03/25/2010 | ML10092009 | <strong>Invalid Isolation Signal Results in Shutdown Cooling Interruption</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2009, the shutdown cooling mode of operation for the Residual Heat Removal (RHR) system was interrupted for one hour and four minutes. At the time of the event, the plant was in MODE 5 (Refueling). Plant operators verified the designated alternate methods for decay heat removal were available. Reactor coolant temperature increased three degrees F. The event initiated as Instrumentation and Control technicians were installing an electrical jumper for a surveillance test. During the installation process, the jumper slipped off the terminal connector and created a short circuit to ground which blew the circuit's protective fuse. The blown fuse caused an RHR common suction valve to close (i.e., invalid signal) and trip the operating RHR A subsystem. Loss of the common suction flow path also prevented the'RHR B subsystem from being operated. The fuse was replaced and logic reset to open the suction valve and establish RHR B shutdown cooling operation. The individual human performance deficiencies were addressed in accordance with the company's performance management process. Procedure and program changes were made to address weaknesses in risk perception, use of jumpers and lifted leads, and work on protected equipment. The safety significance of this event is considered to be low. This event is reported in accordance with 10 CFR 50.7.3 (a)(2)(v)(B) as a condition that could have prevented the fulfillment of the safety function of a system needed to remove residual heat.
4402010002 | Perry | 02/16/2010 | 04/16/2010 | ML10112065 | <strong>Piping Leak Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2010, at approximately 2130 hours, a leak was identified on a portion of Emergency Closed Cooling Water subsystem B (ECCW B), American Society of Mechanical Engineers (ASME) Class 3 piping. On February 16, 2010, at 1310 hours, operators determined that ECCW B was inoperable due to the leak. The leak had been identified approximately 15 hours and 40 minutes prior to the inoperability determination; therefore, the plant was in the associated Technical Specification (TS) Limiting Condition for Operation 3.7.10 "ECCW System," Condition B, for longer than the Required Action Completion Time of 12 hours. During this period, ECCW A and its associated supported systems were operable. The cause of the event was that guidance for evaluating the operability impact of flaws in ASME piping was not adequately captured in plant procedures or training. For the leak itself, fatigue cracking was identified as the primary failure mechanism. The piping leak was repaired. The plant procedure for prompt operability determinations (POD) will be revised to direct consideration of reportability ramifications when establishing POD completion times. Procedure guidance will be developed to address through-wall piping leaks. Training courses will also be revised and Operations as well as other support personnel will be trained to lessons learned from this event. The safety significance of this event is considered to be low. This event is reported in accordance with 10 CFR 50.73 (a)(2)(i)(B) as an operation or condition which was prohibited by the plant's TS.
4402010003 | Perry | 05/11/2010 | 07/12/2010 | ML10201028 | <strong>Loss of Control Rod Drive Header Pressure Results in Manual RPS Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 11, 2010, at 2318 hours, a manual Reactor Protection System actuation was inserted in accordance with Technical Specification (TS) 3.1.5, "Control Rod Scram Accumulators." Control Rod Drive (CRD) system charging water header pressure was less than 1520 pounds per square inch gauge and multiple accumulator fault alarms were received on withdrawn control rods. A failed master trip unit caused an invalid Division 2 loss of coolant accident initiation signal and loss of electrical control power to the operating CRD pump and standby CRD pump. Control logic for the operating CRD pump was in an alternate electrical line-up at the time and could not be transferred to its normal source for a timely restart. A replacement trip unit was installed and tested satisfactorily. Future replacement trip units will be required to have 100 hours burn-in prior to installation to reduce the potential for early failures. Plant procedures will be revised to improve recognition and evaluation of long-term alternate plant configurations and degraded conditions. The safety significance of this event is considered to be low. This event is reported in accordance with 10 CFR 50.73(a)(2)(i)(A),completion of any nuclear power plant shutdown required by the plant's TS, and 10 CFR 50.73 (a)(2)(iv)(A), an event or condition that resulted in a manual or automatic actuation of plant systems listed in paragraph (a)(2)(iv)(B).
4432010001 | Seabrook | 03/17/2010 | 05/14/2010 | ML10139020 | <strong>Emergency Air Cleanup System Inoperable due to Opening in Boundary</strong><br /><i>Abstract:&nbsp;</i>On March 15, 2010 during operation in mode 1 at 100% power, both trains of the containment enclosure emergency air cleanup system (CEEACS) were rendered inoperable due to an opening in the ventilation area boundary. For approximately five hours on March 15 and approximately 4 hours on March 17, a door in the containment enclosure boundary (CEB) was opened to support planned maintenance activities in the positive displacement charging pump room. Under accident conditions, the CEEACS maintains a negative pressure in the enclosure surrounding the containment to prevent uncontrolled releases of radioactivity into the environment. However, the breach in the CEB created by the open door would have prevented both trains of the CEEACS from establishing the minimum required negative pressure in the enclosure. This condition placed the plant in Technical Specification (TS) 3.0.3, although it was unrecognized at the time, and resulted in a loss of safety function for the CEEACS. The causes of the event included lack of programmatic controls to ensure the control room is notified prior to propping open a CEB door and historical guidance that led the operators to believe that only TS 3.6.5.2, Containment Enclosure Boundary Integrity, applied when a CEB door was open. The planned corrective actions will strengthen an existing program to address opening CEB doors and revise the TS.
4432010002 | Seabrook | 04/09/2010 | 06/08/2010 | ML10165005 | <strong>Containment Penetration Protective Devices Found Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2010 during operation in Mode 1 at 100% power, the instantaneous trip setpoints for the containment penetration conductor overcurrent protective devices for the train-B hydrogen recombiner were found at incorrect settings. Both the primary and secondary protective device trip setpoints were set at 8.75x (equal to 1094 amps) rather than the design value of 6.25x (equal to 781 amps). Following this discovery, the protective devices were reset to their correct setpoints. Technical Specification (TS) 3.8.4.2, Electrical Equipment Protective Devices, confirms operability of the protective devices by verifying the devices trip when current is injected within a specified range of the trip setpoint. A review of test data found that the protective devices failed this surveillance requirement (SR) in May 2004 and April 2008. Therefore, the inoperable protective devices were in service for longer than permitted by the TS. The cause of the overcurrent protective devices being set at incorrect settings was attributed to previously vague procedure guidance. Subsequent revisions clarified the procedure and led to the identification of the incorrect setpoints. Although the protective devices failed to meet the SR, reasonable assurance existed that the devices would have actuated within current levels and response times that would have protected the containment penetration.
4452010001 | Comanche Peak 1 | 01/09/2010 | 03/03/2010 | ML10074029 | <strong>Unit 1 Trip due to Pressure Relay Actuation on Main Transformer 01</strong><br /><i>Abstract:&nbsp;</i>On January 9, 2010, Comanche Peak Nuclear Power Plant (CPNPP) Unit 1 was in Mode 1 operating at 100% power. At 1028 hours, the Unit 1 Main Turbine tripped due to a pressure relay actuation on the Unit 1 Main Transformer 01 and the Main Turbine Trip caused an automatic reactor trip. All control rods fully inserted, and all Auxiliary Feedwater pumps started as expected as a result of the reactor trip. All systems responded normally during and following the event. Internal inspection of the transformer showed that the relay actuation resulted from an internal failure of the Main Transformer as a result of a phase to ground fault. The exact cause of the fault could not be determined. Immediate corrective actions included isolating the Main Transformer 01 from Unit 1 and the other Main Transformer 02. On January 11, 2010, Unit 1 was synchronized to the grid at 0011 hours and reached a 640 megawatt output by 2100 hours. On January 19, 2010, a planned outage was taken on Unit 1 to install a spare transformer. Unit 1 was synchronized to the grid on January 21, 2010 at 2326 hours and reached 100% power the next day at 1341 hours. All times in this report are approximate and are Central Standard Time unless noted otherwise.
4452010002 | Comanche Peak 1, Comanche Peak 2 | 01/20/2010 | 06/23/2010 | ML10181025 | <strong>Loss of Automatic Initiation of Auxiliary Feedwater Upon Loss of Main Feedwater</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2010, Comanche Peak Nuclear Power Plant (CPNPP) Unit 1 was in Mode 3 during a planned outage and Unit 2 was in Mode 1 operating at 100% power. At 1827 hours, during review of an Oconee INPO OE report, parallels were discovered between the Oconee design and the CPNPP design. Further investigation determined that the required completion times for TS 3.3.2, Condition J, may not have been completed in the past when Units 1 and 2 were operating at low power with only one MFWP providing MFW flow. The cause analysis of this event determined that the plant design and original operating philosophy was not compatible with the NRC's clarification of the intent of TS 3.3.2, Function 6.g. Corrective actions include the completion of procedure changes on Unit 1 to ensure compliance with TS. Since Unit 2 has been operating at 100% power with both MFW pumps in service since discovery of this condition, corresponding changes to the Unit 2 procedures will be completed prior to removing one MFW pump from service during the next shutdown of Unit 2 or prior to startup of Unit 2 from any event which results in an unplanned trip of Unit 2. All times in this report are approximate and Central Standard Time unless noted otherwise.
4452010003 | Comanche Peak 1, Comanche Peak 2 | 06/18/2010 | 11/16/2010 | ML10327006 | <strong>Inadequate Surveillance Test Procedure Resulting in Failure to Meet TS Requirements</strong><br /><i>Abstract:&nbsp;</i>On June 18, 2010, during performance of the Component Design Bases Inspection, the NRC inspectors determined that surveillance test procedure (STP) OPT-216, "Remote Shutdown Operability Test" was not adequate to meet the Technical Specification (TS) Surveillance Requirement (SR). TS SR 3.0.3 was entered for the affected components and risk assessments were completed which supported continued operability until such time as the STP could be verified to adequately implement the testing requirements to meet the SR or the affected components could be adequately tested. The cause of this event was due to a lack of clarity in the description for the basis for SR 3.3.4.2 in the CPNPP Technical Bases. There have been no previous similar occurrences of failure to meet TS SRs due to inadequate STPs in the past three years. All times in this report are approximate and Central Standard Time unless noted otherwise.
4452010004 | Comanche Peak 1 | 07/04/2010 | 08/31/2010 | ML10251015 | <strong>Component Cooling Water Train Inoperable due to Inadequate Post Work Test Procedure</strong><br /><i>Abstract:&nbsp;</i>On July 4, 2010 during performance of the Unit 1 Train B Safeguards Slave Relay K644 Actuation surveillance test, unsatisfactory results were obtained. Operations personnel discovered that the Train B Containment Spray Heat Exchanger 1-02 Component Cooling Water Return valve was oscillating from 100 percent open to approximately 22 percent open. Troubleshooting subsequently revealed that an actuator rotor on this motor operated valve had been incorrectly set during the previous Unit 1 outage. The cause of this event was the post work test procedure did not provide specific instructions to ensure that an actuator rotor "dead band" was maintained after all of the rotor adjustments had been completed. Immediate corrective actions included resetting the actuator rotor to the correct position and successfully performing the Slave Relay Actuation test. Long term corrective actions include procedure changes. All times in this report are approximate and Central Time unless noted otherwise.
4462010001 | Comanche Peak 2, Comanche Peak 1 | 04/12/2010 | 06/07/2010 | ML10168041 | <strong>Loss of XST1 due to Breakers 7030 and 7040 Opening as a Result of a B-Phase to Ground Fault</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2010 at approximately 0720, CPNPP experienced a phase-to-ground fault between Startup Transformer XST1 and the 138kV switchyard while Unit 2 was operating at 100% power and Unit 1 was off-line for refueling. Alarms were received in the Unit 2 control room indicating that Startup Transformer XST1 was de-energized, which caused a slow transfer of the Unit 2 Class lE buses to XST2. The Unit 2 blackout sequencers actuated, and the Unit 2 motor-driven feedwater pumps and turbine-driven auxiliary feedwater water pump automatically started. The reactor operator reduced turbine load by 50 mega-watts electric. Spent Fuel Pool (SFP) cooling pumps, common to both Units, were load shed by design due to Unit 2 blackout sequencer actuation, and subsequently restarted by procedure. Investigation determined a B-phase insulator on a 138kV transmission tower had black marks and foreign material hanging down. Eight hours later the insulator was replaced and XST1 was restored as the preferred offsite power source to the Unit 2 Class 1E buses. All times in this report are approximate and are Central Daylight Time unless noted otherwise.
4462010002 | Comanche Peak 2 | 07/29/2010 | 12/14/2011 | ML11356A22 | <strong>Unit 2 EDG 2-02 Inoperable due to Remaining in Droop Mode Versus Isochronous Mode</strong><br /><i>Abstract:&nbsp;</i>On 7/29/2010, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at 100% power. At 1721 hours, Engineering completed an evaluation of a past condition concluding that during the period from 9/8/2008 to 9/20/2009, with the Emergency Diesel Generator (EDG) remaining in Droop Mode, the 2-02 EDG frequency could have been slightly below the Technical Specifications minimum of 58.8 Hz (58.78 Hz) and the EDG could have been Inoperable. However, an evaluation completed by Westinghouse on 8/5/2010 concluded that had the 2-02 EDG operated at the reduced frequency of 58.78 Hz, the applicable Emergency Core Cooling System (ECCS) systems would have performed their safety functions as described in the Safety Analysis. The cause of this event was the Breaker 2EA2-1 Auxiliary Switch 2EA2-1 52b 97-98 did not make-up due to a high-resistance contact causing the Generator Droop Relay (GDR) not to energize. With the GDR not energized, the EDG remained in Droop Mode. Corrective actions included confirming current Operability and procedure revisions to require Operators and Engineering to review voltage and frequency DAS traces during the loss of offsite power (LOOP) restoration portion of the test to verify proper EDG operation. All times in this report are approximate and Central Time unless noted otherwise. As noted above, this report constitutes a 10CFR21 notification.
4552010001 | Byron 2 | 04/19/2010 | 06/18/2010 | ML10172012 | <strong>Reactor Protection and Auxiliary Feedwater System Actuation Signals from Low Steam Generator Level due to Inadequate Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2010, Byron Station Unit 2 was shutting down for a refuel outage and was in Mode 4. An outage activity during Mode 4 was to perform the Feedwater Isolation Valve (FWIV) surveillance procedure. At 0503, during the restoration section of the test procedure, a low level condition on the 2D Steam Generator (SG) inadvertently occurred which resulted in the generation of Reactor Protection trip initiation, Auxiliary Feedwater initiation, and SG Blowdown isolation signals. Due to shutdown conditions, the control rods were already fully inserted, the Reactor Trip breakers positioned open and the Auxiliary Feedwater pumps were removed from service. The causes of the inadvertent actuation signals include Operations supervisory oversight of the FWIV testing activity was less that adequate, and the FWIV surveillance procedure was inadequate in that it did not provide for the specific recovery of SG level during the conduct of the procedure if levels were approaching the low actuation setpoint. Corrective actions include reinforcing the roles and responsibilities of key outage Operations positions, and revising the FWIV stroke procedure to incorporate steps that allow for SG level recovery strategies to manage system parameters to avoid challenges to actuation setpoints.
4552010002 | Byron 2, Byron 1 | 06/04/2010 | 08/03/2010 | ML10218017 | <strong>Essential Service Water System Inoperable Due to Inadequate Seismic Restraint from Original Construction Error</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2010, Engineering identified that the support rails for Unit 2 A and B Containment Ventilation (VP) Chillers were not welded to their base plates in accordance with design requirements. The VP Chillers are non-safety related and isolated from Essential Service Water (SX) during a design basis accident. This design installation discrepancy causes increased loading on the attached SX lines (and consequently may impact the safety function of both trains of SX) during a Safe Shutdown Earthquake (SSE) event. The initial operability assessment concluded, based on engineering judgment, that installed supports and bolting were adequate to restrain the VP Chillers sufficiently to consider the attached SX piping operable. A detailed engineering assessment of this condition continued while welding the VP Chillers' support rails to their base plates. The welding of the support rails to the base plates was completed at approximately 2100 hours on February 3, 2010. The detailed engineering assessment continued in order to determine the historical operability status of the SX system. On June 4, 2010, an engineering assessment, using simplified methodologies, concluded the SX lines attached to the VP Chillers would not have satisfied permanent design or interim operability requirements. Further analysis, using more sophisticated techniques, will be pursued to continue to assess the operability of the SX system and the potential safety significance. The cause was determined to be an installation oversight during the initial construction in the early 1980's timeframe and not identifying the defect since installation. An extent of condition review of Chillers was conducted and all were found to have their required welds in place. In addition, a review of non-safety related components that may provide physical support to safety related components was completed. No additional concerns were identified.
4562010001 | Braidwood 1 | 08/16/2010 | 03/02/2011 | ML11062009 | <strong>Reactor Trip due to Water Intrusion in Breakers Causing Circulating Water Pump Trips and Resulting in Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2010, as a result of a Unit 2 reactor trip, condensate water overflowed from the auxiliary feedwater (AF) standpipes onto the turbine deck. The water spread through openings in the floor to the elevation below, and entered a Unit 1 substation cabinet. This water intrusion resulted in the trip of electrical buses that caused the 1A and 1C circulating water (CW) pumps to trip. Additionally, power to the respective CW pump discharge valves was lost. These conditions caused the Unit 1 condenser vacuum to degrade. At 0219, the Unit 1 main turbine received an automatic trip on low condenser vacuum, resulting in an automatic reactor trip. Following the reactor trip, the auxiliary feedwater pumps auto started on low-low steam generator water levels. The root causes were determined to be: 1) an inadequate design of the AF standpipes; and 2) a lack of sensitivity evolved that tolerated long-term uncontained water issues with inadequate evaluation for potential impacts. The corrective action to prevent recurrence is to install a design feature on the AF suction standpipe which prevents water spill events. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
4562010002 | Braidwood 1 | 08/16/2010 | 10/15/2010 | ML10291015 | <strong>Limiting Condition for Operation Action Not Completed With in the Required Time</strong><br /><i>Abstract:&nbsp;</i>At 0241, Unit 1 received a volume control tank high level alarm, causing a loss of the boron dilution protection system (BDPS) function. Entry into Technical Specification Limiting Condition for Operation (LCO) 3.3.9 Conditions A and C for BDPS was required, which includes a one-hour Required Action to close non-borated water source isolation valves. This action was not completed within the one-hour requirement. The root causes were determined to be 1) the procedure for reactor trip response does not provide adequate guidance to alert operators to potential LCO 3.3.9 entry during plant transients, and 2) the BDPS annunciators are not adequately human factored. The corrective action to prevent recurrence is to revise the reactor trip response procedure to include guidance for potential LCO 3.3.9 entry. An additional corrective action is to evaluate human factors improvements for the plant annuniciator system. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which is prohibited by the plant's Technical Specifications.
4562010003 | Braidwood 1 | 09/15/2010 | 11/15/2010 | ML10319075 | <strong>Through-weld Leak of the Line from the1B Seal Injection Filter to the Vent Valve</strong><br /><i>Abstract:&nbsp;</i>On September 15, 2010, at 0758, Operations was notified that a potential for leakage existed on a weld on a 3/4-inch diameter stainless steel line which extends from the reactor coolant pump seal water injection filter to the 1B seal water injection filter vent valve. Limiting Condition for Operation (LCO) 3.5.5, "Seal Injection Flow," was conservatively entered based on a postulated failure of this line due to pressure boundary leakage. The LCO was exited at 0939 when the 1B seal injection filter, including the potentially leaking vent pipe, was isolated from the chemical volume and control system within the allowed completion time of the LCO. At 1121 on September 15, 2010, following cleaning, a through-weld leak was confirmed on one weld through visual inspection. The cause of the leakage was determined to be transgranular stress corrosion cracking (TGSCC) that was accelerated by the existence of an original fabrication flaw. The corrective action was to repair the through-weld leak. This action has been completed. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which is prohibited by the plant's Technical Specifications.
4562010004 | Braidwood 1 | 09/20/2010 | 11/19/2010 | ML10326008 | <strong>Reactor Trip due to Performance of a Channel Calibration with a Coincident Bistable in a Half-Trip Condition</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2010, Maintenance initiated performance of a Technical Specification surveillance calibration of a steam generator water level channel. At 1704, when a bistable for the channel under test was placed in the tripped condition per the surveillance, an automatic turbine trip was received. The turbine trip was immediately followed by an automatic reactor trip due to the turbine trip while the reactor was greater than 30% power. Following the reactor trip, the auxiliary feedwater pumps auto started on low-2 steam generator water levels. Investigation determined that a universal logic card in the solid state protection system failure resulted in one input being in the tripped state, creating an unknown half trip condition. During performance of the channel calibration when the coincident loop bistable was tripped, the 2-of-4 logic was met which caused an immediate turbine trip. The direct cause for this event was failure of the universal logic card. The root cause evaluation has not been completed. The corrective actions to prevent recurrence include implementing first time preventative maintenance replacements of the SSPS universal logic cards for Unit 1 (completed) and Unit 2 (scheduled). There were no actual safety consequences impacting plant or public safety as a result of the event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
4562010005 | Braidwood 1, Braidwood 2 | 11/12/2010 | 01/11/2011 | ML11012014 | <strong>Incorrect Methodology Used in Calculations in 1999 Resulted in Non-Conservative Control Room Outside Air Intake Monitor Alarm Setpoints</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2010, during a review of setpoint calculations for process monitors, an error was identified in the methodology used in a historic calculation of the setpoints for the control room outside air intake noble gas channels, making the setpoints non-conservative. On November 12, 2010, at 0818, the four channels were declared inoperable, and the appropriate Technical Specification (TS) Limiting Condition for Operation (LCO) Conditions A and B were entered. The setpoints were revised for the gas channels, and at 1725 Technical Specification LCO 3.3.7 Conditions A and B were exited. The apparent cause for this event was that the procedure for determining the alarm setpoints did not have details of the methodology for the calculation. The corrective actions include revising the setpoint calculations and correcting the setpoints for the affected gas channels, verifying that all required TS radiation monitors are set in compliance with TS requirements, and revising the procedures that perform setpoint calculations for the process radiation monitors to address details on the method used for setpoint calculations, and include instructions for the basis for the review criteria. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by Technical Specifications.
4562010006 | Braidwood 1, Braidwood 2 | 11/12/2010 | 01/11/2011 | ML11012014 | <strong>Technical Specifications Allowed Outage Time Extension Request for Component Cooling System Contained Inaccurate Design Information That Significantly Impacted the Technical Justification</strong><br /><i>Abstract:&nbsp;</i>On September 27, 1987, a License Amendment Request (LAR) was submitted for Byron and Braidwood Stations to request an increase in the Allowed Outage Times (AOT) from 72 hours to seven days for several systems, including the Component Cooling (CC) System and an Emergency Core Cooling System (ECCS) sub-system (i.e., the Residual Heat Removal (RH) System). This LAR was based on the 1984 WCAP-10526, which provided a probabilistic risk assessment technical justification. On July 7, 2010, an issue was identified concerning an apparent discrepancy in this 1987 LAR. Based on CC design discrepancies that have been known to exist approximately since the 1987 timeframe, the CC system description contained in the WCAP was incorrect and was likely also modeled incorrectly in the PRA analysis. In the WCAP CC system description, the common CC system pump was described as a maintenance spare that could be substituted for any of the CC system unit-specific pumps. Due to the design discrepancies, the common pump could not be substituted for either unit's B CC trains. This discrepancy would have significantly impacted the PRA results of the WCAP and possibly affected NRC approval of the LAR. In addition, another potentially significant discrepancy was discovered in the RH system analysis of the WCAP, in that it did not correctly account for the operational requirement to preemptively split CC trains in a post accident scenario. The Technical Specifications for CC and RH were declared non-conservative and administrative controls put in place to restrict their AOTs to 72 hours, and ensuring the Unit 0 CC pump shall not be used to satisfy the requirements of the 1B or 2B CC pump. The most probable causes are limited procedural guidance for preparing correspondence, and ambiguity in intended system operation. The cause of the inaccurate LAR is indeterminate due to the timeframe when the event occurred. Modifications are being investigated to the CC system to eliminate the design discrepancies.
4562010007 | Braidwood 1, Braidwood 2 | 11/19/2010 | 01/18/2011 | ML11018042 | <strong>Potential Loss of Residual Heat Removal System Safety Function in Mode 4 When Aligned for Shutdown Cooling due to Potential for Flashing or Voiding of Coolant During a Shutdown Loss of Coolant Accident</strong><br /><i>Abstract:&nbsp;</i>In November 2009, Westinghouse issued Nuclear Safety Advisory Letter (NSAL) 09-8, "Presence of Vapor in Emergency Core Cooling System/Residual Heat Removal System in Modes 3/4 Loss-of-Coolant Accident Conditions." This NSAL clarifies the guidance provided in a previous document, and was issued to ensure consideration of the significantly reduced elevation head present when the residual heat removal (RH) system supply is transferred from the refueling water storage tank (RWST) to the emergency core cooling system (ECCS) recirculation sump. An evaluation confirmed that the temperature limit currently applied at Braidwood to the RH system for alignment for ECCS injection was sufficient when aligned to the RWST, but could result in flashing of liquids in the hot leg suction lines when the RH system is transferred to the ECCS recirculation sump. The evaluation concluded that the RH temperature must be reduced to eliminate the potential for flashing of hot water within the isolated hot leg suction piping during transfer to the ECCS recirculation sump. On November 19, 2010, a review identified four occurrences (two on Unit 1 and two on Unit 2) in the past three years where both RH trains were placed into operation prior to reaching Mode 5 (</= 200 degrees F). The cause of this event was the failure to consider bounding conditions when calculating the temperature limit to prevent flashing in the RH system. Corrective actions include implementation of a standing order for RH to address the new temperature limits for these conditions, revise the associated operating and emergency procedures to reflect the more restrictive temperature limits, and revise Technical Specification Bases 3.5.3, "ECCS - Shutdown," to reflect the new temperature limit. There were no actual safety consequences impacting plant or public safety as a result of the event.
4572010001 | Braidwood 2 | 02/15/2010 | 04/16/2010 | ML10106056 | <strong>Essential Service Water Pump 2A Braided Hose Failure Resulted in a Condition Prohibited by Technical Specifcations</strong><br /><i>Abstract:&nbsp;</i>On January 29, 2010. an equipment operator identified a leak on the 2A essential service water (SX) Pump. The leak was from a braided flexible metal hose that provides cooling/flushing water from the casing of the pump to the inboard pump seal. The size of the leak was determined not to prevent the 2A SX pump from delivering required flow to safety related loads, and was not affecting any components on the 2A SX pump or any other equipment in the area. Initial inspection indicated the leak was from the connection of the braided hose and was not pressure boundary leakage. Therefore, the SX Technical Specifications (TS) Condition for Operation (LCO) Condition A was not entered, and it was decided to replace the flexible hese during an upcoming work window. Following replacement, the hose was sent to a vendor for failure analysis. On February 15, 2010, the station was notified that the failure analysis identified a pinhole leak approximately seven inches from the end of the hose The leak was caused by vibration induced wear at the contact points of the braided wire jacket against the metal hose surface. The leak was classified as ASME Section III Class 3 pressure boundary leakage. The 2A SX pump was inoperable due to the ASME component failure. Therefore, TS 3.7.8 Condition A should have been entered. Corrective actions include installation of a cushioning bronze inner braid on the SX seal water flexible hoses: implementing a 6-year replacement preventive muinteilan(le program (PM) for the SX seal water flexible hoses and providing operator training related to ASME code applicability and system design and on short term LCO actions requiring assistance from other groups. There were no actual safety consequences impacting plant or public safety as a result of the event, The event is being reported pursuant to 50.73(a)(2)(1)(F3), as a condition prohibited by TS 3 7 3 Condition C.
4572010002 | Braidwood 2, Braidwood 1 | 06/17/2010 | 08/16/2010 | ML10236053 | <strong>Containment Spray Pump Suction Valve Failed to Close Resulting in an Unanalyzed Plant Condition due to Procedure Error</strong><br /><i>Abstract:&nbsp;</i>On June 17, 2010, containment spray pump suction valve 2CS009B was successfully stroked full open during a surveillance test, however during restoration failed to stroke fully closed. The valve was subsequently manually restored to the normally closed position. It was determined that a bypass flow path would exist if a safety injection occurred with both suctions from the refueling water storage tank (RWST) and the emergency core cooling system sump open. This alignment provides an increased flow rate of the RWST to the containment sump, and was potentially not bounded by an existing analysis of an SI8812 valve failing open. Therefore, this condition created a potentially unanalyzed condition when 2CS009B failed to fully close. This is applicable to both trains of containment spray (train A and train B) and to both Unit 1 and Unit 2. The direct cause of this event was that the procedure was not properly evaluated for an unanalyzed plant condition due to the process controls, standards, and license conditions at the time of development. Corrective actions include revising the surveillance tests for the containment spray sump isolation valves. This action is complete. There were no actual safety consequences impacting plant or public safety as a result of the event. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) for being in an unanalyzed condition that significantly degraded plant safety. The potential safety significance is being assessed and will be reported in a supplement to this report.
4572010003 | Braidwood 2 | 08/16/2010 | 10/15/2010 | ML10288032 | <strong>Reactor Trip Caused by Phase to Ground Fault of a Failed Crossover Damper/Deionizer Assembly Due to an Inadequate Inspection Acceptance Criteria and Preventive Maintenance Inspection Frequency</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2010 at 0206, Unit 2 main generator received generator lockout relay trips, which caused the Unit 2 reactor to trip on a turbine trip above 30 percent power. Following the reactor trip, the auxiliary feedwater pumps automatically started on low-low steam generator water levels. The root cause of the Unit 2 reactor trip was determined to be an inadequate damper inspection acceptance criteria and preventive maintenance (PM) frequency that did not account for the more turbulent flow characteristics that the crossover damper is subjected to. Corrective actions to prevent recurrence include revising the PM schedules to ensure the crossover damper assembly is inspected and/or replaced prior to failure, and revising the maintenance procedure for isophase bus duct PM to include additional inspection criteria for the crossover damper assembly. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to actuation of the reactor protection system (reactor trip) and the auxiliary feedwater system.
4572010004 | Braidwood 2 | 08/24/2010 | 10/25/2010 | ML10298062 | <strong>Unplanned Limiting Condition for Operation Entry due to Low Header Pressure on the 2B Essential Service Water Pump</strong><br /><i>Abstract:&nbsp;</i>On August 24, 2010, Operations was performing a surveillance on the 2B essential service water (SX) pump, which directs throttling of SX flow through the component cooling (CC) heat exchanger through the Unit 2 CC heat exchanger outlet valve 2SX007, to raise total SX system flow to 24,000 gpm. During surveillance performance, an incorrect flow instrument for data collection was used to determine total SX system flow. At 1140, while throttling open the 2SX007 valve, SX system pressure decreased to less than 89 psig, and the main control room received an SX low system pressure alarm. Operations throttled closed the 2SX007 valve to restore SX system pressure to greater than 90 psig to clear the alarm. During the event, SX pressure decreased to 65 psig, and total SX flow increased to approximately 34,450 gpm. The root cause of the event is the surveillance did not clearly identify the instrument to be used. The surveillance directed the use of a flow element instead of the ultrasonic flow instrument. The corrective action to prevent recurrence is to revise the SX pump surveillances to identify the total scope of the ASME surveillance in the purpose, and revise steps to specifically identify the use of the ultrasonic flow meter, equipment number and noun name, and location. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which is prohibited by the plant's Technical Specifications.
4582010001 | River Bend | 04/22/2010 | 06/16/2010 | ML10173047 | <strong>Control Building Chiller Inoperable Greater Than Allowable Outage Time</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2010, an engineering evaluation determined that safety-related chillers serving the main control room envelope had been operated in a configuration outside design parameters, such that the chillers could not be assumed to be operable under all conditions. Specifically, that evaluation and review of operating logs concluded that there was a period beginning in November 2009 when one of the operating chillers was actually inoperable, and was in that condition for a time greater than the allowable outage time cited in the applicable Technical Specifications. Also during this time, a second chiller was inoperable for approximately ten days. This condition was caused by an error in the design basis documentation of the chiller. Actions are being taken to correct this error, and operating procedures have been revised to incorporate the updated information. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications.
4582010002 | River Bend | 05/05/2010 | 07/01/2010 | ML10188027 | <strong>Standby Gas Treatment Filter Inoperable due to Inadequate Surveillance Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2010, an investigation of surveillance test results determined that a deficiency in test acceptance criteria had caused a failure in the standby gas treatment filter "B" to go undetected since May 26, 2005. Technical Specification 5.5.7, "Ventilation Filter Testing Program," requires that the heaters in the filter be able to dissipate 61 kilowatts (kW) of power. The investigation of this event determined that a failure of part of the heater circuitry had resulted in heater power decreasing to approximately 46kW, causing the filter to be inoperable. The test procedure deficiency involved the calculation of electrical heater capacity. The investigation of this event determined that bus voltages assumed by the design basis accident were not considered when developing the criteria for the affected test procedures. The cause of this condition was determined to be a lack of rigor in engineering processes at the time when those acceptance criteria were issued. Actions are being taken to revise the test acceptance criteria. An engineering review of completed test results has been put into place as an interim action. This condition had existed for a period greater than the allowable outage time cited in Technical Specifications 3.6.4.3. This condition did not cause the filter to be incapable of performing its safety function, and, thus, was of minimal significance to the safety of the public. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications.
4582010003 | River Bend | 06/25/2010 | 08/19/2010 | ML10237077 | <strong>High Pressure Core.Spray System Declared Inoperable due to Failure of Pump Room Cooler</strong><br /><i>Abstract:&nbsp;</i>On June 25, 2010, at 8:24 p.m. CDT, with the plant operating at 100 percent power, the unit cooler for the high pressure core spray (HPCS) pump room was shut down by the operators following the report of noise and light smoke coming from the fan motor. This action required that the HPCS system be declared inoperable, as the unit cooler is necessary to support continued operation of the HPCS pump. This condition is being reported in accordance with 10CFR50.73(a)(2)(v)(D) as the loss of a system needed to mitigate the consequences of an accident. The cause of this event was the failure of lubrication in the fan motor bearings resulting from inadequate implementation of vendor recommendations for preventive maintenance. Contributing factors were the inaccurate data collected during vibration monitoring, and improper installation of the original bearings in the motor. The unit cooler was repaired, and the HPCS system was returned to service within the time limit of the Required Action in the plant's Technical Specifications. This event was of minimal safety significance with respect to the health and safety of the public.
4582010004 | River Bend | 11/07/2010 | 03/02/2011 | ML11067016 | <strong>High Pressure Core Spray System Inoperable due to Failed Motor Oil Reservoir Drain Plug</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2010, at 10:23 a.m. CDT, with the plant operating at 100 percent power, the high pressure core spray (HPCS) pump was declared inoperable following the discovery of an oil leak on the pump motor. The source of the oil leak was found to be a cracked drain plug on the lower motor bearing oil reservoir. The oil plug was replaced, and the HPCS system was restored to its standby condition at 7:40 p.m. CDT that same day. The investigation of this event determined that the oil plug cracked due to application of torque to correct an oil leak. The oil leak had been caused by age-related degradation of the O-ring on the plug, attributable to the lack of a preventative maintenance task to provide for its periodic replacement. A new oil plug was installed on the motor, and the system was returned to service. The preventative maintenance program is being updated to include this plug and O-ring. This condition is being reported in accordance with 10CFR50.73(a)(2)(v)(D) as the loss of a system needed to mitigate the consequences of an accident. No other safety-related systems were out of service during the time that the HPCS system was inoperable. This event was of minimal significance with respect to the health and safety of the public.
4612010001 | Clinton 1 | 10/07/2009 | 01/26/2011 | ML11034019 | <strong>Unanalyzed Leakage Pathway Affecting Residual Heat Removal A Pump Room Flooding Analysis</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2009, an unanalyzed leakage pathway affecting the flooding analysis associated with a postulated piping break in the Residual Heat Removal (RHR) A pump room was discovered involving a drain line connecting the RHR A pump room to the radwaste pipe tunnel leading outside secondary containment. Actions were taken on October 8, 2009, to permanently plug the line to eliminate this pathway. This as-found condition had the potential, given a postulated pipe rupture of the RHR A pump suction line, to drain the suppression pool until the level was below the lowest level assumed in the accident analysis. This condition resulted in the plant being in an unanalyzed condition that significantly degraded plant safety and could have prevented the fulfillment of the safety function of the emergency core cooling system. The cause of this event was determined to be a historical design oversight during plant construction that allowed the RHR A pump room floor drains to be connected to the radwaste pipe tunnel.
4612010002 | Clinton 1 | 02/03/2010 | 08/23/2010 | ML10243016 | <strong>Excessive Leakage through Feedwater Isolation Valve 1B21F032B</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2010, after entering Mode 2 (Startup) following refueling outage C1R12, it was discovered that a primary containment local leak rate test (LLRT) performed on feedwater check valve, 1B21-F032B, exceeded its acceptance criteria. Technical Specification (TS) Surveillance Requirement (SR) 3.6.1.3.11 requires that the combined leakage rate for both primary containment feedwater penetrations to be less than or equal to 2 gallons per minute (gpm) for the worst of the isolation valves. The measured leakage rate for 1B21-F032B was reported to be 2.5 gpm. This leakage rate is greater than that assumed in the plant safety analysis. The unit was placed in Mode 4 (Cold Shutdown) to repair the valve and to re-perform the LLRT. After lubricating the valve actuator and stroking the check valve, the LLRT was performed to confirm the valve could meet its safety function for the Feedwater Leakage Control System (FWLCS). Following the satisfactory completion of the LLRT, plant startup was re-commenced on February 4, 2010. The cause of the 1B21-F032B.check valve to fail its leak rate test was age-related degradation of the lubrication causing increased friction in the actuator. Corrective action for this event includes establishing preventive maintenance activities to lubricate and overhaul the actuators.
4612010003 | Clinton 1 | 03/15/2010 | 02/21/2011 | ML11062010 | <strong>Unexpected Component Actuations due to Self Test System Design Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On 3/15/10, during full power operations, Division 2 Drywell Ventilation and Drywell Cooling Primary Containment Isolation Valves (PCIVs) closed for isolation Groups 11 and 17 and shunt trip devices for the breakers of several components were tripped. The actuations were a result of a Division 2 load driver card that spuriously actuated its loads without a valid Loss of Coolant Accident signal or a manual initiation signal present. This event was reported to the NRC by Event Notification 45901 on 5/5/10. The cause of the card failure could not be determined at the time; however during a recent investigation performed following further spurious actuations of Division 1 that occurred between 8/24/10 and 8/26/10, it was determined that the 3/15/10 event was most likely caused by degradation of the Division 2 Self Test System (STS) power supply, resulting in the misoperation of the Nuclear Systems Protection System (NSPS) load driver card. The cause of this event is that the STS has a design deficiency related to its power supplies and NSPS has a design deficiency related to its load driver cards which do not allow the STS to meet its design specification when a power supply is degraded. Corrective action for this event includes replacing STS power supplies with low voltage protection and presenting options for the STS issues to the Plant Health Committee for approval.
4612010004 | Clinton 1 | 01/17/2010 | 01/25/2011 | ML11033019 | <strong>OPDRV Requirements Not Met During Control Rod Drive Mechanism Replacements</strong><br /><i>Abstract:&nbsp;</i>According to a Non-Cited Violation (NCV) issued to Clinton Power Station (CPS), the station revised the Technical Specifications (TS) plain language definition of Operations with a Potential for Draining the Reactor Vessel (OPDRV) in violation of 10 CFR 50.59 when the station reviewed and approved a procedure pertaining to OPDRVs. In the procedure, the station provided limitations which the NRC considered to be a change in the plain language definition of the term OPDRV that, in effect, constituted a change to the TS, which would thus require a license amendment. Based on NRC letter dated 11/29/10 responding to a letter CPS issued to contest the NCV, the station concluded that control rod drive mechanism replacement activities on 1/17/10 to 1/18/10 during a refueling outage were performed without meeting several TS requirements. The cause of this event is the 10 CFR 50.59 evaluation concluded that the change did not require prior NRC approval as the station did not use conservative decision-making before proceeding with implementation of the OPDRV procedure. Corrective action includes suspending the procedure, revising the 10 CFR 50.59 evaluation completed for the procedure, and presenting the details of this event during 10 CFR 50.59 requalification classes and to applicable personnel who do not have 10 CFR 50.59 qualifications.
4822010001 | Wolf Creek | 01/21/2010 | 03/22/2010 | ML10089041 | <strong>Automatic Start of Motor Driven Auxiliary Feedwater Pumps Inoperable During Startup in Mode 1</strong><br /><i>Abstract:&nbsp;</i>Industry operating experience, 0E30255 dated December 16, 2009, identified that a design feature of each main feedwater (MFW) pump can provide a status indication that the MFW pump is in service when the MFW pump may not actually be supplying water to the steam generator. In this condition, if the MFW pump in service tripped, the motor driven auxiliary feedwater (AFW) pumps would not receive an auto-start signal from the trip of both MFW pumps as required by technical specifications. The operating experience provided reference to Watts Bar Nuclear Plant licensee event reports for a similar event. Further research identified on August 7, 2008, the Nuclear Regulatory Commission (NRC) issued Watts Bar Nuclear Plant - NRC Integrated Inspection Report 05000390. The inspection report identified that a non-operating MFW pump in the reset condition impacts operability of the AFW auto-start channel due to the false (i.e., invalid) indication of the MFW pump status. On January 21, 2010, the operating experience was placed into the corrective action program. On February 4, 2010, a review of the operating experience determined that the design and normal operation of the MFW pumps at Wolf Creek Generating Station (WCGS) could result in a condition that does not conform to the WCGS Technical Specification (TS) Table 3.3.2-1, Function 6.g., Trip of All Main Feedwater Pumps. During plant startups, the non-operating MFW pump in the reset condition results in two inoperable AFW auto-start channels. There is no TS Condition for two MFW pump trip channels inoperable. Limiting Condition for Operation (LCO) 3.0.3 specifies that when an associated Action is not provided, action shall be initiated within 1 hour to place the plant in Mode 3 in 7 hours. Action had not previously been taken as required by the TSs.
4822010002 | Wolf Creek | 01/26/2010 | 03/29/2010 | ML10097003 | <strong>Turbine Trip Function of Reactor Trip, P-4 Interlock Defeated During Entry Into and in Mode 3</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2010, a review of a revision to procedure SYS AC-120, "Main Turbine Generator Startup," identified that Step 5.6 allows leads to be lifted that defeat Reactor Trip, P-4 interlock for the turbine trip function when the plant is in Mode 3. Further review identified that Step 5.6 of procedure SYS AC-120 was performed on November 17, 2009 at approximately 1600 hours CST. Wolf Creek Nuclear Operating Corporation (WCNOC) defeated the turbine trip on reactor trip function in Mode 4 and the plant transitioned to Mode 3 on November 18, 2009, at 0014 hours with the function defeated. The leads were relanded on November 20, 2009, at 1559. Technical Specification (TS) 3.3.2, Table 3.3.2-1 specifies the applicable Mode for Function 8.a. (Reactor Trip, P-4) as Modes 1, 2, 3. Defeating the turbine trip on reactor trip function of the Reactor Trip, P-4 interlock using procedure SYS AC-120 results in both channels being defeated. The Mode change was not in conformance with Limiting Condition for Operation (LCO) 3.0.4 which precludes entry into a Mode or other specified condition in the Applicability statement when an LCO is not met and there is no Condition/Required Action for two channels or trains inoperable. Additionally, it was identified that the turbine trip on reactor trip function had been defeated on two occasions while in Mode 3. LCO 3.0.3 specifies that when an associated Action is not provided, action shall be initiated within 1 hour to place the plant in Mode 4 in 13 hours. Action had not previously been taken as required by TSs.
4822010003 | Wolf Creek | 02/09/2010 | 04/08/2010 | ML10106026 | <strong>Post Fire Safe Shutdown Issue with the B Emergency Diesel Generator Voltage Control Circuitry</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2010, engineering reviewed procedure STN RP-002, "Miscellaneous ISO/BYPASS Switch Testing," for an on-going Technical Specification Equipment Outage (TSEO) on the Train B Diesel Generator (DG). During this review, the system engineer identified that a fire induced hot short could energize the unit parallel relay and place the generator in droop mode of operation. In addition, other circuit issues were identified that could adversely affect the DG voltage regulator. This issue could have prevented operation of the Train B DG if a fire occurred in the control room involving these circuits. This could have prevented a safe shutdown of the plant if a severe fire occurred in the control room that also disabled off-site power. No fire actually occurred and this is a historical design issue that has been in place since construction. A temporary modification was prepared and implemented prior to the Train B DG being returned to service.
4822010004 | Wolf Creek | 02/11/2010 | 04/08/2010 | ML10106026 | <strong>Positive Reactivity Addition in Mode 2 with One Source Range Neutron Flux Channel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 2/11/2010 the NRC issued violation 2009005-009, "Positive Reactivity Addition Prohibited by technical specifications while in Mode 2." The inspectors identified a noncited violation of Technical Specification 3.3.1, Condition I, for making positive reactivity addition prohibited by technical specifications in Mode 2 because one Source Range Neutron Flux channel was inoperable. A loss of off-site power event on 8/19/2009 caused a reactor trip and turbine trip and the plant entered Mode 3. As a result, power to the Containment Cavity Cooling fans was lost. During this period, Source Range Neutron Flux channel, SEN0031, was reading somewhat lower than Source Range Neutron Flux channel SEN0032, then increased and stabilized significantly higher than SEN0032. On 08/20/2009, the Cavity Cooling Fan was started and SEN0031 indication rapidly returned to near the same relative indication to SEN0032 as existed initially. On 08/22/2009 Wolf Creek entered the mode of applicability when the reactor trip breakers were closed. Wolf Creek entered Mode 2 and the reactor became critical on 8/23/2009. During the reactor startup and power ascension to point of de-energizing the source range instruments above P-6, both source range instruments indicated normally and passed all normal channel checks. This event is of low safety significance. The source range detector was replaced during Refuel Outage 17 in November 2009.
4822010005 | Wolf Creek | 03/02/2010 | 05/03/2010 | ML10131039 | <strong>Reactor Trip due to Low Steam Generator Level from Trip of Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On 3/2/2010 at 1458 CST, while performing procedure SYS PN-200, "Energizing and Deenergizing Inverters PNO9 or PN10," Wolf Creek Generating Station (WCGS) experienced a reactor trip due to Steam Generator (SG) Water Level - Low Low actuation signal. The unit received a feedwater isolation and auxiliary feedwater actuation (both motor-driven and turbine- driven) because of the low SG level. All control rods inserted fully and the Reactor Trip System and the Engineered Safety Feature System performed as expected. The SG Water Level - Low Low actuation signal was initiated due to a trip of the train "A" main feedwater pump as a result of the failed transfer of inverter PNO9 to an alternate power supply. Inverter PNO9 did not transfer from the normal to alternate power supply due to the sticking of the reed relay on the static transfer switch circuit board. The safety significance of this event is low. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report (USAR) Section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
4822010006 | Wolf Creek | 03/08/2010 | 05/05/2010 | ML10145014 | <strong>Manual Reactor Trip due to Trip of Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On 3/8/2010, Wolf Creek Generating Station (WCGS) was at 42 percent power during a reactor startup when the "A" main feedwater (MFW) pump tripped at 0332 CST. The control room operators manually tripped the reactor due to the decreasing steam generator levels. All control rods fully inserted and the Reactor Trip System and the Engineered Safety Feature Systems performed as expected. The cause of the MFW pump trip was a failed servo in the MFW control circuitry. Emergency boration was actuated when reactor coolant system (RCS) temperature dropped below 550 degrees Fahrenheit. Emergency boration was secured at 0404 CST on 3/8/2010 when RCS temperature was raised to greater than 550 degrees Fahrenheit. The safety significance of this event is low. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report (USAR) Section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
4822010007 | Wolf Creek | 04/20/2010 | 07/09/2012 | ML12202A09 | <strong>Post-Fire Safe Shutdown Fire-Induced Multiple Spurious Operation Issues</strong><br /><i>Abstract:&nbsp;</i>While performing a post-fire safe shutdown review per Enforcement Guidance Memorandum (EGM) 09-002, "Enforcement Discretion for Fire Induced Circuit Faults," and Regulatory Guide 1.189, Revision 2, five fire-induced multiple spurious operation (MSO) issues were determined to be reportable pursuant to 10 CFR 50.73(a)(2)(ii)(B). EGM 09-002 provides enforcement discretion for noncompliances related to multiple fire-induced circuit faults. The five fire-induced MSO issues that were identified are: - Three issues which could potentially prevent operation of the Residual Heat Removal Pump(s), - An issue where pressurizer spray may spuriously actuate, and - An issue where a Centrifugal Charging Pump could spuriously start and fill the pressurizer solid.
4822010009 | Wolf Creek | 07/21/2010 | 09/17/2010 | ML10266003 | <strong>Pressurizer Level Higher than Assumed in the Inadvertent Operation of ECCS Analysis</strong><br /><i>Abstract:&nbsp;</i>During a review of operating experience from another nuclear plant, Wolf Creek Nuclear Operating Corporation personnel identified that the pressurizer level at Wolf Creek Generating Station had exceeded the value in the Inadvertent Operation of Emergency Core Cooling System (IOECCS) analysis, during Mode 3. The IOECCS analysis assumes that initial reactor power is at 102% and initial pressurizer level is at a maximum level of 57%. Given these assumptions, operators must be able to terminate the IOECCS within eight minutes to prevent pressurizer overfill. Operation with pressurizer level above 57% is not bounded by the current analysis. The cause of the event was that the information regarding the assumed pressurizer level for the IOECCS analysis was not identified during the procedure review process.
4822010010 | Wolf Creek | 09/22/2010 | 03/25/2011 | ML11090006 | <strong>Inadequate Analysis Results in a Component Cooling Water Train to be Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>The Wolf Creek Generating Station (WCGS) Component Cooling Water (CCW) system consists of two trains with two 100 percent capacity pumps per train, each supplying cooling water flow to the independent safety loads and a common service loop. On September 22, 2010 a question was raised about the analysis of a postulated pipe break in the non-seismic portion of the common service loop, to Radwaste. Review of the analysis determined that the net positive suction head for the CCW pump could be jeopardized, making the CCW train aligned to Radwaste inoperable. The train of CCW connected to the service loop was declared inoperable on September 22, 2010, at 1317. As interim action, the CCW train was restored to operable status on September 23, 2010, at 0241, by isolating the Radwaste portion of the service loop from the rest of the service loop. Long-term resolution of this issue is the installation of a design modification.
4822010011 | Wolf Creek | 10/05/2010 | 12/06/2010 | ML10349047 | <strong>Completion of a Technical Specification Required Shutdown due to an Essential Service Water Leak</strong><br /><i>Abstract:&nbsp;</i>On October 2, 2010 indications of water leakage from a buried portion of the 'A' Essential Service Water (ESW) system was identified. Wolf Creek Generating Station conservatively declared the train inoperable and entered the applicable Technical Specifications. Workers excavated the soil and found a through-wall leak in the pipe. The leakage could not be fixed within the allowed outage time of the Technical Specifications and the plant was shutdown to Mode 5. The cause of the through-wall leak was internal diameter initiated pitting. The through-wall leak on the 'A' ESW pipe was repaired by encapsulation. Subsequent Engineering evaluation of the through-wall leak concluded that the pipe possessed sufficient structural integrity to endure all design loadings and that the system was capable of performing its design safety function.
4822010012 | Wolf Creek | 10/17/2010 | 12/16/2010 | ML10357004 | <strong>Reactor Trip due to Operators Inability to Control Steam Generator Level Oscillations at Low Power</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2010 at 0952 CDT, Wolf Creek Generating Station was at approximately 15% power during a startup when a turbine trip and Feedwater Isolation Signal occurred due to High-High Steam Generator level. An automatic reactor trip occurred at 0953 CDT due to decreasing SG level. All control rods fully inserted and the Reactor Trip System and the Engineered Safety Feature Systems performed as expected. Emergency boration was initiated when reactor coolant system temperature dropped below 550 degrees Fahrenheit. Emergency boration was secured after 58 minutes when RCS temperature was raised to greater than 550 degrees Fahrenheit. The cause of the trip was the Control Room operators were unable to maintain SG levels at low power. Procedures were revised to address the issue. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report (USAR) Section 15.2.7, "Loss of Normal Feedwater Flow."
4822010013 | Wolf Creek | 11/18/2010 | 01/17/2011 | ML11025033 | <strong>Potential Safe Shutdown Unanalyzed Condition Identified During Post-Fire Safe Shutdown Circuit Analysis</strong><br /><i>Abstract:&nbsp;</i>During performance of a post-fire safe shutdown (PFSSD) circuit analysis, a commitment from Wolf Creek Generating Station LER 2010-003, the following issues were identified for a potential fire in the control room: (1) Certain fuses associated with the Train B emergency diesel generator (EDG) exciter/voltage regulator could fail, that would result in no power being available to supply credited PFSSD equipment. (2) The pressurizer power operated relief valves could fail open and not be closed within 3 minutes as required by the thermal hydraulic analysis. (3) Dampers in the Train B essential service water and Train B EDG rooms could fail and cause the room temperature to exceed the maximum design temperature for the rooms or drop below the minimum design temperature. The cause was determined to be an inadequate review of control room circuitry for impact on PFSSD. A number of opportunities should have identified the issues including a root cause evaluation conducted in 2007. An hourly fire watch is in place in the control room and procedure OFN RP-017, "Control Room Evacuation," has been revised to address these issues. These issues have low safety significance.
4822010014 | Wolf Creek | 12/06/2010 | 02/04/2011 | ML11046068 | <strong>Technical Specification Required Shutdown due to Inadequate Planning Resulting in Extended Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2010, at 0948 Central Standard Time (CST), Wolf Creek Generating Station (WCGS) entered Mode 3 in accordance with Required Action H.1 of Technical Specification (TS) 3.8.1, "AC Sources - Operating." The TS required shutdown was due to inoperability of the Train 'A' emergency diesel generator (EDG), which was removed from service on November 29, 2010, for planned maintenance. The cause of the TS required shutdown of WCGS was the inability to return the EDG to operable status within the seven-day completion time of Required Action 8.4.2.2 of TS 3.8.1. The extended out-of-service time was due to excessive emergent work activities, including a drop in peak firing pressure in one cylinder during the surveillance run of the EDG. The Command and Control structure used for seven-day TSEOs was changed to improve management of work delays and effectively control emergent work.
4832010001 | Callaway | 01/22/2010 | 05/21/2010 | ML10145000 | <strong>Emergency Core Cooling System MODE 4 Operating Practices Prohibited by Current Technical Specification 3.5.3</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2010, while in MODE 1 at 100% power Callaway Plant identified that plant procedure OTO-BB-00010 Rev. 0, SHUTDOWN LOCA, did not instruct operators to align the Residual Heat Removal (RHR) cross-tie valves (EJHV8716A/B) in order to supply low-head emergency core cooling flow to each of the four Reactor Coolant System (RCS) cold leg injection nozzles. High-head and low-head injection into the reactor vessel via four cold-leg nozzles is described as a necessary capability for mitigation of a loss of coolant accident (LOCA) during MODE 4 per the Bases for Plant Technical Specification (T/S) 3.5.3, “Emergency Core Cooling System (ECCS) Shutdown.” This event is being reported as a condition prohibited by T/S per 10CFR50.73(a)(2)(i)(B). This issue is also reportable per 10CFR50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function due to a procedural deficiency. OTO-BB-00010 did not adequately support the RHR low-head ECCS function required for mitigation of a LOCA in MODE 4. OTO-BB-00010 has now been revised to ensure compliance with T/S 3.5.3 and the assumptions of the MODE 4 LOCA analysis which was clarified as a result of this event. The Root Cause is the failure to properly recognize the licensing topical report behind the applicable safety analysis for T/S 3.5.3 and the failure to fully implement the MODE 4 LOCA mitigation capability required by T/S 3.5.3 within site procedures. The Corrective Action to Prevent Recurrence was to develop and implement a site-specific MODE 4 LOCA flow evaluation based on the licensing topical report, thus to confirm the ECCS requirements for accident mitigation.
4832010002 | Callaway | 02/19/2010 | 04/20/2010 | ML10110049 | <strong>Anticipatory Motor-Driven Auxiliary Feedwater Actuation Function Rendered Inoperable in Mode 1</strong><br /><i>Abstract:&nbsp;</i>On 2/19/10, upon review of industry operating experience, Callaway Plant identified a condition in which the actuation logic for anticipatory start of the Motor-Driven Auxiliary Feedwater (AFW) pumps upon trip of both Main Feedwater (MFW) pumps would not be satisfied as required by Table 3.3.2-1 Function 6.g of the Technical Specifications (TS). This condition exists when one MFW pump (MFP) is operating and the second MFP in secured in a 'Reset' configuration. Low pressure on the MFP Turbine Trip Oil Header is used to indicate a MFP trip. However, the Trip Oil Header is also used to keep the 'Reset' MFP turbine stop valves open such that the Trip Oil Header pressure of a 'Reset' MFP is the same as an operating MFP that is providing flow to the steam generators. As a result, all MFW flow would be lost upon the trip of the operating MFP, but the actuation logic for anticipatory start of AFW upon trip of both MFPs would not be satisfied. The cause of this event has been identified as a lack of detailed design basis information regarding this function. Corrective actions include TS to allow both channels associated with a 'Reset' MFP turbine to be placed in a tripped condition (enabling the AFW actuation logic to be satisfied as required upon trip of the operating MFP) and the addition of information related to this function into licensing documents and procedures.
4832010003 | Callaway | 02/19/2010 | 04/20/2010 | ML10110048 | <strong>Safety System Actuation After Loss of a Switchyard Bus</strong><br /><i>Abstract:&nbsp;</i>Loss of B Train Off-site Vital Power Callaway Plant was in Mode 1 at 100 percent power on February 19, 2010. Work was in progress to install grounds on a switchyard breaker. At 2145, the 'A' Safeguard Transformer was lost which resulted in loss of the 'A' switchyard bus. Electricians in the switchyard reported hearing a loud boom and saw what looked like an arc off of one of the ends of the 'A' safeguard transformer, and then saw sparks cascading down. The loss of the 'A' switchyard bus combined with the breaker the electricians were working on being out of service, resulted in loss of `13' train offsite power with subsequent actuations consistent with loss of one vital AC train. The 'B' emergency diesel generator started and loaded. 'A' train offsite vital power and emergency diesel generator were available. Emergency systems responded as expected, except for one steam generator blowdown isolation valve. The cause for the loss of the 'A' Safeguard Transformer was a low side phase-to-phase fault external to the 'A' Safeguard Transformer. The most probable cause of the fault was a conductive foreign material or that an animal bridged the air gap between transformer low side bushing terminals. No evidence of the fault initiator was found and therefore a root cause could not be verified.
4832010004 | Callaway | 03/02/2010 | 04/30/2010 | ML10120053 | <strong>Unanalyzed Single Failure Component for Ultimate Heat Sink/Essential Service Water</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2010 with the plant in MODE 1 at 100% reactor power, a latent design issue was identified in regard to the essential service water (ESW) system and ultimate heat sink (UHS). Upon review of a calculation for UHS performance, it was determined that a limiting single failure had not been evaluated. During a Loss of Coolant Accident (LOCA), both ESW trains are assumed to operate for the first 8 hours of the accident. If a UHS bypass valve were to fail during a LOCA, flow from one train of ESW would be cooled by the UHS cooling tower while flow from the other train of ESW would flow directly to the UHS pond. This would lead to the UHS pond temperature increasing more quickly than previously analyzed, potentially exceeding the UHS pond temperature design basis accident limit in as little as an hour with no operator actions. The cause for this unanalyzed condition is failure to re-evaluate the UHS/ESW single-failure analysis when UHS cooling tower capacity was questioned during construction of the plant. For corrective action, emergency operating procedures will be revised to include operator action if UHS bypass valves are lost during an accident scenario. Design procedures are being updated to minimize the probability of generating non-conservative specifications, using non-conservative design inputs and assumptions in a calculation, and not evaluating single active failure in plant modifications as the corrective action to prevent recurrence.
4832010006 | Callaway | 04/15/2010 | 06/11/2010 | ML10165007 | <strong>Absence of Vent Valve in RHR Heat Exchanger 'B' Discharge Line Resulted in Incomplete TS Surveillance</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2010, during the performance of an inspection following the guidance of NRC Inspection Manual Temporary Instruction 2515/177-01, the NRC Resident Inspectors identified a location upstream of the 'B' RHR accumulator injection supply isolation valve, EJHV8809B, where the Emergency Core Cooling System (ECCS) surveillance procedure does not direct venting or the performance of ultrasonic testing (UT) to verify there is no accumulated gas. This resulted in the failure to verify the subject piping was full of water every 31 days as required by Technical Specification (TS) Surveillance Requirement (SR) 3.5.2.3. This condition therefore constituted a condition prohibited by the Technical Specifications, as TS SR 3.0.3 (for a missed surveillance) was neither able to be applied nor met. An evaluation has determined that there were two causes of this event: inadequate design and inadequate performance monitoring. Corrective actions taken as a result of this condition include installation of a vent valve upstream of EJHV8809B and on line EJ-026-BCB-6". Corrective actions intended to reduce the probability of similar events occurring in the future include revisions to Operations procedures.
4832010007 | Callaway | 08/11/2010 | 10/07/2010 | ML10281051 | <strong>Violation of Technical Specification 3.6.3, "Containment Isolation Valves"</strong><br /><i>Abstract:&nbsp;</i>At 2215 on August 10, 2010, a surveillance was being performed on normally open containment isolation valve (CIV) EGHV0059. During this surveillance, CIV EGHV0131 (EGHV0059 bypass) was opened under administrative controls to maintain a flow path. An operations technician (OT) was stationed near EGHV0131 and in communication with the Main Control Room (MCR) to close EGHV0131 when directed by the reactor operator. During this surveillance, EGHV0059 failed and was closed and deactivated in accordance with Technical Specification (TS) 3.6.3, while EGHV0131 continued to be maintained open. At approximately 0015 on August 11, 2010, the OT was relieved as the dedicated operator and an operator stationed in the auxiliary building (AB) became the designated operator for closing EGHV0131 as directed by the MCR. This configuration remained until a concern was expressed at 1422 on August 11, 2010 that the administrative controls provision of TS 3.6.3 was not being met. However, it was concluded that a violation of TS 3.6.3 had occurred for the time when the operator in the AB was credited to be the designated operator. The root cause of this event was determined to be conflicting/incomplete procedure guidance. The Corrective Action to Prevent Recurrence is to revise the affected procedures, thus to provide complete and consistent guidance on administrative controls for the purpose of TS 3.6.3.
4832010008 | Callaway | 09/23/2010 | 02/28/2011 | ML11060074 | <strong>Inadequate Analysis Results in a Component Cooling Water Train Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>The Component Cooling Water (CCW) system consists of two trains with two 100% capacity pumps per train, each supplying cooling water flow to its independent safety loads and a common service loop. On September 23, 2010 several non-conservative assumptions were identified in the calculation that analyzed a postulated pipe break in the non-seismic portion of the service loop to the Radwaste building. Review of the analysis determined that the net positive suction head for the CCW pump could be jeopardized, making the CCW train inoperable. The train of CCW connected to the service loop was declared inoperable on September 23, 2010 at 1730. The CCW train was restored to operable status on September 23, 2010 at 1802 by isolating the service loop from the CCW train. As an interim measure, CCW to loads in the Radwaste building will remain isolated. During times when CCW is needed for the Radwaste building loads, Callaway will comply with the Action requirements of TS 3.7.7, Component Cooling Water System. Calculation M-EG-12-C, Component Cooling Water System, was superseded by a new calculation. A flow orifice will be installed in the safety related seismic Category 1 portion of the CCW supply lines to the Radwaste building. A check valve will be installed in the safety related seismic Category 1 portion of the CCW return lines from the Radwaste building.
4832010009 | Callaway | 12/01/2010 | 12/06/2011 | ML11340036 | <strong>High Energy Line Break (HELB) Program Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On 12/01/2010, evaluation of a Nuclear Oversight audit of Engineering Programs identified cases in which Callaway Plant did not properly implement High Energy Line Break (HELB) defenses. These cases of improper HELB barrier and boundary control challenged equipment Operability. In some cases, components may not have been able to perform their HELB mitigation functions if the associated HELB event had occurred. These components include a Component Cooling Water heat exchanger bypass valve, a control room air conditioning unit, and level transmitters for the Reactor Vessel Level Indication System. The failure to properly implement HELB defenses was determined to be a programmatic deficiency of the HELB Program at Callaway Plant. Technical guidance in the Hazard Barrier Program procedure and management oversight of the HELB program were both determined to be insufficient to prevent challenges to equipment Operability. Corrective actions include the development of appropriate compensatory measures, calculation of HELB hazard information and barrier capabilities, increased management oversight, and verification that HELB analysis of record reflects current plant configuration.
4832010010 | Callaway | 12/01/2010 | 03/31/2011 | ML11091014 | <strong>Violation of Technical Specification 3.0.3 due to 'B' Class 1E Electrical Equipment A/C Unit Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 9/21/2010 Callaway Plant questioned the existing practice, per FSAR Sec.16.7.13, of allowing the affected Engineered Safety Feature switchgear, vital AC buses, and safety-related batteries/chargers to be considered OPERABLE for up to 7 days when either of the two Class 1E electrical equipment A/C units is inoperable, provided certain compensatory actions are met. Re-evaluation of the provisions of FSAR Sec. 16.7.13 under the corrective action program determined that the existing practice was not a correct application of the plant Technical Specifications (TS). It has been determined that the correct application of the TS, upon discovery of an inoperable A/C unit, is to immediately declare the affected electrical equipment inoperable and enter the applicable Conditions and Required Actions of TS 3.8.4, 3.8.7, 3.8.9, and 3.0.3. With a correct understanding of the applicable TS for the A/C units and the equipment they support, a review of events involving inoperability of the trains in the past 3 years was conducted to determine whether a reportable condition had existed. Based on a question from the NRC Resident Inspector on 12/1/2010, further review was conducted, from which one event in 2008 involving inoperability of the 'B' unit was identified and has now been determined to be reportable as a condition prohibited by the TS. Corrective actions include developing a Technical Specification for the Class 1 E electrical equipment A/C trains.
4982010001 | South Texas 1 | 02/03/2010 | 04/05/2010 | ML10102005 | <strong>Unit Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2010, with Unit 1 at 100% power, monthly shutdown and control rod testing was being performed. Previously on January 6, 2010, control rod C-5 had been determined to be inoperable, but trippable. During testing on February 3, a second control rod (B-12) was determined to be inoperable, but trippable. Attempts to realign the control rod with its bank were unsuccessful. Consequently, TS 3.0.3 was entered and the Unit was shutdown to Mode 3. This event is reportable per 10 CFR 50.73(a)(2)(i)(A), "The completion of any nuclear plant shutdown required by the plant's Technical Specifications." The cause of this event was insufficient removal and dispersion of the.corrosion products originating from the normal fabrication and passivation process of the new CRDM latch assemblies associated with the Unit 1 Replacement Reactor Vessel Head. All shutdown and control rods remained fully trippable during this event. There were no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
4982010003 | South Texas 1 | 08/20/2010 | 10/19/2010 | ML10298001 | <strong>Unit 1 Reactor Trip During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2010 at 1525 hours, the Unit 1 Reactor automatically tripped during the performance of a scheduled surveillance test of the Solid State Protection System (SSPS). The reactor trip was caused by a human performance error that occurred when the procedure performer and verifier missed a procedure step. The Root Cause for the reactor trip was determined to be: 1. Procedure place keeping standards for the site were less than adequate and 2. Supervisory Oversight of surveillance test procedure 0PSP03-SP-0006R became ineffective when the Senior Reactor Operator (SRO) stepped outside of his oversight role and became involved in the process. There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment.
4982010004 | South Texas 1, South Texas 2 | 09/30/2010 | 11/25/2010 | ML10340008 | <strong>North Switchyard Bus De-Energization Resulting in Loss of Offsite Power ESF Actuation on Train 1B</strong><br /><i>Abstract:&nbsp;</i>At 1904 on September 30, 2010, with South Texas Project (STP) Units 1 and 2 both at 100% power, the north bus in the STP switchyard unexpectedly de-energized. The de-energization of the north bus resulted in a loss of power to Standby Transformer 1 which was supplying power to the Train 1B engineered safety features (ESF) 4160V bus. The loss of offsite power (LOOP) to the 1B ESF bus resulted in a LOOP ESF actuation and starting the 1B train Standby Diesel Generator and subsequent automatic actuation of 1B safety train equipment. The direct cause was attributed to a wiring error during maintenance on 345kV switchyard circuit breaker Y530 performed by a contractor employed by the Transmission & Distribution Service Provider (TDSP). The root cause of the event was insufficient management oversight and reinforcement of expectations and standards for managing switchyard activities. Corrective actions include procedure changes to better integrate TDSP activities into the STP work control process procedures and the assignment of a management owner to act as interface between STP and the TDSP regarding switchyard maintenance and other activities. There were no personnel injuries, no offsite radiological releases, and no damage-to safety-related equipment.
4992010001 | South Texas 2 | 12/14/2009 | 06/27/2010 | ML10183025 | <strong>Essential Cooling Water System Leak</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2009, Unit 2 Essential Cooling Water (ECW) Train C was found to be inoperable due to a crack in the Component Cooling Water (CCW) heat exchanger 2C ECW return line near a connection to a vent valve. Actual inoperability of the ECW train was determined to have occurred on December 14, 2009, but was not recognized at the time. Operability was restored on December 25, 2009, when the repair was complete. Technical Specification 3.7.4.a requires that at least two ECW trains be operable while in Modes 1, 2, 3, and 4. If one ECW train is inoperable, power operation may continue provided that operability is restored within seven days, or the requirements of the Configuration Risk Management Program are met. Otherwise, the plant is to be in Hot Standby within the next six hours and in Cold Shutdown within the following thirty hours. Because Unit 2 ECW Train C was inoperable for eleven days without taking the appropriate action required by Technical Specifications, this event is reportable under 10 CFR 50.73(a)(2)(i)(B). Definitive procedural guidance for applying Generic Letter 90-05, "Guidance for Performing Temporary Non-Code Repair of ASME Code Class 1, 2, and 3 Piping," had not been provided to condition reviewers. The cause of the crack initiation could not be determined. Propagation of the crack was due to vibration in the piping resulting from throttle flow cavitation. Procedure and design changes will be applied to prevent a repeat occurrence. Only one ECW train was affected by this condition. There were no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment.
4992010002 | South Texas 2 | 07/07/2008 | 03/11/2010 | ML10075024 | <strong>Unanalyzed Condition Regarding the Fire Protection System</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2008 at 2211 hours, both Unit 1 and Unit 2 control rooms received fire detection system alarms on the fire detection computer due to reduced pressure in an isolated portion of the fire protection main ring header. In response to the alarms, an Equipment Clearance Order was released that had isolated the header. The number one diesel-driven fire pump was started to maintain system pressure. The fire protection main ring header was restored to service on July 8, 2008 at 0057 hours. The root cause of the inadvertent isolation of a portion of the fire protection main ring header was the general absence of adequate process controls for assessing the aggregate impact of multiple work activities on the fire protection system functionality. Corrective actions included revising procedures for establishing fire protection system functionality requirements and for establishing plant operations department administrative guidelines to provide clear guidance and direction for removal of fire protection system components and/or sections of the fire water main from service. A fire protection system owner was designated to coordinate all activities that affect system configuration. The inadvertent isolation of a portion of the fire protection main ring header adversely impacted three fire areas in Unit 2 containing redundant safe shutdown equipment. The Fire Hazards Analysis credits the availability of water suppression in these affected fire areas for safe shutdown in the event of a fire. This event resulted in no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment.
4992010003 | South Texas 2 | 05/22/2010 | 07/19/2010 | ML10207010 | <strong>Containment Purge in Operation When Not Permitted by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2010, the Unit 2 Supplemental Containment Purge Subsystem was used to reduce containment pressure. This is a routine operation used to maintain containment pressure consistent with Technical Specification requirements. A surveillance test was in progress that required one of the two Solid State Protection System (SSPS) containment isolation automatic actuation logic channels be taken out of service. With one logic channel out of service, containment purge valves are required to be kept closed. Required actions for an inoperable ESFAS instrumentation channel or interlock are shown in Technical Specification Table 3.3-3. With fewer than the minimum of two automatic actuation logic channels operable, operation may continue only if the containment purge supply and exhaust valves are maintained closed. Opening the containment purge valves when only one SSPS train is operable is not permitted under Technical Specifications. This condition is considered reportable under 10 CFR 50.73(a)(2)(i)(B) as a condition not allowed by the Technical Specifications. Initiation of supplementary containment purge with an inoperable SSPS train/channel resulted from inadequate personnel communications and a deficient procedure. Conduct of Operations requirements will be revised to ensure adequate communications and assignment of responsibilities, and procedures will be revised to enhance control over containment purge initiation. There were no personnel injuries, no offsite radiological releases, and no damage to other safety-related equipment. Because containment purge valves could still be closed on a signal from the operable logic channel, this is not a safety system functional failure.
4992010004 | South Texas 2 | 10/28/2010 | 12/20/2010 | ML10363040 | <strong>Loss of the Train A Essential Cooling Water (ECW) System due to a Loss of the ECW Intake Structure Ventilation Fan 21A</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2010 at 1235 hours, with Unit 2 in Mode 1 at 100 per cent power, the Train A Essential Cooling Water (ECW) System was declared inoperable due to a loss of the ECW intake structure ventilation fan 21A. The ventilation fan is a required support system for ensuring the operability of the Train A ECW System. The ECW System provides cooling for the Train A Engineered Safety Features (ESF) Standby Diesel Generator (SDG). Therefore, the Train A ESF SDG was declared inoperable and Action b of Technical Specification (TS) 3.8.1.1. was entered. Action b of TS 3.8.1.1 requires that with a SDG inoperable, demonstrate the operability of the TS required A.C. offsite sources by performing Surveillance Requirement (SR) 4.8.1.1.1.a within 1 hour. A subsequent investigation discovered that the ECW System had been inoperable earlier than the time that the ventilation fan was initially discovered not to be running so that the performance of SR 4.8.1.1.a. was not performed within the required TS time. The inoperability of the ventilation fan occurred at 1030 hours on October 28, 2010 during calibration of the fan's high temperature switch. The root cause of this event was failure to adhere to human performance practices such as a questioning attitude and failure to adhere to the referenced procedure provided in the work instructions regarding how to perform cable terminations during implementation of a design change to install the new switch in 2005. Corrective actions include revising work instructions for calibrating the high temperature switch to verify that control power is available to start the fan circuit after the calibration is completed; add the Operating Experience of this event to the Cable Termination training class; and discussing the Operating Experience with the appropriate disciplines at the station. There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment.
4992010005 | South Texas 2 | 11/03/2010 | 07/07/2011 | ML11195A02 | <strong>Startup Feed Pump 24 Breaker Failure and Unit 2 Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2010, the Startup Feed Pump (SUFP) 24 was being started to support a scheduled Partial Discharge Analysis as a preventive maintenance activity. At 1021 hours the SUFP was started but then after approximately 4 seconds the pump breaker tripped open. Computer data shows that approximately 8 seconds after the pump breaker tripped the voltage on Standby Bus 2H (which supplies power to the SUFP) spiked low to near zero volts and the Unit 2 reactor tripped on Reactor Coolant Pump (RCP) Undervoltage (the 2C RCP is also powered by Standby Bus 2H) . Standby Diesel Generator 23 started and began supplying Engineered Safety Features (ESF) Bus E2C due to Loss of Offsite Power to the ESF bus. Standby Bus 2F experienced a momentary voltage drop of approximately 1 second (Standby Buses 2F and 2H are both fed by the X winding of the Unit 2 Auxiliary Transformer) resulting in some A train loads being secured. Following the reactor trip, the plant was stabilized in MODE 3 at Normal Operating Pressure and Temperature. At 1038 hours an Unusual Event was declared for Unit 2 due to the breaker cubicle explosion associated with the SUFP breaker failure (ENS Event Number 46387). The breaker malfunction did not result in a fire. The Unusual Event was terminated at 1240 hours when the plant was stabilized in MODE 3. There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment. This LER is the planned LER supplement described in Revision 1 including a correction to the reporting criteria where criterion 20.2203(a)(3)(i) was inadvertently checked. This LER supplement provides the results of the respective Root Cause Evaluation and revises the appropriate reporting criteria accordingly.
4992010006 | South Texas 2 | 11/10/2010 | 01/18/2011 | ML11025026 | <strong>Technical Specifications Not Met for Reactor Coolant System Unidentified Leakage</strong><br /><i>Abstract:&nbsp;</i>At 0910 on November 10, 2010, while Unit 2 was in Mode 3, the operating crew identified an unexpected lowering of Volume Control Tank (VCT) level and an increased frequency of makeup. Unit 2 entered Action b of TS 3.4.6.2, Reactor Coolant System Operational Leakage, for unidentified leakage greater than one gallon per minute. Action b requires that the leakage be reduced to within limits within 4 hours or be in at least HOT STANDBY within the next 6 hours and in COLD SHUTDOWN within the following 30 hours. At 1052 RCS unidentified leak rate was measured at 1.955 gpm. Leakage was discovered through the Reactor Coolant Filter 2B vent valve. The filter was removed from service at 1531. TS 3.4.6.2 Action b was exited at 1728. Engineering review determined that the leak rate through the 2B Reactor Coolant (RC) Filter vent valve had exceeded 1.0 gpm since November 5, 2010 when the filter was replaced with Unit 2 in Mode 5. The leakage was not isolated until November 10, 2010 at 1531 hours, which exceeded the time permitted by TS 3.4.6.2 to be in cold shutdown if the leakage could not be reduced within limits. Additionally, the plant heatup to Modes 4 and 3 was made with the limiting condition of operability not met, a condition prohibited by Technical Specification 3.0.4. The root cause was determined to be a lack procedural guidance. The applicable procedure is being revised to ensure monitoring for indications of excessive leakage prior to entry into Mode 4.
5282010001 | Palo Verde 1 | 03/07/2010 | 05/06/2010 | ML10133026 | <strong>Automatic Reactor Trip Due to a Loss of a Non-Class 13.8 kV (Calvert) Bus</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2010, at approximately 1115, Mountain Standard Time, Unit 1 experienced an automatic reactor trip subsequent to a ground fault on a non-class 13.8 kV (Calvert) bus (1 E-NAN-A03). The ground fault on 1 E-NAN-A03 caused a loss of power to the non-class 13.8 kV bus 1 E-NAN-S01. Consequently, two of the four Reactor Coolant Pumps were de-energized resulting in the reactor trip. The Main Feedwater Pump B was manually tripped, and the Auxiliary Feedwater Pump B was manually started. Due to the loss of power on the affected non-class 1 E buses, several main turbine and main steam valves failed to close resulting in higher than normal post shutdown steam flow and an undesired Reactor Coolant System (RCS) cooldown. Auxiliary Operators manually closed the affected valves, but cooldown of the RCS continued due to seat leakage of some secondary system valves. The Main Steam Isolation Valves (MSIVs) were closed to mitigate the undesired RCS cooldown. Subsequently, it was determined prudent to cooldown to Mode 5 to establish plant conditions for the bus repair. No automatic engineered safety feature actuations occurred during the event and none were required. All safety-related buses remained energized from normal off-site power during and following the reactor trip. The bus was taken off-site for evaluation and repair prior to restarting Unit 1 on March 19, 2010. The event investigation revealed the fault was caused by a combination of water intrusion and degraded bus insulation. In the past three years, Palo Verde Nuclear Generating Station has not reported a similar event where the loss of a non-class power bus due to a bus failure resulted in a reactor trip.
5282010002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 05/07/2010 | 12/29/2010 | ML11014054 | <strong>Main Steam Isolation Bypass Valve Calculation Error Resulting in Operation Prohibited by Tech Spec</strong><br /><i>Abstract:&nbsp;</i>On May 7, 2010, Palo Verde discovered that a calculation used for the closing force required for Main Steam Isolation Bypass Valves (MSIBVs) was non-conservative. During the Component Design Basis Review (CDBR), it was determined that the closing force would be inadequate to fully close the MSIBVs upon the receipt of a Main Steam Isolation Signal when Steam Generator (SG) pressure is greater than 700 psi. This condition renders the MSIBVs inoperable when SG pressure is above 700 psi. At the time of discovery, Unit 1 was in Mode 5 and the MSIBVs were not required to be operable; Unit 2 and Unit 3 were in Mode 1, and the MSIBVs were required to be operable. Both Unit 2 and Unit 3 entered the applicable Technical Specification (TS) Limited Condition for Operation (LCO) 3.6.3, Containment Isolation Valves. As an immediate corrective action, Unit 2 and Unit 3 ensured the MSIBVs were closed, with their penetration flowpath isolated to comply with the conditions of TS LCO 3.6.3. Administrative barriers that existed at the time of the calculation revision (December 2000) were unsuccessful in preventing the error due to ineffective reviews and the lack of a questioning attitude. Calculations with the potential for this error were reviewed and evaluated. The extent of condition evaluation determined the error was limited to safety-related Air Operated Valve (AOV) gate valves. No similar events involving a non-conservative calculation for an AOV have been reported by PVNGS in the last three years.
5282010003 | Palo Verde 1 | 05/02/2010 | 07/07/2010 | ML10197006 | <strong>Technical Specification Violation - Loss of Containment Building Equipment Hatch Closure Capability</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2010, during the Unit 1 refueling outage, the station discovered that the containment building equipment hatch (hatch) was not capable of being fully closed while core alterations were in progress on May 2, 2010. On two occasions, totaling approximately 4 hours and 47 minutes, core alterations were in progress and a potential existed that the hatch could not be fully closed. The investigation found that post-maintenance test procedures were not followed to ensure proper hatch motion after maintenance on both the east and west hatch hoist upper limit switches. As an immediate corrective action, the hatch west hoist upper and lower limit switches were readjusted and the hatch was closed and secured. In the past three years, Palo Verde Nuclear Generating Station has not reported a similar event where the containment equipment hatch was not able to be fully closed during core alterations.
5292010001 | Palo Verde 2 | 01/26/2010 | 03/29/2010 | ML10099016 | <strong>Essential Chiller B Inoperable Due to Incorrectly Positioned Head Pressure Control Bypass Valve</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2010, at approximately 1:17 p.m., Mountain Standard Time, the Essential Chilled Water System Chiller B (EC B) was declared inoperable due to low condenser pressure. The cause was the refrigerant head pressure control bypass valve was in the locked-open position instead of the required locked-closed position. The bypass valve had been left in the open position following Essential Cooling Water System (EW) B pump testing on December 24, 2009. In that configuration, EC B could have tripped on low chiller condenser pressure during low EC B heat loads. Operations restored EC B operability by repositioning the valve to the locked-closed position. During that 33-day inoperable period (a condition prohibited by Technical Specifications), the redundant train EC A chiller was also inoperable (a condition that could prevent the fulfillment of a safety function) for one hour and 40 minutes during a similar EW A pump test on January 7, 2010, while the respective refrigerant head pressure control bypass valve was open. No actual component failures occurred. The root cause was independent verification practices allowed verification of component positions without briefings and without use of verification signoff pages in the field. To prevent recurrence, verification practices will be revised to require use of those error prevention tools.
5292010002 | Palo Verde 2 | 09/15/2010 | 01/17/2012 | ML12031A19 | <strong>Inoperable Emergency Diesel Generator Due to Fuel Oil Transfer Pump Failure</strong><br /><i>Abstract:&nbsp;</i>On September 15, 2010, at approximately 05:46 Mountain Standard Time, during a surveillance test of Emergency Diesel Generator 2A (EDG-2A), the Diesel Fuel Oil Transfer Pump (DFOTP) for EDG-2A failed. An electrical short to ground had occurred in the DFOTP's motor termination box, caused by water in the motor termination box. The motor termination box and sections of the control and power cables from the pull box to the motor termination box inside the diesel fuel oil vault were replaced. The conduit was drained and cleaned. The control and power cables were spliced to interrupt the drain path and prevent possible future water drainage into the motor termination box through a path internal to the jackets around the cables. The condition which caused the failure would likely have prevented EDG-2A from meeting its mission time for a period of time that was in violation of technical specifications. Correspondingly, during periods when the redundant train, EDG-2B, was unavailable for maintenance or testing, DFOTP-2A's condition could have prevented fulfillment of the emergency AC power function. PVNGS reported a prior failure of DFOTP-2B which caused EDG-2B to become inoperable in LER 50-529/2009-001-00.
5302010001 | Palo Verde 3 | 10/07/2010 | 12/06/2010 | ML10349013 | <strong>Remote Shutdown Panel Pressurizer Auxiliary Spray Valve - Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2010, at approximately 1745 Mountain Standard Time (MST), while performing surveillance test 40ST-9ZZ20, Appendix Q, "Remote Shutdown Disconnect Switch and Control Circuit Operability," the pressurizer auxiliary spray valve, 3JCHBHV0203, failed to open from the remote shutdown panel (RSP) while the local/remote disconnect switch was in the local position. At the time of discovery, Unit 3 was in Mode 6 and the applicable Technical Specification (TS) Limited Condition for Operation (LCO) 3.3.11, Remote Shutdown System, did not apply. The inability to operate the pressurizer auxiliary spray valve from the RSP was due to a missing wire that was not installed during valve replacement in the previous Unit 3 refueling outage (May 2009). Investigation determined an inadequate design validation test failed to identify the missing wire. The missing wire was installed as an immediate corrective action, restoring the design configuration of the valve. The valve was tested to verify operation from the RSP, with the local/remote disconnect switch in the local position, with satisfactory results. In the past three years, PVNGS reported one event where post maintenance testing was considered to be inadequate (LER 50-529/2007-004-00). Corrective actions from the previous event would not have prevented this event.
5302010002 | Palo Verde 3 | 10/13/2010 | 06/27/2012 | ML12193A56 | <strong>Condition Prohibited by Technical Specification Resulting from Containment Spray Nozzle Obstruction</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2010, during scheduled surveillance test 73ST-9SI02, "CS Nozzle Air Test," of the Containment Spray (CS) system spray nozzles, seven obstructed nozzles were identified. Unit 3 was defueled at the time of discovery. The nozzles were obstructed for a period greater than allowed by Technica lSpecification (TS) 3.6.6 Limiting Condition for Operation. This represents a condition prohibited by TS and a common cause inoperability of independent trains. The root cause was boric acid solution was not removed from low points that entrapped water in the CS headers after these headers were filled with borated water during past CS header overfill events. The borated water subsequently evaporated causing boric acid to precipitate and form obstructions in the nozzles. The nozzles were inspected, the residue was removed, and the nozzles successfully passed the surveillance test procedure prior to entering Mode 4 at the end of the outage. Actions to prevent recurrence include inspection and cleaning of CS headers with low points to remove boric acid residue in Units 1, 2, and 3. Additionally, the Operations procedure for recovery from shutdown cooling to normal operations was revised to initiate corrective actions to drain the affected CS headers following overfill events. In the past three years, PVNGS reported one similar event in LER 50-530/2007-001-00.
5302010003 | Palo Verde 3 | 11/11/2010 | 01/18/2011 | ML11025047 | <strong>Essential Cooling Water System Train A Inoperable due to Degraded Room Air Handling Unit</strong><br /><i>Abstract:&nbsp;</i>On November 15, 2010, at approximately 0952 Mountain Standard Time (MST), during the monitoring of quarterly vibration measurements, increased vibration levels were noted on the essential cooling water (EW) system train A pump room air handling unit (AHU). After further evaluation, it was determined that reasonable assurance did not exist that the supporting AHU would meet its mission time of 30 days. Accordingly, on November 16, 2010, at 2245 MST, Unit 3 Operations personnel declared the EW train A inoperable due to the degraded EW pump room AHU and entered Condition A of Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.7. The condition was caused by several machined steps in the fan shaft that reduced the diameter of the shaft under the outboard fan bearing on the AHU. This condition subsequently led to the degradation of the outboard fan bearing. The bearing was replaced and Unit 3 exited TS LCO 3.7.7, Condition A, on November 18, 2010, at 1847 MST. No similar conditions have been reported by Palo Verde in the past three years.