## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192011001 | Oyster Creek | 05/04/2011 | 07/01/2011 | ML11188A11 | <strong>Changes and Errors in the Methodology Used by General Electric-Hitachi to Demonstrate Compliance with 10 CFR 50.46 Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2011, General Electric Hitachi (GEH) informed Oyster Creek Nuclear Generating Station (OCNGS) of a change in the calculation of Peak Cladding Temperature (PCT) and the Maximum Local Oxidation (MLO) that was based on corrections to errors in the previous calculation of record that were identified by the fuel vendor. On May 4, 2011, OCNGS determined that the multiple 10 CFR 50.46 Notifications resulted in a cumulative increase in analyzed PCT that exceeded the 10 CFR 50.46 PCT acceptance criterion of 2200°F. Also, the identified effect of the mode change resulted in an increase in the calculated MLO above the 10 CFR 50.46 acceptance criteria. Further review of 10 CFR 50.46(a)(3)(ii) determined that an 8-hour notification report to the NRC was required under 10 CFR 50.72(b)(3)(ii)(B). The notification was completed as required. The combined impact on PCT of the errors/changes described above is 115°F for the GE11 fuel and 145°F for the GNF2 fuel. These increases in PCT result in the licensing basis PCT exceeding the 10 CFR 50.46 acceptance criterion of 2200°F. Therefore, the PCT and MLO impact of these notifications has been offset by the calculation and implementation of revised Maximum Average Planar Linear Heat Generation Rate (MAPLHGR) values such that the maximum PCT and MLO values for both the GE11 and GNF2 fuel designs are returned to their original values of 2150°F and 16.5% respectively as documented in the vendor 10 CFR 50.46 notifications. Accordingly, this reanalysis meets the requirements of 10 CFR 50.46. As a result of the MAPLHGR limit adjustment the current LOCA analysis of record remains applicable and therefore, the offsite dose is still bounded by our current safety analysis. Therefore this event is not significant with respect to the health and safety of the public.
2202011001 | Nine Mile Point 1 | 05/02/2011 | 06/30/2011 | ML11193A06 | <strong>Turbine Trip due to Oil Pressure Fluctuations to the Turbine Master Trip Solenoid</strong><br /><i>Abstract:&nbsp;</i>At 2051 on May 2, 2011, Nine Mile Point Unit 1 (NMP1) experienced a turbine trip while operating at approximately 47 percent power (867 MWth). The main turbine master trip solenoid (MTS) actuated due to oil pressure fluctuations that allowed the pressure to drop below the MTS trip setpoint. These fluctuations were caused by leaking fittings on the MTS oil supply lines, binding of the secondary speed relay linkage, and main shaft oil pump discharge pressure fluctuations. The turbine trip initiated the high pressure coolant injection (HPCI) system as designed. The scram caused a drop in the reactor pressure vessel (RPV) water level that was mitigated by the HPCI injection. At 2052, RPV water level was restored above the HPCI low level actuation setpoint and the HPCI system initiation signal was reset. The root cause of the event was inadequate implementation of management job performance standards which resulted in the development and implementation of work performance documents which lacked sufficient detail associated with turbine maintenance activities. The immediate corrective action was to repair the turbine exciter/generator Falk coupling installation, replace the tubing and connections to the MTS supply lines, repair the secondary speed relay linkage, and repair the gears to the main shaft oil pump. Procedures will be developed to detail the disassembly, inspection, reassembly and testing of the NMP1 turbine, generator, exciter and control components. There have been no similar LERs at NMP1.
2202011002 | Nine Mile Point 1 | 05/06/2011 | 07/01/2011 | ML11193A06 | <strong>Changes and Errors in the Methodology Used by GE Hitachi to Demonstrate Compliance with 10 CFR 50.46 Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2011, Nine Mile Point Nuclear Station, LLC (NMPNS) was informed by its fuel vendor, GE Hitachi (GEH), of a change in its Emergency Core Cooling System (ECCS) evaluation model that would affect the calculation of peak cladding temperature (PCT) and maximum local oxidation (MLO) at Nine Mile Point Unit 1 (NMP1). This change was required to address three individual errors and a model change identified by GEH for the NMP1 calculation of record. On May 6, 2011, based on the information provided by GEH, NMPNS determined that correction of one of the identified errors and the model change would result in an increase in the calculated PCT and MLO above the acceptance criteria delineated in 10 CFR 50.46. Accordingly, this event is reportable in accordance with 10 CFR 50.46(a)(3)(ii). The causes of this event are non-conservative errors and a model change in the ECCS evaluation model. The NMP1 evaluation model was revised prior to startup from the Spring 2011 refueling outage to address the potential errors and the model change (i.e., prior to formal GEH notification). The NMP1 Maximum Average Planar Linear Heat Generation Rate limits were adjusted through a plant monitoring system update to maintain the existing PCT and MLO margins.
2372011001 | Dresden 2, Dresden 3 | 05/17/2011 | 07/18/2011 | ML11207A07 | <strong>Loss of Containment Cooling Service Water System due to Stop Log Installation</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2011, a quarterly preventative maintenance activity was planned to inspect and clean the safety related suction bay (Bay 13) in the plant's crib house. During the performance of the activity, maintenance personnel installed stop logs on both sides of Bay 13. In this configuration, the Containment Cooling Service Water (CCSW) system is rendered inoperable due to the limited capacity of water contained in the bay. Based on a subsequent investigation of the event, it was identified that a maintenance supervisor inappropriately had the work package revised to allow concurrent installation of both stop logs. Personnel involved did not recognize that this configuration would pose an adverse impact to the CCSW system. Following discussions of the package revision with other maintenance supervisors, the job supervisor recognized that installation of both stop logs was an uncommon practice due to its potential for isolating water sources. Operations personnel were notified of the configuration. Operations personnel entered the appropriate Technical Specification (TS) required actions for the system inoperabilities. The stop logs were removed from the 3A side of Bay 13 at approximately 1410 hours, which allowed the TS required actions to be exited. The CCSW system was inoperable for less than 4 hours. Since the probability of occurrence of a design basis accident was low in this case, the health and safety of the public were not compromised as a result of this condition.
2372011002 | Dresden 2 | 08/12/2011 | 10/11/2011 | ML11291A01 | <strong>Steam Leak Results in HPCI Inoperability</strong><br /><i>Abstract:&nbsp;</i>On Friday August 12, 2011, at 1429 CDT Dresden Radiation Protection personnel notified the main control room personnel of a steam/water leak in the Unit 2 Turbine Building. The leak was from the High Pressure Coolant Injection (HPCI) Inlet Drain Pot Inboard Drain line to the Main Condenser. Following removal of piping insulation, it was determined that Air Operated Valve 2-2301-29 had a through-wall leak. The Unit 2 HPCI system was isolated and declared inoperable at 1646, and Technical Specification 3.5.1, Condition G was entered and required actions taken. The failure mechanism of the through-wall leak was erosion of the carbon steel valve material by two-phase flow. The periodic inspection activity performed on the valve contained instructions for internal parts inspection. However, the instructions did not provide adequate guidance to ensure that valve body was inspected for degradation. The valve body was replaced and satisfactorily tested. Additionally, inspection instructions are being revised to ensure adequate inspection of susceptible valves. The safety significance of this condition is low. Automatic Depressurization and Low Pressure Emergency Core Cooling Systems were available and capable of providing makeup to the reactor vessel inventory. The health and safety of the public were not compromised as a result of this condition. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2372011003 | Dresden 2 | 10/17/2011 | 12/16/2011 | ML11362A39 | <strong>MSIV Closure Times outside of Technical Specifications Limits</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2011, with Unit 2 in Mode 4, plant personnel performed closure time testing of the Main Steam Isolation Valves (MSIVs). Dresden's Technical Specification Surveillance Requirement 3.6.1.3.6 requires the isolation time of each MSIV to be verified >= 3 seconds and <= 5 seconds. During testing, it was identified that three of eight valves closed faster than the time specified in the plant's Technical Specifications. The cause of the fast closure times was related to a procedural deficiency which allowed the valves' closure time to be set with little or no margin to the minimum closure time. Additionally, heat degradation of a full closed limit switch was noted in one instance. The valves were repaired and successfully retested. The as-left closure times were within the limits of the required Technical Specifications Surveillance Requirement. The safety significance of this condition is low. A sensitivity case utilizing the actual closure times determined that less than a five psi increase in vessel pressure would have resulted. The turbine control valve fast closure is assumed to occur in 0.1 seconds. Therefore the impact of the MSIV fast closure is bounded by existing analyses. The health and safety of the public were not compromised as a result of this condition. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) and 10 CFR 50.73(a)(2)(vii), any operation or condition which was prohibited by the plant's Technical Specifications and any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system, respectively.
2372011004 | Dresden 2, Dresden 3 | 10/24/2011 | 12/16/2011 | ML11362A47 | <strong>Personnel Error Results in Control Room Emergency Ventilation Air Conditioning System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2011, during refueling activities, plant personnel were performing an in-field verification of a clearance order protective boundary. During this safety walkdown, a maintenance technician opened a Division I 4kV bus compartment which contained the bus potential fuses erroneously. The fuses are directly connected to the compartment drawer. Therefore, the fuses are removed from their fuse holders as the drawer is opened. As the fuses were removed, the 4kV bus sensed an undervoltage condition and loads fed by the 4kv bus received a load shed signal. The Control Room Emergency Ventilation Air Conditioning (CREVAC) system was aligned to the Division I Containment Cooling Service Water (CCSW) system. As a result of the load shed signal, the CCSW system was not capable of supplying cooling flow to the CREVAC system. The cause of the event is due to personnel error. The technician failed to utilized human error prevention tools prior to opening the 4kV bus compartment. Personnel involved were coached. Additionally, an evaluation of robust barriers for bus pot fuse compartments is being performed. The safety significance of this condition is low. The fuses were removed for approximately seven seconds. The Control Room Emergency Ventilation system is required to be initiated within forty minutes following an accident. Due to short duration of the inoperability, the health and safety of the public and plant employees were not compromised as a result of this condition. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2372011005 | Dresden 2 | 10/28/2011 | 12/18/2012 | ML12363A04 | <strong>Standby Liquid Control Explosive Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On October 28, 2011, with Unit 2 in Mode 5, plant personnel performed a functional test of the Standby Liquid Control (SLC) system in accordance with plant procedures. When attempted, the "A" explosive valve failed to actuate during the functional test. The failed explosive valve was replaced and the "B" SLC system was tested to validate functionality was not lost. Troubleshooting by plant personnel revealed that the failure of the "A" explosive valve was related to the trigger assembly. The failed components were sent to the vendor for a failure analysis. The vendor analysis concluded the cause of the "A" explosive valve failure is thermal degradation of the primers explosive material. Upon further investigation it was found that the heat trace modification done in 2009 was not installed in accordance with the modification's specifications. The incorrect installation placed the heat trace around the "A" squib valve trigger assembly which subjected the assembly to higher than expected temperatures. This resulted in the thermal degradation of the explosive material. The safety significance of this condition is low. The "B" SLC system was functionally tested and demonstrated fully operable. The health and safety of the public were not compromised as a result of this condition. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B), Any operation or condition which was prohibited by the plant's Technical Specifications."
2442011001 | Ginna | 08/11/2011 | 10/04/2011 | ML11280A27 | <strong>Unanalyzed Condition due to Postulated Fire Causing a Station Blackout</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2011 the R.E. Ginna NFPA-805 project identified a fire scenario in the Turbine Building that could fail power to safeguards busses resulting in a station blackout, coincident with loss of the Turbine Driven Auxiliary Feedwater pump. While no damage to the emergency diesel generators or the output breakers occurs as a result of the fire, electrical interlocks prevent automatic closure of the diesel generator breakers due to closed normal supply breakers. Manual closure of a diesel generator breaker without first tripping the normal supply breaker may result in overload. Compensatory measures have been established to provide operators with guidance to monitor control power indication prior to attempting to manually close the emergency diesel generator breakers. In the event control power is unavailable to the normal supply breaker, operators will locally open the normal supply breaker prior to closing the emergency diesel generator breaker. Procedure changes have been made to incorporate this guidance. The cause is an inaccurate analysis of interlock effects in the Appendix R Safe Shutdown analysis. Additional corrective actions will be evaluated upon completion of the NFPA-805 Fire PRA and Fire Risk Evaluation.
2442011002 | Ginna | 08/23/2011 | 10/17/2011 | ML11293A11 | <strong>Train "B" Actuation Logic Circuit to Operate the "B" MSIV Was Not Operable</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2011, shortly after the 2011 Refueling outage, the "B" Main Steam Isolation Valve (MSIV) position indicating lights on the Main Control Board were observed to be flickering. Those lights subsequently went out. On August 23, 2011, when a fire water booster pump auto-started, the lights indicating that the "B" MSIV was open turned on. After the booster pump was secured, the lights turned off. Following subsequent troubleshooting, a fuse clip in the control circuit was determined to be not making contact with the fuse. It is suspected that relay actuation from the booster pump vibrated the fuse clip causing it to make contact. Troubleshooting on August 23, 2011, established that the fuse clip for the "B" train actuation circuit was damaged. This condition may have existed since June 11, 2011, thereby exceeding the required action time of the applicable Limiting Conditions for Operations (LCO). Maintenance was performed and the circuit was restored to service. The apparent cause is the use of fuse blanks for hanging clearance tags that caused excessive bending of the fuse clips. The corrective actions are described in Section IV.
2442011003 | Ginna | 10/11/2011 | 12/02/2011 | ML11343A02 | <strong>Reactor Trip due to Failure of Turbine Lube Oil Piping</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2011, the R.E. Ginna Nuclear Power Plant experienced an automatic reactor trip from 100% power. The trip was caused by a failure of the turbine lube oil piping internal to the turbine lube oil reservoir. The failed piping resulted in the main turbine Auto Stop Trip oil pressure switches activating on low oil pressure. The control room operators performed the appropriate actions of procedures E-0, Reactor Trip or Safety Injection and ES-0.1, Reactor Trip Response. Following the reactor trip, all safety systems operated as designed. The reactor was stabilized in Mode 3 while repairs were performed. The cause of the piping failure was determined to be high piping stresses from original construction in combination with substandard welding, routine maintenance, and cyclical fatigue. Corrective actions to prevent recurrence include a redesign of the piping to facilitate maintenance of associated check valves and to eliminate stress risers inherent to the original weld configuration. Additional corrective actions are summarized in section IV.B.
2472011001 | Indian Point 2 | 03/01/2011 | 02/21/2012 | ML12065A01 | <strong>Automatic Actuations of Emergency Diesel Generators due to Undervoltage on 480 VAC Vital Buses 5A and 6A Caused by a Loss of Offsite Power During Switchyard Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2011, Emergency Diesel Generators (EDGs) 21, 22 and 23 automatically actuated as a result of undervoltage on 480 Volt buses 5A and 6A due to a loss of 138 kV offsite power. 480 volt buses 2A and 3A remained energized as 6.9 kV buses 2, and 3 were energized from the Unit Auxiliary Transformer (UAT) which is connected to the Main Generator. All EDGs operated as designed. EDGs 21 and 23 were manually loaded onto buses 5A and 6A. Prior to the event Con Edison personnel were performing troubleshooting in the Buchanan switchyard on a metering circuit for 138 kV feeder 95332. The direct cause was loss of power to 480 volt safeguards buses 5A and 6A due to isolation of 138 kV feeder 95332 to the Station Auxiliary Transformer. Feeder 95332 isolated as a result of an arc on the feeder metering circuit current transformer (CT) switch that caused an imbalance. The CT circuit also supplies the first line pilot wire relay which tripped due to the imbalance. In accordance with design, the pilot wire relay tripped 138 kV breakers F2 and BT3-4 in the Buchanan switchyard and actuated protective relay 87L/138 which actuated lockout relay 86 STP tripping unit 2 breakers BT4-5 and 6.9 kV breakers 52/ST5 and 52/ST6 thereby isolating feeder 95332. The apparent cause was a failure of the current transformer (CT) test switch associated with the 138 kV feeder metering circuit to make-before-break. The test switch did not make-before-break due to corrosion on the contact surfaces. Corrective actions include closure of the test switch and restoring feeder 95332 to service. A Con Edison deficiency tag was placed on the switch. Troubleshooting was performed on the Buchanan switchyard feeder 95332 CT circuit and the test switch replaced. Con Edison revised their notification procedure for work impacting the switchyard. The event had no significant effect on public health and safety.
2472011002 | Indian Point 2 | 10/03/2011 | 12/01/2011 | ML11348A19 | <strong>Technical Specification (TS) Prohibited Condition Caused by an Inoperable 21 Service Water Pump for Greater than TS AOT due to a Faulty Inertia Latch in the Supply Breaker</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2011, the 21 Service Water Pump (SWP) failed to start as required. Personnel were sent to investigate the 21 SWP breaker and discovered the control power fuse had blown. Subsequently the breaker inertia latch was found to be stiff and binding throughout its movement. With the breaker inertia latch toggled and not reset, the breaker will be mechanically blocked from closing and will result in control fuse actuation. The direct cause was the breaker inertia latch was not reset and prevented the breaker from closing on demand. The root cause was a failure of workers to perform the required cleaning to remove the Zinc Dichromate plating as required by the Preventive Maintenance (PM) procedure. A contributing cause was a lack of OEM notification and ineffective direction for cleaning and removal of the zinc dichromate coating. Corrective actions included replacement of the breaker inertia latch, testing and return to service, review of previous DB breaker work packages to identify which latches and associated pins were not cleaned. Maintenance completed a human performance error review and re-enforced expectations of worker practices in department communications and prejob briefs. A Snapshot assessment on procedure use and adherence was performed and the MARC process implemented for placekeeping/procedure use events. The OEM provided a detailed step list for onsite breaker cleaning that will be incorporated into the breaker PM procedures. Breaker PM procedures (2-BRK-022-ELC, 0-BRK-410-ELC, and 0-BRK-401-ELC) will be revised to include the new OEM detailed step list for onsite cleaning of inertia latch bushing and pivot pin and include independent verification sign offs for the latch and pin cleaning steps. The event had no significant effect on public health and safety.
2472011003 | Indian Point 2 | 10/03/2011 | 12/01/2011 | ML11348A19 | <strong>Technical Specification (TS) Violation for Entry into TS 3.0.3 Inoperable Fan Cooler Unit Trains and Failure to Correct within 1 Hour and Actions Taken for Plant Shutdown</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2011, during performance of the quarterly surveillance test of the Containment Fan Cooler Unit (FCU) cooling water flow, all five FCUs failed to meet minimum flow requirements with the essential service water (SW) header (1/2/3 header) supplied by the 22 and 23 SW pumps. Operations entered Technical Specification (TS) 3.0.3 per TS 3.6.6.F for 3 trains of FCUs inoperable. In accordance with TS 3.0.3 operations initiated actions to place the plant in Mode 3 within 7 hours. Operations initiated turbine load reduction by approximately 5 MW and swap of the essential SW supply to the 4/5/6 header. Upon completion of the essential header swap, operations re-performed the quarterly surveillance test on the 4/5/6 header with satisfactory results. Based on successful completion of the test, Operations exited the TS 3.0.3 action statement and commenced power ascension to 100% power. The direct cause was excessive accumulation of silt in the SW Bay that resulted in degraded inlet flow to the SW pumps. The root cause was ineffective barriers established to monitor and remove silt accumulations that would affect SW pump Net Positive Suction Head (NPSH) margin failed to include predictive elements that account for changing environmental conditions. Corrective actions included sonar mapping and de-silting of the SW Bay. The sonar mapping frequency will be increased and the SW System Monitoring Plan will be revised to include alert and action levels for silt buildup. A comprehensive silt monitoring and mitigation plan will be developed to include predictive trending and monitoring methods. The event had no significant effect on public health and safety.
2492011001 | Dresden 3 | 01/15/2011 | 06/13/2011 | ML11173A05 | <strong>Control Rod Block Instrumentation Failure</strong><br /><i>Abstract:&nbsp;</i>On January 15, 2011, during control rod exercising Technical Specifications (TS) surveillance testing on Dresden Nuclear Power Station (DNPS) Unit 3, it was observed by control room personnel, that at times, the Rod Block Monitor (RBM) count circuit appeared to display too many local power range monitor (LPRM) inputs when a control rod having three LPRM strings was selected. Based on the information at the time, the crew concluded that the RBM remained operable. During subsequent troubleshooting on January 21, 2011, it was determined that both RBM channels had been inoperable since January 15, 2011 due to a failed circuit card. TS 3.3.2.1 Condition B required a channel to be placed in trip within one (1) hour. However on January 15, 2011, the operators did not properly identify this inoperability. Therefore the required action was not completed within the completion time specified by the plant's TS. The failed card was replaced on January 21, 2011, and the system returned to an operable condition. A subsequent causal investigation determined that a knowledge deficiency in conjunction with improper procedure usage resulted in an error in determining the operability of the RBM. Training Requests were submitted to perform a review of this event and the function of the count circuit meter. The RBM upscale rod block is not credited in the analysis of a rod withdrawal error and therefore the safety significance of the failure of the relay card is minimal. Health and safety of the public was not compromised as a result of this condition.
2502011001 | Turkey Point 3 | 03/06/2011 | 10/27/2011 | ML11314A10 | <strong>Manual Reactor Trip Due to Secondary Sodium Concentrations Exceeding Chemistry Limits</strong><br /><i>Abstract:&nbsp;</i>At approximately 11:35 on March 6, 2011, a sodium spike was detected in the 3AS hotwell. Subsequently the 3A1 and 3A2 circulating water pumps (CWP) were stopped. A rapid power reduction was commenced after a second sodium spike was experienced, in accordance with plant procedures 3-ONOP-100, "Fast Load Reduction", to approximately 23% power. A manual reactor trip was initiated per procedure at 16:44 (EST). Unit 3 was stabilized in Mode 3. All rods fully inserted and all safety systems functioned as required and there was no impact on the health and safety of the public. The NRC was notified of the event due to manual actuation of the Reactor Protection System [JC] (Event Number 46660) at approximately 19:38 (EST) on March 6, 2011. The cause of the sodium intrusion event was due to a tube flaw near the tubesheet of tube [SG, COND] R305/T5 in the 3BS tube bundle. High cycle, low stress fatigue, and cold work induced residual stresses likely contributed to the event. Corrective actions involved plugging several tubes and applying an overcoat of Duromar after tube plugging. Eddy Current Testing was performed on a selected tube population. A combination of foam/dimple plug testing was performed. Several tubes in the 3AN and 3BS water boxes were plugged and coated. A root cause analysis was performed. Long term, the Unit 3 and Unit 4 condenser tube bundles will be replaced under the Extended Power Uprate Project.
2502011002 | Turkey Point 3 | 08/11/2011 | 10/10/2011 | ML11291A01 | <strong>Loss of Intake Cooling Water due to Butterfly Valve Failure in Common Discharge Line</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2011 with Unit 3 at 100% power, Intake Cooling Water (ICW) System valve 3-50-406 (manually operated butterfly valve) failed in the closed position. Failure of this valve isolated the discharge flow path of ICW from the Component Cooling Water heat exchangers for approximately 28 minutes. During this period there was a loss of ICW function (communication with ultimate heat sink). The root cause of the event was inadequate evaluation of a configuration change in 2005 resulting in the creation of a single failure vulnerability. A contributing cause was station personnel failed to adequately risk rank a known condition resulting in low corrective maintenance prioritization. The valve failure mechanism was cyclic fatigue due to valve flutter from worn actuator parts. The fluttering condition was known from about 2001. Corrective actions include: 1) An alternate discharge flow path was opened on both units; 2) the actuator of valve 3-50-406 was repaired; 3) revision of the procedure for procedure control to require Engineering review of procedure revisions that change plant configuration; 4) revise the system and program health reporting procedure to require validation of risk ranking for all work orders; 5) review open green and white work orders to validate current risk ranking; and, 6) revise and implement Engineering and Operations initial and continuing training programs regarding butterfly valve failure modes and effects of these valves failing closed. The total conditional core damage probability is 5.6E-08 for this event, well below the NRC threshold of 1E-06 for additional inspections.
2542011001 | Quad Cities 1 | 04/19/2011 | 06/20/2011 | ML11174A03 | <strong>Loss of Both Divisions of Residual Heat Removal System</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2011, at 1430 hours, a water leak was discovered on the Unit 1 Emergency Diesel Generator Cooling Water Pump (EDGCWP) room cooler. As a result, the Unit 1 EDG (Division II) was declared inoperable and Technical Specification (TS) 3.8.1 was entered. (ENS Report No. 46769). At this time, Division I Residual Heat Removal (RHR) was inoperable for planned maintenance on the Division I RHR room cooler. In the event of a LOOP/LOCA scenario, RHR would not have been able to perform its safety function (i.e., Division I RHR was impacted by the ongoing room cooler maintenance and Division II RHR would not have had an operable on-site emergency power source). Note that at the time of discovery, offsite power was available to Division II RHR as well as the Division I and Division II Core Spray systems. At 1816 hours, the Division I RHR system room cooler was restored and Division I RHR was declared operable. The room cooler leak was caused by under-deposit corrosion on the piping due to raw water conditions. The through wall leak on the cooler was subsequently repaired and the Unit 1 EDGCWP room cooler was returned to operable status on April 21, 2011. Given the impact on the RHR system, this report is submitted in accordance with the requirements of 10 CFR50.73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2542011002 | Quad Cities 1 | 06/13/2011 | 08/12/2011 | ML11231A25 | <strong>Unit 1 Manual Reactor Scram due to Steam Leak</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2011, Quad Cities Unit 1 was performing startup from refueling outage Q1R21. During power ascension while at 61% power (560 MWe) a steam leak was identified on the main steam line downstream of turbine control valve #1 (1-5699-CV1). Reactor power was reduced and the reactor was manually scrammed. The steam leak occurred at a recently repaired sensing line that had previously leaked. A forced outage was initiated to investigate and performs repairs. The reactor and turbine responded as designed. Operators performed required actions safely and in accordance with procedures and training. There were no complications during the reactor scram and turbine trip, and all systems functioned as required. The root cause for the manual scram due to a steam leak from a pressure sensing line repair was that the capped pipe stub repair failed due to a fatigue induced flaw that was not known to exist at the time of the repair. Corrective actions included replacing the Unit 1 sensing line sock-o-lets with gamma plugs. Future corrective actions include replacement of the equivalent Unit 2 sensing line sock-o-lets with gamma plugs. The safety significance of this event was minimal. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A), as any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram.
2542011003 | Quad Cities 1, Quad Cities 2 | 07/06/2011 | 09/06/2011 | ML11252B07 | <strong>Control Room Emergency Ventilation Air Conditioning System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 6, 2011 at 1410 hours, the Unit 1/2 (common) "B" Control Room Emergency Ventilation (CREV) Refrigeration Condensing Unit (RCU) was declared inoperable due to an increase in vibration amplitude caused by a broken chiller compressor connecting rod. Operators performed required actions to safely secure the CREV RCU in accordance with procedures and training, and without complications. This resulted in entering Technical Specification 3.7.5, Condition A (30 day Action). This event affected both the Unit 1 and Unit 2 Control Rooms since they share a common control room and CREV system. The Train B CREV Air Conditioning (AC) system is a single train safety-related system that is designed to operate in a post-accident condition to maintain design temperature in the Control Room Envelope (CRE), and loss of the CREV AC could impact the plant's ability to mitigate the consequences of an accident. The CREV RCU chiller compressor connecting rod failure was caused by flooded starts of the compressor. The root cause of the flooded start was an unanticipated failure mode for the design application of the system. Corrective actions included replacing the failed compressor with a new compressor, and revising the frequency for vibration analysis on the B CREV RCU to monthly. Future corrective actions include installation of an automatic pump-down modification for the B CREV RCU compressor. The safety significance of this event was minimal. Given the impact on the CREV AC system, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2552011002 | Palisades | 01/22/2011 | 03/23/2011 | ML11083000 | <strong>Automatic Reactor Trip and Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2011, at 1735 hours, with the plant in Mode 1 at 100% power, the operation of relay 251-2/SPG3, station power transformer 1-3 neutral to ground, actuated relay 386B, generator direct trip lockout relay (backup), opening the main generator output breakers to the transmission system causing a turbine trip. The turbine trip actuated the reactor protective system to trip the reactor due to a loss of load. As expected, the auxiliary feedwater system started automatically to recover steam generator level. The cause for operation of the neutral to ground relay, and subsequent automatic plant trip, was a ground fault on a medium voltage cable that provides electrical power to bus 1G, via breaker 252-401, from station power transformer 1-3. The probable cause of the ground fault on the cable was determined to be flaws in the insulation, with the effects of moisture acting on these flaws over time, causing the insulation to degrade. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an actuation of both the reactor protection system and the auxiliary feedwater system.
2552011003 | Palisades | 04/18/2011 | 06/16/2011 | ML11171029 | <strong>Potential Condition Prohibited by Technical Specifications due to Jacket Water Pump Seal Leakage</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2011, the 1-2 emergency diesel generator (EDG) was removed from service for planned maintenance. The 1-2 EDG jacket water pump was replaced as part of the planned maintenance activities. On March 12, 2011, during the post-maintenance Technical Specifications (TS) surveillance testing, Entergy Nuclear Operations, Inc. (ENO) personnel discovered water leaking from the jacket water pump seal tell-tale drain, in intermittent volumes, at approximately one milliliter per minute. The subsequent operability evaluation determined that the leakage rate would not affect the operability status of the EDG. On March 13, 2011, 1-2 EDG was returned to operable status. On April 18, 2011, during the 1-2 EDG monthly TS surveillance test, increased leakage from the jacket water pump seal tell-tale drain hole was identified. The leakage was subsequently quantified at a rate of approximately ten milliliters per minute. Possible causes of the leakage are a manufacturing defect, damage to the pump seal during the manufacturing assembly process, damage during transport, or during the installation process. Due to the leakage rate rise, on April 21, 2010, ENO concluded additional detailed evaluations were required to maintain reasonable assurance the 1-2 EDG would be able to operate satisfactorily for the required thirty-day mission time. Without reasonable assurance of past operability, this condition is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS. Due to the ongoing evaluation of the condition, ENO may request a cancellation of this LER, or a supplement will be submitted to provide additional details.
2552011004 | Palisades | 05/10/2011 | 01/31/2012 | ML12031A23 | <strong>Turbine-Driven Auxiliary Feedwater Pump Inoperable in Excess of Technical Specification Requirements Due to Unexpected Trip</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2011, during routine auxiliary feedwater (AFW) pump Technical Specification (TS) testing, the turbine-driven AFW pump, P-8B, tripped due to the unexpected actuation of the mechanical overspeed trip linkage. Examinations revealed that the knife-edge of the trip resetting lever had disengaged from the hand trip lever latch area allowing the trip valve assembly to isolate steam flow to the turbine-driver. The initial causal evaluation determined supplemental contract employees had inappropriately applied grease to knife-edge area on the mechanical overspeed trip linkage during maintenance activities performed in the October 2010 refueling outage. Therefore, P-8B and its corresponding AFW train were considered inoperable for a period of time longer than the 72 hours allowed by TS 3.7.5.A. Based on the information available at that time, greasing of the knife-edge area on the mechanical overspeed trip linkage was considered to be the sole cause of the P-8B trip. Subsequent discussions with the turbine vendor revealed other possible causes for the trip. In addition, an independent analysis determined that the greasing alone, would not account for the overspeed trip of the pump turbine. As a result, additional investigations were completed. The outcome of the investigations did not identify any single physical cause for the pump trip. However, several other potential causes were identified. All the identified potential causes for the overspeed trip were addressed to ensure overspeed trip reliability. Planned corrective actions include a revision to the applicable maintenance procedure to incorporate vendor recommendations, process enhancements in the identification of critical maintenance activities and ensuring appropriate oversight of supplemental workers performing critical maintenance activities.
2552011005 | Palisades | 08/09/2011 | 10/03/2011 | ML11276055 | <strong>Service Water Pump Shaft Coupling Failure</strong><br /><i>Abstract:&nbsp;</i>On August 9, 2011, at 1202 hours, service water system (SWS) pump, P-7C, failed to deliver discharge pressure. As a result, a 72-hour limiting condition for operation (LCO) was entered in accordance with Technical Specification (TS) 3.7.8 condition A, due to one or more SWS trains being inoperable. The TS 72-hour LCO was exited after approximately 63 hours on August 12, 2011, at 0309 hours when repairs and testing on P-7C had been completed. Investigation into the failure revealed a broken pump shaft coupling. The failure mechanism of the coupling was determined to be intergranular stress corrosion cracking (IGSCC). A past operability evaluation concluded that, based on the failure mechanism of the coupling, P-7C would have been unable to operate satisfactorily for the required 30-day mission time. Therefore, P-7C was inoperable from July 10, 2011, until the coupling failed on August 9, 2011. During the period P-7C was considered inoperable, SWS pumps P-7B and P-7A were removed from service, on separate occasions for brief periods of times, for the performance of routine maintenance activities. The requirement of TS 3.7.8 condition C, that 100% of the required post accident SWS cooling capability be available, was met at all times during the 30-day period when P-7C was considered inoperable. The cause of the IGSCC was due to inadequate coupling design specifications. P-7A and P-7B shaft couplings were replaced using newly designed couplings. Replacement of the shaft couplings on P-7C, with the new design, is scheduled. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by TS and 10 CFR 21.21(c) for reporting defects, and failures to comply, associated with substantial safety hazards for dedicated items.
2552011006 | Palisades | 09/16/2011 | 11/10/2011 | ML11314036 | <strong>Valve Packing Failure Resulted in Reactor Trip and Auxilia Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2011, at 1402 hours, with the plant in Mode 1 at 100% power, primary coolant system (PCS) unidentified leakage increased to greater than one gallon per minute (gpm) for greater than four hours, and was unable to be reduced to within Technical Specification (TS) limiting condition for operation (LCO) 3.4.13 limits. TS 3.4.13, Required Actions B.1 and B.2 were entered, which required the plant to be in Mode 3 in 6 hours and Mode 5 in 36 hours. Power reduction commenced at 12% per hour. Subsequently, leakage increased to greater than 10 gpm. The site entered an unusual event at 1450 hours. The reactor was manually tripped at 1454 hours, and an emergency notification was made in accordance with the Site Emergency Plan. As expected, the auxiliary feedwater system started automatically to recover steam generator level. The unusual event was exited at 1934 hours The cause of the increased leakage requiring the reactor trip is attributed to a failed packing on a pressurizer spray control valve. The valve was repaired and the reactor was returned to full service on September 21, 2011. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in an actuation of both the reactor protection system and the auxiliary feedwater system.
2552011007 | Palisades | 09/25/2011 | 11/21/2011 | ML11326052 | <strong>Direct Current Electrical System Fault Causes Reactor Trip and Multiple Safety System Actuations</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2011, at 1506 hours, during planned maintenance activities on a direct current (DC) electrical distribution (ED) panel, ED-11-2, a short circuit fault between the positive and negative bus bars was introduced into the system. The fault was caused by the accidental contact between bus bar connectors within the panel. Subsequently, a partial loss of DC electrical system power occurred, causing an automatic reactor trip and multiple safety system actuations. The fault from ED-11-2 propagated upstream, resulting in a loss of left train DC power to two-of-four inverters and subsequent loss of alternating current (AC) power from the inverters to two-of-four preferred busses. The loss of power initiated a reactor trip via the automatic actuation of the reactor protection system (RPS). Additional automatic actuations include the closure of the main steam isolation valves (MSIVs), actuation of the safety injection system (SIS), actuation of the containment isolation system (CIS), and actuation of the auxiliary feedwater system (AFS). The MSIVs, RPS, SIS, CIS and AFS performed as designed for the loss of power condition. The root cause of the event was attributed to risk management processes not being followed, resulting in the failure to adequately manage the risk associated with the maintenance on the ED-11-2 panel. In addition, there was insufficient breaker and fuse coordination for the left train of the 125 volt DC system. An engineering change was approved and installed to reduce the probability of recurrence. Repairs to the affected DC electrical system components were completed and the reactor was returned to full power operation on October 3, 2011.
2552011008 | Palisades | 12/14/2011 | 02/13/2012 | ML12044066 | <strong>Reactor Protection System and Auxiliary Feedwater System Actuation</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2011, main feedwater (MFW) pumps, P-1A and P-1B, tripped due the loss of suction pressure. Operators entered the loss of MFW procedure and appropriately carried out the procedurally directed action to manually trip the reactor. As expected, the auxiliary feedwater system started automatically to recover level in the steam generators. The immediate cause for the loss of suction pressure to the MFW pumps was the spurious opening of MFW pump, P-1A, recirculation control valve, CV-0711. The spurious opening of CV-0711 resulted from a loss of electrical control power to the valve. The loss of electrical control power to CV-0711 was due to insufficient contact between the fuse holder clip and a fuse ferrule within a fuse block assembly of the control power circuitry. The possible causes for the lack of sufficient contact between the fuse holder clip and the fuse ferrule were the stretching of the fuse holder clip during the installation/removal of a fuse tag-out device, and/or fatigue of the fuse holder clip, induced by the repetitive removal/installation of the fuse. The control power circuitry, for CV-0711, was rerouted through an acceptable spare fuse block assembly and reenergized. The event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual actuation of the reactor protection system and the automatic actuation auxiliary feedwater system.
2592011001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/27/2011 | 06/27/2011 | ML11180A05 | <strong>Three-Unit Scram Caused by Loss of All 500-kV Offsite Power Sources</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2011, severe weather in the Tennessee Valley Service Area caused grid instability and loss of all 500-kV offsite power sources that resulted in automatic scrams of all three units. All three units were in Mode 1 at the time of the event. All scram systems were actuated, all actuations were complete, and required systems started and functioned successfully with the exception of an indeterminate position indication for the Unit 3 B Inboard Main Steam Isolation Valve. All onsite safe shutdown equipment was available with the exception of the 3B Emergency Diesel Generator (EDG), which was inoperable and unavailable due to planned maintenance. After the event, only one 161-kV line remained available for offsite power - all (seven) 500-kV lines and one (of two) 161-kV line were lost. All three units immediately entered Mode 3 (Hot Shutdown) with their respective 4-kV busses supplied by the onsite EDGs. On April 27, 2011, at 1701 hours, a Notification of Unusual Event (NOUE) was declared due to the loss of normal and alternate supply voltage to all unit-specific 4-kV shutdown boards for greater than 15 minutes and at least two EDGs supplying power to unit-specific 4-kV shutdown boards. On May 2, 2011, at 2050 hours, the NOUE was terminated following restoration of qualified offsite power sources.
2592011002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 04/28/2011 | 03/21/2012 | ML12083A19 | <strong>Loss of Safety Function (SDC) Resulting from Loss of Power from Unit 1/2 C EDG Due to Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On April 28, 2011, at 2338 hours Central Daylight Time, with all three units in cold shutdown and power supplied to the 4-kV shutdown buses by onsite emergency diesel generators (EDGs), Browns Ferry Nuclear Plant personnel performed a shutdown of the Unit 1/2 C EDG. The Unit 1/2 C EDG was shutdown due to a hydraulic oil leak in piping for the EDG governor that was causing voltage and frequency fluctuations. Following shutdown of the Unit 1/2 C EDG, the 4-kV shutdown board C, which was being powered by the Unit 1/2 C EDG, de-energized. This resulted in a loss of power to the 1B Reactor Protection System causing a Primary Containment Isolation System (PCIS) actuation. The PCIS isolation (Group 2) caused the loss of Shutdown Cooling on Unit 1 for 47 minutes. In addition, the loss of power to the 4-kV shutdown board C also caused the loss of the 2B Residual Heat Removal (RHR) pump leading to a momentary suspension of Shutdown Cooling for Unit 2. Shutdown Cooling for Unit 2 was immediately restored using the 2D RHR pump. The root cause of the oil leak was determined to be a less than adequate design of the Unit 1/2 C EDG governor oil piping to compensate for vibration loading. This report also constitutes a 10 CFR 21 notification.
2592011003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 05/02/2011 | 09/30/2013 | ML13275A14 | <strong>Loss of Safety Function (SDC) Resulting from Emergency Diesel Generator Output Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2011, severe weather in the Tennessee Valley service area caused grid instability and loss of all 500-kV offsite power sources that resulted in scrams of all three Browns Ferry Nuclear Plant (BFN) units. On May 2, 2011, at approximately 0626 hours Central Daylight Time, with all three BFN units in cold shutdown and power supplied by onsite emergency diesel generators (EDGs) and one 161-kV offsite power source, the output breaker of the Unit 1/2 A EDG tripped. <br /><br /> The Unit 1/2 A EDG output breaker tripped, interrupting power to 4-kV Shutdown Board A, causing a loss of power to a portion of the Unit 1 Reactor Protection System, and leading to Primary Containment Isolation System Group 2, 3, 6, and 8 isolations. The Group 2 isolation caused the loss of Shutdown Cooling on Unit 1 for approximately 57 minutes. Unit 2 was not affected by this event. <br /><br /> Control room annunciation indicated an overspeed trip condition with the Unit 1/2 A EDG. The root cause of this event was concluded to be inadequate procedural guidance for setup of the diesel generator overspeed trip limit switch (OTLS). Corrective actions included procedure revisions to include steps for proper switch setup. <br /><br /> Due to concurrent plant conditions, this event constitutes a reportable condition as described in 10 CFR 50.73(a)(2)(i)(B) for BFN Units 1, 3, and 3.
2592011005 | Browns Ferry 1 | 04/27/2011 | 06/27/2011 | ML11180A00 | <strong>Reactor Water Level Scram due to Distracted Operations Crew</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2011, at 2120 hours Central Daylight Time, the Unit 1 reactor water level system generated a low reactor water level scram due to a distracted operations crew allowing reactor water level to lower below +2 inches; the Low Level 3 reactor vessel level setpoint. The cause of the event was an operations crew error, because operations personnel did not perform in accordance with accepted or approved practice. At the time of this event, the Reactor Core Isolation Cooling (RCIC) and the Control Rod Drive Systems were injecting into the vessel and the reactor water level band was specified between +2 to +51 inches. The low level scram generated a valid Containment Isolation signal and Groups 2, 3, 6, and 8 isolated as designed. Water level was immediately restored by the operations crew to the specified band using RCIC. This condition is reportable in accordance with 10 CFR 50.72(b)(3)(iv)(A) for any event or condition that results in a valid actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B), except when the actuation results from and is part of a pre-planned sequence during testing or reactor operation.
2592011006 | Browns Ferry 1 | 05/20/2011 | 07/19/2011 | ML11203A01 | <strong>Loss of Safety Function (HPCI) due to Primary Containment Isolation</strong><br /><i>Abstract:&nbsp;</i>On May 20, 2011, Operations personnel were preparing to vent the High Pressure Coolant Injection (HPCI) System discharge piping. When the normally closed HPCI Injection Valve was opened, the HPCI System discharge and suction piping rapidly pressurized to near reactor pressure. Some components in the lower design pressure suction piping leaked, some equipment in the HPCI Room was sprayed with water, and flood level alarms in the Main Control Room were received. Approximately one minute later, Operations personnel closed the HPCI Injection Valve and HPCI System pressure decreased. Seat leakage past the HPCI System Testable Check Valve, a primary containment isolation valve (PCIV), caused the increase in piping pressure. The cause of the valve seat leakage was misalignment of valve and operator parts. To satisfy PCIV Technical Specifications, primary containment was maintained for the HPCI System penetration flow path by closing and de-activating the HPCI Injection Valve. Once this valve was de-activated, the HPCI System was rendered incapable of performing its accident mitigation safety function.
2592011007 | Browns Ferry 1 | 08/06/2011 | 10/05/2011 | ML11285A04 | <strong>Multiple Containment System Isolations from Loss of RPS M-G Set 1B</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2011, at 0522 hours Central Daylight Time, Browns Ferry Nuclear Plant Unit 1 Reactor Protection System (RPS) Motor-Generator (M-G) set 1B failed resulting in a partial loss of power to Primary Containment Isolation System (PCIS) groups and an invalid actuation of those PCIS groups. PCIS groups 1 and 2 received partial isolation signals with no subsequent system isolations, as designed. PCIS groups 3, 6, and 8 received partial isolation signals with resulting system isolations, as designed. The combination of RPS M-G set 1B loss and PCIS group 6 isolation resulted in the isolation of the Drywell Floor Drain Sump and the Drywell Continuous Atmospheric Monitor for both particulate and gaseous activity. Thus, both means of automatic monitoring of Reactor Coolant System leakage became inoperable. Unit 1 entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.5 Condition D, all required leakage detection systems inoperable, and immediately entered TS LCO 3.0.3 as required. Trouble-shooting activities did not identify a specific condition that caused the voltage drop on the RPS M-G set 1B. However, there were two potential causes: (1) a loose connector or cable assembly at a terminal on the RPS M-G set control panel due to the machine design and operational characteristics (i.e., vibration induced), and (2) discontinuity within the voltage adjustment potentiometer.
2592011008 | Browns Ferry 1 | 07/23/2011 | 11/16/2012 | ML12325A05 | <strong>High Vibrations on High Pressure Coolant Injection Booster Pump Thrust Bearings</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2011, Browns Ferry Nuclear Plant (BFN) personnel performed quarterly surveillance procedure 1-SR-3.5.1.7, "HPCI Main and Booster Pump Set Developed Head and Flow Rate Test at Rated Reactor Pressure." During this surveillance, BFN personnel recorded an unexpected increase in the vibration level on the High Pressure Coolant Injection (HPCI) booster pump thrust bearings. Upon performing a disassembly for inspection on July 23, 2011, the bearings were discovered to be in a tandem arrangement, which transmits thrust in only one direction (away from the gearbox). The correct bearing configuration is back-to-back. New bearings were installed in the proper configuration. The Tennessee Valley Authority (TVA) has determined that this condition affected the HPCI system mission time and thus the operability of the HPCI system for an unknown period. Therefore, it was conservatively concluded that the BFN Unit 1 HPCI system was inoperable longer than allowed by Technical Specification 3.5.1 Actions. The TVA is reporting this event in accordance with 10 CFR 50.73(a)(2)(i)(B), as an operation or condition which was prohibited by the plant's Technical Specifications, and 10 CFR 50.73(a)(2)(v)(B) and (D), as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat and to mitigate the consequences of an accident, respectively.
2592011009 | Browns Ferry 1, Browns Ferry 3 | 10/06/2011 | 07/29/2013 | ML13211A31 | <strong>As-Found Undervoltage Trip for the Reactor Protection System 1A1 Relay that Did Not Meet Acceptance Criteria During Several Surveillances</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2011, while performing an evaluation for past operability on the Reactor Protection System (RPS) 1A1 relay undervoltage trips, Browns Ferry Nuclear Plant determined that the as-found undervoltage trip for the RPS 1A1 relay was less than the required acceptance criteria during several Technical Specification (TS) Surveillances performed from April 2007 to August 2011. Therefore, the RPS 1A1 relay was inoperable for an indeterminate period of time between these surveillances. During a review of the surveillance procedure performance for RPS circuit protector calibration and functional test for 3C1 and 3C2 relays, it was determined that the as-found undervoltage trip for the RPS 3C1 relay was less than the required acceptance criteria during several surveillances performed from June 2006 to February 2012. The RPS 3C1 relay was inoperable for an indeterminate period of time between these surveillances.<br><br> The root cause of these events was determined to be the surveillance test program did not provide specific instructions for past operability reviews when out of TS conditions are corrected during surveillances.<br><br> The corrective actions to prevent recurrence were to revise the surveillance test program procedure, issue a new past operability evaluation procedure, and revise the operability determination and limiting condition for operation procedure to provide guidance on performing past operability evaluations and to address the requirements associated with past operability evaluations.
2592011010 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 10/25/2011 | 12/27/2011 | ML12003A25 | <strong>DC Ammeter Cables Not Adequately Isolated</strong><br /><i>Abstract:&nbsp;</i>During a design review in support of the Browns Ferry Nuclear Plant (BFN) Unit 1 transition to National Fire Protection Association 805, a condition was identified that non-safety related ammeters (also called remote ammeters) were installed in several safety-related battery board circuits (i.e. Battery Boards 1, 2, and 3) without electrical isolation protection required by Design Criteria BFN-50-7200C. Design Criteria BFN-50-7200C requires the addition of fuses to provide protection for battery board ammeter circuits. This constitutes a design flaw that has existed from the initial startup and the subsequent re-start of BFN Units 1, 2, and 3 since November, 1995, in all modes and all mode combinations of operation of all three units. The equipment impacted by this condition are Battery Boards 1, 2, and 3, which are credited for Appendix R safe shutdown for a fire event in Fire Area (FA) 16. Corrective actions included preparing a design change to add fuses for the remote ammeter circuits, adding this condition to the BFN Fire Protection Impairment Report, as well as improvements in Engineering technical rigor and human performance.
2602011001 | Browns Ferry 2 | 08/08/2011 | 10/07/2011 | ML11287A03 | <strong>Core Spray Relay Found in Incorrect Position</strong><br /><i>Abstract:&nbsp;</i>On August 8, 2011, Surveillance Procedure 2-SR-3.3.5.1.6 (CS II) "Core Spray System Logic Functional Test Loop II," was being performed. Contacts 3-7 and 4-8 for normally energized relay 14A-K30B were determined to be not fully open. On August 9, 2011, the cover on the relay was adjusted per WO 112545536 and the contacts went fully open. 2-SR-3.3.5.1.6 (CS II) testing recommenced and the relay is subsequently reenergized. The surveillance and LCO were exited. During a walkdown on august 12, 2011, contacts 3-7 and 4-8 for normally energized relay 14A-K30B were again determined to be not fully open. The troubleshooting revealed there was a relay armature problem. An LCO was entered. On August 13, 2011, the relay was replaced and the surveillance was successfully completed. A failure analysis indicated the HGA's relay hinged armature can intermittently become bound in an undesired position, limiting the ability of the relay to operate as expected. The binding occurs within the hinged armature mechanism, particularly on the right side. This report also constitutes a Part 21 notification.
2612011001 | Robinson 2 | 05/04/2011 | 07/05/2011 | ML11192A01 | <strong>Condition Prohibited by Technical Specifications When Non-Seismic System Was Aligned to Refueling Water Storage Tank due to Regulatory Requirements Not Adequately Incorporated in Plant Documentation</strong><br /><i>Abstract:&nbsp;</i>On May 4, 2011, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at 100% power, it was determined that over the last 40 years, HBRSEP, Unit No. 2, periodically performed cleanup of the Refueling Water Storage Tank (RWST) by aligning the non-seismically qualified refueling water purification system to the safety related and seismically qualified RWST without recognizing that the action rendered the RWST inoperable. As a result, on multiple occasions, the RWST was inoperable for a period longer than allowed by Technical Specification (TS) Limiting Condition for Operation 3.5.4, EmergencyCore Cooling Systems - Refueling Water Storage Tank. The cause of this event was that regulatory requirements for the separation of seismically qualified and non-qualified systems, structures, and components were not adequately incorporated into the Design Basis Document (DBD) and Updated Final Safety Analysis Report (UFSAR). Administrative controls have been put in place on the alignment restrictions for piping that could affect the operability of the RWST. Additional corrective actions planned include DBD and UFSAR changes and modifications of applicable plant procedures. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications.
2612011002 | Robinson 2 | 09/26/2011 | 11/15/2011 | ML11325A19 | <strong>Reactor Trip due to a Failed Relay Coil on RCP-3-X(B) and Actuation of Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>At 1145 hours EDT on September 26, 2011, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, while in Mode 1 at approximately 100% power, an automatic reactor trip occurred. At the time of the trip, the control room received a "One Loop Low Flow" alarm indicating that Reactor Coolant Pump (RCP) 'C' had shut down. The Reactor Protection System (RPS) tripped the reactor on an input that breaker 52/14, for RCP 'C,' had opened. Verification of plant conditions immediately following the event identified that RCP 'C' was still running and that breaker 52/14 was still closed. The false indication signal, from relay RCP-3-X(B) was the source of the RPS trip signal. This event has been investigated in accordance with the HBRSEP, Unit No. 2, Corrective Action Program (CAP) and is documented in Nuclear Condition Report (NCR) 490203. The investigation concluded that the reactor trip was due to a defective coil lead wire, as supplied by the vendor, on the RCP-3-X(B) relay. Relay RCP-3-X(B) was replaced and post maintenance testing was performed. Relays at risk for a similar failure were also replaced. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B).
2632011001 | Monticello | 11/12/2010 | 03/20/2011 | ML11090026 | <strong>Reactor Vessel Overfill in Appendix R Scenario</strong><br /><i>Abstract:&nbsp;</i>During the performance of a fire protection assessment, a determination was made that the fire protection safe shut down analysis does not address a postulated reactor vessel overfill event. In a postulated fire event that required the evacuation of the Control Room with a loss of offsite power, High Pressure Coolant Injection and Reactor Core Isolation Cooling pumps would start if the low reactor water level setpoint is reached. For this fire, damage could result in the failure of the high reactor water level trip circuit for the High Pressure Coolant Injection and Reactor Core Isolation Cooling systems. This could result in a reactor vessel overfill. Compensatory measures for this issue have been implemented.
2632011002 | Monticello | 12/20/2010 | 02/17/2011 | ML11049010 | <strong>ESF Actuation due to Failed Power Supply</strong><br /><i>Abstract:&nbsp;</i>At 0357 December 20, 2010, with the plant in Mode 1 operating at 100% reactor power, the 'A' division Fuel Pool/Reactor Building Exhaust Plenum Primary Power Supply failed. The failure resulted in upscale trips on both the Fuel Pool and Reactor Building Ventilation Plenum radiation monitors. This condition resulted in closure of the Group II Primary Containment Isolation Valves (PCIV), isolation of Secondary Containment (SCT), initiation of the Standby Gas Treatment System (SBGT), and a transfer of the Control Room Ventilation (CRV) and Control Room Emergency Filtration (CREF) systems to the High Radiation Mode. Conditions and Required Actions were entered for Technical Specification 3.3.6.2 (SCT Instrumentation), 3.3.7.1 (CREF Instrumentation), and 3.4.5 (RCS Leakage Detection - CAM). Radiation levels were verified to be normal in the affected areas. Isolation signals were reset and Secondary Containment ventilation systems were restored to a normal lineup. Repairs to the power supply were complete within the allowed completion times. All systems functioned properly and there were no human performance errors associated with this event.
2632011003 | Monticello | 02/11/2011 | 03/30/2011 | ML11090025 | <strong>Secondary Containment Damper Icing</strong><br /><i>Abstract:&nbsp;</i>On February 11, 2011, at 0327 hours, Secondary Containment isolation damper V-D-61 (Reactor Building Outboard Isolation Damper) was discovered frozen closed due to ice buildup, with the actuator broken. The inboard damper, V-D-62, was found blocked partially open, again due to icing. A Secondary Containment (SCT) penetration flow path with two isolation valves inoperable condition existed, and Limiting Condition for Operation (LCO) 3.6.4.2 was declared not met. Technical Specification Condition 3.6.4.2.B was entered for one or more penetration flow paths with two isolation valves inoperable. The ice was removed and V-D-62 was verified closed at about 0354 hours, isolating the affected penetration flow path by use of at least one closed and de-activated automatic valve and satisfying the required action of Condition 3.6.4.2.B. Repairs were completed, the system retested, and LCO 3.6.4.2 was met by about 2001 hours on February 11, 2011. On March 11, 2011, with SCT not required, the site tested V-D-61 with the actuator disconnected (event condition), Reactor Building 1027 Supply Fan V-AH-4A operating, and without ice on the damper. The test demonstrated that the damper would not open under these conditions, thereby validating that the safety function of the damper was maintained throughout the event.
2632011004 | Monticello | 06/08/2011 | 08/08/2011 | ML11220146 | <strong>Secondary Containment Inoperability due to Ventilation Alignment Issue</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2011 at 0800, with the reactor operating at 100% power, secondary containment (SCT)[NG] was declared inoperable after swapping the operating refuel floor supply air handling unit from V-AH-4A[AHU] to V-AH-4B. SCT differential pressure (D/P) was reduced to 0.17 inches of water column (WC) vacuum, which did not meet Technical Specification (TS) surveillance requirement SR 3.6.4.1.1 to maintain secondary containment vacuum greater than or equal to 0.25 inches WC vacuum. Refuel floor ventilation was restored to the previous configuration andsecondary containment D/P returned to greater than 0.25 inches of WC vacuum. Vacuum was less than 0.25 inches WC vacuum for approximately 4 minutes. The event was caused by a change in supply air flow rates between V-AH-4A and V-AH-4B when swapped. Corrective actions include repairing a seized bypass damper [CDMP] on V-AH-4A and a procedure change to add precautions to the operating procedure for transferring refuel floor fans.
2632011005 | Monticello | 06/30/2011 | 08/26/2011 | ML11238076 | <strong>Power Range Monitor Channels Out of Alignment</strong><br /><i>Abstract:&nbsp;</i>On June 30, 2011, at 0516 with the reactor operating at 80% power, three of four Average Power Range Monitors (APRMs) exceeded Technical Specification 3.3.1.1.2 surveillance requirement to maintain the absolute difference between the Average Power Range Monitor (APRM) channels and the calculated power at <= 2% rated thermal power (RTP) while operating at >= 25% RTP. The event occurred during a control rod pattern adjustment supporting plant restart following a brief maintenance outage. The cause was a greater than typical change in APRM response due to a power shape change following the completion of a reactivity maneuvering step. The impact on the APRMs of the power shape change had not been determined in advance and was therefore not anticipated. No requirement existed to perform this calculation. An interim corrective action includes revising reactivity management procedures to include guidance for monitoring and adjusting gains on APRM's prior to each reactivity maneuvering step which could challenge the +/- 2% criteria.
2632011006 | Monticello | 09/02/2011 | 02/28/2012 | ML12060A14 | <strong>lntake Structure Fire Suppression System Blockage</strong><br /><i>Abstract:&nbsp;</i>On September 2, 2011, at approximately 1600, Mechanical Maintenance personnel informed Operations that portions of the Intake Structure sprinkler system piping were found to be partially blocked and incapable of passing flow. The Intake Structure sprinkler system is relied upon in part to satisfy an approved exemption to 10 CFR 50 Appendix R, Section III.G.2.b concerning separation of components in the Intake Structure. Installation of the Intake Structure sprinkler system in 1983 did not comply with design requirements for providing required pipe slope to ensure proper draining. This condition allowed excessive water to remain in the system which then contributed to accelerated internal corrosion and accumulation of corrosion byproducts in the piping system. Immediate corrective actions taken included flushing the sprinkler system and performing internal inspections to confirm removal of blockage before returning the system to service.
2632011007 | Monticello | 09/29/2011 | 02/28/2012 | ML12060A15 | <strong>Both Emergency Diesel Generators Declared Inoperable due to Inadequate Surveillance</strong><br /><i>Abstract:&nbsp;</i>On September 29, 2011, at 1700 hours CDT, Monticello Nuclear Generating Plant (MNGP) determined that the surveillance test procedure used to demonstrate compliance with Technical Specification (TS) surveillance requirement (SR) 3.8.1.7 involving load reject testing of the Emergency Diesel Generators (EDGs) with the single largest post-accident load did not fully satisfy the TS surveillance requirement. This condition resulted in both EDGs being declared inoperable. MNGP requested and was granted enforcement discretion to permit development and performance of a new surveillance test that meets the surveillance requirement. The cause of the event was an inadequate surveillance test procedure resulting from a failure to fully reflect the changes enacted through the implementation of the Improved Standard Technical Specifications in 2006. On October 2, 2011, the 12 EDG was successfully tested in accordance with the new surveillance test procedure at which time 12 EDG was declared Operable and the enforcement discretion period exited.
2632011008 | Monticello | 10/21/2011 | 02/28/2012 | ML12060A15 | <strong>Reactor Scram due to Loss of Normal Offsite Power</strong><br /><i>Abstract:&nbsp;</i>At 1250 on October 21, 2011, at the Monticello Nuclear Generating Plant, a 2R Auxiliary Transformer lockout unexpectedly occurred causing off-site power to automatically transfer to the 1R Auxiliary Transformer, which resulted in a reactor scram. One cable of the "A" phase conductor, supplying power from 2RS to 2R Transformer, faulted to ground, resulting in the 3N4 breaker opening, as designed, to protect 2RS Transformer and other equipment from fault current damage. Subsequent testing indicates the cable suffered from environmental and age-related degradation. Implementation efforts to replace the cables between 2R Transformer and 2RS Transformer were in progress at the time of the event. A portion of the new raceway was under construction. The cables were replaced entirely employing a route designed to avoid cable submergence in water. Subsequent to installation, cables were successfully tested and returned to service.
2632011009 | Monticello | 11/19/2011 | 03/01/2012 | ML12062A14 | <strong>Automatic Reactor Scram While Performing Turbine-Generator Testing</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2011, at approximately 2312 CST, during performance of regularly scheduled Turbine-Generator Quarterly Surveillance, an unplanned reactor scram occurred. Following the reactor scram, reactor water level lowered below the Group II isolation initiation setpoint (+9") and an actuation of Primary Containment Isolation System occurred. The direct cause of the scram was the actuation of the Main Turbine acceleration relay (load rejection) pressure switches. The root cause was ineffective management of Turbine Lube Oil (TLO) Tank Vacuum which resulted in oil build up on the turbine shaft resulting in fouled grounding braids. The shaft grounding device is intended to prevent damage to turbine generator components caused by circulating currents. Resulting circulating currents degraded the speed governor drive gear which resulted in governor oscillations ("bobble") that manifested itself during speed load changer testing and caused pressure oscillations at the acceleration relay (load rejection) pressure switches. Corrective actions include replacing the TLO Tank Vacuum Indicator with High Accuracy Device, and updating the operator round sheet to reflect new control bands as required. Repairs were also made to the speed governor gear drive components and main shaft oil pump components which were damaged by electrolysis and a modification was performed to install a more robust grounding apparatus.
2632011010 | Monticello | 11/27/2011 | 01/26/2012 | ML12027A05 | <strong>Rod Worth Minimizer Bypassed During Startup</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2011, while performing the Rod Worth Minimizer (RWM) Operability Test as part of startup activities, it was discovered that the RWM control switch was in Bypass. With the control switch in the Bypass position, the RWM was inoperable and did not enforce the pre-determined control rod withdrawal sequence. The RWM control switch was restored to the Operate position and the RWM was verified to be operable. The apparent cause was determined to be the crew failed to precisely identify the sequence of surveillances/procedures required to be completed, prior to the mode change. The pre-job brief was inadequate in that the specific sequence and details were not discussed and the licensed operators on duty failed to identify that the RWM configuration did not support the mode change. Additionally, control room indications available to the operators were not properly utilized to prevent the out of sequence control rod withdrawal.
2632011011 | Monticello | 12/01/2011 | 01/26/2012 | ML12027A21 | <strong>Failure to Lock Mode Switch in Refuel Position During Control Rod Exercises</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2011, the plant was in MODE 4 (cold shutdown) with the Reactor Mode Switch in Refuel position for a Control Rod Drive (CRD) exercise. The CRD exercise testing was being performed under Special Operations Technical Specification (TS) 3.10.4, "Single Control Rod Withdrawal - Cold Shutdown". TS Limiting Condition for Operation (LCO) 3.10.4 requires TS LCO 3.9.2, "Refuel Position One-Rod-Out Interlock" to be met. One of the Surveillance Requirements (SR) for TS 3.9.2, SR 3.9.2.1, requires verification every 12 hours that the Mode Switch be locked in the Refuel position. The TS Bases for SR 3.9.2.1 defines "locking" as removing the key from the Mode Switch. During a panel walkdown on December 1, 2011, the Control Room crew found the Reactor Mode Switch was unlocked in the Refuel position. While the Reactor Mode Switch remained in the Refuel position during the CRD exercises, the switch was not locked as required by SR 3.9.2.1. Failure to lock the Mode Switch in the Refuel position during the Control Rod Drive exercises was not in compliance with SR 3.9.2.1, and TS LCO 3.10.4. The cause of this event was Operator work practices, and inadequate procedural requirements. Personnel were remediated and applicable procedures were revised as part of the corrective actions for this event.
2652011001 | Quad Cities 2 | 01/12/2011 | 03/10/2011 | ML11076005 | <strong>Loss of Unit 2 Essential Service 480V Bus</strong><br /><i>Abstract:&nbsp;</i>On January 12, 2011, at 1020 hours, the Unit 2 Essential Service (ESS) 480V Bus 29 [BU] was inadvertently de-energized. The cause of this bus trip was due to inadvertent contact with the bus feed breaker local trip pushbutton [JS] by a station employee during unrelated work activities in the bus feed breaker area. While Bus 29 was de-energized, Division II core and containment cooling systems [BO] were unavailable and inoperable; however, normal power to Bus 29 was restored within 6 minutes. The plant responded as designed to the loss of Bus 29, with the exception that the normally supplied reactor building ESS 480V Bus Motor Control Center (MCC) 28/29-5 did not receive the auto transfer of supplied power from its reserve feed 480V Bus 28. Since either 480V Bus 29 or Bus 28 can feed Bus 28/29-5, this condition resulted in a loss of power to Bus 28/29-5 and rendered both divisions of the Low Pressure Coolant Injection (LPCI) [BO] mode of the Residual Heat Removal (RHR) [BO] system inoperable. Therefore, Technical Specification 3.5.1.E was entered, requiring restoration of LPCI within 72 hours. It was subsequently determined that the "M" auxiliary contactor [CNTR] from Bus 29 had failed which caused the auto transfer logic from Bus 29 to Bus 28 to fail. Bus 28/29-5 was manually reenergized from Bus 28 at 1213 hours; however, LPCI remained inoperable pending investigations. Restoration of Bus 28/29-5 auto-transfer function occurred at 2151 hours, allowing LPCI to be returned to operable status and TS 3.5.1.E to be exited. This report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2662011001 | Point Beach 1 | 11/27/2011 | 01/25/2012 | ML12031A06 | <strong>Loss of Offsite Power to Unit 1 Safeguards Buses</strong><br /><i>Abstract:&nbsp;</i>On 11/27/2011 at 0226 CDT, an undervoltage condition occurred on Unit 1, 1A-05 and 1A-06 safety-related buses during the restoration of 1X-03 high voltage station auxiliary transformer (HVSAT). The four emergency diesels (EDGs) started. The G-01 and G-03 EDGs loaded onto buses 1A-05 and 1A-06. Offsite power remained available to Unit 2 throughout the event via an alternate path. During switchyard realignment of the 1X03 HVSAT, the 1F89-112 circuit switcher failed. This resulted in a low voltage condition which started the standby EDGs. The fault did not cause a lockout of 1X03, the associated switchyard component. As a result, the automatic transfer to the redundant offsite power supply in the switchyard was not initiated, and GO1 and G03 automatically loaded onto Unit 1 safety system buses 1A05 and 1A06 once the diesels had reached operating voltage and frequency. The safety significance of this event was low because at the time of the event Unit 1 was in MODE 5, and shutdown cooling capability was maintained via the steam generators. Following the event, station procedures were revised to check local circuit switcher indicators for proper configuration prior to and following operation. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in a manual or automatic actuation of any of the systems listed in 10 CFR 50.73(a)(2)(iv)(B) including any event or condition that results in the actuation of the emergency AC electrical power system.
2692011002 | Oconee 1 | 01/08/2011 | 05/14/2012 | ML12136A24 | <strong>Tech Spec Required Shutdown for an Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2011, during performance of Engineered Safeguards (ES) logic testing, the wiring jumper intended to prevent travel of letdown line containment isolation valve 1HP-5 became dislodged. The signal to close the valve became active, but 1HP-5 did not fully close as expected. Upon investigation, 1HP-5 was found to be approximately 25 percent open. Because the valve did not fully close, it was declared inoperable. Technical Specification (TS) 3.6.3 Required Action A.1 entry conditions were met at 0148 hours on January 8, 2011, for an inoperable containment isolation valve. Unit 1 initiated a shutdown at 1401 hours on January 8, 2011 (NRC Event Notification 46526), completed the shutdown required by TS when Unit 1 entered Mode 3 at 1731 hours on January 8, 2011, and exited the TS mode of applicability when Unit 1 entered Mode 5 at 1419 hours on January 9, 2011. Investigation identified the failure of 1HP-5 was due to a lack of actuator capability caused by changes in seat material. Corrective actions included replacement of the valve actuator spring with a stronger spring to restore closing margin. This event is similar to the failures of 2HP-5 and 3HP-5 reported under LER 270/2011-01. There were no actual adverse consequences to the health and safety of the public as a result of this event.
2692011003 | Oconee 1, Oconee 2, Oconee 3 | 02/24/2011 | 12/19/2011 | ML12006A19 | <strong>Inoperability of the Standby Shutdown Facility Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On May 13, 2010, an unanticipated Standby Shutdown Facility (SSF) differential lockout relay (86D) actuation occurred while performing an emergency power switching logic function test (i.e., J-test). This lockout rendered the SSF Diesel Generator (D/G) incapable of starting in any mode. The root cause was inadequate consideration of all failure modes and effects due to personnel not fully understanding the impact of a design change on the SSF D/G. The design change modified the output contacts of new chart recorders from normally open to normally closed, changing the design function. But, the design inputs were not re-validated. During the J-test, the chart recorders were load shed and repowered (as expected); however, until the recorder completes its "reboot," the output contact is maintained in its shelf state. As a result, the SSF D/G Control Logic received a "false" diesel engine high bearing temperature trip signal for approximately 25 seconds that resulted in actuation of the 86D relay. The design issue with the SSF chart recorders existed since design change implementation in November 2008. Since this time span exceeded the seven days allowed by Technical Specification 3.10.1, the event is reportable. Immediate corrective action involved resetting the 86D lockout relay to clear alarms and to restore Diesel Emergency Start-Ready to Start light indication. The high bearing temperature trip interlocks were removed from the chart recorders and the circuit functionally tested.
2692011004 | Oconee 1, Oconee 2, Oconee 3 | 04/04/2011 | 05/22/2013 | ML13144A59 | <strong>Inability to Detect RCS Leak Rate Using the Particulate Radiation Monitor</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2011, it was determined that the requirements of Technical Specification (TS) 3.4.15, "Reactor Coolant System (RCS) Leakage Detection Instrumentation," had not been met for all three units. The Reactor Building Particulate Radiation Monitor (RIA-47) may not have been able to consistently detect a one gallon-per-minute (1 gpm) reactor coolant pressure boundary (RCPB) leak and alarm in the main control room (MCR), within one (1) hour, for all Modes of applicability required by TS 3.4.15. This TS requires RIA-47 to be Operable in Modes 1 through 4. The function of RIA-47 is to alert operators of excessive RCPB leakage via the MCR alarm. This adverse condition resulted because the setpoint methodology used to establish the RIA-47 alarm was determined to be nonconservative. An engineering change was performed that modified the setpoint methodology such that RIA-47 is able to consistently alarm for a 1 gpm RCPB leak within 1 hour during full power steady state operation. In Modes 2, 3, and 4, and Mode 1 less than full power, RIA-47 may still require greater than or equal to 1 hour to detect a 1 gpm RCPB leak and alarm in the MCR, because RCS activity is decreased due to improvements in fuel quality and improved filtration/clean-up processes used during reactor refueling. Revision 1 includes the complete LER content that was not available in Revision 0 of the report.
2692011005 | Oconee 1 | 06/10/2011 | 02/23/2012 | ML12055A33 | <strong>Reactor Protection System Overpower Flux/Flow/Imbalance Channels Inoperable</strong><br /><i>Abstract:&nbsp;</i>During Refueling Outage 1EOC26 for Oconee Unit 1, implementation of the digital Reactor Protection System/Engineered Safeguards (RPS/ES) upgrade was performed. During initial startup and after increasing power to 48 percent, site personnel questioned the unexpected response of the RPS power range nuclear instrumentation (NIs). Although appearing to respond appropriately for total reactor power, the power range NIs did not appear to be responding adequately to power imbalances compared to the incore detector indications. Investigation into the cause of the Unit 1 NI imbalance indications determined that the triaxial cables for the top and bottom chambers of the power range nuclear instrumentation signals were reversed at the RPS Power Range Test Module for each RPS channel. At 0802 on June 10, 2011, the four channels of the RPS Flux/Flow/Imbalance parameter were declared inoperable. This resulted in a loss of safety function, operation prohibited by Technical Specifications, and a single cause resulting in multiple independent RPS channels being inoperable. This event was reported via an 8-hour notification per 10 CFR 50.72(b)(3)(v)(D) (Event Report 46947). The triaxial cable connections were corrected and the RPS channels were declared operable at 1511 on June 10, 2011. This event is considered to have no consequence with respect to the health and safety of the public.
2692011006 | Oconee 1, Oconee 2 | 08/11/2011 | 05/29/2012 | ML12151A28 | <strong>Pressurizer Heater Capacity Non-Compliant with Technical Specification 3.4.9</strong><br /><i>Abstract:&nbsp;</i>An extent of condition review associated with the temperature induced trip of Standby Shutdown Facility pressurizer (PZR) heater panel board breakers inside containment determined that during a loss-of-offsite-power (LOOP) event, the power supply breakers in each unit's east penetration room, supplying PZR Heater Groups 'A' and 'E' through 'K', may trip on thermal overload due to elevated ambient temperature in the penetration room. Technical Specification (TS) 3.4.9 requires a minimum of 400 kilowatts of PZR heaters be Operable and capable of being powered from an emergency power supply. However, the above described review determined that the total available emergency-powered heater capacity did not comply with TS 3.4.9 for Unit 1 and Unit 2. This condition has existed since March 2005, which exceeds TS 3.4.9 Action Condition 'C' 72-hour completion time. Thus, this condition is reported in accordance with 10 CFR 50.73(a)(2)(i)(B), as an operation prohibited by TSs. An alternate configuration of breakers and in-service heaters was developed and implemented that restored compliance with TS 3.4.9. Actions to prevent recurrence include planned changes to documents that will strengthen design evaluation processes.
2692011007 | Oconee 1 | 01/14/2011 | 05/14/2012 | ML12136A24 | <strong>Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 8, 2011, Oconee Unit 1 containment isolation valve, 1HP-5, was declared inoperable, and Unit 1 initiated a shutdown. Investigation identified galling between the gland ring and valve body of 1HP-5. Corrective actions included replacement of the valve gland ring with one made from material that is less susceptible to galling and increasing the clearance between the gland ring and valve body. After successfully completing post-maintenance valve stroke testing, Unit 1 was returned to service on January 14, 2011. However, further analysis identified that a valve seat material change in 2003 resulted in a reduction in actuator margin such that valve 1HP-5 could not be assured of closing. On June 2, 2011, inadequate actuator sizing was confirmed. Therefore, 1HP-5 was inoperable, and in a condition prohibited by Technical Specifications, from January 14, 2011, until Unit 1 entered Mode 5 for the planned refueling outage, April 2, 2011. Also, because 1HP-5 remained inoperable following the forced shutdown, TS LCO 3.0.4 was violated since Unit 1 was unintentionally returned to service with 1HP-5 still inoperable. This event is associated with the failure of 1HP-5 previously reported under LER 269/2011-02 and is similar to the failures of 2HP-5 and 3HP-5 reported under LER 270/2011-01. There were no actual adverse consequences to the health and safety of the public as a result of this event.
2702011001 | Oconee 2, Oconee 3 | 06/02/2011 | 08/01/2011 | ML11215A19 | <strong>Technical Specification Violation Involving a Notice of Enforcement Discretion for an Inoperable Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2011, Technical Specification (TS) 3.6.3, "Containment Isolation Valves", Condition A was entered upon confirmation that errors discovered in approved vendor calculations, when corrected, indicated insufficient closing margin for containment isolation valves HP-5 and HP-21 for Oconee Units 2 and 3. The completion time for Required Action A.1 was not met, and the station started preparations to shut down both units. On June 2, 2011, at approximately 1830 hours, the NRC verbally granted enforcement discretion for TS 3.6.3, Required Action A.1. The period of enforcement discretion began on June 2, 2011, at 1210 hours and was effective until June 16, 2011, at 1210 hours. Subsequent evaluation determined that valves 2HP-21 and 3HP-21, containment isolation valves in the respective unit's flow path that returns Reactor Coolant Pump Seal Water to the Seal Return Coolers, had sufficient margin to remain operable. Valve 2HP-5 was returned to operable status via an engineering design change at 0705 on June 11, 2011. Valve 3HP-5 was returned to operable status via an engineering design change on at 2345 on June 10, 2011. A root cause evaluation was performed, and the root cause and the resultant corrective actions are described in the body of this LER. This event is similar to the failure of 1HP-5 reported under LER 269/2011-02. This event is considered to have no significance with respect to the health and safety of the public.
2702011002 | Oconee 2 | 08/17/2011 | 10/17/2011 | ML11299A13 | <strong>Inoperable Containment Isolation Valve Violates TS 3.6.3</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2011, Operations personnel noted that the OPEN light for containment isolation valve 2HP-4 was not illuminated. Investigation identified that control power had been lost to the valve when a wire in the control power circuit became detached from the sliding link terminal. Upon identification of the cause of the loss of indication, valve 2HP-4 was declared inoperable. The wire was landed and the valve was returned to service. A search of the cabinet did not locate the nut that should have been installed to hold the wire to the sliding link. Document searches and interviews did not identify any work activities associated with this wiring. Therefore, it was concluded that the nut was incorrectly left off of the sliding link terminal at some indeterminate time in the past. Current activities within the cabinet of pulling wires and removing and replacing the insulating strip disturbed the unrestrained wire. With no nut holding it in place, the wire slipped from the stud, rendering the valve inoperable. Based on work activities and operator observation, the valve was inoperable for approximately 4 hours and 53 minutes, which exceeds the allowed action statement time of four hours for an inoperable containment isolation valve. The risk significance of this event has not been completed; however, this event is considered to have no consequence with respect to the health and safety of the public.
2712011001 | Vermont Yankee | 02/16/2011 | 04/14/2011 | ML11109A00 | <strong>Inoperability of High Pressure Coolant Injection System due to Failure to Follow Procedures</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2011 with the plant at 100 percent power, Vermont Yankee was preparing to perform a scheduled quarterly surveillance on the High Pressure Coolant Injection (HPCI) system. During initial startup of the system, audible and visual indications of steam leakage were observed. The investigation determined that a flanged connection associated with steam trap ST-23-3 was the source of the leak. This steam trap is on a line that maintains the steam supply piping to the HPCI turbine free of accumulated water. The event was attributed to a maintenance activity that was performed on February 1, 2011 where the steam trap was disassembled to facilitate a piping weld repair. The cause of this event was a failure to follow procedures that resulted in incorrect gasket material being used as a replacement for spiral wound gasket material. This event was determined to be reportable per 10CFR50.73(a)(2)(v)(D) as an event or condition that could have prevented fulfillment of a safety function and under 10CFR50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. The Automatic Depressurization System (ADS) serves as a backup to the HPCI system. If the HPCI System does not operate and one of the low pressure coolant injection pumps is available, the Nuclear System is depressurized using ADS to permit the Low Pressure Coolant Injection (LPCI) and Core Spray (CS) systems to operate to protect the fuel barrier. This event did potentially affect the ability of HPCI to perform its safety function from February 1, 2011 through February 19, 2011 when the system was returned to service. During that time period, ADS and either LCPI or CS were available to perform the required safety functions. Therefore, this event did not pose a threat to public health and safety.
2712011002 | Vermont Yankee | 12/02/2011 | 01/20/2012 | ML12027A19 | <strong>Inoperability of Both Emergency Diesel Generators due to a Lack of Adherence to Procedures</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2011, with the plant at 100 percent power, Vermont Yankee (VY) was modifying the tagging lineup on the "B" Emergency Diesel Generator (EDG) that was out of service for scheduled maintenance. During the tagging evolution, an operator mistakenly entered the "A" EDG room and tripped the "A" EDG fuel rack making the "A" EDG inoperable. This resulted in both EDGs being inoperable requiring entry into a 24 hour limiting condition for operation. This event is reported in accordance with 10CFR50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function since both EDGs were inoperable. The investigation determined that this event was caused by a lack of adherence to procedures that provide administrative controls over tagging evolutions and direct the use of human performance tools to prevent occurrence of this type of an event. The condition was immediately identified by operations personnel due to alarms received in the main control room and the "A" EDG was returned to operable status in two minutes. There were other sources of AC power available and therefore, this event did not pose a threat to public health and safety.
2722011001 | Salem 1 | 01/17/2011 | 03/18/2011 | ML11088009 | <strong>Service Water Loop Inoperable for Time Greater Than Allowed by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On December 9, 2010, during a walkdown of the No. 1 Service Water Intake Structure (SWIS) bay, severe corrosion was observed at the base of a six inch stanchion (pipe) that supports the cable for the No. 12 Service Water (SW) strainer motor. Based on the degree of corrosion, the Service Water (SW) pump was declared inoperable. The stanchion was repaired and returned to service on December 16, 2010. On January 17, 2011, an engineering review of past SW pump operability determined that concurrent with the No. 12 stanchion condition, there were occasions when another SW pump in the SWIS bay was inoperable for greater than 72-hours. The inoperability of two service water pumps resulted in a service water loop being inoperable for greater than allowed by Technical Specifications. The cause of this event was determined to be the untimely repair of a corroded Service Water strainer stanchion. Actions taken included walk downs of all SW stanchions in SWIS bays and repairs to the No. 12 SW Strainer stanchion. This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), "any operation ... prohibited by the plant's Technical Specification."
2722011002 | Salem 1 | 02/24/2011 | 04/23/2011 | ML11123A12 | <strong>Bypass of Steam Generator Blowdown Valve Isolation During Testing</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73(a)(2)(ii)(B), "any event or condition that resulted in the nuclear plant being in an unanalyzed condition that significantly degraded plant safety." The loss of normal feedwater analysis assumes the failure of the turbine driven auxiliary feedwater pump (AFW) pump and isolation of the steam generator blowdown lines. Installation of the jumper discussed below prevented closure of the blowdown isolation valves and would reduce the heat removal capability of the AFW injected into the steam generators below the AFW flow required by the accident analysis with only the motor driven AFW pumps running. On February 24, 2011, the Control Room Supervisor (CRS) questioned the testing being performed for the replacement of the steam generator high radiation relay (HR1) in the steam generator blowdown radiation monitor (1R19B) test circuit. Jumpers were to be installed in accordance with section 5.1.5 of procedure S1.IC-FT.RM-0129 to prevent the closure of the 11 to 14GB4 Steam Generator blowdown isolation valves during functional testing of the 1R19B radiation monitor. The CRS questioned whether the jumpers affected more than just the radiation monitor closure of the GB4 valves. The jumper was determined to not only prevent closure of the GB4 valves from a radiation monitoring signal but would also prevent closure of the valves on the automatic start of the Auxiliary Feedwater (AFW) pumps. The jumper installation did not impact the ability of the GB4 valves to close on a containment isolation signal. The cause of bypassing the AFW pump automatic closure of the steam generator blowdown isolation valves during steam generator blow down radiation monitor functional testing was due to knowledge errors during the preparation and review of procedure S1.IC-FT.RM-0129. Corrective actions included personnel accountability and procedure revisions.
2722011003 | Salem 1 | 04/21/2011 | 06/06/2011 | ML11305A00 | <strong>Manual Reactor Trip due to Degraded Condenser Heat Removal</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(A...." On April 21, 2011, at approximately 16:00, a manual reactor trip was initiated with reactor power level at approximately 89%. The manual reactor trip was initiated in response to a degraded Circulating Water (CW) system and in accordance with abnormal operating procedures. The CW system degradation was due to heavy detritus loading that affected the ability of CW traveling water screens (TWS) to operate, and the resultant loss of circulating water pumps. The unit was returned to service on April 23, 2011, at 05:19 after the debris was cleared from the screens, condenser water boxes were cleaned and the established management criteria developed in the Operational and Technical Decision Making Process were met.
2722011004 | Salem 1 | 08/22/2011 | 10/21/2011 | ML11333A01 | <strong>11 Component Cooling Water Pump Inoperable for Greater than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73(a)(2)(i)(B), "any event or condition which was prohibited by the plant's Technical Specification." On August 22, 2011, during the performance of rounds, an equipment operator found one of the two outboard pedestal mounting bolts for the 11 Component Cooling Water (CCW) pump dislodged and the other outboard mounting bolt was backed out approximately 1-inch. At 0217, the 11 CCW pump was declared inoperable and Technical Specification Action Statement (TSAS) 3.7.3.1 was entered. The 11 CCW pump was in service at the time of discovery. The pump was stopped and the 12 CCW pump placed in service. The 11 CCW pump pedestal bolts were replaced and torqued. The 11 CCW pump was retested satisfactory. The pump was returned to operable status on August 23, 2011 at 0057 hours and TSAS 3.7.3.1 exited. The cause of the loose bolting was the original vendor supplied pedestal bolting was not adequately torqued during factory assembly of the 11 CCW pump and pedestal. Once torqued properly the bolts should have remained captured due to adequate bolt stretch and preload. Corrective actions include replacement and torque of the 11 CCW pump pedestal bolts, a walk down of the similar type pumps (CCW, Containment Spray and Spent Fuel Cooling) and the validation of pedestal bolts torque values for the Containment Spray, Spent Fuel Cooling, and the remaining CCW pumps.
2722011005 | Salem 1 | 11/24/2011 | 02/09/2012 | ML12055A38 | <strong>Incorrect NIS Trip Setpoints Results in TS 3.0.3 Entry</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73(a)(2)(i)(B), "Any event or condition which was prohibited by the plant's Technical Specification." On November 23, 2011 with Unit 1 at 47% reactor power, the full power intermediate range trip setpoints were calculated in accordance with the Intermediate Range (IR) Nuclear Instrumentation System (NIS) Setpoint Evaluation and Determination procedure. On November 24, 2011 with Unit 1 at 55% reactor power, l&C technicians installed the IR NIS trip setpoints. Prior to the installation of the setpoints, the IR High Level Trip and Rod Stop bistables were in the tripped condition, as expected. Once the setpoints were installed, the IR High Level Trip and Rod Stop bistables were not tripped for both 1N35 and 1N36 channels. With reactor power at 55%, the proper state of the bistables would be tripped. The fact that the bistables were not in the tripped condition after the setpoints were installed was not immediately identified by the plant staff. On December 11, 2011, with Unit 1 at 100% reactor power, the Unit 1 reactor operator observed that the IR NIS bistables were not in a tripped condition, as would be expected. The IR NIS trip setpoints were determined to be incorrect and the IR NIS channels were declared inoperable. Technical Specification 3.0.3 was entered at 1258 hours. New IR trip setpoints were calculated and installed in 1N35 and Technical Specification (TS) 3.0.3 was exited at 1628 hours. 1N36 was completed and declared operable at 1733 hours. The cause was the failure to properly record the input data (IR currents) used to calculate the IR trip setpoints. This led to the miscalculation of the IR trip setpoints that were installed. Corrective actions included the installation of the correct IR trip setpoints and a procedure revision to include a Concurrent Verification when obtaining the data used to calculate the IR trip setpoints.
2752011001 | Diablo Canyon 1 | 11/06/2010 | 01/27/2012 | ML12030A02 | <strong>Mode Transition with Turbine-Driven Auxiliary Feedwater Pump 1-1 Inoperable</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2011, Pacific Gas and Electric (PG&E) identified that the Turbine-Driven Auxiliary Feedwater Pump 1-1 (TD AFW PP 1-1) was inoperable in Mode 3 (Hot Standby) on November 6, 2010, due to an improperly set speed governor. The TD AFW PP 1-1 governor had been replaced on October 27, 2010, prior to entry into Mode 3. The TD AFW PP 1-1 post maintenance test (PMT) required steam generator pressure to be greater than 650 psig, necessitating entry into Mode 3 to perform the test. This testing and adjustment was performed on November 6, 2010. On January 3, 2011, plant staff reviewing the PMT and the governor adjustment performed on November 6, 2010, identified that the TD AFW PP 1-1 as-found condition exceeded 4,300 rpm. This initial speed was greater than the engineering-established acceptance criteria of 4,260 rpm for surveillance testing of the pump. PG&E determined that the TD AFW PP 1-1 was consequently inoperable during the mode transition from Mode 4 (Hot Shutdown) to Mode 3. Technical Specification Limiting Condition for Operation (TS LCO) 3.7.5 requires three trains of AFW to be operable in Modes 1 through 3. With the TD AFW PP 1-1 inoperable during the mode transition, entry into Mode 3 without TS LCO 3.7.5 being met constitutes a violation of TS LCO 3.0.4. The cause of this event was that plant-specific specifications were not provided for refurbishment of the replacement governor, resulting in the improperly set speed governor. Maintenance plans and procedures were modified to ensure the proper specifications are provided for refurbishment/replacement of TD AFW PP speed governors.
2752011002 | Diablo Canyon 1, Diablo Canyon 2 | 01/10/2011 | 12/16/2011 | ML11353021 | <strong>Single Failure Vulnerability of Unit 1 and 2 Auxiliary Building Ventilation System</strong><br /><i>Abstract:&nbsp;</i>On January 10, 2011, at 1321 PST, Diablo Canyon Power Plant (DCPP), Unit 2, entered Technical Specification Limiting Condition of Operation (TS LCO) 3.0.3 when both trains of auxiliary building ventilation system (ABVS) [VF] became inoperable following closure of Damper M-4A [DMP] and the ensuing loss of both ABVS Exhaust Fans E-1 and E-2. TS LCO 3.0.3 was exited on January 10, 2011, at 1342 PST following a system reset and restart of Fan E-2. An 8-hour nonemergency report was made pursuant to 10 CFR 50.72(b)(3)(v) (reference ENS # 46531). The cause of the loss of both trains of ABVS of Unit 2 was a nonconforming single failure vulnerability in the ABVS design. This design vulnerability existed as part of the original plant design for both DCPP Units 1 and 2 and was not identified and corrected when the ABVS control system was replaced. Corrective actions include modifying the design of both DCPP Units 1 and 2 ABVS to meet the single failure design criteria. This revision clarifies that only Unit 2 experienced an event that could have prevented fulfillment of its safety function.
2752011004 | Diablo Canyon 1 | 05/17/2011 | 11/08/2011 | ML11313007 | <strong>Emergency Diesel Generator Actuated Upon 230 kV Isolation Due to Maintenance Activities on Relay Panel</strong><br /><i>Abstract:&nbsp;</i>On May 17, 2011, at 0954 PDT, with Unit 1 at 100 percent power, 230 kV startup power was isolated following the actuationof the 230 kV Line Differential Relay 287. As a result, all Unit 1 emergency diesel generators (EDGs) started in standbymode as designed, with no problems observed. No vital loads were affected by the loss of startup power as they remainedpowered by the Unit 1 main generator. At the time, Unit 2 was in a refueling outage with the core offloaded and startuppower cleared; therefore, it was unaffected by the event. All Unit 1 EDGs were shut down and returned to auto, StartupTransformers 1-1 and 1-2 were returned to service, and on May 17, 2011, at 1125 PDT, Unit 1 startup power was declaredoperable. The actuation of Differential Relay 287 was due to modifications being performed on the 12 kV startup relay board (PanelRU) that contains components for both units. Mechanical vibration induced by a reciprocating saw caused the relay to actuate, thus opening the 12 kV Feeder to Startup Bus Breaker 52VU12 and isolating Unit 1 230 kV startup power. The cause was that plant personnel failed to perform an adequate risk assessment during the planning stage of the modification, misjudging the possible impact of mechanically agitating an adjacent active relay while cutting. Corrective actions include revising procedures to assure adequate risk assessments are performed when working on or near equipment that can potentially impact both units, and strengthening the consistent use of human performance tools.
2752011005 | Diablo Canyon 1 | 05/26/2011 | 11/08/2011 | ML11313007 | <strong>Emergency Diesel Generator Actuations Upon Loss of 230 kV Startup Due to Electrical Maintenance Testing</strong><br /><i>Abstract:&nbsp;</i>At the time of the events, the Unit 2 Sixteenth Refueling Outage (2R16) was ongoing and electrical maintenance personne lwere performing scheduled 230 kV system testing on the 230 kV electrical protection equipment. On May 26, 2011, at 0226PDT, and again on May 27, 2011, at 1212 PDT, while personnel were performing testing on Unit 2 to verify functionality of the 230 kV electrical protection equipment, Unit 1 lost 230 kV startup power. The isolation of the offsite standby power source, and subsequent loss of power to startup feeder breakers for the 4.16 kV operating buses, caused all Unit 1 emergency diesel generators (EDGs) to start in standby mode. For both events, all Unit 1EDGs started as designed, and were shutdown and returned to auto with no problems observed. Plant operators returnedStartup Transformers 1-1 and 1-2 to service, and declared Unit 1 startup power operable. Startup power on Unit 2 was cleared due to the maintenance activities being performed; therefore, it was unaffected by the events. The cause of the events was human error enabled by inconsistent reinforcement of human performance tools on the part of Electrical Maintenance leadership. A contributing cause for the event on May 26, 2011 was an inadequate procedure which lacked precise written work instructions, and did not call for the use of human performance tools and verification practices.Corrective actions focus on developing precise work instructions and strengthening the consistent use of correct human performance tools. Also, for equipment which can potentially impact both units, plant personnel will use robust barriers while work is in progress.
2752011006 | Diablo Canyon 1, Diablo Canyon 2 | 08/29/2011 | 01/27/2012 | ML12030A02 | <strong>Loss of Control Room Envelope Due to the Work Control Shift Foreman Incorrectly Authorizing Removal of a Blank Flange</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2011, at 1724 PDT, an operator attempted to reposition Unit 2 Control Room Ventilation System (CRVS) Dampers MOD-2 and MOD-2A using the CRVS mode switch in the control room, but was unable to do so. During a follow-up investigation, at about 2230 PDT, plant operators discovered that the integrity of the Units 1 and 2 common control room envelope (CRE) boundary was lost due to maintenance personnel removing a blank flange on the inlet duct to Dampers MOD-2 and MOD-2A with the dampers still inoperable (in mid-position). This condition is contrary to the requirements of Technical Specification (TS) 3.7.10 "Control Room Ventilation System (CRVS)." Maintenance personnel reinstalled the blank flange on August 30, 2011, at 0110 PDT. On August 30, 2011, at 1404 PDT, Pacific Gas and Electric Company made a late 8-hour nonemergency report (Reference NRC Event Notification 47223) under 10 CFR 50.72(b)(3)(ii)(B) and (b)(3)(v)(D). Plant personnel entered this late notification into the Diablo Canyon Nuclear Power Plant corrective action system. The cause was human error by the work control shift foreman when he prematurely authorized removal of the blank flange prior to all work being complete. Insufficient controls existed to assure CRE integrity was maintained during maintenance. Corrective actions included personnel coaching, revising or creating clearances, and separate maintenance procedures for working on control room ventilation.
2752011007 | Diablo Canyon 1, Diablo Canyon 2 | 09/12/2011 | 01/24/2013 | ML13025A16 | <strong>Inadequate Control Room Envelope Testing Due to Inadequately-Documented In-leakage Test Data</strong><br /><i>Abstract:&nbsp;</i>On September 12,2011, at 1745 PDT, operators declared the Unit 1 and 2 common control room envelope (CRE) boundary inoperable and entered Technical Specification (TS) 3.7.10, "Control Room Ventilation System (CRVS)." Pacific Gas and Electric Company (PG&E) had concluded that 2005 test data did not demonstrate that the CRE had no unfiltered in-leakage. On September 13, 2011, plant personnel verified that administrative controls were in place to maintain post loss-of-coolant-accident emergency core cooling system leakage at a rate that would ensure operator doses would not exceed the General Design Criterion (GDC) 19 limits for the highest in-leakage rate reported in the test. On January 30, 2012, PG&E submitted LER 1-2011-007-01, for Diablo Canyon Power Plant as an unanalyzed condition. PG&E is submitting this supplemental report under 10 CFR 50.73(a)(2)(i)(B) also, as a condition prohibited by TS following review of NRC Task Interface Agreement dated November 20, 2012.<br /><br /> Human error affected the interpretation oftest results and led to the nonconservative determination of zero in-leakage in 2005. Plant staff reassessed the previously implemented administrative controls and concluded that control room operator doses would not exceed GDC 19 limits. PG&E performed an assessment of the testing and revised procedures to specify separate acceptance criteria for each of the tested CRVS configurations in accordance with Regulatory Guide 1.197. PG&E subsequently modified the CRVS and successfully completed CRE testing using a single CRVS train.
2752011008 | Diablo Canyon 1, Diablo Canyon 2 | 11/03/2011 | 01/24/2013 | ML13025A16 | <strong>Control Room Ventilation System Design Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2011, at 1550 PDT, operators determined that the Diablo Canyon Power Plant (DCPP) control room ventilation system (CRVS) had a design vulnerability whereby unfiltered air supplied to the control room (CR) could exceed the flowrates used in the licensing-basis analysis of design basis accident consequences. Pacific Gas and Electric Company (PG&E) discovered this vulnerability during performance of CR in-leakage testing required by Technical Specification (TS) Surveillance Requirement (SR) 3.7.10.5. Therefore, PG&E reported this event as an unanalyzed condition. Plant staff established configuration controls to ensure two CRVS trains would remain available and completed the in-leakage testing using both trains. PG&E is submitting this supplemental report to identify this concern as a condition prohibited by TS, following clarification from the NRC that the completed testing did not meet the requirements of SR 3.7.10.5. Human error on the part of a 1991 Technical Review Group to eliminate the design vulnerability was the apparent cause of this issue. PG&E has implemented modifications to eliminate the design vulnerability, and successfully completed CR envelope testing using a single CRVS train. The incorrect conclusion that testing with both trains met SR 3.7.10.5 was due to unclear SR 3.7.10.5 bases. PG&E will revise the SR 3.7.10.5 bases, and the in-leakage test to provide the NRC's clarification in its Technical Interface Agreement 2012-08.
2772011001 | Peach Bottom 2 | 03/16/2011 | 05/06/2011 | ML11131A04 | <strong>High Pressure Coolant Injection System Inoperable due to Leaking Cooling Water Header Relief Valve</strong><br /><i>Abstract:&nbsp;</i>On 3/16/11, licensed operations personnel declared the High Pressure Coolant Injection (HPCI) system inoperable as a result of the discovery of voiding in a portion of the HPCI pump discharge piping while the HPCI system suction was aligned to the Suppression Pool. It was determined that the leak was from the HPCI cooling water header relief valve (RV-2-23B-066). When HPCI was aligned to the Suppression Pool as the suction source, this leakage was sufficient to create voids in the HPCI discharge piping. The relief valve was replaced and HPCI was declared operable on 3/18/11. A subsequent laboratory analysis of the relief valve was performed. Although the cause could not be definitively determined, the cause of the unexpected failure could be the introduction of fine particulate, such as iron oxide, between the disc outside diameter and nozzle bore. There was no actual safety consequence associated with this event. There were no previous similar events identified.
2772011002 | Peach Bottom 2, Peach Bottom 3 | 06/06/2011 | 07/29/2011 | ML11213A26 | <strong>Condition Prohibited by Technical Specifications due to Degraded Spent Fuel Pool Racks Boraflex® Panels</strong><br /><i>Abstract:&nbsp;</i>On 6/6/11, the plant staff determined that certain fuel assemblies in the Unit 2 Spent Fuel Pool (SFP) racks needed to be relocated to other Unit 2 SFP rack locations to gain additional fuel assembly subcriticality margin. This determination was based on information provided by the Nuclear Regulatory Commission (NRC) as part of the development of an NRC Task Interface Agreement (TIA). The TIA was performed as a result of an NRC unresolved item involving the plant staff's assessment of the degradation rate of the SFP rack neutron absorbers (i.e., Boraflex®). This event is considered to be a condition prohibited by Technical Specifications (TS) since additional SFP subcriticality margin was determined to be appropriate to meet TS design requirements for the SFP racks. The cause of the event was due to a degradation of the SFP rack neutron absorbing material (i.e., Boraflex®). The previous station assessment for the rate of degradation of Boraflex® was found by the NRC, as part of their TIA, to not have been conservative enough. Modifications to both the Unit 2 and Unit 3 SFPs will be performed. No subcriticality margin concerns existed on the Unit 3 SFP. There were no actual safety consequences associated with this event. Reduced margin in SFP racks containing Boraflex® is an industry concern and has been the subject of previous NRC generic correspondence.
2772011003 | Peach Bottom 2, Peach Bottom 3 | 09/21/2011 | 10/21/2011 | ML11298A07 | <strong>Delayed Relay Operation Results in E-3 Emergency Diesel Generator Actuation During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On 9/21/11 at approximately 1020 hours, an unplanned, valid actuation of the E-3 Emergency Diesel Generator (EDG) occurred during surveillance (functional) testing of the E-33 4 kV emergency bus undervoltage relays. The E-3 EDG started unexpectedly when time delay relay 3-54-183-1708 did not operate properly resulting in a delay in the E-33 bus transfer from the 00A019 to the 00A020 off-site source. This delay resulted in the operation of a Technical Specification undervoltage relay, which resulted in the valid actuation of the E-3 EDG on low voltage. Because the E-33 bus transfer from the 00A019 offsite source to the 00A020 offsite source occurred prior to the EDG reaching full speed and voltage, the EDG output breaker was not required to close. The cause of the event was due to the failure of the 3-54-183-1708 time delay relay to properly function. The relay was replaced. Additional actions and extent of condition considerations are being evaluated within the corrective action program. There were no actual safety consequences associated with this event.
2772011004 | Peach Bottom 2, Peach Bottom 3 | 09/23/2011 | 11/21/2011 | ML11329A06 | <strong>Oil Leak Resulting in E1 Emergency Diesel Generator Inoperability</strong><br /><i>Abstract:&nbsp;</i>On 9/23/11 at approximately 0127 hours, an oil leak was discovered on the E1 Emergency Diesel Generator (EDG). The leak was discovered when the EDG was being shut down as part of functional testing of the emergency 4-kV bus. The leak was from a crack on the lube oil drain line for the combustion air intake blower (supercharger). Analysis determined that the condition had previously existed and would have resulted in the EDG being unable to perform its safety function. This was a condition prohibited by Technical Specification 3.8.1, which requires all four EDGs to be operable or, if one is inoperable, then it must be returned to operable status within 7 days. The drain line was removed and replaced with a new line. The failure was caused by a crimp in the drain line that, when combined with the bending vibrations experienced by the line, caused a fatigue crack to develop. Inadequate maintenance work practices during maintenance performed in 2009 resulted in the damaged line not being identified. The use of a flexible drain line is being evaluated to prevent vibration fatigue. There were no actual safety consequences associated with this event.
2772011005 | Peach Bottom 2, Peach Bottom 3 | 10/26/2011 | 12/15/2011 | ML11356A07 | <strong>Inoperability of Qualified Offsite Power Circuit due to Design Weakness</strong><br /><i>Abstract:&nbsp;</i>On 11/16/11, Engineering personnel determined that a condition prohibited by Technical Specifications (TS) occurred as a result of two time periods within the last 3 years where the alignment of the two qualified circuits between the offsite transmission network and the onsite Class 1E AC electrical power distribution system did not comply with the NRC General Design Criterion (GDC) 17 (10CFR 50 Appendix A) concerning electric power systems. Contrary to GDC 17, alignments of the offsite power circuits to the station credited for TS compliance did not minimize, to the extent practical, their simultaneous failure under postulated operating and environmental conditions. It was determined that a lack of separation occurred due to the auxiliary power supply to the two credited offsite power source transformers (i.e., the 00X011 and 00X005 transformers) being provided from a common power source. The cause of the event was attributed to an inadequate design of the auxilliary power to the 00X011 transformer. In order to upgrade the reliability of the offsite sources, the 00X011 was installed in the mid-1990s to provide the station with a third offsite power source that could be made available to feed a TS qualified circuit. Interim controls have been established to ensure that the 00X005 and 00X011 are not simultaneously credited as part of the two TS operable qualified circuits. Procedural and / or design changes will be performed as part of the corrective action program to ensure that GDC 17 criteria is met. There were no actual safety consequences associated with this event.
2782011001 | Peach Bottom 3 | 09/21/2011 | 11/09/2011 | ML11343A68 | <strong>Containment Isolation Valve Inability to Close for a Design Basis Event due to Degraded Lubricant</strong><br /><i>Abstract:&nbsp;</i>On 09/22/11, during the P3R18 refueling outage, it was identified that the ability of the Reactor Water Cleanup Outboard Isolation Valve (MO-3-12-018) to close was degraded due to a motor-operator greasing deficiency. This deficiency was identified during performance of routine motor-operated valve (MOV) maintenance and diagnostic testing. It was determined that this condition was prohibited by Technical Specifications (TS) since this Primary Containment Isolation Valve (PCIV) was determined to be inoperable for containment isolation purposes during the previous operating cycle for a time period longer than allowed by TS. The cause of the greasing deficiency was due to inadequate lubrication. The valve was repaired on 9/23/11. Appropriate upgrades to the MOV lubrication program had already been made and were being implemented at the time of discovery. There were no actual safety consequences associated with this event.
2782011002 | Peach Bottom 3 | 05/04/2010 | 11/17/2011 | ML11325A38 | <strong>Residual Heat Removal Leaking Relief Valve Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 9/19/11, during the P3R18 refueling outage, Engineering personnel determined that a leak on the inlet connection to the D Residual Heat Removal suction piping thermal relief valve was due to cracking of the relief valve body and not due to a mechanical joint leak as originally identifed during cycle 18 operations on 4/27/10. Because the leak involved an American Society of Mechanical Engineers (ASME) Code Class 2 component, the associated component should have been considered inoperable when originally identified on 4/27/10. The inoperable component affected the operability of the B Residual Heat Removal Low Pressure Injection Subsystem. This event is considered as a condition prohibited by Technical Specifications and loss of safety function. The cause of the delay in identifying the inoperable condition was due to inadequate technical rigor when evaluating the operability of the relief valve on 4/27/10. The leaking relief valve was replaced on 10/2/11. Extent of condition reviews were performed for similar components in Unit 2 and Unit 3. Operations has instituted additional training and procedure revisions to drive improved performance regarding operability evaluations. There were no actual safety consequences as a result of this event.
2782011003 | Peach Bottom 3 | 09/25/2011 | 11/18/2011 | ML11325A38 | <strong>Automatic Depressurization System Safety Relief Valve Actuator Diaphragm Thread Seal Leak</strong><br /><i>Abstract:&nbsp;</i>Based on evaluation of the 9/25/11 surveillance testing performed on Safety Relief Valves (SRVs) during the P3R18 Refueling Outage, site Engineering personnel determined that the 71B SRV did not meet its allowable leak rate for the pneumatic actuation controls for the Automatic Depressurization System (ADS) feature of the SRV. This resulted in a degradation of the number of times the 71B SRV could be used during a design basis event. This event was considered as a condition prohibited by Technical Specifications. The cause of the excessive leak rate was due to a failure of the 71B SRV actuator diaphragm thread seal. The thread seal was replaced on 9/26/11. As-left leak testing was performed and the valve was restored to an operable condition to support startup from the P3R18 Refueling Outage. Based on March 2011 vendor technical evaluation report, upgrades to the diaphragm thread seal for ADS SRVs on Units 2 and 3 are planned. There were no actual safety consequences as a result of this event.
2782011004 | Peach Bottom 3 | 10/13/2011 | 01/13/2012 | ML12018A33 | <strong>HPCI Cable Routing Error Results in Degraded Post Fire Safe Shutdown (FSSD) Analysis</strong><br /><i>Abstract:&nbsp;</i>On 11/15/11, a Fire Protection Program (FPP) document impact review was performed for the Multiple Spurious Operation (MSO) modifications installed during the Unit 3 refueling outage in September 2011 (P3R18). During this review, it was determined that the modification for the High Pressure Coolant Injection (HPCI) turbine steam supply valve (MO-3-23-014) implemented during the refueling outage adversely impacted the PBAPS post-fire safe shutdown (FSSD) analysis. A new cable was routed through a room that relies on the HPCI system to achieve safe shutdown following a fire in the room. The design of the modification was performed by a contract engineering firm, who did not communicate the change in the route of the cable to PBAPS. Further investigation determined that procedures and other administrative controls were not followed, resulting in the FSSD analysis of the modification not being performed until after the modification was completed. An hourly fire watch patrol was established in the room upon identification of the issue. The circuit design for the valve was modified so that a new cable is not needed. These modifications were completed on 12/19/11. Additional actions to address the root causes have been identified and progress in completing the actions is being tracked by the corrective action program. There were no actual safety consequences as a result of this event.
2812011001 | Surry 2 | 02/02/2011 | 04/01/2011 | ML11105A03 | <strong>Auto Reactor Trip on Low Coolant Flow Due to Loop Stop Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2011, at 0533, the Unit 2 reactor automatically tripped from 98.3% power as a result of low flow in the "C" loop of the reactor coolant system (RCS). The plant responded to the reactor trip as designed. All three auxiliary feedwater (AFW) pumps automatically initiated on low-low steam generator (SG) water level providing flow to the SGs. The AFW pumps were secured by 0613. At 1222, the reactor coolant pump for "C" loop was stopped. With no flow, compliance with Technical Specification (TS) 3.17.1 was not maintained and a 30 hour action statement to place the unit in a cold shutdown condition was entered in accordance with TS 3.0.1. A preliminary root cause evaluation (RCE) determined that the low flow condition in the "C" RCS loop resulted from a separation of a loop stop valve's disc assembly from the stem, which allowed the disc assembly to drop into the flow stream. Approved RCE recommendations, designed to prevent the recurrence of a similar event, will be implemented through the corrective action program. This report is being submitted pursuant to 10CFR50.73 (a)(2)(iv)(A) as an event that resulted in the automatic actuation of engineered safety features and the reactor protection system and pursuant to 10CFR50.73 (a)(2)(i)(B) for operation prohibited by TS 3.17.1.
2812011002 | Surry 2 | 05/26/2011 | 07/25/2011 | ML11214A21 | <strong>Spurious Safety Injection Results in Exceeding Pressurizer Heatup Rate</strong><br /><i>Abstract:&nbsp;</i>On May 26, 2011, at 1524 hours, with Surry Power Station Unit 1 at 100% power and Unit 2 at intermediate shutdown (ISD), a spurious actuation of the Unit 2 Train B of the Safety Injection (SI) system occurred during performance of the Consequence Limiting Safeguards (CLS) Logic Test. The cause of the spurious SI was a failed relay. The relay was replaced and sent to the vendor for a failure analysis. Plant systems and components responding to the Train B SI signal started and functioned as designed. Train B SI was reset and the affected systems were restored to their pre-event configuration. The reactor was maintained at ISD and the health and safety of the public were not affected. At 1531 hours, the Pressurizer liquid space temperature began to increase and over a 45 minute period, the Pressurizer heatup rate exceeded the Technical Specification (TS) limit of 100°F per hour due to Pressurizer heaters remaining energized during the event. Also contributing to the temperature increase was the dynamic mixing caused by the insurge coupled with the warmer fluid already in the pressurizer when the SI initiated. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) for automatic actuation of an emergency core cooling system and actuation of an EDG, as well as 10CFR50.73(a)(2)(i)(B) for operation or condition prohibited by TS.
2812011003 | Surry 2 | 05/30/2011 | 08/01/2011 | ML11227A24 | <strong>Isolation of Main Feedwater Pump Results in Auxiliary Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2011, at 0808 hours, with Surry Power Station Unit 1 at 100% power and Unit 2 at intermediate shutdown, securing of a Unit 2 Main Feedwater pump resulted in the actuation of the Unit 2 motor driven Auxiliary Feedwater (AFW) pumps. The Unit 2 B Main Feedwater (MFW) pump was undergoing maintenance when the running Unit 2 A MFW pump outboard motor bearing experienced high temperature due to low oil flow. A decision was made to secure the Unit 2 A MFW pump to prevent bearing damage. The pump motor breakers for the Unit 2 A MFW pump were opened and the Unit 2 motor driven AFW pumps automatically started as expected and fed the Unit 2 steam generators until the plant was realigned to feed the steam generators with the condensate pumps. Plant equipment responded as designed and the health and safety of the public were not affected. This report is being submitted pursuant to 10CFR50.73(a)(2)(iv)(A) for automatic actuation of the AFW system.
2822011001 | Prairie Island 1, Prairie Island 2 | 12/23/2010 | 10/07/2011 | ML11284014 | <strong>Unplanned Actuation of 121 Motor Driven Cooling Water Pump, Supplement 2</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2011, an evaluation determined that the 121 Motor Driven Cooling Water Pump (MDCLP) when. not aligned as a safeguards replacement pump is included in the list of systems in 10 CFR 50.73(a)(2)(iv)(B). As a result, an actuation of the 121 MDCLP on 12/23(2010 was determined to be reportable under 10 CFR 50.73(a)(2)(iv)(A). The causal evaluation determined that the 121 MDCLP autostart was due to operation of the in service 21 Motor Driven Cooling Water Pump at near run out pump curve condition. When 11 Containment and Auxiliary Building Chiller tripped onlow evaporator temperature (from being operated under low load conditions) the Cooling Water System cooling waterdemand increased when the containment fan coil cooling water valves switched to the Cooling Water System. The increased cooling water flow demand dropped cooling water header pressure down to the autostart setpoint of 121 Cooling Water Pump. 121 Cooling Water Pump started as designed. Corrective actions to resolve the issue include performing a Cooling Water System review to determine methods and any single point vulnerabilities that can be performed to minimize the potential for autostarts of a cooling water pump.Operating procedures will also be evaluated to determine if procedural or operatioh period changes can be made toreduce the likelihood of autostarting a Cooling Water Pump.
2822011002 | Prairie Island 1 | 07/01/2011 | 08/23/2011 | ML11237006 | <strong>Unit 1 Reactor Manually Tripped in Response to an Inadvertent Turbine Stop Valve Closure .</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2011, Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was manually tripped from approximately 100% steady-state power. The manual reactor trip was in response to the right main turbine stop valve failing closed as the result of an Electro-Hydraulic (EH) oil leak located at the stop valve. As designed, 11 and 12 Auxiliary Feed Water (AFW) pumps auto started on steam generator low water level. The causal evaluation determined that right main turbine stop valve failed closed due to excessive oil leakage from a failed O-ring. An age related compression set and slight extrusion near the outside contact surface resulted in the failed O-ring.
2822011003 | Prairie Island 1 | 08/19/2011 | 10/15/2011 | ML11290124 | <strong>Unit 1 Reactor Coolant System Leak Detection Was Inoperable</strong><br /><i>Abstract:&nbsp;</i>On Saturday, August 13, 2011, the 1R11 radionuclide monitor failed and was taken out of service for maintenance. On August 18, 2011, at approximately 09:00 CDT, electrical Bus 310 was isolated for maintenance. The full consequences of isolating Bus 310 were not recognized during maintenance planning. When the de-energizing of Bus 310 was completed, 1R11 and both Containment Sump A Pumps were inoperable. Unit 1 entered TS 3.4.16, Condition D (all required monitors inoperable) with the required action to enter TS, LCO 3.0.3 immediately. On August 19, 2011, the station recognized that TS LCO 3.0.3 should have been entered (on August 18th at 09:00 CDT) and that this condition is reportable under 10 CFR 50.73(a)(2)(i)(B) as an operation or condition prohibited by TS (TS LCO 3.4.16, Condition D). The causal evaluation determined that station processes for complex electrical clearance order development and approval do not preclude the use of logic diagrams as a sole and final source of information to determine effect on plant conditions.
2852011001 | Fort Calhoun | 01/27/2011 | 03/28/2011 | ML11087199 | <strong>Inadequate Flooding Protection due to Ineffective Oversight</strong><br /><i>Abstract:&nbsp;</i>During identification and evaluation of flood barriers, unsealed through wall conduit penetrations in the outside wall of the intake structure were identified that are below the licensing basis flood elevation. A summary of the root causes included: a weak procedure revision process; insufficient oversight of work activities associated with external flood matters; ineffective identification, evaluation and resolution of performance deficiencies related to external flooding; and "safe as is" mindsets relative to external flooding events. The penetrations were temporarily sealed and a configuration change was developed and implemented whereby permanent seals were installed. Comprehensive corrective actions to address the root and contributing causes are being addressed through the corrective action program.
2852011002 | Fort Calhoun | 02/04/2011 | 07/27/2011 | ML11208199 | <strong>Failure of an RPS Trip Unit</strong><br /><i>Abstract:&nbsp;</i>On November 29, 2010, during the performance of a work order, voltage at reactor protective system (RPS) connection T-74 was found 39 millivolt (mV) higher than connection T-17 (RPS ground). The allowed limit is 4 mV. T-74 is the signal common lead for steam generator (SG) pressure channels 902 and 905 inputs to Trip Unit 6 (Low SG Pressure) and Trip Unit 7 (Asymmetric SG Transient). Further investigation determined that the affected channels should have been declared inoperable. With a channel of RPS inoperable the appropriate section of Technical Specifications should have been entered. The TS LCO action times were not met. The root causes are determined to be the following: 1. Management has not effectively enforced expectations of rigorous troubleshooting standards for equipment important to safety and/or operation. 2. The standards for implementation of the Corrective Action Program have been ineffective in identifying and driving resolution of repeat and less-significant failures of equipment important to safety and/or operation. The wire between terminals T-74 and relay contact terminal 12 was replaced.
2852011003 | Fort Calhoun | 02/03/2011 | 12/16/2011 | ML11353055 | <strong>Inadequate Flooding Protection due to Ineffective Oversight</strong><br /><i>Abstract:&nbsp;</i>During identification and evaluation of flood barriers, unsealed through wall penetrations in the outside wall of the intake, auxiliary and chemistry and radiation protection buildings were identified that are below the licensing basis flood elevation. Additionally a potential flooding issue was identified on the inside of the Intake Structure. Holes were noted in the floor at the 1007’6” level, which is the ceiling of the Raw Water Vault. A summary of the root causes included: a weak procedure revision process; insufficient oversight of work activities associated with external flood matters; ineffective identification, evaluation and resolution of performance deficiencies related to external flooding; and “safe as is” mindsets relative to external flooding events. The penetrations were temporarily sealed and a configuration change was developed and implemented whereby permanent seals were installed. A one foot sandbag berm was placed around the holes. Comprehensive corrective actions to address the root and contributing causes are being addressed through the corrective action program.
2852011004 | Fort Calhoun | 02/05/2011 | 07/28/2011 | ML11210147 | <strong>Isolation of Both Trains of Safety Related Auxiliary Feedwater</strong><br /><i>Abstract:&nbsp;</i>On February 5, 2011, during plant startup activities, operations personnel initiated a transition from auxiliary feedwater (AFW) to main feedwater (MFW) while in Mode 2 (Hot Standby Condition). During the transition, AFW was being supplied by a safety-related motor-driven AFW pump (FW-6) through the AFW nozzles (HCV-1107A/B and HCV-1108A/B). With MFW aligned and feeding both steam generators, the control room operator was directed to shut down FW-6 and return the system to its normal alignment. During this activity the control room operator placed both inboard isolation valves, as directed by procedure, HCV-1107A and HCV-1108A, into their closed position. This action defeated automatic initiation via an auxiliary feedwater actuation signal to open the valves, rendering both trains of AFW inoperable. The condition lasted approximately three minutes. The root cause analysis for this event determined that technical reviews performed on the operating instruction for AFW were incomplete in their consideration of how plant mode changes affected auxiliary feedwater safety system status. The condition was recognized and the control switches were placed in "Auto" restoring both trains to operable. The affected procedure will be revised to correct the problem prior to plant startup following the 2011 refueling outage.
2852011005 | Fort Calhoun | 06/14/2010 | 05/09/2011 | ML11130009 | <strong>Failure to Correctly Enter Technical Specifications Limiting Condition for Operation for the Reactor Protective System</strong><br /><i>Abstract:&nbsp;</i>On June 14, 2010, the reactor protective system (RPS) M2 contactor (similar to the RPS breakers) failed to open during periodic surveillance testing. Operations declared the RPS M2 contactor inoperable and entered Technical Specification (TS) Limiting Condition for Operation (LCO) action 2.15(1) because the RPS M2 contactor did not have a specifically defined LCO. Subsequent reviews determined that the station continued to operate in a condition not allowed by TS on June 14 and 15 for a period of approximately 20.5 hours. TS 2.0.1 should have been invoked. (Section 2.0.1, similar to standard TS 3.0.3.) The root cause for this error was determined to be the failure to implement an interim TS strategy when funding for standard improved TS was deferred. The operations staff has been directed to enter TS 2.0.1 for any failures of these contactors. FCS will conduct a formal review of other components which do not have specific TS LCO action statements and station actions that could be non-conservative with regard to entering TS 2.0.1. The review will identify those items that need administrative controls and place them in the appropriate station procedures.
2852011006 | Fort Calhoun | 03/22/2011 | 05/23/2011 | ML11144021 | <strong>Inoperability of Both Trains of Containment Coolers due to a Mispositioned Valve</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2011, during the performance of a test on containment cooler valves, a technician discovered that NG-HCV-400A-A3, "CCW Inlet Valve HCV-400A Nitrogen Supply Isolation Valve," was in the closed position. This is not the correct position. He informed the control room of the condition. At the time of discovery, containment cooler VA-3B was inoperable to support the performance of a surveillance test. Operations declared VA-3A inoperable as the backup nitrogen supply to HCV-400A for containment cooler VA-3A cooling coil was unavailable. Operations entered Technical Specification (TS) 2.0.1 (similar to Standard TS 3.0.3) since both VA-3A and VA-3B were simultaneously inoperable. An equipment operator was dispatched to open NG-HCV-400A-A3. After NG-HCV-400A-A3 was opened, VA-3A was declared operable. TS 2.0.1 was then exited. The root cause analysis determined the cause of this event was the station's leadership oversight effort has not been effective in the areas of use of the station's Corrective Action Program, human performance tools and safe work practices in reducing the potential for mispositioning events. The immediate corrective action of opening the affected valve restored VA-3A to an operable condition. Additional corrective actions to address the root and generic implications of this event will be addressed by the station's corrective action process.
2852011007 | Fort Calhoun | 04/12/2011 | 06/17/2011 | ML11171027 | <strong>Violation of Technical Specifications due to Reactor Coolant System Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2011, during the performance of an inspection of Reactor Coolant Pump (RCP), RC-3C, and its studs, a small boric acid leak was discovered. The leak was on a 3/4 inch nominal diameter stainless steel pipe welded to the pump upstream of isolation valve RC-270 (RC-3C, Reactor Coolant Pump Casing Gasket Leak Detection Pressure Indication Alarm PIA-3195 Root Valve). The pipe connects the area between the inner and outer gaskets on the reactor coolant pump casing to a pressure indicator alarm. The pipe had a through-wall crack. On May 30, 2011, it was determined that the failure of the pipe violated technical specifications for zero pressure boundary leakage. The root cause of the crack was transgranular stress corrosion cracking (TGSCC) caused by a post-manufacturing bend in a susceptible material that was in a corrosive environment. The affected pipe was replaced. Equivalent indicator piping for the other three RCPs was inspected and one of those lines was also replaced due to an unacceptable bend in the pipe. The line was evaluated for TGSCC and no indications were found. Associated instrument lines for the RCPs were evaluated and no susceptibility to TGSCC was noted.
2852011008 | Fort Calhoun | 06/07/2011 | 10/27/2011 | ML11301020 | <strong>Fire in Safety Related 480 Volt Electrical Bus</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2011, at approximately 0930 CDT, a failure of a safety related 480 volt AC (V) load center supply breaker in the switchgear room occurred (Bus 1B4A). Fire alarms were received in the control room and the Halon system that protects the switchgear rooms discharged. The fire brigade responded and found the room filled with smoke, but no active fire. At 0940 CDT an Alert was declared for a fire affecting the operability of plant safety systems required to establish or maintain safe shutdown. At 1313 CDT on June 7, 2011, Fort Calhoun Station (FCS) exited the Alert after confirming that the fire was extinguished and the area was ventilated to restore access. Shutdown cooling remained in-service during the event. FCS was also in an emergency classification of a Notification of Unusual Event (NOUE) due to high Missouri river level. The root cause of the event was the FCS design process failed to identify the silver plating of bus bar material as a critical interface when specifying replacements for the original circuit breakers. The design process failure extended to other safety-related 480 V load center circuit breakers as well. Corrective actions included replacing 480 V bus 1B4A and performing bus maintenance. Affected circuit breaker cradles will be realigned to ensure proper fit in the bus cubicles. Maintenance procedures are being revised to enhance maintenance practices.
2852011009 | Fort Calhoun | 06/26/2011 | 08/24/2011 | ML11236058 | <strong>Manual Start of a Safety System</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2011, at approximately 0125 CDT, the AquaDam®, which was providing enhanced flood protection for Fort Calhoun Station (FCS), failed after being struck by a skid loader. As a precautionary measure, plant operators used the abnormal operating procedures to align necessary plant equipment to alternate (emergency) power supplies. Emergency Diesel Generator (DG)-2 was manually started to remove bus 1A4 from offsite power. Diesel Generator (DG)-1 was manually started to remove bus 1A3 from offsite power as well. Both Emergency Diesel Generators loaded on their respective busses as designed. Offsite power remained available throughout the event. No safety-related equipment was impacted by the water intrusion. Plant equipment was realigned to the off-site power operating configuration and the emergency diesel generators were secured. FCS was also in a Notification of Unusual Event (NOUE), since June 6, 2011, due to high Missouri river level. River level at the time of this event was 1006 feet 6 inches mean sea level.
2852011010 | Fort Calhoun | 06/07/2011 | 06/29/2012 | ML12185003 | <strong>Fire Causes a Circuit Breaker to Open Outside Design Assumptions</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2011, a bus fault in load center 1B4A initiated a switch gear fire that resulted in the opening of a circuit breaker which supplies power to load center 1B3A, associated with the opposite train. A fire in one fire area that resulted in a loss of power to a load center associated with the opposite train is not in compliance with 10 CFR 50, Appendix R. The analysis assumes that a fire in a fire area affecting one train of power will be isolated such that power associated with the redundant train will be maintained. The direct cause of the circuit breaker trip was improperly configured zone selective interlock jumpers on circuit breaker 1B3A. The zone selective interlock jumpers were properly configured and the circuit breaker returned to service.
2862011001 | Indian Point 3 | 01/19/2011 | 03/10/2011 | ML11081006 | <strong>Technical Specification Prohibited Condition Caused by an Inoperable 32 Containment Spray Pump due to High Contact Resistance in the Supply Breaker Closing Circuit</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2010, during performance of the quarterly functional test of the 32 Containment Spray Pump (CSP) the supply breaker failed to close. The breaker was fully charged and there were no abnormal indications. A second attempt to close the breaker failed and the breaker was racked out and visually inspected with no anomalies identified with the breaker or cubicle. A test of the close circuit was satisfactory and the breaker and cubicle secondary contacts were cleaned and inspected. With the breaker in the test position it operated successfully, but when racked into the connect position it failed to close. The trip circuit was verified to operate. The breaker problem was isolated to the close circuit. With the breaker racked in and charged, the fuses were removed and the control switch was positioned to close while measuring continuity across the closing circuit. With the breaker in the test position all indications were as required. With the breaker in the connect position, an open circuit was measured. Measurements and contact alignment inspections were performed with no problems identified. The breaker was replaced with a spare breaker and the quarterly test successfully performed. The direct cause was the breaker closing circuit was not reset to allow breaker closure. The apparent cause was a malfunction in the breaker closing circuit resulting in an open circuit. Engineering's review of a vendor equipment failure evaluation (EFE) concluded the breaker failed to close due to a high contact resistance of the motor cutoff switch. Corrective actions include breaker replacement and revision of the Preventive Maintenance procedure to include resistance testing of the motor cutoff switch contacts. The event had no significant effect on public health and safety.
2862011002 | Indian Point 3 | 10/13/2010 | 04/25/2011 | ML11123A07 | <strong>Technical Specification Prohibited Condition Caused by an Inoperable 31 Battery Charger Due to Low Voltage Caused by a Degraded Gate Driver Board</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2010, during performance of the weekly station battery inspection, the float voltage was found to be low but within the operability span but adjustments could not be performed due to a faulty float potentiometer. Subsequently, the control room received a 31 Static Inverter (SI) auto transfer alarm. Investigation determined the 31 SI had reversed transferred then swapped back to forward transfer. The 35 BC was placed in service and the 31 BC shutdown. A troubleshooting plan was prepared for the 31 battery charger (BC), and the 31 SI was verified to be in forward transfer and carrying instrument bus loads. The 31 BC float potentiometer and the Float/Equalize switch were replaced. The 31 BC was re-energized and proper operation of the new potentiometer and switch was verified while unloaded. A post maintenance test (PMT) was performed on the 31 BC but the results were unsatisfactory because the voltage could not be set within the required range. Further troubleshooting identified 31 BC output voltage oscillations. The gate drive board (A14) was replaced on the 31 BC and testing results were satisfactory. The 31 BC was returned to service on October 21, 2010. The direct cause was due to unstable DC input voltage from the 31 BC due to a faulty gate drive board (A14). The apparent cause could not be determined. The most likely cause was random failure of the A14 board. The Al4 failure was not likely age related as the A14 board was replaced in 2005. Corrective actions included replacement of the gate drive board (A14) and load testing. The BC vendor was contacted to determine what may have caused the A14 board to malfunction and to provide recommendations. The vendor responded that there has been no history of failures for this component. The event had no significant effect on public health and safety.
2862011003 | Indian Point 3 | 02/22/2011 | 04/25/2011 | ML11117027 | <strong>Technical Specification Required Shutdown and a Safety System Functional Failure for a LeakingService Water Pipe Causing Flooding in the SW Valve Pit Preventing Access for Accident Mitigation</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2011, the Control Room was notified of flooding in the south service water (SW) valve pit. Subsequent investigation determined there was approximately three feet of water in the south valve pit with leakage in the area of Conventional Essential Header Discharge Isolation Valves SWN-6 and SWN-7. The leak was estimated to be approximately 150 gpm and not isolable. Technical Specification (TS) 3.7.9 (Service Water System) Condition E was entered. After further evaluation, it was concluded there was a loss of safety function because the condition would prevent the credited method of isolating the SW loads in the event of a Design Basis Accident due to the inaccessibility to the valve pit for valve operation. As a result of this determination TS 3.7.9 Condition E was no longer applicable and the plant was in a condition not specified in the TS and required a plant shutdown per TS 3.0.3. The direct cause was a 3/4 inch hole in the 10 inch SW pipe (line 1222) downstream of valve SWN-6. The root cause was an inadequate installation plan and repair of a flaw identified in 1992. Interim corrective actions included installation of a modified pipe clamp and UT readings to determine pipe operability. Corrective action was replacement of the effected pipe section in spring 2011 refueling outage. An engineering guideline will be developed providing direction on how SW leak repairs should be performed. The Generic Letter 89-13 program will be revised to prioritize inspection frequencies of SW pipe welds and include SW lines 1221 and 1222. Inspections of SW piping in the Unit 2 SW valve pit and the Unit 3 north SW valve pit will be performed. The event had no significant effect on public health and safety.
2862011004 | Indian Point 3 | 03/08/2011 | 05/03/2011 | ML11133A21 | <strong>Technical Specification Prohibited Condition Caused by Two Main Steam Safety Valves Outside Their As-Found Lift Setpoint Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2011, during the performance of surveillance procedure 3-PT-R006A, main steam safety valves (MSSV) MS-47-4 and MS-48-4 failed their As-Found lift set point test. In accordance with the test, these valves must lift at +/- 3% of their required setting. Valve MS-47-4 lifted at 1135.4 psig, 8.4 psig outside its acceptance range of 1063 to 1127 psig. Valve MS-48-4 failed to lift at greater than 1161.9 psig which is outside its acceptance range. The other 8 MSSVs tested passed their As-Found test criteria. Technical Specification (TS) 3.7.1,"Main Steam Safety Valves," requires the MSSVs to be operable in accordance with TS Table 3.7.1-1 and Table 3.7.1-2 TS Surveillance Requirement (SR) 3.7.1.1 requires each MSSV be verified to lift per Table 3.7.1-2 in accordance with the Inservice Testing Program. Operability of the MSSVs includes the ability to open within the setpoint tolerances. As these two valves were found outside their limit they failed their As-Found testing. In accordance with NUREG-1022, Section 3.2.2, reporting guidelines, the existence of similar discrepancies in multiple valves is an indication that the discrepancy may have arose over a period of time, and therefore existed during plant operation and is reportable. The direct cause of the two MSSVs lifting greater than 3% of their nominal setpoint is internal friction caused by spindle wear and spring skew. The apparent cause is inadequate frequency for preventive maintenance (PM). Corrective actions include, adjusting and re-testing with an As-Left setting within the +/- 1% As-Left set point criteria, valve overhaul and testing and the increase of PM frequency from 8 years to 6 years, and processing a modification to install bronze wear sleeves in the spring washers and adjusting bolts. The event had no effect on public health and safety.
2862011006 | Indian Point 3 | 11/12/2011 | 01/09/2012 | ML12020A23 | <strong>Technical Specification Prohibited Condition Due to Exceeding the Allowed Completion Time for an Inoperable Isolation Valve Seal Water System Due to an Out of Position Valve</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2011, during operator rounds a Nuclear Plant Operator (NPO) discovered the normally open valve IV-1400 of the Isolation Valve Seal Water (IVSW) System (IVSWS) closed. A review of the Check Off List (COL), plant drawings and Technical Specification (TS) 3.6.9 (IVSW System) determined that valve IV-1400 should be open in Modes 1, 2, 3 and 4. A review of the electronic Shift Operator Management System (eSOMS) equipment data base and past surveillances determined valve IV-1400 has been out of position since performance of refueling surveillance 3PT-R025D5 on March 27, 2011. With valve IV-1400 closed an IVSW header was inoperable. TS 3.6.9, Limiting Condition for Operation (LCO) requires the IVSWS to be operable. With one IVSW system header inoperable, TS 3.6.9 Condition A requires the restoration of the IVSWS to operable within 7 days. The condition is reportable because the inoperable header exceeded the TS 3.6.9 allowed completion time. The apparent cause was inadequate procedure use and adherence. Valve IV-1400 was not restored to the open position at completion of testing (3PT-R025D5) as required as a result of the inappropriate use of N/A contrary to guidance provided in procedure OAP-115 (Operations Commitments and Policy details) for use of the N/A provision. OAP-115 was inappropriately applied since the IV-1400 test position differed from the COL position. Corrective actions included opening the valve, counseling individuals involved, briefing of operations personnel of the event on procedure use and adherence and effective use of human performance tools. The event had no effect on public health and safety.
2892011001 | Three Mile Island 1 | 09/26/2011 | 11/20/2011 | ML11326A28 | <strong>Unanalyzed Condition Affecting Probable Maximum Flood (PMF) Level</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2011, an analysis titled "River Stage Discharge and Discharge Frequency Analysis" was completed. The analysis predicts the water level at the TMI-1 Intake Structure Pump House (ISPH) at the peak flow during a Probable Maximum Flood (PMF) will be 4.3 feet higher than the previous analysis. The new analysis predicts a PMF water level at 313.3 feet at the ISPH. The flood barrier system currently protects TMI Unit I for river levels up to 313.5 feet elevation. Because the original flood barrier system protected TMI Unit 1 for river levels up to 311 feet, if the PMF had occurred prior to September 2011, the event had the potential to adversely affect plant safety. No actual flooding occurred. The validity of the flood analysis had not been re-assessed due to the lack of a programmatic requirement to perform periodic re-assessments of the external flood hazard. A repetitive task will be instituted to periodically re-assess the external flood hazard.
2892011002 | Three Mile Island 1 | 12/22/2011 | 02/20/2012 | ML12053A01 | <strong>Remote Shutdown Relay 69X1RR Contact Failure</strong><br /><i>Abstract:&nbsp;</i>On 12/22/11, the Reactor Building Emergency Cooling Water pump discharge valve "B" (RR-V-1B) failed to open during performance of an Engineered Safeguards Actuation System (ESAS) quarterly surveillance test. RR-V-1B was declared inoperable placing TMI-1 in an unplanned 72-hour Limiting Condition for Operation (LCO). RR-V-1B was demonstrated to open and close via the control room console pushbutton. Troubleshooting determined a Remote Shutdown (RSD) transfer selector switch relay/contact was open. The open contact associated with the Remote Shutdown (RSD) transfer selector switch is in series with the ESAS signal to RR-V-1B. Intermittent contact make-up was determined to be the cause of the failure. The RSD transfer switch was cycled several times, and the manual portion of ESAS testing was repeated successfully. Administrative controls were applied to ensure the switch contact closed properly if the RSD transfer switch was manipulated pending replacement. The relay was replaced on 1/6/12. Based upon the failure analysis the relay/contact was considered inoperable at the plant start up (reactor criticality 11/24/11) to the date of discovery (12/22/11). This is reportable under 10 CFR 50.73 (a)(2)(i)(B), "a condition prohibited by Technical Specifications" due to exceeding the allowable outage time and changing plant mode without satisfying the minimum conditions for criticality.
2932011001 | Pilgrim | 02/20/2011 | 04/20/2011 | ML11112A12 | <strong>Technical Specification (TS) Required Shutdown - RBCCW 'B' Declared inoperable</strong><br /><i>Abstract:&nbsp;</i>At 0055 hours on Sunday, February 20, 2011, the Pilgrim Nuclear Power Station (PNPS) commenced a controlled shutdown of the reactor due to the 'B' train of Reactor Building Closed Cooling Water (RBCCW) being declared inoperable and expected to exceed its 72-hour Limiting Condition for Operability (LCO) as required by TS prior to return to operable status. With the plant operating at 100% power, leakage of Salt Service Water (SSW) was detected in the RBCCW system due to high chloride levels and increased inventory in the system. An investigation into the event determined that the source of the SSW was isolated to the 'B' RBCCW heat exchanger which is designed to cool RBCCW under normal and post-accident conditions. The quantity of the leakage was determined to exceed the design limits established to ensure post-accident operation of the system and the 'B' train of RBCCW was subsequently declared inoperable. The leak detection and repair activities identified a single tube leak resulting from an improperly modified tube sleeve (shortened and incorrect bevel) which accelerated wear on the parent tube. This event had no impact on the health and/or safety of the public.
2932011002 | Pilgrim | 02/20/2011 | 04/20/2011 | ML11112A12 | <strong>Reactor Scram During A Planned Reactor Cool-Down with All Control Rods Fully Inserted</strong><br /><i>Abstract:&nbsp;</i>On Sunday, February 20, 2011 at 1034 EST, with the reactor shutdown and all control rods fully inserted a valid Reactor Protection System (RPS) low reactor water level initiation signal (+12 inches) was received. The RPS actuation signal resulted in a reactor scram and actuation of Primary Containment Isolation System (PCIS) Group II (Dryvvell) isolation, Group VI (RWCU) isolation and a Reactor Building Isolation System (RBIS) actuation. At the time of the event, a controlled reactor shutdown and cooldown was in progress. The Reactor Mode Selector Switch was in "Startup" and the low reactor water level actuation signal was the result of reactor water level control difficulties during the cool-down using the Mechanical Pressure Regulator (MPR). Reactor water level was immediately restored, the isolations (Group II and VI) were reset; and the RPS signal was reset at 1135 EST. All systems operated as expected, in accordance with design. Corrective actions taken included the revision of the reactor heat-up / cool-down procedure to incorporate lessons learned and to identify the Bypass Valve Opening Jack (BVOJ) as the preferred method for executing a reactor pressure vessel cool-down. Corrective actions planned include the performing of an analysis of MPR/RPV and level response during plant cool-down at the plant simulator and evaluate results for disposition. This event had no impact on the health and/ or safety of the public.
2932011003 | Pilgrim | 05/10/2011 | 07/08/2011 | ML11195A14 | <strong>Reactor Scram on Intermediate Range Monitor High - High Flux</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2011, during STARTUP Mode with reactor thermal power at approximately 1.7 percent, Pilgrim Nuclear Power Station(PNPS) experienced an automatic reactor scram while raising reactor temperature and pressure. The reactor scrammed on intermediate range monitor (IRM) hi-hi flux on both reactor protection system channels. Prior to the scram, operators took the reactor critical, reached the point of adding heat, and established a heatup rate. During the heatup, operators observed a high heatup rate and in response, the shift manager directed operators to insert control rods to reduce the heatup rate. The number of rods or number of notches to insert was not specified. Power began to lower as expected; however, operators did not recognize that inserting control rods to reduce heatup rate with rising moderator temperature caused the reactor to become subcritical. After achieving a temperature change from the power reduction, operators withdrew the same control rods before evaluating the core condition. The resultant reactor response was a faster power ascension rate than expected, which led to an automatic intermediate-range high-flux reactor trip. All systems operated as expected, in accordance with design. The root cause of this event was determined to be the failure to adhere to established standards and expectations due to a lack of consistent supervisory and management enforcement. Investigation into the event revealed several examples of inconsistent enforcement of administrative procedure requirements and management expectations for command and control, roles and responsibilities, reactivity manipulations, clear communications, proper briefings, and proper turnovers. Numerous corrective actions have been taken or are planned to reinforce standards and retrain crew members on the fundamentals of criticality and heating range operation. This event had no impact on the health and/ or safety of the public.
2932011004 | Pilgrim | 05/14/2011 | 07/12/2011 | ML11228A02 | <strong>Technical Specification (TS) Required Shutdown - Drywell to Torus DP</strong><br /><i>Abstract:&nbsp;</i>At 0245 hours on May 14, 2011, with the plant operating at approximately 14% power and the mode switch in RUN, Pilgrim Nuclear Power Station (PNPS) commenced a controlled shutdown of the reactor due to inoperable Drywell to Suppression Chamber (i.e., Torus) Vacuum Breakers. The Drywell to Torus vacuum breakers were declared inoperable due to inability to set the conditions necessary to demonstrate that Technical Specification (TS) limits for Drywell to Torus differential pressure decay rate were satisfied. An investigation of the event determined that inability to maintain Drywell to Torus differential pressure was caused by improper sealing on three (3) of ten (10) Drywell to Torus vacuum breakers. The direct cause of improper valve sealing was identified to be improper magnet to striker plate clearance adjustment. The root cause of the event was identified to be lack of relevant information in a maintenance procedure. The plant was shutdown and action was taken to locate the leakage path between the Drywell and Torus airspace. The leakage path was identified and corrective action was performed to restore Drywell to Torus vacuum breaker seal capability. This event posed no threat to public health and safety.
2932011005 | Pilgrim | 11/17/2011 | 01/16/2012 | ML12018A33 | <strong>Technical Specification Required Shutdown due to Inoperable Feedwater Check Valve</strong><br /><i>Abstract:&nbsp;</i>On Thursday, November 17, 2011, at 1515 hours, with the reactor at approximately 50% core thermal power, the station entered a 24 hour cold shutdown action statement due to the inability to provide a manual isolation for a main feedwater line check valve that had been declared inoperable due to a leak. The reactor was at reduced power in order to perform a planned main condenser thermal backwash. While at reduced power an inspection of the main steam tunnel (a normally locked closed high radiation area) was performed as part of a scheduled system inspection. The inspection identified a leak on the feedwater line 'B' outboard check valve (6-CK-62B). The feedwater check valve was declared inoperable and the Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.7.A.2.a.5 "All containment isolation check valves are operable or at least one containment isolation valve in each line is secured in the isolated position" was entered. Because there was no ability to manually isolate the primary containment penetration the station was required to be in cold shutdown within 24 hours per TS 3.7.A.5. This event was initially reported to the USNRC under 10 CFR 50.72 (b)(2)(i) via Event Report #47454 and had no impact on the health and/ or safety of the public.
2932011006 | Pilgrim | 11/30/2011 | 01/30/2012 | ML12032A27 | <strong>HPCI Turbine Governor Control Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On November 30, 2011, at 1747 hours, with the reactor at 100% core thermal power and steady state conditions, Pilgrim Nuclear Power Station (PNPS) declared the High Pressure Coolant Injection (HPCI) system inoperable due to the HPCI turbine governor control valve (HO-2301-24) failing to open during planned post-maintenance testing. The governor control valve is a hydraulically operated valve and its normal position is closed. The valve has a safety function to open on a demand signal during certain event mitigation scenarios requiring the HPCI system operation. The governor control valve failed to open during the post-maintenance testing from the Alternate Shutdown Panel (ASP) and subsequently from the Main Control Room. The HPCI system was declared inoperable and the Limiting Condition for Operation (LCO) for Technical Specification (TS) 3.5.C.2 was entered. This event had no impact on the health and/or safety of the public.
2932011007 | Pilgrim | 12/25/2011 | 12/21/2012 | ML12361A30 | <strong>Safety Relief Valve Declared Inoperable Due to Leakage</strong><br /><i>Abstract:&nbsp;</i>On Monday, December 26, 2011, at 1250 hours, with the reactor at 100% core thermal power, the stationentered a 24-hour action statement to initiate a controlled shutdown and be less than 104 psig reactorpressure due to suspected leakage across the first stage of safety relief valve (SRV) RV-203-3D. The SRVwas declared inoperable due to criteria specified in a Pilgrim plant procedure. Specifically, the SRV isinoperable if the pilot stage thermocouple temperature is 35° F below its baseline temperature. The safetyrelief valve was declared inoperable and the Limiting Condition for Operation (LCO) for TechnicalSpecification (TS) 3.6.D was entered. Due to the valve being declared inoperable, the station was required tobe shutdown and reactor coolant pressure be below 104 psig within 24 hours per TS 3.6.D.2. Following the shutdown, RV-203-3D was repaired with a new pilot valve and the plant was returned to full power operation. This event had no impact on the health and/or safety of the public.
2952011001 | Zion 1, Zion 2 | 07/14/2011 | 09/06/2011 | ML11257A04 | <strong>Improper Storage of Fuel Rod Storage Canister in Spent Fuel Pool</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2011, during a fuel data management software program site training class, it was identified that a Fuel Rod Storage Canister (FRSC) was stored in the wrong region of the Spent Fuel Pool (SFP). A fuel reconstitution campaign was conducted in 1992. Thirteen damaged fuel rods from seven different fuel assemblies were placed in the FRSC designed by Westinghouse and stored in the SFP during that campaign. At that time the SFP contained a single region rack design with no fuel assembly storage restrictions based on initial enrichment and fuel burnup. In 1993, a new SFP rack design utilizing a two region configuration was installed. The design included Region 2 storage restrictions based on the initial fuel enrichment and fuel burnup in accordance with Permanently Defueled Technical Specification (PDTS) 3.1.3, "Spent Fuel Assembly Storage." Following installation of the new rack design, the FRSC was placed in a SFP Region 2 rack cell. The criticality analysis for the FRSC contains restrictions on the storage location based on the most limiting rod stored within the FRSC. This means that if the FRSC contains rods from a fuel assembly with SFP region storage restrictions, then those same restrictions apply to the FRSC. A review of records conducted on July 14, 2011 determined that nine of the thirteen fuel rods stored in the FRSC did not satisfy the requirements to allow Region 2 rack storage. Consequently, storage of the FRSC in SFP Region 2 since 1993 is considered a violation of Permanently Defueled Technical Specification (PDTS) 3.1.3. Upon discovery, immediate actions to relocate the FRSC to SFP Region1 were initiated. The FRSC relocation was completed on July 20, 2011. A subsequent technical evaluation has concluded that Region 2 storage of the FRSC was within the rack design basis criticality limits.
2962011001 | Browns Ferry 3 | 05/12/2011 | 01/05/2012 | ML12010A16 | <strong>Loss of Shutdown Cooling (RHR)</strong><br /><i>Abstract:&nbsp;</i>On May 12, 2011, at 1825 hours Central Daylight Time (CDT), Browns Ferry Nuclear Plant (BFN)- Unit 3 was in Mode 4, as a result of the severe weather event that occurred on April 27, 2011. Relay maintenance activities in the Primary Containment Isolation System (PCIS) inadvertently de-energized a Group 2 PCIS relay, which initiated a partial Group 2 PCIS isolation. The partial Group 2 isolation caused a trip of the 3B Residual Heat Removal (RHR) pump, which subsequently resulted in a loss of shutdown cooling (SDC). The relay wires were re-connected and SDC was restored on BFN-Unit 3 at 1905 hours CDT. Moderator temperature prior to the event was 112.5 degrees Fahrenheit (F) and the highest moderator temperature recorded during the loss of SDC event was 122 degrees F. This condition is reportable under 10 CFR 50.72(b)(3)(v), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove Residual Heat. A 60 day written report was required in accordance with 10 CFR 50.73(a)(2)(v), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (B) Remove Residual Heat.
2962011002 | Browns Ferry 3 | 05/22/2011 | 07/21/2011 | ML11203A51 | <strong>Reactor Scram due to Scram Discharge Volume High Water Level</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2011, at 17:37 hours Central Daylight Time (CDT), with Browns Ferry Nuclear Plant (BFN) Unit 3 in Cold Shutdown and surveillance testing in progress, Unit 3 received a valid Reactor Protection System (RPS) actuation signal from both channels of the RPS due to Scram Discharge Volume (SDV) high water level. The scram occurred as Maintenance personnel were performing Intermediate Range Monitor (IRM) correlation for range 6 to 7. Maintenance personnel were measuring voltage during the reconnection of a high voltage cable to IRM G channel. A spike occurred on IRMs C and D channels indicating an invalid (safety function had already been completed) full reactor scram. After diagnosing the cause of the IRM scram, Operations personnel reset the scram and immediately received a valid RPS scram signal due to Scram Discharge Volume (SDV) high water level. The cause of the event was that Operations personnel did not place the SDV high water level switch in bypass as required by procedure before resetting the first RPS scram. Thus, as the initial scram was being reset, the SDV filled with water causing the second scram.
2962011003 | Browns Ferry 3 | 09/28/2011 | 11/26/2012 | ML12333A01 | <strong>Automatic Reactor Scram due to a Main Turbine Generator Load Reject</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2011, at 0414 hours Central Daylight Time, Browns Ferry Nuclear Plant (BFN) Unit 3 automatically scrammed due to a main turbine generator load reject. Seven safety relief valves cycled due to the reactor pressure transient. All systems responded to the turbine trip as expected. No Emergency Core Cooling System or Reactor Core Isolation Cooling System reactor water level initiation set points were reached. Primary containment isolation and initiation signals for groups 2, 3, 6, and 8 were received as expected. Reactor water level was automatically controlled by the Feedwater System. There were two root causes identified: 1) preventive maintenance instructions did not contain adequate inspection criteria for a generation risk sensitive component (debris screen) and 2) weaknesses within the welding program allowed multiple repetitive welds on trip sensitive equipment. A corrective action to prevent recurrence is to verify installation of a non-welded debris screen in BFN Units 1, 2, and 3 isolated-phase bus A, B, and C ducts. Another corrective action to prevent recurrence is to revise procedure MMDP-10, Controlling Welding, Brazing, and Soldering Processes, to include controls that limit the number of attempts to repair the same weld area on plant equipment.
2982011001 | Cooper Station | 01/18/2011 | 03/14/2011 | ML11077005 | <strong>Both Loops of Residual Heat Removal Inoperable Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On January 18, 2011, the open position indication light for Reactor Recirculation Pump "A" Discharge valve (RR-MO-53A) was discovered de-energized. Investigation found a damaged socket resistor for the bulb, causing fuses to the control power circuit for the valve to be open-circuited, preventing RR-MO-53A from closing to support the Residual Heat Removal (RHR) "A" Low Pressure Coolant Injection (LPCI) safety function, if needed. At the time of discovery, the RHR Loop "B" of LPCI was inoperable for planned maintenance. This condition resulted in a loss of safety function for the Emergency Core Cooling System. The fuses were replaced and the RR-MO-53A indication changed state from "closed" to "open" on the Plant Monitoring Information System (PMIS). After satisfactory completion of Post Maintenance Testing, RHR Loop "A" was declared operable. The root cause of this event is that there were no significant barriers in existence that could have provided prompt indication that the starter circuit had become inoperable. To prevent recurrence, the station procedure was revised to include shiftly verification of this valve position and the PMIS will be upgraded to indicate power loss to the starter circuit for RR-MO-53A and RR-MO-53B. CNS reported this event per Event Notification 46563. This event was not risk significant.
2982011002 | Cooper Station | 04/17/2011 | 07/26/2011 | ML11213A02 | <strong>Technical Specification Prohibited Condition for Service Water Booster Pump</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2011, Cooper Nuclear Station (CNS) observed that the outboard oiler reservoir for Service Water Booster Pump (SWBP) B motor was low, and there was an oil sheen on the floor and motor. As a result, oil was added to the reservoir. On April 27, 2011, the outboard oiler reservoir was discovered empty. SWBP B was declared inoperable at 15:40 Central Daylight Time (CDT) on April 28, 2011. Further investigation found that the four cap bolts that hold the upper bearing in place were loose, the lock washers were not compressed, and the seal between the bearing halves was cracked. The two bearing halves were resealed, the bolts tightened, the lock washers compressed, and oil added to the reservoir. SWBP B was declared operable at 02:30 CDT on May 7, 2011. The root cause of the event is a lack of inspection protocol for large electric motors which includes a check for loose bolts. To prevent recurrence, CNS will develop a process that requires inspection of large motors to include loose, damaged, or missing components. CNS will conduct a vendor inspection of the Appendix B programs of the supplier(s) for the SWBP motors provided to CNS. This shall include a review of the corrective action to fix the loose bolts problem and a review of the effectiveness of that fix. This event was not risk significant.
2982011003 | Cooper Station | 03/27/2010 | 10/12/2011 | ML11291A18 | <strong>Loss of Safety Function and Past Inoperability of Service Water Strainers</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2010, the 'A' Service Water (SW) strainer failed to operate as expected. Cooper Nuclear Station (CNS) found the strainer wiper motor-to-gearbox coupling was not engaged to turn the gearbox shaft. The gear side key had become dislodged allowing the coupling half to move enough to disengage the coupling sleeve. This condition impacted the ability of the strainer to perform the automatic backwash function to keep it clear of debris. CNS did not enter the applicable Technical Specification limiting condition for operation due to acceptable differential pressure across the strainer, the ability to take actions to maintain the strainer operable, and the lack of available information indicating an inoperable condition existed. CNS' evaluation of the failure identified a history of performance problems for both divisions of SW strainer couplings. The root causes are design and design control of the reduction gear-to-motor shaft configuration for the SW strainers, specifically including the coupling, is inadequate; and historical coupling failure evaluations failed to identify the original design fault. As an interim measure, CNS installed new worm gear shafts and couplings with solid sleeves for both SW strainers. To prevent recurrence of the failure, CNS will implement a new SW strainer modification. The equipment failure is not risk significant.
2982011004 | Cooper Station | 06/13/2011 | 08/09/2011 | ML11224A03 | <strong>Technical Specification Prohibited Condition for Non-Compliance with LCO 3.0.4</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2011, while reviewing a post Refueling Outage 26 (RE26) report, it was discovered that Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.4.b was not complied with during startup from RE26. TS LCO 3.0.4.b requires, in part, "When an LCO is not met, entry into a MODE or other specified condition in the Applicability shall only be made: b. After performance of a risk assessment addressing inoperable systems and components, consideration of the results, determination of the acceptability of entering the MODE or other specified condition in the Applicability, and establishment of risk management actions..." Cooper Nuclear Station changed from Mode 2 to Mode 1 while in an LCO for the Low Pressure Coolant Isolation (LPCI) subsystem "B" being inoperable without performing a risk assessment prior to changing modes. The root cause of this event was determined to be a deficient procedure that does not prompt operations to review all methods of LCO tracking to ensure that LPCI system LCOs related to Suppression Pool Cooling activities are closed prior to the change from Mode 2 to Mode 1. To prevent recurrence of this event, the procedure will be revised to prompt the reviews. As an interim action, a standing order was created that directs the reviews. The safety significance of this event is negligible.
2982011005 | Cooper Station | 06/22/2011 | 08/19/2011 | ML11236A10 | <strong>Technical Specification Prohibited Condition due to Valve Test Failure</strong><br /><i>Abstract:&nbsp;</i>On June 22, 2011, one of eight Target Rock safety relief valve (SRV) pilot valve assemblies, removed during Cooper Nuclear Station (CNS) refueling outage 26, failed to lift within Technical Specification (TS) lift setpoint requirements. Wyle Laboratories, Inc. performed this testing. The pressure setpoint of the failed pilot assembly is 1090 +/- 32.7 psig; the SRV pilot assembly lifted at 1199 psig. Two subsequent informational lifts were performed for the SRV pilot assembly and were within the TS pressure setpoint tolerances. The remaining seven SRV pilot valve assemblies tested satisfactory for TS lift setpoint requirements. The mechanistic cause is the same as reported in previous licensee event reports, pilot disc-to-seat corrosion bonding. CNS submitted a license amendment request (LAR) on January 5, 2011, to the Nuclear Regulatory Commission (NRC) to revise the number of SRVs required to be operable. This LAR is pending NRC approval. As such, corrective actions to implement a license amendment, related to TS 3.4.3 and the number of SRVs required to be operable, were not completed prior to the SRV testing in June 2011. This event is reportable as a condition prohibited by TS. The event has negligible safety significance.
2982011006 | Cooper Station | 08/15/2011 | 11/14/2011 | ML11321A22 | <strong>Loss of Safety Function and Past Inoperability of Service Water</strong><br /><i>Abstract:&nbsp;</i>On August 15, 2011, the 'A' Service Water (SW) strainer backwash outlet air-operated valve (AOV) failed to open as expected. Cooper Nuclear Station (CNS) found the AOV's internal rubber sleeve had ruptured and caused the AOV to fail. This condition impacted the ability of the strainer to perform the automatic backwash function to keep it clear of debris. CNS personnel replaced the sleeve, but it ruptured again prior to returning the subsystem to operable. CNS replaced the AOV with a temporary pipe spool piece and returned SW 'A' subsystem to operable on August 19, 2011. CNS' evaluation identified a history of ruptures with the strainer backwash outlet AOV's internal rubber sleeve for both divisions of SW. The previous sleeve ruptures did not result in either SW subsystem being declared inoperable. CNS identified two root causes: Inadequate application of the design process to ensure vendor specifications and design functions are met; and, nonconservative decision making resulted in the failure to implement actions to resolve equipment problems. CNS initiated compensatory measures to maintain both SW strainers operable and subsequently installed manual ball valves. To prevent recurrence, CNS will ensure that a valve that incorporates the lessons learned from the root cause evaluation is specified in the SW strainer replacement modification. This event has low risk significance.
2982011007 | Cooper Station | 11/22/2011 | 01/12/2012 | ML12024A32 | <strong>Primary Containment Lost Safety Function due to Open Drywell Vacuum Breaker</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2011, the top corner of a rolling podium that was being used during a surveillance at Cooper Nuclear Station (CNS) contacted the Master Control Switch for the Torus to Drywell Vacuum Breakers. The contact was sufficient to cause the switch to move from the normally closed position to the open position, causing one Torus to Drywell Vacuum Breaker to open. The Control Room operator performing the surveillance, along with a peer, recognized what had occurred and repositioned the Master Control Switch to the closed position, which returned the affected Torus to Drywell Vacuum Breaker to the normally closed position. The Torus to Drywell Vacuum Breaker and Primary Containment were declared inoperable, and the appropriate Technical Specification for Limiting Condition of Operation (LCOs) were entered. After the Torus to Drywell Vacuum Breaker closed, the vacuum breaker and Primary Containment were declared operable and the LCOs were exited. CNS identified the root cause to be the design of the rolling podium was deficient with respect to its use in the Control Room. The rolling podium has been removed from the Control Room. To prevent recurrence of this event, the rolling podium will be replaced with one designed such that it cannot contact the switches and instrumentation. This event has low safety significance.
3012011001 | Point Beach 2 | 02/27/2011 | 04/22/2011 | ML11112033 | <strong>Both Trains of SI Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 27, 2011, at 2159 CST, during the testing of the A train safety injection (SI) system [BQ], it was discovered that the oiler for the Unit 2, B train SI pump, had rotated and the oil had drained out. The B train SI pump was declared inoperable. At the time of the event, the A train of SI was out of service for performance of a routine inservice test. Because both trains of SI were inoperable, LC[) 3.0.3 was entered. Upon completion of the A train inservice test, Unit 2 exited LCO 3.0.3 at 2211 CST. Immediate corrective actions taken included restoring the oiler to the vertical position, refilling it and performing a 5-minute pump run. The root cause of the event was determined to be a 1995 modification to the SI pump oiler which introduced a latent design/configuration flaw. Additional corrective actions will include a design change to the SI pumps and oiler assemblies for both units to reduce the possibility of accidental misalignments. The actions are being tracked to completion in the corrective action program. An 8-hour ENS report was made in accordance with 10 CFR 50.72(b)(3)(v)(D) on February 28, 2011 at 0345 CST.
3012011002 | Point Beach 2 | 03/07/2011 | 05/03/2011 | ML11124027 | <strong>Engineered Safety Feature Steam Line Pressure Dynamics Modules Discovered Outside of Technical Specification Values</strong><br /><i>Abstract:&nbsp;</i>Between March 4, 2011 and March 16, 2011, procedure 2ICP 04.001 E, Reactor Protection and Safeguards Analog Racks Steam Pressure Refueling Calibration, was performed to satisfy Point Beach Nuclear Plant (PBNP) Technical Specification (TS) Table 3.3.2-1 Function 1e, Surveillance Requirement (SR) 3.3.2.8. Results showed that the as-found values for four out of six Unit 2 engineered safety feature (ESF) steam line pressure (SLP) dynamic compensation module lead time constants were slightly below the TS-required time constant limit of greater than 12.0 seconds. The drift calculation to address the static and dynamic settings was not performed in a timely manner. The drift calculation subsequently showed the modules' positive bias was small, but the setpoint was too low for the potential amount of drift. Corrective actions include implementing a performance monitoring plan, revising the setpoint tolerances to reflect the appropriate dynamic settings and refurbishing the SLP compensation modules with new setpoints and tolerances during the ongoing refueling outage. Pursuant to 10 CFR 50.73(a)(2)(i)(B), the event is reportable as a condition prohibited by TS and 10 CFR 50.73(a)(2)(vii), as a common cause inoperability of independent trains or channels.
3012011003 | Point Beach 2, Point Beach 1 | 04/08/2011 | 06/07/2011 | ML11159018 | <strong>Condition Prohibited by Technical Specification 3.8.2, AC Sources-Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2011, power to the Unit 2 Train A safeguards rack was removed from service under a clearance order. The clearance order did not identify that the removal of power affected the service water (SW) pump automatic-start on breaker closure for the 2A-05 safeguards bus. SW pump auto-start is required for standby emergency power operability on the associated Train A safeguards bus. The absence of the auto-start feature for the affected SW pumps rendered G-02, Train A emergency diesel generator (EDG), inoperable. On April 8, 2011, Train B EDG G-04 was removed from service for monthly surveillance testing. This action resulted in standby emergency power to the 2B-03 and 2B-04 safeguards buses being inoperable for a period of approximately four hours. This exceeded the Completion Time for Technical Specification (TS) 3.8.2, Condition B, Required Action B.1 of Immediately. It was not identified that there was an issue until near the end of a G-04 surveillance test, when operators were unable to initiate a containment isolation (CI) signal during the performance of a refueling test. By the time the reason for this condition had been determined, EDG G-04 testing had been completed and the EDG returned to service and declared operable. The event was caused by human performance errors that occurred in the development and approval of the clearance order. Corrective actions are being tracked to completion in the corrective action program. Pursuant to 10 CFR 50.73(a)(2)(i)(B), the event is reportable as a condition prohibited by Technical Specifications.
3012011004 | Point Beach 2 | 06/13/2011 | 10/13/2011 | ML11287008 | <strong>Automatic Reactor Trip During Startup Physics Testing Due to Source Range Detector Failure</strong><br /><i>Abstract:&nbsp;</i>On 06/13/11 at 1924 CDT, during beginning-of-life (BOL) physics testing with the reactor critical in MODE 2, an automatic reactor trip occurred while operators were inserting a shutdown bank during dynamic rod worth testing of Shutdown Bank A control rods. As power lowered during testing, the two source range nuclear instruments automatically energized, however, one of the two instruments subsequently failed high, thus establishing the required logic to initiate the automatic reactor trip. All plant systems functioned as required following the trip. All control rods fully inserted into the core. No emergency core cooling system or auxiliary feedwater systems actuated; the emergency diesel generators did not start; and power continued to be supplied from off-site sources. The reactor coolant system had forced circulation with the atmospheric steam dump valves being used for decay heat removal from the steam generators. The event was caused by the failure of a high voltage power supply in the source range nuclear detector. The failed power supply unit was replaced. Additional actions tracked in the corrective action program include establishment of a life cycle management program and periodic replacement of NIS high voltage power supplies in accordance with a preventive maintenance schedule. EN 46957 has been amended and reported in accordance with 10 CFR 50.72(b)(2)(IV)(B). The senior resident inspector was notified of the event.
3052011001 | Kewaunee | 12/13/2010 | 02/11/2011 | ML11053003 | <strong>Auxiliary Building Special Ventilation Inoperability Results in Prohibited Technical Specification Condition</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2010 with the Station at 100% power, charcoal laboratory radioiodine test results were found to be below the acceptance criteria for Auxiliary Building Special Ventilation Train A, which caused the train to be inoperable for a period that exceeded the Technical Specification allowed outage time. This occurred because the elapsed time, from removal of the sample to the time the vendor analysis was obtained, plus the time required for corrective actions to be completed to address the condition, exceeded the seven day Technical Specification allowance for one train being inoperable. Although the charcoal test results were below the minimum charcoal adsorber efficiency required for surveillance test acceptance, the efficiency assumed in the design basis accident analysis continued to be met. Therefore, the system remained capable of performing its specified safety function. Additionally, there are two trains of Auxiliary Building Special Ventilation and Train B passed its surveillance test. Therefore, there is no safety significance associated with this event. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B), for any operation or condition which was prohibited by the plant's Technical Specifications.
3052011002 | Kewaunee | 03/10/2011 | 05/03/2011 | ML11131A04 | <strong>Loss of Station Backfeed Results in Loss of One Train of Offsite Power During Refueling Outage</strong><br /><i>Abstract:&nbsp;</i>At 1549 CST on March 10, 2011 with the plant shutdown and the reactor defueled, power was lost to safeguards 4160 volt bus 6. Emergency diesel generator B started and re-energized bus 6. At the time of the event, bus 6 was energized from the main auxiliary transformer on backfeed. The event was caused by the opening of the 138kV breaker TA2066 as a result of an error by technicians working in the substation. All equipment operated as expected for the voltage restoration to safeguards bus 6. Safeguards bus 5 remained energized from offsite power through the tertiary auxiliary transformer during the event. Spent fuel pool cooling train A remained in operation during the event. Spent fuel cooling train B was restarted following restoration of power to bus 6. The event also caused loss of non-safeguards 4160 volt bus 4. In response to the loss of power to bus 4, the technical support center/station blackout diesel generator started but failed to load on 480 volt bus 46 resulting in continued loss of power to the technical support center. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) for any event or condition that resulted in the automatic actuation of emergency ac electrical power systems.
3052011003 | Kewaunee | 03/24/2011 | 05/23/2011 | ML11151A10 | <strong>Valve SI-11A, Safety Injection to Loop A Cold Leg, Breaker Found ON with Plant in MODE 3</strong><br /><i>Abstract:&nbsp;</i>At 1125 CST on March 24, 2011 with the plant shutdown and in Mode 3, it was identified that the electrical breaker for motor operated valve SI-11A, Safety Injection to Loop A Cold Leg, was in the ON position with the valve open, instead of the required breaker position of LOCKED OFF for the plant conditions as required by Technical Specifications. The valve itself was properly in the open position and was thereby providing the required safety injection flow path. The breaker being mispositioned was as a result of performance of procedure SP-33-297A, Safety Injection to Loop A Cold Leg Check Valve Leakage Measurement. As written, the procedure did not provide direction for performing valve breaker manipulations, nor did it include steps to verify valve SI-11A was in the open position upon completion of the check valve leakage measurement activities. When the condition was identified, SI-11A was verified open and the breaker was placed in the OFF position and LOCKED. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition prohibited by the plant's Technical Specifications.
3052011004 | Kewaunee | 03/31/2011 | 09/06/2011 | ML11258A04 | <strong>Required Action for One Offsite AC Electrical Circuit Inoperable Not Performed Until After Discovery</strong><br /><i>Abstract:&nbsp;</i>At 1744 CDT on March 28, 2011, with reactor power being raised while in Mode 1 following a refueling outage, one offsite AC electrical source became inoperable. The inoperability was due to operators' adjusting transformer load taps on that circuit, without adequately communicating information to the offsite grid operator regarding the onsite electrical demand caused by the specific configuration of operating plant equipment, such that predicted post-trip electrical grid voltage decreased below acceptance criteria. This condition was not discovered until March 31 at 0245, following which, the transformer tap settings were properly adjusted and the electrical circuit restored to an operable status at 0255. With one offsite AC electrical source inoperable, Technical Specification (TS) 3.8.1, Required Action A.1, applies. Required Action A.1 has a Completion Time of one hour. Performance of Required Action A.1 was not done prior to discovery of this condition. Therefore, this event is being reported pursuant to 10CFR 50.73(a)(2)(i)(B) for any operation or condition prohibited by the plant's Technical Specifications.
3052011005 | Kewaunee | 01/26/2011 | 05/04/2012 | ML12159A12 | <strong>Shield Building Ventilation Train Inoperable for Longer Period Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During a routine equipment inspection at 1725 CST on January 26, 2011, one printed circuit board in the "A" shield building ventilation (SBV) system control cabinet was found partially detached from its mounting plate with three of its four mounting posts broken. The card remained electrically connected and operating, but was only supported by its attached electrical wiring and one mounting post. This condition rendered "A" train SBV inoperable since the partially restrained card could not be assured to function during a seismic event. The mounting post failures were due to separation (tearing) of a neoprene section of the standoff extension fasteners on the posts. This condition was subsequently determined to have likely existed since shortly after the circuit board was installed on December 3, 2010, until the mounting posts were replaced on January 27, 2011. With one SBV system train inoperable, Technical Specification (TS) 3.6.c.1, applied. SBV system train "A" was inoperable for greater than the time periods permitted by TS 3.6.c.1. Therefore, this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition prohibited by the plant's Technical Specifications. Since the redundant SBV train (B) was twice removed from service concurrent with train "A" being inoperable, and the other train's circuit mounting posts also could not be assured to function during a seismic event, this condition is also being reported as an event or condition that could have prevented the fulfillment of a safety function, pursuant to 10 CFR 50.73(a)(2)(v) and as a common cause inoperability of independent trains, pursuant to 10 CFR 50.73(a)(2)(vii).
3052011006 | Kewaunee | 08/30/2011 | 10/31/2011 | ML11312A15 | <strong>Misapplication of Testing Allowance Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During routine surveillance testing of the control rod system on August 30, 2011, a rod control urgent failure alarm was received, indicating an electrical fault in the control rod drive system. Surveillance activities were temporarily suspended upon receipt of the urgent failure alarm while troubleshooting activities were carried out to address the cause of the urgent failure alarm. Control Bank A Group 2 was one step outside the required insertion limit at the time of the event. However, the provision of a Note in the applicable Technical Specification (TS), which provided an allowance that waived certain requirements of the TS while performing the surveillance, was being used to maintain compliance with the TS. The cause of the urgent failure alarm was not readily resolved and troubleshooting activities continued into the following shift. During subsequent evaluation of this event, use of this TS Note to maintain compliance with TS while the surveillance was suspended for an extended period was determined to be inappropriate. Consequently, the TS was no longer met and the required actions should have been taken. The inappropriate use of this Note was not recognized until the following day, by which time the required actions could not be carried out within the completion time of the TS. Therefore, this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition prohibited by the plant's Technical Specifications.
3062011001 | Prairie Island 2 | 02/19/2011 | 04/20/2011 | ML11111054 | <strong>Unit 2 Shield Building is Inoperable Due to Maintienance Activity</strong><br /><i>Abstract:&nbsp;</i>While Unit 2 was operating at 100% power, improper control of Unit 2 Shield Building access doors (Doors 172 and 173) during planned maintenance resulted in an unplanned Limiting Condition for Operation (LCO) entry and a Loss of Safety Function (LOSF) for the Shield Building system. During the maintenance work, the doors were simultaneously opened several times, for approximately ten seconds each time, resulting in a LOSF. This was reportable per 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of the safety function that was needed to control the release of radioactive material. The causal evaluation determined that Planning did not identify within the Work Order (WO) the latent impact of the LOSF when two Shield Building access doors were to be simultaneously opened.
3062011002 | Prairie Island 2 | 05/09/2011 | 06/30/2011 | ML11181062 | <strong>Unit 2 Trip as a Result of A Weather Related Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2011, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 tripped from approximately 100% steady-state power as a result of a turbine trip from a generator lockout signal. At the time of the trip Unit 1 was in a planned refueling outage in Mode 6 Operation and thunderstorms were in the vicinity of the plant. Post event diagnostics determined that the relay ground potential circuit had a missing link (wire) between substation panels which resulted in the loss of the reference ground potential to the associated protective relaying in the Switchyard panels. This resulted in the improper operation of the breaker protection relays. The causal evaluation determined that the proximate cause of the relaying scheme failure was inadequate ground wire installation during a modification to the substation equipment. The evaluation also determined that NSPM (Transmission and Nuclear) did not establish the appropriate standard for procedure quality with respect to work under System Control Center jurisdiction in the PINGP substation such that a means of effectively utilizing human performance tools to minimize errors during work, which directly impacts the safe and reliable operation of nuclear plants, was not in place.
3062011003 | Prairie Island 2 | 06/27/2011 | 08/23/2011 | ML11236059 | <strong>Unit 2 Offsite Power Sources Declared Inoperable as a Consequence of the Loss of the 2RY Transformer Bus Duct</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2011, the off-site AC power sources to Unit 2 Prairie Island Nuclear Generating Plant (PINGP) were declared inoperable as a result of Transformer 2RY lockout and less than the required minimum voltage on the transmission system. The paths to the transmission system was declared inoperable. Although inoperable, transmission system sources remained connected to Unit 2; emergency diesel generators were available but not required to run. The overcurrent ground detection relay actuated due to a bus phase to ground fault resulting from failed gasket material resulting in the Transformer lockout. It was determined that a less than adequate review of the Preventive Maintenance (PM) Deferral Process delayed the bus duct inspections that would have likely identified and corrected the deficient gasket material.
3112011001 | Salem 2 | 05/17/2010 | 04/15/2011 | ML11116A07 | <strong>21SW122 Isolation Function Inoperable Greater Than Allowed by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), any operation ... prohibited by the plant's Technical Specification" for the containment integrity function of valve 21SW122 being inoperable for greater than one-hour, contrary to the requirements of TS 3.6.1.1. On May 17, 2010 at 0116 hours, while performing a high flow flush of the No. 21 Component Cooling Heat Exchanger (CCHX), the required Service Water (SW) flow range of 9000-10000 gpm could not be achieved. Technical Specification Action Statement (TSAS) 3.7.3 was entered. Containment integrity was not at issue as the 21SW122 valve appeared to have stroked closed. A team established to investigate the CCHX low SW flow issue determined that the 21SW122 valve was not controlling flow. The valve was declared inoperable on May 17 at 1005 hours and Containment Integrity TSAS 3.6.1.1 was entered. The No. 21 CCHX was isolated on May 17 at 1053 hours and TSAS 3.6.1.1 was exited. Troubleshooting activities identified that the shaft of the No. 21 CCHX inlet air operated valve 21SW122 had corroded to the point of complete severing at the stem to body interface. The valve stem was replaced and the valve returned to OPERABLE status on May 18, 2010. A past operability evaluation was completed on May 28, 2010. This evaluation concluded that the valve was INOPERABLE for the closed (Containment Integrity) direction. On February 16, 2011, during an NRC inspection of the 21SW122 repair and extent of condition reviews, it was discovered that the 21SW122 being inoperable greater than the TS allowed action time had not been reported in accordance with 10CFR50.73 (a)(2)(i)(B). The cause of the 21SW122 valve shaft failure was severe localized microbiologically influenced corrosion attack. Actions taken included replacement of all SW122 valve stems, identification of susceptible valves, procedure revisions and preventive maintenance task changes to remove the shaft for inspection.
3112011002 | Salem 2 | 04/11/2011 | 06/06/2011 | ML11172A10 | <strong>Failure to Comply with Technical Specification 3.4.5 and 3.4.10.3</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73 (a)(2)(i)(B), "any operation or condition which was prohibited by the plant's Technical Specifications..." On April 11, 2011, at 11: 51 control room personnel entered TS 3.4.10.3 Act b to support testing of the Pressurizer Overpressure Protection System (POPS) channel 1 (2PR1) in accordance with procedure S2.OP-ST.PZR-0003 "Inservice Testing Pressurizer and Reactor Head Vent Valves." When the 2PR1 valve was demanded to open as the test key switch was turned to the test position, the channel 1 test light illuminated, but the valve did not respond as expected. 2PR1 was restored to its pretest position; however, 2PR1 remained inoperable and OFF. Following satisfactorily testing of 2PR2, control room personnel attempted to open 2PR1 from normal control room bezel, but 2PR1 failed to open again. At this point it was determined that 2PR1 had been inoperable since the entry into Mode 5 on April 10 at 02:21, and that Salem Unit 2 had operated in a condition prohibited by Technical Specifications. The troubleshooting and the as-found condition of the valve plug OD & cage ID confirmed that foreign material was the most likely cause of the failure of the valve to open upon initial demand. A new trim set was installed into the valve, and the valve was tested satisfactorily.
3112011003 | Salem 2 | 04/05/2011 | 06/06/2011 | ML11172A11 | <strong>Technical Specification Maximum Airflow in the Fuel Handling Building Exceeded</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73(a)(2)(i)(B), "any operation or condition which was prohibited by the plant's Technical Specifications." At approximately 0100 hours on April 8, 2011, a test of the Unit 2 Fuel Handling Building Ventilation System (FHV) was performed following the replacement of the high efficiency particulate air (HEPA) filter on the 21 FHV filtration train. The fuel handling building exhaust flow was measured at 24,627 cfm with the 21 FHV filtration train in service. Technical Specification (TS) 4.9.12.c requires a system flow rate of 19,490 cfm +/- 10% during system operation. Movement of irradiated fuel in the Fuel Handling Building (FHB) is to be suspended in accordance with TS 3.9.12 Action 'a' when the FHB ventilation system is inoperable. The measured flow rate was approximately 26% above the TS flow rate of 19,490 cfm. On April 5, 2011, irradiated fuel was moved in the Unit 2 FHB with the air flow rate exceeding the requirements of TS 3.9.12. The cause of the high air flow rate in the Unit 2 FHB is attributed to the air supply balancing damper being out of position; the air pressure regulator on the FHB roll up door was incorrectly set not allowing the door seal to inflate and the FHB exhaust fan inlet guide vanes operating in a degraded condition. Corrective actions consisted of setting the supply damper in the correct position, restoring the FHB roll up door air regulator to the proper setting, repairing the FHB exhaust fans, and revising the procedure for control of fuel movement in the fuel handling building.
3112011004 | Salem 2 | 06/26/2011 | 10/24/2011 | ML11305A12 | <strong>Automatic Reactor Trip due to Trip of the 23 Reactor Coolant Pump</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73(a)(2)(iv)(A), "any event or condition that resulted in manual or automatic actuation of any of the systems listed paragraph (a)(2)(iv)(B)." At approximately 1800 hours on June 26, 2011, the 23 Reactor Coolant Pump (RCP) tripped resulting in an automatic reactor trip on low flow in one reactor coolant loop above the P-8 permissive (36% power permissive). As expected, the 21, 22 and 23 Auxiliary Feedwater (AFW) pumps started on low steam generator level following the unit trip. Unit 2 was stabilized in Mode 3 at normal operating temperature and pressure with the 21, 22 and 24 RCPs in-service. Salem Unit 2 tripped on low reactor coolant flow in the 23 reactor coolant loop. The low flow condition was the result of the trip of the 23 RCP due to two separate phase to ground faults. Both ground faults occurred at the termination to the motor where the cable shield interfaces with the stress tube of the termination kit. The insulation at this location was found to be brittle. Existing cable testing practices performed in accordance with industry standards would not detect this cable condition. Failure analysis determined that a partial discharge test or potentially destructive testing would have to be performed to detect the cable insulation degradation. The 23 RCP motor was tested satisfactorily. The damaged sections of the RCP motor leads were removed and new terminations were made. Megger testing and visual examination of the 21, 22, and 24 RCP motor leads was performed. The post maintenance testing procedure will be revised. The RCP motor feeder cables for the Unit 1 and 2 RCPs will be replaced.
3112011005 | Salem 2 | 07/14/2011 | 11/09/2011 | ML11333A13 | <strong>Completion of a Plant Shutdown in Accordance with Technical Specification 3.0.3</strong><br /><i>Abstract:&nbsp;</i>This report is being made in accordance with 10CFR50.73 (a)(2)(i)(A) "The completion of any nuclear plant shutdown required by the plant's Technical Specification." At 2038 on July 14, 2011, during the performance of the Salem Unit 2 Emergency Core Cooling System (ECCS) fill and vent monthly surveillance test, a leakage path was identified from the Boron Injection Tank (BIT) relief valve 2SJ10 piping. Investigation determined that the leakage was approximately 15 gpm due to lifting of the 2SJ10 relief valve. Upon closure of the BIT inlet valve 2SJ4 to isolate the flow through the relief valve, a through wall socket weld crack developed on the 2SJ10 relief valve inlet piping. The BIT is part of the flow path of the high head safety injection system. Without the high head safety injection flow path operable, Technical Specification (TS) 3.0.3 was entered. The 2SJ10 relief valve lifting was the result of missed opportunities to correct a component design application deficiency. The socket weld cracking was determined by laboratory analysis to be caused by a combination of fatigue and transgranular stress corrosion cracking. The affected 2SJ10 piping has been replaced with a new straight run of pipe and the relief valve internals were replaced. Design changes will be performed to resolve 1/2SJ10 operating margin, eliminate unnecessary non-isolatable socket welds in the BIT system and replace the remaining non-isolatable socket welds in the BIT system with low carbon weld filler and install a stiffener on the 2SJ10 relief valve piping.
3132011001 | Arkansas 1 | 02/14/2011 | 04/11/2011 | ML11102025 | <strong>Violation of Technical Specification Due to the Failure to Enter the Appropriate Techncial Specification or Complete the Associated Required Action Prior to the Appropriate Completion Time</strong><br /><i>Abstract:&nbsp;</i>During the period beginning January 22, 2008 until January 4, 2011, Arkansas Nuclear One Unit 1 (ANO-1) periodically implemented compensatory measures during maintenance or failure of Emergency Switchgear Chillers (VCH-4A, VCH-4B), Battery Room Unit Coolers (VUC-14A, VUC-14C), or Switchgear Room Unit Coolers (VUC-2B, VUC-2D). During some of these instances, compliance with Technical Specification (TS) 3.8.4, "DC Sources - Operating" and TS 3.8.9, "Distribution Systems - Operating was not met. ANO-1 1 did not enter or remain in the appropriate TS for an inoperable system, subsystem, train or component when all the necessary attendant non-technical specification support equipment that are required for the system, subsystem, train, component or device to perform its specified safety function are also capable of performing their support function. VCH-4A or B individually have not been shown to be capable of supporting 100% of the room cooling requirements of both trains of vital switchgear when one of the chillers is out of service without implementing additional compensatory actions. Therefore, reliance on the opposite train chiller alone is not sufficient to maintain all cooling requirements of the affected train's vital switchgear. A misapplication of industry guidance resulted in the use of non-safety related unit coolers and additional compensatory measures as an acceptable alternative. Currently, TS LCO compliance is maintained when the switchgear room cooling is removed from service.
3152011001 | Cook 1 | 09/07/2011 | 11/07/2011 | ML11320A11 | <strong>Unit 1 Reactor Trip due to Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On September 07, 2011, at 0854 hours, Donald C. Cook Nuclear Plant (CNP) Unit 1 Reactor tripped automatically due to a trip of the main turbine. All control rods fully inserted and the auxiliary feedwater system (AFW) started and performed as designed. The reactor trip was uncomplicated and all major plant components functioned as designed; as such, there were no safety system functional failures. The reactor trip was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and the AFW actuation was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). The reactor trip and AFW actuation are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). The main turbine tripped due to an automatic turbine trip signal generated by the main turbine thrust bearing wear detection system. The initial investigation has concluded that there was no actual thrust bearing wear condition. The cause of the inadvertent trip signal has been determined to be a result of inadequate installation of sensing equipment. This inadequate installation resulted in a spurious trip signal common to both channels. Corrective actions have been taken to correct the installation.
3152011002 | Cook 1 | 11/25/2011 | 12/20/2011 | ML12004A16 | <strong>Manual Actuation of Auxiliary Feedwater Systems in Response to Loss of One Main Feedwater Pump</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2011, at 0517 hours, in response to rising vibrations of the Unit 1 East Main Feedwater Pump (MFP), Donald C. Cook Nuclear Plant control room operators initiated the Rapid Power Reduction Procedure in an effort to quickly lower power to remove the East MFP from service. At 0522 hours, operators tripped the East MFP due to rapidly rising vibrations and entered the procedure for Loss of One Main Feed Pump, which directs manually starting Auxiliary Feedwater (AFW) pumps, as required. Operators manually started both Motor Driven AFW Pumps and the Turbine Driven AFW Pump. Power was lowered and stabilized at approximately 58 percent. The East MFP was found with a cracked turbine rotor shaft during inspection. Completed corrective actions involved disassembly, inspection, and repair of the East MFP. These actions included replacement of the turbine rotor and coupling. Manually starting the AFW Pumps in response to actual plant conditions resulting from equipment failure was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A), Event Notification 47477, submitted on November 25, 2011. The event is also reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(iv)(A).
3172011001 | Calvert Cliffs 1 | 08/27/2011 | 10/20/2011 | ML11297A11 | <strong>Reactor Trip due to a Phase-to-Phase Short Circuit on Main Transformer</strong><br /><i>Abstract:&nbsp;</i>On August 27, 2011, at 2248 eastern daylight time, Unit 1 experienced an automatic reactor trip from 100 percent power. The Reactor Protective System actuated on loss of load. The loss of load occurred due to a phase-to-phase short circuit on the main transformer when main transformer lines were struck by dislodged Turbine Building siding caused by winds associated with Hurricane Irene. Immediately following the short circuit, 14 Containment Air Cooler stopped operating. Shortly after the plant trip occurred, 1A Emergency Diesel Generator was declared inoperable due to a shorted speed switch. The root cause analysis performed to address this event concluded that the Turbine Building Northwest corner siding was not installed per design during original construction. This resulted in a weaker siding connection to the Turbine Building structure, allowing the siding to come off in wind speeds less than design. At Calvert Cliffs, there have been no recent similar events involving a reactor trip associated with severe weather. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) due to Reactor Protective System actuation. Corrective actions include testing and inspection of the main transformer, replacement of B and C phase high line drops to the main transformer and inspection and repair of electrical connectors on the 1A Emergency Diesel Generator.
3172011002 | Calvert Cliffs 1, Calvert Cliffs 2 | 10/03/2011 | 12/02/2011 | ML11340A03 | <strong>Technical Specification 3.0.3 Entry for Inoperable 125 VDC Channels</strong><br /><i>Abstract:&nbsp;</i>At 1035 on October 3, 2011, Operators entered Limiting Condition for Operation (LCO) 3.0.3 for Calvert Cliffs Units 1 and 2. The LCO 3.0.3 entry was due to an emergent failure of 1A Diesel Generator (DG) Battery Charger which caused 1A DG to be inoperable concurrent with planned maintenance on No. 21 Saltwater Subsystem which caused 2A DG to be inoperable. The concurrent inoperability of both A Train DGs caused the A Train 125 VDC channels for each Unit to be declared inoperable and required entry into LCO 3.0.3 on both Units. At 1605 on October 3, 2011, 1A DG battery charger was returned to service and the 1A DG and all supported A Train components became operable. Limiting Condition for Operation 3.0.3 was exited for both Units at 1605. The apparent cause of the battery charger failure was age related degradation of its circuit board due to exceeding its expected service life. The affected circuit boards were replaced. Corrective actions include updating the preventive maintenance task to replace the battery charger circuit boards on a set periodicity.
3172011003 | Calvert Cliffs 1, Calvert Cliffs 2 | 10/21/2011 | 12/16/2011 | ML11354A24 | <strong>1A Emeraencv Diesel Generator Inoperabilitv due to Water Intrusion</strong><br /><i>Abstract:&nbsp;</i>On October 21, 2011, Calvert Cliffs Nuclear Power Plant discovered that a reportable condition existed. On August 28, 2011, numerous alarms were received for the 1A Emergency Diesel Generator (EDG) (train A, one of two safety-related EDGs dedicated to Unit 1). Water was intruding down the diesel generator intake piping, resulting in a short circuit on the 1A2 engine speed switch circuit. The 1A EDG was declared inoperable and appropriate Technical Specifications were implemented. The 1A2 engine speed switch assembly was cleaned, dried, and inspected. The 1A EDG was returned to operable status. Corrective actions include repair of the affected piping penetrations. A root cause analysis determined the most probable root cause to be the penetration around the 1A2 engine combustion air intake pipe on the 80 foot level of the 1A EDG Building was unable to perform its design function of being leak tight. This may have occurred due to improper installation, manufacturing defect, degradation, or original design considerations. This condition may have existed since construction of the 1A EDG Building in 1996. There have been no licensee event reports for similar events at Calvert Cliffs.
3182011001 | Calvert Cliffs 2 | 02/17/2011 | 04/15/2011 | ML11108A13 | <strong>Pressure Boundary Leakage Caused by Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2011, while Unit 2 was in a refueling outage, it was verified that during a bare metal examination of all pressurizer heater locations, dry boric acid.was noted on heater N3 outer sleeve to weld pad J-Groove weld location indicating reactor coolant leakage. Based on this visual examination and the results from chemical analysis, the leak most likely existed during plant operation. Additional non-destructive and destructive examinations were performed. This non-destructive and destructive examination concluded that this leak is attributed to primary water stress corrosion cracking in the J-Groove weld. This heater location was repaired by removal of the N3 heater, sleeves, J-Groove weld, and installing an American Society of Mechanical Engineers Code approved welded plug. An additional thirteen pressurizer heater sleeve locations received additional non-destructive examinations and no additional non-conforming indications were found. All pressurizer heater penetrations received a non-destructive visual examination at normal operating pressure and temperature with no further visual signs of leakage. The scope of identified leakage and pressurizer repair was isolated to the pressurizer heater N3 location.
3182011002 | Calvert Cliffs 2 | 07/07/2011 | 02/02/2012 | ML12038A01 | <strong>Pressurizer Safety Valve Setpoint High due to Setpoint Variation</strong><br /><i>Abstract:&nbsp;</i>On July 7, 2011, a reportable condition was determined to have existed at Calvert Cliffs Nuclear Power Plant. On March 11, 2009, during scheduled testing at an offsite testing facility, the as-found lift setting for pressurizer safety valve, serial number BS03213, was measured higher than the Technical Specification allowable value. However, test results were submitted to Calvert Cliffs stating that the as-found test was successful. The valve had been installed in Unit 2 at the 2RV201 location (Unit 2 pressurizer safety valve) and was removed during the 2009 Unit 2 refueling outage for scheduled testing and maintenance. No material conditions were found that contributed to the high setpoint discovered during the test. The apparent cause is a greater than expected setpoint variation. The currently installed valves are operable. The corrective action is to increase the Technical Specification setpoint tolerance. A similar event is documented in Licensee Event Report 317/2010-002. The cause for that event was setpoint variation.
3232011001 | Diablo Canyon 2 | 03/26/2011 | 05/25/2011 | ML11152A06 | <strong>Unit 2 Reactor Trip from Loss of Main Feedwater Pump 2-1</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2011 at 1449 PDT operators at Diablo Canyon Power Plant (DCPP) Unit 2 manually initiated a reactor trip in response to loss of main feedwater pump 2-1. The main feedwater pump 2-1 tripped after non-radioactive water sprayed on its control console. The water spray was caused by leakage from the flange of the relief valve on the feedwater heater 2-1A condenser dump valve line. All rods fully inserted on the reactor trip. The reactor was cooled by the auxiliary feedwater system with the condenser in service. All systems performed as designed with no unexpected pressure or level transients. Automatic main feedwater isolation, auxiliary feedwater actuation, and steam generator blowdown isolation occurred as expected. ENS notification 46701 provided the 4-hour non-emergency event report for the manual reactor trip of DCPP Unit 2 in accordance with 10 CFR 50.72(b)(2)(iv)(B), RPS Actuation (scram). Additionally, this notification provided the 8-hour non-emergency event report of the automatic actuation of the auxiliary feedwater system as a result of the reactor trip in accordance with 10 CFR 50.72(b)(3)(iv)(A), Specified System Actuation. The cause of the event was determined to be a failed gasket for the relief valve due to bolt torquing practices. Corrective actions include revising DCPP's bolt torquing procedure to provide bolt torquing specifications for bolted connections.
3242011001 | Brunswick 2 | 07/28/2011 | 01/20/2013 | ML13032A07 | <strong>Condition Prohibited by Technical Specifications due to RWCU Instrumentation Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 28, 2011, a system data review identified that the Unit 2 Reactor Water Cleanup (RWCU) System inlet flow rate was reading approximately 18 percent lower than the system outlet flow rate. Investigation subsequently determined that the inlet flow was inaccurate because the flow orifice for the system inlet flow element, 2-G31-FE-N035, had been installed backwards during maintenance activities completed on March 20, 2011. It was concluded that the lower flow readings from the RWCU inlet flow instrumentation would result in non-conservatism and, subsequently, it has been determined that this non-conservatism resulted in the RWCU system isolation on Differential Flow-High (i.e., Technical Specifications Table 3.3.6.1-1, "Primary Containment Isolation Instrumentation," Function 5.a) being inoperable. This condition is being reported as an operation or condition prohibited by Technical Specifications. The safety consequences of this event were minimal. This event was caused by inadequate work instructions, which did not illustrate or describe flow directional characteristics of the orifice. Additionally, the individual planning the work activity did not provide the rigor commensurate with the importance of the task being planned. Corrective actions were taken to reinstall the flow orifice in the correct orientation, enhance existing plant drawings associated with RWCU flow orifices, and reinforce expectations regarding work order development with work planners.
3242011002 | Brunswick 2 | 11/16/2011 | 01/16/2012 | ML12031A16 | <strong>Unanalyzed Condition due to Reactor Pressure Vessel (RPV) Head Detensioned During Startup</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2011, Unit 2 was in power ascension following a mid-cycle maintenance outage which required reactor vessel disassembly. At 0309 Eastern Standard Time (EST), with Unit 2 operating in Mode 2 at a maximum of 7 percent of rated thermal power, a manual reactor scram was inserted due to elevated drywell leakage. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the Reactor Protection System (RPS). On November 17, 2011, at 1345 EST, it was determined that an unanalyzed condition existed on Unit 2. With Unit 2 operating in Mode 4, leak investigation activities determined that the reactor pressure vessel (RPV) head was not fully tensioned. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B), as a condition that resulted in the plant being in an unanalyzed condition that significantly degraded plant safety. The root cause of this event is the failure to provide the proper training and procedure guidance to correctly interpret critical data used to validate that the RPV head nuts were properly tightened. Corrective actions include implementing refueling procedure and training program changes to ensure that adequate training and guidance is provided to refueling floor personnel.
3252011001 | Brunswick 1 | 04/07/2011 | 06/02/2011 | ML11165A22 | <strong>Loss of Control Room Emergency Ventilation</strong><br /><i>Abstract:&nbsp;</i>On April 7, 2011, at approximately 1740 hours Eastern Daylight Time (EDT), a loss of the Control Room Emergency Ventilation (CREV) system occurred. At the time of the event, the plant was performing OMST-DG13R, "DG-3 Loading Test." During performance of this test, the 480 VAC Emergency Bus E-7 main feeder breaker tripped unexpectedly. As a result, the CREV emergency makeup damper 2-VA-2J-D-CB closed on loss of power, resulting in two CREV subsystems required by TS 3.7.3, "CREV System," being inoperable. This condition could have prevented the fulfillment of the safety function for this system. BSEP has a shared Control Room, but only Unit 1 was required to enter TS 3.7.3, Required Action C.1, for two CREV subsystems inoperable (i.e., be in Mode 3 within 12 hours). Unit 2 was operating in Mode 4 for a scheduled refueling outage and did not meet any applicability conditions for TS 3.7.3. This condition is being reported as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The safety consequences of this event were minimal. The condition existed for approximately one hour and 51 minutes, and plant staff took immediate action to return the equipment to service. The direct cause of the E-7 breaker trip was a spurious actuation of the solid state trip unit (i.e., no root cause could be determined). The corrective actions included replacement of the breaker.
3252011002 | Brunswick 1, Brunswick 2 | 10/13/2011 | 12/08/2011 | ML11355A15 | <strong>Fire Related Unanalyzed Condition That Could Impact Equipment Credited in Safe Shutdown Analysis</strong><br /><i>Abstract:&nbsp;</i>On October 13, 2011, in preparation for converting from 10 CFR 50, Appendix R, to NFPA 805, a review of the Brunswick Steam Electric Plant (BSEP) Safe Shutdown Analysis identified conditions that may not ensure a protected train of equipment remains available under certain postulated fire scenarios. The analysis determined that a postulated fire in specific fire areas could cause spurious actuation of critical components, potentially resulting in loss of equipment required for safe shutdown. A fire in one of the specified fire areas could potentially adversely affect the following: Suppression Pool level instrument 2-CAC-LT-2602, Residual Heat Removal net positive suction head (i.e., drywell containment overpressure), Reactor Core Isolation Cooling (RCIC), Emergency Bus E-1, and Emergency Bus E-3. The safety significance of this event is minimal. Fire watches were established for the affected portions of fire areas RB1-1, RB2-1, TB1, CB-2, CB-13, and CB-23. Additionally, fire detection and suppression equipment in the affected areas were fully functional. This was determined to be a historical condition and no root cause could be identified. Corrective actions include establishing an hourly fire watch in the affected fire areas, revision of alternative safe shutdown procedures, and completion of a new safe shutdown analysis.
3252011003 | Brunswick 1, Brunswick 2 | 12/01/2011 | 01/30/2012 | ML12046A83 | <strong>Loss of Control Room Air Conditioning and Emergency Ventilation</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2011, at 1344 hours Eastern Standard Time (EST), the Control Building (CB) instrument air dryer failed resulting in loss of control air. As a result, the three Control Room Air Conditioning subsystems required by Technical Specification (TS) 3.7.4, "Control Room Air Conditioning (AC) System," and the two Control Room Emergency Ventilation subsystems required by TS 3.7.3, "Control Room Emergency Ventilation (CREV) System," became inoperable. Because Brunswick has a shared control room, Unit 1 and Unit 2 entered TS 3.7.3 Required Action B.1, for two CREV subsystems inoperable (i.e., be in Mode 3 within 12 hours) and TS 3.7.4, Required Action E.1, for three Control Room (CR) AC subsystems inoperable (i.e., enter LCO 3.0.3 immediately). At 1410 hours, operability of two Control Room AC subsystems and one CREV subsystem was restored, and LCO 3.0.3 was exited, when the CB instrument air dryer was bypassed. No power reduction took place as a result of the LCO 3.0.3 entry. The failure of the CB instrument air dryer was due to low refrigerant pressure leading to ice blockage of the instrument air supply line. The cause was inadequate monitoring to detect the low refrigerant pressure. Corrective actions include replacing the instrument air dryer and a procedure revision to bypass the dryer when low refrigerant pressure conditions exist.
3272011001 | Sequoyah 1, Sequoyah 2 | 02/15/2011 | 04/15/2011 | ML11110A14 | <strong>Both Trains of Control Room Air Conditioning Systems Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2011, at 0705 Eastern Standard Time (EST), Sequoyah Nuclear Plant (SQN) Unit 1 and 2 entered Technical Specification Limiting Condition for Operation (LCO) 3.0.3 due to both trains of control room air conditioning systems inoperable. LCO 3.0.3 was entered because "B" train Main Control Room (MCR) chiller failed and "A" train MCR chiller was tagged out of service for scheduled maintenance. Actions were expedited to return both trains of MCR chillers to service. At 1005 EST on February 15, 2011, the "A" train MCR chiller was returned to operable status and LCO 3.0.3 was exited on both units. An investigation discovered that the "B" train MCR chiller failed because of a ruptured air supply line in a temperature transmitter on the chiller control circuit. The cause was determined to be an inadequate preventative maintenance procedure. The inoperability of both trains of control room air conditioning systems is reportable as a condition which was prohibited by Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(B). In addition, this condition is reportable as a condition that could have prevented the fulfillment of the safety function per 10 CFR 50.73(a)(2)(v)(D).
3272011003 | Sequoyah 1 | 06/26/2011 | 11/10/2011 | ML11318A25 | <strong>Unit 1 Reactor Trip as a Result of Turbine Control Card Failure - Supplement 1</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2011, at 1615 Daylight Saving Time (DST), Sequoyah Nuclear Plant (SQN) Unit 1received an automatic reactor trip as a result of the failure of a turbine control analog electro-hydraulic (AEH) signal conditioning card. The card failure created an indication that the main turbine had tripped (auto stop latch signal) resulting in the governor and throttle valves closing. When the throttle valves closed, an automatic reactor trip was received from the turbine trip at greater than 50 percent rated thermal power. An immediate corrective action was to replace the failed AEH signal conditioning card. The root cause of this event was determined to be a failure to eliminate and mitigate single point vulnerabilities in AEH signal conditioning printed circuit boards.
3272011004 | Sequoyah 1 | 07/20/2011 | 12/15/2011 | ML11354A24 | <strong>Reactor Trip as a Result of a Loss of Preferred Inverter - Revision 1</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2011, at approximately 2129 Daylight Saving Time (DST), Sequoyah Nuclear Plant (SQN) Unit 1 automatically tripped as a result of loss of the Unit 1 Preferred Inverter. The loss of the preferred inverter caused the turbine governor valves to close, and the load rejection caused a Power Range Neutron Flux High Negative Rate Reactor Trip signal. At the time of the reactor trip, plant personnel were installing test equipment inside the preferred inverter to monitor frequency. A ground was introduced on the preferred inverter output when the frequency check was performed, which caused the preferred inverter output to be lost. The direct cause of the event was that the acting Maintenance foreman incorrectly decided to perform missed steps in a preventative maintenance procedure. This resulted in the preferred inverter frequency check steps being performed out of sequence from the sequence in the test procedure. The root cause of this event was that Operations has not sustained written guidance for supervisory review of applicable work documents prior to returning equipment to service. Corrective actions will include establishing procedural guidance for Operations supervisory review of applicable work documents prior to returning equipment to service.
3272011005 | Sequoyah 1 | 08/18/2011 | 12/14/2011 | ML11354A24 | <strong>Reactor Trip as a Result of Reactor Coolant Pump Bus Undervoltage - Revision 1</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2011, at approximately 2250 Daylight Saving Time (DST), Sequoyah Nuclear Plant (SQN) Unit 1 automatically tripped as a result of reactor coolant pump (RCP) 1 and 3 bus undervoltage. The undervoltage condition on the two unit boards that feed RCPs 1 and 3 was caused by a slow transfer of the 1A Start Bus from normal to alternate supply. A failure of the 1A Start Bus potential transformer (PT) secondary side fuse initiated the slow transfer of the 1A Start Bus. Unit 1 was stabilized in hot standby following the automatic reactor trip. The cause of the fuse failure was determined to be mechanical separation of end plate from end cap due to inadequate manufacturing aggravated by age. The root cause was determined to be no preventative maintenance to address periodic replacement of fuses for the Start Bus protective relay circuits. The corrective actions will include creating preventative maintenance procedures to address replacing fuses in locations that are trip risk sensitive or could result in engineered safety feature actuations.
3282011001 | Sequoyah 2 | 06/22/2011 | 09/29/2011 | ML11276A14 | <strong>Nuclear Instrumentation System Power Range Neutron Flux Trip Low Range Bistable Incorrectly Calibrated - Revision 1</strong><br /><i>Abstract:&nbsp;</i>0n June 23, 2011, at 0222 day light saving time (DST) Operations personnel entered into abnormal operating procedure for a malfunction of nuclear instrumentation during operation to increase reactor power above 25 percent. It was noted by Operations personnel that the power range nuclear instrumentation system (NIS) Channel N44 "Hi Flux Low Setpoint Bistable" indicating light was dark. Actions were taken to comply with technical specification (TS) limiting condition for operation (LCO) 3.3.1, "Reactor Trip System Instrumentation," Action 2, to place the inoperable channel in tripped condition. During an investigation following the event, it was determined that during the Unit 2 refueling outage, Maintenance personnel incorrectly performed a channel calibration on the Unit 2 power range NIS Channel N44. Following the refueling outage, NIS Channel N43 was made inoperable because it was connected to the plant reactivity computer for low power physics testing. Both the NIS Channel N43 and N44 were inoperable when Unit 2 entered into Mode 2 after the refueling outage. This resulted in a condition prohibited by TSs and is reportable, specifically limiting conditions of LCOs 3.0.4a, "Applicability," 3.3.1, and 3.10.3, "Physics Tests," were not met. The root cause evaluation determined that no robust physical barriers were used to prevent the inadvertent adjustment of the power range neutron flux low range bistable set point. Actions taken to prevent recurrence include changes to procedures to require use of barriers and training for the changes.
3312011001 | Duane Arnold | 05/03/2011 | 06/30/2011 | ML11181010 | <strong>Emergency Based Suspension of Safeguards under Provisions of 10CFR50.54(x)</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2011 at 1328, while operating at 100% power, a fire occurred at the site's hydrogen station (IEEE System Code LJ). In response to the fire, the incident commander requested that security personnel evacuate a security post due to the evident safety risk posed by the fire. At 1354 it was determined that there were no adequate or equivalent compensatory measures available, and the request to suspend safeguards was granted by the Operations Shift Manager and the Technical Specification (TS) for License Condition for Physical Protection (safeguards) were deviated from pursuant of 10CFR50.54(x). The decision to suspend safeguards was necessary due to the fact that the security post area was uninhabitable due to life-threatening safety concerns since the security post structure did not provide sufficient protection from the fire. At 1820 the area was declared safe for the security post personnel and they were returned to re-establish the post. The cause of this event was the lack of adequate or equivalent compensatory measures for the security post. This event is being reported as Deviation from TS under 1 0CFR50.54(x). Additionally, this event was reported under 10CFR50.72(b)(1), Deviation from TS, reference Event Notification 46813. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3312011002 | Duane Arnold | 08/11/2011 | 10/10/2011 | ML11284015 | <strong>Loss of Ultimate Heat Sink and Completion of Technical Specification Required Shutdown</strong><br /><i>Abstract:&nbsp;</i>On August 11, 2011 at 0008, while operating at 100% power, both trains of River Water Supply (RWS) were declared inoperable due to the failure of river Intake Structure traveling screens. This required entry into Technical Specification(TS) 3.7.2, River Water Supply System and Ultimate Heat Sink, Condition B, Both RWS subsystems inoperable. ThisLimiting Condition for Operation (LCO) requires that the reactor be in Mode 3 within 12 hours and Mode 4 within 36hours. The LCO was entered because of the high indicated differential pressure on the intake traveling screens and their inability to be rotated. Subsequent inspections of the Intake Structure found several feet of sand in the forebay and pump pitareas. The required action to be in Mode 3 was completed at 1138 with the insertion of a manual scram. Upon inserting themanual scram, reactor water level dropped below 170 inches resulting in Primary Containment Isolation System (PCIS)Groups 2, 3 and 4 being received. This reactor water level response is considered normal following a reactor scram from power due to void collapse in the reactor vessel. The PCIS isolations all functioned properly. This event was caused byinadequate management of river sediment buildup.This event is being reported as an Event or Condition that Could Have Prevented Fulfillment of a Safety Function,10CFR50.73(a)(2)(v)(B and D), a Common-cause Inoperability of Independent Trains or Channels, 10CFR50.73(a)(2)(vii),and Completion of a TS Required Shutdown, 10CFR50.73(A)(2)(i)(A), reference EN 47142. Additionally, this event was reported under 10CFR50.73(A)(2)(iv)(A), Specified System Actuation, reference Event Notification 47143. There were no actual safety consequences and no effect on public health and safety as a result of this event.
3332011001 | FitzPatrick | 09/23/2010 | 11/15/2011 | ML11320040 | <strong>Reactor Core Isolation Cooling System Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 7, 2011, with the plant operating in Mode 1 at 100% power, 13MOV-131, Reactor Core Isolation Cooling (RCIC) Steam Admission Isolation Valve failed to stroke full open during surveillance test ST-24J. Trouble shooting determined the most probable cause to be loose connections in the motor control circuit, 71BMCC-3-OB1(MC). Preventive Maintenance (PM) had been performed on the motor control circuit on September 23, 2010, during Refueling Outage 19. Because the identified condition could have resulted in a failure of the RCIC system to operate properly, if needed, it is considered that the RCIC System was Inoperable from the time that RCIC was required to be Operable on October 16, 2010, until the completion of the Post Maintenance Testing on January 8, 2011. Since Limiting Condition for Operation (LCO) 3.5.3 requires RCIC to be Operable in Mode 1 and in Modes 2 and 3 with steam dome pressure greater that 150 psig, this period of Inoperability exceeded the Technical Specification allowed out of service time.
3332011002 | FitzPatrick | 01/11/2011 | 03/10/2011 | ML11069120 | <strong>Failure to Isolate the Reactor Building Results in a Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On January 11, 2011, with the "A" Refueling Floor Exhaust Radiation Monitor inoperable, the required action for Technical Specification (TS) 3.3.6.2 Condition A was not met within the required completion time of 24 hours. In addition, the required actions for TS 3.3.6.2 Condition C were also not met within the completion time of 1 hour after the action for Condition A was not completed. The failure to perform the TS required actions within the required completion times resulted in a condition prohibited by the TS which is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The apparent cause of this event is that control room personnel failed to verify that the actual plant configuration matched the configuration needed to remain compliant with the TS. Immediate corrective actions included isolating the reactor building ventilation system to restore compliance with the TS and briefing the operating crews on the error prior to assuming future watch standing duties. The briefings were conducted by operations management who also reinforced expectations regarding shift turnover and T5 compliance. Additionally, active LCOs are now visibly posted in the control room. Planned corrective actions include providing additional training and simulator scenarios on configuration control.
3332011003 | FitzPatrick | 06/08/2011 | 08/08/2011 | ML11220146 | <strong>Safety Relief Valve Setpoints Outside of Allowable Tolerances</strong><br /><i>Abstract:&nbsp;</i>Review of the as-found test results for eleven Safety / Relief Valve (S/RV) pilot assemblies removed and replaced during the September 2010 Refueling Outage, determined that five S/RVs were outside the allowable as-found tolerance of 1145 psig +/- 3% (+/- 34.3 psig) required by Technical Specification (TS) Surveillance Requirement (SR) 3.4.3.1. Also, two of the eleven S/RVs tested were found to have excessive seat leakage to the point where as-found testing could not be performed. The effect of these S/RVs being out of tolerance was analyzed and the results of this analysis show that nuclear plant safety was not adversely affected due to the availability of the Electric Lift System. Consequently, the safety significance of this event was minimal. The Root Cause for the failure of the S/RVs was determined to be corrosion bonding between the S/RV pilot disc and seat, a recognized industry generic problem with 2-stage Target Rock relief valves.
3342011001 | Beaver Valley 1 | 11/02/2011 | 12/20/2011 | ML11362A35 | <strong>Use of Liquid Tight Flexible Conduits Installed in Fire Barrier Penetrations Results in Unanalyzed Configurations</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2011, the Beaver Valley Power Station NFPA 805 transition team personnel identified that samples taken from the outer coating from certain liquid tight flexible conduits installed through fire barrier penetrations did not exhibit expected flame resistant characteristics and were not in conformance with documented previously tested fire barrier configurations at Beaver Valley Power Station Unit 1 (BVPS-1). The liquid tight flexible conduits installed through fire barrier penetrations are non-conforming with the provisions of NRC Branch Technical Position (BTP) APCSB 9.5-1. The BVPS-1 plant areas that require fire barriers for train separation for safe shutdown equipment are potentially affected, except for the reactor containment and the river water main intake structure. The concern is whether the liquid tight coating could ignite and spread the fire to the opposite side of the barrier. The apparent cause of this latent issue is inadequate review of the accumulative effects from all field changes. Specifically, subsequent installation of otherwise qualified fire seals did not consider potential compromise by the jacket material of the previously installed liquid tight flexible conduit acting as a penetrant. Following identification of this issue, compensatory actions were promptly implemented to provide an adequate level of protection for redundant equipment. These include a twice per twelve hour shift fire watch patrol in the affected plant areas, and the restrictions for performing hot work in the vicinity of the affected penetrations. In addition, transient combustible materials are prohibited in affected plant areas from being stored adjacent to electrical penetrations fire seals or adjacent to conduit within five feet of an electrical penetration fire seal as a compensatory action. A fire has not occurred in the affected fire areas that has challenged these penetrations. The overall safety significance due to the impact of these potentially non-compliant flexible conduits being used in penetration fire barriers is considered to be low to moderate, based on the summation of all the analyzed individual fire compartment delta Core Damage Frequencies for the affected areas. Degraded fire barriers, such that the required degree of separation for redundant safe shutdown trains is lacking, is reportable as an unanalyzed condition that significantly degraded plant safety. Therefore, this report is being submitted pursuant to 10 CFR 50.73(a)(2)(ii)(B).
3342011002 | Beaver Valley 1 | 12/13/2010 | 03/16/2012 | ML12081A11 | <strong>Failure to Comply with Technical Specifications 3.7.5 due to the Inoperability of Two or More Trains of the Auxiliary Feedwater System</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2011, plant personnel identified that a maintenance activity performed on December 13, 2010, may have resulted in non-compliance with the Required Actions of Technical Specification (TS) 3.7.5. Specifically, on December 13, 2010, the Beaver Valley Power Station Unit Number 1 (BVPS-1) "A" Train Motor Driven Auxiliary Feedwater (AFW) system pump (1FW-P-3A) was removed from service and declared inoperable at 0339 hours to perform maintenance. TS 3.7.5 Condition B for one AFW Train being inoperable was entered due to removal of 1FW-P-3A pump from service. The turbine driven AFW pump (1FW-P-2) remained aligned to the "A" train supply header as required by TS 3.7.5 Required Action B.1. This Required Action applies when both AFW supply headers are Operable. With the 1FW-P-3A pump inoperable and the 1FW-P-2 pump aligned to the "A" supply header, the automatic open signal timing circuit for the Train "A" AFW flow throttle valves was de-energized as part of a clearance to perform a calibration on relay 62-AFPA at 0950 hours on December 13, 2010, and was not re-energized until 1642 hours on December 13, 2010. Although the Train "A" AFW flow throttle valves were in the open position, this action resulted in the inability to meet TS Surveillance Requirement 3.7.5.3 and, therefore, resulted in Train "A" AFW flow throttle valves being inoperable. TS 3.7.5 Condition D for two AFW trains being inoperable was not applied when the automatic open signal timing circuit for the Train "A" flow throttle valves was de-energized. As a result, the required action of TS 3.7.5 Condition D to place the plant in Mode 3 within the following six hours was not met. This event is reportable per 10 CFR 50.73(a)(2)(i)(B) (Operations or Condition prohibited by TS) due to two trains of AFW being inoperable for greater than six hours while the BVPS-1 was operating in Mode 1. The Apparent Cause of this event was the lack of knowledge/correct interpretation of the auto-open feature and its impact on operability by the on-shift crew tasked with approving and issuing the clearance for posting. The safety significance of the event was very low. This supplement is being issued due to four additional events that have been identified as violations of TS 3.7.5 as a result of the extent of condition investigation from the original event. The safety significance of each of these four events was very low.
3352011001 | St. Lucie 1 | 08/22/2011 | 10/20/2011 | ML11301A07 | <strong>Unit 1 Manual Reactor Trip due to High Condenser Backpressure Caused by Severe Influx of Jellyfish into the Intake Structure</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2011, St. Lucie Unit 1 was operating in Mode 1 at 89% when it was manually tripped due to rising condenser back pressure. All control element assemblies (CEAs) fully inserted into the core. The cause of the rising back pressure was an influx of jelly fish into the intake structure degrading Unit 1 circulating water system performance. Decay heat removal was initially from the main feedwater and steam bypass to the main condenser. However, subsequent to the manual trip, the 1B main feedwater pump was manually secured due to a leak on the pump casing. The 1A main feedwater pump subsequently tripped due to low suction pressure after manually securing the 1B condensate pump and decay heat removal was transitioned to the atmospheric dump valves and auxiliary feedwater. Root cause evaluation determined the jellyfish intrusion rate exceeded the current capacity of the traveling water screens and trash pits. In addition, procedural guidance did not anticipate the possible rapidly escalating jellyfish intrusion rate and the urgency for response regarding the negative effect of the rapid jelly intrusion on condenser back pressure was not recognized. Contributing causes included: plant maneuvering did not account for condenser back pressure margin, equipment degradation and malfunctions, and design deficiencies. Corrective actions include procedure revisions and design changes to address procedure deficiencies and correct design deficiencies.
3352011002 | St. Lucie 1 | 10/19/2011 | 12/17/2011 | ML12003A23 | <strong>Unit 1 Manual Reactor Trip due to High Condenser Backpressure</strong><br /><i>Abstract:&nbsp;</i>On October 19, 2011, St. Lucie Unit 1 was operating in Mode 1 at 86% when the unit was manually tripped due to rising condenser backpressure. The cause of the rising backpressure was an unplanned trip of the 1A1 circulating water (CW) pump. Condenser backpressure reached procedural limits which required a manual unit trip. The 1A1 CW pump breaker tripped as a result of an internal motor fault. Unit 1 was in a planned power reduction at the end of the cycle. All control element assemblies (CEAs) fully inserted and decay heat removal was achieved through main feedwater and steam bypass to the main condenser. A root cause evaluation (RCE) concluded that ineffective condition monitoring of the 1A1 CW pump motor for degraded air flow passages prior to scheduled motor overhauls, resulted in a buildup of salt and corrosion products in the rotor cooling air flow passages, restricting air flow. Contributing causes included previous actions to implement quarterly resistance temperature detector measurements for the CW pump motors were ineffective. Corrective actions will implement temperature monitoring using the CW pump motor winding resistance temperature detectors (RTDs) .
3352011003 | St. Lucie 1 | 11/03/2011 | 03/06/2012 | ML12081A28 | <strong>Long-Term Post-LOCA Hot Leg Injection Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2011, with St. Lucie Unit 1 in Mode 1 at 85% power, the Onsite Review Group determined that past operation with unproceduralized manual actions to mitigate postulated single failures in the hot leg injection (HLI) flow path constituted a reportable condition. St. Lucie failed to recognize that the historical condition was reportable due to weaknesses in corrective action program (CAP) implementation and legacy issues with operability/functionality determinations. Programmatic CAP improvements have been implemented to ensure condition reports are appropriately screened and dispositioned, and the operability/functionality determination program requirements have been updated. The legacy design issue is being handled in the interim via proceduralized manual actions that are being tracked as an open operable but degraded condition via the station RIS 2005-20 list until an appropriate long-term solution is implemented. This LER supplement concludes that there were no adverse effects of postulated HLI flow on the integrity of the regenerative heat exchanger.
3362011001 | Millstone 2 | 04/03/2011 | 05/24/2011 | ML11154A09 | <strong>Enclosure Building Rendered Inoperable due to Dislodged Bushings</strong><br /><i>Abstract:&nbsp;</i>On April 3, 2011, with Millstone Power Station Unit 2 (MPS2) in a refueling outage at 0% power in Mode 5, data taken during plant shutdown indicated that the Enclosure Building Filtration System had not met acceptance criteria rendering the Enclosure Building inoperable while MPS2 was in Mode 4. Plant Technical Specification (TS) 3.6.5.2 requires that the Enclosure Building shall be operable in Modes 1, 2, 3, and 4. The TS 3.6.5.2 Action requirements were met. Since the Enclosure Building did not meet the acceptance criteria, the safety function of the Enclosure Building to limit radiological releases in the event of a design basis accident could not be assured. The direct cause for not meeting the Enclosure Building acceptance criteria was that sliding bushings on the main steam safety valves (MSSVs) exhaust piping had dislodged and not reseated. The apparent cause of this event was determined to be a design/application deficiency in the use of MSSV exhaust piping sliding bushings as an Enclosure Building boundary. A design change was implemented that no longer relies on the MSSV sliding bushings as Enclosure Building boundaries. Instead, improved boot seals located on the MSSV exhaust piping form the boundary for the MSSVs. This condition is being reported pursuant to 10CFR50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material.
3362011002 | Millstone 2 | 06/20/2011 | 08/18/2011 | ML11242A01 | <strong>Reactor Trip on Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>At 1152 on June 20, 2011, with Millstone Power Station Unit 2 operating at 59 percent power in Mode 1, the reactor tripped automatically on low steam generator water level. The decreasing water level condition was due to a low suction pressure trip on the "B" steam generator feed pump (SGFP) that occurred while placing the "A" SGFP in service. The event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in a manual or automatic actuation of any of the systems listed in 50.73(a)(2)(iv) (B). The actuation of the Auxiliary Feedwater Actuation System also is a reportable condition under the same paragraph. The cause of the event was gaps in the application of operator fundamentals and some procedure quality issues associated with operations procedure OP 2204, Load Changes. Procedure OP 2204 has been revised to ensure the second steam generator feedwater pump is placed in service at a lower power level. Additional corrective actions to address the underlying causes of the gaps in the application of operator fundamentals are being addressed in accordance with the station's corrective action program.
3362011003 | Millstone 2 | 09/03/2011 | 10/26/2011 | ML11307A37 | <strong>Completion of a Plant Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 09:31 on September 3, 2011, with Millstone Power Station Unit 2 operating at 100 percent power in Mode 1, the "A" train service water loop was declared inoperable when leakage from a degraded service water spool piece degraded beyond pre-established limits. Plant Technical Specification 3.7.4.1 stipulates with one service water loop inoperable, restore the inoperable loop to operable status within 72 hours or be in cold shutdown (Mode 5) within the next 36 hours. Since the leak was unisolable, operators commenced a plant shutdown. Cold Shutdown Mode 5 was entered at 17:03 on September 4, 2011. The direct cause of the service water leak was a degraded coating on the piping flange located in the "A" train 10-inch service water line to the emergency diesel generator heat exchangers. The degradation mechanism of the flange is attributed to galvanic corrosion of the carbon steel material. Carbon steel is anodic to the adjacent alloy surfaces. The pipe spool flange was replaced. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) as completion of a nuclear plant shutdown required by the plant's Technical Specifications.
3362011004 | Millstone 2 | 09/14/2011 | 11/07/2011 | ML11319A14 | <strong>Reactor Trip Circuit Breaker Testing Not in Compliance With Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On, September 14, 2011, with Millstone Power Station Unit 2 (MPS2) in Mode 1, at 100 % power, a historical condition was discovered where the surveillance procedure used to test the reactor trip circuit breakers (TCBs) specified the TCBs be closed (i.e., applying power to the control rod drive motors thus enabling the control element assemblies (CEAs) to be capable of being withdrawn) prior to demonstrating the TCBs to be OPERABLE. This is contrary to the requirements of Technical Specification (TS) 4.0.4 which prohibits entry into an operational mode or other specified condition unless the surveillance requirement(s) have been performed within the stated interval. This condition is being reported pursuant to 10 CFR 73(a)(2)(i)(B) as an operation or condition prohibited by TS. The cause was determined to be an inadequate procedure review. During the implementation process for a 2003 TS change, when the surveillance procedure was revised, it was not recognized that the surveillance procedure test method for the TCBs allowed MPS2 to enter a mode or condition prior to demonstrating the TCBs to be operable as required by TS 4.0.4. The surveillance procedure is being revised to specify an alternate method for testing the TCBs that does not result in rendering the CEA drive system capable of CEA withdrawal prior to closing the TCBs for performance of Matrix Logic and Trip Path testing.
3362011005 | Millstone 2 | 12/03/2011 | 01/30/2012 | ML12039A10 | <strong>Enclosure Building Rendered Inoperable due to Degraded Door Seal</strong><br /><i>Abstract:&nbsp;</i>At 1230 on December 3, 2011, with Millstone Power Station Unit 2 operating at 100 percent power in Mode 1, the control room was notified that a door sweep became dislodged on a door credited as a boundary door for the Enclosure Building. Operators declared the door inoperable and entered the Action for plant Technical Specification (TS) 3.6.5.2 Enclosure Building at 1235. TS 3.6.5.2 Action requires that the Enclosure Building be restored to operable status with 24 hours or be in Cold Shutdown within the next 36 hours. Repairs to the door were completed and operators exited the Action at 1524 on December 3, 2011. The last known time where the door sweep was not dislodged was within 18 hours of the time of discovery. The operability of the Enclosure Building ensures that the release of radioactive materials from the primary containment atmosphere will be restricted to those leakage paths and associated leak rates assumed in the accident analyses. Since there is no bounding analysis on the impact of this size opening on the ability to complete the safety function, this condition is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to control the release of radioactive material. The direct cause of the door seal failure was that the mounting hardware (screws) loosened and fell out. The apparent cause is the door was not being properly maintained. The door was repaired. Doors that are part of the Enclosure Building boundary have been added to the preventive maintenance program.
3382011001 | North Anna 1 | 02/03/2011 | 04/01/2011 | ML11102030 | <strong>Annunciator Card Failure Due To Carbon Resistor Degradation</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2011, at 0345 hours, with Unit 1 at 100 percent power, Mode 1, annunciator 1 H-G4, Annunciator System DC Ground was received in the Main Control Room (MCR). At 0348 hours annunciator 1B-D3, Boric Acid Tank 1B Hi-Lo Level CH I-II was received which, when acknowledged, locked in and annunciator 1 H-G4 cleared. While investigating, an acrid smell was noticeable in the MCR. At 0353, upon entry into the annunciator system cabinet room, adjacent to the MCR, the door of the cabinet, 1-EI-CB-21, was opened and flames approximately 2 - 4 inches long were observed coming from an annunciator circuit card. Operations personnel entered fire contingency action procedure 0-FCA-0, Fire Protection - Operations Response. At 0354 hours, a two second discharge of a portable CO2 fire extinguisher put out the fire and a re-flash fire watch was established. At 0437 hours the fire contingency action procedure was exited. This event posed no significant safety implications since the fire was small, extinguished quickly, did not pose an actual threat to the safety of the nuclear power plant and it did not affect equipment required for safe operation of the plant. Therefore, the health and safety of the public were not affected by this event. This event is being reported voluntarily to share information and lessons learned.
3382011002 | North Anna 1, North Anna 2 | 06/29/2011 | 08/27/2011 | ML11249A05 | <strong>Condition Prohibited by Technical Specifications When a Non-Seismic System was Aligned to a Seismic System</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2011, with both Units 1 and 2 operating 100 percent power, Mode 1, a condition prohibited by Technical Specifications was identified. North Anna Power Station has had a long standing practice of aligning the non-seismic Refueling Purification (RP) system to the seismic Refueling Water Storage Tank (RWST) for purification purposes prior to refueling outages while in Modes 1-4. This has been done without entering the one-hour completion time of Technical Specification 3.5.4 Condition B. In 1996 this practice was questioned by the NRC and it was determined that a weakness existed in that administrative controls were not in place to promptly isolate the RP system from the RWST following a seismic event. As a result administrative controls to isolate the RP system from the RWST were added to operating procedures and the Updated Final Safety Analysis Report (UFSAR) was updated to discuss this mode of operation. Recent Operating Experience (OE) determined that aligning the RP system to the RWST when the RWST is required to be operable per Technical Specification is not allowed. Therefore, this is a condition prohibited by Technical Specifications and reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). This event had no significant safety consequence since a seismic event had not occurred while the RP system was in service on the RWST.
3382011003 | North Anna 1, North Anna 2 | 08/23/2011 | 10/20/2011 | ML11299A01 | <strong>Dual Unit Reactor Trip and ESF Actuations During Seismic Event with a Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2011, at 1351 hours, with both units in Mode 1 at 100% power, a magnitude 5.8 earthquake occurred approximately 11 miles WSW of North Anna Power Station. The earthquake caused an automatic reactor trip of both Units, and a loss of offsite power. At 1403 hours, an Alert was declared based on Shift Manager judgment, due to significant seismic activity onsite with the loss of offsite power. All Engineered Safety Feature equipment responded as designed with the exception of the Unit 1 turbine driven auxiliary feedwater pump, which was undergoing surveillance testing when the earthquake occurred. All 4 Emergency Diesel Generators (EDG) started as designed but the 2H EDG was manually tripped 49 minutes later due to a coolant system leak. The alternate AC diesel generator was subsequently aligned to re-energize the 2H emergency bus. Offsite power was fully restored at 2258 hours on August 23. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in system actuations. On August 26, 2011, at 1623, a non-emergency 8-hour report was made to the NRC Operations Center, in accordance with 10CFR50.72(b)(3)(ii)(B) due to the seismic activity potentially exceeding design basis levels. It was later determined that the seismic activity did exceed design levels at some frequencies. The event posed no significant safety implications and the health and safety of the public were not affected by the event.
3392011001 | North Anna 2 | 09/28/2011 | 11/23/2011 | ML11340A03 | <strong>Inoperable Emergency Diesel Generator due to Coolant Leak</strong><br /><i>Abstract:&nbsp;</i>On August 23, 2011, at 1440 hours with Units 1 and 2 offline, as a result of the Central Virginia earthquake, the Unit 2 "H" (2H) emergency diesel generator (EDG) was manually tripped due to a coolant system leak forty-nine minutes after its demand start due to a loss of offsite power. A Root Cause Evaluation determined the 2H EDG could have developed a coolant leak during its next operation (i.e., post maintenance or periodic testing or a demand start). On September 28, 2011 a completed prior operability evaluation determined the 2H EDG gasket failure resulted in fault exposure unavailable hours totaling 337.6 hours. During the fault exposure unavailable hours, approximately fourteen days, the limiting action of TS 3.8.1.b was entered three times. Had a demand start of the 2H EDG occurred during any of these times the gasket failure could have occurred resulting in more than one inoperable EDG. This event is reportable pursuant to 10 CFR 50.73(a)(2)(v)(A), 50.73(a)(2)(v)(B), and 50.73(a)(2)(v)(D) for a condition that could have prevented fulfillment of the safety function of a system required to maintain the reactor in a safe shutdown condition, remove residual heat, and mitigate the consequences of an accident. The event posed no significant safety implications and the health and safety of the public were not affected by the event.
3412011001 | Fermi 2 | 09/06/2011 | 11/01/2011 | ML11306056 | <strong>High Pressure Coolant Injection System Inoperable due to Inoperable Minimum Flow Valve</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2011, at approximately 0104 EST during surveillance testing of the High Pressure Coolant Injection (HPCI) system, control room position indication was lost on the HPCI minimum flow valve as the valve was stroking closed following shutdown of HPCI. The minimum flow valve main power fuses were checked, found blown, and replaced. During a subsequent stroking of the valve, control room position indication was lost and main power fuses found blown when the open pushbutton was depressed. The valve was locally verified closed to comply with the Technical Specification Action of Limiting Condition for Operation (LCO) 3.6.1.3 to isolate the penetration. A 14-day LCO was entered per Technical Specification Action 3.5.1. System troubleshooting, diagnostic testing, and analysis were performed. The minimum flow valve motor series winding was determined to have developed turn-to-turn shorts causing the fuses to blow. The HPCI minimum flow valve motor, valve torque switch, thermal overloads, and Motor Control Center (MCC) main and auxiliary contactors were replaced. Circuit leads were inspected and tightened, and power fuse tightness was verified during fuse replacement. Post maintenance testing was successfully completed and, the HPCI system was returned to service on September 10, 2011 at 2300 EST. The safety consequences of this event were determined to be low.
3462011001 | Davis-Besse | 08/06/2010 | 03/15/2011 | ML11076001 | <strong>Pressurizer Code Safety Valve Setpoint Test Failures</strong><br /><i>Abstract:&nbsp;</i>The two pressurizer safety valves (PSVs) at the Davis-Besse Nuclear Power Station (DBNPS) were replaced during an outage in Spring, 2010 with tested spares. The removed PSVs were sent to an offsite vendor for testing and refurbishment. In December, 2010 the test results were received showing both PSVs lifted higher than the allowed one percent tolerance above the 2500 psig set point (2525 psig) for As-Found testing. Because both valves had As-Found setpoints above the Technical Specifications (TS) allowed value, a past operability evaluation was performed, which concluded on January 12, 2011, that both valves were inoperable during their time in service. Based on the as-found lift setting pressures (2531 psig and 2535 psig), there was no adverse effect on transients described in the Updated Safety Analysis Report (USAR) that can produce a Reactor Coolant System (RCS) overpressurization. The cause of this event, which was due to setpoint drift, is the small allowable setpoint range. Procedures will be revised to establish an as-left setpoint as low in the band as possible, and the feasibility of increasing the TS limit from 2525 to 2575 psig will be evaluated. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation in a condition prohibited by the TS.
3462011002 | Davis-Besse | 11/30/2010 | 03/23/2011 | ML11087096 | <strong>Containment Air Cooler Isolation Valve Disabled due to Drawing Omission</strong><br /><i>Abstract:&nbsp;</i>On January 22, 2011, with the Davis-Besse Nuclear Power Station in Mode 1 at approximately 100 percent power, routine testing discovered the outlet temperature control valve for Containment Air Cooler (CAC) 3 could not be closed from the control room. This containment isolation valve had been inadvertently rendered inoperable on November 30, 2010, while electrically isolating the CAC 3 fan motor that had tripped its supply breaker on overload when the motor was started on October 24, 2010. The root cause of this event was determined to be a lack of information on the elementary wiring diagram used to prepare the clearance for isolating the fan motor. This drawing did not reference an additional drawing showing that the fan motor breaker contacts impact the power supply to the temperature control valve controls. When a clearance for the fan motor was revised, this lack of information led to the electrical isolation of the valve control circuitry, failing the valve in the open position. Corrective actions include revision of these drawings. This issue is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation prohibited by the Technical Specifications for the inoperable containment isolation valve. Because an additional failure would be required for a potential containment bypass pathway to exist, this event had very low safety significance.
3462011003 | Davis-Besse | 03/03/2011 | 05/02/2011 | ML11124A13 | <strong>Radio Usage Renders Emergency Feedwater Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 3, 2011, with the Davis-Besse Nuclear Power Station (DBNPS) operating at approximately 100 percent power, fire detector testing was being conducted at the Auxiliary Shutdown Panel (C3630). When a radio used by Instrumentation and Control personnel for communications was keyed twice while instrumentation cabinet doors were open, momentary reductions in the control signals to the Auxiliary Feedwater Pump and Motor Driven Feedwater Pump discharge valves occurred. These momentary signal reductions resulted in the rendering of all three trains of Emergency Feedwater inoperable for approximately two minutes. The cause of this event was a station decision made in 1991 to remove the specific requirement to exclude radio usage in the vicinity of the Auxiliary Shutdown Panel. A sign restricting radio usage in the Auxiliary Shutdown Panel Room was installed shortly after this event occurred, and procedures will be revised to prohibit the use of portable radios within six feet of cabinets in the room when the cabinet doors are open. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(A) and (B) as a loss of safety function.
3462011004 | Davis-Besse | 07/26/2011 | 03/06/2012 | ML12072A03 | <strong>Direct Current System Design Issues</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2011, with the Davis-Besse Nuclear Power Station in Mode 1 at approximately 100 percent power, information was received from the NRC regarding design issues with the Direct Current (DC) System. The first issue was that non-essential equipment in containment, powered by the DC System, was not environmentally qualified as required. This could challenge the adequacy of electrical separation between potentially grounded equipment and the safety related batteries. The second was that automatic transfer switches supplying power to non-essential instrumentation could transfer a fault to the redundant power source, potentially impacting both safety related DC power sources. The breakers for the four Reactor Coolant Pump backup oil lift pump motors and for the emergency power supply to the Containment Lighting Panel were opened, and one train of instrumentation power was placed on its alternate power source from the Alternating Current system. Modifications have been implemented to provide the alternate power supply from a regulated instrumentation distribution panel to restore compliance with NRC Bulletin 79-27 for the automatic transfer switch loads while maintaining separation of the DC power system trains. The cause of these issues was inadequate design during initial plant design and during installation of the automatic transfer switches in the 1980s.
3522011001 | Limerick 1 | 05/09/2011 | 07/07/2011 | ML11188015 | <strong>1B Reactor Enclosure Recirculation System Charcoal Sample Analysis Results Exceeded TS Limit</strong><br /><i>Abstract:&nbsp;</i>The 1B Reactor Enclosure Recirculation System Subsystem was inoperable for a period that exceeded the Technical Specification allowed outage time. This occurred due to the time from removal of the charcoal sample to the time the unsatisfactory results of the vendor analysis were obtained exceeding the 7-day Technical Specification allowed outage time for one subsystem being inoperable. The sample analysis was completed within 31 days after removal as specified by the surveillance requirement. The affected charcoal bed was replaced and the subsystem was returned to operable status within 5 days of receiving the unsatisfactory sample results.
3522011002 | Limerick 1 | 06/03/2011 | 08/02/2011 | ML11214025 | <strong>Automatic Actuation of the Reactor Protection System due to A Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>An automatic actuation of the reactor protection system occurred due to a main turbine trip. The main turbine tripped due to an actuation of the reactor vessel high level trip logic during surveillance testing. The high level trip actuation was due to use of an incompatible volt-ohm meter to verify the state of the opposite high level trip logic channels prior to introducing trip signals during the test. The root cause of the event was the reactor vessel high level trip calibration and functional surveillance test revisions did not fully assess the impacts of the test equipment on the direct current turbine trip circuit. The procedure for the control of portable measurement and test equipment program will be revised to include a requirement to evaluate changes to the type of test equipment used and test methodology. The reactor vessel high level trip calibration and functional surveillance tests will be revised to incorporate test equipment that is compatible with the digital feedwater level control system.
3522011003 | Limerick 1 | 06/22/2011 | 08/22/2011 | ML11234087 | <strong>High Pressure Coolant Injection System Turbine Control Valve Failed to Fully Close During Testing</strong><br /><i>Abstract:&nbsp;</i>The high pressure coolant injection system turbine control valve failed to fully close as expected when the system was secured following surveillance testing. A subsequent inspection identified that the No.1 control valve sub-assembly was degraded to the degree that the system safety function could not be assured. The cause of the turbine control valve failure to fully close was binding between the pilot venturi valve and the venturi valve guide. The failure of the lifting beam to venturi valve stem antirotation pin initiated accelerated wear of the valve assembly parts, which led to intermittent binding of the parts during turbine operation and ultimately fatigue failure of the pilot venturi valve stem. The Unit 1 turbine control valve No. 1 valve sub-assembly was reworked to replace all damaged parts. The procedure that directs periodic inspection of the turbine control valve assembly will be revised to require non-intrusive inspection of No.1 control valve assembly each refueling outage and to require disassembly of the turbine control valve assembly for detailed inspection of all valve sub-assemblies and replacement of any worn or suspect parts at each turbine major inspection.
3532011001 | Limerick 2 | 01/26/2011 | 03/25/2011 | ML11084021 | <strong>Condition Prohibited by Technical Specifications due to Inoperable Remote Shutdown Panel Instrument</strong><br /><i>Abstract:&nbsp;</i>During restart from a refueling outage the 2A Residual Heat Removal Heat Exchanger Bypass motor operated valve position indication on the remote shutdown panel was inoperable due to excessive transmitter instrument drift which had not been identified by Operations personnel. This resulted in an unidentified condition prohibited by Technical Specifications when OPCON 2 (STARTUP) was entered. The inoperable instrument was later identified during the routine 24-month instrument calibration surveillance test when the degraded transmitter could not be calibrated due to a failed diode. The root cause of the event was less than adequate administrative barriers were present to ensure the senior licensed operator properly assessed the remote shutdown panel Technical Specification impact of the deficiency. A daily channel check was added to the Operations daily surveillance tests for the main control room instruments that share instrument loops with remote shutdown panel instruments.
3532011002 | Limerick 2 | 02/25/2011 | 04/22/2011 | ML11112005 | <strong>Manual Actuation of the Reactor Protection System Due To Stator Cooling Water High Temperature Actuation</strong><br /><i>Abstract:&nbsp;</i>A manual actuation of the reactor protection system was initiated following an automatic trip of both reactor recirculation pumps. The pumps tripped due to a main generator stator cooling water high temperature actuation which also resulted in an automatic main turbine electro-hydraulic control load set runback. The root cause of the event was a failure to properly control a degraded stator cooling water temperature control valve that required manual operator action in lieu of an automatic control function. The automatic temperature control valve was repaired. The "Adverse Condition Monitoring and Contingency Planning" and "Operational and Technical Decision Making Process " procedures will be revised regarding actions required to substitute a manual operator action for an automatic control function.
3532011003 | Limerick 2 | 05/23/2011 | 06/22/2012 | ML12174A33 | <strong>Condition Prohibited By Technical Specifications due to Inoperable Reactor Core Isolation Cooling System</strong><br /><i>Abstract:&nbsp;</i>The reactor core isolation cooling system was rendered inoperable due to valve seat leakage on two feedwater long path flush motor operated valves. The valves failed to fully close when long path flushing was secured during a refueling outage. This was later detected during an investigation for a loss in main generator electrical output. The valve indicating lights indicated the valves were full closed. The cause of the event was degradation and design of the long-path recirculation valves. The corrective actions planned are valve in-body maintenance, diagnostic testing, a preventive maintenance scope revision, and long-path recirculation operating procedure revision. The valves were restored to the full closed position which restored the reactor core isolation cooling system and the primary containment isolation valve to operable. Main generator output increased to normal.
3532011004 | Limerick 2 | 05/29/2011 | 07/27/2011 | ML11208202 | <strong>Automatic Actuation of the Reactor Protection System due to Actuation of Turbine Control Valve Closure Logic</strong><br /><i>Abstract:&nbsp;</i>An automatic actuation of the Unit 2 reactor protection system occurred due to an actuation of the turbine control valve fast closure logic. The actuation occurred during restoration from maintenance on a main turbine control valve. The "A1" channel of turbine control valve fast closure logic was placed in the trip condition during the maintenance. The "B1" channel tripped when the electrohydraulic control relayed emergency trip supply oil supply was restored to the control valve. The root cause of the event was a void in the electrohydraulic control relayed emergency trip supply oil supply line that resulted in a perturbation of the oil supply pressure at the adjacent control valve. A procedure will be developed and implemented to provide specific restoration steps for turbine control, stop, and combined intermediate valves.
3532011005 | Limerick 2 | 05/30/2011 | 07/27/2011 | ML11208203 | <strong>Manual Actuation of the Reactor Protection System due to Both Recirculation Pumps Trip</strong><br /><i>Abstract:&nbsp;</i>A manual actuation of the reactor protection system was performed following trips of both reactor recirculation pumps. The pumps tripped due to a failure of a main turbine first stage pressure trip unit. The cause of the event was a loose wiper terminal on a trip unit potentiometer. The degraded trip unit was replaced and a preventive maintenance activity will be implemented for replacement of similar trip units.
3542011001 | Hope Creek | 07/28/2011 | 09/22/2011 | ML11277A01 | <strong>HPCI Operation Credit in UFSAR Scenario Not Supported by Existing Documentation</strong><br /><i>Abstract:&nbsp;</i>Hope Creek Engineering identified a condition in which the high pressure coolant injection (HPCI) system potentially could be prevented from fulfilling its safety function. The HPCI room ventilation delta-temperature trip of 70 degrees F, which is to isolate HPCI in the event of a steam leak, has the potential to isolate HPCI prematurely in extreme winter conditions. This could impact the ability of HPCI to fulfill its design function during the accident scenario listed in UFSAR Table 6.3-6 where one of the assumed single failures listed is the loss of an emergency diesel generator (EDG) coincident with a loss of coolant accident (LOCA) and a loss of offsite power (LOP). An engineering assessment determined that HPCI is not challenged by maximum room differential temperatures under warmer ambient operating conditions. However, the ability of HPCI to perform its design function during the above accident scenario under extreme winter conditions (i.e., resulting in max room inlet to outlet delta temperatures) was not fully evaluated. As a result of the assessment on July 28, 2011 this issue was entered into the corrective action program. This condition is reportable under 10CFR50.73 (a) (2) (v) (D) as an event or condition that could have prevented the fulfillment of the safety function of a SSC that is needed to mitigate the consequences of an accident.
3612011001 | San Onofre 2, San Onofre 3 | 01/14/2011 | 03/15/2011 | ML11075019 | <strong>Non-Class 1E 6.9 kV Electrical System Shared Between Units Affects Safety Analysis Report</strong><br /><i>Abstract:&nbsp;</i>On January 14, 2011, SCE identified the electrical alignment of the non-Class 1E 6.9 kV electrical system at SONGS was shared between Units 2 and 3 during two recent refueling outages without an adequate evaluation that considered the impact on the UFSAR Chapter 15 safety analyses. This alignment was considered during the original design of the plant and is allowed in accordance with UFSAR Section 8.3.1 "AC Power Systems" and station operating procedures, but did not consider General Design Criterion 5. The 6.9 kV busses supply the Reactor Coolant Pumps (RCPs) and automatically transfer to off-site power on a loss of main generator output. In October, 2010, with both units in Mode 1, the Unit 2 off-site 6.9 kV source was redirected to Unit 3 for maintenance on the Unit 3 transformer. If Unit 2 had tripped, the RCPs would have lost power, resulting in a natural circulation cooldown; Unit 3 would not have been affected. A similar alignment was established in 2009 during the Unit 2 outage. The alignment had a potential to more than minimally increase the probability of the Loss of Forced Flow event and increase the consequences of other UFSAR Chapter 15 events. Corrective action was to restrict use of the cross connection to a shutdown unit to maintain power to the operating unit RCPs. During the brief period the 6.9 kV system was shared the RCPs remained operable and the significance of the event was determined to be minimal.
3612011002 | San Onofre 2, San Onofre 3 | 09/08/2011 | 11/01/2011 | ML11306023 | <strong>Dual Unit Automatic Reactor Trip on High Pressurizer Pressure due to Grid Disturbance</strong><br /><i>Abstract:&nbsp;</i>On 09/08/2011 at 1538 PDT, San Onofre Nuclear Generating Station (SONGS) Units 2 and 3 were in Mode 1 operating at 100 percent power, when actuation of the Reactor Protection System occurred resulting in automatic reactor trips of both units. This event was caused by the loss of a 500 kV transmission line from Arizona to San Diego Gas and Electric (SDG&E) resulting in a cascading grid disturbance, automatic separation of the SDG&E and Southern California Edison (SCE) electrical systems, and collapse of the SDG&E grid voltage. The partial loss of external load caused increasing turbine speed, governor valve fast closure, a momentary reduction of heat removal from the reactor coolant system, and increasing pressure. Both reactors tripped on high pressurizer pressure followed by a turbine trip. All control rods inserted to shut down the reactors. Offsite power remained available from the SCE grid and emergency diesel generators were not required. Safety systems responded as designed. Both units were placed in a stable condition in Mode 3. Loss of qualified offsite circuits required entry into Condition A of Technical Specification Limiting Condition for Operation (LCO) 3.8.1, with Required Action to verify remaining offsite circuits within one hour. This verification was performed approximately 1.5 hours late, which is a condition prohibited by TS.
3622011001 | San Onofre 3 | 01/25/2011 | 03/26/2011 | ML11087200 | <strong>Missed TS LCO Surveillance Requirement When One Source Range Monitor Removed from Service</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2011, it was discovered that on January 24, 2011, at 1715 PST, with Unit 3 in Mode 5, SCE found Source Range Monitoring (SRM) Channel 2 had been removed from service at 0843 PST without implementing the Shutdown Margin (SDM) verification within four hours as required by Technical Specification Limiting Condition for Operation (LCO) 3.3.13 Condition A.2. The Reactor Coolant System (RCS) boron concentration was being monitored for SDM, however the 0935 PST sample was not reviewed until 1320 PST and the SDM verification procedure was not completed until 1755 PST. SRM Channel 2 had been temporarily made operable, suspending planned maintenance work. When the maintenance work on SRM Channel 2 was resumed, the work control operator failed to activate the administrative controls to reinitialize the LCO surveillance. The on coming operating shift identified the deficiency by reviewing the control board status. Corrective Action was taken to improve the controls for resuming suspended maintenance work. There was no safety significance. Boron concentration was stable, there were no temperature changes or activities with potential to add positive reactivity (control rods were de-energized), and the redundant SDM Channel 1 was in service during this period.
3622011002 | San Onofre 3 | 04/07/2011 | 06/03/2011 | ML11159A16 | <strong>As-Found Condition of LOVS Relays Not Within Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>On 04/07/11, it was determined that SONGS Loss of Voltage Signal (LOVS) relays had been previously calibrated incorrectly, which would result in detecting an undervoltage condition at a higher voltage than specified in Technical Specification (TS) Surveillance Requirement (SR) 3.3.7.3.b. Two of the four Unit 3 LOVS relays on the Train B 4.16kV bus 3A06 were found with setpoints outside the allowable TS voltage range, thus meeting the logic for two channels inoperable (TS Condition 3.3.7.B). The 3A0615-127F1 relay failed surveillance testing on 03/01/11; however, this failure was initially attributed to voltage drift based on information available at that time. The subsequent cause evaluation discovered evidence that this failure was due to improper calibration prior to relay installation in the plant. All LOVS relays in Unit 2 and 3 were then retested; Unit 2 relays were found acceptable, and one additional Unit 3 relay (3A0615-127F2) was found failed on 04/08/11. Based on the investigation, this relay was miscalibrated during surveillance testing on 02/01/11. There was minimal safety significance because an undervoltage condition would have been detected within the design margins ensuring the safety function was performed (i.e., automatic transfer to alternate power source and emergency diesel generator start).
3622011003 | San Onofre 3 | 06/08/2011 | 08/05/2011 | ML11220028 | <strong>Wiring Error in Charging Pump Motor Circuitry Results in Loss of Fire Isolation Capability</strong><br /><i>Abstract:&nbsp;</i>On June 8, 2011, it was determined that the fire isolation switch for the Unit 3 Train A Charging Pump (3P190) motor control circuit had not been wired correctly in both the as-built drawing and field wiring configuration. This condition existed since original installation of the fire isolation switch in 1981. Consequently, if a postulated fire-induced circuit fault developed on the circuit and operators stopped 3P190, the circuit fault would result in a loss of capability to restart the pump locally at the switchgear. 3P190 is credited in the 10 CFR 50 Appendix R Safe Shutdown program for fire scenarios in the Alternative Shutdown Fire Areas (including Control Room). Due to the wiring error, this pump may have been unavailable during a postulated Appendix R fire event, resulting in a condition outside the Appendix R design basis. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition that significantly degraded plant safety. Although the fire isolation switch was impaired, 3P190 remained operable and capable of fulfilling its safety function for all design basis accidents. Appropriate compensatory measures were taken and 3P190 was subsequently returned to fully qualified status on June 14, 2011. The safety significance of this event was determined to be minimal.
3642011001 | Farley 2 | 07/07/2011 | 09/22/2011 | ML11269024 | <strong>Turbine Driven Auxiliary Feedwater Pump Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 30, 2011 at 23:04 while at 100% power, the Unit 2 Turbine Driven Auxiliary Feedwater Pump (TDAFWP) automatically tripped on overspeed during surveillance testing. Through subsequent investigation it was determined that Unit 2 was not in compliance with Technical Specification (TS) 3.7.5 in that the Unit 2 TDAFWP had been rendered inoperable on July 7, 2011 at approximately 10:44 as a result of an inappropriately planned maintenance activity to correct an apparent wiring discrepancy that impacted turbine governor speed control. Electrical leads were incorrectly identified as spares and erroneously removed per plant drawings that contained unknown legacy errors. In addition, on several occasions during the time the Unit 2 TDAFWP was unknown to be inoperable; a second train of Auxiliary Feedwater (AFW) was made inoperable to support routine scheduled maintenance of Emergency Diesel Generators (EDG) and a Motor Driven Auxiliary Feedwater Pump (MDAFWP). This resulted in two of three trains of AFW being inoperable. This represents a condition that could have prevented the fulfillment of a safety function because two out of the three trains of AFW are required to meet flow requirements for limiting design basis accidents (DBA). The Unit 2 TDAFWP wiring was restored to the correct configuration and subsequent surveillance testing was completed satisfactory on August 1, 2011 at 03:40.
3662011001 | Hatch 2 | 04/16/2011 | 12/09/2011 | ML11347A19 | <strong>Primary Containment Isolation Penetration Exceeded Overall Allowable Technical Specification Leakage Limits</strong><br /><i>Abstract:&nbsp;</i>On April 16, 2011, during the Hatch Nuclear Plant outage, a local leak rate test (LLRT) was performed on torus purge supply primary containment isolation valve (PCIV) 2T48-F324 which is associated with primary containment penetration 2T23-X205. At that time, plant engineers and technicians were performing an LLRT for penetration 2T23-X205 when it was discovered that both PCIVs had failed their LLRTs for this penetration. This resulted in the penetration leakage exceeding the overall allowable leakage (La) required by the Technical Specifications (TS) for primary containment. This is considered a safety system functional failure of the primary containment function for this penetration. The primary cause for the excessive leakage for valve 2T48-F324 was attributed to "over-travel" of the valve disc which reduced the seat contact with the disc. This was caused by inadequate procedural guidance for adjusting the valve travel. The excessive leakage for 2T48-F309 was attributed to the valve disc failing to "center" on the seat and wear on the actuator and its linkage. The necessary repairs and adjustments were made and the valves subsequently passed their respective LLRTs, which restored penetration 2T23-X205 to within its TS leakage limits. Additional procedural guidance is being provided to better control "travel" adjustments and in performance of valve inspections.
3662011002 | Hatch 2 | 07/05/2011 | 08/30/2011 | ML11243009 | <strong>Corrosion Induced Bonding Results in Setpoint Drift for Multiple Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2011, at approximately 1000 EDT, Unit 2 was at 100 percent rated thermal power (RTP) when the "as-found" testing results of the 2-stage main steam safety relief valves (SRVs) were received which indicated that eight of eleven SRVs had experienced setpoint drift which resulted in their allowable Tech Spec limits being exceeded. The root cause of the SRV setpoint drift is attributed to corrosion-induced bonding between the pilot disc and seating surfaces. This conclusion is based on previous root cause analyses and the repetitive nature of this condition at Hatch and within the BWR industry. The 2-stage SRVs were removed from Unit 2 in April 2011, and preemptively replaced with 3-stage SRVs as the long term corrective action for the historically observed setpoint drift. The use of 3-stage SRVs is regarded as an industry-wide solution for the corrosion-induced bonding phenomenon which has been a historic industry issue since the early 1980s.
3662011003 | Hatch 2 | 10/24/2011 | 02/12/2012 | ML12045A30 | <strong>Manual Reactor Scram During Startup due to Too Few Operable Intermediate Range Monitors (IRMs)</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2011, at approximately 0% power during startup from a scheduled maintenance outage, the 'A' IRM signal showed increasing levels of electrical noise while on Range 1. A spike in the signal resulted in a half-scram signal that prompted Operations personnel to bypass the 'A' IRM and declare it inoperable. The 'C' IRM subsequently began exhibiting erratic behavior and slowly drifted downscale while on Range 7. Operations personnel "ranged" down the 'C' IRM. Its signal continued to display the same behavior. Operations personnel declared the 'C' IRM inoperable, resulting in no operable IRM channel in one quadrant of the reactor core. Further control rod withdrawal to maintain the core critical was prohibited. Operations personnel were then directed to insert a manual scram signal. Testing revealed the direct cause to be degraded signal cable shielding at under-vessel connectors in six of eight IRM channels allowing electrical noise to couple to the signal conductor. The noise was caused by a consistent low frequency signal on the preamplifier signal input and output cables and by degraded connectors. PM intervals were previously based on time rather than on duty cycle resulting in unidentified connector degradation. Connectors were replaced and post maintenance testing confirmed noise had been reduced to acceptable levels. PM frequency changed based on duty cycle.
3692011001 | McGuire 1, McGuire 2 | 01/20/2011 | 04/01/2011 | ML11102030 | <strong>Shutdown of two Units due to entry into LCO 3.0.3 caused by the inoperability of all four trains of the Nuclear Service Water System due to strainer macro-fouling.</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Units 1 and 2 were in Mode 1 at 100% power. Event Description: On January 18, 2011, during testing of the 1B Nuclear Service Water (RN) pump while aligned to the Standby Nuclear Service Water Pond (SNSWP), its associated strainer became fouled with small, bluegill fish. After further investigation and testing, it was determined that both RN trains on each Unit were potentially inoperable due to macro-fouling from the SNSWP. Both Units entered TS LCO 3 0 3 and initiated shutdowns. McGuire requested and received a Notification of Enforcement Discretion (NOED) for both Units to remain in Mode 3 until the macro-fouling source was eliminated. Event Cause: The causes of this event were lack of an effective macro fouling barrier in the SNSWP, deferral of the fish eradication treatment of the SNSWP in 2010, and lack of risk recognition. Corrective Actions: The SNSWP was chemically treated to eliminate the macro-fouling source and the RN intake lines were flushed. A periodic chemical treatment was established and a macro-fouling barrier modification is planned.
3692011002 | McGuire 1, McGuire 2 | 01/20/2011 | 03/21/2011 | ML11088009 | <strong>Completion of Dual Unit Shutdown and Occurrence of Unit 1 Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On January 20, 2011, while shutting down Unit 1 and Unit 2, operators experienced a loss of feed water (CF) to the Unit 1 Steam Generators. At the time of the event, Unit 1 was at 28% power and the operating crew was transferring steam supplies for the Unit 1 "B" (1B) CF Pump Turbine (CFPT) from the normal steam supply to the alternate steam supply. This required opening valve 1HM-95 to supply steam to the 1B CFPT while monitoring several parameters. Upon opening 1HM-95, the 1B CF pump discharge pressure increased to the trip set point and 1B CF pump tripped on high discharge pressure resulting in a loss of all CF flow. This was followed by an automatic main turbine trip and a manual trip of the reactor. The root cause for the CF pump trip is the use of equipment for a purpose it was not designed. Transferring steam supplies to the 1B CFPT uses a gate valve (1HM-95) which is not designed for throttling. Actions will be taken to discontinue the use of 1HM-95 as a throttle valve and utilize the new CFPT governor steam supply controls for governor modulation.
3702011001 | McGuire 2 | 08/02/2011 | 10/03/2011 | ML11285A30 | <strong>Emergency Diesel Generator 2B Inability to Achieve Overload Operation</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the event, Units 1 and 2 were in Mode 1 at 100% power. Event Description: On 8/2/11, Emergency Diesel Generator (EDG) 2B did not meet overload acceptance criteria (Technical Specification Surveillance Requirement 3.8.1.14). EDG 2B achieved 4150 kilowatts (kW) versus the required 4200 kW. It was subsequently determined EDG 2B was inoperable from 7/16/11. EDG 2A was also inoperable from 7/19/11, 04:36 to 7/20/11, 04:01. This event is not safety significant since EDG 2B was available to provide power to the required emergency loads of approximately 3900 kW. Event Cause: The root cause is lack of documented guidance on engine fuel rack linkage setting requirements in the original engine manufacturer (OEM) drawings which resulted in an inadequate governor actuator replacement setup procedure. Corrective Actions: The governor actuator replacement setup procedure was revised to require engine fuel rack linkage adjustment any time a governor is removed and replaced.
3702011002 | McGuire 2 | 03/30/2011 | 10/26/2011 | ML11307A37 | <strong>Unit 2 Reactor Manually Tripped When Control Rod Did Not Respond as Expected During Control Rod Movement Testing</strong><br /><i>Abstract:&nbsp;</i>On March 30, 2011, Unit 2 was in Mode 5, performing control rod movement testing at the end of a refueling outage. A control rod system malfunction resulted in a control rod misalignment. The condition was terminated when the operators manually opened the Unit 2 Reactor Trip Breakers as prescribed by the test procedure. As part of subsequent troubleshooting, the identical control rod misalignment recurred, and the operators again manually opened the Unit 2 Reactor Trip Breakers. This event is considered to be of no significance with respect to the health and safety of the public. A cause evaluation determined that the control rod drive mechanism head cable for the L13 control rod, which was replaced during the refueling outage, was incorrectly wired by the vendor, and subsequent testing failed to detect the issue. The affected cable was replaced with a correctly wired cable.
3702011003 | McGuire 2 | 12/20/2011 | 02/16/2012 | ML12060A26 | <strong>2B Annulus Ventilation Filter Train Heater Inoperable Longer than Allowed by Tech Specs</strong><br /><i>Abstract:&nbsp;</i>On December 20, 2011, it was determined the 2B Annulus Ventilation (AVS) Filter Train heater did not meet the acceptance criteria of the Ventilation Filter Testing Program (VFTP) heater dissipation test in accordance with Technical Specification (TS) Program 5.5.11 and Surveillance Requirement (SR) 3.6.10.2. It was subsequently determined that the 2B AVS heater was in this condition and inoperable from October 29, 2011 until December 10, 2011. This inoperability time exceeded the Completion Times of TS 3.6.10 Condition B. This event was not safety significant because the AVS heaters are not required or credited for the operability of the AVS Filter Trains. The causes of this event were insufficient troubleshooting after the 2B AVS heater breaker trip on October 29, 2011 and incorrect acceptance criteria in the AVS Filter Train Operability Test procedure. Immediate action was taken to replace the 2B AVS heater and test per the VFTP requirements. Subsequent action was to revise the acceptance criteria of the AVS Filter Train Operability Test procedures. The planned corrective action is to clearly delineate the Operations Procedure requirements for restoring inoperable systems and components to operable status.
3732011001 | LaSalle 1 | 02/01/2011 | 03/25/2011 | ML11089094 | <strong>Automatic Reactor Scram due to Main Power Transformer "C" Phase Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>On February 1, 2011, at 1918 hours CST, LaSalle Unit 1 automatically scrammed from 100% power. The scram was due to a main generator load reject caused by a fault on the C-phase of the 1W Main Power Transformer (1W MPT). The safety significance of this event was minimal. All control rods fully inserted, all systems responded as expected to the scram, and Emergency Core Cooling Systems were not challenged. The root cause of the event was determined to have been external bushing flashover due to moist snow and ice buildup along the exterior bushing skirts of the 1W MPT that surpassed its flashover resistance (i.e., creep length rating) during unusually adverse weather conditions. Corrective actions included diagnosis of extent of damage along with the repair and restoration of the 1W MPT that included replacement of the C-phase bushing, the C corona ring and the MPT mechanical relief valve. Corrective action to prevent recurrence includes replacement of the MPT bushings with a more robust anti-flashover design that exceeds minimum Basic Insulation Level (BIL) rating.
3732011002 | LaSalle 1 | 02/09/2011 | 04/01/2011 | ML11094001 | <strong>Unit Shutdown Required by Plant Technical Specifications due to Pressure Boundary Leakage</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2011, LaSalle Unit 1 was in Mode 2 (Startup) following a forced outage. During a walkdown of the drywell, a steam leak was observed coming from the Reactor Core Isolation Cooling Steam Supply Inboard Isolation Bypass/Warm up Valve (1E51-F076), a normally-closed, one inch, motor operated valve. The leak was determined to be on the valve bonnet extension-to-bonnet upper seal weld. At 1804 hours, the leak was classified as Pressure Boundary Leakage, and Technical Specification (TS) 3.4.5 Condition C was entered. TS 3.4.5 Required Action C.1 and C.2 require that the unit be in Mode 3 within 12 hours and Mode 4 within 36 hours. On February 9, 2011, at 1830 hours, a plant shutdown of Unit 1 commenced. The unit entered Mode 3 at 2258 hours on February 9, and reached Mode 4 at 0353 hours on February 10, 2011. The seal weld was repaired, and the unit was restarted on February 10, 2011. The equipment apparent cause evaluation determined that the cause was due to a weld defect or discontinuity from the original weld construction (i.e., manufacturing, installation/construction errors, etc.) of the upper seal weld that propagated through wall as a result of system loading and conditions (i.e., high pressure steam) during normal plant operations. Corrective action included repair of the defective upper seal weld area.
3732011003 | LaSalle 1 | 03/02/2011 | 04/29/2011 | ML11122007 | <strong>Secondary Containment Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2011, Unit 1 was in Mode 1 at 100% power and Unit 2 was in Mode 5 in a refueling outage, with fuel moves in progress. At 0928 hours CST, the Unit 1 Reactor Operator reported that the control room indication for secondary containment vacuum was 0.17 inch of vacuum water gauge. Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.1 requires that secondary containment vacuum be greater than or equal to 0.25 inch of vacuum water gauge. Secondary containment was declared inoperable, and a four-hour timeclock to restore secondary containment to operable status was started in accordance with TS 3.6.4.1 Required Action (RA) A.1. In addition, TS RAs C.1, C.2, and C.3 were entered, and fuel moves and core alterations on Unit 2 were immediately suspended. Personnel were dispatched to the Unit 1 Reactor Building and the Refuel Floor ventilation panels to observe local differential pressure readings, where the control room indication was confirmed. Shortly thereafter, secondary containment vacuum indication returned to its normal reading of approximately 0.5 inches of vacuum water gauge. At 0942 hours CST, secondary containment was declared operable and the associated RAs were exited. At 1000 hours, fuel moves and core alterations were resumed on Unit 2. The cause of the event could not be determined; however, it is suspected that both Unit 2 steam tunnel airlock doors were simultaneously opened for a short period. Corrective actions include replacing the interlock magnets and switches to assure reliability, and to provide plant barrier training for personnel who traverse secondary containment doors.
3732011004 | LaSalle 1 | 02/02/2011 | 12/14/2011 | ML11348043 | <strong>Loss of Secondary Cooling Function due to Spurious Closure of the Shutdown Cooling Suction Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On February 2, 2011, Unit 1 was in Mode 3 (Hot Shutdown), and was being cooled down to Mode 4 (Cold Sutdown) in order to perform forced outage work following an unplanned reactor scram. At 16:57 hours CST, while in Mode 3, the 1B Residual Heat Removal (RHR) pump was started in preparation for starting the Shutdown Cooling (SDC) system. When the pump was started, a momentary high pump suction flow signal was received, causing the common pump suction isolation valve 1E12-F009 to close and the 1B RHR pump to trip. Both SDC trains were declared inoperable, and Technical Specification (TS) 3.4.9, "RHR Shutdown Cooling System - Hot Shutdown," Required Action (RA) A.1 was entered, which requires that action be intitiated immediately to restore the RHR shutdown cooling system to operable status. The control room operators determined that the isolation was spurious, reset the containment isolation logic, and at 17:10 hours reopened 1E12-F009 and exited the TS RA. The cause of the isolation was determined to be a spurious high pump suction flow signal. Corrective actions included increasing the time delay for the RHR SDC isolation for SDC suction high flow from one second to three seconds.
3742011001 | LaSalle 2 | 05/27/2011 | 07/26/2011 | ML11207098 | <strong>Turbine Control Valve Fast Closure Trip Oil Pressure Switch Inoperable due to Incomplete Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On May 27, 2011, Unit 2 was in Mode 1 at 100% power. At 1804 hours CDT, the 2A Turbine Control Valve Fast Closure Trip Oil pressure switch (2C71-N005A) was declared inoperable, following the discovery that incomplete post maintenance testing (PMT) had been performed after replacement of the switch during the previous refueling outage. Response time testing as required by Technical Specification (TS) Surveillance Requirement 3.3.1.1.17 had been inadvertently omitted. Technical Specification (TS) 3.3.1.1 Required Action (RA) A.1 was entered to place the channel in trip within 12 hours, and TS 3.3.4.1 RA A.1 was entered to restore the channel to OPERABLE status within 72 hours. The required TS surveillance was completed by 2114 hours, and at 2153 hours on May 27, 2011, 2C71-N005A was declared operable, and the associated TS RA timeclocks were exited. The cause of the event was that inadequate procedural guidance was provided to the work planner to identify the response time testing requirement. Corrective actions include providing flags in the Work Management Passport program for components that require response time testing following replacement, and to recommend revision of the corporate Post Maintenance Testing procedure to indicate that response time testing must be considered when replacing pressure switches.
3822011001 | Waterford 3 | 02/16/2011 | 04/16/2011 | ML11109A11 | <strong>Waste Gas System Oxygen Exceeded Technical Specification Allowed Duration</strong><br /><i>Abstract:&nbsp;</i>This LER reports the operation of Waterford 3 in a condition prohibited by Technical Specification 3/4.11.2.5, Radioactive Effluents, Explosive Gas Mixture. Specifically, Technical Specification 3/4.11.2.5 requires that the concentration of oxygen in the waste gas holdup system shall be limited to less than or equal to 2 percent by volume at all times whenever the hydrogen concentration exceeds 4 percent by volume. At 4:10 p.m. on February 14, 2011, it was identified that Gas Decay Tank C oxygen concentration had exceeded the allowed concentration for the existing hydrogen concentration specified in Technical Specification 3.11.2.5. Technical Specification 3/4.11.2.5 Action 'a' states in the event that oxygen concentration is greater than 2 percent by volume, but less than 4 percent by volume, oxygen concentration must be reduced to 2 percent or less within 48 hours. Contrary to this requirement, a review of the condition determined that the 48 hour action limit specified in Technical Specification 3/4.11.2.5 Action 'a' was exceeded and is reportable. The oxygen concentration was returned to within limits at 10:47 p.m. on February 18, 2011, and compliance with Technical Specification 3/4.11.2.5 was restored. There have been no previous similar licensee events reported in the last three years.
3822011002 | Waterford 3 | 04/07/2011 | 06/06/2011 | ML11158060 | <strong>Main Feedwater Isolation Valve "A" Failed Surveillance Requirement</strong><br /><i>Abstract:&nbsp;</i>On 4/7/2011, Main Feedwater Isolation Valve (MFIV) "A" failed the in-service test (IST) stroke time. Due to the failed stroke time, the plant operated in a condition prohibited by Technical Specifications. Technical Specification 3.7.1.6 requires MFIV "A" to be operable in Modes 1 through 4, with a surveillance requirement 4.7.1.6 that requires the closure time of less than or equal to 6 seconds. MFIV "A" uses a hydraulic actuator, which contains two separate hydraulic accumulators. An actuation signal results in both accumulators closing the valve. The Root Cause Evaluation determined that the hydraulic actuator four way valves are marginally designed to provide the motive force needed to overcome infrequent valve operation coupled with the condition that Fyrquel hydraulic fluid is susceptible to breakdown. Corrective actions included replacing the four way valves and replacing the hydraulic fluid for MFIV "A".
3822011003 | Waterford 3 | 04/30/2011 | 06/29/2011 | ML11181010 | <strong>Emergency Diesel Generator Output Breaker Failed to Automatically Close During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2011, the Emergency Diesel Generator (EDG) A output breaker failed to automatically close during Technical Specification (TS) surveillance testing. This was caused by a human performance error on November 2, 2010 when an electrical lead was reconnected to the wrong terminal on a timing relay following maintenance. With this incorrect configuration, EDG A was not able to automatically energize the Train A electrical safety bus. Operator action would have been required to energize the bus by locally closing the EDG A output breaker. Waterford 3 was in mode 5 at the time of discovery, and was in compliance with TS requirements with EDG B operable. Due to EDG A being inoperable from November 2, 2010 to after the time of discovery, the TS 3.8.1.1 Limiting Conditions for Operation (LCO) requirements were not met. Additionally, Train B equipment had been inoperable during this period which presented a condition that could have prevented the fulfillment of a safety function. The wiring error was corrected on May 1, 2011 and EDG A was restored to service on May 2, 2011. Planned corrective actions include procedure changes that will require the use of plant design documents to verify as left conditions and strengthening post maintenance testing.
3822011004 | Waterford 3 | 07/27/2011 | 09/26/2011 | ML11272A03 | <strong>Vendor Notification of Non-Conforming Part Renders Both Trains of QSPDS Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2011, the Waterford 3 Steam Electric Station (W3) received a Westinghouse Nuclear Safety Advisory Letter which informed W3 that a power supply harness supplied for the Qualified Safety Parameter Display System (QSPDS) may be undersized and not be able to handle the current to which it is exposed under all environmental conditions. W3 determined that the suspect harness had been installed in both QSPDS channels. No actual failure occurred. Technical Specification (TS) 3.3.3.6 requires the accident monitoring instrumentation channels (including QSPDS) to be OPERABLE in MODES 1, 2, and 3. The identified condition rendered both channels of QSPDS inoperable. TS 3.3.3.6 Action 30 specifies an allowed outage time (AOT) of seven days. The same vendor letter recommended installation of a jumper to restore operability. This was performed by site maintenance personnel to both QSPDS channels on July 29, 2011.
3822011005 | Waterford 3 | 10/20/2011 | 12/19/2011 | ML11356A07 | <strong>Loss of Essential Chiller B Caused Less Than 100% Emergency Feedwater Supply Capability</strong><br /><i>Abstract:&nbsp;</i>At 08:00 CDT on 10/20/2011, Essential Chilled Water Loop B was declared inoperable due to equipment failure while turbine driven Emergency Feedwater (EFW) Pump AB was out of service for planned maintenance. Operability of Essential Chilled Water Loop B was restored at 08:50. During this time period, the application of cascading technical specifications rendered motor driven EFW Pump B inoperable. The remaining operable EFW Pump A is a design rated 50 percent pump; therefore, this event could have prevented fulfillment of the residual heat removal safety function. Offsite power and Train A safety related equipment and systems were verified operable. Essential Chilled Water Loop B was declared inoperable because Essential Chiller B failed to automatically restart from a load recycle. The Operations crew took immediate action to align Essential Chiller AB to restore operability to Essential Chilled Water Loop B. Restoration of operability to Essential Chilled Water Loop B concurrently restored operability to EFW Pump B. No plant transient or safety system actuations occurred. Stable plant operation continued at 100 percent power.
3872011001 | Susquehanna 1, Susquehanna 2 | 01/03/2011 | 03/02/2011 | ML11062071 | <strong>Single Point Vulnerability with the Potential to Cause Isolations</strong><br /><i>Abstract:&nbsp;</i>On January 3, 2011, PPL Susquehanna, LLC (PPL) identified a single point vulnerability associated with the steam leak detection system (SLD) for Unit 1 and Unit 2. Specifically, PPL determined that the design and setpoint selection for the SLD Delta Temperature function might not be able to accommodate a sudden complete failure of the non-safety related Reactor Building (RB) HVAC heating system temperature controls during cold weather conditions without causing an isolation of high pressure injection systems (HPCI and RCIC) and main steam lines (MSIVs). This design deficiency had existed since original plant design. This event is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as an unanalyzed condition. The cause of the event was a less than adequate single failure analysis that did not provide sufficient detail to identify the vulnerability. There were no actual adverse consequences. With regard to potential significance, incorporation of the postulated isolation events into the risk model resulted in very small changes to the CDF and LERF. Based on this information, the potential safety impact of the reported event was insignificant. A corrective action to eliminate the isolation function of the SLD delta T instrumentation has been implemented. In addition, a Failure Modes and Effects Analysis (FMEA) will be performed on all non-Q support systems that could cause an isolation of ECCS systems or all the MSIVs. This proposed action will address the extent of cause.
3872011002 | Susquehanna 1 | 01/25/2011 | 02/01/2012 | ML12033A08 | <strong>Unit 1 Manual Scram due to Unisolable Extraction Steam System Leak</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2011, Susquehanna Steam Electric Station Unit 1 reactor was manually scrammed due to an unisolable extraction steam system leak in the 1C Feedwater Heater Bay area (EIIS: SJ). Reactor power was lowered from 98.4% to 65% prior to the scram. Non-safety-related electrical equipment exposed to the condensing steam began malfunctioning. Attempts to isolate the source of the leakage were unsuccessful. Based on continued indications of an unisolable steam leak, the decision was made to shut down the unit. The mode switch was placed in shutdown. All rods inserted. Reactor water level lowered to minus 31 inches causing a Level 3 (plus 13 inches) isolation. The Reactor Core Isolation Cooling System (RCIC) (EIIS: BN) automatically initiated on a minus 30 inch level signal and was manually secured after water level was restored. Reactor water level was maintained at the normal operating band using feedwater. No steam relief valves opened. All safety systems (RPS and PCIS) operated as expected. The direct cause of the unisolable leak was the loss of a bleeder trip valve cover plug. The two root causes were 1.) Less than adequate (LTA) management oversight of the work activity and work planning process and 2.) Deficient work instruction and task assignment for the Bleeder Trip Valve (BTV) repair task. Corrective actions were to replace and seal weld the cover plug on the affected valve and to seal weld the cover plugs on other valves of similar design. Other key corrective actions included planning procedure changes related to threaded pipe assemblies, evaluation and training of maintenance foremen, implementation of a more risk informed screening process, procedure changes and an enhanced coaching card on procedure use and adherence, and management observations using the revised coaching card. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) due to the manual scram and the Reactor Protection System initiation. There were no actual adverse consequences to the fuel, any safety-related plant equipment, or to the health and safety of the public as a result of this event since the dose consequences from the additional leakage would not have exceeded regulatory limits.
3872011003 | Susquehanna 1 | 02/25/2011 | 04/26/2011 | ML11116059 | <strong>HPCl Inoperability Due to Valve Packing Leak I</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2011 at 2027, the Unit 1 High Pressure Coolant Injection (HPCI) Steam Supply Inboard Isolation Valve (HV155F002) was declared inoperable as a result of a packing leak. HPCI was subsequently declared inoperable at 2136 hours on February 25, 2011 as a result of closing the inoperable inboard isolation valve. Subsequently, the HPCI outboard isolation valve was also closed and deactivated. An 8-hour report was made since HPCI is a single train safety system and the event resulted in a loss of safety function. Since inspection of HV155F002 indicated that the grease was completely washed away from the valve stem and an engineering analysis showed inadequate margin to assure the valve would stroke under design basis conditions with no grease on the stem, a determination was made that HV155F002 was inoperable for some time prior to entry into LCO 3.6.1.3. As a result, this was a condition prohibited by Technical Specifications. The root cause was determined to be a failure to recognize the implications of gland liner failure and the failure modes and mechanisms on the packing system during changes to gland design. Causal factors were less than adequate technical rigor during design of the gland liner and less than adequate attention to detail during fabrication of the liner. Key corrective actions that are planned include: 1) replacing the brass lined packing gland with a bronze lined packing gland for each valve with a brass liner; 2) performing a design review of gland liner modification documents to ensure all design considerations for packing gland liners are appropriately addressed, and 3) revising applicable procedures to ensure that packing gland liners are inspected during all future re-packs.
3872011004 | Susquehanna 1, Susquehanna 2 | 09/21/2011 | 02/13/2012 | ML12045A06 | <strong>"C" Emergency Diesel Generator Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 6, 2011, Susquehanna Steam Electric Station declared the common "C" Emergency Diesel Generator (EDG) (ElIS: EK) inoperable due to loss of firing from cylinder 8R during surveillance testing. LCO 3.8.1 was entered, the "E" Emergency Diesel Generator was substituted for the "C" EDG and the LCO exited. The direct cause of the loss of firing was due to interruption of the spray pattern in the fuel injection nozzle and partial blockage. The root causes were determined to be 1) the work package to install the delivery valve springs was insufficient, 2) the work crew proceeded using an inadequate work package and 3) Quality Control activities were insufficient to prevent the incorrect reassembly of the fuel injector pump components. Immediate corrective action was to replace the 12 fuel injection pumps. Additional corrective actions include revision to the procedure on work package standards, reinforcement of stopping work when the work package is inadequate, and revision to the procedure on Quality Control Inspection Program to include guidance on construction, formatting, wording and use of notes and verification steps in hold point development. A review of past maintenance on the "C" EDG determined that the EDG was inoperable from the time maintenance was performed on September 21, 2011 until it was shutdown on December 6, 2011 because it could not have fulfilled its mission time. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications. There were no actual adverse consequences to the health and safety of the public as a result of this event.
3882011001 | Susquehanna 2 | 05/02/2011 | 07/01/2011 | ML11182076 | <strong>Multiple Inoperable Main Steam Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>During the Susquehanna Unit 2 15th Refueling and Inspection Outage, three (3) Main Steam Safety Relief Valves (SRVs) failed to meet the set point criteria of +/- 3% set forth in Technical Specification 3.4.3. The three SRVs actuated at a setpoint less than the -3% criteria. The causes of the lower setpoint actuation are attributed to setpoint drift and seat leakage. Thus with three (3) SRVs inoperable at the same time, the required number of operable SRVs per Technical Specification 3.4.3 was not met. This event was determined to be a Condition Prohibited By Technical Specifications and reportable under 10 CFR 50.73(a)(2)(i)(B). This event was also determined to be a Common-Cause Inoperability of Independent Trains or Channels and reportable under 10 CFR 50.73(a)(2)(vii) due to having more than one failure due to setpoint drift. The SRVs remained functional and would have relieved pressure. There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event.
3882011002 | Susquehanna 2 | 06/27/2011 | 05/11/2012 | ML12132A22 | <strong>Condition Prohibited by Technical Specification due to Unknown RCIC lnoperability</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2011 during startup from a refueling outage, Operations conducted the RCIC quarterly flow surveillance. During the testing, RCIC tripped on overspeed. Subsequent troubleshooting determined the problem to be the ramp generator signal converter (RGSC). Engineering evaluation determined that RCIC had been inoperable as a result of the RGSC problem on June 27, 2011 when the plant exceeded 150 psig and the RCIC LCO became applicable. Since RCIC was not known to be inoperable when the inoperability occurred on June 27, 2011, a condition prohibited by Technical Specifications occurred. Also, HPCI was made inoperable for testing for approximately two hours while RCIC was unknowingly inoperable. The direct cause/apparent cause of the component failure was a voltage induced spike/over voltage on the supply input that caused the RGSC U1 Op-Amp to fail as a result of failure to incorporate vendor recommended information into test procedures. The causes of the condition prohibited by Technical Specifications were less than adequate procedures and less than adequate system health monitoring. Key corrective actions included replacing the failed RGSC, creating high priority computer alarms to alert personnel of anomalies associated with the HPCI and RCIC RGSC and Electronic Governor Module (EGM), revising the applicable Unit 1 RCIC and HPCI test procedures, and revising the station health reporting procedure. Key corrective actions planned include revising the applicable Unit 2 RCIC and HPCI test procedures, revising applicable RCIC and HPCI calibration procedures, and developing a matrix to systematically review systems to determine if testing is adequate to ensure Technical Specification compliance. For the seven key corrective actions identified in the LER, three have been completed and two of the remaining four have been completed for Unit 1. There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3882011003 | Susquehanna 2 | 08/19/2011 | 10/18/2011 | ML11292013 | <strong>Unit 2 Scram due to Main Turbine Trip During ICS Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On August 19, 2011, at 10:46 hours, Susquehanna Steam Electric Station (SSES) Unit 2 automatically scrammed from 100 percent power due to a main turbine trip. The main turbine trip occurred during the performance of the quarterly functional surveillance test of the reactor water high level trip channels for feedwater / main turbine. The surveillance test was being performed for the first time since the 2011 upgrade of the Unit 2 feedwater level control system with a digital Integrated Control System (ICS). As part of the test, operations personnel transferred the reactor water level input signal from average level to narrow range 'B' biased as required by the procedure. The main turbine and feedwater trip system design uses three narrow range reactor water level channels in a two-out-of-three trip logic. When the first narrow range reactor water level channel ('2A') was tested, an unexpected automatic main turbine trip occurred. ENS notification (47172) was made to the NRC in accordance with 10 CFR 50.72(b)(2)(iv) for an event or condition that resulted in the actuation of the RPS when the reactor was critical, and 10 CFR 50.72(b)(3)(iv)(A) due to a valid actuation of the RPS. This Licensee Event Report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A). This event had no impact to the health and safety of the public. The direct cause was an incorrectly terminated internal jumper. The wiring anomaly in the ICS Level 8 turbine trip logic circuitry resulted in one of the Level 8 trip logic contacts being jumpered out of the channel trip circuitry, causing a Unit 2 main Turbine Trip from the initiation of one single channel instead of the designed two-out-of-three channel logic. The root causes for this event are 1) Conflicting and unclear procedure requirements, and less than adequate (LTA) reinforcement of management expectations for work package content resulted in a key visual check of internal jumpers being omitted from the scheme check work package during its preparation. Therefore, testing failed to check and discover the miswired jumper, 2) LTA procedure adherence during development of engineering change functional testing resulted in insufficient testing of the ICS Level 8 main turbine trip logic, and 3) The work order review process weaknesses related to procedure content, procedure adherence, reinforcement of expectations, and definition of work order scope resulted in the review of the ICS Level 8 scheme check work package not identifying the missing key internal jumpers. This resulted in a missed opportunity to identify the incorrectly terminated conductor. Corrective actions include 1) Revise the control scheme testing procedure to clearly identify the specific responsibilities of the preparer, technical reviewer and the implementer of scheme checks and to align scheme check work order content to meet requirements of SSES maintenance work practices, 2) Require the use of risk managed defenses for functional test procedure development and field installation activities for risk significant modifications, 3) To improve the use of and compliance with procedures on a sustainable basis, and reinforce through observation, the use of the SSES Station Fundamentals Tool Kit that the 'Procedures' core fundamental and supporting behaviors shall be maintained, and 4) Conduct reinforcement sessions regarding management's expectation for scheme check work order preparation, technical review and implementation support.
3882011004 | Susquehanna 2 | 10/06/2011 | 12/05/2011 | ML11339012 | <strong>Unit 2 HPCI lnoperability</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2011, Susquehanna Steam Electric Station Unit 2 High pressure Coolant Injection System (HPCI) (EIIS: BJ) was declared inoperable due to fluctuations occurring on the output signal of the HPCI pump electronic governor. These fluctuations were occurring while the system was in standby and were an early indication of potential governor failure. The governor output signal fluctuations were discovered by the system engineer while performing system trending analysis via the plant computer points. HPCI was declared inoperable and LCO 3.5.1 was entered. The direct cause of the electronic governor output signal fluctuations was a buildup of resistance across the Overspeed Test Controller subcomponent. The root cause was determined to be an incorrect component criticality code which did not identify periodic maintenance under Susquehanna SES's preventive maintenance program. Immediate corrective action was to replace the Overspeed Test Controller. Additional corrective actions include reclassification of the component criticality code, evaluation of the removal of the Overspeed Test Controller and periodically exercising the Overspeed controller test switches. The Unit 1 HPCI and Unit 1 and Unit 2 Reactor Core Isolation Cooling System (RCIC) were unaffected as the electronic governor for this equipment was stable and trending as expected. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) due to a condition that could have prevented the fulfillment of a safety function. There were no actual adverse consequences to the health and safety of the public as a result of this event.
3882011005 | Susquehanna 2 | 07/27/2011 | 07/23/2013 | ML13205A16 | <strong>Core Flow Mis-Calibrated Resulting in Core Flow Above 108 Mlb/Hr</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2011, a Unit 2 core flow calibration was performed in accordance with Procedure TP-264-032, "Core Flow Calibration". During the performance of the calibration, Recirculation System Loop A flow was adjusted down by approximately 2.4 Mlb/hr and Loop B was adjusted down by approximately 0.2 Mlb/hr (approximately 2.6 Mlb/hr total adjustment). A subsequent core flow calibration was performed on August 16, 2012 that identified that total core flow was indicating approximately 2.3 Mlb/hr lower than actual core flow. Assuming the core flow was indicating approximately 2.3 Mlb/hr low during that entire timeframe, core flow exceeded the 108 Mlb/hr limit at various times between July 27, 2011 and August 16, 2012. Licensing analyses for Susquehanna are performed with a maximum assumed value for core flow of 108 Mlb/hr. The analyses assume uncertainties around the analyzed value of 108 Mlb/hr. The maximum instantaneous flow during the period was determined to be 109.18 Mlb/hr; the maximum 3 minute average was determined to be 109.09 Mlb/hr. <br><br> There are no existing concerns associated with this issue since core flow is currently calibrated correctly. <br><br> An apparent cause evaluation is in progress. <br><br> There were no adverse consequences to the health and safety of the public as a result of this event
3892011001 | St. Lucie 2 | 12/02/2010 | 01/29/2011 | ML11039052 | <strong>Inadvertent Crosstie of Component Cooling Water (CCW) to Control Room A/C Units</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2010 at 2320 St. Lucie Unit 2 was in Mode 1, while performing Plant Operator daily rounds, it was discovered the Unit 2 component cooling water (CCW) train A and B headers were cross-connected at control room A/C unit HVA/ACC-3C via CCW cooling flow being supplied from the A header and returning to the B header. This condition was a violation of Technical Specification (TS) 3.7.3 and required entry into a 1-hour shutdown action statement in accordance with TS 3.0.3. The Control Room staff immediately realigned CCW to 2-HVA/ACC-3C to Train B; no power reduction was necessary. This event is reportable as a condition prohibited by Technical Specifications, 10CFR50.73 (a) (2) (i) (B) and 10CFR50.73 (a) (2) (vii), a common cause inoperability of independent trains. A root cause evaluation (RCE) determined the valve misalignment relied on one procedure as the sole configuration control method for the CCW valves to the control room A/C Unit HVA/ACC-3C. Contributing causes included inadequate instructions for verifying CCW valve position to control room A/C unit HVA/ACC-3C by Procedure 2-0010123, "Administrative Control of Valves, Locks and Switches". Corrective actions included procedure revisions to ensure CCW and ICW valves have positions tracked when transferring the 2AB bus and components from A side to B side and from B side to A side and that locked open / locked closed tags reflect the current alignment of the valves.
3892011002 | St. Lucie 2 | 06/06/2011 | 11/21/2011 | ML11334A05 | <strong>Unplanned Automatic Reactor Trip During Reactor Protection System Testing</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2011 St . Lucie Unit 2 was in Mode 1, when an unplanned automatic reactor trip occurred. The trip occurred while Operators were performing a reactor protection system (RPS) test in which the Operator inadvertently moved the matrix relay trip select switch one position too far, causing the reactor trip circuit breakers (TCBs) to open. Upon reactor trip all CEAs fully inserted into the core, auxiliary feedwater actuation system (AFAS) initiated as designed on low steam generator water level and was restored using auxiliary feedwater. All safety related systems functioned as designed. A root cause evaluation (RCE) determined the trip was a result of latent single human error vulnerability in the test methodology. Contributing causes included human error during performance of the test and inadequate "problem resolution" which required the matrix relay hold pushbutton to be depressed during performance of the entire test. This event is reportable under 10 CFR 50.73 (a) (2) (iv) (A) , as any event or condition that resulted in a manual or automatic reactor trip and actuation of the auxiliary feedwater system. Corrective actions include procedure revisions to test methodology to remove the human error vulnerability and replacement of the RPS matrix relay hold pushbuttons with rotary switches.
3902011001 | Watts Bar 1 | 05/09/2011 | 07/08/2011 | ML11192007 | <strong>Safety Injection Pump Capable of Injecting into Reactor Coolant System in Mode 5</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2011 at 15:17 Eastern Standard Time (EST) with Watts Bar Nuclear Plant, Unit 1 in Mode 5, and the Reactor Coolant System (RCS) in a near water solid condition, the licensed operator started Safety Injection Pump 1A-A (SIP 1A-A) to fill and vent the Cold Leg Accumulators (CLAs) in accordance with System Operating Instruction SOI-63.01. Following startup of SIP 1A-A, RCS pressure immediately began to rise and reached a maximum pressure of 328 psig before the operators secured the pump. The RCS pressure transient during this event did not exceed the Cold Overpressure Mitigation System (COMS) setpoint. The unexpected pressure transient was due to improper alignment of the Safety Injection System (SIS) when used to fill and vent the CLAs. Specifically, SIP 1A-A Crosstie Valve (1-FCV-63-152) was opened when it should have been closed. Misalignment of the SIS was due to a failure to follow procedures for a temporary clearance lift. LCO 3.4.12 was not met because a SIP was capable of injecting into the RCS in Mode 5, which is reportable as a condition prohibited by Technical Specifications in accordance with 10 CFR 50.73(a)(2)(i)(B).
3902011002 | Watts Bar 1 | 06/22/2009 | 06/10/2011 | ML11164046 | <strong>ERCW System Valve Misalignment</strong><br /><i>Abstract:&nbsp;</i>While performing Surveillance Instruction 1-SI-67-1 on June 22, 2009, TVA discovered that both Primary Essential Raw Cooling Water (ERCW) Supply Valve (2-FCV-67-66) and Backup ERCW Supply Valve (2-FCV-67-68) to the 2A-A Emergency Diesel Generator heat exchangers were open. Under normal operating conditions, 2-FCV-67-66 is open and 2-FCV-67-68 is closed. With both supply valves open, the system was not properly aligned, and ERCW supply headers 1A and 2B were cross-connected. This misalignment caused the ERCW system to be inoperable in accordance with Technical Specifications (TS) Limiting Condition for Operation (LCO) 3.7.8 and the system could not meet surveillance requirement (SR) 3.7.8.1, to verify valves are in the correct position. With both ERCW trains inoperable, the plant entered LCO 3.0.3. Valve 2-FCV-67-68 was closed immediately upon discovery, and the plant exited LCO 3.0.3. Evaluation of the system alignment indicates that there was no loss of safety function, but because of the incorrect alignment, the ERCW system was inoperable for over nine hours, and Watts Bar failed to be in mode 3 within seven hours as required by LCO 3.0.3. This event is reported as a condition prohibited by TS under 10 CFR 50.73(a)(2)(i)(B) because the plant was in LCO 3.0.3 for a period longer than allowed by TS.
3902011004 | Watts Bar 1 | 05/29/2011 | 04/12/2013 | ML13102A13 | <strong>Reactor / Turbine Trip due to Loss of Main Generator Excitation</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2011, 01:55 Eastern Daylight Saving Time (EDT) with Watts Bar Nuclear (WBN) Unit 1 at 100% rated thermal power, the reactor tripped automatically on a Main Generator/Turbine trip due to loss of main generator excitation, which resulted from a spurious fault signal from the Extended Gate Controller (EGC) in the Automatic Voltage Regulator (AVR). The most probable cause of the spurious signal was an intermittent fault in a ribbon cable to the EGC. Following cooldown to no-load equilibrium conditions, main feedwater isolation occurred due to Reactor Trip coincident with low Reactor Coolant System TAVG. Main feedwater isolation resulted in a Main Feed Pump Turbine (MFPT) trip signal which resulted in the automatic startup of the AFW System. No overcooling transient occurred and no safety injection signal was initiated for this event. <br /><br /> Plant personnel immediately entered appropriate trip response procedures and stabilized the plant. <br /><br /> The EGC circuit has been bypassed to prevent further spurious trips. The ribbon cable will be replaced at the next outage, and EGC output will be monitored for approximately one cycle to confirm no spurious trip signals before placing the EGC back in service. <br /><br /> This event is reported as an LER in accordance with 10 CFR 50.73(a)(2)(iv) for the valid actuation of the reactor protection system and the auxiliary feedwater system.
3952011001 | Summer 1 | 05/03/2011 | 07/01/2011 | ML11186A97 | <strong>Failure to Maintain One Train of Safe Shutdown Systems in Accordance with Appendix R Section III.G.a/III.G.3</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2011 at 0514 hours, V.C. Summer Nuclear Station (VCSNS) determined the following: During circuit analysis review for transitioning the Fire Protection Program to NFPA 805, VCSNS identified a violation of the Appendix R requirement to maintain one train of systems free of fire damage, which are necessary to achieve and maintain Hot Shutdown conditions. VCSNS determined that a fire in the Main Control Room (MCR), the Cable Spreading Room (CSR), or the Control Building (CB) 412 North Chase could result in a hot short that could actuate a relay and trip and lock out all incoming breakers to the B-train essential electrical bus (XSW1DB). A root cause analysis was conducted and determined the cause was human error in the Appendix R analysis performed for VCSNS by a vendor. Immediate corrective actions consisted of establishing roving fire watches in the affected areas and revising the FireEmergency Procedures (FEPs) to ensure the ability to achieve/maintain Hot Shutdown conditions. This report also provides a 10 CFR Part 21 written notification.
3952011002 | Summer 1 | 05/03/2011 | 07/01/2011 | ML11186A97 | <strong>Failure to Maintain One Train of Safe Shutdown Systems in Accordance with Appendix R Section III.G.a/III.G.3</strong><br /><i>Abstract:&nbsp;</i>On May 3, 2011 at 0514 hours, V.C. Summer Nuclear Station (VCSNS) determined the following: During circuit analysis review for transitioning the Fire Protection Program to NFPA 805, VCSNS identified a violation of the Appendix R requirement to maintain one train of systems free of fire damage, which are necessary to achieve and maintain Hot Shutdown conditions. This violation applies to postulated fires in the Main Control Room (MCR) or Cable Spreading Room (CSR). Circuits were identified in the MCR and the CSR that impact a control power circuit that could result in the loss of ability to start the B Emergency Diesel Generator (EDG) using local controls. A root cause analysis was conducted and determined that the root cause was a less than adequate design change/configuration management process. Specifically, a design modification caused the subject vulnerability and the associated Appendix R review (both performed by a vendor for VCSNS) did not ensure the issue was corrected. Immediate corrective actions consisted of establishing roving fire watches and installing jumpers to defeat the subject control power start permissive contacts.
3952011003 | Summer 1 | 05/27/2011 | 09/27/2011 | ML11272A15 | <strong>Inadvertent Safety Injection During Reactor Startup due to Excessive Differential Steam Line Pressure</strong><br /><i>Abstract:&nbsp;</i>At 1201 hours on 05/27/2011 with the plant in Mode 3 at normal operating temperature and pressure, a Safety Injection (SI) occurred due to opening the 'C' Main Steam Isolation Valve (MSIV), with the downstream steam header depressurized. The resulting steam flow depressurized the 'C' Steam Line to greater than 97 psid below the 'A' and 'B' Steam Lines, which caused an SI on both Engineered Safety Feature (ESF) trains. Following the Safety Injection actuation, all plant systems functioned as designed. Immediate actions consisted of securing the SI and stabilizing the plant in Mode 3 via Emergency Operating Procedures (EOPs). In addition, the MSIVs and Bypass valves were tagged closed to ensure proper controls were in place prior to operating the valves. Oncoming Operating Crews were briefed prior to taking the shift on the importance of maintaining cognizance of changing plant conditions and providing thorough turnover when relieving other crew members during the shift. The root cause of this event was determined to be failure to follow procedures while manipulating a plant system.
3972011001 | Columbia | 06/29/2011 | 08/29/2011 | ML11256A02 | <strong>Failure to Follow Technical Specification During Control Rod Exercise</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2011, while the plant was in Mode 5 for refueling outage R20, Columbia Generating Station (Columbia) failed to enter a required Technical Specifications (TS) Action Statement while performing control rod exercises. During stroke time testing, control rod 34-47 displayed an erroneous indication. Upon initial withdrawal, the four rod display showed an alternating indication of "XX" (meaning the reed switch was not open during movement) and "00" (full in indication) requiring the position indication to be declared inoperable per TS 3.9.4. Control rod 34-47 was subsequently fully inserted and testing resumed on other rods contrary to the required action statement of TS 3.9.4. Upon discovery of the noncompliance, the TS required actions were subsequently performed and the failed reed switch replaced. The Control Room Supervisor and Shift Manager did not verify the required action statements specified in the TS and Bases as required. This was determined to be the apparent cause. A contributing cause included not performing all of the required steps in the procedure for control rod stroke time testing. Columbia has had no previous occurrences of a failure to enter the required action statement of TS 3.9.4. This condition is reportable under 50.73(a)(2)(i)(B) as a condition prohibited by TS.
3972011002 | Columbia | 08/27/2011 | 10/25/2011 | ML11305A07 | <strong>Loss of Shutdown Cooling due to Logic Card Failure</strong><br /><i>Abstract:&nbsp;</i>At 2021 hours on August 27, 2011, a loss of shutdown cooling occurred due to a spurious undervoltage signal in one of two, in series, Electrical Protection Assembly (EPA) circuit breaker supplying the B train of the Reactor Protection System (RPS) power bus (RPS-B). Response to the spurious signal resulted in loss of power to RPS-B and associated actuations including isolation of the common shutdown cooling suction valves.The spurious signal originated in a logic board (GE Model 147D8652G007) associated with the EPA Breaker. Post event testing was unable to specifically identify the discrete component responsible for the failure. The root cause was that Energy Northwest was not proactive in replacing older, obsolete model boards (including the one that caused the event) with a new model recommended by the vendor. The faulty logic board and the other logic board in series for RPS-B were replaced with newer model boards. Further corrective actions will replace the remaining logic boards currently installed in the plant with the newer models. This event is being reported under 10 CFR 50.73(a)(2)(v) as an event that could have prevented fulfillment of a safety function, as well as an invalid actuation of containment isolation in multiple systems per 10 CFR 50.73(a)(2)(iv).
3972011004 | Columbia | 12/10/2011 | 02/08/2012 | ML12055A39 | <strong>Secondary Containment Low Differential Pressure due to Ice Buildup</strong><br /><i>Abstract:&nbsp;</i>On 12/10/11, secondary containment was declared inoperable due to differential pressure exceeding technical specification allowable limits for a period of approximately two minutes. While technical specification limits were exceeded the resulting excursion was bounded by analytical results and thus there were no safety consequences for this event. The cause for the event was determined to be ice buildup and subsequent release on exterior air filters supplying the reactor building HVAC system. Corrective actions will enhance standard operating procedures for cold weather operations to lower the threshold at which positive steps are taken to mitigate potential for icing on filters.
4002011001 | Harris | 04/12/2011 | 06/13/2011 | ML11172A12 | <strong>Containment Vacuum Relief System Inoperable for Greater Than Time Allowed by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On April 12, 2011, with the Harris Nuclear Plant at 100% power in Mode 1, CB-Z2SN, a safety-related tornado damper, was discovered stuck in the open position during a function test. The safety function is accomplished by two independent dampers in parallel. The north damper would not move from its open position which caused the Containment Vacuum Relief System to be inoperable. The seal clamping bar was found installed incorrectly which prevented the blades from being moved from the normal open position. This condition may have existed since May 1999 as a result of incorrectly performed maintenance on the damper which was not detected during periodic functional checks. This condition likely existed longer than permitted by technical specifications and is reportable under 10 CFR 50.73(a)(2)(i)(B). The root cause of this condition is inadequate procedure direction for testing and inspection of tornado dampers. Immediate corrective actions included the testing and repair of other tornado dampers. The corrective action to prevent recurrence is to establish a new Plant Operating Manual (POM) procedure for tornado damper maintenance and testing. There were no safety significant consequences as a result of this event.
4002011002 | Harris | 04/02/2011 | 02/20/2012 | ML12068A19 | <strong>Emergency Diesel Generator Inoperable due Mechanical Governor Speed Setting Drift</strong><br /><i>Abstract:&nbsp;</i>At 0840 on 12/20/11, at 100% power in Mode 1, the 1B-SB Emergency Diesel Generator (EDG) was declared inoperable due to drift of the speed setting for the mechanical governor. Drift of the mechanical governor speed setting over the seven-day mission time could result in the mechanical governor interfering with the ability of the electric governor to perform its design basis function for controlling EDG speed. The drifting of the speed setting was identified on April 2, 2011 but the impact of this condition relative to the 7-day mission time was not immediately recognized. The root cause was determined to be that technical guidance does not exist for adjustment of the speed adjusting motor to prevent shaft movement. The primary contributing cause was a failure to initially recognize that the 'B' EDG speed setting drift could adversely impact the 7-day mission time. Corrective actions were taken to revise the existing engine monitoring instructions to add a periodic check and adjustment of the speed setting during engine operation. Planned corrective actions include revising the maintenance procedure to prevent output shaft movement.
4102011001 | Nine Mile Point 2 | 04/01/2011 | 08/12/2011 | ML11237A03 | <strong>As-Found Safety Relief Valve Lift Setpoints Exceed Technical Specification Allowable Values</strong><br /><i>Abstract:&nbsp;</i>On April 1, 2011, Nine Mile Point Nuclear Station, LLC (NMPNS) determined that, based on the results of completed as-found testing, four (4) of eighteen (18) Main Steam Safety Relief Valves (SRVs) mechanically actuated at pressures that exceeded the allowable Technical Specification (TS) limit, which is the TS-specified setpoint plus or minus 3 percent. These 18 SRVs had been removed and replaced with pre-tested, certified SRVs during the 2010 Nine Mile Point Unit 2 (NMP2) refueling outage. NMP2 TS 3.4.4 requires the safety function of sixteen (16) SRVs to be operable in reactor operating modes 1, 2, and 3. Since the as-found testing determined that 4 of the 18 SRVs were inoperable for an indefinite period of time during the operating cycle that preceded the 2010 refueling outage, it is probable that NMP2 operated longer than the TS allowed Completion Time. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's Technical Specifications. The cause for the 4 SRVs exceeding the allowable as-found setpoint tolerance is attributed to inaccurate as-left lift pressure settings that resulted from the use of nitrogen as the test medium for SRV testing performed onsite prior to the 2010 refueling outage. Nitrogen testing of the NMP2 SRVs is no longer being performed. The SRV testing is now being conducted at an offsite test facility using saturated steam as the test medium.
4102011002 | Nine Mile Point 2 | 08/06/2011 | 10/05/2011 | ML11286A09 | <strong>Reactor Shutdown Due to Reactor Coolant System Unidentified Leakage Above Technical Specification Limits</strong><br /><i>Abstract:&nbsp;</i>At 0152 on August 6, 2011, the containment gaseous radiation monitors went into alarm and it was identified that Reactor Coolant System (RCS) unidentified leakage was increasing. At 0205, a Technical Specifications Condition was entered for RCS unidentified leakage increase above the specified limit. The RCS unidentified leakage peaked at 11.35 gpm, which resulted in an Unusual Event being declared due to reaching an Emergency Action Level (unidentified leakage greater than 10 gpm). At 0227, commenced lowering reactor power. Reactor power was reduced to 20% and, at 0941, the Reactor Protection System was manually actuated by placing the reactor mode switch in the Shutdown position. The unidentified leakage was due to a packing leak from the "A" RCS pump discharge blocking valve. The cause of the packing leak was determined to be vibration/turbulent flow that caused packing relaxation and failure. The valve packing was replaced, torqued and the gland follower nuts were secured in place. The packing for other similar valves was re- torqued and the gland follower nuts were secured in place. A Preventive Maintenance Surveillance Test (PMST) activity will be created to re-torque the packing for RCS pump blocking valves every two years. Additionally, a modification will be implemented to install a live loading design on the RCS pump blocking valves in an upcoming outage. There have been two other similar LERs involving RCS valve packing leakage: Nine Mile Point Unit 1 LER-2006-001 and Nine Mile Point Unit 2 LER-2001-007.
4102011003 | Nine Mile Point 2 | 08/11/2011 | 10/10/2011 | ML11293A04 | <strong>Reactor Shutdown due to an Unisolatable Leak on a Feedwater Pump Minimum Flow Line</strong><br /><i>Abstract:&nbsp;</i>On August 10, 2011 at 2200, during power ascension from an outage with the reactor operating at approximately 15% of rated thermal power, a leak was identified on a vent pipe connected to the minimum flow line for the "A" feedwater pump. At 0016 on August 11, the reactor was manually shut down due to the unisolatable leak on the feedwater pump minimum flow line. The leak was the result of a failed weld on the feedwater minimum flow line vent pipe due to vibration induced fatigue failure. The vibration increased due to two recent design modifications that affected the "A" feedwater pump minimum flow line. The potential for these design changes to increase vibration and adversely impact system operation had been identified, but was not anticipated to result in a failure of this type. Although the minimum flow piping had been evaluated and was being monitored, the small bore vent line had not been equally modeled or evaluated. The vent pipe was rewelded to the minimum flow line using an improved 2:1 weld profile and a pipe-to-pipe support was installed to make the pipe more robust and less susceptible to vibration.
4102011004 | Nine Mile Point 2 | 10/24/2011 | 12/23/2011 | ML12019A06 | <strong>Reactor Water Cleanup System Automatic Isolation Function Disabled During Troubleshooting</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2011, at 09:15, Nine Mile Point Unit 2 (NMP2) was operating at 100 percent of rated thermal power when the Division I reactor water cleanup system (RWCU) differential flow - high channel was declared inoperable due to failing its channel check. A troubleshooting plan was developed to determine the cause for the failed channel check. While performing the troubleshooting plan, at three separate times (October 24, 2011 at 01:52, 02:58, and 05:19), both the Division I and Division II RWCU differential flow timers were placed in bypass, and Technical Specification (TS) 3.3.6.1, Condition B was entered for one or more automatic functions with isolation capability not maintained. In each of the three instances, one channel of the RWCU differential flow - high function was restored to operable status within 1 hour as required by TS 3.3.6.1 Required Action B.1. In the morning of October 24, 2012 the oncoming crew recognized that bypassing both RWCU differential flow timers in this manner could have prevented the fulfillment of a safety function. The cause of this event was human performance error. The operating crew became focused on the completion time associated with the LCO condition and never fully evaluated the Technical Specification Bases. The crew involved in this event has been coached. An Operations department communication has been sent as a result of this event which reinforced the requirements of TS 3.0.2 Bases and the importance of an operating crew to use all available information with the Shift Manager as the single point of accountability. The RWCU system operating procedure has been revised to clarify the reportability requirements when removing both divisions of the RWCU high differential flow isolation from service. A training needs assessment has been initiated to determine if additional training is needed on TS Bases.
4122011001 | Beaver Valley 2 | 03/25/2011 | 05/19/2011 | ML11145A17 | <strong>Defective Fuel Injection Pump Supply Lines Provided by the Diesel Engine Manufacturer Results in an Emergency Diesel Generator Being Inoperable</strong><br /><i>Abstract:&nbsp;</i>At the time of discovery on March 25, 2011, during the Beaver Valley Power Station Unit Number 2 (BVPS-2) fifteenth Refueling Outage, BVPS-2 was in Mode 6 with all fuel loaded in the reactor vessel, the upper internals installed and approximately 23 feet of water in the reactor cavity. Both trains of the Residual Heat Removal (RHR) System were operable and one RHR train was in operation. At 0305 hours, the BVPS-2 Train A Emergency Diesel Generator (EDG) (2EGS-EG2-1) was returned to operable status following scheduled maintenance activities which included replacing the fuel injection pump supply lines to the fuel injectors. Within the following hour, the Train B EDG (2EGS-EG2-2) was placed on clearance for scheduled maintenance. At 1400 hours on March 25, 2011, the Train A EDG was declared inoperable, based on information from the manufacturer concerning the adequacy of the assembly method for the replacement fuel injector supply line compression fittings. Considering risk insights, site management determined that one EDG would be maintained available at all times during the restoration activities to restore a required EDG to operable status. Following successful surveillance testing, the BVPS-2 Train A EDG was declared operable at 0058 hours on March 27, 2011. With both EDGs inoperable, this event is reportable pursuant to 10 CFR 50.73(a)(2)(v)(D) as a loss of safety function for systems needed for accident mitigation. The event is also reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as an inadvertent operation/condition prohibited by the plant's Technical Specifications. Pursuant to 10 CFR 21.2(c), this report also satisfies the reporting requirements of 10 CFR Part 21. The direct cause is the ferrules were incorrectly swaged onto fuel injection pump supply lines as supplied by the vendor (Fairbanks Morse Engine). The root cause is the vendor (Fairbanks Morse Engine) design change control process was inadequate in that the design change made to the fuel injection pump supply lines incorporated the use of an unsuitable ferrule. Corrective actions included removal of the replacement fuel injection pump supply lines and reinstalling the previously removed fuel injection pump supply lines. The safety significance associated with the inadequate engagement of the EDG fuel injection pump supply lines compression fittings is considered very low.
4122011002 | Beaver Valley 2 | 04/09/2011 | 06/03/2011 | ML11159A16 | <strong>Auxiliary Feedwater System Vent Line Weld Crack Results in Technical Specification Required Plant Shutdown and Valid Reactor Protection System / Engineered Safety Feature Actuation System Actuations</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2011, Beaver Valley Power Station Unit No. 2 (BVPS-2) was in the process of power ascension near the end of the fifteenth refueling outage (2R15). BVPS-2 entered Mode 1 at 0931 hours. At approximately 2309 hours on April 9, 2011, a field operator identified an active leak on the 0.75 inch pipe nipple on vent valve 2FWE-940 located on the Auxiliary Feedwater System (AFW) "A" Steam Generator (SG) feedwater injection header. On April 9, 2011 at 2349 hours, the Shift Manager declared the "A" SG feedwater injection header inoperable due to the observed condition. Per Condition D of Technical Specification (TS) 3.7.5 "Auxiliary Feedwater (AFW) System, " BVPS-2 was required to be in Mode 3 within six hours and be in Mode 4 within 18 hours. During the plant shutdown, level in "A" SG was approaching the predetermined low level manual trip criterion point of 25 percent and a manual reactor trip was performed. The manual reactor trip was successfully completed without complications. The Reactor Coolant System (RCS) cooldown resulted in a shrink of level in the "A" SG and the steam driven AFW pump successfully automatically started on low-low SG level in the "A" SG. AFW flow was injected into SGs "B" and "C". Since the "A" SG feedwater injection header had been previously isolated to repair the pipe nipple leak, AFW flow injection to the "A" SG did not occur. A manual main steam line isolation (SLI) was initiated to limit RCS cooldown. These events are reportable per: 10 CFR 50.73(a)(2)(i)(A) due to a completion of a plant shutdown required by Technical Specification, per 10 CFR 50.73(a)(2)(v)(B) and (D) as an event that could have prevented the fulfillment of a safety function for systems needed to remove decay heat and to mitigate the consequences of an accident, and per 10 CFR 50.73(a)(2)(iv)(B)(1) as a Reactor Protection System manual actuation (manual reactor trip), and also as a valid Engineered Safety Feature Actuation System (ESFAS) automatic actuation of the AFW system per 10 CFR 50.73(a)(2)(iv)(B)(6) and manual actuation of the SLI system per 10 CFR 50.73(a)(2)(iv)(B)(2). The root cause of the branch line crack was determined to be less than adequate design guidance contained in the design process to prevent vibration induced high cycle fatigue failure of the pipe nipple associated with 2FWE-940. The root cause of the manual reactor trip and automatic start of the steam driven AFW pump event was determined to be that the shutdown procedure guidance was not adequate for RCS temperature control and steam generator level control at the beginning of life conditions. The safety significance associated with these events is considered to be very low.
4122011003 | Beaver Valley 2 | 06/10/2011 | 08/08/2011 | ML11224A01 | <strong>Automatic Actuation of Standby Service Water Pumps following Unexpected Service Water Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On June 10, 2011 at 1457 hours, Beaver Valley Power Station (BVPS) Unit No. 2 unexpectedly experienced a trip of the "A" Service Water Pump (2SWS-P21A) which was operating on the "A" Service Water System (SWS) pipe header. The pump tripped on motor over current. The "A" and "B" Standby Service Water System pumps (2SWE-P21A and 2SWE-P21B) automatically started on low Service Water header pressure on the "A" and "B" piping train headers and recovered pressure in both the "A" and "B" SWS headers. The downstream side of each SWS header is connected to each other via non-safety related cooling loads. The non-safety related loads are isolated on a containment isolation signal phase "A" or if a low pressure condition exists on the SWS header(s) for greater than 45 seconds. The "B" Service Water Pump (2SWS-P21B) continued to operate normally during this event supplying "B" SWS header. This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in an unplanned valid actuation of an emergency service water system per 10 CFR 50.73(a)(2)(iv)(B)(9) that does not normally run and that serves as ultimate heat sink. The unexpected trip of the BVPS Unit 2 Service Water Pump 21A was the direct cause for the automatic actuation of the BVPS Unit 2 Standby Service Water Pumps 21A and 21B. The reason for the unexpected trip of 2SWS-P21A was due to an over current condition in the motor which led to a motor trip. The safety significance associated with the over current trip of the running service water pump 2SWS-P21A that occurred at BVPS Unit 2 on June 10, 2011 is considered to be very low.
4132011001 | Catawba 1 | 02/26/2011 | 04/27/2011 | ML11119A14 | <strong>Technical Specification Violation Involving Notice of Enforcement Discretion Due to Failure of Diesel Generator Mechanical Governor</strong><br /><i>Abstract:&nbsp;</i>On February 26, 2011 at 0432 hours, Technical Specification (TS) 3.8.1, "AC Sources - Operating" and three supported system TS were violated when the 72-hour Completion Time for Diesel Generator (DG) 1B expired. TS 3.8.1, Condition B had been previously entered following a problem experienced with the DG mechanical governor during the conduct of its 24-hour run. On February 25, 2011 at 1655 hours, the NRC granted enforcement discretion concerning TS 3.8.1, Condition B and its supported system TS. The period of enforcement discretion began on February 25, 2011 at 1655 hours and was effective until February 28, 2011 at 0432 hours. DG 1B was subsequently returned to operable status on February 27, 2011 at 1454 hours. The most probable cause of the problem with the DG mechanical governor was that the mechanical governor speed setting drifted within the operating range of the primary electronic governor. A root cause evaluation was performed and two root causes were determined to have resulted in this event. These root causes and the resultant corrective actions are described fully in the body of this LER. Throughout this event, DG 1A was operable and capable of performing its required safety related function. Therefore, the health and safety of the public were not adversely affected by this event.
4132011002 | Catawba 1 | 04/23/2011 | 06/22/2011 | ML11178A09 | <strong>Safety System Actuation of Auxiliary Feedwater due to Feedwater Isolation During Unit Shutdown</strong><br /><i>Abstract:&nbsp;</i>On April 23, 2011 at 0921 hours, the Auxiliary Feedwater (CA) System was automatically actuated. This resulted from Main Feedwater (CF) being inappropriately isolated with the Unit in Mode 4 during the shutdown for a refueling outage. The Loss of Steam Generator (SG) Feedwater procedure was entered, and through the addition of CA, SG level was stabilized to normal levels. At 1026 hours CF was restored to service. This event was caused by the placement of a tagout prior to its scheduled execution time without fully recognizing its effect on plant operation. The tagout closed two CF valves which isolated all CF flow to the SGs. A root cause evaluation was performed and two root causes were determined to have resulted in this event. These root causes and the resultant corrective actions are described fully in the body of this LER. Throughout this event, the 1A Motor Driven Pump Train of the CA System was operable and performed its required safety related function. The CF system was subsequently restored, CA was secured, and the Unit was cooled down to Mode 5 where the CA System was no longer required. Therefore, the health and safety of the public were not adversely affected by this event.
4132011003 | Catawba 1, Catawba 2 | 12/15/2011 | 02/14/2012 | ML12052A00 | <strong>Technical Specification Required Shutdown of Unit 1 and Unit 2 and Associated Technical Specification Violation Involving Notice of Enforcement Discretion due to Two Inoperable Trains of the Control Room Area Chilled Water System</strong><br /><i>Abstract:&nbsp;</i>On December 15, 2011 at 1421 hours and 1422 hours, respectively, Unit 1 and Unit 2 entered Mode 3 to complete a Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 required shutdown due to both trains of the Control Room Area Chilled Water System (CRACWS) being inoperable. The primary cause of this event was failure of a microprocessor for the Train "B" CRACWS Chiller. Further testing is being conducted to determine the cause and support implementation of changes to improve the reliability of the microprocessor. Two additional causes identified include the 1) lack of procedures to replace the Train "B" microprocessor component within the allowable LCO 3.0.3 completion time and 2) insufficient maintenance procedural guidance for alignment of the chilled water pump. Corrective actions include developing a procedure to replace the microprocessor, and revising the procedure to provide additional detail for pump alignment. Throughout this event, all other plant safety related systems were capable of performing their required safety related functions.
4162011001 | Grand Gulf 1 | 03/19/2011 | 05/12/2011 | ML11132054 | <strong>High Pressure Core Spray (HPCS) Failure due to Failed Test Equipment</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2011 at 2236, with the plant operating at 96 percent power, the high pressure core spray (HPCS) pump was declared inoperable following the discovery of a degraded breaker that supplied power to the HPCS Minimum Flow Valve. The cause of the degraded breaker was the breaker's instantaneous overcurrent trip setpoint found out of tolerance during testing. The investigation of this event determined that the cause of the degradation was the result of a loss of power to a current calibrator installed for the performance of the HPCS System Flow Rate Low (Bypass) Functional Test. The loss of power caused repeated cycling of the valve and the resulting surge currents created excessive heat in the circuit breaker instantaneous trip and overload circuits. This degraded the instantaneous overcurrent trip setpoint which resulted in the breaker tripping at a setpoint that was out of tolerance. The breaker was replaced and the HPCS system was restored to its standby condition on March 20, 2011 at 0700. The functional test procedure was updated to require either new batteries to be utilized or the test equipment to be used with AC power. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as the loss of a system needed to mitigate the consequences of an accident. No other safety-related systems were out of service during the time that the HPCS system was inoperable. This event was of minimal significance with respect to the health and safety of the public.
4232011001 | Millstone 3 | 09/10/2011 | 11/07/2011 | ML11319A14 | <strong>Failure to Enter Technical Specification Action Statement</strong><br /><i>Abstract:&nbsp;</i>On September 10, 2011, while operating in MODE 1 at 100% power, Millstone Power Station Unit 3 (MPS3) identified that a value recorded on August 11, 2011, for the Bandpass Filter Offset Voltage for one channel of MPS3's Gamma Metrics wide range nuclear instrumentation 3NME*AMPL2 was left outside of the acceptance criteria defined in Surveillance Procedure SP3441E01. The condition was not noted on August 11, 2011, and the Technical Specification (TS) action statement was not entered. TS action statement 3.3.3.6 a (1) was entered upon discovery at 0025 on September 10, 2011. The surveillance procedure was successfully completed and the equipment was restored to operable status at 0425 on September 10, 2011. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's Technical Specifications. The cause of the failure was inadequate review of the calculated surveillance results. Subsequent to identification, further investigations revealed that the parameter was not necessary for operability of the equipment. The surveillance procedure has been revised to specify that measured offset voltage is not a TS acceptance criterion. Procedure changes being implemented will include independent reviews of calculated results on data sheets from l&C surveillances to ensure acceptance criteria are met prior to returning equipment to service.
4232011002 | Millstone 3 | 10/06/2011 | 11/28/2011 | ML11340A03 | <strong>Failure of Two Main Steam Safety Valves to Lift within the Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>With the plant in MODE 1 at 100% power on October 6, 2011, set pressure testing of Millstone Power Station Unit 3 (MPS3) Main Steam Safety Valves (MSSVs) was conducted per plant procedures. Two MSSVs, 3MSS*RV23B and 3MSS*RV22D, failed to lift within the +/- 3% acceptance criteria listed in Technical Specification (TS) 3.7.1.1. The failure of two MSSVs to lift within the required set pressure range is attributed to a corrosive oxide locking action between surface layer materials of the disc-seat interface, sometimes referred to as "oxide locking" or "microbonding." This cause is validated because the valves initially lifted above the required setpoint and subsequently lifted at lower pressures approaching the nominal lift setpoint. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by the plant's TS. Both valves were declared inoperable, and retested. All twenty MPS3 MSSVs were verified to be within + / - 1% of the lift setpoint. Valves are being replaced in accordance with a multi-year plan with seats containing materials less susceptible to microbonding. Additional corrective actions to address microbonding are being implemented in accordance with the station's Corrective Action Program.
4232011003 | Millstone 3 | 11/20/2011 | 01/18/2012 | ML12039A10 | <strong>Reactor Trip due to Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2011 at 1758 hours, during power ascension with Millstone Power Station Unit 3 (MPS3) in Mode 2, at 1.7 % reactor power, the operators manually tripped the reactor as required by procedure upon the loss of main condenser vacuum due to the loss of the auxiliary boilers supplying gland sealing steam. All control rods fully inserted into the reactor and all emergency systems functioned as designed. There were no radiological challenges as a result of the event. There were no detrimental effects to station equipment. No limiting safety system settings were exceeded. The operators responded properly to the loss of condenser vacuum and followed the correct procedure flow path. There were no deviations from the procedure guidance in effect. The auxiliary boilers were restarted, auxiliary steam, gland sealing steam, along with main condenser vacuum were re-established, the unit start-up recommenced and the unit placed in service. Additional corrective actions are being taken in accordance with the station's corrective action program. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual or automatic actuation of systems listed in 10 CFR 50.73(a)(2)(iv)(B).
4242011001 | Vogtle 1 | 04/20/2011 | 06/17/2011 | ML11168039 | <strong>Reactor Trip due to 1A Reactor Trip Breaker Opening</strong><br /><i>Abstract:&nbsp;</i>On April 20, 2011 with Unit 1 operating in Mode 1 at 100 percent rated thermal power at approximately 1734 hours Eastern Daylight Time, reactor trip breaker 1A unexpectedly opened. This initiated a turbine trip and subsequent trip of the 1B reactor trip breaker. Feedwater isolation occurred on low average reactor coolant system temperature and an auxiliary feedwater system actuation occurred on low steam generator level as expected. All rods fully inserted and the plant was stabilized in Mode 3. Extensive troubleshooting was performed to identify the cause of the 1A reactor trip breaker spuriously opening. However, the exact cause was not identified. Consequently, as a precautionary measure the reactor trip breaker, the under voltage driver card and shunt trip relay were all replaced. Additionally, recorders were installed to monitor voltages at various components in the breaker UV trip circuit in an attempt to identify the source of the spurious signal, should another trip occur.
4242011002 | Vogtle 1 | 08/31/2011 | 10/24/2011 | ML11298025 | <strong>Reactor Trip due to Main Feedwater Regulating Valve Maintenance</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2011 with Unit 1 operating in Mode 1 at 100 percent rated thermal power at approximately 0906 hours Eastern Daylight Time, the Unit 1 reactor automatically tripped. In preparation for maintenance on the controls for the main feedwater regulating valve (MFRV) on steam generator (S/G) 2, the valve was placed on an air gag. The air gag maintains the MFRV in position and allows minor changes in steam generator water level to be controlled by the bypass feedwater regulating valve (BFRV). However, shortly after the air gag was installed, feedwater flow to S/G 2 increased beyond the capability of the BFRV to control. The increase in feedwater flow to S/G 2 resulted in water level on S/G 2 exceeding the Hi-Hi nominal trip setpoint (NTS). This caused a main feedwater isolation, turbine trip and subsequent reactor trip in accordance with plant design. The cause of the event was due to increased air pressure being supplied to the MFRV when the valve was placed on the air gag. The first corrective action was revising the procedure to ensure calibrated test gauges are used to determine the pressure setting of the regulator for the air gag and for an operator to be present while the MFRV is controlled by the air gag. The second corrective action is to replace the contact type potentiometer used in the MFRV control circuit which has been proven unreliable.
4242011003 | Vogtle 1 | 09/19/2011 | 11/18/2011 | ML11333A13 | <strong>Control Room Air Damper Found Closed Results in Technical Specification Non-Compliance</strong><br /><i>Abstract:&nbsp;</i>On September 22, 2011 at approximately 0155 hours Eastern Daylight Time (EDT) as a System Operator entered the control room, he noted that the differential pressure across the door was not what he was accustomed to. The Unit Operator was notified and it was determined that the Control Room Normal HVAC (Heating, Ventilation, and Air Conditioning) Outside Air Damper, AHV-12153 was closed. With AHV-12153 closed, all air flow through the control room radioactive gas monitors is stopped, rendering them inoperable. After verifying that there was not a valid reason for the damper to be closed, AHV-12153 was opened restoring air flow through the control room radioactive gas monitors. A subsequent review of the plant computer shows that the damper closed on September 19, 2011 at approximately 2029 hours EDT. Because the Technical Specifications (TS) require the control room emergency filtration system (CREFS) to be placed in the emergency mode if the control room air intake radioactive gas monitors are inoperable for more than one hour, and this was not done, the units operated in a condition prohibited by the TS. An investigation into the cause for the damper to close was inconclusive. However, to preclude this event from happening in the future, a design change will be implemented to provide a control room annunciation to alert the operators of the condition.
4252011001 | Vogtle 2 | 10/10/2011 | 12/15/2011 | ML11350016 | <strong>Inoperable Core Exit Thermocouple Indicator on the B Train Remote Shutdown Panel</strong><br /><i>Abstract:&nbsp;</i>Following completion of refueling outage 2R15 and with the unit in Mode 1 at 100 percent rated thermal power, the B train quadrant 1 core exit thermocouple (CETC) indicator located on the B train shutdown panel was found to be inoperable during a scheduled surveillance test on October 27, 2011. The indicator is driven from a signal that is processed by the data processing unit (DPU). The algorithm in the DPU is set up such that it requires at least four B train CETCs in quadrant 1 to be functioning. Subsequent investigation determined that there were only three of eight B train CETCs in quadrant 1 that were functioning when the plant entered Mode 3 on October 10, 2011. Therefore the B train quadrant 1 CETC indicator which is required to be Operable in Modes 1, 2 and 3 in accordance with Technical Specification 3.3.4 had been inoperable from the time the unit had entered Mode 3. Consequently, this represented operation of the unit contrary to the requirements of Technical Specification LCO 3.0.4. To restore the B train quadrant 1 CETC indicator to Operable status, a Temporary Modification was implemented to reconfigure the leads on one of the five non-functioning B train quadrant 1 CETCs. The indicator was declared Operable on November 8, 2011 at 2154 hours Eastern Standard Time (EST) following satisfactory completion of the surveillance test.
4402011001 | Perry | 07/05/2011 | 08/23/2011 | ML11243A05 | <strong>Fire Protection Design Vulnerability Results in an Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2011, during a review for applicability of a 10 CFR 21 (Reporting of Defects and Noncompliance) notification, an original plant design deficiency was discovered. The deficiency resulted in the plant being vulnerable to a hot short in the unlikely event of a postulated control room fire, which could result in a loss of the capability to safely shutdown the plant. The identified deficiency was corrected utilizing temporary modifications to the plant that eliminated the potential for a control room fire to induce a hot short. The cause of the design deficiency was a latent design error that was made during plant construction and was not identified during the design review for 10 CFR 50 Appendix R Section III.G (Fire protection of safe shutdown capability). The corrective actions to address this condition include the design and implementation of a permanent plant modification to isolate the indication circuits in the unlikely event of a control room fire. A probabilistic risk assessment was performed for this condition and evaluated the condition to be of low safety significance. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety. Additionally, this report also constitutes a 10 CFR Part 21 notification.
4402011002 | Perry | 09/26/2011 | 02/08/2012 | ML12055A38 | <strong>Condition Prohibited by Technical Specifications and Plant Shutdown due to Unit 1 Startup Transformer Issues</strong><br /><i>Abstract:&nbsp;</i>On September 26, 2011, at 0158 hours, the unit 1 startup transformer was taken out of service to perform scheduled maintenance. The unit 2 startup transformer and the manual unit 1 backfeed lineup were OPERABLE and were considered to be the two qualified offsite circuits required by Technical Specifications (TS). Further review of this configuration determined that the backfeed lineup could not be credited as a qualified offsite circuit. This review also revealed that required TS actions were not completed when the startup transformer was declared inoperable on September 26, 2011. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as an operation or condition which was prohibited by the plant's TS. Transformer maintenance was secured and the unit 1 startup transformer was returned to service. Subsequently the transformer tripped due to an internal fault. On October 2, 2011, at 0100 hours, a planned shutdown was commenced to repair the unit 1 startup transformer. On October 2, 2011, at 1614 hours, plant shutdown was completed by manual actuation of the Reactor Protection System. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(A) for completion of any nuclear plant shutdown required by the plant's TS. Corrective actions for these events include approval of a License Amendment to clarify the use of a delayed access circuit as a qualified offsite circuit and installation of a replacement startup transformer. The safety significance of these events is considered to be small.
4402011003 | Perry | 10/18/2011 | 02/29/2012 | ML12072A08 | <strong>Switchyard Configuration During Startup Results in Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2011, at 0351 hours, the plant entered MODE 2 during plant startup. One of the two offsite power circuits required by Technical Specification (TS) 3.8.1, "AC Sources-Operating," was the delayed access circuit through the unit one auxiliary transformer. At 1619 hours, the manual disconnects for yard breakers S610 and S611 (isolation between offsite and onsite AC power distribution), were found to be open with danger tags installed. In this configuration, a TS Required Action was not performed within its designated Completion Time and a MODE change was made without satisfying the associated Limiting Condition for Operation (LCO). By 1730 hours, the danger tags were removed and the delayed access circuit was returned to OPERABLE status. Switchyard equipment configuration, necessary to maintain reliable sources of offsite power, was not held to the same operational configuration standards required for plant controlled equipment, due to less than adequate policies governing the plant's switchyard configuration cognizance. Corrective actions include completed and planned procedure revisions to ensure control room personnel are aware of switchyard configuration and training will be provided to appropriate plant personnel. The safety significance of this condition is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as any operation or condition which was prohibited by the plant's Technical Specifications.
4402011004 | Perry | 11/16/2011 | 03/15/2012 | ML12083A30 | <strong>Flooding Calculation Deficiency Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>On November 16, 2011, at 2000 hours, it was determined that internal flooding calculation JL-083 contained undocumented assumptions regarding operator actions required to isolate a postulated Service Water system piping Moderate Energy Line Crack in the Control Complex Building. The cause of this event was a calculation deficiency that credited operator actions to perform the appropriate system isolations without the actions being delineated in operating procedures. This deficiency existed since the original preparation and approval of the calculation (i.e., August 27, 1982). Corrective actions included development of procedural guidance to direct all required operator actions and installation of a temporary flood barrier. A permanent flood barrier will be installed in accordance with plant processes. A probabilistic risk assessment was performed and this condition was determined to have small safety significance. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(ii)(B) as a condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety.
4432011001 | Seabrook | 03/24/2011 | 05/20/2011 | ML11144A29 | <strong>Noncompliance with Technical Specification for Leakage Detection Instruments</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2011 during operation in mode 1 at 100% power, station personnel, while reviewing station documents, determined that one of the two containment gaseous radioactivity monitors did not meet the qualifications for a reactor coolant system leakage detection monitor required by the technical specifications (TS). The indication provided by the backup gaseous monitor did not meet the seismic requirements of Regulatory Guide (RG) 1.45, Reactor Coolant Pressure Boundary Leakage Detection Systems, and the monitor should not have been used to satisfy TS requirements. TS 3.4.6.1 requires a containment gaseous monitor and a particulate monitor. On several occasions, the plant operated with the normal particulate and gaseous monitors out of service and relied on the backup gaseous monitor to meet TS requirements. This situation resulted in a condition prohibited by the TS when plant operation continued with two inoperable leakage detection monitors for longer than the 6 hours permitted by the TS. No adverse consequences resulted from this event The cause of the condition was the design change that installed the backup monitor in the early 1990's did not qualify the monitor's indication to seismic requirements in accordance with RG 1.45. The condition was corrected in April 2011 by a design change that upgraded the gaseous monitor indication to meet seismic requirements.
4432011002 | Seabrook | 10/06/2011 | 12/02/2011 | ML11342A09 | <strong>Automatic Reactor Trip following Loss of Main Feed Pump</strong><br /><i>Abstract:&nbsp;</i>At approximately 1226 on October 6, 2011 with the plant operating in Mode 1 at 100% power, Seabrook experienced a plant trip on low steam generator water levels following loss of an operating main feed pump. The main feed pump tripped on low suction pressure while restoring a condensate pump to service following maintenance. During restoration of the pump, air entered the condensate system and caused a drop in condensate pump discharge pressure, which resulted in a low pressure condition at the suction of the main feed pump. The trip of the main feed pump on low suction pressure initiated a turbine setback; however, with reduced feedwater flow, steam generator levels decreased to the low level reactor trip setpoint. The automatic systems functioned as designed. The emergency feedwater system automatically actuated and recovered steam generator levels. No adverse consequences resulted from this event. The cause of this event was the lack of a procedure for restoring a condensate pump to service during operation at power. The corrective action revised the operating procedure to provide instructions for filling and venting a condensate pump following maintenance.
4432011003 | Seabrook | 12/21/2011 | 02/14/2012 | ML12052A25 | <strong>Offsite AC Source Inoperable During Diesel Generator Operation</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2011, during operation at approximately 65% power, station personnel identified a condition that previously rendered one of the offsite AC power sources inoperable. The plant design includes two independent offsite AC sources: (1) one circuit through the unit auxiliary transformers (UAT) to both trains of emergency buses, and (2) a second source through the reserve auxiliary transformers (RAT) to both trains of emergency buses. Offsite power is normally provided through the UAT, and the RAT supply is in standby. Operability of the RAT supply is contingent on the ability of the system to perform a fast transfer to the RAT supply upon opening of a UAT supply breaker. A review of the system design determined that when the emergency diesel generator (EDG) is operating in parallel with offsite power, the fast transfer feature to the RAT supply is unavailable, rendering this offsite AC source inoperable. On at least two occasions, this previously unrecognized condition rendered the offsite AC source inoperable for a period longer than permitted by the technical specifications. This event resulted from a failure to recognize the impact of EDG operation on the fast transfer feature. Operations issued guidance that the offsite AC source is inoperable during parallel operation of an EDG. No adverse consequences resulted from the event.
4452011001 | Comanche Peak 1, Comanche Peak 2 | 03/22/2011 | 01/30/2013 | ML13042A41 | <strong>Potential for Steam Voiding Causing Residual Heat Removal System Inoperability</strong><br /><i>Abstract:&nbsp;</i>In November 2009, Westinghouse issued Nuclear Safety Advisory Letter (NSAL) 09-8,"Presence of Vapor in Emergency Core Cooling System/Residual Heat Removal System in Modes 3/4 Loss-of-Coolant Accident Conditions." This NSAL clarified the guidance provided in a previous document, and was issued to ensure consideration of the significantly reduced elevation head present when the residual heat removal (RH) system supply is transferred from the refueling water storage tank (RWST) to the emergency core cooling system (ECCS) recirculation sump. An evaluation confirmed that the temperature limit currently applied at Comanche Peak to the RH system for alignment for shutdown cooling could result in flashing of liquids in the hot leg suction lines when the RH system suction is transferred to the RWST or the ECCS recirculation sump. The evaluation concluded that the RH temperature must be reduced to eliminate the potential for flashing of hot water within the isolated hot leg suction piping during transfer to the RWST or ECCS recirculation sump. On March 22, 2010, a review identified three occurrences (one on Unit 1 and two on Unit 2) in the past three years where both RH trains were placed into operation prior to reaching Mode 5 («/= 200 degrees F). Further review identified one additional occurrence on Unit 1 during 1RF14 on 4/3/10. The cause of this event was the failure to recognize the RHR system limitations necessary to support all modes of RHR operation (shutdown cooling, ECCS injection, and ECCS recirculation) without adversely impacting each other and the consequent failure to take steps necessary to preclude voiding in the RHR system under all postulated system operating conditions. Corrective actions included revising station operating procedures to prohibit both RHR pumps from being aligned in the Shutdown Cooling Mode with RCS temperature >= 200°F. There were no actual safety consequences impacting plant or public safety as a result of the event. All times in this report are approximate and Central Standard Time unless noted otherwise.
4452011002 | Comanche Peak 1 | 09/17/2011 | 11/16/2011 | ML11327A03 | <strong>Unit 1 Containment Personnel Airlock (PAL) Door Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 17, 2011, at 2330 hours, Operations personnel were unable to pressurize the Unit 1 Containment Personnel Airlock (PAL) during a routine performance of OPT-802A, "Appendix J Leak Rate Test of Personnel Air-lock Door Seals," which placed the PAL in an inoperable condition. Due to the time span, approximately 36 hours, since the Unit 1 PAL door had been operated and closed, a violation of Technical Specification LCO 3.6.2, "Containment Air Locks," occurred. The cause of this event was a piece of tape inadvertently attached to the sealing surface of the inner PAL door that prevented proper door sealing. This was due to insufficient controls in place to ensure that the PAL seals remained free of foreign material during modes 1 through 4 containment entries. Corrective actions included removal of the tape, satisfactory performance of OPT-802A, and procedure revisions to prevent recurrence. All times are in Central Daylight Time, unless otherwise noted.
4452011003 | Comanche Peak 1, Comanche Peak 2 | 10/18/2011 | 12/19/2011 | ML11363A17 | <strong>Unsuitable Material on Containment Airlock</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2011 Unit 1 was in Mode 5 for the 1RF15 refueling outage and Unit 2 was in Mode 1 at 100% power. At 1545 hours, an installed valve on the containment side of the Unit 1 personnel airlock hydraulic system was determined to have an aluminum body. Aluminum is a restricted/limited material in containment because it is not compatible with accident conditions. The aluminum valve body could potentially lose pressure integrity during a LOCA with containment spray actuation. Subsequently, on October 19 at 2002, two pressure gauges on the Unit 1 personnel airlocks and two pressure gauges on Unit 2 personnel airlocks, located inside the Reactor Containment Buildings, were also found to have an external epoxy coated aluminum casing and pressure boundary parts which have not been completely verified to be resistant to containment spray. The pressure gauges in all 4 airlocks have been isolated by closed ASME Class 2 isolation valves. The cause of this event was an inadequate design change for the airlocks. Corrective actions include encasing the personnel airlock hydraulic system valve inside containment to prevent exposure of the valve body to the sodium hydroxide in the containment spray and removing and replacing the airlock pressure gauges inside containment with stainless steel plugs. All times in this report are approximate and Central Time unless noted otherwise.
4462011001 | Comanche Peak 2 | 04/26/2011 | 06/27/2011 | ML11188A08 | <strong>Inoperability of ECCS Trains due to Gas Void</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2011, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 2 during a planned outage. At 0020, ultrasonic testing in support of Unit 2 Emergency Core Cooling System (ECCS) void verifications identified a void calculated to be approximately 3.71 ft3. Using conservative analytical methods at the time of discovery, the size and location of the void rendered both trains of the Containment Spray (CT), Safety Injection (SI), and Residual Heat Removal (RHR) systems inoperable requiring entry into Technical Specification 3.0.3. Limiting Condition for Operation Action Requirement (LCOAR) A2-11-231 was subsequently entered. The void was then vented via vent valve 2SI-8978 and the piping ultrasonically verified free of voids. LCOAR A2-11-231 was exited at 0143, April 26, 2011. The direct cause of this event was the introduction, transport, and accumulation of gases in the vicinity of 2SI-0047, resulting in a void of sufficient size that very conservative analytical methods used at the time of discovery determined the CT, SI, and RHR systems were rendered inoperable. Subsequent analysis of the event has shown that both trains of RHR and SI would have fulfilled their respective safety functions. However, the same analysis determined that one (1) train of containment spray would have been inoperable upon Unit 2 entry into Mode 4. Corrective actions include revision of the post-outage void verification program to require the conduct of preliminary void verifications at locations where potentially dual-train operability-affecting voids may form after entry into Mode 5 but prior to entry into Mode 4 and revision of STA-698 to include a requirement to periodically review fill and vent procedures to ensure all known gas intrusion mechanisms (e.g., pressure damming) are considered. In addition, vent valves 2SI-8978 and 1SI-0240 will be incorporated into the appropriate venting procedures. All times in this report are approximate and Central Daylight time unless otherwise noted.
4462011002 | Comanche Peak 2 | 05/19/2011 | 07/14/2011 | ML11203A07 | <strong>Unit 2 Manual Trip due to High Steam Generator Sodium Concentration</strong><br /><i>Abstract:&nbsp;</i>On 5/19/2011, at approximately 1407 hours, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was manually tripped due to high sodium concentration in all four steam generators. Unit 2 was operating at 100 percent power at normal operating temperature and pressure when chemistry instrumentation indicated a condenser tube leak. Steam generator sodium concentrations rapidly exceeded the manual trip criteria. All systems responded normally during and following the manual reactor trip. The leak from two condenser tubes was caused by a falling object impacting the tube exteriors. All tubes considered to have been susceptible to damage were examined by eddy current testing and visual exams. Leaking or damaged tubes were plugged and the unit was returned to 100 percent power once chemistry parameters were reestablished within limits. All times in this report are approximate and Central Standard Time unless noted otherwise.
4462011003 | Comanche Peak 2 | 06/21/2011 | 08/22/2011 | ML11243A04 | <strong>Unit 2 EDG 2-02 Inoperable due to Fuel Oil Leak</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2011, Unit 2 was in Mode 6 for the 2RF12 refueling outage. At 1130 hours, a 12 drop per minute (dpm) fuel oil leak was discovered on the Train B Emergency Diesel Generator (EDG 2-02). The leak was not corrected during 2RF12 because the leak was believed to be through the pipe threads, it did not constitute a structural failure, and the size of the leak did not affect the operability of EDG 2-02. On May 10, 2011, a 24-hour run of EDG 2-02 was commenced at 2304 hours per Technical Specification (TS) requirements. At the start of the run, the fuel leak was 12 dpm. Over the course of the run, the leak worsened, until at the 13-hour point it exceeded one liter per minute (1pm). EDG 2-02 was secured and declared inoperable at 1326 on May 11, 2011. Repairs were completed at 0425 hours on May 12, 2011 and EDG 2-02 was declared operable. The cause of the event was fatigue failure caused by long-term vibration stresses. Corrective actions included inspecting EDGs 1-01, 1-02, and 2-01, and no other leaks were identified. All times in this report are approximate and Central Time unless noted otherwise.
4462011004 | Comanche Peak 2 | 07/11/2011 | 09/09/2011 | ML11257A03 | <strong>Human Error Resulting in Inoperability of All Safety Injection Accumulators</strong><br /><i>Abstract:&nbsp;</i>Technical Specification (TS) Surveillance Requirement (SR) 3.5.1.5 requires that power be removed from the accumulator isolation valve motor operators when RCS pressure is above 1000 psig. On July 11, 2011, at approximately 1035 CDT, with Unit 2 in Mode 1 (Power Operations) at 100 percent power, TS 3.0.3 was entered when power was restored to all Safety Injection (SI) accumulator isolation valves while the Reactor Coolant System (RCS) pressure was at approximately 2235 psig. This condition resulted when a non-licensed operator who had been directed to operate equipment for Unit 1, which was being cooled down and depressurized in preparation for a mid-cycle outage, erroneously operated Unit 2 equipment. The incorrect operation of equipment on the wrong Unit was immediately recognized by the Unit 1 Reactor Operator and reported to the Unit 2 Reactor Operator. The Unit 2 Unit Supervisor declared all four Unit 2 SI Accumulators inoperable and entered TS 3.0.3. The Unit 2 Unit Supervisor directed a second non-licensed operator to re-open the breakers providing power to the Unit 2 SI Accumulator isolation valve motor operators and TS 3.0.3 was exited at 1115. The condition was caused by a personnel error. Corrective actions include reinforcement of station expectations regarding use of error reduction tools and issuance of an "Operations Human Performance Event Communication" regarding this event to all station managers and supervisors. All times in this report are approximate and Central Daylight Time unless noted otherwise.
4542011001 | Byron 1, Byron 2 | 01/05/2011 | 03/07/2011 | ML11066022 | <strong>Potential Loss of Residual Heat Removal System Safety Function in Mode 4 When Aligned for Shutdown Cooling due to Potential for Flashing or Voiding of Coolant During a Shutdown Loss of Coolant Accident</strong><br /><i>Abstract:&nbsp;</i>In November 2009, Westinghouse issued Nuclear Safety Advisory Letter (NSAL) 09-8, "Presence of Vapor in Emergency Core Cooling System/Residual Heat Removal System in Modes 3/4 Loss-of-Coolant Accident Conditions." This NSAL clarifies the guidance provided in a previous NSAL, and was issued to ensure consideration of the significantly reduced elevation head present when the residual heat removal (RH) system supply is transferred from the refueling water storage tank (RWST) to the emergency core cooling system (ECCS) recirculation sump. An evaluation confirmed that the temperature limit currently applied to the RH system for alignment for ECCS injection was sufficient when aligned to the RWST, but could result in flashing of liquids in the hot leg suction lines when the RH system is transferred to the ECCS recirculation sump. The evaluation concluded that the RH temperature must be reduced to eliminate the potential for flashing of hot water within the isolated hot leg suction piping during transfer to the ECCS recirculation sump. A review of operating logs identified three occurrences where both RH trains were placed into operation prior to reaching Mode 5 (</= 200 degrees F). The cause of this event was inadequate operating procedure temperature limits, which were based on technical error in the vendor communication. Corrective actions include implementation of a standing order for RH to address the new temperature limits for these conditions, revise the associated operating and emergency procedures to reflect the more restrictive temperature limits, and revise Technical Specification Bases 3.5.3, "ECCS - Shutdown," to reflect the new temperature limit. There were no actual safety consequences impacting plant or public safety as a result of the event.
4542011002 | Byron 1 | 03/19/2011 | 05/18/2011 | ML11138041 | <strong>Unit 1 Reactor Pressure Vessel Head Penetration Nozzle Weld Flaws Attributed to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>During the Byron Station Unit 1 spring 2011 refueling outage, Exelon Generation Company, LLC performed volumetric and surface examinations of the reactor Vessel Head Penetration (VHP) nozzles in accordance with 10 CFR 50.55a(g)(6)(ii)(D). Examination results identified flaws for VHP nozzles 64 and 76, as well as 31 and 43 that did not meet the applicable acceptance criteria and therefore required repair prior to returning the reactor head to service. Some of the flaws in VHF nozzles 31 and 43 were considered in the Reactor Coolant system pressure boundary region. The flaws were identified and repaired prior to through wall leakage occurring using an alternate weld overlay method in accordance with NRC approved Westinghouse WCAP-15987-P, Revision 2-P-A. The cause of the recordable indications is attributed to Primary Water Stress Corrosion Cracking (PWSCC). The frequency of Unit 1 reactor head penetrations examinations will be accelerated to each refuel outage and future preemptive repairs on VHPs nozzles that may be more susceptible to PWSCC will be evaluated. This condition had no actual safety consequences.
4542011003 | Byron 1, Byron 2 | 03/29/2011 | 05/31/2011 | ML11152001 | <strong>Drained Sections of Piping in Auxiliary Feedwater Suction Lines Result on System lnoperability due to Inadequate Technical Evaluation</strong><br /><i>Abstract:&nbsp;</i>In February 2011, the NRC questioned past evaluations relating to the auxiliary feedwater (AF) drained section of piping that existed between two suction valves in the essential service water (SX) system for each unit. The issue was entered into the Corrective Action Program for resolution. The space between the SX suction valves is intentionally drained and monitored for leak-by as an added measure to ensure raw SX water does not intrude into the AF system and challenge the integrity of the steam generator tubes, a fission product barrier. The pump vendor and the original design had maintained that this volume of air would pass through the AF pumps without damage. Actions were taken to fill the dry piping pending a re-analysis of the acceptability of the voids. At 2000 hours, on March 29, 2011, preliminary analysis results indicated the void fraction to reach the AF pumps would not meet the maximum void acceptance criteria. Consequently, Exelon Generation Company, LLC concluded that historically, when the voids existed, operability of the AF trains could not be sufficiently supported. The root cause of the event is in progress. A full-scale mock up of the AF system configuration is being tested and a risk assessment to determine the risk significance the AF pump suction pipe void is in progress and results will be reported in a supplement to this report.
4552011001 | Byron 2 | 11/17/2010 | 06/22/2011 | ML11173066 | <strong>Unit 2 Emergency Diesel Generator Inoperable for Longer than Allowed by Technical Specifications due to Inadequate Work</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2010, during a surveillance run, the Unit 2 "A" (2A) Emergency Diesel Generator (DG) was operating when the Equipment Operator (EO), assigned to monitor the 2A DG, identified a significant lubricating oil leak from the upper oil cooler. The EO tripped the DG by depressing the emergency stop pushbutton. The 2A DG was declared inoperable and Technical Specifications 3.8.1, "AC Sources - Operating" Condition B was entered. The oil leak source was determined to be coming from the upper lubricating oil cooler at the bolted flange connection between the cooler's shell and the stationary channel head. The as-found bolt torque values were found to be significantly less than the expected value of 110 foot pounds. It was determined the bolt loosening was caused by the torquing of another flange that was misaligned during 2A DG maintenance in January 2010. It was also identified that the Electric Power Research Institute (EPRI) provided recommendations for assembly of misaligned joints to prevent short term relaxation. This recommendation was not incorporated into the appropriate maintenance procedure for work on DG oil coolers. The cause was determined to be a lack of a formal process to ensure EPRI documents are systematically reviewed for good practices and then incorporated into maintenance procedures. Corrective actions include revising the maintenance procedure for assembly of bolted connections to incorporate the EPRI recommendations and revising the Operating Experience program to include EPRI documents. The 2A DG was restored to operable status on November 22, 2010.
4552011002 | Byron 2 | 10/13/2011 | 12/12/2011 | ML11346088 | <strong>Containment Pressure Not within Limits Longer than Allowed by Technical Specifications due to Personnel Error</strong><br /><i>Abstract:&nbsp;</i>On October 12, 2011, Operations personnel noticed Safety Injection (SI) containment pressure indications (wide range) exceeded Technical Specifications limits while the Containment Ventilation (VP) pressure indicator (narrow range) indicated pressure was within limits. The VP indicators are used to verify containment pressure is within Technical Specifications limits. This discrepancy was entered into the Corrective Action Program to investigate. On October 13, 2011, it was determined that the SI containment pressures were functioning correctly and the VP pressure indicator was non-functional. The appropriate Technical Specifications Condition was entered and containment pressure reduced to within limits. The cause of the non-functioning VP pressure indicator was due to instrument technicians inappropriately installing a foreign material exclusion (FME) cap over an external fitting of the inside containment pressure transmitter's housing during a recent calibration activity. This fitting is connected to the transmitter pressure sensing unit. The technicians failed to use the Maintenance Alteration Process correctly by installation of this FME cap when the Maintenance Alteration log did not indicate a FME cap was removed. Corrective actions include reinforcement of the requirement to use the Maintenance Alteration Process with Maintenance personnel and revising the inside containment pressure transmitter's calibration procedures to contain a warning that the external fitting on the transmitter's housing must remain open during plant operations.
4562011001 | Braidwood 1 | 02/25/2011 | 04/26/2011 | ML11116040 | <strong>Through Wall Crack on 1A Safety Injection Pump Discharge Line Due to Outside Diameter (Transgranular) Stress Corrosion Cracking Initiated at External Diameter of Pipe</strong><br /><i>Abstract:&nbsp;</i>On February 25, 2011, dried boric acid was identified on a 1A safety injection (SI) pump discharge line. At 1830 hours, upon receipt of the non-destructive examination results indicating a potential pressure boundary leak, the 1A SI train was declared inoperable, and Technical Specification Limiting Condition for Operation (LCO) 3.5.2, "Emergency Core Cooling Systems - Operating," Condition A was entered for one train inoperable. Following pipe replacement, on March 3, 2011, at 2028 hours, the system was returned to service and LCO 3.5.2 Condition A was exited. The apparent cause of the through wall crack is outside diameter (transgranular) stress corrosion cracking that initiated from the external surface of the pipe caused by chloride exposure. Corrective actions included replacing the portion of the SI line containing the flaw with new stainless steel pipe, and performing extent of condition walkdowns of portions of the SI discharge piping. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which is prohibited by the plant's Technical Specifications.
4562011002 | Braidwood 1 | 03/04/2011 | 05/03/2011 | ML11123061 | <strong>Loss of Unit 1 Train A Bus 141 Degraded Undervoltage Function</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2010, during execution of an undervoltage relay surveillance on Train A of the 4.16 kV Engineered Safety Feature bus 141, the as-found trip values of the A-to-B phase degraded voltage relay were found out of tolerance. The relay was replaced. An evaluation identified that the undervoltage relay had a manufacturing defect. A polarity sensitive capacitor was incorrectly installed with the polarity reversed. On March 4, 2011, a review of this evaluation was initiated to identify when the instrument out of tolerance occurred. Based on a review of this event against known conditions and trends, there was insufficient evidence to predict when the relay failure would have occurred, and no past surveillance history would indicate degraded conditions prior to the out of tolerance condition. Therefore the relay out of tolerance issue may have existed for a longer period of time than is allowed by the plant's Technical Specifications. Corrective actions included replacement of the degraded voltage relay. There were no actual safety consequences impacting plant or public safety as a result of the event. This event is reportable under 10 CFR 50.73(a)(2)(i)(B), any operation or condition which is prohibited by the plant's Technical Specifications.
4562011003 | Braidwood 1, Braidwood 2 | 03/29/2011 | 05/31/2011 | ML11151089 | <strong>Drained Sections of Piping in Auxiliary Feedwater Suction Lines Result in System Inoperability due to InadequateTechnical Evaluation</strong><br /><i>Abstract:&nbsp;</i>In February, 2011, the NRC questioned past evaluations relating to the auxiliary feedwater (AF) drained section of piping that existed between two suction valves in the essential service water (SX) system for each unit. The issue was entered into the corrective action program for resolution. The space between the SX suction valves is intentionally drained and monitored for leak-by as an added measure to ensure raw SX water does not intrude into the AF system and challenge the integrity of the steam generator tubes, a fission product barrier. The pump vendor and the original design had maintained that this volume of air would pass through the AF pumps without damage. Actions were taken to fill the drained section of piping pending a re-analysis of the acceptability of the voids. At 2000 hours on March 29, 2011, preliminary analysis results indicated the void fraction to reach the AF pumps would not meet the maximum industry accepted void fraction acceptance criteria. Consequently, Exelon Generation Company, LLC concluded that historically, when the voids existed, operability of the AF trains could not be sufficiently supported. Modifications were completed to include permanent vents to the AF drained sections of piping and the piping was filled and verified water solid. The root cause of the event is in progress. A full scale mock-up of the AF system configuration is being tested, and a risk assessment to determine the risk significance the AF pump suction pipe void is in progress and results will be reported in a supplement to this report.
4562011004 | Braidwood 1, Braidwood 2 | 11/01/2011 | 12/22/2011 | ML11357018 | <strong>Non-Conservative Historic Assumptions Identified in Turbine Building High Energy Line Break Analyses Result in Potential for Two Channels in a System to Become Inoperable</strong><br /><i>Abstract:&nbsp;</i>In March 8, 2011, errors were noted in calculations related to turbine building high energy line breaks (HELB), which can affect safety related equipment since some areas have ventilation connections to the turbine building. An operability evaluation was completed and determined that pre-evaluated compensatory actions that are included in the plant barrier impairment procedure may not be appropriate. The procedure was subsequently revised, revisions to the calculations were initiated, and a detailed engineering review was initiated in support of a review for past operability. On July 6, 2011, during a review associated with a revision to the HELB calculations to address the rollup door issue, it was identified that the assumed time delay for the fire dampers and rollup doors to close was not supported. The operability evaluation was subsequently revised to account for additional information, and the scope of the detailed engineering review expanded to include this new information. On November 1, 2011, following the completion of the detailed engineering review, a review of plant records for past operability identified instances where the HELB rollup doors to the rooms that contain one division of the instrument inverters were open. There were no actual safety consequences impacting plant or public safety as a result of the event. The cause of the event is indeterminate due to the time that has passed since the original analyses were performed. Corrective actions included revising the station plant barrier impairment procedure to remove the pre-evaluated compensatory actions for the applicable rollup doors, revising the calculations for the turbine building HELB analyses to reflect the actual plant design and door performance, and pursuing station modifications to improve design margins for room temperatures in the post turbine building HELB environments. This event is being reported in accordance with 10 CFR 50.73(a)(2)(vii) for any event where a single cause or condition caused at least two independent trains or channels to become inoperable in a single system designed to shut down the reactor and maintain it in a safe shutdown condition.
4572011001 | Braidwood 2 | 05/20/2011 | 07/19/2011 | ML11201017 | <strong>Asiatic Clam Shells in Essential Service Water Supply Piping to the 2A Auxiliary Feedwater Pump Resulted in Auxiliary Feedwater System Inoperability</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2011, Asiatic clam shells were found in the essential service water (SX) suction piping between the cross-tie valves 2AF006A and 2AF017A (SX, through these valves, provides a backup water source for the Train 2A auxiliary feedwater (AF) system in the event the normal water source for the AF system, becomes unavailable). On May 20, 2011, the evaluation of past operability concluded Train 2A of AF was not operable with this quantity of shells. The clam shells which were identified in the suction piping between the 2AF006A and 2AF017A valves had the potential to be transported through the 2A AF system and block flow through the AF flow control valves (2AF005A-D). The root causes for the event were determined to be: 1) Historical inadequate chemical feed biocide treatment of SX prevented the termination of Asiatic clam larvae, allowing Asiatic clams to grow in the low flow section of the SX header to 2A AF suction; and 2) Historical ineffective Problem Identification and Resolution associated with discoveries of Asiatic clam shells in the 2A AF suction allowed the condition to remain unanalyzed and uncorrected. Corrective actions include flushing the line between the 2AF006A and 2AF017A valves, revising the service water heat exchanger inspection guide to incorporate additional guidance on actions to be taken upon the discovery of macro fouling and biological fouling of NRC Generic Letter 89-13 systems, and revising the AF 1/2AF006A/B and 1/2AF017A/B valve stroke surveillance to clarify where and how to document the discovery of debris in the system. There were no actual safety consequences impacting plant or public safety as a result of this event.
4572011002 | Braidwood 2 | 07/14/2011 | 09/12/2011 | ML11263A18 | <strong>Auxiliary Feedwater System Inoperability due to Additional Asiatic Clam Shells in Essential Service Water Supply Piping</strong><br /><i>Abstract:&nbsp;</i>On July 14, 2011, relic Asiatic clam shells were found in the essential service water suction piping between the cross-tie valves 2AF006A and 2AF017A, which provides a backup water source for the 2A Train auxiliary feedwater (AF) system. At 1418, Technical Specifications Limiting Condition for Operation (LCO) 3.7.5, "Auxiliary Feedwater (AF) System," Condition A, "One AF train inoperable" was entered for the 2A AF train. Additional flushing of the suction piping was performed, and at 1151 on July 16, 2011, the 2A AF train was declared operable and the LCO exited. The apparent causes for the event were: 1) Failure to perform a complete borescope inspection of the piping to verify no additional relic clam shells remained in the 2A AF suction piping from a May 9, 2011 event (reference LER 2011-001); and 2) Inadequate flushing techniques to remove shells from the 2A AF suction allowed for a significant amount of clam shells to remain in the system. Corrective actions taken included flushing of the 2A AF suction piping between the 2AF006A and 2AF017A valves using improved flushing techniques, performing a complete borescope inspection of the 2A AF suction piping for remaining clam shells, and completion of the extent of condition flushing activities for the 1A, 1B and 2B AF trains. There have been two similar Licensee Event Reports in the past three years: Unit 2 2008-001 and Unit 2 2011-001.
4582011001 | River Bend | 01/20/2011 | 03/21/2011 | ML11087091 | <strong>Unplanned Actuation of Standby Service Water System due to Procedure Inadequacy</strong><br /><i>Abstract:&nbsp;</i>At 2:34 p.m. CST on January 20, 2011, while the plant was in a refueling outage, standby service water (SSW) pump "C" started automatically during system realignment. The Division 1 SSW subsystem (pumps "A" and "C") was being started to facilitate maintenance on the normal service water system. When the "A" pump was manually started, the pressure transient caused by the realignment of the motor-operated valves in the system caused a momentary low system pressure, actuating SSW pump "C" automatically. This event resulted from a weakness in the operating procedure, in that the intended system configuration for this operation exceeded the flow capacity for one pump. Actions are being taken to strengthen this and other similar procedures to prevent recurrence. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as a condition that resulted in the automatic actuation of the "C" SSW pump.
4582011002 | River Bend | 02/13/2011 | 04/14/2011 | ML11109A00 | <strong>Operations Prohibited by Technical Specifications Due to Instrument Isolation Valve Mispositioning</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2011, at approximately 5:00 a.m. CST, during power ascent following a refueling outage, operators found that one channel of main turbine first stage pressure instrumentation was not responding to changing plant parameters. This instrument provides a permissive to the reactor protection system (RPS) to enable a reactor scram signal from main turbine control valve control valve fast closure and main turbine stop valve closure. Also enabled by that permissive is a reactor recirculation pump trip signal initiated by the main turbine stop valve closure. While performing the initial troubleshooting, a maintenance technician discovered that a valve at the affected steam pressure transmitter was closed, isolating it from the system. This valve had apparently been left closed following the calibration of the instrument during the outage. The valve was opened, and the instrumentation channel was declared operable at 5:52 p.m. that day. The signals enabled by this pressure transmitter are required to be operable when reactor power is greater than 40 percent. Reactor power had exceeded 40 percent at approximately 3:24 a.m. that day. This event is being reported as operations prohibited by Technical Specifications in accordance with 10CFR50.73(a)(2)(i)(B).
4582011003 | River Bend | 12/23/2011 | 02/21/2012 | ML12059A09 | <strong>Automatic Reactor Scram due to a Main Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On December 23, 2011, at approximately 6:10 a.m. CST, the main turbine tripped unexpectedly, resulting in a reactor scram. The plant was stable at 100 percent power at the time of the event, and no safety-related systems were out of service. Operators implemented the appropriate response procedures, and began to stabilize reactor vessel pressure and water level. The closure of the turbine control valves resulted in the actuation of at least fifteen of sixteen main steam safety relief valves. A subsequent high reactor water level caused a trip of all three reactor feedwater pumps. As reactor water level lowered back through the normal operating range, operators attempted to restart a feedwater pump, but component malfunctions were encountered on "B" and "C" pumps. The reactor core isolation cooling (RCIC) system was manually actuated approximately nine minutes after the scram and injected water into the reactor for approximately two minutes. The "A" feedwater pump was restored to service approximately one minute after RCIC was initiated. The cause of the turbine trip was a spurious backup over-speed trip resulting from an electrical discharge from the turbine shaft in the vicinity of the EHC turbine speed pickup probe. The cause of the electrical discharge was due to a failure of the shaft grounding system. The plant responded as designed, and no emergency core cooling system actuation setpoints were exceeded. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in the automatic actuation of the reactor protection system (RPS).
4612011001 | Clinton 1 | 02/08/2011 | 04/06/2011 | ML11109A00 | <strong>Postulated Spurious High Pressure Core Spray Initiation Result Unanalyzed</strong><br /><i>Abstract:&nbsp;</i>On 2/8/11, Engineering reviewed the current off-normal procedural methodology for closing the High Pressure Core Spray (HPCS) injection valve in lieu of opening the pump breaker. The review identified the HPCS system could be postulated to spuriously initiate due to concurrent fire induced hot short cable damage to the two automatic initiation logic instrument cables routed in the same raceway. In this event, the reactor pressure vessel (RPV) would fill and flood the Main Steam Lines because shorting would prevent HPCS pump shutdown and shutting the injection valve. In response to the continuing HPCS injection, Main Steam Safety Relief Valves (SRVs) would lift after RPV pressure reaches the SRV setpoint and RPV water would be discharged through the SRVs and downcomers to the suppression pool. This would result in high pressure, high temperature water discharge through SRVs, which would flash to two phase flow. SRVs and associated downcomers have not been analyzed in the current design basis for stresses expected due to two-phase flow at high pressure. The cause of this event is failure to follow a procedure that required engineering review of the revised off-normal procedure. Corrective actions include briefing procedure writers on procedure requirements, reviewing selected procedures, and completing a transient and stress analysis of high pressure two-phase SRV discharge flow.
4612011002 | Clinton 1 | 05/23/2011 | 07/22/2011 | ML11216A13 | <strong>Main Control Room HVAC Return Fan B High Vibrations</strong><br /><i>Abstract:&nbsp;</i>On 5/23/11, Operators in the Main Control Room (MCR) noticed a change in noise levels originating from ventilation equipment outside the MCR. Investigation revealed the increased noise was from the MCR (VC) B Return Fan. Vibration readings on the fan assembly were in the alert range, but not in the shutdown range. Vibration readings were taken over an 8-hour period after the increase in vibration was noted. During that time, vibration levels remained constant. All other MCR Ventilation parameters for the VC B train were normal and unchanged. After this run, VC B train was placed in standby and VC A train was placed in service. An operability evaluation was completed for VC B which concluded VC B was operable. On 6/7/11, an inspection of the fan was performed. The inspection identified a crack in the fan hub. A new fan was installed and the system was restored to an operable status on 6/10/11. The fan hub was sent offsite for failure analysis, which concluded that the crack was the result of end-of-life fatigue, caused by low stress, high cycle loading. Analysis concluded that the hub assembly could not support the ability of the fan to perform its specified safety function over the designed mission time of 30 days, and thus the fan was inoperable. The VC A system was operable during this period; therefore, no loss of safety function occurred during the period of inoperability.
4612011003 | Clinton 1 | 08/31/2011 | 10/13/2011 | ML11293A04 | <strong>Inadequate Procedure Direction Results in Missed Response Time Testing</strong><br /><i>Abstract:&nbsp;</i>On 8/31/11, with the plant in Mode 1 at 97 percent power, a system manager identified that incomplete post maintenance testing (PMT) had been performed following replacement of Turbine Control Valve (TCV) Fast Closure Pressure Switches 1C71N005A, 1C71N005B, and 1C71N005C. Response Time Testing required by Technical Specification (TS) Surveillance Requirement (SR) 3.3.1.1.17 was not identified in the work order and thus not performed as a PMT for the affected channels of the three pressure switches prior to declaring the channels operable. Further investigation identified that Response Time Testing was subsequently performed for each of the affected channels with acceptable results during subsequent refueling outages. This testing provides reasonable assurance that the affected channels would have performed their safety functions following replacement of the pressure switches. The cause of this event was inadequate procedural guidance provided to the work planner to identify the Response Time Testing requirement. Corrective actions include revising the PMT procedure to indicate that a Response Time Test must be considered when replacing a pressure switch and revising the Model Work Orders for TCV Fast Closure Pressure Switch Replacement to include the required Response Time Testing PMT.
4612011004 | Clinton 1 | 11/29/2011 | 01/12/2012 | ML12031A14 | <strong>Automatic Reactor Scram During Removal of Main Generator</strong><br /><i>Abstract:&nbsp;</i>On November 29, 2011, with the reactor at 16.1 percent thermal power, Operators were reducing generator load to 50 Megawatts in order to trip the Main Turbine to start refueling outage C1R13. Turbine Bypass Valve (BPV) #1 had begun opening and was approximately 8 percent open when it ramped closed contrary to system demand. A Steam Bypass Control Pressure Regulator error alarm was received in the Main Control Room. Due to the loss of the steam flow path through the bypass valve to the Main Condenser, Reactor Pressure Vessel (RPV) pressure began to increase and subsequently reached the high reactor pressure scram setpoint resulting in an automatic reactor scram. Reactor pressure control was established manually utilizing the Steam Bypass Valve opening jack. Troubleshooting determined that BPV #1 closed due to failure of a Bypass Valve Demand (BVD) card in the Steam Bypass and Pressure Control (SBPC) System causing RPV pressure to increase. The cause of this event is attributed to the failure to replace or refurbish the BVD card prior to it failing. Corrective actions include replacement of both the A and B BVD cards, establishment of periodic preventive maintenance for the cards, and performing an extent of condition review for other cards in the SBPC system.
4612011005 | Clinton 1 | 12/01/2011 | 01/24/2012 | ML12039A15 | <strong>Missed Surveillance due to Preconditioning Valve prior to Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2011, with the reactor shut down for refueling, an as-found Local Leak Rate Test (LLRT) was performed for Reactor Core Isolation Cooling turbine exhaust check valve 1E51-F040. The station primary containment leakage rate testing program which implements the requirements of 10 CFR 50, Appendix J, requires an as-found test to be performed prior to a scheduled maintenance activity to open and inspect the valve. The recorded leakage for the as-found LLRT was within acceptable limits. A step in the test procedure establishing the test lineup required the valve to be stroked open and shut by normal means. A subsequent evaluation concluded that the pre-test stroking was unacceptable preconditioning; therefore, the as-found LLRT was invalid and considered to be a missed surveillance and a condition prohibited by Technical Specification 3.6.1.3. The test procedure incorrectly required the preconditioning and caused this event. Corrective actions include revising the test procedure and reviewing other similar check valve test procedures to determine the extent of this condition. An analysis to determine the actual impact of the valve stroke concluded that the preconditioning, although unnecessary to establish the test conditions, would have had little actual influence on the as-found test results.
4612011006 | Clinton 1 | 12/07/2011 | 01/26/2012 | ML12039A10 | <strong>Condition Prohibited by Technical Specifications due to Failed Missed Surveillance</strong><br /><i>Abstract:&nbsp;</i>On December 7, 2011, Clinton Power Station (CPS) was in Mode 5 (Refueling) for refueling outage C1 R13. During leakage testing of Reactor Coolant System Pressure Isolation Valve (PIV), 1E12-F042C, Low Pressure Coolant Injection from Residual Heat Removal C Shutoff Valve, was performed in accordance with Technical Specification (TS) Surveillance Requirement (SR) 3.4.6.1. This test was performed in accordance with SR 3.0.3 to address a missed surveillance that was discovered on April 7, 2011. During the test, the valve would not pressurize due to the amount of water passing through the seat at low pressure. The test pressure for the surveillance test is 1000 to 1025 pounds per square inch gauge. Since the valve would not pressurize, the leakage was determined to be in excess of the specified leakage criteria of five gallons per minute and was declared an as-found failure. The valve repair team identified wear on the guide ribs and excessive disc to rib clearances, which appeared to be original dimensional tolerances rather than recent wear. Engineering determined the cause of the as-found failure was that the disc became cocked during closing causing the valve to not fully seat. Corrective actions included repairing the valve and retesting the valve with satisfactory results.
4612011007 | Clinton 1 | 12/08/2011 | 01/27/2012 | ML12053A09 | <strong>Unfused DC Ammeter Circuits Result in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>During a Clinton Power Station (CPS) review of an event at the Browns Ferry Station (ENS 47374), CPS determined that the original plant wiring design for the station battery ammeter circuits contains a shunt in the current flow from each direct current (DC) battery. Bolted onto the shunt bar are two Institute of Electrical and Electronics Engineers (IEEE) IEEE-383 qualified leads to an ammeter in the main control room (MCR). The small difference in voltage between the two taps on the shunt is enough to deflect the current meter in the MCR when current flows from the battery through the shunt. The ammeter wiring attached to the shunt does not have fuses, and if one of the ammeter wires shorts to ground at the same time another DC wire from the opposite polarity on the same battery also shorts to ground, a ground loop through the unfused ammeter cable could occur. With enough current going through the cable, the potential exists that the overloaded ammeter wiring could damage safe shutdown wiring in direct physical contact with the cable resulting in a loss of the associated safe shutdown function/capability. The cause of this deficiency is the original design criteria not specify protection for shunt fed ammeter circuits. A modification is planned to correct the deficiency. Compensatory measures have been established until the modification has been installed.
4612011008 | Clinton 1 | 12/18/2011 | 08/06/2012 | ML12229A04 | <strong>Reactor Protection System Actuation and Loss of Shutdown Cooling</strong><br /><i>Abstract:&nbsp;</i>On 12/18/11, the plant was in Cold Shutdown conducting restoration activities following the Reactor Pressure Vessel (RPV) hydrostatic pressure test. While lowering RPV water level to a target level, a low RPV water level (Level 3) reactor protection system actuation occurred resulting in a residual heat removal (RHR) system isolation, and a subsequent loss of shutdown cooling. RPV water level was immediately restored above the Level 3 setpoint using the control rod drive system. Operators reset the RHR isolation logic within minutes of the scram signal, and shutdown cooling was fully restored in 26 minutes. Reactor coolant temperature increased approximately three degrees Fahrenheit during this event. The causes of this event were lack of rigorous process controls while removing and installing the permanent shutdown and upset level instruments reference leg pipe and not having an alternate for shutdown range level indication to allow monitoring reactor water level during times when the shutdown and upset level instruments are not in service. Corrective actions include revising the procedure to control the entire evolution of shutdown and upset level instruments reference leg pipe reassembly and recovery of vessel level indication, and developing an alternate method for determining RPV level during shutdown conditions.
4612011009 | Clinton 1 | 12/01/2011 | 04/11/2012 | ML12110A08 | <strong>Missed Surveillance due to Preconditioning Valve prior to Leak Rate Test</strong><br /><i>Abstract:&nbsp;</i>On December 1, 2011, with the reactor shutdown for refueling outage, an as-found Leak Rate Test (LRT) was performed for Residual Heat Removal "A" Reactor Pressure Vessel Isolation check valve 1E12-F041A. In accordance with the station reactor coolant system pressure isolation valve testing program this as-found test was required to be performed. The recorded leakage for the as-found LRT was not within acceptable limits due to the testing sequence of other system valves unseating 1E12-F041A prior to testing. Following performance of procedure CPS 9053.05, RHR/LPCS Valve Operability (Shutdown), which stroked the valve with no additional closing force applied, the as-left LRT was completed with satisfactory results. On February 13, 2012, during review of the performance of the LRT, a question arose regarding if stroking of the valve was acceptable preconditioning. A subsequent evaluation of this activity concluded that stroking of the valve was unacceptable preconditioning. February 13, 2012, is used as the discovery date for this LER based on a review of the performance of the LRT that questioned if the valve was preconditioned prior to as-found testing.
4822011001 | Wolf Creek | 01/03/2011 | 04/09/2011 | ML11109A05 | <strong>Potential for a CVCS Through-Weld Leak to Affect Reactor Coolant System Inventory After a Loss of Coolant Accident</strong><br /><i>Abstract:&nbsp;</i>At 1551 on January 3, 2011 with the plant at 100 percent power in Mode 1, operators identified a 300 drop-per-minute leak from a weld on a three-quarter-inch connection that joined a four-inch line in the Chemical Volume and Control System (CVCS) to a vent-valve assembly. A through-weld crack caused the leak and the weld was repaired on January 4, 2011. The vent-valve assembly was installed on October 24, 2009 during Refueling Outage 17. Operations initiated a reportability evaluation on January 5, 2011 to determine whether this event should be reported as a condition prohibited by technical specifications under 10 CFR 50.73(a)(2)(i)(B). Wolf Creek Nuclear Operating Corporation (WCNOC) determined on March 26, 2011 that this event was not required to be reported under 10 CFR 50.73(a)(2)(i)(B) because this failure would not prevent the CVCS from fulfilling the high-pressure safety injection (HPSI) function. However, on April 1, 2011, based on questioning by a Nuclear Regulatory Commission inspector during an In-Service Inspection, it was determined that WCNOC did not address the extent to which the CVCS leak would impact Reactor Coolant System (RCS) inventory after a Loss of Coolant Accident. WCNOC is currently evaluating this issue.
4822011002 | Wolf Creek | 02/22/2011 | 04/25/2011 | ML11123A16 | <strong>Diesel Generator Declared Inoperable Due to Inadequate Installation of a Fuel-Rack Control Pin</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2011, with the plant at 100 percent power in Mode 1 and the "A" Diesel Generator (DG) in stand-by condition, a Wolf Creek Nuclear Operating Corporation (WCNOC) engineer on a system walk down identified that a control pin on the fuel rack for the "A" DG was not completely inserted and not secured by a washer and cotter pin in accordance with the design. The "A" DG was declared inoperable at 1537 Central Standard Time (CST) on February 22, 2011 and returned to service at 0520 CST on February 23, 2011 after the control pin, washer and cotter pin were properly installed. The "B" DG and both offsite circuits were operable while the "A" DG was inoperable on February 22 and 23, 2011. The "A" DG may have been inoperable from 0200 CST on December 3, 2010, when it was removed from service for planned maintenance, to 0520 CST on February 23, 2011. Evaluations are in progress to determine the root cause of this event and the impact of an incorrectly installed fuel-rack control pin on diesel generator operation.
4822011003 | Wolf Creek | 03/12/2011 | 05/12/2011 | ML11139A15 | <strong>Diesel Generator Declared Inoperable Due to Inadequate Reinstallation of Pipe Connection Resulting in Excessive Governor Oil Coolant Leak</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2011, with the plant at 100 percent power in Mode 1, a jacket water cooling system leak was identified during the performance of procedure STS KJ-011A, "EDG NE01 24 Hour Run." Procedure STS KJ-011A is performed to satisfy Technical Specification Surveillance Requirement 3.8.1.14, endurance and margin test. A leak in excess of the 9.1 ml/min limit resulted in declaring the "A" diesel generator (DG) inoperable at 0419 Central Daylight Time (CDT). Performance of procedure STS KJ-011A commenced on March 11, 2011 at 1300 CDT. The "A" DG was returned to service at 1815 CDT on March 12, 2011 after the leaking threaded pipe connection supplying the "A" DG governor oil cooler was reassembled. The "B" DG and both offsite circuits were operable while the "A" DG was inoperable on March 12, 2011. The "A" DG may have been inoperable from December 2, 2010 to March 12, 2011, when the inlet pipe connection to the governor oil cooler had not been properly reinstalled after being removed to support a foreign material inspection during the 7 day DG maintenance outage.
4822011004 | Wolf Creek | 03/19/2011 | 12/28/2011 | ML12004A16 | <strong>Automatic Safety Injection Actuation due to Operating Crew Failure to Follow Procedures</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2011 at 0000 Central Daylight Time (CDT), the unit was taken offline for the start of a refueling outage. At 0404 CDT with the plant in Mode 3, while opening the "C" main steam isolation valve (MSIV), a safety injection (SI) actuation and steam line isolation occurred. A momentary large steam flow and pressure drop were observed in the affected steam generator. The pressure drop was rapid enough to actuate all three rate-sensitive low steam generator pressure bistables based on rate alone, with the lowest steam pressure still well above the setpoint. The low steam generator pressure bistables cleared prior to MSIV closure. Control room operators utilized procedure EMG E-0, "Reactor Trip or Safety Injection," at the initiation of the event and EMG ES-03, "SI Termination," to terminate the SI. The SI and steam line isolation resulted in actuation of both trains of Emergency Core Cooling Systems. The steam line isolation signal closed the only open MSIV. Both diesel generators started and operated in standby mode without tying to the engineered safety features busses. All control rods were previously inserted as part of the controlled shutdown; however, the SI actuation resulted in opening of the reactor trip breakers. Operator action terminated the SI into the Reactor Coolant System (RCS) prior to pressurizer overfill at 0411 CDT.
4822011005 | Wolf Creek | 04/30/2011 | 06/29/2011 | ML11188A01 | <strong>Procedure Weakness Allowed Entry into Mode 6 with One Source Range Monitor Inoperable</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2011, during Refueling Outage 18, fuel was being loaded into the reactor vessel and the plant changed from a defueled condition to Mode 6. As the second fuel assembly was loaded next to source range detector SEN0031, the detector did not respond. Core alterations were suspended. A pulse shaper card required for source range detector operation had failed on April 14, 2011, and the failure was not detected at that time. The failed pulse shaper card was replaced later on April 30, 2011, and SEN0031 was declared operable and fuel loading resumed. The cause of the event was a procedural weakness in procedure STS CR-002, "Shift Log for Modes 4, 5, and 6," which did not require plant operators to check the operability of the source range detectors using the plant computer prior to loading fuel. All applicable surveillance requirements were met using instrumentation located in the control room, but those meters would not indicate an inoperable source range detector before fuel was loaded. Corrective action has been initiated to revise applicable procedures to direct the operator to check the plant computer before entering Mode 6 to ensure both source range channels are operable.
4822011006 | Wolf Creek | 05/24/2011 | 07/25/2011 | ML11214A21 | <strong>Auxiliary Feedwater Actuation due to Operators Inability to Control Steam Generator Level in Mode 4</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2011 at 1120 CDT, Wolf Creek Generating Station (WCGS) was in Mode 4 during a startup at the end of Refueling Outage 18. A reactor trip signal, a Feedwater Isolation Signal actuation and an Auxiliary Feedwater actuation occurred due to a Lo-Lo Steam Generator level. Steam Generator levels were being maintained at 30 - 35% level in anticipation of full flow auxiliary feedwater testing which would increase the steam generator levels. The cause of the event was inadequate operator control of steam generator levels. Remedial training was conducted for the control room staff. The safety significance of this event is low. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report Section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
4822011007 | Wolf Creek | 06/26/2011 | 08/24/2011 | ML11244A07 | <strong>Manual Reactor Trip due to Failed Controller Cards in the 'B' Feedwater Pump Turbine Control System</strong><br /><i>Abstract:&nbsp;</i>On June 26, 2011, Wolf Creek Generating Station (WCGS) was at 82 percent power during a reactor startup when the 'B' Main Feedwater pump tripped at 1609 CDT. The control room operators manually tripped the reactor. All control rods fully inserted and the Reactor Trip System and the Engineered Safety Feature Actuation System performed as expected. The cause of the trip was the failure of one or both of two controller cards in the Main Feedwater turbine control system. Two controller cards in the main turbine control system were replaced. The safety significance of this event is low. This event is bounded by analyses as reported in the WCGS Updated Safety Analysis Report Section 15.2.7, "Loss of Normal Feedwater Flow." There were no adverse effects on the health and safety of the public.
4822011008 | Wolf Creek | 07/20/2011 | 09/19/2011 | ML11270A09 | <strong>Post-Fire Safe Shutdown Latent Desiqn Issue May Cause Essential Service Water System Flow Imbalance</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2011 at 1313 CDT, during a review of the post-fire safe shutdown analysis for valve EFHV0060, "ESW Return from CCW Heat Exchanger," a condition was discovered where a fire in the Control Room could cause valve EFHV0060 to open. Valve EFHV0060 is required to be closed for post-fire safe shutdown when operating Train "B" essential service water (ESW). The opening of EFHV0060 would cause a flow imbalance in the ESW system and could reduce the ESW flow to other essential components. The direct cause is a latent design deficiency that did not ensure that valve EFHV0060 was isolated/protected from the potential effects of a Control Room fire. An hourly fire watch was in place in the Control Room and will remain in place until this issue is resolved. Procedure OFN RP-017, "Control Room Evacuation," was revised to include interim compensatory actions to deenergize, and verify closed, valve EFHV0060. A plant modification will be implemented to resolve the PFSSD issue with EFHV0060.
4822011009 | Wolf Creek | 08/14/2011 | 01/20/2012 | ML12031A13 | <strong>Inadequate Oil Analysis Causes Inoperable Auxiliary Feedwater Pump Longer than Allowed Outage Time</strong><br /><i>Abstract:&nbsp;</i>On 8/11/2011 at 1145 CDT the turbine driven Auxiliary Feedwater (AFVV) pump was declared inoperable due to oil sample results that indicated a high particulate count in the turbine lube oil system. The cause of the condition was determined to be residual quantities water, dirt, wear and oxide particles found after an inadvertent addition of Fyrquel to the system in March 2011. The lube oil system was drained, flushed and filled multiple times followed by oil sample testing to determine particulate content. On 8/14/2011, Wolf Creek Nuclear Operating Corporation requested a Notice of Enforcement Discretion (NOED) to extend the Completion Time for the turbine driven AFW pump an additional 24 hours. The NRC granted the approval of the NOED on 8/14/2011. A Technical Specification required shutdown was initiated on 8/15/2011. The turbine driven AFW pump was returned to operable status on 8/15/2011 and the plant was returned to full power. Procedure I-ENG-004, "Lubricating Oil Analysis," was revised on 12/07/2011 to specify the actions to take when oil sample results reach alert levels and to strengthen oil sample processing controls. An evaluation is in progress to confirm that the turbine driven AFW pump was capable of performing its specified safety function from 3/11/2011 to 8/11/2011.
4822011010 | Wolf Creek | 09/01/2011 | 10/31/2011 | ML11312A05 | <strong>Diesel Generator Declared Inoperable Due to Inadequate Adjustment of the Diesel Generator Governor</strong><br /><i>Abstract:&nbsp;</i>On September 1, 2011, during the performance of procedure STS KJ-005A, "Manual/Auto Start, Sync and Loading of EDG NE01," the kilowatt (kW) output, current output and the fuel racks oscillated excessively at full load on the "A" Diesel Generator (DG). The peak-to-peak oscillations in kW output observed in the Control Room were 300 to 400 kW. The "A" DG was declared inoperable at 1443 Central Daylight Time (CDT) on September 1, 2011. The cause of the oscillations was due to an adjustment made to the "A" DG governor in May 2011. The governor was restored to its previous adjustment and the "A" DG was returned to service at 1032 CDT on September 4, 2011. The "B" DG and both offsite circuits were operable while the "A" DG was inoperable from 1443 CDT on September 1, 2011 through 1032 CDT on September 4, 2011. Further evaluation of this event is in progress and includes determining whether the "A" DG was capable of performing its specified safety function from May 21, 2011 through September 4, 2011.
4822011011 | Wolf Creek | 11/03/2011 | 01/03/2012 | ML12018A24 | <strong>Inadequate Analysis Assumptions Resulting in Deficient Control Room Evacuation Procedure</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2011, during the 2011 Triennial Fire Protection Inspection, it was determined that procedure OFN RP-017, "Control Room Evacuation," had two deficiencies. For a postulated fire in the control room, the procedure does not adequately protect the steam generators from overfill and does not adequately protect the pressurizer from filling to above 100% indicated water level, possibly causing the primary system to go solid. The direct cause of the event is an inadequate analysis assumption translated into procedure OFN RP-017. When the event scenarios supporting OFN RP-017 were developed, the engineers who worked on the Post Fire Safe Shutdown analyses did not fully consider the potential adverse effect of automatic functions and improperly credited closure of the main steam isolation valves from the control room. Procedure OFN RP-017 was revised to provide compensatory measures that would prevent overfill of either the steam generators or the pressurizer.
4832011004 | Callaway | 07/20/2011 | 09/16/2011 | ML11259044 | <strong>Post-Fire Safe Shutdown Latent Design Issue with Essential Service Water (ESW) Flow Balance</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2011, during a review of the post-fire safe shutdown analysis for valve EFHV0060, "ESW Return from CCW B Heat Exchanger," a condition was discovered where a fire in the control room could cause valve EFHV0060 to open. Valve EFHV0060 is required to be closed for post-fire safe shutdown when operating the "B" essential service water (ESW) train. The opening of EFHV0060 would cause a flow imbalance in the ESW system and could reduce the ESW flow to other essential components. The direct cause is a latent design deficiency that did not ensure that valve EFHV0060 was isolated/protected from the potential effects of a Control Room fire. An hourly fire watch was put into place in the control room and will remain in place until this issue is resolved. Procedure OTO-ZZ-00001, "Control Room Inaccessibility," was revised to include interim compensatory actions to de-energize, and verify closed, valve EFFIV0060. Callaway Plant is in the process of transitioning its Fire Protection Program to NFPA 805, "Performance-Based Standard for Fire Protection for Light Water Reactor Electric Generating Plants, 2001 Edition," pursuant to 10 CFR 50.48(c). The request to transition to 10 CFR 50.48(c) was submitted to the NRC on August 29, 2011 via letter ULNRC-05781. Implementation of the provisions of NFPA 805 is considered the final corrective action for this issue.
4832011005 | Callaway | 10/24/2011 | 12/20/2011 | ML11355011 | <strong>Manual Isolation Valve Unable to Meet Closure Requirements</strong><br /><i>Abstract:&nbsp;</i>On October 24 and 27, 2011, atmospheric steam dump manual isolation valve ABV0040 was operated in preparation for B steam generator maintenance. During both of these events, more than 20 minutes were required to stroke ABV0040 closed. This exceeds the response time required in a postulated steam generator tube rupture (SGTR) event concurrent with a loss of offsite power and a failed-open atmospheric steam dump valve (ASD). In such a scenario, the affected atmospheric steam dump line is credited to be isolated within 20 minutes of ASD failure. The failure of ABV0040 to close within the required time was caused by the presence of hardened grease within the valve actuator. This hardened grease was the result of a lack of preventative maintenance to replace grease in the valve actuator. The site failed to develop a maintenance/testing program for the ASD isolation valves to ensure that they could be stroked closed to meet the time requirement in the Safety Analysis. Corrective actions for this event include the implementation of preventative maintenance to replace the grease in the ASD manual isolation valve actuators and procedure changes to periodically verify that the ASD manual isolation valves can be closed in a time that supports SGTR event response.
4832011006 | Callaway | 11/09/2011 | 01/06/2012 | ML12009016 | <strong>Postulated Fire Could Damage High Density Polyethylene (HDPE) Essential Service Water Piping</strong><br /><i>Abstract:&nbsp;</i>On 11/09/2011, Callaway Plant staff determined that the effects of a postulated design basis fire hazard in Control Building Room 3101 could potentially damage High Density Polyethylene (HDPE) piping in the Essential Service Water (ESW) system. In this scenario, fire-induced damage to the HDPE sections of a single train of ESW piping could cause Room 3101 to flood in excess of previously analyzed flood levels. Such a flood could adversely affect valves in redundant trains that function to realign ESW during a fire and the assumed concurrent loss of offsite power. The root cause of this condition was attributed to human performance error during development of a modification to replace sections of steel piping with HDPE piping in the ESW system. Specifically, personnel developing this modification did not effectively evaluate the failure modes of the HDPE piping installed in Room 3101. Following identification of this condition, an hourly fire watch was implemented in accordance with the Callaway Plant fire protection program. Corrective actions include implementation of additional management oversight of the design process to ensure Failure Mode and Effects Analysis quality and effective use of subject matter experts. The configuration of HDPE piping described herein will be analyzed and submitted to the NRC staff as part of Callaway Plant's transition to 10 CFR 50.48(c).
4832011007 | Callaway | 11/13/2011 | 01/10/2012 | ML12010053 | <strong>Inadvertent Non-Compliance With TS 3.9.2, Unborated Water Source Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>Per Technical Specification (TS) 3.9.2, all unborated water source isolation valves that are connected to the Reactor Coolant System must be secured in the closed position to prevent unplanned boron dilution of the reactor coolant during Mode 6. While the plant was in Mode 6 on 11/13/2011, one of the valves used to isolate an unborated water source was found to be closed but was not secured in that position. The valve was in this condition when the plant entered Mode 6 from "No Mode," but this was not identified until after subsequent completion of loading fuel into the reactor vessel. The plant entered Mode 6 on 11/07/2011. No core alterations were in progress when the valve was found to be unsecured. Having the valve closed but not secured during Mode 6 (and without meeting the Required Actions of Condition A under LCO 3.9.2) is a condition prohibited by the TS. After the valve was found to be unsecured, the valve was secured in the closed position. Additionally the reactor coolant system boron concentration was verified to be within TS limits. Procedure OSP-BL-00001 did not include adequate instructions to control the status of valve BGV0601 in "No Mode." Plant procedures will be revised to clarify the administrative guidance. Additionally, operations personnel were coached on requirements for procedure compliance.
4982011001 | South Texas 1, South Texas 2 | 04/30/2011 | 05/03/2012 | ML12135A21 | <strong>Technical Specification Requirement Not Met Regarding Unborated Water Sources</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2011, South Texas Project (STP) Unit 1 was in refueling outage 1RE16, with the unit in Mode 5, Reactor Coolant System loops not filled. In support of a planned evolution to transfer water from the 1B Recycle Holdup Tank (RHT) to the Volume Control Tank, a Senior Reactor Operator (SRO) assigned to review atypical plant conditions during the outage identified a potential dilution source that was not included in the plant surveillance procedure used to confirm compliance with Technical Specification 3.4.1.4.2 regarding unborated water sources. Although the valves were not secured closed as required by TS, the valves were closed and no dilution occurred. Technical Specifications were revised in 2003 to remove references to specific valves required to be isolated with respect to unborated water sources and replaced with more generic language. However, the impact of using the RHT as a fill source was not adequately addressed with respect to compliance with the new TS requirements, and thus the surveillance procedure used to ensure compliance did not address all unborated water sources. Because the same TS, plant procedures, and administrative controls applied to both units, Unit 2 was similarly affected. The corrective action was to revise the plant surveillance procedure used by both Units to ensure compliance with TS 3.4.1.4.2 and TS 3.9.1 to reflect the additional valves that must be secured in the closed position to comply with the TS. This corrective action was implemented in accordance with the STP Corrective Action Program. There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this event. This event did not have an adverse effect on the health and safety of the public.
4992011001 | South Texas 2 | 05/05/2011 | 09/06/2011 | ML11255A19 | <strong>Exceeding ESF Bus Voltage Technical Specification Surveillance Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 14, Class 1E 4.16 kV Bus E2B was declared inoperable due to load center (LC) voltage being greater than Engineering Safety Features (ESF) Power Availability surveillance procedure acceptance criteria. Per the Integrated Computer System (ICS), Class 1E 4.16 kV ESF Bus E2B was inoperable longer than allowed by Technical Specifications. The associated ESF buses were inoperable longer than allowed by Technical Specifications. Therefore, this condition is reportable as a condition prohibited by Technical Specifications. The Root Causes are: 1) the range of voltage allowed by the bandwidth of the Load Tap Changers (LTC) on the Unit AuxiliaryTransformer and the ESF B Transformers was not conservatively modeled; 2) The Failure Modes and Effects Analysis (FMEA) for the ESF Transformer LTC was inadequate; and 3) Management oversight did not have a method to identify, classify, control and monitor highly complex modifications. The associated corrective actions are as follows: 1) Develop and issue an electrical design calculation methodology guideline or procedure; 2) Develop and issue a guideline or a procedure for completing a Failure Modes and Effects Analysis and 3) Define complex modifications in the design change procedure including defining the requirements for management oversight over providing adequate resources, development of project schedules, and ensuring site involvement in reviews of project documents. There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
4992011002 | South Texas 2 | 11/29/2011 | 01/30/2012 | ML12037A06 | <strong>Unit 2 Reactor Trip on Main Generator Lockout</strong><br /><i>Abstract:&nbsp;</i>On 11/26/11 at 2121 hours, Unit 2 received the Stator Coil Water (SCW) Differential Temperature high alarm. The crew determined generator thermocouple T6144 on the SCW outlet of Coil 33T was reading higher than the other thermocouples. l&C Technicians conducting a local check subsequently reported the Coil 33T thermocouple was reading within the differential temperature band. On 11/27 multiple Generator Condition Monitoring (GCM) alarms were received. The operating crew subsequently removed the Coil 33T thermocouple from service by substituting a known value. At 0310 on 11/29/11 a Stator Cooling Water trouble alarm was received. The Unit 2 Reactor tripped at 0329 hours on 11/29/11 due to Main Generator Lockout. An initial inspection of the main generator revealed significant stator coil damage. Approximately three feet of stator Coil 33T (top coil in slot 33) was melted or missing on the exciter end. The failure analysis determined the most likely cause was a very small leak in a hollow strand in Coil 33T. Analysis supports that this leak existed for a long time and allowed moisture to travel inside the coil. The moisture degraded the resin in the coil allowing the conductor bundle to come loose. This condition allowed some individual conductor strands to move and vibrate. The strand-to-strand vibrations wore away the insulation and created shorts. The shorts caused excessive heating. The affected area grew due to thermal damage until the coil arced across the missing melted area. The potential exists that the small leak was located in the portion of the coil that is melted/missing. If so, it will not be possible to ascertain the root cause of the leak. After the final failure analysis reports are received, the root cause report and LER will be evaluated and revised if warranted. This condition is considered reportable under 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph 10 CFR 50.73(a)(2)(iv)(B). There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
4992011003 | South Texas 2 | 11/30/2011 | 01/30/2012 | ML15211A02 | <strong>Unit 2 Plant Mode Change with Turbine Trip Disabled</strong><br /><i>Abstract:&nbsp;</i>On November 20, 2011 at 0546 hours [CST], STP Unit 2 transitioned modes from Mode 4 to Mode 3. Prior to the mode change, the Solid State Protection System (SSPS) generated turbine trip signals were defeated by a maintenance work activity that installed a jumper in both channels (Train R and S) of non-class relays to the turbine trip circuit. The SSPS signals to the non-class relays that were defeated by the jumpers included the turbine trip from reactor trip breakers open (P-4), turbine trip from a reactor trip signal (P-16), and the turbine trip from Steam Generator HI-HI (P-14). In accordance with Technical Specification (TS) 3.3.2 Item 5a and 5b, P-4 and P-14 are required in Modes 1, 2, and 3. The jumpers were removed around 0930 on November 20, 2011 with U2 still in Mode 3. Since Unit 2 had changed Modes from 4 to 3 with TS 3.3.2 Item 5a and 5b and the associated Limiting Conditions of Operation (LCO) Actions not met, this is a condition prohibited by Technical Specification 3.0.4. A review of the performance of this activity in previous outages was conducted. It was identified that a similar event had occurred during 2RE14 in April of 2010. This event, including the one in April 2010, was reported as required by 10 CFR 50.72(b)(3)(v) parts (C) and (D). <br /><br /> The Cause of the event was determined to involve the revision of the associated maintenance work activity's Preventive Maintenance Instruction (PMI). Specifically, the MODE requirement prerequisites in the PMI were revised without full consideration of the Operational restrictions associated with changing plant conditions during procedure performance. The corrective action to prevent reoccurrence includes removing the mode restrictive steps of the associated PMI while adding them to the 7300 Protection System Channel Trip Function Bypass procedure.<br /><br /> There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public.
5282011001 | Palo Verde 1, Palo Verde 3 | 02/21/2011 | 08/03/2012 | ML12228A38 | <strong>Unit 1 and Unit 3 Emergency Diesel Generator Actuation on Loss of Offsite Power to Class 4.16kV Bus</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2011, at approximately 2001 Mountain Standard Time, a valid actuation of the circuitry that starts the emergency diesel generators (EDG) for Palo Verde Nuclear Generating Station Unit 1 train 'B' and Unit 3 train 'A' occurred due to an undervoltage condition on their respective 4.16 kV safety buses. Both EDGs started and loaded as designed. The loss of power to the Unit 1 and Unit 3 safety buses was the result of a protective relay actuation on the AE-NAN-X02 startup transformer which de-energized the transformer and the Unit 1 13.8 kV intermediate bus 1E-NAN-S06 and the Unit 3 13.8 kV intermediate bus 3E-NAN-S05. The affected intermediate buses provide offsite power to the Unit 1 safety bus 1E-PBB-S04 and the Unit 3 safety bus 3E-PBA-S03 respectively. The cause of the undervoltage was a cable splice failure on the cable for the 'Y' winding of the AE-NAN-X02 startup transformer. Unit 1 and Unit 3 entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, Condition A, for one required offsite circuit inoperable. Offsite power was restored to Unit 1 safety bus through the intermediate bus from the alternate supply. Offsite power was restored to Unit 3 safety bus through the intermediate bus from the alternate supply. The LCO condition was exited by Unit 1 and Unit 3. No similar events involving a cable splice failure have been reported by PVNGS in the last three years.
5282011002 | Palo Verde 1 | 06/29/2011 | 09/11/2012 | ML12258A37 | <strong>Nonconforming Condition Renders the Qualified Safety Parameter Display System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 1, 2011, at approximately 15:30 Mountain Standard Time, both trains of the Qualified Safety Parameter Display System (QSPDS) were declared INOPERABLE when it was discovered that the 120 volt class power supply cables to the A and B train QSPDS display modems did not meet the physical separation criteria per Regulatory Guide 1.75 contained in the PVNGS Installation Specification for Cable Splicing and Terminations 13-EN-0306. Accordingly, Conditions A and C of Technical Specification Limiting Condition for Operation (LCO) 3.3.10, Post Accident Monitoring (PAM) Instrumentation, were entered. On July 3, 2011, at 16:05, Conditions A and C of Technical Specification LCO 3.3.10 were exited after the power supply cables to the A and B train QSPDS display modems were rerouted per work order instructions to meet the physical separation criteria. The root cause of this event was inadequate adherence to cable separation criteria during modification and maintenance activities which led to the installation of power supply cables for the A and B train QSPDS display modems with less than six inches of physical separation. To prevent recurrence, the maintenance work order writer's guide was revised to require that cable separation criteria be incorporated into Main Control Board (RM) work instructions. In the past three years, PVNGS has not reported a similar event of nonconformance to Regulatory Guide 1.75.
5282011003 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/13/2011 | 01/17/2012 | ML12072A11 | <strong>Control Room Essential Filtration Misalignment Resulting in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2011, control room essential filtration system (CREFS) outside air intake (OSA) dampers were found to be in the normally closed position instead of the normally open position stipulated in the updated final safety analysis report. This incorrect configuration was the result of procedure changes made in 1986. Each train of the CREFS system contains two OSA dampers in series, with each damper actuated from one of the two separate channels of the control room essential filtration actuation signal (CREFAS). Upon identification, Unit 1 and Unit 3 entered Technical Specification (TS) 3.3.9, condition A when both channels of CREFAS were determined to be inoperable. In response, both units placed an OPERABLE train of CREFS into operation per required action A.1. Unit 2 was defueled and irradiated fuel assemblies were not being moved; therefore, TS 3.3.9 was not applicable to Unit 2 at the time this condition was identified. In the three years prior to this event, a similar legacy issue was reported in which station procedures directed system configurations not permitted by the plant design (LER 0500528/529/530/2009-001-00, Safety Injection System Recirculation Alignment Results in Unanalyzed Condition).
5282011004 | Palo Verde 1 | 08/06/2011 | 10/05/2011 | ML11291A01 | <strong>Unit 1 Reactor Trip Due to Reactor Protection System Actuation which Resulted from a Dropped CEA</strong><br /><i>Abstract:&nbsp;</i>On August 6, 2011, at approximately 1119 Mountain Standard Time, during the performance of surveillance test 40ST-9SF01, Control Element Assembly (CEA) Operability Checks, the Unit 1 reactor tripped due to an automatic actuation of the reactor protection system. The actuation occurred when CEA 37 of shutdown group B fully inserted causing a deviation of greater than 9.9 inches from other CEAs in its subgroup. This deviation generated a CEA calculator penalty factor and actuated the low departure from nucleate boiling ratio and the high local power density trips on all four core protection calculator channels. Following the reactor trip, plant operators observed CEA 16 of regulating group 5 did not indicate that it had fully inserted. While operators prepared to borate the reactor coolant system, full insertion indication for CEA 16 was received approximately 1.5 minutes following the reactor trip. The cause for the reactor trip was determined to be a loose terminal lug on the CEA power switch assembly which developed a high resistance connection and led to the improper operation of the control element drive mechanism upper gripper coil. As an immediate corrective action, the terminal lug was replaced and retested satisfactorily. Troubleshooting of CEA 16 did not identify any problems. Unit 1 returned to service and entered Mode 1 at 2140 on August 10, 2011. No similar conditions have been reported by Palo Verde in the past three years.
5282011005 | Palo Verde 1 | 11/22/2011 | 06/21/2012 | ML12193A09 | <strong>Unit 1 Manual Reactor Trip due to Slipped Control Element Assemblies</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2011, at approximately 1925 Mountain Standard Time, during the performance of post-refueling low power physics testing, the Unit 1 reactor was manually tripped as required by the control element assembly (CEA) malfunction abnormal operating procedure after a subgroup of four CEAs slipped greater than 6.6 inches. An intermittent failure of a power switch assembly (PSA) which provides electrical power to the control element drive mechanisms (CEDMs) resulted in the CEA slippage. After troubleshooting was completed, the power switch assembly was replaced. Retesting was completed on November 24, 2011. The root cause was determined to be latent organizational weaknesses with the modification and corrective action processes that delayed installation of automatic CEDM timer modules (ACTMs) which would minimize the occurrence of dropped or slipped CEAs. The corrective action to prevent recurrence is to install the ACTM modification during subsequent refueling outages in each of the units. This modification was successfully installed in Unit 3 during the 16th refueling outage completed in April, 2012. LER 50-528/2011-004-00 reported a prior similar event.
5292011001 | Palo Verde 2 | 04/08/2011 | 06/07/2011 | ML11168A06 | <strong>Irradiated Fuel Movement with Misaligned Control Room Essential Filtration System</strong><br /><i>Abstract:&nbsp;</i>At 1803 on April 8, 2011, during reactor core offload for the 16th Unit 2 refueling outage, Unit 2 entered Technical Specification Limiting Condition for Operation (TS LCO) 3.3.9 when the Control Room Essential Filtration Actuation Signal (CREFAS) was declared inoperable due to both Control Room intake radiation monitors being out of service. Irradiated fuel movement was allowed to continue due to an incorrect understanding that the already in-service Control Room Essential Filtration System (CREFS) "B" train air handling unit fulfilled the required action of the LCO. At 2140, the Outage Shift Manager entered the Control Room and noted that the Control Room was not fully pressurized and questioned whether the required actions of LCO 3.3.9 were met. At that time, the Control Room staff recognized that required dampers had not been closed. Re-alignment of the dampers was completed at 2146 to comply with the required actions of the LCO. The root cause was imprecise terminology in LCO 3.3.9 Required Action C.1, which did not specify that CREFS shall be placed in the essential filtration mode required for post-accident emergency alignment. A License Amendment Request will be submitted to provide more specific direction in LCO 3.3.9 regarding alignment of CREFS. The station has not reported any other TS 3.3.9 violations in the past three years.
5292011002 | Palo Verde 2 | 05/02/2011 | 07/23/2012 | ML12220A35 | <strong>Inoperable Steam Generator Low Pressure Reactor Trip and Main Steam Isolation Signal Channels</strong><br /><i>Abstract:&nbsp;</i>On May 5, 2011, at approximately 01:53, Unit 2 was in Mode 3 and preparing for entry into Mode 2 at the completion of its 16th refueling outage. Prior to Mode 2 entry, the Channel A setpoint for Steam Generator (SG) #1 Low Pressure (SGLP) Reactor Trip and Main Steam Isolation Signal (MSIS) was found to be 950.4 pounds per square inch absolute (psia), which is below the allowable value, greater than or equal to 955 psia, required by Technical Specifications (TSs) 3.3.2 and 3.3.5 for the reactor trip channel and the MSIS channel, respectively. The setpoint for those channels had been at the discovered value since approximately the time Unit 2 had reached normal operating temperature on May 2, 2011. Upon identification, SG #1 SGLP Channel A was placed into bypass as required by the TSs. Subsequently, the SGLP setpoint was adjusted to a value above 955 psia, the channel was taken out of bypass, and was declared operable at 17:19 on May 5, 2011. The cause of the event was procedural inadequacies. Station procedures did not require verification of SGLP bistable setpoints after completion of outage activities and prior to plant conditions requiring them to be OPERABLE in Mode 3. Corrective actions included the establishment of procedure requirements to verify the plant protection system variable setpoints prior to plant conditions requiring them to be OPERABLE. Similar reportable events have not occurred within the last three years.
5302011001 | Palo Verde 3 | 01/19/2011 | 03/21/2011 | ML11090006 | <strong>Unit 3 Reactor Trip Due to Failed Open Main Feedwater Pump A Minimum Flow Recirculation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2011, at approximately 1840 Mountain Standard Time, Unit 3 was at 100 percent power at normal operating temperature and normal operating pressure when the main feedwater pump A minimum flow recirculation valve (mini-flow valve) failed open causing a percentage of feedwater flow to be diverted to the condenser. Subsequently, Unit 3 experienced a reactor power cutback when main feedwater pump B tripped on low suction pressure. The combination of the main feedwater pump B trip and the main feedwater pump A mini-flow valve failure caused both steam generator water levels to lower causing an automatic reactor trip. Both steam generator levels continued to drop which initiated an auxiliary feedwater actuation signal. The plant was stabilized in Mode 3. The failed open mini-flow valve was caused by a failed diaphragm in a pneumatic 3-way precision relay within the mini-flow valve control loop. The relay was replaced and Unit 3 was returned to 100 percent power on January 23, 2011, at approximately 0100. No similar conditions have been reported by Palo Verde in the past three years.