## Sheet1
LER Number | Plant Name | Event Date | Report Date | Accession # | Title
2192012002 | Oyster Creek | 10/29/2012 | 06/20/2013 | ML13190A46 | <strong>Loss of Offsite Power During Hurricane Sandy</strong><br /><i>Abstract:&nbsp;</i>At 20:18 on October, 29, 2012, while the reactor was in the Cold Shutdown Condition during a planned refueling outage, Oyster Creek experienced a Loss of Offsite Power (LOOP) event. The LOOP resulted in a valid automatic actuation signal for both the Emergency Diesel Generators (EDGs) to start, a valid Reactor Protection System (RPS) actuation with automatic containment isolations, and a trip of Shutdown Cooling to the reactor. Shutdown Cooling was expeditiously restored, following the initial EDG loading sequence, with electrical power from the EDGs. <br><br> The primary cause of the LOOP is attributed to equipment damage caused by the winds associated with Hurricane Sandy. Prior to reactor startup from the Refueling Outage, Oyster Creek verified that all required electrical distribution power lines and equipment required by Technical Specifications were available, operable, and functioning as required. <br><br> There were no Emergency Plan (EP) Emergency Action Levels (EALs) applicable for this event. <br><br> A detailed investigation was performed and found that the root cause of this event was a wall falling in the switchyard causing a ground fault on the 34.5KV system. Contributing to this event was a stuck breaker which allowed the ground fault to propagate to the 34.5KV system resulting in a local loss of the 34.5KV system. To prevent recurrence, the wall was removed and a stuck breaker modification was performed. <br><br> This event is being reported pursuant to 10CFR50.73(a)(2)(iv)(A) due to automatic actuation of the EDGs, RPS actuation, and containment isolation.
2192012003 | Oyster Creek | 11/07/2012 | 04/30/2013 | ML13128A06 | <strong>Control Rod Drive Return Nozzle Weld NC-4-1A PT Indications at N9</strong><br /><i>Abstract:&nbsp;</i>On November 07, 2012 at 1240 EST while the reactor was in the Cold Shutdown Condition and during Refueling Outage 1R24 In-Service Inspections, indications were identified in the adjacent base material area of the safe end to pipe weld of Reactor Pressure Vessel (RPV) Control Rod Drive Return Nozzle (N9). The indications were identified to be on the outside surface of the piping, during dye penetrant testing. The most probable cause of the surface indications was determined to be outside diameter stress corrosion cracking. The investigation performed, as a result of finding the indications, revealed that there was no moisture or leakage found in the area of the indications. Ultrasonic examinations also confirmed the indications were not inside diameter connected. Corrective action included repair to this location using a full structural weld overlay (WOL.) The WOL was installed using resistant stainless steel WOL material with a delta ferrite level above 7.5 FN (Ferrite Number). There were no Emergency Plan Emergency Action Levels applicable for this event.<br><br> This event is being reported pursuant to 10CFR50.73(a)(2)(ii)(A), "Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded."
2192012004 | Oyster Creek | 10/29/2012 | 01/08/2013 | ML13025A08 | <strong>MCR HVAC System Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2012, the Main Control Room (MCR) Heating Ventilation and Air Conditioning (HVAC) system (B) flow began oscillating. In order to stop the oscillations, the MCR team swapped to opposite system (A) of MCR HVAC. After swapping to the opposite system, the oscillations stopped. An Issue Report (IR) was written to document the issue. During the shift review of IRs, the (B) MCR HVAC system was declared inoperable by the Shift Manager (SM) and documented as such in the IR. On November 09, 2012 during troubleshooting activities, a different SM was independently reviewing IRs associated with MCR HVAC and discovered that the inoperable MCR HVAC system was not being properly tracked. Additionally, since the operability was not being properly tracked. Additionally, since the operability was not being properly tracked, it was also found on November 09 that the actions required for an inoperable MCR HVAC system were not being performed, as required by Technical Specification 3.17.B.1. When and MCR HVAC system is declared inoperable, Technical Specifications (TS) require placing the operable system in the partial recirculation mode once every 24 hours. Once the issue was identified, the operable system was successfully placed in partial recirculation mode. Corrective actions include reinforcement of IR review expectations with operations Senior Reactor Operators (SROs) and reinforcement of the procedural requirements of OP-AA-108-115, Operability Determinations, with all crews. The shift Operations Superintendent (SOS) expectations will be revised to ensure all necessary actions/reviews are completed, all requirements for operability are considered during the review including peer check documentation. This event is reportable under 10CFR50.73(a).(2).(i).(B), “operation or condition which was prohibited by Technical Specifications.”
2202012001 | Nine Mile Point 1 | 07/17/2012 | 11/05/2013 | ML13318A00 | <strong>Automatic Reactor Scram due to Electronic Pressure Regulator Failure</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2012, at 1118, Nine Mile Point Unit 1 (NMP1) experienced an automatic reactor scram on high neutron flux due to a failure of the Electronic Pressure Regulator (EPR). Following the reactor scram, the High Pressure Coolant Injection (I-IPCI) system automatically initiated on low Reactor Pressure Vessel (RPV) water level as designed. Failure of the Linear Variable Differential Transformer (LVDT) for servo position feedback (DT-1) to the EPR circuitry resulted in the EPR circuitry sending a close signal to the Turbine Control Valves (TCVs), resulting in a high neutron flux scram.<br /><br /> The root cause of this event is the Operational Decision Making Issues (ODMI) checklist and associated monitoring plan had unclear roles and responsibilities assigned which resulted in less than adequate communication, oversight of the plan's implementation, and assessment of the monitoring plan's data.<br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as a valid actuation of the reactor protection system and initiation of the high pressure coolant injection system.<br /><br /> Actions included removing the EPR from service, procedure revisions and training for ODMIs and abnormal condition monitoring and contingency planning. In addition, the EPR electronics and DT-1 were replaced in the 2013 NMP1 refueling outage. Previous LERs for similar EPR failures include 1987-014, 1992-003 and 1994-005.
2202012002 | Nine Mile Point 1 | 09/20/2012 | 11/05/2013 | ML13318A00 | <strong>Automatic Reactor Scram due to Automatic Generator Protective Trip</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2012, at 0923, Nine Mile Point Unit 1 (NMP1) experienced an automatic reactor scram due to an automatic generator protective trip. The NMP1 main generator excitation controls failed to maintain reactive load below the trip setpoint when transferred from automatic regulation to manual regulation. Following the reactor scram, the High Pressure Coolant Injection system automatically initiated on low Reactor Pressure Vessel (RPV) water level as designed.<br /><br /> One root cause of this event is that in 2003, a failure to follow the existing administrative procedure guidance for procedure change evaluations resulted in an inadequate review of the procedure change and introduction of a latent error into the amplidyne operating procedure. Additionally, the single point vulnerability life cycle management (LCM) strategy for this system was not developed or implemented in a timely manner and did not address the increased risk from aging electronic/electrical components.<br /><br /> Corrective actions include replacing degraded electronic components of the automatic voltage regulator, revising LCM strategies and procedure revisions for amplidyne operation.<br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as a valid actuation of the reactor protection system and initiation of the high pressure coolant injection system.<br /><br /> There are no previous LERs for similar failures.
2202012003 | Nine Mile Point 1 | 10/18/2012 | 10/03/2013 | ML13284A12 | <strong>Loss of Isolation Function on Shutdown Cooling System Suction Line due to an Operating Procedure Deficiency</strong><br /><i>Abstract:&nbsp;</i>During the Nine Mile Point Unit 1 forced outage which began on September 20, 2012, the Shutdown Cooling (SDC) system was in service with both suction line isolation valves (IV 38-01 and IV 38-02) open and de-energized, in accordance with the system operating procedure (OP). This system alignment was used to prevent inadvertent or spurious interruption of the SDC decay heat removal function. On October 18, 2012, a determination was made that this condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function needed to mitigate the consequences of an accident, because both of the SDC system suction line isolation valves were incapable of closing in the event of a leak in the SDC system. Concurrently, the reactor let-down path was shifted to the Reactor Bottom Head Drain, which operators did not recognize as an Operation with the Potential to Drain the Reactor Vessel (OPDRV). Failure to maintain the SDC isolation function while an OPDRV is in progress is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by plant Technical Specifications. <br /><br /> The cause of defeating the SDC isolation function is attributed to the failure of Operations personnel to recognize the need for, or coordinate, reviews from other key station stakeholders when the SDC system OP was revised. The cause of the TS violation was a failure to implement the change management process, which resulted in the station not fully assimilating NRC guidance on OPDRVs into existing processes. Corrective actions include revising the operating procedures and conducting additional licensed operator training.
2202012004 | Nine Mile Point 1 | 10/29/2012 | 11/05/2013 | ML13318A00 | <strong>Automatic Reactor Scram due to a Generator Load Reject</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2012 at 21:00:57 hours, Nine Mile Point Unit 1 (NMP1) experienced an unplanned, automatic, reactor scram due to a Turbine Trip from 100 percent power caused by activation of a generator lockout relay. The generator trip was an unexpected consequence and was initiated by a high fault current condition in the Scriba switchyard detected by both NMP1 instantaneous ground directional overcurrent relays. A polarity wiring error within the generator step up transformer neutral ground current transformers (CTs) caused the relay protection circuits to actuate on the fault in the Scriba switchyard. This was not expected because the relay protection circuits were designed to detect a fault condition between the main generator and the station output breakers. The error was caused by less than adequate oversight by CENG personnel of transformer XF-TB01 testing with respect to unclear specificity of requirements for vendor performed testing and inadequate methods of verification for ensuring vendor compliance with engineering specifications.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the reactor protection system and an actuation of the high pressure coolant injection system while the reactor was critical.<br /><br /> Corrective actions include correcting the wiring of the CT circuits, verifying all the requirements in the engineering specification have been met, revising the associated electrical drawings, and revising engineering procedures to require the listing of critical attributes for equipment/components and to define testing criteria/verification methods to be performed when factory acceptance testing or modification functional testing cannot be performed to verify the functionality of equipment/components.
2202012005 | Nine Mile Point 1 | 11/03/2012 | 11/05/2013 | ML13318A00 | <strong>Feedwater Level Control Failure, HPCI Initiation and Reactor Scram</strong><br /><i>Abstract:&nbsp;</i>On November 3, 2012, at 0825, Nine Mile Point Unit 1 (NMP1) experienced an unexpected rise in reactor water level followed by a turbine trip and subsequent reactor scram on low Reactor Pressure Vessel (RPV) water level at 53 inches. During this sequence of events, multiple separate and valid initiation signals for High Pressure Coolant Injection (HPCI) occurred.<br /><br /> The initial rise in RPV water level was caused by a failure in the Feedwater System three element control of reactor water level resulting in a maximum demand open signal being sent to the 11 Feedwater flow control valve (11 FCV). Subsequent-level transients were due to the failure of the 11 FCV to operate properly to control water level. The root causes of this event were selection of an inappropriate Preventive Maintenance (PM) strategy and not changing the PM program to test electronic components for end-of-life failure mechanisms. Corrective actions to address the root cause include replacement of the failed electronic components, revision of the PM program for the feedwater FCVs and revision to the electronic module refurbishment program to check transistors.<br /><br /> This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A) as a valid actuation of the reactor protection system and initiation of the high pressure coolant injection system.<br /><br /> LERs for similar events are; 85-004, 86-024, 90-015, 96-004 and 04-004.
2202012006 | Nine Mile Point 1 | 12/13/2012 | 06/14/2013 | ML13172A04 | <strong>Technical Specification Required Shutdown Due to Containment Leakage</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2012 at 16:30:10 hours, the primary containment was declared inoperable due to a primary containment leakage rate that was in excess of the Technical Specification (TS) 3.3.3.a limit. TS 3.0.1 requires that in the event Limiting Condition for Operation (LCO) requirements cannot be satisfied because of circumstances in excess of those addressed in the Specification, the unit shall be placed in a condition in which the LCO is not applicable. A normal orderly plant shutdown commenced at 16:45:00 hours and at 19:12:46 hours, a manual reactor scram was initiated from 18 percent power, in order to reduce the reactor coolant temperature to a value less than 215 degrees F within 10 hours of declaring the containment inoperable. At 23:33:00 hours, the reactor coolant temperature was below 215 degrees F. <br><br> This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A) as a plant shutdown required by Technical Specifications, with 10 CFR 50.73(a)(2)(iv)(A) as an actuation of the high pressure coolant injection system, and with 10 CFR 50.73(a)(2)(v)(C) as a condition that could have prevented the fulfillment of a safety function of a system needed to control the release of radioactive material. <br><br> Corrective actions include cleaning the inside surfaces of drywell purge isolation valves IV-201-31 and 1V-201-32 and associated piping to remove corrosion and testing the valves to restore containment integrity and containment isolation valve operability.
2202012007 | Nine Mile Point 1 | 11/06/2012 | 06/03/2013 | ML13158A30 | <strong>High Pressure Coolant Injection System Logic Actuation Following an Automatic Turbine Trip Signal due to High Reactor Water Level</strong><br /><i>Abstract:&nbsp;</i>On November 6, 2012, while in the cold shutdown reactor operating condition, Nine Mile Point Unit 1 experienced an unexpected rise in reactor water level that caused an automatic turbine trip signal and actuation of the High Pressure Coolant Injection (HPCI) initiation logic. The HPCI system is a mode of operation that uses selected equipment of the condensate and feedwater system to perform its function. The HPCI system is not an emergency core cooling system. At the time of the event, the HPCI system was not required to be operable. Though the HPCI initiation logic was actuated, HPCI system injection into the reactor vessel neither occurred nor was required.<br><br> The rise in reactor water level resulted from the unexpected opening of the 12 Feedwater flow control valve (FCV) during the application of a tagout to perform feedwater level control circuitry maintenance that was caused by a failure to use adequate human performance tools when performing the last periodic test of the feedwater FCVs. This resulted in the testing being performed improperly such that degradation of o-rings within the FCV actuator lockup valves was not detected. The o-ring degradation prevented the lockup valves from maintaining the FCV in the closed position.<br><br> This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event or condition that resulted in automatic actuation of the HPCI system.<br><br> To prevent recurrence, maintenance personnel have been briefed on the importance of continual use of human performance tools, and the applicable FCV test procedure has been revised to provide additional guidance for properly testing the FCV actuator lockup valves.
2372012001 | Dresden 2 | 02/19/2012 | 12/06/2012 | ML12355001 | <strong>One Division of APRM Neutron Flux-High Channels Inoperable as a Result of Power Maneuver</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2012, the oncoming control room operating crew prepared to perform daily control room surveillances. The Unit 2 licensed operator observed that average power range monitors (APRM) 4, 5, and 6 were indicating lower than actual calculated power and exceeded the allowable error tolerance of 2 percent. In this condition, the Division 2 APRM system would not have generated a Fixed Neutron Flux-High trip signal prior to exceeding the Allowable Value specified in the plant's Technical Specifications. Once identified, the APRM gains were adjusted within the allowable tolerance. During a planned down power, the night shift operating crew reduced reactor power to approximately seventy-three percent. As expected, the down power maneuvers affected the gain setting for the APRMs. However, the magnitude of the change to the gain settings was not anticipated. This resulted in all the gains on one of the two APRM Divisions experiencing an out of tolerance concurrently during the evolution. The movement of control rods, which are adjacent to Local Power Range Monitors (LPRM), have a definite affect on the power inputs being received by the APRMs. These local power inputs resulted in the Division 1 and 2 APRMs indicating conservatively and non-conservatively, respectively. This occurrence is inherent to boiling water reactors. The operation rounds were revised to include an hourly check of APRM gain settings. Additionally, a computer alarm was implemented to alarm on a sustained non-conservative indication for an APRM. The safety significance of this condition is low. The Flow Biased Neutron Flux-High trip function was conservatively set and would have generated a trip signal at approximately 104 percent rated thermal power which is well below the specified Technical Specification Allowable Value of 122 percent rated thermal power. Therefore the health and safety of the public and plant employees was not compromised as a result of this condition. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(A), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shut down the reactor and maintain it in a safe shutdown condition.
2372012002 | Dresden 2, Dresden 3 | 05/22/2012 | 12/21/2012 | ML13004A09 | <strong>Inlet Steam Drain Pot Drain Line Leaks Result in HPCI Inoperabilities</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2012, at 1055 hours CDT, plant personnel identified a small steam leak from the Unit 2 High Pressure Coolant Injection (HPCI) Inlet Drain Pot Drain line. Additionally, on June 10, 2012, at 0200 hours CDT, plant personnel identified a small steam leak from the Unit 3 HPCI Inlet Drain Pot Drain line. The drain line connects the HPCI Inlet Drain Pot to the Main Condenser. Following removal of piping insulation, it was determined that the piping had a through-wall leak on a 90 degree elbow upstream of the inboard drain line isolation valve. The steam supplies for the HPCI systems were isolated and declared inoperable. Technical Specification 3.5.1, Condition G was entered and required actions taken. Based on a failure analysis, the failure of the HPCI drain lines was due to local internal thinning from a mechanical erosion mechanism. Based on the cratered appearance of the eroded surfaces, most of the thinning was due to liquid droplet impingement erosion. The leaking pipes were replaced with stainless steel piping components. A Preventative Maintenance activity is being added for both units' HPCI system drain piping to periodically inspect for thinning and replace as necessary. The safety significance of this condition is low. Following isolation of HPCI, Automatic Depressurization and Low Pressure Emergency Core Cooling Systems were available and capable of providing makeup to the reactor vessel inventory. The health and safety of the public were not compromised as a result of this condition. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident."
2442012001 | Ginna | 06/03/2012 | 07/26/2012 | ML12212A21 | <strong>Automatic Start of "B" Emergency Diesel Generator Caused by Loss of Offsite Circuit 767 due to Wildlife</strong><br /><i>Abstract:&nbsp;</i>On Sunday, 06/03/2012 at approximately 0239, offsite power circuit 767 tripped offline resulting in a loss of Bus 12B. Upon investigation, the cause was determined to be a fault caused by a raccoon. With the electrical system in the normal 50%/50% alignment, the loss of circuit 767 caused the 480v safeguards buses 16 and 17 to momentarily lose power until the B emergency diesel generator automatically started and reenergized the safeguards buses as designed. The cause of the loss of power to Circuit 767 was determined to be a temporary fault caused by a raccoon, no damage to the plant equipment occurred. Additional Animal Deterrent Devices are being developed for installation.
2472012001 | Indian Point 2 | 02/08/2012 | 04/05/2012 | ML12111A25 | <strong>Technical Specification (TS) Prohibited Condition Caused by an Inoperable 23 Emergency Diesel Generator Fuel Oil Storage Tank Due to Fuel Oil Below TS Limit</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2012, during performance of special log 02-11-086, a field operator discovered the 23 Emergency Diesel Generator (EDG) Fuel Oil Storage Tank (FOST) below Technical Specification (TS) 3.8.3 required value per procedure 2-PT-W1 (EDG). On July 22, 2011, the 23 EDG FOST level indicator (LI-1135) was declared inoperable and a special log was initiated (02-11-086) to manually sound (stick measure) the 23 FOST on normal dayshift routine rounds and following the completion of a EDG run. A review of the 23 EDG operating history determined the 23 EDG was run for its monthly surveillance test on February 8, 2012. During post test lineup the field operators took the final FOST level from the local indicator and failed to manually sound the 23 FOST. During the 23 EDG surveillance run approximately 200 gallons of FO were transferred to the 21 FOST and 21 EDG day tank thereby reducing the 23 FOST to below TS required minimum volume. This condition exceeded the TS allowed outage time of 2 hours and the completion of other actions associated with an inoperable EDG. The apparent cause was a lack of a questioning attitude and understanding by operations watch personnel of out of service equipment (LI-1135) and the requirements of the special log in affect for LI-1135. Corrective actions will include coaching on management's expectations on use of Human Performance tools, initiation of a shift order on requirements for hanging deficiency tags in the field, and update of pre-job brief database. The event had no significant effect on public health and safety.
2472012002 | Indian Point 2 | 02/17/2012 | 11/19/2012 | ML12340A40 | <strong>Technical Specification (TS) Prohibited Condition Caused by New Fuel Assemblies Stored in a Configuration Prohibited by the TS</strong><br /><i>Abstract:&nbsp;</i>On February 17, 2012, a Fuel Transfer Form preparer using Technical Specification (TS) 3.7.13 (Spent Fuel Pit Storage) as a reference, recognized an error in the Transfer Form (2-TF-2012-004) that had allowed 11 fresh fuel assemblies (FA) to be moved into the Spent Fuel Pool (SFP) on January 23 thru 24, 2012, in Region 1-1 locations in a face-adjacent location to spent FAs. This configuration was not permitted by TS 3.7.13, which requires empty cells in between the Region 1-1 checkerboard locations of fresh fuel. The direct cause was that Reactor Engineering (RE) move sheets issued in January 2012 were incorrect. The root cause was weak/ineffective use of Human Performance (HP) tools during preparation and verification of the move sheets. Both the preparer and verifier did not review TS 3.7.13 in its entirety. The error was a result of poor self and peer check/review, overconfidence during performance of the task and weak supervisory oversight due to failure to perform a pre-job brief. Corrective actions included preparation of a new Transfer Form, disciplinary action which suspended qualifications of the preparer and verifier, performance of a Level 1 HP error review and stand-down to reinforce expectations for TS compliance, and performance of a HP Engineering Department clock reset. A training plan was developed to reinforce expectations of TS compliance and independent verification and self checking. The event had no significant effect on public health and safety.
2472012003 | Indian Point 2 | 03/12/2012 | 05/09/2012 | ML12144A15 | <strong>Technical Specification (TS) Prohibited Condition Caused by Through Wall Defects in Reactor Coolant Pressure Boundary Branch Lines</strong><br /><i>Abstract:&nbsp;</i>On March 12, 2012, during a scheduled refueling outage (RO) boric acid program walk down inspection, two locations on Reactor Coolant System (RCS) pressure boundary (RCPB) branch piping had boron deposits that appeared not to be due to packing or mechanical joint leakage. The areas were cleaned and non-destructive surface examinations confirmed that the boric acid deposits were due to through wall defects. 1) Pressure Control Valve PCV- 455A Spray Inlet Stop valve 4152 contained a defect on the top of the horizontal leak-off pipe in the base metal approximately one inch from where the pipe connects to the valve bonnet. 2) The socket weld of a 3/8 inch diameter tubing "tee" fitting down stream of valve 4138 contained a defect. Technical Specification 3.4.13 does not allow any RCPB leakage. The apparent cause of defect 1 (leak-off pipe) was stress corrosion cracking due to surface contamination. The apparent cause of defect 2 was poor quality weld due to insufficient weld reinforcement in part of the weld. Corrective actions included replacement of the bonnet of valve 4152 containing the leak-off pipe, and replacement of the socket welded "tee" with a Swagelok "tee" eliminating the two field welds that were lacking reinforcement. An engineering change (EC) and associated work orders (WO) will be prepared to eliminate the capped leak-off pipes on RCS valves at unit 2 and 3. A visual inspection on 10% (random sampling) of applicable field welds will be performed. The event had no significant effect on public health and safety.
2472012004 | Indian Point 2 | 03/28/2012 | 05/25/2012 | ML12158A19 | <strong>Unanalyzed Condition and Safety System Functional Failure due to Use of Rad Bypass Switch for Steam Generator Blowdown Isolation Valves Which Defeats Their Automatic Isolation for Analyzed Events</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2012, it was identified that use of the Rad Bypass switch position for Steam Generator (SG) blowdown isolation valves would defeat the automatic isolation of the blowdown isolation valves for degraded heat sink events (Loss of Normal Feedwater, Loss of All AC Power to Station Auxiliaries). The normal valve position is open and Auto close for heat sink events in addition to containment Phase A isolation. These analyzed events assume SG blowdown (SGBD) isolation occurs and continuous SG blowdown during these events has not been analyzed. SG inventory would not be maintained because one Auxiliary Feedwater pump would not provide adequate flow with the blowdown isolation valves open. On January 19, 2011, test 2-PC-2Y23-49 (Liquid Radiation Monitor Calibration) was initiated which positioned all SG blowdown isolation valve switches to Rad Bypass. During this time on January 20, 2011, the 21 Auxiliary Feedwater Pump was removed from service for testing. On January 27, 2011, testing per 2-PC-2Y23-49 was completed. The apparent cause was the inappropriate revision of test procedure 2-PC-2Y23-49 in 2002 that deleted information previously incorporated from an operating event at unit 3 that restricted when the blowdown radiation monitor could be tested. Corrective actions included revision of procedure 2-PC-2Y23-49 to delete steps to place in Rad Bypass while performing Radiation Monitor R-49 calibration and installation of a test jumper to disable the blowdown function. The UFSAR will be revised to provide the assumptions credited in accident analysis for SGBD isolation. The event had no significant effect on public health and safety.
2472012005 | Indian Point 2 | 03/02/2012 | 11/19/2012 | ML12340A40 | <strong>Technical Specification Prohibited Condition Caused by a Main Steam Safety Valve Outside its As-Found Lift Setpoint Test Acceptance Criteria Due to Spring Skew/Spindle Wear</strong><br /><i>Abstract:&nbsp;</i>On March 2, 2012, during the performance of surveillance procedure 3-PT-R006A, main steam safety valve (MSSV) MS-46D failed its As-Found lift set point pressure test. In accordance with the test, these valves must lift at +/- 3% of their required setting. Valve MS-46D lifted at 1136.9 psig, 24.9 psig outside its acceptance range of 1048 to 1112 psig. The other 9 MSSVs tested passed their As-Found test criteria. Technical Specification (TS) 3.7.1,"Main Steam Safety Valves," requires the MSSVs to be operable in accordance with TS Table 3.7.1-1 and Table 3.7.1-2 TS Surveillance Requirement (SR) 3.7.1.1 requires each MSSV be verified to lift per Table 3.7.1-2 in accordance with the Inservice Testing Program. Operability of the MSSVs includes the ability to open within the setpoint tolerances. As valve MS-46D was found outside its limit it failed As-Found testing and was declared inoperable. Valve MS-46D was adjusted and returned to operable. Subsequent disassembly and evaluation identified the cause. The direct cause of MSSV MS-46D failing its pressure test was lifting outside its acceptable range (greater than 3% of its nominal set point). The apparent cause was internal friction caused by spring skew and spindle wear. Corrective actions included valve disassembly/inspection and repair, valve adjustment to the operability set-pressure band, and re-testing. A modification approved in 2011 will install bronze wear sleeves along the inner diameter of the spindle contact points (adjusting bolt inner diameter, upper and lower spring washer inner diameter). The event had no effect on public health and safety.
2472012006 | Indian Point 2 | 06/06/2012 | 08/02/2012 | ML12222A34 | <strong>Automatic Reactor Trip as a Result of a Turbine-Generator Trip due to a Loss of Generator Field Excitation Caused by a Failed Exciter Trigger Generation Card</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2012, an automatic reactor trip (RT) was initiated as a result of a main Turbine-Generator trip due to a trip of the Generator backup lockout relay 86 BU on loss of main generator field excitation. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. Investigations determined the 86 BU relay actuation was triggered by relay 62BU1/AUX which serves as a time delay for the KLF-40 loss of field relay. The actuation of the loss of field relay was in response to a loss of generator excitation field from the Generrex voltage regulator system. The direct cause of the RT was loss of generator field excitation due to failure of the Generrex C-Phase Trigger Generation Card. The root cause was indeterminate but most likely due to premature failure of the U5 operational amplifier on the C-Phase Trigger Generation Card causing the U3 and U6 operational amplifiers to also degrade. Corrective actions included replacement of the C-Phase Trigger Generator and AC/DC Gate cards with new cards which were then calibrated and monitored for proper operation, and shipped failed card to a vendor for an equipment failure analysis. The event had no effect on public health and safety.
2472012007 | Indian Point 2, Indian Point 3 | 06/21/2012 | 08/20/2012 | ML12235A54 | <strong>Technical Specification (TS) Prohibited Condition Caused by Diesel Generator Reserve Fuel Oil (FO) Storage Tank Total Particulates Not Within Limits for Greater than TS AOT</strong><br /><i>Abstract:&nbsp;</i>On June 21, 2012, the results of a diesel fuel oil (FO) sample from the Diesel Generator (DG) Reserve FO Storage Tank were received from an offsite vendor that showed the total particulates were not within the allowable value per Technical Specification (TS) 5.5.11 (Diesel Fuel Oil Testing Program) for Unit 2 and TS 5.5.12 for Unit 3. FO sampling is performed in accordance with TS Surveillance Requirement 3.8.3.4 to verify that FO properties of new and stored FO are within the limits specified in the Diesel FO Testing Program. TS 3.8.3 (Diesel Fuel Oil and Starting Air) Condition D was entered with a required action to restore stored FO total particulates to within limits within 30 days. Actions were initiated to provide the required total usable reserve FO that met FO properties per the Diesel Fuel Oil Testing Program. TS 3.8.3 Condition D was exited on July 5, 2012. Previous FO sample results were reviewed and some were not within the TS allowable value and in some cases there was no credible documentation to verify operability during past operation. The apparent cause was a failure to trend adverse conditions identified for out of spec FO particulates and failure to use the Corrective Action Process to document out of spec FO particulate results. Corrective actions included implementation of a process for formal trending of safety related chemistry analysis results, updating the duty matrix to ensure responsibilities for trending are assigned and documented. A stand down will be performed to review the CR process and sampling protocol and training will be performed on the event and lessons learned. In addition, the cause of the increase in particulates after the change in sample vendor will be determined. The event had no significant effect on public health and safety.
2472012008 | Indian Point 2 | 09/07/2012 | 11/05/2012 | ML12340A15 | <strong>Technical Specification (TS) Prohibited Condition Due to an Inoperable 22 Static Inverter for Greater than the TS allowed Outage Time Caused by a Failed Frequency Meter</strong><br /><i>Abstract:&nbsp;</i>On September 7, 2012, Technical Specification (TS) 3.8.7 Condition A was entered for an inoperable 22 Static Inverter (SI) after the 22 SI swapped to its alternate power source. Troubleshooting determined the SI frequency meter optical sensor light was out. Tapping on the meter resulted in the frequency meter light illuminating allowing SI to sense that the correct frequency was present. After testing, operations transferred the 22 SI back to its normal power supply and exited TS 3.8.7. On September 10, 2012, operability of the 22 SI was questioned concerning the 22 SI seismic qualification. Because the cause of the failure of frequency meter could not be determined, operations concluded there was no reasonable assurance that the 22 SI would be able to maintain its design function in the event of a seismic event and the 22 SI was declared inoperable. TS 3.8.7 was entered, the meter was replaced and the 22 SI returned to its normal power supply. The apparent cause was inadequate use of human performance (HP) tools. Shift management did not effectively use questioning attitude. The Operations team level of knowledge on the operation of the optical sensor was insufficient to assess the seismic effect on its operation. Corrective actions included replacement of 22 SI frequency meter, inclusion of event in operations training, and update of vendor manual on meter function. The System Description for electrical systems will be revised to include a discussion of SI frequency meter optical sensor, a Temp Mod had been installed for the 24 SI and was issued for the 21-23 SIs to bypass the out of frequency transfer. A mod will be prepared to replace the meters with a model that does not include transfer on out of frequency. An equipment failure analysis will be performed to determine the cause of the failure of the 22 SI frequency meter photocell LED. The event had no significant effect on public health and safety.
2472012009 | Indian Point 2 | 11/28/2012 | 04/15/2013 | ML13114A26 | <strong>Unanalyzed Condition and Safety System Functional Failure due to Use of Rad Bypass Switch for Steam Generator Blowdown Isolation Valves Which Defeats Their Automatic Isolation for Analyzed Events</strong><br /><i>Abstract:&nbsp;</i>On November 26, 2012, Operator review of a tag-out for a Preventive Maintenance of the Steam Generator (SG) blowdown (SGBD) radiation monitor R-49 determined the tagout would have placed all the SGBD isolation valves (ISVs) in Rad Bypass. Operators could not identify any procedure allowing this action and determined this action was previously reported in LER-2012-004 as an unanalyzed condition and safety system functional failure when an Auxiliary Feedwater pump is out of service. The normal ISV position is open which allows the ISVs to Auto close for heat sink events (Loss of Normal Feedwater, Loss of All AC Power to the Station Auxiliaries) in addition to containment Phase A isolation. Analyzed degraded heat sink events assume SGBD isolation occurs and continuous SGBD during these events has not been analyzed. SG inventory would not be maintained if only one motor-driven AFW pump was operable as it may not provide adequate flow with the SGBD ISVs open. A review identified previous tagouts that placed the SGBD ISVs in Rad Bypass with an Auxiliary Feedwater pump or its emergency power supply inoperable. The apparent cause (AC) was the reviews associated with the condition recorded in CR-IP2-2012-02408 were too narrowly focused. Reviewers failed to consider processes other than procedures that could place the SGBD ISV in Rad Bypass. Corrective action was revision of procedure 2-PC-2Y23-49 to delete steps to place in Rad Bypass while performing Radiation Monitor R-49 calibration and installation of a test jumper to disable the blowdown function (as reported in LER-2012-004). Applicable archived tagouts were locked from further use. UFSAR Section 14.1.9 was revised to state SGBD isolation is assumed starting from event initiation. The AC and lessons learned will be shared with applicable plant personnel. The event had no significant effect on public health and safety.
2492012001 | Dresden 3 | 07/10/2012 | 09/10/2012 | ML12263A42 | <strong>Unexpected Isolation of the Isolation Condenser due to Test Switch Failure</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2012, at 0236 hours CDT, plant personnel were performing the high condensate and steam flow calibration surveillance for the Isolation Condenser. The surveillance was being performed to satisfy technical specification (TS) surveillance requirements for the primary containment isolation instrumentation TS 3.3.6.1. In order to prevent actuation of the isolation logic, a test toggle switch is installed in parallel with the channel contacts that are being tested. This configuration provides electrical continuity around the channel contacts that will be actuated during the testing. The test toggle switch was installed around the contacts associated with the steam line flow differential pressure switch. At the time that the high flow signal was simulated for the channel being tested, an unexpected Isolation Condenser isolation occurred. The cause of the isolation is attributed to the failure of the test toggle switch to maintain electrical continuity during the test. The Isolation Condenser was declared inoperable and the associated TS 3.5.3 actions were performed. The Isolation Condenser system was restored to operable status at approximately 1055 hours. The safety significance of this condition is low. Following isolation of the Isolation Condenser, the High Pressure Coolant Injection system, was available and capable of providing pressure control and makeup to the reactor vessel inventory. The health and safety of the public were not compromised as a result of this condition. This event is being reported in accordance with 10 CFR 50.73(a)(2)(v)(B), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to remove residual heat."
2502012001 | Turkey Point 3 | 03/21/2012 | 05/21/2012 | ML12160A05 | <strong>Containment Concrete Thickness at Spalled Patch Does Not Meet Technical Specification Design Value</strong><br /><i>Abstract:&nbsp;</i>On March 21, 2012, during the 40 year tendon surveillance, a patch on the exterior face of the Unit 3 Containment was observed to be spalling. The patch is located along the top edge of the original construction opening. It is presumed that the patch was applied to fill the gap that would typically be created when the opening was filled in at the end of construction. The depth of the spall was measured as approximately 2 inches deep, and shallow re-bar was exposed at the top edge of the patched area. Technical Specification 5.2.1.c specifies the minimum thickness of the Containment concrete wall to be 3.75 feet. Plant drawing 5610-C-132 shows the thickness of the Containment exterior wall as 3.75 feet. Because there is no specified tolerance on the concrete thickness, literal compliance with the Technical Specifications leads to a conservative conclusion that the spall thickness has reduced the Containment concrete wall thickness to less than 3.75 feet in this very limited area. Therefore, this is reportable as a condition prohibited by Technical Specifications. Evaluation of the condition has determined that there is no effect on the integrity of the Containment to perform its function. Therefore, there was no effect on the health or safety of the public.
2502012002 | Turkey Point 3 | 06/25/2012 | 08/21/2012 | ML12250A62 | <strong>Non-compliance with TS 3.4.9.3 due to Manual Isolation Valve Found in Incorrect TS Configuration</strong><br /><i>Abstract:&nbsp;</i>On 6/25/12, Turkey Point Unit 3 was in Mode 5. The High Head Safety Injection (HHSI) manual isolation valve, 3-867 was previously closed, but not locked, while the HHSI Cold Leg Injection Isolation valves MOV-3-843A/B were closed and de-energized. At approximately 1710, Turkey Point Unit 3 inadvertently entered into an unplanned 4 hour Technical Specification (TS) Action for not meeting TS 3.4.9.3 Limiting Condition for Operation (LCO), when during the preparations for Engineered Safeguards Testing, Equipment Clearance Order (ECO 63-62) closed the breakers for MOV-3-843A/B. This condition was recognized on 7/1/12 at approximately 1000, while the Unit 3 Reactor Controls Operator (RCO) was reviewing Technical Specification (TS) requirements for an upcoming evolution and noted the requirement for manual valve 3-867 to be locked closed. Operations recognized that Turkey Point Unit 3 had been in TS 3.4.9.3 Action (a), restored manual isolation valve 3-867 to its correct TS configuration by locking it closed. On 7/1/12 at approximately 1045, Unit 3 exited TS 3.4.9.3 Action (a) and complied with TS 3.4.9.3 LCO. The root cause determined that the Engineered Safeguards Testing lacks a rigorous control process to ensure verification of manual valve 3-867 is in its required TS 3.4.9.3 configuration prior to energizing MOV-3-843A/Bs. Corrective actions include process and procedural changes to add a verification step just prior to energizing MOV-3-843A/B breakers to ensure locally that manual isolation valve 3-867 is locked closed along with procedurally disallowing the breakers from being included on the ECO.
2502012003 | Turkey Point 3 | 08/25/2012 | 10/24/2012 | ML12313A00 | <strong>Condition Prohibited by Technical Specifications Due to Instrument Valve Mispositioning</strong><br /><i>Abstract:&nbsp;</i>On 8/25/12, at approximately 1140, Turkey Point Unit 3 was in Mode 2. The Operations Department was performing the Main Turbine Valve Alignment, in preparation for turbine start-up following a refueling outage. During the alignment verification, Operations discovered the root isolation valves for the Turbine inlet pressure transmitters closed when they were required to be open. The Main Steam pressure transmitters, PT-3-446 and PT-3-447, provide input to various protection and control functions. Upon discovery of this condition, operators entered Technical Specification (TS) 3.0.3for Unit 3 because the Minimum Channels Operable requirements of TS 3.3.2, Table 3.3-2, Functional Unit 1.f (Safety Injection, Steam Line flow - High coincident with SG pressure Low or Low Tavg) and TS 3.3.2, Table 3.3-2, Functional Unit 4.d (Steam Line Isolation) were not met. The isolation valves were then opened and TS 3.0.3 was exited at approximately 1239. The cause was determined to be lack of rigor in ensuring a proper follow-up review of a modification, which added the new root isolation valves at the High Pressure Turbine inlet pressure tap locations.
2502012004 | Turkey Point 3 | 09/06/2012 | 11/05/2012 | ML12348A00 | <strong>Condition Prohibited by Technical Specifications due to Instrument Process Line Reversal During Replacement</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2012 at approximately 2300, the indication associated with feedwater flow transmitter FT- 3-476, [JB:FT] was noted to be reading lower than expected. After further assessment, on September 7, 2012 at approximately 0540 the associated Reactor Protection System channel was declared inoperable, and at approximately 0837 the channel was placed in the tripped condition. Troubleshooting determined the high and low side process tubing for the differential pressure transmitter was reversed. The tubing was repaired and FT-3-476 was returned to service at approximately 1100 on September 7, 2012. The tubing reversal occurred when it was replaced during the recent refueling outage. The causes of this event are: The work order task description (WOTD) specified "Skill-of-the-Craft", leading to a failure to use or ineffective use of human error prevention tools, and the post maintenance test did not provide for a positive method of tubing orientation verification after replacement. Corrective actions include addition of rule-based instructions in the WOTD. The event is reportable because FT-3-476 was inoperable for a time greater than allowed by Technical Specifications and the required actions were not taken. Because redundant and diverse reactor trip instrumentation was available, the safety significance is very low.
2542012001 | Quad Cities 1, Quad Cities 2 | 02/03/2012 | 03/23/2012 | ML12095A28 | <strong>Control Room Emergency Ventilation Air Conditioning System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 3, 2012, at 1035 hours, the Unit 1/2 (common) "B" Control Room Emergency Ventilation (CREV) Refrigeration Condensing Unit (RCU) was declared inoperable when the electrical feed breaker to the RCU was found in the tripped condition. Operators performed required actions to safely secure the CREV RCU in accordance with procedures and training, and without complications. This resulted in entering Technical Specification 3.7.5, Condition A (30 day Action). This event affected both the Unit 1 and Unit 2 Control Rooms since they share a common control room and CREV system. The Train B CREV Air Conditioning (AC) system is a single train safety-related system that is designed to operate in a post-accident condition to maintain design temperature in the Control Room Envelope (CRE), and loss of the CREV AC could impact the plant's ability to mitigate the consequences of an accident. The CREV RCU chiller compressor breaker trip was caused by insufficient margin in the breaker setting for MCC 18-4 Cubicle 1D. The original breaker setting did not take into account that the compressor motor load had the potential for a high locked-rotor current, and the breaker setting for instantaneous (magnetic) setting needed to be set higher to avoid nuisance trips. Corrective actions included modifying the breaker setting under a revised evaluation. Future corrective actions include the review of breaker settings for similar type loads, and to modify the breaker settings as deemed necessary by the evaluations. The safety significance of this event was minimal. Given the impact on the CREV AC system, this report is submitted in accordance with the requirements of 10 CFR 50.73(a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident.
2542012002 | Quad Cities 1 | 04/02/2012 | 06/01/2012 | ML12160A07 | <strong>Standby Gas Treatment System Loss of Safety Function due to Loss of Emergency Power</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2012, at 1452 hrs, Unit 1 received an Emergency Diesel Generator (EDG) trouble alarm. Equipment Operators were dispatched and the Unit 1 EDG was found running unloaded, without a generator field flash, and no auto start signal had been received. Troubleshooting identified that a 125 VDC ground had caused the Unit 1 EDG to start. As a result, the Unit 1 EDG was declared inoperable. At that time Unit 2 was in refueling outage Q2R21 and the Unit 2 EDG was previously inoperable for repairs. Due to the inoperability of the Unit 1 and Unit 2 EDGs, at 1652 hrs, Technical Specifications (TS) 3.8.1.F was entered, and Unit 1 commenced actions for a reactor shutdown. Since the EDGs supply emergency power to both Unit 1 and Unit 2 Standby Gas Treatment Systems (SBGTS), emergency power was unavailable to SBGTS; however, the normal power supply remained available. At 2151 hrs, the Unit 1 EDG was declared operable following repairs and successful operability testing. TS 3.8.1.F was exited and Unit 1 load increase to full power achieved at 2300 hrs. Corrective actions included replacement of the Unit 1 EDG governor oil booster pump motor. Future corrective actions include replacement of remaining EDG governor oil booster pump motors, and development of improved related work instructions. The safety significance of this event was minimal. Given the impact on the SBGTS, this report is submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), and (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: control the release of radioactive material, and mitigate the consequences of an accident.
2542012003 | Quad Cities 1, Quad Cities 2 | 08/05/2012 | 10/04/2012 | ML12290A02 | <strong>Degraded Flood Protection Barrier</strong><br /><i>Abstract:&nbsp;</i>On August 5, 2012, station operating personnel initiated surveillance, Reactor Building Floor Drain Sump Ball Valve Leakage Testing. This surveillance verifies the leak tightness of the Reactor Building Floor Drain Sump Ball Valves for Unit 1 and Unit 2. The drain sump ball valves (one associated with each Emergency Core Cooling System (ECCS) corner room, four per unit) are normally closed to isolate the four-inch drain line between the ECCS corner room and associated reactor building basement sump. During the surveillance, two of the eight sump ball valves exhibited a small amount of leakage (pencil size stream). The associated ECCS equipment was declared inoperable upon discovery in accordance with Station procedures. For the Unit 1 drain sump ball valve leak identified on August 5, 2012, Technical Specifications (TS) 3.5.1 Condition B was entered for the 1B Core Spray subsystem. For the subsequent Unit 2 drain sump ball valve leak identified on August 6, 2012, TS 3.5.1 Condition B was entered for the 1A and 2B Core Spray subsystems, and TS 3.5.3 Condition A was entered for the Unit 1 and Unit 2 Reactor Core Isolation Cooling (RCIC) systems. A temporary plug was installed in the drain path to restore operability and facilitate repairs. The cause of the 1B and 2B Core Spray Room Floor Drain Ball Valves to fail their leakage test was due to wear related degradation that occurred at the valve-to-actuator coupling that allowed the valve to not be fully seated despite the actuator indicating full travel closed. Corrective actions included adjusting the ball valves to allow an additional 1.5 turns of the operator to achieve full closure. The associated Preventive Maintenance (PM) frequency was increased from 4 years to 2 years. New PMs will be developed to perform periodic repair/replacements of the valve-actuator coupling and gearbox, and the valve internals. The safety significance of this event was minimal since the remaining operable ECCS systems were capable of supporting safe shutdown. Further, the leakage rate was small and would not pose an immediate threat to ECCS equipment during a postulated flooding event. Since the as-found leakage was the result of the valve actuator not properly indicating the valve position, the as-found leakage condition also likely existed prior to discovery, therefore this event is reportable (Units 1 and 2) per 10 CFR 50.73(a)(2)(i)(B), which requires the reporting of any operation or condition which was prohibited by the plant's Technical Specifications.
2542012004 | Quad Cities 1, Quad Cities 2 | 09/06/2012 | 11/15/2012 | ML12321A02 | <strong>Breech in Secondary Containment</strong><br /><i>Abstract:&nbsp;</i>On September 6, 2012, at 1314 hours, the reactor building ventilation system was being restored to service following planned maintenance and surveillance activities. During the reactor building pressure transition when restoring reactor building ventilation (from the Standby Gas Treatment System), a worker entered the Unit 2 Reactor Building (RB) 595 Interlock door (a secondary containment interlock) and found the Unit 2 RB Interlock (RBI) HRSS-Side door (which leads to the environment) had opened at the same time. The worker immediately secured the door and notified Operations personnel. A review of the door alarm history determined the door had been opened for approximately eight seconds, therefore secondary containment had been breeched for a short duration. Since both Units 1 and 2 share a common reactor building, a breech occurred for eight seconds that impacted both Units 1 and 2 secondary containments when the Unit 2 RB 595 Interlock door and the Unit 2 RBI HRSS-Side door were opened at the same time. The cause of the secondary containment breech event was that the Unit 2 RBI HRSS-side door latching mechanism was not fully engaged at the time that the Unit 2 RB 595 Interlock door opened. Corrective actions included immediate closure of the Unit 2 RBI HRSS-side door (2-0020-153), confirmation of being fully latched, and removal of the Unit 1 and 2 RBI HRSS-side doors from service. Door latch repairs will be made, and the Unit 1 and 2 RBI HRSS-side doors will be removed by permanently enclosing the door openings. The safety significance of this event was minimal. Given the impact on the secondary containment, this report is submitted (for Units 1 and 2) in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), and (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: control the release of radioactive material, and mitigate the consequences of an accident.
2552012001 | Palisades | 08/12/2012 | 10/11/2012 | ML12285A32 | <strong>Degraded Condition due to Control Rod Drive Mechanism Housing Assembly Crack</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2012, with the plant in Mode 3, a primary coolant system pressure boundary leak was identified in control rod drive mechanism (CRDM) number 24 upper housing assembly. Upon identification, the plant was placed in Mode 5 to effect repairs. Initial examination, using liquid penetrant testing in the area of the leak, identified a 1/8" x 1/16" L-shaped crack indication on the outside surface of the type 316L stainless steel pipe section of the CRDM-24 upper housing assembly. Subsequent non-destructive and destructive examinations revealed a total of nine axially oriented crack indications, located in the proximity of an inside surface weld onlay. One of the nine crack indications was a through-wall crack at the leak point approximately 3" in length. The CRDM-24 upper housing assembly was removed and replaced with an upper housing assembly of modified design. Examinations using ultrasonic testing of eight additional CRDM upper housing assemblies were performed on an area 1" below to 1-1/2" above the area of interest. No deficiencies were noted. The direct cause for the cracking identified in CRDM-24 was transgranular stress corrosion cracking (TGSCC). TGSCC was the result of stress in the proximity of the inside surface weld onlay caused by manufacturing irregularities and misalignments between CRDM-24 upper housing assembly and supporting components. Based on the lack of crack indications in the additional eight upper housing assemblies examined, the failed CRDM-24 upper housing assembly was subject to an additional stress that has not yet been identified.
2552012002 | Palisades | 11/04/2012 | 12/20/2012 | ML12356A05 | <strong>Technical Specification Required Shutdown Due to Un-isolable Secondary Side Drain Valve Leak</strong><br /><i>Abstract:&nbsp;</i>On November 04, 2012, at 1115 hours, Primary Coolant System (PCS) loop 2 was declared inoperable due to the discovery of an un-isolable steam/water leak near a drain valve of an atmospheric dump valve from the "B" Steam Generator. The leak originated from a pin-hole size through-wall flaw in the socket weld on the inlet side of the drain valve. The drain valve is part of the ASME Section XI Class 2 piping system that provides steam to the turbine. Due to the inoperable PCS loop, Technical Specification 3.4.4, Condition A, required the plant be placed in Mode 3 within six hours. The plant entered Mode 3 at 1621 hours on November 4, 2012. At 1224 hours on November 5, 2012, the plant entered Mode 5 to execute repairs. During fabrication of the socket weld in 1986, the welder did not utilize proper welding techniques to create a quality weld for the shield metal arc welding process used at that time. Lack of a quality weld resulted in a through-wall flaw. The drain valve was replaced using a gas tungsten arc welding process.
2592012001 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 05/11/2010 | 12/26/2012 | ML13002A06 | <strong>Unanalyzed Conditions Discovered During NFPA 805 Transition Review</strong><br /><i>Abstract:&nbsp;</i>A National Fire Protection Association 805 transition review discovered several unanalyzed conditions associated with multiple spurious operation (MSO) of equipment during Appendix R fires. On May 11, 2010, it was determined that multiple hot shorts affecting reactor pressure instrument loops, Safety Relief Valve (SRV) overpressure logic, or Automatic Depressurization System logic could cause as few as 2 and up to 13 SRVs to spuriously open. On September 30, 2010, it was determined that fire induced multiple hot shorts could cause both inboard and outboard Residual Heat Removal test return valves, arid Drywell Spray valves and Suppression Pool Spray valves to spuriously open due to damage to the valve control circuit cables. On August 22, 2011, it was determined that fault propagation during a fire due to loss of the breaker control circuit in conjunction with power cable damage could result in de-energization of the associated 4kV Shutdown Board. Also, on August 22, 2011, it was determined that fire induced multiple hot shorts could cause the Main Steam Isolation Valves to fail to close or to re-open. The cause of these conditions was the historical design basis which did not consider MSOs credible in a fire scenario.
2592012002 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 08/18/2010 | 12/26/2012 | ML13002A06 | <strong>Fault Propagation During A Postulated Appendix R Event Could Result In An Inability To Close Motor Operated Valves</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2010, at 1557 Central Daylight Time, during the National Fire Protection Association 805 transition review, it was discovered that the current Browns Ferry Nuclear Plant (BFN) Appendix R analysis does not adequately evaluate fire induced circuit damage. Fire damage to the control circuits of a motor operated valve (MOV) has the potential to bypass the open/close limit switch and/or torque switch causing the valve actuator motor to stall and subject the valve train to forces which exceed design. This has the potential to damage the actuator or the moving parts of the MOV (i.e., Main Steam Line Drain valves, Residual Heat Removal Heat Exchanger Outlet valves, and Emergency Equipment Cooling Water pump cross-tie valves) such as the stem, stem threads, actuator mount, or anti-rotation device which could prevent the ability to move the valve with the associated hand wheel. The failure to manually close these valves could result in the loss of decay heat removal function and loss of credited emergency diesel generators to power required Appendix R safe shutdown equipment. These issues have significant safety impact since the capability to manually close these valves is necessary to ensure adequate core cooling during performance of BFN Safe Shutdown Instructions. Compensatory actions in the form of fire watches have been established in accordance with the BFN Fire Protection Report to mitigate this condition. The cause was the failure to review and resolve issues related to industry and NRC guidance on fire induced circuit damage as a result of process deficiencies.
2592012003 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 02/08/2012 | 12/26/2012 | ML13002A06 | <strong>Reactor Protection System Circuit Could Potentially Remain Energized During An Appendix R Fire</strong><br /><i>Abstract:&nbsp;</i>On February 8, 2012, as a result of the National Fire Protection Association 805 transition reviews, a 10 CFR 50 Appendix R non-conforming condition associated with the 120 Volt (V) lighting (utility) circuit feed to Reactor Protection System (RPS) cabinets 9-15 and 9-17 on all three Browns Ferry Nuclear Plant (BFN) units was identified. Due to lack of physical separation with 120 V Alternating Current (AC) lighting circuitry, the RPS circuit could remain energized due to a postulated hot short during a fire which could prevent the control rods from inserting into the reactor. The 120V lighting circuit is normally energized and routed in the subject cabinets in a manner that could result in hot short(s) following a fire event to the 120V AC RPS circuit. The 120V AC RPS circuit is required to be de-energized to initiate a scram in accordance with BFN Safe Shutdown Instructions in the event of a serious fire. The potential hot short(s) as a result of a fire in Fire Area 16 could cause the RPS circuit to remain energized and the RPS would fail to initiate a scram. Compensatory actions in the form of fire watches to mitigate this condition are in place in accordance with the BFN Fire Protection Report. The cause of this issue is engineers' lack of technical rigor during the initial review to verify conformance with 10 CFR 50 Appendix R Section III.G.2. Corrective actions include implementing a design change to provide separation of the 120V lighting (utility) circuit feed to the cabinet lights and duplex receptacles in the RPS cabinets 9-15 and 9-17 on all three BFN units, and conducting additional training of engineering personnel.
2592012004 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 03/14/2012 | 12/26/2012 | ML13002A06 | <strong>Fire Damage to Cables in Fire Areas Could Cause a Residual Heat Removal Service Water Pump to Spuriously Start</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2012, as a result of the National Fire Protection Association 805 transition reviews, a 10 CFR 50 Appendix R non-conforming condition associated with a postulated spurious start of a Residual Heat Removal Service Water (RHRSW) pump due to cable damage during an Appendix R fire was identified. The spurious start of this pump could overload the Emergency Diesel Generator associated with the shutdown board that powers the pump. Compensatory actions in the form of fire watches to mitigate this condition are in place in accordance with the Browns Ferry Nuclear Plant Fire Protection Report. The cause of this condition was identified as human performance errors by engineers. The corrective actions for this condition include implementing a modification to reconfigure the wiring of the eight affected RHRSW pumps to eliminate the potential of Emergency Diesel Generator overloading due to RHRSW pump auto start, and to conduct additional training of engineering personnel.
2592012005 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 12/22/2011 | 07/13/2012 | ML12198A24 | <strong>Combustible Materials Not in Compliance with the 20-Foot Exclusion Zone Requirements</strong><br /><i>Abstract:&nbsp;</i>At Browns Ferry Nuclear Plant (BFN), exclusion red zones are established for compliance with 20-foot separation requirements of Appendix R Section III.G.2.b, i.e., separation of cables and equipment and associated non-safety circuits of redundant trains by a horizontal distance of more than 20 feet with no intervening combustible or fire hazards. On December 22, 2011, during an extent of condition inspection of red floor areas, transient combustibles were identified in exclusion red zones of BFN Units 1, 2, and 3. Additionally, on February 3, 2012, during walkdown of the Reactor Buildings, more combustibles were identified in an exclusion red zone of BFN Unit 2. On March 28, 2012, it was determined that intervening combustible materials (i.e., cables and insulation) found in the 20-foot exclusion red zones were not in compliance with Appendix R Section III.G.2.b and the associated NRC approved exemption issued for BFN. As a result of the intervening combustible material found in the 20-foot exclusion red zones, the degree of separation is lacking for redundant Appendix R safe shutdown trains. The cause was the misclassification by Operations personnel of the combustible materials as "in-use materials" in the 20-foot exclusion red zones.
2592012006 | Browns Ferry 1 | 04/19/2012 | 12/31/2012 | ML13003A17 | <strong>High Pressure Coolant Injection System Turbine Failed to Trip Using the Manual Trip Pushbutton</strong><br /><i>Abstract:&nbsp;</i>On April 19, 2012, at approximately 1117 hours Central Daylight Time (CDT), the Browns Ferry Nuclear Plant, Unit 1, High Pressure Coolant Injection (HPCI) System was declared inoperable for performance of surveillance procedure 1-SR-3.5.1.7, HPCI Main and Booster Pump Set Developed Head and Flow Rate Test at Rated Reactor Pressure. On April 19, 2012, at approximately 1430 hours CDT, at the end of the HPCI pump run for surveillance procedure 1-SR-3.5A .7, while attempting to trip the HPCI turbine using manual trip pushbutton 1-HS-073-0018A, the HPCI turbine failed to trip. The manual trip pushbutton was pressed four times with no results. Pressing the manual trip pushbutton should have resulted in the closure of the HPCI turbine stop valve 1-FCV-073-0018. As a result of the failure, the capability of electrical and mechanical automatic and manual trip functions of the HPCI System was lost. The HPCI turbine was stopped by securing the HPCI steam supply with closure of the HPCI turbine steam admission valve 1-FCV-073-0016. The root cause was determined to be inadequate procedural guidance in MCI-0-073-VLV001, High Pressure Coolant Injection Turbine Stop Valve - FCV 73-18 Disassembly, Inspection, Rework and Reassembly.
2592012007 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 06/01/2012 | 12/26/2012 | ML13002A06 | <strong>Cable Routing Errors Found in the Appendix R Separation Analysis</strong><br /><i>Abstract:&nbsp;</i>On June 1, 2012, at 0900 hours Central Daylight Time (CDT), during the National Fire Protection Association (NFPA) 805 transition review, it was discovered that a cable routing error would result in failure of direct current control power to credited 4kV Shutdown Board 3EA during an Appendix R fire in Fire Area 23. On July 11, 2012, at 1520 hours CDT, during the NFPA 805 transition review, it was discovered that an Appendix R cable was routed in Fire Zone 03-02. However, the Appendix R computerized separation analysis does not recognize the Appendix R cable as being routed in Fire Zone 03-02. The root cause was determined to be the lack of an effective program for technical human performance tools during the performance of the Appendix R separation analysis. The corrective action to prevent recurrence is to implement a technical human performance procedure for knowledge worker human performance tools for all programs/calculations performed by engineering.
2592012008 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 08/02/2012 | 12/14/2012 | ML12361A00 | <strong>Standby Gas Treatment System Train C Inoperable Longer Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 2, 2012, at 1232 hours Central Daylight Time, the Browns Ferry Nuclear Plant (BFN), Unit 2 Standby Gas Treatment (SGT) Train C relative humidity heater was placed into service which resulted in an Annunciator Alarm, SGT C Filter Bank Heater Element Power Lost. Troubleshooting identified the 2A Motor Control Center (MCC) breaker bucket containing the associated breaker was misaligned resulting in poor contact with the C phase of the electrical supply bus. Only the top retaining device, out of the two required retaining devices, used to secure the breaker bucket in the cubicle, was installed in the MCC. On August 3, 2012, a spare retaining device was installed to replace the missing device. It is unlikely the SGT Train C relative humidity heater would have functioned properly during a seismic event without the bottom retaining device. Therefore, SGT Train C was concluded to have been inoperable from September 12, 2011, when the breaker bucket was removed for maintenance, to August 3, 2012, when the bottom retaining device was installed. The root cause of this event is the result of an inadequate maintenance instruction that allowed the installation of a breaker bucket in an ITE Gould 5600 Series MCC with a single retaining device. The corrective actions to prevent recurrence were to revise Maintenance Instructions EPI-0-000-MCC001 and ECI-0-000-BKR008 to address identified issues.
2592012009 | Browns Ferry 1, Browns Ferry 2, Browns Ferry 3 | 10/31/2012 | 12/28/2012 | ML13002A01 | <strong>480 Volt Shutdown Board Breaker Actions in Safe Shutdown Instruction Procedures May Not Work as Written Due to Cable Fire Damage</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2012, at approximately 1253 hours Central Daylight Time, it was determined that in the event of an Appendix R fire, the ability to provide power to equipment needed to achieve and maintain safe shutdown may be adversely impacted. Fire damage to the Main Control Room 480 Volt Shutdown Board transfer switch cables could cause the control circuit fuse for the credited breaker to clear prior to the use of the emergency switches used for backup control operation. This would inhibit the ability to isolate the breakers using the associated emergency transfer switches and thereby inhibit local operation of the breakers. Therefore, Safe Shutdown Instruction steps to use the emergency switches to perform local breaker operation to supply power to safe shutdown equipment may not work as written during a postulated Appendix R fire. The root cause was determined to be a legacy human performance error that occurred during the technical resolution of Appendix R fire protection analyses associated with cable separation and operator manual actions. The corrective action to prevent recurrence is to revise the human performance tools procedure to incorporate the five Institute of Nuclear Power Operations Technical Conscience Principles, focus technical task risk factors, mitigation strategies, and decision making.
2592012010 | Browns Ferry 1 | 11/22/2012 | 01/22/2013 | ML13025A31 | <strong>Primary Containment Isolation Valve Inoperable for Longer than Allowed by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 22, 2012, at 0600 Central Standard Time, during a Browns Ferry Nuclear Plant (BFN), Unit 1, refueling outage, Sense Line A3 Excess Flow Check Valve, 1-ECKV-068-0065B, failed to meet the acceptance criteria of surveillance 1-SR-3.6.1.3.8(4), Instrument Line Excess Flow Check Valve Operability Test. Further troubleshooting identified the failure resulted from the valve being incorrectly installed in a reverse orientation in the system. The valve was originally installed in a reverse orientation on October 15, 2006. This configuration would not have reduced flow downstream of the check valve in the event of a sensing line rupture outside of primary containment. The check valve was replaced and installed in its correct orientation, followed by successful the completion of the surveillance, on November 27, 2012. The root cause of the condition was identified to be Mechanical Corrective Instruction MCI-0-000-CKV002, Maintenance of Marotta Instrument Line Check Valves, does not contain a step to ensure the valve was installed correctly, or an independent step to verify correct installation. The corrective actions to prevent recurrence are to revise MCI-0-000-CKV002 to include steps to ensure proper installation of check valves, include steps to independently verify installation, and to review and revise, as necessary, BFN mechanical maintenance check valve procedures to ensure adequate direction for correct installation of check valves.
2602012001 | Browns Ferry 2, Browns Ferry 3 | 04/13/2012 | 06/12/2012 | ML12166A31 | <strong>Browns Ferry Nuclear Plant, Units 2 and 3, Inappropriate LOCA Modeling of Core Spray for Limiting LOCA Event with Manual Actuation of Automatic Depressurization System</strong><br /><i>Abstract:&nbsp;</i>On April 13, 2012, the Nuclear Regulatory Commission (NRC) notified Browns Ferry Nuclear Plant (BFN) of a NRC-identified non-cited violation. This violation was formally issued in the NRC Integrated Inspection Report for BFN, dated April 27, 2012. The violation was issued due to BFN's failure to accurately maintain design control regarding single-failure assumptions for the Emergency Core Cooling System (ECCS) and to perform sufficiently bounding analyses to ensure that the calculated maximum fuel element cladding temperature of 2200 degrees Fahrenheit would not be exceeded in the event of a small break Loss of Coolant Accident (LOCA). Due to this condition, there was a potential that the Peak Clad Temperature limit of fuel rods in BFN, Units 2 and 3, could have been exceeded starting March 30, 2004 for BFN Unit 3 and April 16, 2005 for BFN, Unit 2 and ending May 20, 2011. The cause of this condition was sufficient barriers were not in place to require the appropriate reviews for design document control associated with ECCS availability in a LOCA scenario. Corrective actions are established to correct the flawed barriers to prevent this condition.
2602012002 | Browns Ferry 2 | 06/07/2012 | 08/13/2012 | ML12227A68 | <strong>High Pressure Coolant Injection System Rendered Inoperable due to an Inoperable Primary Containment Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2012, at approximately 1305 hours Central Daylight Time (CDT), during performance of a surveillance procedure, a steam leak was identified on a Browns Ferry Nuclear Plant (BFN), Unit 2, High Pressure Coolant Injection (HPCI) steam line valve. The condition was evaluated and the valve was determined to be Operable. On June 12, 2012, based on advice from Engineering, Operations personnel requested a Prompt Determination of Operability. On June 13, 2012, at approximately 1700 hours CDT, the HPCI steam line valve was determined to be incapable of performing its primary containment isolation valve (PCIV) function. Due to the steam leak coming from a valve leak sealant injection port, it was estimated that the allowable primary containment leak rate was exceeded. In accordance with Technical Specification (TS) actions for an inoperable PCIV, the associated penetration was isolated, rendering the HPCI System inoperable. The TS actions were entered for the inoperable HPCI System. The root cause of the event was inadequate work instructions for ensuring the final plant configuration matched the required configuration. The corrective action to prevent recurrence is to revise the Work Control Planning Procedure to require work orders to include verification that components affected by maintenance or modification are returned to the required configuration.
2602012003 | Browns Ferry 2 | 07/10/2012 | 03/15/2013 | ML13080A02 | <strong>480V Reactor Motor Operated Valve Board 2E Failed to Manually Transfer to Alternate Power</strong><br /><i>Abstract:&nbsp;</i>On July 10, 2012, the alternate power supply for the Browns Ferry Nuclear Plant, Unit 2, 480V reactor motor operated valve (RMOV) board 2E was declared inoperable for performance of preventive maintenance (PM) activities. During these PM activities, the alternate feeder breaker was racked in and out of the cubicle. When the alternate feeder breaker was racked in after performance of PM activities, the manual trip pushbutton remained in the depressed position. On July 19, 2012, while preparing to perform PM activities, the 480V RMOV board 2E failed to manually transfer to its alternate power supply. Operations discovered the alternate feeder breaker manual trip pushbutton in the depressed position. The alternate feeder breaker would not close with this manual trip pushbutton in the depressed position. As a result, the 480V RMOV board 2E would not manually transfer and would also not have automatically transferred to its alternate power supply. The root cause was a process failure to provide positive verification that the critical aspects of the alternate feeder breaker were acceptable before the alternate feeder breaker was returned to service. The corrective action to prevent recurrence was to revise the operating instruction to provide verification that the manual trip pushbutton returned from the depressed position after racking in the alternate feeder breaker.
2602012004 | Browns Ferry 2 | 08/17/2012 | 10/16/2012 | ML12291095 | <strong>High Pressure Coolant Injection System Rendered Inoperable due to an Inadvertent Actuation of Primary Containment Isolation System</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2012, at approximately 0445 hours Central Daylight Time (CDT), the Browns Ferry Nuclear Plant (BFN), Unit 2, High Pressure Coolant Injection (HPCI) System unexpectedly received a Group 4, Primary Containment Isolation System signal during the performance of surveillance procedure 2-SR-3.3.6.1.3(3DFT), HPCI Steam Line Space High Temperature Functional Test. On August 17, 2012, at approximately 0450 hours CDT, Operations personnel declared the HPCI System inoperable and entered Technical Specification 3.5.1 Condition C and Abnormal Operating Instruction 2-AOI-64-2B, Group 4 High Pressure Coolant Injection Isolation. The root cause of the event was the use of incorrect wire bending practices to assemble steam line space high temperature switches. The corrective action to prevent recurrence is to replace the BFN, Units 1, 2, and 3, HPCI and Reactor Core Isolation Cooling steam line space high temperature switches with switches that are designed by EGS and are supplied with Rockbestos switchboard wire, ensuring the correct wire bending practices specified in Special Instrument Instruction SII-0-TS-00-320, EGS Corporation/Fenwal Environmental Qualified Temperature Switch Assembly and Repair, have been used.
2602012005 | Browns Ferry 2, Browns Ferry 3 | 10/18/2012 | 12/17/2012 | ML12355004 | <strong>Unanalyzed Conditions Discovered During National Fire Protection Association 805 Transition Affecting Division II of the Residual Heat Removal System</strong><br /><i>Abstract:&nbsp;</i>On October 18, 2012, at approximately 1314 hours Central Daylight Time, it was determined that in the event of an Appendix R fire, fire induced circuit damage could potentially create two conditions that would prevent Browns Ferry Nuclear Plant (BFN), Units 2 and 3, Division II of the Residual Heat Removal System, Low Pressure Coolant Injection (LPCI) inboard valves from opening. First, a potential open circuit, caused by fire damage in BFN, Unit 3, may prevent the LPCI injection valve open contactor from energizing and inhibit the ability to open the LPCI inboard valves. Second, a potential hot short, caused by fire damage in BFN, Unit 2 or 3, could spuriously close LPCI inboard valves in a way that by-passes the close limit switch or torque switch, meaning that the valve could continue to drive itself closed to the point of damaging the valve. This potential damage could result in the inability to open the valve electrically or mechanically. The root cause was determined to be legacy human performance errors that occurred during the resolution of Appendix R cable routing failures. The corrective actions to prevent recurrence are to implement a fleet wide technical human performance procedure and revise the human performance tools procedure to incorporate the five INPO Technical Conscience Principles, focus technical task risk factors, mitigation strategies, and decision making.
2602012006 | Browns Ferry 2 | 12/22/2012 | 12/06/2013 | ML13343A15 | <strong>Unplanned Automatic Reactor Scram due to Loss of Power to the Reactor Protection System</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2012, at 1152 Central Standard Time (CST), the Browns Ferry Nuclear Plant (BFN), Unit 2, reactor automatically scrammed due to actuation of the Reactor Protection System (RPS) from loss of power to both RPS buses. At 1134 CST, the 4kV Shutdown Board D unexpectedly de-energized resulting in the loss of power to the RPS 2B bus. While attempting to re-energize the RPS 2B bus, the RPS 2A bus was inadvertently de-energized resulting in the BFN, Unit 2, automatic reactor scram. During this event the Reactor Core Isolation Cooling system and the High Pressure Coolant Injection system automatically initiated as designed to restore water level above the initiation set point. All affected safety systems responded as expected for the loss of the RPS buses.<br /><br /> The root cause was that Operations' standards for the use of Error Prevention Tools were not understood nor properly applied by Operations personnel during transient plant conditions.<br /><br /> Corrective actions to prevent recurrence are: to develop and deliver training to provide expected behaviors for leaders and craft that support their roles and responsibilities, to perform paired observations between management and direct reports, from the level of department directors to first line supervisors, in order to verify or establish that the standards possessed by the department leaders are adequate and shared uniformly among the group, and to revise the Training Program Description for License Operator Requalification to specify that Operations Management provide training on standards and expectations for the implementation of the requirements of procedure OPDP-1, Conduct of Operations.
2612012001 | Robinson 2 | 01/17/2012 | 08/27/2012 | ML12250A62 | <strong>Technical Specification Required Plant Shutdown due to Missed Surveillance and Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>Improved Technical Specifications (ITS) Limiting Condition For Operation (LCO) 3.8.4 states that Train A and Train B DC electric power subsystems shall be OPERABLE in Modes 1, 2, 3, and 4. TS Surveillance Requirement (SR) 3.8.4.6 requires that the operability of Station Batteries be verified every 60 months by conducting a performance capacity test. On January 17, 2012, with H. B. Robinson Steam Electric Plant (HBRSEP), Unit No. 2, in Mode 1 at 85.5% power, it was determined that the surveillance test for the Station-B Battery had become overdue. The last performance of SR 3.8.4.6 on Station-B Battery was completed on October 12, 2005. With the addition of the 25% grace period, the performance test should have been conducted no later than January 12, 2012. As a result of the missed surveillance requirement, SR 3.8.4.6, the plant completed a Technical Specification required shutdown for failure to meet the LCO 3.8.4. SR 3.8.4.6 for the Station-B Battery was successfully completed on January 28, 2012, with a recorded capacity of 116.4%. The cause of the event was HBRSEP, Unit No. 2, not having an accurate means of monitoring ITS due dates and over due dates to support scheduling and completion of SRs required to ensure ITS compliance. The condition described in this Licensee Event Report is reportable in accordance with 10 CFR 50.73(a)(2)(i)(A), the completion of any nuclear plant shutdown required by the plant's Technical Specifications, 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant's Technical Specifications, and 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the Reactor Protection System, including a reactor trip.
2612012002 | Robinson 2 | 03/16/2012 | 05/09/2012 | ML12144A08 | <strong>Unplanned LCO 3.5.4 Entry Due to RWST Alignment to Purification</strong><br /><i>Abstract:&nbsp;</i>The Refueling Water Storage Tank (RWST) was placed on purification in accordance with OP-913, Refueling Water Purification Pump Operation, as directed from OP-301-1, Chemical And Volume Control System (Infrequent Operation), at 04:00 on March 16, 2012, to support make up of level to the RWST. The Plant was in MODE 4 with the Reactor Coolant System at approximately 285 degrees Fahrenheit. This condition, connection of the purification loop, is not currently allowed based on unresolved seismic concerns with purification piping to the RWST. This was later discovered during a log review at 05:45, and operators were immediately directed to remove the RWST from purification. Technical Specification (TS) 3.5.4 was applied from 04:00 based on when it was determined that this condition had been entered. TS 3.5.4 was exited at 06:22 when the RWST was removed from purification. The cause of this event was determined to be a result of ineffective implementation of previous corrective actions from HBRSEP, Unit No. 2 Condition Report (CR) 463557 and reported in LER 2011-001-00. Operating procedures associated with placing the non-seismic Refueling Water Purification (RWP) loop in service on seismic systems were suspended and Caution Tags (CTs) on SFPC-805A, RWP Pump Suction Isolation Valve from RWST, and SFPC-805B, RWST Return Isolation Valve were replaced with DangerTags which state "DO NOT OPERATE." The condition described in this Licensee Event Report is reportable in accordance with 10 CFR50.73(a)(2)(i)(B), Any operation or condition which was prohibited by the plant's Technical Specifications and 10 CFR 50.73(a)(2)(v)(D), Event or Condition that could have prevented fulfillment of a safety function.
2612012003 | Robinson 2 | 03/08/2012 | 08/27/2012 | ML12250A62 | <strong>Plant Modification Interfered with the Operation of Containment Wide Range Level Indicator</strong><br /><i>Abstract:&nbsp;</i>On January 19, 2012, at approximately 0557 hours EST, while the H.B. Robinson Unit 2 was shutdown in MODE 5, Condition Report (CR) 510240 was initiated documenting that an NRC inspector identified a chain interfering with the float for the Post Accident Containment Vessel (CV) Water Level Transmitter (LT) for Channel-B. The chain prevented the LT from working correctly. The CV LT was inoperable because it could not indicate a flooded containment level of 375 inches required by the Critical Safety Function Status Trees. On March 7, 2012, work was completed which removed the obstruction. This condition existed since October 15, 2005 when the chain had been installed to restrain a folding gate that is used as a radiation dose barrier during outages. This chain was intended to prevent the folding gate from interacting with safety related equipment during normal operation. LCO 3.3.3 Condition A requires an inoperable channel to be restored in 30 days and if not restored in 30 days, Condition B requires immediate action in accordance with Technical Specification (TS) 5.6.6, PAM Instrumentation Report. TS 5.6.6 is an administrative TS with a 14 day reporting requirement. Since the LT was not returned to an OPERABLE status in 30 days and the required report was not filed in 14 days, this event is reportable under 10 CFR 50.73 (a)(2)(i)(B), operation or condition which was prohibited by the plant's TS.
2612012004 | Robinson 2 | 03/28/2012 | 05/23/2012 | ML12160A05 | <strong>Reactor Tripped due to a Turbine Trip Caused by a Feedwater Isolation Signal from Steam Generator 'B' High Level</strong><br /><i>Abstract:&nbsp;</i>At 1503 hours EDT on March 28, 2012, with the unit in Mode 1 at 55% power, the H.B. Robinson Steam Electric Plant, Unit No. 2 (HBRSEP, Unit No. 2) reactor tripped due to a turbine trip caused by a Feedwater Isolation signal from Steam Generator (SG) 'B' High Level. The Feedwater Regulating Valve FCV-488 had gone 100% percent open causing a Feed Flow greater than Steam Flow alarm and the SG 'B' level to increase rapidly. The operators placed the valve in manual control and attempted to close the valve; however, the feedwater flow could not be brought under control before the SG 'B' high level set point on 2 of the 3 level protection loops initiated a Feedwater Isolation, turbine trip and corresponding reactor trip. The site failed to recognize the need for periodic replacement of low wattage control switches based on the guidance in the Control Switch Preventive Maintenance Basis Template, and the apparent lack of site Operating Experience (OE) indicating the need for preventive replacement. This resulted in no preventive maintenance on the failed switch over an extended period. The most likely cause was determined to be high resistance readings on the contacts that caused the feedwater flow signal to reduce to zero. This event is being reported pursuant to 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of any system listed in paragraph (a)(2)(iv)(B); the Reactor Protection System and Auxiliary Feedwater system.
2632012001 | Monticello | 05/08/2012 | 07/05/2012 | ML12187A77 | <strong>Degraded Voltage Transfer Scheme Not in Compliance with T.S. 3.3.8.1</strong><br /><i>Abstract:&nbsp;</i>At approximately 0900 CDT on May 8, 2012, it was determined that the Monticello Nuclear Generating Plant did not meet Technical Specification (TS) Limiting Condition for Operation 3.3.8.1 because the requirement of Table 3.3.8.1-1 for the 4.16 KV Essential Bus Degraded Voltage function time delay transfer to the Emergency Diesel Generators (EDGs) of <=9.2 seconds could not be met under all postulated conditions. The degraded voltage transfer scheme has the ability to transfer to a standby offsite source (1AR Transformer) which, under a degraded voltage condition, would delay the transfer to the EDGs an additional 5 seconds. Both EDGs were subsequently declared inoperable. During the development of the 1980's modification that added the 1AR time delay degraded voltage requirements, the TS submittal did not include the total time delay required to disconnect the Essential Buses from all Offsite Sources. The interim corrective action was to remove 1AR Transformer from service which disabled the additional 5 second degraded time delay and restored TS compliance. A license amendment request has also been submitted which, pending NRC approval, would remove the 5 second time delay for 1AR Transformer and directly transfer the Essential Buses to the EDGs under a degraded voltage condition. This would allow 1AR Transformer to be returned to service.
2632012003 | Monticello | 09/25/2012 | 01/18/2013 | ML13022A48 | <strong>Automatic Reactor Scram During Maintenance on 4160V 12-Bus Ammeter</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2012 at the Monticello Nuclear Generating Plant, during maintenance on 4160V 12-Bus ammeter switch, a 12-Bus lockout occurred removing power from 12-Reactor Feed Pump and 12-Reactor Recirculation pump. With both Main Feed Regulating Valves in auto, the level transient reached the Reactor Water Level Hi Hi setpoint (+48 inches). The Main Turbine and 11-Reactor Feed Pump tripped as designed and a Reactor scram occurred. The root cause for the 12-Bus lockout was determined to be that fleet work management guidance does not require the appropriate level of detail needed to expose the potential impact when injecting energy into plant structures, systems, and components. Additionally, a second root cause focused on the level transient determined that the Digital Feedwater Control System (DFCS) was not designed to control reactor pressure vessel level below +48 inches on a 12-Bus lockout from 100% power. The organization had a mind-set based on procedure bases and training that DFCS in automatic would maintain reactor level below +48 inches following a 12-Bus lockout. Immediate corrective actions were to remove the test equipment and reset the 12-Bus lockout. Long-term corrective actions include revising the work management guidance to require the appropriate level of detail. Classroom and simulator training for all licensed operators will be performed on this event and will include changes to the abnormal operating procedures to address DFCS.
2632012004 | Monticello | 10/20/2009 | 11/30/2012 | ML12338A03 | <strong>High Pressure Coolant Injection Inoperable when Inverter is Out of Service</strong><br /><i>Abstract:&nbsp;</i>On October 20, 2009 at 0316 hours, the Division 2 120Vac Class IE Inverter was removed from service and supported loads supplied by the maintenance bypass source. Removing the Inverter from service caused the High Pressure Coolant Injection system to be inoperable. Monticello Nuclear Generating Plant (MNGP) engineering confirmed the condition through a past operability review that was completed on October 8, 2012. The apparent cause was determined to be MNGP's response to Generic Letter 1991-11 failed to properly evaluate the effect on inverter supplied loads when removing an inverter from service and supplying its loads from the maintenance bypass source. Based on the fact that the response to Generic Letter 1991-11 was submitted more than 20 years ago, specific details as to why this evaluation was not performed could not be identified. Corrective actions include performing an evaluation of the impact on the operability of safety-related loads with the Inverter out of service and powered by maintenance bypass source. Updated controls for removing the Division 1 and Division 2 Inverters from service and supplying the inverter loads from the maintenance bypass source will also be developed.
2632012005 | Monticello | 11/12/2012 | 01/11/2013 | ML13014A12 | <strong>Partial Group II Isolation During Removal of Original Steam Dryer</strong><br /><i>Abstract:&nbsp;</i>On November 12, 2012 at 1551 hours, the "A" Refuel Floor Radiation Monitor tripped during movement of the steam dryer on the reactor building refuel floor. This resulted in isolation of the drywell containment air monitor and the oxygen analyzer primary containment isolation valves. The signal also resulted in a reactor building isolation (Secondary Containment), initiation of the "A" Standby Gas Treatment, and transfer of the Control Room Ventilation to the High Radiation Mode. The apparent cause was determined to be the infrequently performed test or evolution process was not adequately tied to the risk management process to ensure that the high risk plans and validation of critical parameters were reviewed prior to execution. Corrective actions to address the apparent cause include updating the infrequently performed test or evolution process to institutionalize a review of the high risk plan and mitigating actions including validation of critical parameters prior to work.
2652012001 | Quad Cities 2 | 03/19/2012 | 05/18/2012 | ML12152A15 | <strong>Main Steam Isolation Valve Local Leak Rate Test Exceeds Technical Specifications Limit</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2012, at 0830 hours, with Unit 2 shutdown for refuel outage Q2R21, the as-found local leak rate tests (LLRT) for the four main steam lines (MSL) were performed following closure of the main steam isolation valves (MSIV). The initial as-found LLRT on the "B" MSL MSIVs exceeded the minimum pathway criteria (smaller leakage in a line) of the Technical Specification (TS) Surveillance (34 standard cubic feet/hour (scfh)). Recorded leakage was 54.50 scfh inboard, and 45.60 scfh outboard. The total combined as-found min-path LLRT results for all MSIVs (49.12 scfh) did not exceed the TS Surveillance criteria limit allowed (86 scfh), verifying primary containment integrity during the past operating cycle. Therefore, the MSIVs were capable of performing their intended function prior to shutdown. The valves were disassembled and inspected. No abnormal wear was noted on the valve internals since some wear on the plug and seat is expected. The plugs were replaced, the valve seats were repaired by skim cuts, and the valves were reassembled. The as-left leak rate tests were satisfactory. The most likely cause for the higher than expected leakages has been determined to be a valve design that allows for minor seat ring wear to degrade the LLRT performance which may also result in misalignment between the plug and the seat ring. Corrective actions included repairing the valves. Future corrective actions include pursuing a new plug and seat design, as well as improve trending methodology for predicting MSIV LLRT failures. The safety significance of this event was minimal. Although this MSIV line/path leak rate exceeded the as-found TS limit, the combined MSIV path leak rate TS limit was not exceeded. This event is therefore, a past operation or condition which was prohibited by the plant Technical Specifications, and is therefore reportable per 10 CFR 50.73(a)(2)(i)(B).
2652012002 | Quad Cities 2 | 04/04/2012 | 06/04/2012 | ML12165A24 | <strong>Reactor Vessel Instrument Nozzle Leakage due to Intergranular Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2012, at 1716 hrs, while Unit 2 was shutdown for refueling outage Q2R21, leakage was identified exiting from a 2-inch reactor vessel instrumentation nozzle (N-11B) during a Reactor Pressure Vessel (RPV) pressure test. The leakage amount was approximately 60 drops per minute (dpm). The vessel penetration (N-11B) provides the connection point for the reference leg of the "B"-train of the Reactor Vessel Level Instrumentation System (RVLIS). The leakage originated from the area where the nozzle penetrates the vessel wall. The nozzle is welded on the inside of the vessel, so the actual attachment weld could not be examined. The RPV pressure test was stopped and the reactor vessel depressurized to allow additional inspections and necessary repairs. The most probable cause of the leakage was determined to be Intergranular Stress Corrosion Cracking (IGSCC) that was likely influenced by higher residual stresses that remained in the nozzle assembly following nozzle replacement in 1970, prior to the initial start-up of Unit 2. Corrective actions included repairing the nozzle with IGSCC resistant material, and obtaining approval of a Relief Request from the NRC prior to startup to allow the flaw to remain for one operating cycle. Future corrective actions include inspecting other similar RPV nozzles, and performing a specialized flaw evaluation to support safe operation for continued operating cycles. The safety significance of this event was minimal given the leakage was very small, was found while the reactor was shutdown, and if leaked during plant operation, did not exceed Technical Specification (TS) leakage limits for unidentified drywell leakage. Given the impact on the reactor vessel pressure boundary, this report is submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(ii)(A), which requires the reporting of any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.
2652012003 | Quad Cities 2, Quad Cities 1 | 04/18/2012 | 06/14/2012 | ML12174A20 | <strong>Unit 2 Automatic Reactor Scram due to Digital Electro Hydraulic Control System Failure</strong><br /><i>Abstract:&nbsp;</i>On April 18, 2012, at 1511 hrs, while at low power conditions after refueling outage Q2R21, an automatic reactor scram occurred on Unit 2 due to high reactor pressure. The pressure increase occurred during post-modification testing on the main generator automatic voltage regulator (AVR) which had been upgraded during refueling outage Q2R21. The testing included a generator load reject, which was in progress when the pressure transient occurred. There were no complications during the reactor scram and subsequent turbine trip, and all systems functioned as required. Operators performed required actions safely and in accordance with procedures and training. The cause of the automatic scram was due to high reactor pressure created by the load rejection associated with the main generator voltage regulator testing, coincident with unresponsive opening demand of turbine control valves (TCVs) that impacted the turbine bypass valves (TBVs) ability to control reactor pressure. Since the digital electro hydraulic control (DEHC) system design lacked the required Intercept (IV) EHC shutoff valves, this resulted in low EHC pressure and caused the TCVs to be unresponsive. Unit 1 was unaffected by the event and remained at 100% power. Corrective actions included evaluating the impact of the event on the operability of the TBVs, and applying a Minimum Critical Power Ratio (MCPR) Operating Penalty (TS 3.7.7) when reactor power is between 25% and 50%. Future corrective actions include development of a hardware/software modification to the DEHC system to correct the design deficiency. The safety significance of this event was minimal. This event is reportable (Unit 2) per 10 CFR 50.73(a)(2)(iv)(A), which requires the reporting of any event or condition that resulted in manual or automatic actuation of the reactor protection system (RPS), including reactor scram; (Units 1 and 2) 10 CFR 50.73(a)(2)(i)(B), which requires the reporting of any operation or condition which was prohibited by the plant's Technical Specifications; and (Units 1 and 2) 10 CFR 50.73 (a)(2)(v)(C), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems needed to control the release of radioactive material.
2652012004 | Quad Cities 2 | 09/21/2012 | 11/20/2012 | ML12334A40 | <strong>Drywell Radiation Monitor Failed Downscale</strong><br /><i>Abstract:&nbsp;</i>At 1449 hours on September 21, 2012, the Unit 2, 2B Drywell Radiation Monitor was found downscale during control room panel monitoring. This monitor provides the input into one division of the primary containment isolation logic for a Group 2 isolation. Troubleshooting identified that this one of the two divisions of the isolation logic was inoperable. As a result, the division was placed in a tripped condition at approximately 1515 hours in accordance with Technical Specifications 3.3.6.1, Conditions A and B; and 3.3.3.1, Condition A. The cause of the event was monitor failure due to dust and dirt inside the module which caused some of the sub-components to malfunction and result in a downscale indication. Inadequate periodic maintenance, in combination with the chassis ventilation design had allowed the components inside the chassis to be vulnerable to dust and dirt buildup since its installation. Corrective actions included immediate replacement of the 2B Drywell Radiation monitor to return it to an operable condition. Future corrective actions include, detailed failure analysis by the vendor, and development of improved preventive maintenance activities on the monitor. The safety significance of this event was minimal. Since both divisions of drywell radiation monitoring are required to complete the Group 2 isolation logic, but only one was available during this event, this report is submitted in accordance with the requirements of 10 CFR 50.73 (a)(2)(v)(C), and (a)(2)(v)(D), which requires the reporting of any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: control the release of radioactive material, and mitigate the consequences of an accident.
2662012001 | Point Beach 1, Point Beach 2 | 04/26/2012 | 06/25/2012 | ML12178A41 | <strong>Operability of G-01 and G-02 Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>NextEra Energy Point Beach (NextEra) is providing this voluntary LER regarding the Operability of the Point Beach Nuclear Plant (PBNP) G-01 and G-02 Emergency Diesel Generators (EDGs). Emergency Diesel Generators G-03 and G-04 were not affected by the condition. In an NRC Task Interface Agreement (TIA), Evaluation of Point Beach Nuclear Plant Tornado Missile Protection Licensing Basis, dated August 16, 2011 (TIA 2011-011), the NRC concluded that the licensing basis for Point Beach Nuclear Plant (PBNP) required the EDG exhaust stacks to be protected from tornado missiles. NextEra determined in a prompt operability determination (POD) that the EDGs were Operable, but non-conforming. The NRC issued a second TIA, Applicability of GDC Requirements in Operability Determinations and Assessment of the Point Beach Operability Determination for Emergency Diesel Generators With Respect to Tornado Missiles, dated April 24, 2012 (TIA 2012-07). Based on TIA 2012-07, PBNP Operations directed that Operability of the EDGs should be reevaluated. Based on concerns with TIA 2012-07, PBNP Operations conservatively declared the EDGs Inoperable pending further evaluation, and entered the 7-day Technical Specification Action Condition (TSAC) for TS 3.8.1. A protective structure was designed and built around the EDG exhaust stacks and PBNP Operations subsequently declared the EDGs Operable.
2662012002 | Point Beach 1 | 05/21/2012 | 12/18/2012 | ML12354A46 | <strong>Condition Prohibited by Technical Specification 3.7.5, Auxiliary Feedwater</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2012 at 0054, the 1P-29 Turbine Driven Auxiliary Feedwater Pump (TDAFWP) was removed from service to perform quarterly testing. During the testing a degraded coupling condition was identified. At 0319 on May 21, 2012, the quarterly test was aborted and an investigation was started to determine the cause of the degraded coupling. During the investigation a misalignment between the 1P-29 turbine and pump was discovered. NextEra concluded that the misalignment between the turbine and pump was the cause of the degraded coupling. The coupling was replaced and the turbine and pump were re-aligned. A technical assessment for reportability was completed on June 21, 2012. NextEra determined that from the time surveillance was performed on the 1P-29 TDAFWP on March 13, 2012, until it was returned to service at 1900 on May 23, 2012, 1P-29 may not have been able to perform its design and licensing basis functions. Therefore, Technical Specification 3.7.5 was not met. Pursuant to 10 CFR 50.73(a)(2)(i)(B), the event is reportable as a condition prohibited by Technical Specifications.
2662012003 | Point Beach 1, Point Beach 2 | 06/06/2011 | 08/28/2012 | ML12236A14 | <strong>2B-04 Safeguards 480V Bus De-Energized</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2011, while Unit 1 was in MODE 1 and Unit 2 was in MODE 4, the feeder breaker to safeguards 480V bus, 2B-04, opened on overcurrent. The feeder breaker tripped on overload after energizing a pressurizer heater group. This trip resulted in deenergizing electrical bus 2B-04. No other breakers tripped during this event. The results of an investigation determined the overload trip was improperly set low. A technical assessment for reportability was completed. Nextera Energy Point Beach, LLC (NextEra) determined that electrical bus 2B-04 was inoperable for specific time periods from March 23, 2011 through June 7, 2011 for Unit 1 and Unit 2. Technical Specification Limiting Conditions for Operation (LCOs) and associated Action Conditions (TSACs) for TS 3.8.9 Distribution System - Operating (TSAC 3.8.9 A and B), TS 3.8.10 Distribution Systems - Shutdown (TSAC 3.8.10 A), and TS 3.5.3 ECCS - Shutdown (TSAC 3.5.3 A and B) were not met during specific time periods. Therefore, pursuant to 10 CFR 50.73(a)(2)(i)(B), the event is reportable as a condition prohibited by Technical Specifications. This event is also being reported pursuant to 10 CFR 50.73(a)(2)(v)(D), any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. The feeder breaker overload trip setting was corrected.
2662012004 | Point Beach 1 | 08/14/2012 | 10/03/2012 | ML12277A32 | <strong>Unit 1 Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2012 at 2031, a Point Beach Nuclear Plant (PBNP) Unit 1 manual reactor trip was actuated due to indications of a loss of load to the main turbine. At approximately 2031 alarms were received in the control room indicating reduced PBNP Unit 1 turbine first stage pressure and generator megawatts, indicative of a reduction in turbine load. Control rods were responding as designed by inserting into the reactor to reduce reactor power. Based on these indications, the Shift Manager directed that the reactor be shutdown by manually actuating the reactor protection system. No automatic reactor protection setpoints were exceeded and an automatic shutdown was not actuated or required. Based on troubleshooting, NextEra determined that the loss of turbine load was due to a failure of the main speed channel card in the electro-hydraulic (EH) system. The speed channel card was replaced. Pursuant to 10 CFR 50.73 (a)(2)(iv)(A), the event is reportable as an event or condition that resulted in manual actuation of the reactor protection system.
2662012005 | Point Beach 1 | 10/08/2012 | 06/27/2013 | ML13196A34 | <strong>Potential Operation Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2012, at 2255, Point Beach Nuclear Plant (PBNP) Operators declared Unit 1 Containment INOPERABLE due to a Service Water (SW) leak into Containment. Unit 1 entered Technical Specification Action Conditions (TSAC) for LCO 3.6.1, Containment. These TSACs required restoring Containment to OPERABLE status within one hour, followed by MODE 3 in the next six hours and MODE 5 in 36 hours. <br><br> The leak was found to be on the return piping for the B Train reactor cavity cooler and was isolated by shutting the containment isolation valves. The leak was stopped, as verified by local observation. Containment was then declared OPERABLE, and the TSACs were exited. The degraded pipe was repaired and returned to service on October 26, 2012. <br><br> After the event, a question was raised relative to the use of the closed valves to re-establish an operable containment penetration with a closed system inside containment since the valves had not been leak rate tested. Sufficient documentation was not provided to support operability. This event is being reported as a condition which was prohibited by Technical Specifications pursuant to 10 CFR 50.73(a)(2)(i)(B).
2692012001 | Oconee 1, Oconee 2, Oconee 3 | 04/05/2012 | 06/04/2012 | ML12157A32 | <strong>Unanalyzed Conditions Exist for Standby Shutdown Facility Mitigated Events</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2012, Duke Energy entered into the corrective action program that unanalyzed conditions exist for Standby Shutdown Facility (SSF) mitigated events since associated thermal and hydraulic analyses do not consider Oconee Nuclear Station (ONS) operating conditions during shutdown and startup, especially those involving lower operating modes and lower decay heat. Subsequent evaluation and analysis efforts did not support SSF operability for all credited events, and on April 6, 2012, the NRC was notified via Event Notification System (ENS) Report Number 47810. Subsequently, it was determined that the SSF would be declared inoperable for Units 1 and 2 when less than 85% power and Unit 3 below 70% power, or for any unit operating at full power less than four effective full power days (4 EFPDs) since its most recent shutdown. The apparent cause of this condition was inadequate transfer of licensing information during initial development of the SSF Technical Specifications.
2712012001 | Vermont Yankee | 05/24/2012 | 09/12/2012 | ML12262A35 | <strong>Potential to Flood Switchgear Rooms due to Missing Conduit Flood Seal</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2012, with the plant at 100 percent power, Vermont Yankee (VY) discovered the potential for water intrusion into the Vital Switchgear Rooms via an underground spare conduit that was found to be missing its flood seal. The missing flood seal compromised the interior flood design controls for the Switchgear Rooms. Were flooding of the Switchgear Rooms to occur, the operability of switchgear providing electrical power to Division I and II Engineered Safety Feature systems and Emergency Core Cooling Systems could be affected. This could threaten the capability to shut down the reactor and maintain it in a safe shutdown condition. The causal analysis determined that the flood seal used in this spare conduit did not provide an adequate seal to prevent the flood seal from becoming dislodged. The condition was corrected by installing a new flood seal of a different design, thus removing the potential flood path. Plant procedure requires inspection of the Switchgear Rooms during a flood event and includes actions that would have mitigated any flooding; therefore this event did not pose a threat to public health and safety.
2722012001 | Salem 1 | 04/30/2012 | 06/27/2012 | ML12184008 | <strong>Single Train Actuation of Safety Injection due to Failure of Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>On April 30th, 2012, at 1003 hours. Salem Unit 1 experienced an invalid Train A Safety Injection, Reactor Trip, Main Steam Line Isolation, Emergency Diesel Generator start, Phase A Isolation, and start of the Auxiliary Feedwater Pumps. Technical Specification 3.0.3 was entered due to both trains of Safety Injection actuation logic being blocked after actuation per system design. The plant exited Technical Specification 3.0.3 at 1428 hrs. when Train B of the Solid State Protection System was reset. The operating crew however, failed to recognize all Technical Specification Action Statements associated with inoperability of a single train of the Solid State Protection System and did not meet the requirement for entry into Mode 4. On May 1st at 0802 hours operators identified the applicable Action Statement and commenced a plant cooldown. The plant entered Mode 4 at 1739 hrs. and entered Mode 5 at 2129 hours. The Safety Injection was caused by invalid actuation of Train A of the Solid State Protection System. The apparent cause of the failure to recognize entry into Technical Specification Action Statements was a lack of procedural adherence. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) for actuation of the Reactor Protection and Safety Injection systems and under 10 CFR50.73(a)(2)(i)(B) for conditions which were prohibited by the plant's Technical Specifications.
2722012004 | Salem 1 | 10/30/2012 | 12/26/2012 | ML13002A00 | <strong>Loss of Circulating Water and Manual Reactor Trip Due to Hurricane Sandy</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2012, Salem Unit 1 was in Mode 1, operating at 100% power when its Circulating Water Intake structure was subjected to heavy river debris from Hurricane Sandy. At 0109 hours, the reactor was manually tripped in accordance with operating procedures due to a loss of four of its six Circulating Water Pumps (CWP) {KE/P}. An automatic start of the Auxiliary Feedwater system occurred as expected on unit trip due to low Steam Generator water levels. By 0118 hours, the two remaining CWPs had been tripped due to continuing heavy debris buildup on the Circulating Water (CW) Traveling Screens {KE/SCN}. The unit was stabilized in Mode 3, Hot Standby conditions and operators transitioned from emergency response to normal operating procedures at 0141 hours. A Main Steam Line Isolation was manually initiated at 0513 hours in response to a loss of condenser vacuum. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A), for actuation of the Reactor Protection, Auxiliary Feedwater and Main Steam Line Isolation systems.
2722012005 | Salem 1 | 12/21/2012 | 02/14/2013 | ML13086A09 | <strong>Reactor Trip due to Failure of the Main Power Transformer Overexcitation Relay</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2012, at 0527 hours, Salem Unit 1 was in Mode 1 operating at 100% rated thermal power when it experienced an automatic reactor trip due to a turbine trip. The turbine trip was the result of a Main Generator trip due to a Main Power Transformer overexcitation signal. An automatic start of the Auxiliary Feedwater system occurred as expected on unit trip due to low Steam Generator water levels. The unit was stabilized in Mode 3, Hot Standby conditions and operators transitioned to normal operating procedures at 0621 hours. The cause of this event is attributed to setpoint drift of the Main Power Transformer General Electric type STV Overexcitation trip relay. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A), for actuation of the Reactor Protection and Auxiliary Feedwater systems.
2752012002 | Diablo Canyon 1 | 03/08/2012 | 05/07/2012 | ML12129A10 | <strong>Failure to Comply with Technical Specification 3.0.3 Time Requirement</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2012, at 1850 PST, Diablo Canyon Power Plant (DCPP) operators declared two of the three steam generator (SG) 1-1 narrow-range low-low level transmitter (LT) channels inoperable placing Unit 1 in Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 as a result of evaluating Rosemount pressure transmitter (PT) 10 CFR Part 21 report described in NRC Event Notification (EN) 47693. Eight of these PTs were installed on LT channels for DCPP SGs, but only SG 1-1 had the subject PTs installed on two of the three low-low level channels. At 1953 PST (63 minutes later), after adjusting the setpoints, operators declared the subject LTs operable, and exited TS LCO 3.0.3. On March 9, 2012, DCPP voluntarily reported this event to the NRC (EN 47728). This event is being reported as a condition prohibited by TS per 10 CFR 50.73(a)(2)(i)(13), since DCPP remained in LCO 3.0.3 in excess of 1 hour and operators did not initiate a shutdown (addition of negative reactivity). Operators delayed initiation of a shutdown transient because of imminent completion of corrective maintenance, consistent with NRC Technical Interface Agreement 92-08, "Use of Shutdown Times for Corrective Maintenance." Subsequent engineering evaluations concluded the subject PTs would still have been able to perform their safety functions prior to adjusting the setpoints.
2752012003 | Diablo Canyon 1 | 06/07/2012 | 08/06/2012 | ML12220A16 | <strong>Low Temperature Overpressure Protection System Inoperable due to Human Performance Error</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2012, at 0129 PDT, Pacific Gas and Electric Company (PG&E) declared both trains of the Low Temperature Overpressure Protection (LTOP) system inoperable when the vital 120 VAC Panel PY13 was de-energized due to a human performance error. Unit 1 was in Mode 5 and the reactor coolant system (RCS) loops were not filled. Plant technicians were troubleshooting a de-energized vital 120 VAC Panel PY14 that had resulted from the supply breaker inadvertently tripping open. During troubleshooting, a plant technician incorrectly opened the supply breaker to Panel PY13 instead of PY14. With PY14 de-energized, one train of LTOP was inoperable due to loss of signal from RCS Wide Range Pressure Transmitter PT-405A. With PY13 de-energized, the second train of LTOP was rendered inoperable due to loss of signal from RCS Wide Range Pressure Transmitter PT-403A. Plant staff immediately recognized the error and the technician closed the PY13 supply breaker, thereby re-energizing Panel PY13, returning one train of LTOP to service. On June 7, 2012, at 0856 PDT, PG&E made an 8-hour non-emergency report (Reference NRC Event Notification 48002) under 10 CFR 50.72(b)(3)(v)(D). As corrective actions, PG&E will conduct human performance skills assessments for Electrical Maintenance (EM) personnel, reinforce human performance expectations with EM supervisors, and revise troubleshooting standards.
2752012004 | Diablo Canyon 1 | 06/13/2012 | 08/13/2012 | ML12227A29 | <strong>Mode Transition with Turbine-Driven Auxiliary Feedwater Pump 1-1 Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2012, at 1115 PDT, during the 17th Refueling Outage for Unit 1 (1R17), Diablo Canyon Power Plant (DCPP) entered Technical Specification (TS) 3.7.5.B, due to one auxiliary feedwater (AFW) train being inoperable in Mode 3. After entering Mode 3, steam turbine-driven AFW Pump (TD AFW PP) 1-1 failed its routine and post-maintenance surveillance testing when the pump speed was higher than the acceptable limit and could not be lowered. Plant operators declared TD AFW PP 1-1 inoperable as required by TS 3.7.5. TS 3.7.5.B.1 requires action to restore the AFW train to operable within 72 hours and 10 days from discovery of failure to meet the Liming Condition for Operation. Mechanical Maintenance (MM) rebuilt TD AFW PP Governor Valve FCV-15 and replaced the valve stem during 1R17. MM reassembled the valve and installed the stem positioning jam nuts. However, due to inadequately detailed work instructions, the jam nuts were installed such that the valve could not be fully closed. The procedure used to perform the work did not include steps requiring a final verification that the valve would fully close. During troubleshooting activities, MM confirmed that FCV-15 was partially open when it should have been fully closed. After repair and reassembly of FCV-15, plant operators successfully completed surveillance testing for TD AFW PP 1-1. On June 14, 2012, at 2256 PDT, plant operators declared the AFW train operable within the TS time limit imposed. DCPP will revise plant procedures to provide detailed instructions to verify a full-closed valve position.
2752012005 | Diablo Canyon 1, Diablo Canyon 2 | 07/05/2012 | 06/03/2013 | ML13155A23 | <strong>Unanalyzed Condition due to Nonconservative Change in Atmospheric Dispersion Factor</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2012, Pacific Gas and Electric Company (PG&E) identified a nonconservative change in the Diablo Canyon Power Plant (DCPP) Updated Final Safety Analysis Report (UFSAR) Chapter 15, "Accident Analyses," control room (CR) atmospheric dispersion factor (X/Q) methodology, made in Revision 2 of the DCPP UFSAR in 1986. As a result of further investigation into the adequacy of the original analyses, on August 28, 2012, PG&E identified additional release pathways that had not been correctly modeled in the original analyses and could affect the CR operator dose following a large break loss of cooling accident. Consequently, PG&E declared the CR Envelope inoperable and established mitigative actions. PG&E concluded that the CR Ventilation System (CRVS) would not have been capable of performing its safety function. PG&E has since established modifications and compensatory measures to ensure the containment, CR Envelope/CRVS, and fuel handling building ventilation system safety functions remain capable of satisfying General Design Criterion 19 limits.<br><br> The cause of this event was determined to be an inadequate design control process in 1986, whereby the analysis change was made without evaluating the change in accordance with 10 CFR 50.59 to determine whether or not prior NRC review and approval was required. The corrective actions include 1) revising the X/Qs used in the analyses and incorporate them into the DCPP licensing basis, and 2) completing the licensing basis verification project that is reviewing, validating, and revising the current DCPP licensing basis.<br><br> This condition did not have an adverse effect on the health, and safety of the public.
2752012006 | Diablo Canyon 1, Diablo Canyon 2 | 08/17/2012 | 10/16/2012 | ML12290A67 | <strong>Violation of Technical Specifications due to Incorrect Bases</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2012, Pacific Gas & Electric Company (PG&E) identified that the intent of Diablo Canyon Power Plant's (DCPP's) Auxiliary Building Ventilation System (ABVS) Technical Specification (TS) 3.7.12, ''Auxiliary Building Ventilation System," had been changed via a revision to the TS Bases Section 3.7.12 in 2002. This change eliminated the ABVS function to cool emergency core cooling system motors and eliminated the ABVS supply fans from the definition of an operable ABVS train. Following the 2002 change, contrary to the original intent of TS 3.7.12, both trains of supply fans were occasionally removed from service at the same time for maintenance, and single supply fans were removed from service longer than would have been permitted by TS 3.7.12. These events are therefore reported under 10 CFR 50.73(a)(2)(i)(B). PG&E has restored TS Bases 3.7.12 back to the applicable TS bases previously reviewed and approved by the NRC in DCPP License Amendment 135 in NRC Letter, "Conversion To Improved Technical Specifications For Diablo Canyon Power Plant, Units 1 and 2 - Amendment No. 135 to Facility Operating License Nos. DPR-80 and DPR-82 (TAC Nos. M98984 and M98985)," dated May 28, 1999.
2752012008 | Diablo Canyon 1, Diablo Canyon 2 | 11/27/2012 | 01/24/2013 | ML13025A16 | <strong>Loss of Control Room Ventilation System due to Inadequate Design</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2012, at 2038 PST, while performing a functional test of the Control Room Ventilation System (CRVS) pressurization system using surveillance test procedure (STP) 1-118A, ''Functional Test of Control Room Pressurization Rad Monitors RM-51, 52, 53, and 54," Pacific Gas and Electric Company (PG&E) identified that none of the four CRVS pressurization fans would continuously operate if they started in response to a Phase A or control room radiation atmosphere intake actuation signal. Operators declared the Units 1 and 2 CRVS actuation instrumentation and CRVS inoperable and entered Technical Specifications (TS) 3.3.7, "Control Room Ventilation System (CRVS) Actuation Instrumentation," and TS 3.7.10, "Control Room Ventilation System (CRVS)," respectively. PG&E reports this condition in accordance with 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(v)(D), and 10 CFR 50.73(a)(2)(vii). Following troubleshooting activities in response to this event, PG&E developed, issued, and implemented a design change to modify the logic scheme for the CRVS pressurization fans to bypass the opposite unit pressure switch interlocks for a running CRVS pressurization fan. Investigation following the initial failure determined that these interlocks were not necessary. PG&E performed an apparent cause evaluation and concluded that the loss of CRVS was due to inadequate design controls.
2772012001 | Peach Bottom 2 | 09/25/2012 | 11/02/2012 | ML12311A02 | <strong>Laboratory Analysis Identifies Safety Relief Valves and Safety Valve Set Point Deficiencies</strong><br /><i>Abstract:&nbsp;</i>Based on information received from a laboratory performing Safety Relief Valve (SRV) / Safety Valve (SV) as-found testing, Site Engineering personnel determined on 9/25/12 that SRV / SV setpoint deficiencies existed with six SRVs and one SV that were in place during the Unit 2 19th operating cycle. The SRVs / SV were determined to have their as-found setpoints outside of the Technical Specification allowable ± 1% tolerance. The six SRVs outside of their Technical Specification (TS) allowable setpoint range were within the ASME Code allowable ± 3% tolerance. The one SV outside of its TS allowable setpoint range also exceeded the ASME Code allowable ± 3% tolerance. The cause of the SRVs / SV being outside of their allowable as-found setpoints is due to setpoint drift. The SRVs / SV were replaced with refurbished SRVs / SV for the 20th Unit 2 operating cycle. There were previous LERs identified involving SRVs / SVs exceeding their Technical Specification ± 1% setpoint requirement. There were no actual safety consequences associated with this event.
2772012002 | Peach Bottom 2 | 10/01/2012 | 11/21/2012 | ML12333A00 | <strong>Common Cause Inoperability of Reactor Protection System Turbine Control Valve Instruments</strong><br /><i>Abstract:&nbsp;</i>Based on surveillance testing performed on 10/01/12 during the P2R19 refueling outage, Instrumentation and Controls (I&C) personnel identified that two of the four instruments used to perform the Reactor Protection System (RPS) scram and End-of-Cycle Recirculation Pump Trip (EOC-RPT) functions for Turbine Control Valve (TCV) Fast Closure were outside of their Technical Specification allowable value of >= 500 psig trip oil pressure. The 'A' pressure sensing instrument (PS-4121A) was found at a trip setting of 495 psig and the 'B' pressure sensing instrument (PS-4121B) was found at a trip setting of 493 psig. The cause of this event is due to instrument drift. This occurrence is reportable as a result of a common cause inoperability that resulted in two instruments drifting low outside of the Technical Specification allowable value. The 'A' and 'B' instruments were replaced and calibrated to within acceptable limits. There were no actual safety consequences associated with this event. If an operational transient would have occurred during power operations, the 'C' and 'D' instrument channels were operable and would have provided the RPS scram and EOC-RPT trip functions.
2782012001 | Peach Bottom 3 | 04/19/2012 | 06/13/2012 | ML12167A27 | <strong>Concurrent Inoperability of Two Trains of Core Spray Pressure Switches Results in Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On 4/18/12, during a calibration surveillance test for the 'A' Core Spray Pump, a differential pressure indicating switch was found to be out of calibration. The switch is used to determine if the minimum flow bypass valve should be opened or closed. On 4/19/12, the same test was performed on the corresponding switch for the `D' Core Spray Pump and the switch was found to be out of calibration. This occurrence is reportable since both Core Spray subsystems were concurrently inoperable due to a single cause. The preferred method for corrective maintenance had been replacement of the entire pressure switch. Replacement and obtaining replacement parts became increasingly difficult during a period of time when manufacture of qualified Barton switches was interrupted. As a result, PBAPS began to place more emphasis on adjustments to the internal components of the switch instead of replacement. The declining trend was due to insufficient knowledge and skill by maintenance personnel to effectively troubleshoot and maintain the switches. In addition, maintenance procedures did not provide adequate guidance for detecting component failures and to differentiate them from instrument drift. Corrective actions include replacement of the eight Barton pressure switches used for low flow protection of the Units 2 and 3 Core Spray pumps. A site training and qualification program is being developed to establish a group of subject matter experts for Barton pressure switches. Also, procedure enhancements have been made to provide improved guidance for troubleshooting. There were no actual safety consequences as a result of this event.
2782012002 | Peach Bottom 3 | 05/17/2012 | 08/22/2012 | ML12240A01 | <strong>Failure of Primary Containment Isolation Valve due to Foreign Material Results in Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On June 24, 2012, during a surveillance test for the High Pressure Coolant Injection (HPCI) system, primary containment isolation valve (PCIV) AO-3-23-137 failed to close. Investigation determined a triangular, metallic piece of foreign material was lodged between the valve poppet and the valve seat. The PCIV is located on a 2-inch diameter condensate drain line that is connected to the HPCI pump turbine steam exhaust line and is required to close upon receipt of a containment isolation signal. The material was likely in the valve since May 17, 2012, resulting in the valve being inoperable for a period of 38 days. With one inoperable PCIV, Technical Specifications require the affected containment penetration flow path to be isolated in four hours. This was not done, resulting in a condition prohibited by Technical Specifications. The foreign material was removed, the valve seat was repaired and the valve was returned to an operable status on June 27, 2012. It was determined that the foreign material was likely a piece from a partition in the reversing chamber of the HPCI turbine. Inspection of the system will be performed during a future refueling outage to identify any additional foreign material. This event did not affect operability of the HPCI system. There were no actual safety consequences as a result of this event.
2782012003 | Peach Bottom 3 | 10/04/2012 | 11/30/2012 | ML12335A33 | <strong>Loss of Control Room Emergency Ventilation Function due to Failure of Ventilation Fan to Start</strong><br /><i>Abstract:&nbsp;</i>On October 4, 2012, during surveillance testing of a 4 kV emergency bus, Operations personnel were in the process of placing the Main Control Room Emergency Ventilation (MCREV) System in service. When an initiation signal was generated, with the "A" MCREV fan control switch positioned in 'Auto', the fan did not start as expected. The "B" MCREV fan started approximately 45 seconds later, as designed for the fan in standby. The bus that powers the "B" MCREV train was energized, but was considered inoperable due to testing and other work being performed. With both MCREV subsystems inoperable, Technical Specification (TS) 3.7.4 Condition E was entered, which requires the plant to be in Mode 3 in 12 hours. The cause of this event was that the switch was positioned such that the switch contacts were still open, which prevented a start of the "A" MCREV fan. The switch position indication is not precise enough to ensure the switch contact block is set for a given indicated position. The switch was repositioned, normal system lineup was restored and the system was returned to an operable status. This event has been placed in the station's corrective action program to further evaluate and track additional actions. There were no actual safety consequences as a result of this event.
2802012001 | Surry 1 | 02/01/2012 | 04/02/2012 | ML12102A01 | <strong>Oil Foaming in Speed Increaser Results in Inoperable Charging</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2012 at 0033 hours, with Surry Power Station Units 1 and 2 at 100% power, oil foaming was observed in the Unit 1B Charging (CH) pump gearbox sight glass. The pump was secured and oil level verified. On January 31, 2012, the 1B CH pump was started and within 30 seconds, foaming was again observed. On February 1, 2012 at 1410 hours, the 1B CH pump was declared inoperable. Air ingress was considered to be the cause and oil pump suction line fittings were tightened and sealed. The pump was started on February 4, 2012 with no foaming observed. Technical Specifications (TS) require one flow path of charging to be in operation with an additional CH pump to be operable when the reactor is critical. The TS limiting condition for operation (LCO) for one of the two CH pumps being inoperable is 72 hours. Without supporting information about the foaming, CH pump 1B was considered inoperable from January 25, 2012, when oil could not be defined in the sight glass due to foaming, until the charging pump was declared inoperable on February 1, 2012, exceeding the 72 hour LCO. Therefore, this report is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. This event was determined to be of very low safety significance and the inoperable pump did not affect the health and safety of the public.
2822012001 | Prairie Island 1 | 02/15/2012 | 04/12/2012 | ML12107A03 | <strong>Non-Conservative Calculation Of Diesel Fuel Storage Requirements</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2012, a reportability review was completed regarding an error identified in the pre-operation test records for the Unit 1 diesel generators (D1 and D2). The error, along with the subsequent discovery of an additional error regarding fuel oil energy content assumptions, affected the fuel oil storage calculation, which increased the volume of stored diesel fuel required to operate D1 or D2 and a diesel-driven cooling water pump for 14 days in the event of a postulated maximum probable flood. A review using the corrected values determined that for a single period of up to 738 continuous hours and 2202 total hours in 2010 the revised requirements were not met, rendering D1and D2 inoperable. Compensatory measures were updated to ensure a minimum 14-day supply of diesel fuel oil until a previously submitted Technical Specification amendment to revise LCOs 3.7.8 and 3.8.3 is approved.
2822012002 | Prairie Island 1 | 04/02/2012 | 05/30/2012 | ML12152A18 | <strong>Unplanned Actuation of 121 Motor Driven Cooling Water Pump</strong><br /><i>Abstract:&nbsp;</i>On April 2, 2012, while Prairie Island Nuclear Generating Plant (PINGP) Unit 1 was operating at 100% power,121 Motor Driven Cooling Water Pump (MDCLP) auto started. The 121 MDCLP auto started while shutting down 22 Diesel Driven Cooling Water Pump (DDCLP). Five cooling water (CL) pumps are connected to a common pump discharge header that directs CL flow into two separate headers. There are three motor driven pumps (121 MDCLP, 11 CLP and 21 CLP) and two diesel driven pumps (12 DDCLP and 22 DDCLP). The Equipment Cause Evaluation (ECE) determined that when only one motor driven pump is supplying both CL headers while removing 12 or 22 DDCLP, the momentary drop in header pressure can auto start 121 MDCLP.
2822012004 | Prairie Island 1 | 06/07/2011 | 09/14/2012 | ML12258A14 | <strong>Unit 1 Emergency Diesel Generators Declared Inoperable due to High Ambient Temperatures</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2011, while Unit 1 was in Mode 3 (Hot Standby), the outside ambient air temperature exceeded the maximum analytical limit of 100.5 degree Fahrenheit and D1 and D2 Emergency Diesel Generators (EDGs) were declared inoperable at 13:49 CDT. This was reported to the NRC via Event Notification (EN) 46934. Based on a July 2011 evaluation, EN 46934 was retracted on July 29, 2011. However, additional analysis completed on April 14, 2012 determined that the calculated heat inputs to the EDG rooms were non-conservative and that EN 46934 should not have been retracted. As originally reported in EN 46934, a Unit 1safety system functional failure did occur. Laboratory component testing for the limiting lube oil pressure switches is ongoing. Depending on the test results a supplement to this LER may be submitted.
2822012005 | Prairie Island 1 | 08/14/2012 | 07/25/2013 | ML13207A09 | <strong>Unit 1 Diesel Generators Inoperable Due To Exhaust Fire</strong><br /><i>Abstract:&nbsp;</i>On August 13, 2012, at 1048 CDT, D1 Diesel Generator (DG) was declared inoperable due to a sustained flame on the control side turbocharger exhaust extension. D2 DG was run on August 14, 2012, to determine if a common cause failure was present. At 0312 CDT on August 14, 2012, D2 was declared inoperable due to an exhaust leak with a visible flame on the control side turbocharger exhaust extension. The flame on D2 DG was detected at the same location as the flame that rendered D1 inoperable. With both DGS inoperable, this required Unit 1 to be placed in Mode 3 (Hot Standby) within 6 hours and Mode 5 (Cold Shutdown) within 36 hours per Technical Specifications (TS) 3.8.1 Condition F. While shutting down the unit, there was an auto actuation of the Auxiliary Feedwater system. <br><br> The direct cause of this event is that inadequate compression and gasket material on the D1 and D2 exhaust extension resulted in excessive oil and hot gas leakage causing fires on D1 and D2 exhaust
2852012001 | Fort Calhoun | 02/10/2012 | 05/17/2013 | ML13137A37 | <strong>Inadequate Flooding Protection Procedure</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2012, during an inspection of flood preparations by the NRC in response to previously identified NRC findings, it was concluded that Abnormal Operating Procedure (AOP) 01 Revision, 28, Acts of Nature, Section I, Flooding, did not adequately protect equipment required to maintain safe shutdown from external flooding to an elevation of 1014 feet Mean Sea Level (MSL). This condition could have prevented the raw water pumps from being available to provide cooling to the component cooling water system. This condition was entered into the station's corrective action program.<br><br> The causal analysis determined that station senior management, at the time the condition was identified, did not effectively lead recovery efforts to address the NRC component design basis inspection (CDBI) and FCS self-identified flooding issues in AOP-01. This resulted in important flooding related corrective actions not being effectively planned, prioritized or resourced to ensure a success path for AOP-01 within the established timeline.
2852012002 | Fort Calhoun | 03/02/2012 | 07/02/2013 | ML13184A27 | <strong>Inadequate Qualifications for Containment Penetrations Renders Containment Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2012, with Fort Calhoun Station (FCS) defueled, Event Notification (EN) 47884 initially reported that during a review of environmental qualification records for containment building electrical penetration feed-through subassemblies, Omaha Public Power District (OPPD) identified six that may not provide an adequate seal during worst-case design-basis accident conditions as required due to failure of the Teflon in the connectors. <br><br> OPPD updated the EN June 26, 2012, to include the inboard and outboard seals of the penetration, which contain Teflon and updated it again July 17, 2012, to include the containment sump outlet valve submarine hull enclosures and the containment personnel airlock. The initial LER submittal, dated May 1, 2012 did not contain this updated information. OPPD performed causal analyses to determine why Teflon was used at Fort Calhoun as a containment integrity seal and insulation on power and control cabling to environmentally qualified components. These analyses determined that a lack of managerial and technical oversight allowed Teflon and Teflon like materials to be used in containment penetration applications. <br><br> The Fundamental Performance Deficiencies are addressing the managerial and technical oversight causes. OPPD is replacing all containment penetrations where Teflon is used as sealant or conductor insulation and is capping unused penetrations prior to core reload.
2852012003 | Fort Calhoun | 03/12/2012 | 11/16/2012 | ML12324A24 | <strong>Non-Conservative Error in Calculation for Alternate Hot Leg Injection Results in Unanalyzed Condition</strong><br /><i>Abstract:&nbsp;</i>A non-conservative error was identified in the input calculation for post-LOCA cooling flow (post-RAS (recirculation actuation signal)). The calculation used an incorrect (non-conservative) input for LPSI pump performance. The associated procedure (EOP/AOP Attachment 11) as written does not provide adequate direction during the Alternate Hot Leg Injection mode of operation. Therefore, the procedural guidance may not ensure the completion of the safety function of providing adequate core cooling during the Alternate Hot Leg Injection mode of operation under a worst case scenario. The apparent cause was identified to be inadequate use of vendor oversight when design information was transmitted to the vendor. The analysis also identified a contributing cause of inadequate review of the calculation provided by the vendor during the owner acceptance process. Procedural requirements to conduct peer reviews prior to transmitting design information to vendors and contractors preparing safety-related calculations have been incorporated into the governing procedures. Additional corrective actions will revise the deficient calculation and procedure.
2852012004 | Fort Calhoun | 03/29/2012 | 10/27/2012 | ML12305A31 | <strong>Inadequate Analysis of Drift Affects Safety Related Equipment</strong><br /><i>Abstract:&nbsp;</i>While investigating industry operating experience, it was determined that Fort Calhoun Station is subject to similar conditions where Static "O" Ring pressure switches with certain housing styles exhibit a setpoint shift when exposed to a change in temperature if the switch body is not vented. Fort Calhoun Station pressure switches that provide signals for high containment pressure to the reactor protection system and engineered safeguards actuation circuitry may have this configuration. The impact of the potential drift was evaluated and it was initially determined that neither reactor protection system nor the engineered safeguard circuitry may actuate at the required containment pressure of 5 psig. A subsequent evaluation of actual data concluded that safety analysis limits were not exceeded. However, two Technical Specification limits were not protected by the calibration procedure nominal trip setpoint when applying the additional uncertainty. The Apparent Cause was determined to be poor vendor documentation which led to Engineering personnel to improperly interpret and apply the information contained in the Static “O” Ring vendor manual. Corrective actions were initiated to remove the vent caps, revise the affected calculations to the temperature correction factor and drift. Additional actions to revise and re-perform surveillance testing were initiated.
2852012005 | Fort Calhoun | 02/21/2012 | 06/01/2012 | ML12157A12 | <strong>Technical Specification Violation due to Inadequate Testing of Emergency Diesel Fuel Pumps</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2012, during a review of Fort Calhoun Station surveillance procedures, it was identified that the Emergency Diesel Generator (EDG) fuel oil transfer pumps have not been tested in accordance with the requirements of Technical Specifications (TSs). The inadequate testing was caused by a procedure change made in 1990 that removed the required monthly test of the automatic low level start feature of the fuel oil transfer pumps. There is reasonable assurance that the EDGs and fuel transfer pumps would function as required as the low level switches are calibrated on a refueling frequency. The apparent cause of this event is a lack of technical rigor in the procedure change process employed in 1990s. Corrective actions have been developed to revise the EDG surveillances to include fuel oil transfer pump surveillance testing.
2852012006 | Fort Calhoun | 04/24/2012 | 06/25/2012 | ML12178A29 | <strong>Operation of Component Cooling Pumps Outside of the Manufacturers Recommendation</strong><br /><i>Abstract:&nbsp;</i>The station identified that the CCW pumps were operating beyond their pump curves with the motor running into the service factor, runout conditions were not observed as there were no fluctuations in pressure, no fluctuations in motor amps, no visible signs of pitting or damage on impeller vain trailing, no damage to internal pump casing surfaces, no abnormal vibration, and no abnormal noise. A review of this condition determined that operation in this condition is a violation of plant technical specification for CCW operation. A cause analysis is in progress. The results of the analysis will be published in a supplement to this LER.
2852012007 | Fort Calhoun | 05/09/2010 | 10/27/2012 | ML12305A53 | <strong>Failure of Pressurizer Heater Sheath</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2010, during power operation, pressurizer heater number 26 failed on ground fault. There was no indication of a reactor coolant system barrier breach at that time. During inspections to determine the physical integrity of a failed pressurizer heater it was determined that the heater sheath (number 26) was cracked. Due to the location of the heater sheath crack, this is considered a degradation of the reactor coolant system boundary. The initial visual inspection of heater 26 in November 2011 did not identify the cracking. During efforts to remove the heater, a crack was observed on May 19, 2012. The crack was above and below the heater support plate. The crack was an axial crack showing some branching. The crack was about an inch above and inch below the heater support plate. These inspections were being performed as a result of operating experience. On May 23, 2012, it was determined that the pressurizer heater sheath was part of the reactor coolant system boundary. The root cause of this failure is fabrication of the heater sheath during the manufacturing process induced high tensile residual stresses on the outer surface of the sheaths. The heater sheath has been removed and replaced. The other heater sheaths have been inspected and none of them had indications of cracking.
2852012008 | Fort Calhoun | 09/28/2011 | 11/29/2012 | ML12335A05 | <strong>Technical Specification Violation for Fuel Movement (VA-66)</strong><br /><i>Abstract:&nbsp;</i>On September 28, 2011, Fort Calhoun Station (FCS) Condition Report 2011-7800 identified the failure of the spent fuel pool area charcoal filter (VA-66) to pass the elemental iodine removal test. During a subsequent review of this CR by the Recovery Engineering group, it was determined that on June 6, 2012, fuel had been moved during a time when VA-66 was required to be OPERABLE. The FCS Technical Specification, 2.8.3(4), requires the Spent Fuel Pool Area ventilation system to be IN OPERATION during REFUELING OPERATIONS. A cause analysis determined that a lack of management oversight and the failure of Engineering to take a proactive approach in the prevention of future test failures led to this event. Completed corrective actions include 1) a revision of the applicable procedure to trend charcoal sample results and predict replacement 2) replacement of the depleted charcoal currently installed, and 3) a change the frequency of the charcoal testing from eighteen months to 1 year.
2852012009 | Fort Calhoun | 12/13/2011 | 10/31/2013 | ML13308C23 | <strong>Inoperable Equipment due to Lack of Environmental Qualifications</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2011, it was identified that the current analysis of record for the Main Steam Line Break (MSLB) inside containment identified a peak temperature of 358.6 degrees Fahrenheit (F) and the Electrical Environmental Equipment Qualification (EEQ) evaluation assumed a maximum temperature of 401 degrees F. It was also identified that the MSLB temperature has a longer exposure time than the EEQ temperature of approximately 160 seconds. However, no evaluation or analysis could be found to address why the original EEQ assumptions remained valid as the longer exposure time of the MSLB analysis could result in an adverse impact on environmentally qualified equipment. This condition was identified when Fort Calhoun Station was shutdown and defueled.<br /><br /> FCS performed a thermal lag analysis to determine the impact of the longer exposure time. The results show that the additional exposure time of the lower MSLB temperature did not adversely affect the EEQ analysis as originally assumed in Event Notification No. 47900 (10 CFR 50.72(b)(3)(ii)(B)). The results of the thermal lag analysis are being documented in the updated program basis documentation. The EEQ Harsh Files for the affected equipment have been revised.<br /><br /> The original condition no longer represents a safety system functional failure and this condition is being submitted as a voluntary report.
2852012010 | Fort Calhoun | 12/06/2011 | 08/03/2012 | ML12219A01 | <strong>Seismic Qualification of Instrument Racks</strong><br /><i>Abstract:&nbsp;</i>While preparing an engineering package to relocate two transmitters, Fort Calhoun Station engineering identified seismic class 1 components in a seismic class 2 instrument rack. This appears to be a legacy issue. The instrument racks in the auxiliary building and containment were assessed with respect to the Updated Safety Analysis Report (USAR) specified class 1 requirements for seismic design. The seismic calculations for two instrument racks were over the analyzed weight for the seismic analysis. The instruments on these racks are used for reactor coolant system (RCS) pressure transmitters. During a seismic event, the excessive weight of these instrument racks could cause the racks to fail, resulting in an unisolable leak from the RCS. A cause analysis is in progress. The results of the analysis will be published in a supplement to this LER.
2852012011 | Fort Calhoun | 04/16/2012 | 08/06/2012 | ML12220A16 | <strong>Emergency Diesel Inoperability due to Bus Loads During a LOOP</strong><br /><i>Abstract:&nbsp;</i>An Engineering review identified that a potential issue existed concerning Emergency Diesel Generators (EDG) capability to power required loads in certain loss of offsite power (LOOP) scenarios, specifically those scenarios during which a Loss of Coolant Accident (LOCA) or Main Steam Line Break (MSLB) does not occur. In a LOOP without a concurrent accident signal, the 480 V load shed that would be initiated as a direct result of the accident signal does not occur. Therefore, the electrical load that the EDGs must pick up when the EDG output breaker automatically closes could be significantly higher than the dead load that exists in an accident scenario. A review of design basis calculations and engineering analyses has identified several evaluations that consider the EDG dead load during accidents. However, no documents evaluating EDG dead loads in non-accident conditions were found. If one EDG were inoperable due to maintenance or other activities and the electrical distribution system loading conditions were such that the other EDG could have reached the output breaker trip settings during a LOOP event, both EDGs would be inoperable and FCS would have to take action per Technical Specification (TS) 2.0.1. It is conservative to assume that such conditions existed for those EDG outages that exceeded six hours. However, actions were not taken for two inoperable EDGs per the requirements of TS 2.0.1, resulting in operation or condition prohibited by TS. A cause analysis is in progress. The results of the analysis will be published in a supplement to this LER.
2852012012 | Fort Calhoun | 03/19/2012 | 12/18/2012 | ML12353A61 | <strong>Multiple Safety Injection Tanks Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>Fort Calhoun Station (FCS) operating procedures allow filling and sluicing multiple safety injection tanks (SITs) while at power, rendering the SITs inoperable during the evolution. The use of this procedure allowed multiple safety injection tanks to be concurrently filled while FCS was at power. FCS Technical Specifications (TS) and accident analysis do not allow more than one SIT to be inoperable. This condition was identified on March 19, 2012, while the unit was in Mode 5, by the NRC during initial license examination preparation. The cause of this condition was the failure to recognize that the passive design of the SITs cannot credit the use of active components for operability. The event was entered into the Corrective Action Program and the following corrective actions were taken. Operating Procedure OI-SI-1, the Technical Specification basis, and the Updated Safety Analysis Report have been revised to clearly state the SITs operability requirements.
2852012013 | Fort Calhoun | 12/07/2011 | 08/17/2012 | ML12233A17 | <strong>Inadequate Calculation of Uncertainty Results a Technical Specification Violation</strong><br /><i>Abstract:&nbsp;</i>Technical Data Book Procedure (TDB)-III.40, “Technical Specification Required SIRWT Levels,” lists the administrative requirements to maintain the Technical Specification (TS) required Safety Injection Refueling Water tank (SIRWT) levels. The required SIRWT level for TS 2.3 accounts for instrument uncertainty, as described in the basis for TS 2.3. However, the required SIRWT levels listed in TDB-III.40 for TS 2.2.7 and 2.2.8 do not account for instrument uncertainty. Therefore, the TS described levels in TS 2.2.7 and 2.2.8 did not adequately account for SIRWT instrument level uncertainty. As a result, using the levels described in TDB-III.40 for compliance with TS 2.2.7 and 2.2.8 was non-conservative. The analysis concluded that there was inadequate/incomplete procedural guidance for developing Administrative Limits used to protect TS Limits. This includes guidance for understanding how to evaluate and apply uncertainties when developing TS Administrative Limits. SIRWT level was increased to a level that accounted for instrument uncertainty. TDB-III.40 has been modified to change the Administrative Limits to account for uncertainty.
2852012014 | Fort Calhoun | 07/11/2012 | 01/18/2013 | ML13022A47 | <strong>Containment Beam 22 Loading Conditions Outside of the Allowable Limits</strong><br /><i>Abstract:&nbsp;</i>On January 24, 2012, during the modification preparation for pipe supports for component cooling water piping in containment, multiple discrepancies were identified between the design calculations and the design drawings for concrete beams in the steam generator bays, 1060 foot platform elevation, and the floor slab at the 1045 foot elevation of containment. On July 11, 2012, while performing the Extent of Condition, it was determined that the loading conditions for Beam B-22, a structural member of the containment internal structure at the 1013 foot elevation, were outside the allowable limits for both Working Stress and No Loss of Function load combinations as noted in the USAR Section 5.11. Additional analysis has been completed which shows that with a live load of 140 psf or less, Beam 22 is able to meet its design function.<br /><br /> The Root Cause Analysis completed December 21, 2012, and determined the condition described in this report was due to inadequate ownership review by Omaha Public Power District of plant construction architect/engineer produced calculations.
2852012015 | Fort Calhoun | 09/16/2011 | 10/02/2013 | ML13274A63 | <strong>Electrical Equipment Impacted by High Energy Line Break Outside of Containment</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2011, while reviewing a draft of the Master List Reconstitution for Electrical Equipment Qualification (EEQ) (EA-FC-08-011), Fort Calhoun Station (FCS) Engineering Department identified that some of the listed components located outside of containment may not be qualified for the environments where they are located. This was discovered during a comprehensive re-evaluation of potential high energy line breaks and radiological impacts outside containment initiated in response to issues identified by the station staff. This condition was identified when Fort Calhoun Station was shutdown and defueled. <br /><br /> The causal analysis identified a number of components located in auxiliary building rooms 4, 13, 21, 22, and 81 that should have been included in the EEQ program. This omission was determined to be the result of insufficient engineering rigor by the preparer and reviewer of the EEQ Program Basis Document. <br /><br /> The identified components are being qualified by additional analysis, replacement with qualified components, providing shielding or electrical isolation capabilities, or moving to the component to a location where EEQ is not required.
2852012016 | Fort Calhoun | 07/17/2012 | 06/25/2013 | ML13176A40 | <strong>Unanalyzed Charging System Socket Welds to the Reactor Coolant System</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2012, Fort Calhoun Station (FCS) identified a deficiency as part of the analyses being performed in support of resolution to the question as to whether some Class I pipe was potentially not qualified as Class 1. Condition Report (CR) 2012-07724 documented that preliminary results from an Thermal Fatigue Analysis on the chemical and volume control system (CVCS) concluded that; 1) The 2 inch socket welded fittings on Reactor Coolant System (RCS) branch line piping cannot be qualified, and 2) The 2 inch charging lines are considered to be in an unanalyzed condition exceeding thermal cycle fatigue and seriously degraded.<br><br> A cause analysis was completed and determined that the CVCS Class 1 piping was constructed using socket welded fittings.<br><br> CVCS was declared inoperable. The normal charging headers to the RCS are classified as inoperable until further evaluations or required repairs are performed. CVCS has been isolated to prevent any further thermal transients to the suspect welds. In addition, the affected waste disposal piping line which was scoped under the extent of condition is being addressed under CR 2012-12184. Contingency actions were taken to secure the letdown line so no thermal stress may be introduced to those socket welds. The affected welds have been replaced and thermal fatigue calculations have been completed.
2852012017 | Fort Calhoun | 07/26/2012 | 12/06/2013 | ML13343A18 | <strong>Containment Valve Actuators Design Temperature Ratings Below Those Required for Design Basis Accidents</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2012, while performing an extent of condition review associated with air operated valves (AOV), it was discovered that several valves had nitrile based elastomers used in the air filter regulator and actuator that may not be acceptable for harsh environment conditions. On September 6, 2012, it was also identified that due to a lack of documentation, the States terminal blocks associated with the AOV's control circuit may not be acceptable for harsh environment conditions. These were entered into the station's corrective action program as Condition Reports 2012-08621 and 2012-12739.<br /><br /> During design basis accidents, the limiting analysis temperature inside Containment is 374.2 degrees Fahrenheit (F). The design service temperature for the nitrile elastomers is 180 degrees F and the testing performed on the States terminal blocks did not bound the required accident conditions. Since these valves have both open and/or close functions, failure of the nitrile based elastomers or the States terminal blocks could prevent the valves from fulfilling their intended safety function.<br /><br /> A causal analysis was conducted and found that the station did not fully implement and or maintain the electrical equipment qualification program. This resulted in a lack of qualification documentation and equipment not qualified for expected design basis accident conditions.
2852012018 | Fort Calhoun | 07/27/2012 | 05/08/2013 | ML13129A25 | <strong>Containment Air Cooling Units Not Properly Tested During Cycle 26</strong><br /><i>Abstract:&nbsp;</i>On July 27, 2012, while performing NRC Inspection Manual Chapter 0350 checklist reviews, the Recovery Engineering Team identified that the containment air cooling and filtering system (CACFS) was not properly tested during cycle 26. It was discovered that surveillance test (ST) IC-ST-VA-0013, as written and performed, did not maintain train separation of the system components during single train surveillance testing as required by Technical Specifications (TS) 2.4.1.a.i, 2.4.1.a.ii, and 3.6(3)g. This resulted in Fort Calhoun Station being in a condition prohibited by TS during operating cycle 26.<br><br> Amendment No. 255 changed how pressure is to be controlled during a loss of coolant accident; from the containment spray system to the CACFS. The revision to the ST, required by this change, failed to incorporate the train separation required by the TS. The ST procedure has been revised and CACFS will be tested prior to being required by TS.
2852012019 | Fort Calhoun | 08/14/2012 | 05/14/2013 | ML13134A39 | <strong>Traveling Screen Sluice Gates Found with Dual Indication</strong><br /><i>Abstract:&nbsp;</i>On August 14, 2012, at approximately 2100 hours Central Daylight Time, Operations was cycling all 6 traveling screen sluice gates when it was identified that traveling screen sluice gate CW-14E motor was stopping on high torque and provided indication that the gate was approximately 8 inches open. Traveling screen sluice gate CW-14C was also stopping on high torque and providing indication the gate was not fully closed. During a flooding event, these sluice gates are credited to fully close allowing control of the intake structure cell level with the raw water pumps. Cell level is maintained below elevation 1007-foot 6-inches. This is the point at which the raw water pump bay could become flooded causing a loss of raw water to the component cooling water heat exchangers. On August 25, 2012, divers removed the sediment and debris from all sluice gate bottoms returning the sluice gates’ capability to be fully closed in the event of a design basis flood. The condition was entered into the station's corrective action program as condition report (CR) 2012-10206.<br><br> The cause of the failure of the sluice gates to fully close was debris under the gates. The Apparent Cause is the process for closing the Sluice gates within OI CW-2 did not adequately account for river debris obstructions.
2852012020 | Fort Calhoun | 12/02/2012 | 01/31/2013 | ML13032A31 | <strong>Raw Water Pump Anchors</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2012, while in Mode 5 (De-fueled), Fort Calhoun Station (FCS) determined that raw water pumps (AC-10A/B/C/D) base plate support anchors were not to be in accordance with design requirements due to of inadequate embedment. This resulted in the inoperability of all four pumps and a violation of Technical Specification requirements during past operating cycles. On January 9, 2013, FCS completed calculation FC08216, Rev 0, Raw Water Pump AC-10A/B/C/D Ultimate Failure. This calculation, without safety/reductions factors, resulted in lower tensile loading requirements during a seismic event and no failure of the anchors. To return the base plate support anchors to design requirements, raw water pumps AC-10A/B/C base plate support anchors have been replaced with maxi bolts. Pump AC-10D repairs are pending. The cause has been determined to be FCS Engineering personnel failing to validate the actual plant configuration and the use of uncorroborated drawing information in completion of design basis calculations.
2852012021 | Fort Calhoun | 01/29/2012 | 02/19/2013 | ML13051A45 | <strong>HCV-2987, HPSI Alternate Header Isolation Valve</strong><br /><i>Abstract:&nbsp;</i>On January 29, 2012, while reviewing design calculations as part of the extent of condition for condition report 2011-9945, it was identified that valve HCV-2987, High Pressure Safety Injection Alternate Header Isolation, would not have been able to fulfill its design safety function found in Updated Safety Analysis Report Table 9.12.1 and Technical Specification 2.3. The last Flow Scan analyses performed in 2008 indicated a higher than acceptable valve packing friction to the point that the valve would not have been able to fulfill its function after the 24 hour mission time with a loss of instrument air. No corrective action was taken after the 2008 FlowScan analyses to fix the condition. At the time of discovery in 2012, Fort Calhoun Station (FCS) was in Mode 5 (refueling). A causal analysis is in progress and the preliminarily root cause identified failure of the station to compare FlowScan data with approved calculations and a lack of corrective actions. Repacking and testing of the valve has been planned. Completion of the AOV Program procedure, currently being developed, will assure that the appropriate test activities are defined and that the results are appropriately addressed.
2862012001 | Indian Point 3 | 02/03/2012 | 04/03/2012 | ML12107A02 | <strong>Common Cause Inoperability of Both Trains of Motor Driven Auxiliary Feedwater (AFW) Pumps due to Inability to Control AFW Regulating Valves after Isolation of Nitrogen Backup</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2011, following completion of a 2 year inspection/overhaul of the Auxiliary Feedwater System (AFWS) nitrogen backup (BU) supply pressure regulator (IA-PCV-1276), the set pressure was increased to the set pressure of relief valve RV-1284 while performing the post maintenance (PM) test (PMT). RV-1284 lifted, chattered and the disc and seat were damaged. When valve PCV-1276 was returned to service, RV-1284 was found to be leaking and the system was isolated which resulted in the unavailability of the AFWS nitrogen BU system. An assessment was conducted on required actions as a result of isolating nitrogen BU. At 18:30 hours, a dedicated operator was stationed in the Auxiliary Boiler Feed Pump building for manual operation of the AFWPs discharge flow control valves (FCV) to mitigate any events that could result in loss of the normal instrument air (IA) supply. Under Design Basis Accident (DBA) events, the IA system (IAS) is not credited as its function to supply AFWS valves is not classified as safety related. Without IA, the BU nitrogen system is relied upon to operate the AFWS including the AFWP FCVs. When the AFWS nitrogen BU is unavailable, a dedicated operator is required to manually operate the AFWPs FCVs. The direct cause of the unavailable nitrogen BU was RV-1284 chattering due to inadequate PMT work order (WO) instructions for control of air regulator set-pressure following overhaul. The apparent cause of operators not recognizing the need to station an operator locally prior to isolating the AFWP nitrogen BU supply was inadequate procedural basis and licensing bases documents (UFSAR, TS Basis, TRM) from a missed opportunity from a previous event. Corrective actions include RV-1284 replacement, revision of model PMT WOs with guidance on regulator set pressures, revision of TS Basis, TRM, UFSAR, DBD, applicable System Descriptions, Operations procedures and lesson plans. The event had no significant effect on public health and safety.
2862012002 | Indian Point 3 | 02/13/2012 | 04/13/2012 | ML12115A05 | <strong>Technical Specification Prohibited Condition due to Exceeding the Allowed Completion Time for an Inoperable Refueling Water Storage Tank During Connection to Purification System</strong><br /><i>Abstract:&nbsp;</i>On February 13, 2012, a review of NRC Information Notice (IN) 2012-01 (Seismic Considerations-Principally Issues Involving Tanks) determined there was a clarification in NRC's position regarding aligning non-seismic piping to the seismically qualified Refueling Water Storage Tank (RWST). The IN identified failures by licensees to recognize that aligning non-seismic piping to the RWST would require Technical Specification (TS) Limiting Condition of Operation (LCO) action statement entry or license amendments. Intentionally aligning the seismically qualified RWST piping to non-seismic Fuel Pool Purification System (FPPS) by opening a boundary valve can cause the RWST to become inoperable. TS LCO 3.0.2 requires that upon discovery of a failure to meet an LCO, the required actions of the associated conditions must be met. TS LCO 3.0.2 does not allow applying compensatory measures such as manual actions in place of a closed boundary valve for periods longer than the TS completion time for restoring the RWST to operable unless the TS expressly permit such operation. Indian Point unit 3 had performed a safety evaluation based on IN 97-78 that allowed operator action. IN 2012-01 clarifies that application of compensatory actions for periods longer than the TS completion time is not allowed. The apparent cause was historical interpretation. Original issue was resolved using the NRC guidance for operator manual actions. Corrective actions will include revision of system operating procedure 3-SOP-SI-003 to prevent aligning the RWST to the FPPS during applicable Modes until the issue is resolved, evaluate the feasibility of a license amendment to allow operator action, assessment of FPPS piping for upgrade to seismic. The event had no effect on public health and safety.
2862012003 | Indian Point 3 | 05/01/2012 | 06/20/2013 | ML13178A22 | <strong>Technical Specification Prohibited Condition due to a Pressurizer Safety Valve Discovered Outside Its As-Found Lift Set Point Test Acceptance Criteria</strong><br /><i>Abstract:&nbsp;</i>On May 1, 2012, Engineering was notified by Wyle Laboratories that one of three Pressurizer Code Safety Valves (RC-PCV-468) (SV) was outside its As-Found lift set point test acceptance criteria (2411 - 2559 psig). The SVs were removed during the last refueling outage (RO) in the spring of 2011 and sent offsite for testing. Testing was performed within one year of removal as required by the Inservice Testing Program. The initial As-Found lift was 5.3% above the 2485 set pressure therefore, the 110% design pressure limitation provided by the ASME code was not exceeded. The remaining two SVs both tested satisfactorily. During the RO all three SVs were removed and replaced with certified pre-tested spare SVs. All three SVs were found with zero seat leakage. The SVs installed during the RO were As-Left tested to 2485 psig +/-1% with zero seat leakage in accordance with surveillance procedure 3-PT-R5A. Technical Specification (TS) 3.4.10 (Pressurizer Safety Valves), requires three pressurizer safety valves to be operable with lift settings set at greater than 2460 psig and less than 2510 psig. TS Surveillance Requirement (SR) 3.4.10.1 requires each PSV to be verified operable in accordance with the Inservice Testing Program. The direct cause of SV RC-PCV-468 lifting greater than 3% of its nominal set point was spring fatigue. The apparent cause was a lack of periodic spring assembly inspection/testing/replacement Preventive Maintenance (PM). Corrective actions include revision to the inspection and repair plan to include SV disassembly and spring assembly inspection, revision of the relief valve component monitoring database to include trending spring-rate results. SV purchase orders will be revised to include spring rate testing and assembly inspection. The event had no effect on public health and safety.
2862012004 | Indian Point 3 | 10/29/2012 | 12/11/2012 | ML13002A01 | <strong>Automatic Reactor Trip as a Result of a Turbine-Generator Trip Due to a Loss of 345kV Feeders W97 and W98 Caused by Storm Damage to Feeder Insulators</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2012, an automatic reactor trip (RT) was initiated as a result of a main turbine-generator trip due to a trip of the Generator Primary and Backup Lockout relay 86P and 86BU on a direct trip from the Buchanan switchyard. The Buchanan switchyard south ring bus was isolated from output feeder W96 as a result of faults on 345 kV feeders W97 and W98 causing the generator output breakers 1 and 3 to open initiating a direct trip signal from Buchanan. All control rods fully inserted and all required safety systems functioned properly. The plant was stabilized in hot standby with decay heat being removed by the main condenser. The Auxiliary Feedwater System automatically started as expected due to SG low level from shrink effect. The Emergency Diesel Generators did not start as offsite power remained available and stable. The cause of the RT was the trip of generator output breakers 1 and 3 due to isolation of the south ring bus from output feeder W96. Generator output breakers 1 and 3 tripped as a result of a fault on feeders W97 and W98 due to Con Edison 345 kV feeder line insulator damage from the effects of superstorm Sandy. Corrective action was taken to repair 345 kV feeders W97 and W98 by Con Edison. The event had no effect on public health and safety.
2872012001 | Oconee 3 | 04/13/2012 | 06/07/2012 | ML12160A34 | <strong>Three Main Steam Relief Valves (MSRV) Lift Pressure Exceeds +1% Tolerance</strong><br /><i>Abstract:&nbsp;</i>On 4/13/2012, prior to shutdown of Unit 3 for refueling, all 16 of the Unit 3 Main Steam Safety Valves, referred to as Main Steam Relief Valves (MSRV) at Oconee, were tested to satisfy Technical Specification (TS) Surveillance Requirement (SR) 3.7.1.1. The testing found that the as-found lift pressure for 3 valves was higher than allowed by SR 3.7.1.1; the remaining 13 MSRVs all met the SR. Guidance from NUREG 1022 characterizes the test failure of multiple MSRVs as an indicator that the valves likely exceeded their acceptance criteria during Unit 3 operation, and thus is considered an operation in a condition prohibited by TS and reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The cause of the MSRV test failures was determined to be setpoint drift, in parallel with current plant design restrictions which limits the upper setpoint tolerance to a maximum of +1% of nameplate set pressure. Although the lift pressures were above the acceptance criteria of +1%, [3MS-1 (1.6%), 3MS-3 (1.1%) and 3MS-4 (2.2%)], this condition is bounded by safety analysis limits and assumptions. Plant modifications will be made to increase plant/design margins such that setpoint drift can be accommodated and procedure revisions will enhance MSRV maintenance. Four previous similar occurrences at Oconee were reported by LER 270/2008-02-01.
2892012001 | Three Mile Island 1 | 05/09/2012 | 07/06/2012 | ML12191032 | <strong>Single Condition Making Independent Trains Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 05/09/12 a TMI-1 station review of Operating Experience (OE) event # OE30225 was provided to the NRC. The station recognized at that time that this response would need to be revised and entered an issue report (IR# 1364596) into the corrective action database. Subsequent review determined that in a condition in which one main feedwater pump had been reset but was not aligned and providing main feedwater flow to the steam generators, a trip of the other main feedwater pump while providing main feedwater flow to the steam generators, would not have resulted in an actuation to start the emergency feedwater system. It was concluded that the described condition occurred on six different occasions at TMI-1 in the past three years. This condition was not recognized as an entry condition into the TMI-1 Technical Specifications. Corrective actions include revising the OE30225 response, revising applicable procedures, evaluating modifications, operator/technical training and improvements to the Technical Specifications. This event is considered to have no significance with respect to the health and safety of the public. The submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73(a)(2)(vii)(A) and 10 CFR 50.73 (a)(2)(vii)(B).
2892012002 | Three Mile Island 1 | 08/10/2012 | 02/22/2013 | ML13057A10 | <strong>Missing Seals in Air Intake Tunnel Conduits</strong><br /><i>Abstract:&nbsp;</i>On 08/10/12 a TMI-1 flood inspection walkdown discovered that conduits carrying cabling from yard electrical vaults through the Air Intake Tunnel (AIT) to the Auxiliary Building (AB) did not contain internal seals for flood protection. When the plant was constructed in the early 1970's the conduit seals were never installed. The conduit seals are internal to the conduit fittings and not visible externally. The cause has been attributed to inadequate configuration management during original construction. The corrective action to modify the design to provide the required flood protection for AIT conduits was completed in October 2012. The safety significance of the past condition was evaluated. Had a probable maximum flood (PMF) event occurred at TMI-1, after a greater flood hazard was recognized in September 2011 and before the AIT conduit deficiency was identified and temporarily mitigated in August 2012, it is likely that some safe shutdown equipment would have been adversely affected but safe shutdown conditions would have been maintained and there would not have been any adverse impact on public health and safety. The submittal of this LER constitutes reporting to the NRC in accordance with 10 CFR 50.73(a)(2)(v)(B).
2892012003 | Three Mile Island 1 | 08/22/2012 | 10/22/2012 | ML12298A03 | <strong>Pressurizer Heater Bundle Leak</strong><br /><i>Abstract:&nbsp;</i>On August 22, 2012 Three Mile Island (TMI) Unit 1 discovered an unisolable leak in the upper pressurizer heater bundle diaphragm plate and shut down the reactor. The cause of the leak was Primary Water Stress Corrosion Cracking (PWSCC). The root cause was determined to be "The use of Alloy 600 materials in high temperature locations was a design weakness in the construction of the TMI station." The corrective actions include replacement of the upper pressurizer heater bundle (completed September 2012) and planned replacement of the remaining Alloy 600 susceptible pressurizer heater bundle. The leak was not a threat to the safety of the reactor and did not represent a reduction in the public health and safety. A previous PWSCC condition was reported in LER 50-289/2003-003-00. This LER is being submitted pursuant to 10 CFR 50.73(a)(2)(i)(A).
2892012004 | Three Mile Island 1 | 08/22/2012 | 10/22/2012 | ML12298A03 | <strong>Reactor Trip During Downpower Due to Condensate Booster Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, August 22, 2012, Three Mile Island, Unit 1, was conducting a Technical Specification required (T.S. 3.1.6.6) plant shutdown to repair a leak on a pressurizer heater bundle. At 8:01:26 AM with the plant at 30% power, the reactor tripped by Reactor Protection System (RPS) actuation on high reactor coolant system (RCS) pressure. The high RCS pressure setpoint was reached due to a loss of suction to the main feedwater pumps when the only operating condensate booster pump tripped. A "counting circuit" relay stuck in the energized position when the number of operating condensate booster pumps was reduced to one, CO-P-2C. The remaining condensate booster pump tripped when one of the two operating condensate pumps was secured. Suction to the main feedwater pumps was severely reduced and produced a loss of feedwater (LOFW) event and caused RCS pressure to rise and RPS to actuate on high pressure. Emergency feedwater (EFW) automatically actuated on low steam generator level (<10"). This LER is being submitted pursuant to the requirements of 10 CFR 50.73(a)(2)(iv)(A) and 10 CFR 50.73(a)(2)(iv)(B).
2892012005 | Three Mile Island 1 | 09/20/2012 | 11/19/2012 | ML12325A94 | <strong>Reactor Trip Due to RC-P-1C</strong><br /><i>Abstract:&nbsp;</i>On September 20, 2012, Reactor Coolant Pump RC-P-1C at Three Mile Island (TMI) Unit 1 tripped on an apparent differential overcurrent condition 55 seconds after Vital Bus C was secured in support of inverter maintenance. An automatic runback was initiated, but the Reactor Protection System (RPS) actuated on flux to flow imbalance and the reactor tripped at 14:17:34. The RC-P-1C trip was attributed to the differential overcurrent condition due to a differential overcurrent relay (ITH 87 relay) for the RC-P-1C, "C" phase operational indicator being flagged. Complex troubleshooting was performed with an emphasis on an RC-P-1C Motor or RC-P-1C\87 Differential Relay failure as the probable cause; however, the troubleshooting did not reveal a definitive cause of the initiating RC-P-1C trip. An operational decision evaluation was performed to assess plant restart without identifying the cause of the RC-P-1C trip during the complex troubleshooting. A subsequent investigation was performed to determine why RC-P-1C tripped but could not determine a definitive root cause. The most likely causes were addressed by the replacement of the relay, adjusting the trip setpoint, and eliminating this type of vital bus outage at power. This LER is being submitted pursuant to the requirements of 10 CFR 50.73 (a)(2)(iv)(A).
2932012001 | Pilgrim | 03/28/2012 | 05/29/2012 | ML12151A28 | <strong>Safety Relief Valves' Test Pressure Exceeded Setpoint Limits</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2012, Pilgrim Nuclear Power Station (PNPS) was notified that three of four, two-stage Target Rock Safety Relief Valve (SRV) pilot assemblies exceeded the Technical Specification (TS) tolerance limit for routine set point pressure testing performed at the Wyle Laboratories test facility. Certified replacement three-stage SRVs were installed in the plant at the time Pilgrim was notified. The cause of the as-found initial popping pressures exceeding the TS tolerance limit for the pilot valves was "setpoint variance" and "corrosion bonding." Corrective action was taken to replace the two-stage Target Rock SRVs with certified tested replacement three-stage Target Rock SRVs during Refueling Outage 18. The corrective action also included revising the PNPS Safety Analysis and Technical Specifications (TS) to reflect a 3% tolerance on set pressure for the new SRVs. The safety significance of the event was negligible and the condition posed no threat to public health and safety. An evaluation of the as-found set pressures and the potential increase in peak reactor pressure indicates that the increase would have been negligible and reactor vessel system integrity would not have been impaired.
2932012002 | Pilgrim | 05/22/2012 | 07/20/2012 | ML12214A40 | <strong>Manual Reactor Scram due to Degraded Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On Tuesday, May 22, 2012 at 1311 hours, with the reactor at approximately 35% core thermal power, during a planned power reduction to support thermal backwash of the main condenser, a manual reactor scram was inserted due to degrading main condenser vacuum. The direct cause of the degraded vacuum is attributed to loss of the Steam Jet Air Ejector (SJAE) inter-condenser loop seal due to a partially open SJAE steam supply valve (1-HO-163). The root cause of the 1-HO-163 valve being partially open was due to inadequate processing of an emergent work order related to the reach rod position indication versus the actual valve position. Following the reactor scram, all rods were verified to be fully inserted and the Primary Containment Isolation System Group II (Reactor Building) and Group VI (Reactor Water Cleanup System) actuations occurred as designed due to the expected reactor water level shrink associated with the scram signal. Standby Gas Treatment System Train 'B,' which is designed to shutdown 65 seconds after the Group II signal is received if the Standby Gas Treatment Train 'A' is inservice, continued to operate until manually secured. With this exception all other plant systems responded as designed. This event had no impact on the health and/or safety of the public because emergency core cooling systems were operable and available to perform their required safety functions.
2932012003 | Pilgrim | 10/31/2012 | 12/31/2012 | ML13002A39 | <strong>Both Trains of Standby Gas Treatment System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On Wednesday, October 31, 2012 at 1200 hours, with the reactor mode switch in RUN at approximately 100 percent core thermal power and steady state conditions, Standby Gas Treatment (SBGT) System Train "B" was removed from service (made inoperable) for surveillance testing. At 1441 hours, the control room staff declared the SBGT System Train "A" inoperable as a result of an engineering analysis that determined that 480 VAC feeder breaker to Motor Control Center (MCC) B15 had the potential to exceed its trip set point under the worst case bus loading. The inoperability of both SBGT System Trains "A" and "B" could have prevented the fulfillment of the safety functions to "control the release of radioactive material" and "mitigate the consequences of an accident". At 1510 hours, a compensatory measure was taken to preclude the potential overload condition on MCC B15 and the SBGT System Train "A" was restored to operable status to fulfill the safety functions to "control the release of radioactive material" and "mitigate the consequences of an accident". This event had no impact on the health and/or safety of the public.
2962012001 | Browns Ferry 3 | 01/26/2012 | 03/26/2012 | ML12087A30 | <strong>Annunciator Panel Power Supply Fire in Unit 3 Control Room</strong><br /><i>Abstract:&nbsp;</i>On January 26, 2012, at 1908 hours Central Standard Time (CST) Browns Ferry Nuclear Plant (BFN), Unit 3, was in Mode 1 at 100 percent power. Operations personnel in the BFN, Unit 3, Control Room, smelled smoke and observed a flame coming from the bottom of a power supply located in an annunciator panel. Operations personnel opened a breaker, which resulted in the fire being extinguished at 1918 CST. The loss of some annunciator alarms and indications resulted when the breaker was opened. Operations personnel were able to monitor compensatory indications. There was no loss of assessment capability. The event did not result in any entry to a required emergency action level, such as declaring a Notification of Unusual Event (NOUE). The cause of the event was a failed power supply. An overcurrent was caused by an aged capacitor that had not received preventative maintenance to address its service life. A corrective action was initiated to replace the affected power supplies. Previous similar events addressed the failure of an annunciator module in March, 2008; the failure of a power supply in May 2008; and a failed power supply in an annunciator panel in July 2009.
2962012002 | Browns Ferry 3 | 04/07/2012 | 06/06/2012 | ML12160A34 | <strong>Main Steam Isolation Valve Leakage in Excess of Technical Specification Requirements</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2012, at approximately 1415 hours Central Daylight Time (CDT), during the performance of surveillance procedure 3-SR-3.6.1.3.10 (B-OUTBD), Primary Containment Local Leak Rate Test Main Steam Line B Outboard: Penetration X-7B, the 3B Outboard Main Steam Isolation Valve (MSIV) (3-FCV-001-0027) failed to meet the Technical Specification (TS) leak rate limit of 100 standard cubic feet per hour (scfh). On April 7, 2012, at approximately 0233 hours CDT, during an inspection walkdown, steam was found blowing from MSIV 3-FCV-001-0027; therefore, April 7, 2012, is considered the event date for this LER. MSIV 3-FCV-001-0027 was considered to be inoperable for an indeterminate period of time. Since MSIV 3-FCV-001-0027 failed to meet the leak rate limit, it is probable that Browns Ferry Nuclear Plant, Unit 3, operated longer than allowed by the TS. In addition, due to MSIV 3-FCV-001-0027 failing to meet the leak rate limit, it is probable TS Limiting Condition for Operation 3.0.4 was not met for each applicable Mode change since the last recorded as-found MSIV leak rate test on March 28, 2010, when the leak rate was below 100 scfh. The cause of the event was an inadequate packing program. The corrective action for this cause is to implement a new valve packing program.
2962012003 | Browns Ferry 3 | 05/22/2012 | 11/26/2012 | ML12333A00 | <strong>Browns Ferry Nuclear Plant, Units 3, Automatic Reactor Scram due to De-Energization of Reactor Protection System from Actuation of 3A Unit Station Service Transformer Differential Relay</strong><br /><i>Abstract:&nbsp;</i>On May 22, 2012, at 0249 Central Daylight Time, the BFN, Unit 3, reactor was automatically scrammed due to de-energization of the Reactor Protection System from actuation of the 3A Unit Station Service Transformer (USST) differential relay 387SA, which resulted in a loss of 500 kilovolt (kV) power to BFN, Unit 3. All safety systems responded as expected to the loss of 500kV power. No Emergency Core Cooling System or Reactor Core Isolation Cooling (RCIC) System reactor water level initiation set points were reached. The RCIC System was manually started to control reactor water level. Primary Containment Isolation System initiation signals for groups 1, 2, 3, 6 and 8 were received as expected due to loss of power. The immediate cause of this event was the 3A USST differential relay was installed with incorrect design calculation settings which resulted in the BFN, Unit 3, scram. The root cause of this condition was inadequate procedural guidance within NEDP-5, Design Document Reviews, for the types of review required by engineering. The corrective action to prevent recurrence is to revise NEDP-5, Design Document Reviews, to establish the definition and requirements for each type of review.
2962012004 | Browns Ferry 3 | 05/24/2012 | 11/26/2012 | ML12333A00 | <strong>Manual Reactor Scram During Startup due to Multiple Control Rod Insertion</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2012, at approximately 0638 Central Daylight Time, Operations personnel inadvertently ranged 3H intermediate range monitor (IRM) down instead of up resulting in a half scram from the 3B reactor protection system (RPS) trip channel. Subsequently, the IRM was properly ranged and Operations personnel responded in accordance with procedures to reset the half scram. Coincident with Operations personnel placing the scram reset switch in the Group 2/3 position, an electrical spike was received on 3A IRM of the 3A RPS trip channel resulting in control rod insertion for the Groups 1 and 4 control rods. Operations personnel identified the unexpected control rod motion and initiated a manual reactor scram in accordance with Browns Ferry Nuclear Plant (BFN) Abnormal Operating Instructions. The root cause was determined to be high impedance of the BFN, Unit 3, Main Control Room (MCR) common ground to station ground that exposed the 3A IRM to noise feedback. The corrective action to prevent recurrence is to verify that BFN, Unit 3, MCR common ground connections to station ground are as shown in the applicable system drawings. If any ground connections are identified that require repair, work orders will be initiated and repairs performed. Following repairs, the high impedance connection of BFN, Unit 3, MCR common ground to station ground will be confirmed to have been resolved by documenting the results of validation testing.
2962012005 | Browns Ferry 3 | 05/29/2012 | 11/29/2012 | ML12338042 | <strong>Automatic Reactor Scram Due to an Actuation of a Main Transformer Differential Relay</strong><br /><i>Abstract:&nbsp;</i>On May 29, 2012, at 0331 Central Daylight Time, the Browns Ferry Nuclear Plant (BFN), Unit 3, reactor automatically scrammed due to fast closure of turbine control valves, initiated by a load reject signal on the Main Generator. The cause of the load reject signal was actuation of newly installed main transformer differential relay 387T, which caused the scram. All systems responded as expected to the load reject signal. Main steam isolation valves remained open and reactor pressure was controlled by the main turbine bypass valves. No Emergency Core Cooling System or Reactor Core Isolation Cooling System reactor water level initiation set points were reached. Primary Containment Isolation System isolations from Groups 2, 3, 6, and 8 were received, and reactor water level was controlled by the Feedwater System. Three root causes were identified: 1) inadequate procedure, instructions, and testing methodology/equipment used for current transformer (CT) bench testing; 2) inadequate acceptance review by Tennessee Valley Authority (TVA) Engineering of a vendor prepared design change; and 3) inadequate management, oversight, and accountability by the BFN Maintenance organization for work performed by the Protective Relay Group. The corrective actions to prevent recurrence include: 1) revise the CT bench test procedure; 2) revise the human performance procedure to incorporate technical conscience principles, focus technical task risk factors, mitigating strategies, and decision making; and 3) using the Nuclear Operating Model, utilize the TVA's strategic performance management process to ensure management alignment in the ownership and accountability for leadership expectations at BFN.
2962012006 | Browns Ferry 3 | 05/25/2012 | 08/31/2012 | ML12249A19 | <strong>Browns Ferry Nuclear Plant, Unit 3, Main Steam Relief Valves' Lift Settings Outside Technical Specifications Required Setpoint</strong><br /><i>Abstract:&nbsp;</i>On May 25, 2012, the Tennessee Valley Authority determined, 2 of 13 Browns Ferry Nuclear Plant (BFN), Unit 3, Main Steam Relief Valves (MSRVs) mechanically actuated at pressures outside the allowed +/- 3 percent tolerance of their Technical Specification (TS) setpoint. The BFN, Unit 3, TS Limiting Condition for Operation 3.4.3 requires the safety function of twelve (12) MSRVs to be operable in reactor Modes 1, 2, and 3. Since 2 of 13 MSRVs actuated outside their TS setpoint allowance by greater than +/- 3 percent, it is probable that BFN, Unit 3, operated with only 11 operable MSRVs for longer than allowed by the TS. The root cause of this condition was the valve design does not make allowance for corrosion bonding. Corrective actions to prevent recurrence of this condition are to revise Mechanical Corrective Instruction MCI-0-001-VLV002, Main Steam Relief Valves Target Rock Model 7567 Disassembly, Inspection, Rework and Reassembly, to add steps to verify platinum coating on each pilot valve disc during the refurbishment process and to incorporate criteria for replacing pilot valve springs.
2982012001 | Cooper Station | 03/07/2012 | 05/07/2012 | ML12131A43 | <strong>Prohibited Condition due to Fuse Size of Battery Charger</strong><br /><i>Abstract:&nbsp;</i>On March 7, 2012, Cooper Nuclear Station discovered that the fuse ratings associated with the "C" battery charger disconnect switches may prevent the "C" battery chargers from fulfilling an Updated Safety Analysis Report and Technical Specification Bases function. The 125 volt direct current (VDC) and 250 VDC "C" battery chargers can be used as a spare to either "A" battery charger or "B" battery charger. The "A" and "B" battery charger fuses and fuse disconnects are sized at 300 amperes, while the "C" battery charger fuses and fuse disconnects are sized at 200 amperes. Operations declared the "C" battery chargers inoperable. The root cause was determined to be the design preparation, review, and approval process when the original design documents were prepared for installation of "C" battery chargers was not sufficiently rigorous to detect the fuse sizing error. To prevent recurrence, design evaluations and any necessary design changes to the size of the fuses in the "C" battery chargers will be implemented.
2982012002 | Cooper Station | 04/11/2012 | 06/07/2012 | ML12164A40 | <strong>Improper Rotor Installation Causes Failure of Diesel Generator to Start</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2012, Diesel Generator (DG) 1 and DG1 Starting Air were declared inoperable for online maintenance activities. On April 11, 2012, DG1 failed to start. After the first failure to start, the fuel oil line was vented due to suspected air, and DG1 subsequently started successfully. On April 12, 2012, DG1 failed to start. Further troubleshooting identified the rotor in the left bank starting air distributor had been installed 180 degrees out of alignment during on-line maintenance in October 2011. This resulted in DG1 being inoperable from the last successful surveillance on March 6, 2012, until April 15, 2012, when DG1 was declared operable. On March 12, 2012, DG2 was declared inoperable and remained inoperable until March 18, 2012, thus a loss of safety function for both DGs occurred during that time. The root cause of this event was procedural guidance was inadequate to ensure the rotor was properly reinstalled in the DG1 left bank starting air distributor after work scope changed in October 2011. To prevent recurrence of this condition, the procedure will be revised and guidance will also be developed that ensures vendor recommendations and cautions are included. The procedure for diesel maintenance runs will be revised to ensure detection of air distributor malfunctions.
2982012003 | Cooper Station | 09/10/2012 | 11/01/2012 | ML12312A06 | <strong>Reactor Building Doors Opened Simultaneously Causes Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On September 10, 2012, both airlock doors to the Reactor Building were inadvertently opened simultaneously, breaching the secondary containment boundary. Personnel were attempting to exit the Reactor Building through the inner personnel airlock while personnel were also entering the Reactor Building through the outer personnel airlock. This condition resulted in the two airlock doors being open simultaneously for approximately two minutes. As a result, an indication was received in the Control Room and Limiting Condition for Operation (LCO) 3.6.4.1, Condition A, was entered to restore secondary containment. An operator was dispatched to the airlock, reset the door interlocks; the doors were declared operable and LCO 3.6.4.1, Condition A, was exited. Cooper Nuclear Station (CNS) determined the root cause to be previous reportability practices minimized the significance of having both airlock doors open which caused CNS to defer installing equipment that would have precluded this event. Interim corrective actions include establishing persons to serve as door monitors until an automated warning device or system is installed. To prevent recurrence of this event, a change in the reportability guidance has been adopted and new doors with a different interlock will be installed in Refueling Outage 28.
2982012004 | Cooper Station | 10/14/2012 | 12/06/2012 | ML12348A03 | <strong>Isolation of Shutdown Cooling Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On October 14, 2012, Cooper Nuclear Station operations personnel were flushing the B loop of Residual Heat Removal (RHR) in accordance with the station procedure in preparation for the start of the shutdown cooling mode of operation. The radwaste discharge valve was slowly throttled open per station procedure. Due to existing reactor temperature and pressure, and the position of the radwaste discharge valve, flashing of the hot reactor coolant to steam occurred. The pressure perturbation isolated the RHR shutdown cooling loop. The RHR system was subsequently vented and the flush was re-performed successfully. The root cause was the station procedure provides insufficient guidance to avoid automatic closure of the isolation valves during shutdown cooling heatup and flush when the reactor temperature is higher than 212 degrees Fahrenheit. To prevent recurrence of this event, the station procedure will be revised so that the isolation of RHR is an expected effect that will occur during shutdown cooling heatup and flush, and provide more specific instructions concerning throttling time versus reactor vessel conditions.
2982012005 | Cooper Station | 10/17/2012 | 12/12/2012 | ML12354A05 | <strong>Prohibited Condition for Service Water Booster Pump Leak</strong><br /><i>Abstract:&nbsp;</i>On October 17, 2012, Cooper Nuclear Station personnel discovered that a Service Water Booster Pump (SWBP) was leaking. The pump was secured and the leak stopped. Investigation revealed that the flushing port of the pump was only partially filled with plug material. The root cause was corrective actions put in place to preclude the purchase of SWBPs with high pressure volute area flushing ports were not effectively implemented. To prevent recurrence of this event, the SWBP Vendor Manual will be revised to include references to correspondence regarding providing SWBPs without high pressure flushing holes; and the purchase order and SWBP drawing will be revised to include the following statement: Pump shall not have side flushing holes in the high pressure volute area of the pump case. The only hole in the high pressure volute area of the pump case should be the top vent hole located at the top of the pump case. In addition, a Change Evaluation Document will be developed to change the design of the SWBPs to remove the high pressure volute area flushing water ports and accept as permanent.
2982012006 | Cooper Station | 11/07/2012 | 01/04/2013 | ML13008A18 | <strong>Missing Vent Plug Results in Technical Specifications Prohibited Condition</strong><br /><i>Abstract:&nbsp;</i>On November 7, 2012, Cooper Nuclear Station (CNS) personnel discovered that a plug was missing from the top of the Z sump vent connection. The control room and maintenance personnel were notified and the plug was re-installed. Investigation revealed that the plug was removed to obtain an air sample. The work orders and procedure directing work did not state how to obtain the air sample. There was no written documentation indicating that the plug had been removed. At the end of the work activity, the hose was pulled out of an opening in the Foreign Material Exclusion boundary tent, the pipe that the hose was placed in was not visible, and the plug did not get re-installed. The root cause was written instructions requiring the vent cap be replaced to ensure secondary containment integrity when the air sampling was complete and the Z sump was returned to service, did not exist. To prevent recurrence of this event, CNS will modify the procedure and preventive maintenance work items associated with the Z sump so that both note that if the pipe plug is removed for sampling air quality in the Z sump or for some other activity, that the plug must be securely replaced each time the task is complete to preserve secondary containment integrity.
3012012001 | Point Beach 2 | 06/27/2012 | 08/26/2012 | ML12236A32 | <strong>Unit 2 Manual Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2012 at 2046, a Point Beach Nuclear Plant (PBNP) Unit 2 manual reactor trip was actuated due to indications of a loss of load to the main turbine. At approximately 2045 alarms were received in the control room indicating reduced PBNP Unit 2 turbine first stage pressure and generator megawatts, indicative of a significant reduction in turbine load. Control rods were responding as designed by inserting into the reactor to reduce reactor power. Operations noted that the turbine speed indication on the EH control panel was reading high with the generator output breaker closed, indicating a control system failure. Based on these indications, the Shift Manager directed that the reactor be shutdown by manually actuating the reactor protection system. No automatic reactor protection setpoints were exceeded and an automatic shutdown was not actuated or required. Based on troubleshooting, NextEra determined that the loss of turbine load was due to a failure of the speed channel card in the EH system. The speed channel card was replaced. Pursuant to 10 CFR 50.73 (a)(2)(iv)(A), the event is reportable as an event or condition that resulted in manual actuation of the reactor protection system.
3052012001 | Kewaunee | 02/22/2012 | 04/19/2012 | ML12125A04 | <strong>Pressurizer PORV and Reactor Coolant System Vent Valves Appendix R Spurious Operation Concerns</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2012, while developing Design Change KW-12-01049 to address inadequate Appendix R reactor coolant system high/low interface valve cable separation issues for pressurizer power operated relief valves (PORVs) PR-2A and PR-2B, additional concerns were raised regarding the condition originally identified in Condition Report CR109107 and discussed in LER 2008-001-00. Subsequently, on February 28, 2012, additional Appendix R fire spurious operation concerns (related to a postulated fire in the relay room or 480 volt Bus 51/52 area) were identified for the pressurizer and reactor head vent valves PR-33A, RC-45A, and RC-46 than as originally identified in Condition Report CR114409 and discussed in LER 2008-001-00. An evaluation of these concerns determined that the control cables for the valves in question were not adequately protected from potential fire damage in the alternate and dedicated safe shutdown areas and spurious opening of these high/low interface valves could be postulated in the event of a fire. This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B) for any event that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety.
3052012002 | Kewaunee | 02/29/2012 | 04/29/2012 | ML12132A15 | <strong>Safety Injection Inoperable for Longer Period Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On February 29, 2012, during the start of safety injection pump B for surveillance testing, the 4160 volt breaker functioned correctly to start the pump but the breaker charging spring motor did not stop after charging the breaker springs. This condition potentially impacted safety injection pump operability. If the safety injection pump were stopped with the breaker charging motor continuing to run and the breaker was subsequently called upon to close, it potentially would not cycle due to the breaker's closing circuit design. The safety injection pump B breaker was previously cycled successfully on December 7, 2011. Between the period of December 7 through February 29, 2012, safety injection pump A was inoperable on January 6, 2012 and February 7, 2012, thus rendering both trains inoperable simultaneously. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition which was prohibited by the plant's Technical Specifications; and 50.73(a)(2)(v), for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition; (B) Remove residual heat; or (D) Mitigate the consequences of an accident.
3052012003 | Kewaunee | 04/15/2012 | 06/13/2012 | ML12172A40 | <strong>Nuclear Instruments Inoperable for Longer Period Than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2012, with the reactor defueled, "as found" pressure testing of the nuclear source and intermediate range detector cable for channels N31 and N35 identified a leak in the cable wall near a cable penetration connector. Leakage had previously been identified in this cable in April 2008; however, the source of the leakage was considered to have been from the connector interface (based on past experience). Therefore, the cable was determined to have been functional and the leakage was considered acceptable for continued operation. The April 15, 2012 test indicated that the 2008 leak had been incorrectly characterized. During subsequent activities to repair the leak, a second leak was identified in this cable. Since the leakage was through the cable wall itself and not from the connector interface, the ability of the cable to function for an extended period in a post-accident environment could no longer be assured. Since there was no longer a reasonable basis for functionality, the cable was considered to have been nonfunctional since initial discovery of the leak in 2008. With the cable nonfunctional, the supported source and intermediate range neutron detectors were inoperable for a longer period than allowed by Technical Specifications. Thus, this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition prohibited by the plant's Technical Specifications.
3052012004 | Kewaunee | 04/27/2012 | 06/21/2012 | ML12181A20 | <strong>Pressure Boundary Leakage from Socket Weld on 3/4-Inch Pipe to Sample Valve RHR-600</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2012, during follow up inspection of a previously identified inactive boric acid leak, active leakage was identified in the upstream piping between containment isolation valve RHR-600 and the A train 10-inch residual decay heat removal piping. This leakage was determined to be pressure boundary leakage. In the residual heat removal system cooldown lineup, this A train piping is the common flow path for both A and B train residual heat removal loops that maintain flow to the reactor coolant system cold leg and provide core cooling. Although the residual heat removal system remained in service providing decay heat removal, both trains were declared inoperable due to operational leakage from an ASME Code Class 2 component. This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(A), for the plant, including its principal safety barriers, being seriously degraded; 10 CFR 50.73(a)(2)(v), for any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to: (A) Shut down the reactor and maintain it in a safe shutdown condition and (B) Remove residual heat; and 10 CFR 50.73(a)(2)(vii), a single cause where two independent trains became inoperable in a single system designed to: (A) Shut down the reactor and maintain it in a safe shutdown condition and (B) Remove residual heat.
3052012005 | Kewaunee | 06/27/2012 | 08/23/2012 | ML12250A62 | <strong>Both Safety Injection Trains Inoperable due to Venting</strong><br /><i>Abstract:&nbsp;</i>On June 27, 2012, with the Kewaunee Power Station (KPS) operating at 100% power, Safety Injection (SI) Train A and SI Train B were declared inoperable due to venting of the common pump suction line and of the bypass line to remove a void discovered the same day. Within 14 minutes the common SI Train A and SI Train B suction line and bypass line were vented, the void size was reduced to within acceptable limits, and the trains were returned to an Operable status. The effects of an open vent line on this piping are not analyzed, potentially rendering both trains of SI inoperable; placing KPS in an unanalyzed condition. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B), as any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety, 10 CFR 50.73(a)(2)(v), as any condition or event that could have prevented fulfillment of a safety function, and 10 CFR 50.73(a)(2)(vii), as any event or condition where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system.
3052012006 | Kewaunee | 07/18/2012 | 09/14/2012 | ML12300A43 | <strong>Train A Special Ventilation Inoperable for Longer Period than Allowed due to Charcoal Filter Efficiency</strong><br /><i>Abstract:&nbsp;</i>At 1555 CDT on July 18, 2012, while in Mode 1, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.12, Auxiliary Building Special Ventilation (ASV) System, was discovered not met for Train A. This was due to the ASV Train A charcoal sample failing its efficiency test. The test sample was less than the minimum efficiency of 97.5% required by the criteria in TS 5.5.9; Ventilation Filter Testing Program (tested efficiency was 97.13%). With the Train A charcoal filter media efficiency below the test criteria, the associated train of ASV did not meet its TS Surveillance Requirement (SR). Per SR 3.0.1, failure to meet a Surveillance shall be failure to meet the TS Limiting Condition for Operation (LCO). Therefore, LCO 3.7.12, ASV System, was not met for Train A. The SR was considered to have not been met from the time that the charcoal sample was removed for testing (July 11, 2012) until the charcoal filter was replaced (July 21, 2012). With the charcoal filter not meeting its SR for this period, LCO 3.7.12 was also not met for ASV Train A for a longer period than allowed by Technical Specifications. Thus, this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition prohibited by the plant's Technical Specifications. Earlier on July 18, 2012, ASV Train B had been removed from service for routine maintenance and was inoperable for about six hours.
3052012007 | Kewaunee | 08/20/2012 | 10/19/2012 | ML12300A39 | <strong>Minor Thru-Wall Leak at Weld in Safety Injection Suction Piping</strong><br /><i>Abstract:&nbsp;</i>On August 20, 2012, with the Kewaunee Power Station (KPS) operating at 100% power, plant staff discovered a thru-wall leak on the common suction line for the Safety Injection (SI) pumps. The thru-wall leak was located at the weld between the SI-3 valve body and the piping upstream of SI-3. Both trains of SI were declared inoperable until SI-3 was closed, and the trains were returned to an Operable status. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(B), as any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety, 10 CFR 50.73(a)(2)(v)(B) and (D), as any condition or event that could have prevented fulfillment of a safety function, and 10 CFR 50.73(a)(2)(vii), as any event or condition where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system.
3052012008 | Kewaunee | 09/13/2012 | 11/08/2012 | ML12333A23 | <strong>Residual Heat Removal System Interlock Surveillance Not Met due to Improper Setpoint</strong><br /><i>Abstract:&nbsp;</i>On September 13, 2012, while in Mode 1, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.4.14, RCS Pressure Isolation Valve (PIV) Leakage, was discovered not met for the Residual Heat Removal (RHR) System interlock function. This was due to the RHR System interlock bistables having a setpoint of 450 psig decreasing pressure and a reset of 480 psig increasing pressure, +/- 15 psi, (0.5%). Surveillance Requirement (SR) 3.4.14.2 requires verification that the RHR System interlock prevents the valves from being opened with a simulated or actual RCS pressure signal 450 psig. The SR was considered to have not been met from the first time the SR was performed following the implementation of License Amendment 207, conversion to Improved Standard Technical Specifications. TS allow the SR to not be met as long as the Required Action and associated Completion Time of LCO 3.4.14 Condition C are met, isolate each affected line within 4 hours, or comply with LCO 3.0.3. A review of plant operating history determined that the requirements of TS were not complied with during the startup from the last refueling outage in May of 2012. Thus, this event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition prohibited by the plant's Technical Specifications.
3052012009 | Kewaunee | 12/03/2012 | 02/07/2013 | ML13045A48 | <strong>Missed Verification of Offsite Circuit Breaker Alignment and Power Availability</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2012, while in Mode 1, Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1, "AC Sources - Operating," Condition B, Required Action B.1 was discovered to have not been completed within the required Completion Time, following one Emergency Diesel Generator (EDG) [DG] being made inoperable for scheduled "B" train maintenance on December 3, 2012. Required Action B.1, to "Perform SR 3.8.1.1 for the offsite circuit(s)," had been performed, with acceptable results, for the initial 1 hour Completion Time immediately following the EDG being declared inoperable. However, it was not fully performed "Once per 8 hours thereafter for the two subsequent 8 hour periods. The EDG was restored to operable less than 24 hours after being made inoperable and thus LCO 3.8.1 was met and Required Action B.1 was no longer applicable. This incomplete surveillance was due to a missing page in the procedure directing the performance of the Surveillance Requirement (SR). Upon discovery one week later, a prompt review of computer trend data for that time period showed the SR 3.8.1.1 acceptance criteria were met. This event is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) for any operation or condition which was prohibited by the plant's Technical Specifications.
3062012001 | Prairie Island 2 | 02/21/2012 | 03/20/2013 | ML13081A41 | <strong>Unit 2 Manual Reactor Trip due to Feedwater Heater Hi-Hi Alarm</strong><br /><i>Abstract:&nbsp;</i>On February 21, 2012, Prairie Island Nuclear Generating Plant (PINGP) Unit 2 was performing a normal shutdown in preparation for refueling outage 2R27. With Unit 2 at approximately 11.42% power, the reactor was manually tripped in accordance with the 21/22/23 Feedwater Heater Hi-Hi alarm response procedure. There were no other unusual /not understood events associated with the shutdown. The Equipment Cause Evaluation (ECE) determined that the third stage low-pressure FWH bypass line to the condenser is potentially restricting flow to the dump valve. The ECE also determined that the Moisture Separator Reheater Control valves are ramped closed earlier than necessary and are fully closed by approximately 20% reactor power. This causes excessive moisture in the extraction steam at low power and results in more water accumulating in the low-pressure feedwater heaters. "The RCE determined that station implementation of the Corrective Action Program (CAP) and Equipment Reliability processes have not minimized risk of event recurrence while implementing long-term corrective actions by requiring interim/mitigating actions be taken prior to the next potential opportunity for recurrence."
3062012002 | Prairie Island 2 | 07/20/2012 | 04/04/2013 | ML13099A26 | <strong>Unit 2 Emergency Diesel Generators Inoperable Due To Missing Flood Control Barrier Seal</strong><br /><i>Abstract:&nbsp;</i>On July 20, 2012, the Prairie Island Nuclear Generating Plant (PINGP) Unit 2 declared Emergency Diesel Generators (EDGs) D5 and D6 inoperable due to a missing hazard barrier. The missing hazard barrier is required to be installed with Unit 2 in Modes 1, 2, 3 and 4 when the Main Steam Isolation Valves (MSIVs) are open. <br /><br /> Technical Specification (TS) Limiting Condition for Operation (LCO) 3.8.1 Condition B was entered for both EDGs and LCO 3.8.1 Condition E was entered for two EDGs inoperable on the same unit. The Root Cause of this event is attributed to a previous Apparent Cause Evaluation (ACE), which did not perform an extent of cause as part of the evaluation. At that time there were no requirements to perform an extent of cause evaluation on ACES that were identified Significant Condition Adverse to Quality (SCAQ). The ACE did not evaluate the extent of cause and an opportunity was missed to identify and correct this condition.
3092012001 | Maine Yankee | 01/12/2012 | 03/05/2012 | ML12081A00 | <strong>Reportable Safeguards Event</strong><br /><i>Abstract:&nbsp;</i>This report is submitted pursuant to the requirements of 10 CFR 73.71 (d) for a 60-day written report and contains no Safeguards Information (SI). On January 12, 2012 the Maine Yankee Independent Spent Fuel Storage Installation (ISFSI) oncoming night shift security force discovered a partially uncompensated degradation in a security system located in the isolation zone for the Protected Area. The evening shift security force had bypassed security equipment due to environmental conditions and instituted compensatory measures that were not fully effective for the intended purpose. The oncoming night shift security force identified the problem and immediately implemented fully effective compensatory measures. The following significant corrective actions have been taken or are planned to prevent recurrence: 1) Retraining security force members on all Critical Tasks in the Security Training & Qualification Plan. 2) Enhancing procedures on the implementation of compensatory measures. 3) Improving the effectiveness of the Training Program.
3112012001 | Salem 2 | 03/23/2012 | 05/21/2012 | ML12144A29 | <strong>Automatic Reactor Trip due to Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On March 23, 2012, at approximately 1428 hrs. Salem Unit 2 experienced an automatic reactor trip due to a turbine trip. The cause of the turbine trip was the spurious, simultaneous spiking of all three 103% overspeed inputs to the turbine Digital Electro Hydraulic Controller. At the time of the trip, the 22 Station Power Transformer was tagged out of service for maintenance. Upon unit trip and non-vital bus transfer from the Auxiliary to the Station Power Transformers, power to the F and G group buses was lost due to unavailability of the 22 Station Power Transformer. The 23 and 24 Reactor Coolant Pumps tripped as a result of the F and G busses being de-energized. This report is being made in accordance with 10CFR 50.73(a)(2)(iv)(A), "Any event or condition that resulted in manual or automatic actuation of any of the systems listed in paragraph (a)(2)(iv)(B)..."
3112012002 | Salem 2 | 07/05/2012 | 09/04/2012 | ML12251A00 | <strong>Auxiliary Feedwater Flow Control Valve Failed Open with Zero Demand</strong><br /><i>Abstract:&nbsp;</i>On July 5, 2012, at approximately 0307 hours while performing in-service testing of the 21 Auxiliary Feedwater (AFW) Pump {BA/P}, 23AF21, the AFW Flow Control Valve {BA/FCV} to the 23 Steam Generator (SG) {SB/SG}, failed open and could not be closed from the control room. The 21 AFW Pump was stopped and the 23AF21 valve closed automatically. The failure of the 23AF21 valve to respond from the control console was due to a mispositioned air supply valve to the 23AF21 valve electro-pneumatic converter. This report is being made in accordance with 10 CFR 50.73(a)(2)(i)(B), "Any operation or condition which was prohibited by Technical Specifications" and 10 CFR 50.73(a)(2)(v)(D), "Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident."
3112012004 | Salem 2 | 11/04/2012 | 12/26/2012 | ML13002A00 | <strong>Isolation of Service Water to the Emergency Diesel Generators While in Mode 6</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2012, Salem Unit 2 was in Mode 6, with fuel movement in progress. The 22 Service Water {BI} (SW) Nuclear header was isolated for outage maintenance. At approximately 0849 hours, the 21 Diesel {EK} (EDG) Cooling SW Inlet Valve, 21SW21 {BI/ISV}, was inadvertently closed by a Nuclear Equipment Operator (NEO). Closure of 21SW21 resulted in inoperability of all three Unit 2 EDGs by isolating the remaining SW train to the EDGs. Fuel movement was suspended in accordance with Unit 2 Technical Specification (TS) 3.8.1.2.b., Action b. At approximately 0855 hours, 21SW21 was opened, restoring operability to the EDGs. This event is being reported under 10 CFR 50.73(a)(2)(vii), Any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system designed to (D) Mitigate the consequences of an accident."
3112012005 | Salem 2 | 11/25/2012 | 01/15/2013 | ML13023A11 | <strong>Reactor Trip Due to Failure of a Feedwater Control Valve</strong><br /><i>Abstract:&nbsp;</i>On November 25, 2012, Salem Unit 2 was in Mode 1 operating at 92% reactor thermal power. At approximately 1128 hours, operators received an Advanced Digital Feedwater Control System (ADFCS) trouble alarm and entered the abnormal operating procedure in response to indications of a lowering level in the 24 Steam Generator (SG){SJ}. The Reactor Operator (RO) took action to recover SG level by taking manual control of the 24 SG Feedwater Control Valve 24BF19 {SJ/LCV}, but was unsuccessful in recovering 24 SG level control. At 1130 hours while operators were proceeding to manually trip the reactor, an automatic reactor trip occurred due to a Lo Lo Level in the 24 SG. The cause of the trip was the failure of the 24BF19 valve due to debris inside the valve positioner current to pneumatic (I/P) converter. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A), for actuation of the Reactor Protection and Auxiliary Feedwater systems.
3132012001 | Arkansas 1 | 02/15/2012 | 04/12/2012 | ML12103A39 | <strong>Violation of Technical Specification due to the Failure to Enter the Appropriate Technical Specifications or Complete the Associated Required Actions due to Misapplication of Technical Specification Bases</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2012, Arkansas Nuclear One Unit-1 (ANO-1) received the NRC 4th quarter Integrated Inspection Report identifying a noncited violation of Unit 1 Technical Specification (TS) 3.8.4, “DC Sources-Operating,” TS 3.8.7, “Inverters-Operating,” and TS 3.8.9, “Distribution Systems-Operating,” due to the licensee’s failure to complete the associated required actions prior to the specified completion times while the associated emergency switchgear room chillers were out of service for planned maintenance. Specifically, on December 7, 2011, VCH-4A Switchgear Room Chiller was removed from service to perform maintenance for 27.3 hours, and on December 19, 2011, VCH-4B Switchgear Room Chiller was removed from service to perform maintenance for 15.5 hours. During both maintenance periods, ANO-1 did not enter the subject specifications above, but entered the following: (1) TS 3.7.7 Condition “A” for one loop of Service Water System (SWS) being inoperable with an associated completion time of 72 hours, (2) TS 3.8.1 Condition “B” for one Emergency Diesel Generator inoperable with a 7 day completion time, and (3) TS 3.0.6, to support the emergency switchgear room chiller being out of service for planned maintenance. The SWS specification was applied as allowed by the ANO-1 TS Bases, considering that the switchgear room chillers were supplied by the SWS, which is the ultimate cooling medium for rooms which contain the electrical equipment. In light of the aforementioned non-cited violation, ANO-1 currently complies with all applicable switchgear TS actions (the most limiting being 8 hours) when either switchgear room chiller is out of service.
3132012002 | Arkansas 1 | 02/15/2012 | 04/12/2012 | ML12103A39 | <strong>Inoperable Main Feedwater Startup Valve and Low Load Valve Controllers due to a Degraded Resistor in an Integrated Control System Auxiliary Relay Results in a Condition Prohibited by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On 2/15/2012 at 0300 (CST), Arkansas Nuclear One - Unit 1 Control Room Operators discovered that the CV-2673 Feedwater Train “B” Start-Up Valve Hand/Auto (H/A) station and the CV-2672 Feedwater Train “B” Low Load Valve H/A station on Control Room panel C03 had no light indications for the “auto” or “hand” mode. Appropriate Technical Specifications (TS) were entered at the time of discovery, with TS 3.7.3 Condition E (two feedwater control valves in the same flow path inoperable) requiring flowpath isolation within 8 hours; otherwise TS 3.7.3 Condition F requires the unit to be in Mode 3 within 6 hours and Mode 4 within 12 hours. TS 3.7.3 Condition E completion time expired at 1100 on 02/15/2012, at which time the Operations staff began preparations for shutdown. After corrective maintenance, both subject H/A stations were returned to auto, and applicable TS were exited at 1323 on 02/15/2012. Plant computer points indicated that both H/A stations had previously transferred from auto to hand with no operator action at 1924 on 2/14/2012, resulting in the subject valves being inoperable for a total of 18 hours, a condition prohibited by TS. Subsequent investigation revealed that a degraded carbon resistor on an Integrated Control System (ICS) 24 vDC auxiliary relay module resulted in a blown fuse in an ICS transfer relay module, causing both of the subject H/A stations to transfer from auto to hand. The apparent cause was determined to be a latent design change error from 1990 that resulted in the 24 vDC auxiliary relay module being utilized in a 48 vDC service application.
3152012001 | Cook 1 | 02/16/2012 | 04/13/2012 | ML12125A03 | <strong>Two Power Range Nuclear Instruments Inoperable due to Common Cause</strong><br /><i>Abstract:&nbsp;</i>On February 16, 2012, at 2150 hours at Donald C. Cook Nuclear Plant, actions required by Technical Specification Limiting Condition for Operation (LCO) 3.0.3 were not satisfied. Conditions for entry into LCO 3.0.3 had been met on February 16, 2012, at 2050, but were not discovered at the time. Due to a faulty recorder being used to adjust multiple channels of Power Range Nuclear Instrumentation (NI), two channels became inoperable at the same time. The recorder was not discovered to be faulty until after two channels had already been adjusted out of tolerance. On February 17, 2012, at 1005, Operators entered LCO 3.0.3 when they discovered that two NI channels were inoperable at the same time. Having more than one channel inoperable at a time is contrary to LCO 3.3.1 which provides for inoperability of only one NI channel at a time. LCO 3.0.3 was exited on February 17, 2012 at 1046 when one of the two inoperable NI channels was restored to operable after using a replacement recorder to make adjustments. This event is reportable as a Licensee Event Report in accordance with 10 CFR 50.73(a)(2)(i)(B) "Any operation or condition which was prohibited by the plant's technical Specifications...", and 10 CFR 50.73(a)(2)(vii) "Any event where a single cause or condition caused at least one independent train or channel to become inoperable in multiple systems or two independent trains or channels to become inoperable in a single system..."
3152012002 | Cook 1 | 07/19/2012 | 09/14/2012 | ML12272A28 | <strong>Unit 1 Exceeded Technical Specification Time Limit to Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 7/19/2012, at 0734, operators received unexpected annunciators and determined that control power was lost to Unit 1 Train B Steam Generator Stop Valve (SGSV) Dump"Valves on two SGSV's, rendering that train of Steam Line Isolation functions for those stop valves inoperable. Technical Specification (TS) Limiting Condition of Operation (LCO) 3.3.2 Condition C required restoration to operable status within 6 hours (1334). At 1030, one dump valve was declared operable following replacement of a blown fuse and successful testing. When the functions of the remaining dump valve were not restored to operable within 6 hours, LCO 3.3.2 Condition I was entered, requiring the plant to be in Mode 3 within 6 hours (1934). At 1530, power reduction commenced. At approximately 1730, the Nuclear Regulatory Commission (NRC) granted enforcement discretion to extend LCO 3.3.2 Required Actions for 24 hours. Power reduction was terminated at 50%. At 2029, following repairs and successful testing of the remaining dump valve, LCO 3.3.2 Conditions B, C, and I were exited. Loss of power was due to two blown fuses. The first blown fuse was due to low internal resistance in the solenoid cable splice. The second blown fuse was due to a transient ground. The transient ground was induced by the failure which caused the first blown fuse. Replacement of the cable splice, solenoid, and both fuses restored power. While the enforcement discretion allowed remaining in Mode 1, Unit 1 was not in Mode 3 at 1934 as required by TS. Exceeding the time limit is a condition prohibited by TS, reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). Event Report 48120 was submitted at 1828 on 7/19/2012 to report initiation of a shutdown required by TS, reportable in accordance with 10 CFR 50.72(b)(2)(i).
3162012001 | Cook 2 | 03/22/2012 | 05/18/2012 | ML12152A15 | <strong>Containment Divider Barrier Seal Inoperable During Plant Operation</strong><br /><i>Abstract:&nbsp;</i>On March 22, 2012, with Donald C. Cook Nuclear Plant Unit 2 in Mode 5 for a refueling outage, a Technical Specification (TS) required examination of the containment divider barrier seal identified one seal mounting bolt with a loose nut. On April 2, 2012, as the examination continued, two shallow nicks were found in one area of the seal material. An evaluation of the deficiencies concluded that the divider barrier seal was inoperable, as it did not meet the requirements of the seal inspection surveillance. It is not known when the deficiencies occurred. It is conservatively concluded that the deficiencies existed during plant operation in Modes 1 through 4. Because the deficiencies had not been recognized, actions required by TS for an inoperable divider barrier seal in Modes 1 through 4 were not taken. Failure to take the required actions constitutes a noncompliance with the TS and is therefore being reported under 10CFR50.73(a)(2)(i)(B) "Operation or Condition Prohibited by Technical Specifications." The causes of the loose nut and seal damage are unknown. The loose nut was tightened and the damaged seal material was repaired. The evaluation of the seal deficiencies concluded that the divider barrier seal was fully functional. The identified conditions had no effect on plant nuclear safety and were not risk significant.
3162012002 | Cook 2 | 04/30/2012 | 06/26/2012 | ML12193A08 | <strong>Unit 2 Reactor Trip from Generator Trip due to Incorrect Relay Setting</strong><br /><i>Abstract:&nbsp;</i>On April 30, 2012, at 2328 hours, during power ascension following a recent refueling outage, Donald C. Cook Nuclear Plant (CNP) Unit 2 Reactor tripped automatically from a trip of the main turbine. All control rods fully inserted and the auxiliary feedwater system (AFW) started and performed as designed. On May 1, 2012, at 0013 hours, the Main Steam Isolation Valves (MSIV) were closed and the Reactor Coolant System (RCS) temperature was controlled by the steam generator atmospheric relief valves (PORV). Closure of the MSIVs was based on cooldown of the RCS and recovered after closing the MSIVs. All major plant components functioned as designed with no safety system functional failures. The reactor trip was reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and the AFW actuation was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A). The reactor trip and the AFW system actuation are reportable as a Licensee Event Report (LER) in accordance with 10 CFR 50.73(a)(2)(iv)(A). The turbine trip was caused by the actuation of the main generator unit differential and overall differential lockout relays. The overall differential function of a multifunctional digital relay actuated and operated the lockout relays. The relay was installed during a recent refueling outage. The actuation was caused by an incorrect current transformer winding compensation setting within the relay. Action taken included correcting the relay setting.
3172012001 | Calvert Cliffs 1, Calvert Cliffs 2 | 05/18/2012 | 07/17/2012 | ML12201A06 | <strong>Valve Surveillance Requirement Not Met due to Legacy Issues</strong><br /><i>Abstract:&nbsp;</i>On May 18, 2012 a past condition at the site was determined to be reportable. Technical Specification Surveillance Requirement 3.5.2.1 requires the low pressure safety injection (LPSI) flow control valve on each unit to be verified in the open position with power removed from the valve operator. The valve is located in the common discharge header of both LPSI trains so if the valve went shut it would prevent both LPSI trains from performing their safety function. The method previously used to remove power from the valve was to isolate the electric signal going to the valve's current to pneumatic transducer with a key switch from the Control Room. It was determined that this method did not fully remove power to the valve operator. Apparent causes involved technical inaccuracies/omission of relevant information and document changes completed with inadequate reviews and documentation during the 1970s. Since the method did not fully accomplish the Surveillance Requirement, the associated Limiting Condition for Operation was not met. Since this condition unknowingly existed, Required Actions were not taken which placed both units in a condition prohibited by Technical Specifications. In December 2011, Calvert Cliffs switched to locking shut the instrument air valve leading to the valve positioner as the method to ensure power is removed to the valve operator.
3172012002 | Calvert Cliffs 1 | 07/17/2012 | 09/11/2012 | ML12256A98 | <strong>Reactor Coolant Pressure Boundary Leakage due to Tubing High Cyclic Fatigue</strong><br /><i>Abstract:&nbsp;</i>On July 17, 2012, Reactor Coolant System pressure boundary leakage was determined to exist on Unit 1 11A Reactor Coolant Pump differential pressure transmitter tubing. Operators commenced a Technical Specification required unit shutdown. With reactor power at 10 percent a containment entry was made to isolate the leak. This effort stopped the steam emanating from the insulated tubing. Unit 1 returned to full power. Unit 1 leak rate data was monitored for the next several days. It was determined conditions did not improve as expected. An additional containment entry was made on July 21, 2012 which identified that Reactor Coolant System pressure boundary leakage existed past the previously shut isolation valves. Operators conducted a Technical Specifications required shutdown of Unit 1 to MODE 5. The source of the leak was a crack in the tubing side weld of the pipe to tube adapter. The cause of the leak was high cyclic fatigue. The cyclic fatigue was caused due to a vertical support for the tubing that was not connected. Corrective actions included replacement of the adapter, the affected portion of tubing, and the connection of a re-engineered vertical support. The similar welds on the other Unit 1 reactor coolant pump differential pressure transmitter tubing runs were inspected with no issues identified. Unit 1 returned to full power on July 25, 2012.
3172012003 | Calvert Cliffs 1 | 08/12/2012 | 06/21/2013 | ML13175A35 | <strong>Plant Shutdown Completed due to Control Element Assembly Misalignment</strong><br /><i>Abstract:&nbsp;</i>On August 12, 2012, shutdown group Control Element Assembly (CEA) 9 dropped to the fully inserted position. At the time of the event, Unit 1 was operating at 100 percent rated thermal power and no planned CEA motions were in progress. Operators entered applicable Technical Specification Action Statements for the dropped CEA. It was identified that the CEA alignment could not be restored within the required completion time and operators entered Action Statement 3.1.4.F, which required the unit to be in Mode 3 within 6 hours. Operators began the Technical Specification required unit shutdown at 1425. Unit 1 entered Mode 3, Hot Standby, at 1959 on August 12, 2012 and Mode 5, Cold Shutdown, at 1257 on August 13, 2012. The CEA dropped due to the failure of the Control Element Drive Mechanism (CEDM) upper gripper coil. The upper gripper coil failed due to an internal short circuit most likely caused by overheating. The most probable cause is degradation in the CEDM cooling system. A contributing cause is potential low margin in the CEDM cooling system. Corrective actions include replacement of the CEDM coil stack, adjusting holding voltage, testing to identify coil degradation, and review of CEDM cooling system operation. The unit was returned to full power at 1630 on August 18, 2012. No previous occurrences were identified involving a unit shutdown due to a dropped CEA.
3212012001 | Hatch 1 | 02/28/2012 | 05/01/2012 | ML12123A07 | <strong>Non-Compliance with Technical Specification 3.9.4 for Control Rod Position Indication During Shutdown</strong><br /><i>Abstract:&nbsp;</i>On 2/25/2012, with the unit in Mode 5 for refueling, the "full-in" indication for Control Rod (CR) 22-27 was noted to be inoperable, and a required action statement (RAS) for TS 3.9.4 was entered. In accordance with the RAS the control room staff visually verified that the CR was fully inserted, action was taken to electrically disarm the associated CR drive, and a tag-out was conducted as part of the disarming action. A modified probe buffer card was installed to bypass the "full-in" indication signal in order to remove the rod block. Notation of the use of the modified probe buffer card was added to an existing TS RAS to track its installation and loss of the RPIS indication. At 2121 EST on 2/28/2012, the tag-out described above was cleared (i.e., removed) without removing the modified probe buffer card and without performing a functional test of the "full-in" indication prior to moving fuel in the reactor vessel. Fuel movement occurred from the time the tag-out was removed until 0817 EST on 3/2/2012 when the error was discovered; resulting in a condition prohibited by TS for CR position indication. The cause of this event was attributed to less than adequate procedural controls and the failure of involved personnel to effectively "self check" as a human error prevention technique. A procedure change was implemented to require the shift supervisor to sign a tag-out if used to comply with a TS requirement.
3212012002 | Hatch 1 | 03/10/2012 | 08/16/2012 | ML12229A45 | <strong>Failure of 1C EDG Output Breaker to Close Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During the performance of the 1C emergency diesel generator (EDG) loss of offsite power (LOSP) logic system functional test (LSFT), on March 10, 2012, at 2350 EST, the EDG output breaker failed to close and supply power to the 1G 4kV bus. This failure resulted in the inability to energize the 1G bus and the safety-related buses fed by this bus. The operating crew attempted to restore normal power to the bus, but was unsuccessful. A DC ground indication was also received when the 1C EDG output breaker failed to close. Troubleshooting revealed a connecting screw on the circuit breaker auxiliary switch making contact between terminals 8 and 10, creating a fault between the positive and negative portions of the DC circuit when the LOSP test permissive was applied to the closing circuit for the 1C EDG output breaker. This short prevented the output breaker closing coil from functioning as required. The direct cause for the failure of the breaker to close is attributed to an apparent vendor quality issue associated with the alternate supply breaker for the 1G emergency bus that occurred at the vendor facility during the manufacturing/assembly process. The installation of a screw on an auxiliary switch termination that penetrated the insulation of an adjacent lug created a short circuit condition that could only be manifested during an actual or simulated LOSP condition. The breaker was replaced and testing performed to confirm the output breaker "close" permissive functioned as required. The condition was reviewed for applicability to 10 CFR 21 and determined to not be reportable.
3212012003 | Hatch 1 | 03/13/2012 | 05/10/2012 | ML12135A39 | <strong>Leak in Reactor Pressure Boundary at Small Bore Piping Fillet Weld</strong><br /><i>Abstract:&nbsp;</i>On 3/13/2012, during the Reactor Pressure Vessel (RPV) Pressure Test walk-down with the unit in Mode 4 for leakage testing, a through-wall leak was identified in a small bore line located upstream of a High Pressure Coolant Injection (HPCI) valve inboard of the piping's connection to the Main Steam piping. The leak identified during this event was in the thicker portion of the fillet weld adjacent to the socket elbow. Initial evaluation of the crack in the subject HPCI piping and elbow by an experienced site Quality Control inspector and a senior Southern Nuclear metallurgist concluded that the most apparent cause of the weld defect that led to the leak was inadequate root penetration in the weld. The actual cause has not yet been fully determined. The section of piping in which the leak was located will be sent to a vendor for inspection and expert determination of the most probable cause of the through-wall leak. Following removal and repair of the subject piping, a leak test was performed at 920 psig with no leaks identified. The Technical Specification (TS) definition of pressure boundary leakage is leakage through a non-isolable fault in the reactor coolant system. By its location, the leak met this definition. Inspection of the weld and adjacent areas determined the leak had existed when the Unit was in Mode 1, and no such leakage is allowed by TS.
3212012004 | Hatch 1 | 03/26/2012 | 05/25/2012 | ML12146A27 | <strong>Corrosion-Induced Bonding Results in Setpoint Drift for Multiple Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>On March 26, 2012, at approximately 1000 EDT, Unit 1 was at 98.6 percent rated thermal power (RTP) when the "as-found" testing results of the two-stage main steam safety relief valves (SRVs) were received which indicated that eight of eleven SRVs had experienced setpoint drift during the previous operating cycle which resulted in their failing to meet the Technical Specification (TS) opening setpoints of 1150 psig +/- 3% as required by TS surveillance requirement 3.4.3.1. The root cause of the SRV setpoint drift is attributed to corrosion-induced bonding between the pilot disc and seating surfaces. This conclusion is based on previous root cause analyses and the repetitive nature of this condition at Hatch and within the BWR industry. The 2-stage SRVs with stellite-21 seats were removed from Unit 1 during the 2012 refueling outage and replaced with 2-stage SRVs with the application of platinum to the pilot discs as the long term corrective action for the historically observed corrosion-induced bonding with consequential setpoint drift. The use of 2-stage SRVs with platinum coated discs is regarded as a proven industry-wide solution for the corrosion-induced bonding phenomenon with excellent results noted for the first operating cycle after installation.
3232012001 | Diablo Canyon 2 | 08/18/2012 | 10/16/2012 | ML12290A67 | <strong>Failure to Meet Emergency Diesel Generator Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 18, 2012, Diablo Canyon Power Plant (DCPP) Unit 2 Operations personnel discovered that the belt connecting Emergency Diesel Generator (EDG) 2-3 to its fuel oil booster pump (FOBP) was broken. DCPP operators declared EDG 2-3 inoperable, entering Technical Specification (TS) 3.8.1. On August 21, 2012, at 0330, operators declared EDG 2-3 operable after replacing both the FOBP and its drive belt. The cause analysis concluded that the belt and FOBP had failed following satisfactory performance of a surveillance test on August 3, 2012, at 1304 PDT. EDG 2-3 was therefore inoperable longer than allowed by TS 3.8.1.B.4, and is thus reportable under 10 CFR 50.73(a)(2)(i)(B). During the time between August 3, 2012, at 1304 PDT, and August 21, 2012, at 0330 PDT, EDG 2-2 was declared inoperable twice for testing, but was still available. When EDG 2-2 was inoperable, DCPP Unit 2 only had one operable EDG, since the broken belt rendered EDG 2-3 inoperable. Two EDGs are required to be operable to mitigate the consequences of a design basis accident, making this situation reportable under 10 CFR 50.73(a)(2)(v)(D). PG&E will reduce the EDG 2-3 drive belt tension specification in plant procedures pending vendor approval. PG&E will establish a periodic replacement strategy for the FOBP in lieu of the present condition-monitored replacement strategy.
3232012002 | Diablo Canyon 2 | 10/11/2012 | 06/26/2013 | ML13177A27 | <strong>Coupling Capacitor Voltage Transformer Bushing Failure Causes Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On October 11, 2012, at 12:08 PDT, the Diablo Canyon Power Plant (DCPP) Unit 2 500kV line differential relay actuated, resulting in a unit trip. The 500kV coupling capacitor voltage transformer (CCVT) bushing experienced a flashover to ground, resulting in a unit trip and turbine trip. With the turbine tripped and Unit 2 operating above the 50 percent power permissive, the reactor protection system initiated a reactor trip as designed. All plant equipment, including the auto-start of the auxiliary feedwater (AFW) system, responded as designed.<br><br> DCPP determined that the bushing failed because the insulator minimum creepage distance was not consistent with industry codes and standards for its operating environment. When the bushing was replaced in 2011, DCPP staff made unvalidated assumptions, and over-relied on industry experts. DCPP will move CCVT metering to an area with lower contamination levels, and reinforce expectations to review current industry codes and standards.<br><br> Additionally, an unintended AFW pump restart occurred following this event as a result of a human performance error that resulted in a procedure not being revised following a plant modification. DCPP will revise procedure supporting documents and train procedure writing staff on use of the supporting documents to identify all changes required by a plant modification.
3252012001 | Brunswick 1 | 02/22/2012 | 04/21/2012 | ML12124A27 | <strong>Manual Reactor Protection System Actuation in Anticipation of a Loss of Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2012, at 2319 hours Eastern Standard Time (EST), a manual Reactor Protection System (RPS) actuation was inserted on Unit 1 in anticipation of a loss of condenser vacuum. Shortly before the manual RPS actuation, Circulating Water Intake Pump (CWIP) 1B tripped due to high delta-pressure across the intake traveling screen. This caused the trip of the remaining Unit 1 CWIPs. Previously, at 1859 hours, balance of plant (BOP) bus Common C unexpectedly de-energized. This resulted in a loss of power to the CWIP traveling screen motors which, in turn, lead to the high delta-pressure across the traveling screens. As a result of the scram, reactor water level reached the Reactor Vessel Water Level - Low Level 1 actuation set point and Primary Containment Isolation System (PCIS) Groups 2 and 6 isolations occurred. Additionally, the Main Steam Isolation Valves (MSIVs) (i.e., PCIS Group 1) were manually closed prior to reaching the Condenser Vacuum - Low actuation set point. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in manual actuation of the RPS system and automatic and manual actuations of PCIS. The root cause of this event is inadequate preventive maintenance (PM) for the 4160/480 V transformer associated with the Common C BOP bus. Corrective actions include the establishment of appropriate PM tasks for the 4160/480 V transformers.
3252012002 | Brunswick 1 | 03/08/2012 | 05/02/2012 | ML12131A44 | <strong>Implementation of Enforcement Guidance Memorandum (EGM) 11-003</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2012, and on March 13, 2012, Unit 1 implemented the guidance of EGM 11-003, "Enforcement Guidance Memorandum on Dispositioning Boiling Water Reactor Licensee Noncompliance with Technical Specification Containment Requirements During Operations With a Potential for Draining the Reactor Vessel," dated October 4, 2011. Consistent with EGM 11-003, secondary containment operability was not maintained during Operations With a Potential for Draining the Reactor Vessel (OPDRV) activities and Required Action C.1 of Technical Specification (TS) 3.6.4.1, "Secondary Containment," was not completed. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's TSs. Implementation of EGM 11-003 during the Unit 1 refueling outage was a planned activity. As such, there was no root cause evaluation of the event. Consistent with the guidance provided in EGM 11-003, BSEP will submit a license amendment request to adopt a Technical Specifications Task Force (TSTF) traveler associated with generic resolution of this issue, within four months after the issuance of the Notice of Availability of the TSTF traveler.
3252012003 | Brunswick 1, Brunswick 2 | 04/09/2012 | 06/07/2012 | ML12172A34 | <strong>Valid Emergency Diesel Generator Actuation</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2012, at 0529 hours Eastern Daylight Time (EDT), electrical power was lost to the 4160 V emergency bus E1. Activities to support performance of procedure OMST-DG11R, "DG-1 Loading Test," were in progress when technicians connected a recorder to the incorrect terminals of an under-voltage relay on emergency bus E1 and caused the normal supply breakers for emergency bus E1 to open. Emergency Diesel Generator (EDG) 1 automatically started and re-energized emergency bus E1 per plant design. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as an event that resulted in automatic actuation of a system specified in 10 CFR 50.73(a)(2)(iv)(B). The root cause of this event is inadequate use of human performance tools when connecting recorders in preparation for performing OMST-DG11R. Corrective actions include revising the EDG loading test procedures to provide instructions on labeling cables and to incorporate a method to record cable assignments to respective procedural steps.
3252012004 | Brunswick 1 | 05/02/2012 | 06/29/2012 | ML12193A09 | <strong>High Pressure Coolant Injection (HPCI) Inoperable due to Erratic Governor Operation</strong><br /><i>Abstract:&nbsp;</i>On May 2, 2012, at approximately 1758 Eastern Daylight Time (EDT), the Unit 1 High Pressure Coolant Injection (HPCI) system was declared inoperable due to inability to maintain stable system flow and discharge pressure due to erratic governor operation. The failure was discovered during performance of Surveillance Requirement 3.5.1.7 (i.e., HPCI high pressure testing at greater than or equal to 945 psig) during startup from the recently completed refueling outage. This condition is being reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of the safety function of a system that is needed to mitigate the consequences of an accident and 10 CFR 50.73(a)(2)(i)(B) as operation prohibited by the plant's Technical Specifications. The direct cause of the erratic HPCI governor operation was a failed Ramp Generator Signal Converter (RGSC) operational amplifier. The root cause of the RGSC failure is the lack of a replacement preventive maintenance (PM) task for the RGSC. The corrective action to prevent recurrence for this event is to establish the appropriate PM for periodic replacement of the RGSC on both units' HPCI systems.
3252012005 | Brunswick 1, Brunswick 2 | 08/29/2012 | 10/29/2012 | ML12312A06 | <strong>Local Control Capability of Emergency Diesel Generator No. 2 Not Available</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2012, during planned maintenance on Emergency Diesel Generator No.2 (EDG 2), a post-maintenance continuity test associated with the Alternate Safe Shutdown (ASSD) switch on EDG 2 revealed unexpected results when the switch was taken to the LOCAL position. Troubleshooting activities determined the switch to be operating properly. However, a current path preventing isolation of the control room circuit remained. It was determined that a wire, not identified in EDG wiring diagrams, created a short between two ASSD switch contacts. At 2134 hours Eastern Daylight Time (EDT) on August 29, 2012, it was concluded that the condition may impact the ability of EDG 2 to perform its intended ASSD function. In the event of a fire, an induced fault could potentially affect the ability to locally control EDG 2. Local control of EDG 2 is credited in the safe shutdown analysis. This condition did not affect the Technical Specification operability of EDG 2 and it remained fully capable of performing its intended safety function. The direct cause of this event was a wiring error associated with the local control circuitry for EDG 2. This was a historical error which was likely introduced during the original installation. Therefore, no root cause was determined. The error was limited to EDG 2 and has been corrected.
3252012006 | Brunswick 1 | 09/19/2012 | 11/19/2012 | ML12348A39 | <strong>Operation Prohibited by Technical Specifications due to Operation with a Potential for Draining the Reactor Vessel (OPDRV)</strong><br /><i>Abstract:&nbsp;</i>On September 15, 2012, Unit 1 began a forced outage to replace a 1B recirculation pump seal. On September 17, with the unit in Mode 4, a clearance was hung on the 1B recirculation loop and the recirculation pump suction and discharge isolation valves were isolated to provide the reactor coolant system boundary. After the valves were isolated, there was approximately 10 gpm of leakage by the seats. On September 19, 2012, at approximately 0330 hours Eastern Daylight Time (EDT), secondary containment airlock doors were opened to facilitate additional ventilation flow to the reactor building, thereby improving working conditions. The decision to open the secondary containment airlock doors was based on BSEP established guidance that leakage through mechanical joints (e.g., valve or flange packing leaks, seat leakage through an isolation valve, flange leakage) is not an Operation with a Potential for Draining the Reactor Vessel (OPDRV). The NRC Senior Resident Inspector questioned this position and, ultimately, the NRC concluded that the activity did constitute an OPDRV. Conducting an OPDRV activity coincident with secondary containment being inoperable constituted operation prohibited by Technical Specification (TS) 3.6.4.1 and is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B). The cause of this event was inappropriate application of guidance in plant procedure 001-01.01, "BNP Conduct of Operations Supplement." The immediate corrective action was to re-establish secondary containment.
3252012007 | Brunswick 1, Brunswick 2 | 12/14/2012 | 04/11/2013 | ML13128A06 | <strong>Loss of Control Room Emergency Ventilation</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2012, at approximately 1306 hours Eastern Standard Time (EST), inoperability of both subsystems of the Control Room Emergency Ventilation (CREV) system occurred. Because Brunswick has a shared control room, this placed Unit 1 and Unit 2 in Technical Specification (TS) 3.7.3, Required Action C.1, for two CREV subsystems inoperable (i.e., be in Mode 3 within 12 hours).<br><br> At the time of the event, a modification to upgrade the Control Building fire detection system was in progress. The 2A CREV subsystem was placed in the radiation/smoke protection mode in compliance with the Technical Requirements Manual. This action prevented an auto-start of the 2B CREV subsystem and, as such, TS 3.7.3 Condition A was entered to restore 2B CREV subsystem to operable status within 7 days. During work to electrically isolate one of the fire detectors associated with the 2A CREV subsystem, electrical continuity was lost resulting in a charcoal fire signal being sent to the 2A CREV subsystem circuitry and shutting it down. With the 2A CREV subsystem shut down due to the signal, TS 3.7.3 Required Action C.1 applied for both CREV subsystems being inoperable. Actions were taken to re-start the 2A CREV subsystem, and TS 3.7.3 Required Action C.1 was exited within approximately two minutes.<br><br> The safety consequences of this event were minimal. The condition existed for approximately two minutes, and plant staff took immediate action to return the equipment to service. The apparent cause of the event was inadequate documentation and communication of the required system alignment to support the ongoing modification.
3272012001 | Sequoyah 1, Sequoyah 2 | 12/12/2012 | 02/08/2013 | ML13044A01 | <strong>Unanalyzed Condition Affecting Essential Raw Cooling Water System due to External Flooding</strong><br /><i>Abstract:&nbsp;</i>On December 12, 2012, at approximately 1914 Eastern Standard Time, Sequoyah Nuclear Plant determined that Unit 1 and Unit 2 were at risk of external flooding inundating the Essential Raw Cooling Water (ERCW) Pumping Station through inadequate electrical conduit penetration seals entering the ERCW Pumping Station. This condition could allow flood waters to enter the ERCW Pumping Station at a rate greater than the installed sump pump capacity creating a condition that could result in the ERCW system being unavailable to perform its design function during a flood event above plant grade. No actual flooding condition occurred or currently exists. This condition has no impact on ERCW system operability during any non-flooding event. The root cause evaluation determined that existing documentation including licensing documents and configuration controlled drawings for the ERCW Pumping Station do not contain sufficient information to identify the design basis flood barriers. Compensatory measures are currently in place and permanent modification of inadequate conduit seals are scheduled for repair per design requirements.
3282012001 | Sequoyah 2 | 08/16/2012 | 10/15/2012 | ML12291095 | <strong>Automatic Reactor Trip on Loss of Flow due to a Reactor Coolant Pump Trip</strong><br /><i>Abstract:&nbsp;</i>On August 16, 2012, at approximately 1926 Daylight Savings Time, Sequoyah Nuclear Plant (SQN) Unit 2 automatically tripped on a single loop loss of flow following reactor coolant pump (RCP) 2-4 trip. RCP 2-4 tripped as a result of the 250 volts direct current RCP control circuit energizing the trip coil for RCP 2-4 without a valid signal, resulting in a Unit 2 trip. No testing or surveillance was in progress at the time of the event. Unit 2 was stabilized in hot standby following the automatic reactor trip. The cause of the trip was determined to be the inadvertent operation of a GR-5 ground fault relay, designated as device 500. Failure of the GR-5 relay was caused by the failure of the metal oxide varistor, which is an internal component to the solid state GR-5 relay. The root cause for the failure of the metal oxide varistor was determined to be inadequate preventative maintenance instructions and implementation frequency on GR-5 relays in critical systems. The corrective actions include revising preventative maintenance procedures to address replacement of ABB/ITE relays for critical components. An additional action will replace Unit 1 and Unit 2 ABB/ITE relays, for critical components, that have been in service greater than five refueling cycles based on Operations review of critical components that are directly related to causing a plant trip or Limiting Condition for Operation entry for 8 hours or less. There were no actual safety consequences impacting plant or public safety as a result of this event.
3312012001 | Duane Arnold | 12/02/2011 | 01/31/2012 | ML12032A04 | <strong>Inoperability of Low Pressure Coolant Injection Due to Discharge Line Voiding</strong><br /><i>Abstract:&nbsp;</i>On December 2, 2011, while operating at 100% power, with no Technical Specification (TS) Limiting Condition for Operability (LCO) in effect, Ultrasonic Testing (UT) examination of the ‘B’ Residual Heat Removal (RHR) (IEEE System Code BO) injection line identified an air void of approximately 1.5-2 cubic feet. A void of this size had not previously been analyzed and therefore, the Low Pressure Coolant Injection (LPCI) system was declared inoperable at 1311. On December 3, 2011, after operating RHR in the torus cooling mode, venting of the system, acceptable UT examination results, and completion of an engineering evaluation, LPCI was declared operable at 1650. The cause of this event was inadequate design of the ‘B’ RHR inject line vent pipe location. This design deficiency was corrected on December 9, 2011. During the time that LPCI was inoperable, all other Emergency Core Cooling Systems (ECCS) were fully operable and capable of performing their safety functions. As of the date of this Licensee Event Report (LER), the impact of the void discovered on December 2, 2011 is unknown. Engineering analysis of the void is currently ongoing and a supplemental LER is expected to be submitted by March 8, 2012. Based on the information known at the time of discovery, this event did result in a Safety System Functional Failure and was reported under 10CFR50.72(b)(3)(v)(B) on December 8, 2011, reference Event Notification 47511.
3312012002 | Duane Arnold | 12/29/2011 | 02/27/2012 | ML12059A08 | <strong>Loss of Low Pressure Coolant Injection Safety Function due to Inoperable Instrumentation</strong><br /><i>Abstract:&nbsp;</i>On December 29, 2011, at 2009, while operating at 100% power, during the performance of Surveillance Test Procedure (STP) 3.3.5.1-22, Recirculation Riser D/P A > B Instrument, three of the four recirculation riser differential pressure instruments required maintenance, and all four instruments required calibration. The four instruments support the Low Pressure Coolant Injection (LPCI) Loop Select logic by providing input that identifies and directs LPCI flow to the unbroken recirculation loop to mitigate the consequences of an accident. The conditions of the instruments found during the performance of the STP were such that reasonable assurance that the safety function of LPCI could be fulfilled during a design basis Loss of Coolant Accident (LOCA) did not exist. Reference Event Notification (EN) 47561 dated December 30, 2011. On December 29, 2011, at 2356, all of the instruments were either repaired or re-calibrated to restore the LPCI safety function. The cause of this event was a procedural deficiency that omitted guidance for the correct setting and adjusting of instrument microswitch plunger screws. This omission led to the microswitch sticking and instrument drift. The safety significance of this was minimized by having all other Emergency Core Cooling Systems (ECCS) operable during the event.
3312012003 | Duane Arnold | 02/29/2012 | 04/27/2012 | ML12121A01 | <strong>Secondary Containment Dampers Fail to Close During Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On February 29, 2012, at 0905, while operating at 100% power, during scheduled surveillance testing, it was discovered that Secondary Containment isolation damper 1VAD017B3, Reactor Building Ventilation Supply Isolation Damper would not fully isolate. 1VAD017B3 was declared inoperable per Technical Specification 3.6.4.2 Condition A and an 8 hour action statement to isolate the affected flow path via a closed and deactivated damper was entered. While performing subsequent actions to isolate the companion isolation damper, 1VAD017A3, it was found on February 29, 2012 at 1222 that this damper also failed to fully isolate. This left both Secondary Containment isolation dampers in the same flow path unable to isolate, and Technical Specification 3.6.4.2 Condition B was entered with a 4 hour action statement to isolate the affected flow path. Further actions to isolate the flow path were successful and both 4 hour and 8 hour Technical Specification action statements were completed. The root cause of this event was inadequate vendor manual/work instruction guidance. Both dampers were returned to service on March 12, 2012 after completion of maintenance. This condition was reported under 10 CFR 50.72(b)(3)(v)(C), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of the structures or systems that are needed to control the release of radioactive material. Reference EN#47709. The safety significance of this was minimized by the fact that both trains of Standby Gas Treatment were fully operable during the time the dampers were inoperable in the open position.
3312012004 | Duane Arnold | 07/02/2012 | 08/30/2012 | ML12257A48 | <strong>High Pressure Coolant Injection Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 2, 2012, at 15:05, while operating at 100% power, a spurious isolation of the High Pressure Coolant Injection (HPCI) Outboard Steam Supply Valve and Outboard Torus Suction Valve occurred. The isolation resulted from a trip of the HPCI Steam Leak Detection (SLD) system. Immediate investigations into the event determined that there was no steam leak and the probable cause was from a bad connection in the SLD system. Subsequent investigation identified a broken solid conductor thermocouple extension wire. The wire was damaged earlier in the day as part of maintenance activities investigating erroneous readings on unrelated circuits. The damaged wire was replaced and HPCI was declared operable on July 3, 2012, at 0002. The root cause of this event was an inadequate installation position of a recorder in the control room panel. The recorder was installed in such a manner that the removal of its terminal cover placed excessive stress on the thermocouple wire resulting in its failure. This condition was reported under 10 CFR 50.72(b)(3)(v)(D), any event or condition that at the time of discovery could have prevented the fulfillment of the safety function of the structures or systems that are needed to mitigate the consequences of an accident. Reference EN#48064. The safety significance of this event was minimized by the fact that all other Emergency Core Cooling Systems (ECCS) remained fully operable during the time that HPCI was inoperable.
3312012005 | Duane Arnold | 11/24/2012 | 03/14/2013 | ML13074A03 | <strong>Secondary Containment Damper Inoperable, Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 24, 2012, with the reactor shutdown for a planned refueling outage, Surveillance Test Procedure (STP) 3.6.4.1-01B, which demonstrates the ability of the ‘B’ Standby Gas Treatment System to maintain secondary containment under calm wind conditions, failed to achieve a 0.25 inches water gauge (wg) vacuum at a normal SBGT flow rate of 3800 cubic feet per minute (cfm). Subsequent investigations revealed that secondary containment isolation damper 1VAD017B1 was partially open. Further troubleshooting confirmed that maintenance performed on June 21, 2012 caused the damper to remain partially open. In order to comply with the Technical Specification (TS) Limiting Condition for Operations (LCO), 1VAD017A1 was de-energized in the closed position. With the affected flow path isolated, the ‘B’ SBGT train was able to achieve the required 0.25 in. wg vacuum. Since 1VAD017B1 was inoperable from June 21, 2012 to November 24, 2012, it violated its TS LCO action statement 3.6.4.2.A.1 which requires an inoperable flow path be isolated within 8 hours of inoperability. Therefore, this event resulted in a condition prohibited by TS. The root cause of this event is inadequate work order guidance. The safety significance of this event was minimized by the fact that the ‘A’ damper in the flow path containing 1VAD017B1 was fully operable during the time in question and testing results show that SBGT was capable of achieving 0.25 in. wg vacuum with 1VAD017A1 closed.
3312012006 | Duane Arnold | 12/01/2012 | 03/28/2013 | ML13087A65 | <strong>Unplanned Inoperability of 2 Average Power Range Monitors</strong><br /><i>Abstract:&nbsp;</i>On November 27, 2012 during start up from a recent refueling outage, Local Power Range Monitor (LPRM) 32-25A was identified as providing a ‘zero’ input signal to its associated Average Power Range Monitors (APRMs) C and D. At that time it was believed that there was a blown fuse in LPRM 32-25A’s circuit card and therefore, the LPRM was considered operable. On December 1, 2012, while operating at 71% power, a different operating crew reviewed the condition and bypassed LPRM 32-25A. After bypassing LPRM 32- 25A, indicated reactor power on APRMs C and D increased approximately 4%. At this time, the LPRM was determined to be inoperable. Since the inoperable LPRM was providing inputs to APRMs C and D, Technical Specification (TS) Surveillance Requirement (SR) 3.3.1.1.2 which requires verification of the difference between the APRM channels and calculated power to be within 2% of rated thermal power every 24 hours, was not met. Therefore, this event resulted in a condition prohibited by TS. The cause of this event was inadequate procedure guidance. The safety significance of this event was minimized by the fact that the ARPMs C and D remained capable of performing their required safety functions.
3332012001 | FitzPatrick | 01/26/2012 | 06/26/2014 | ML14177A25 | <strong>Unit Cooler Fan Motor Contactor Low Voltage Test Failure Results in Loss of Safety Function and Condition Prohibited by the Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On 1/26/12, a first time low voltage pickup test was performed for 71MCC-163-OE5 (East Crescent Unit Cooler 66UC-22H Fan Motor). The contactor picked up at 102 VAC versus the 90 VAC Level 2(1) Acceptance Criteria. A calculation was performed to determine Level 1(1) Acceptance Criteria for this application. The Level 1 Acceptance Criterion was established as 97 VAC. The Unit Cooler was therefore non-functional, and is assumed to have been non-functional for a period of three years prior to the time of discovery. 66UC-22H is one of five Unit Coolers in the East Crescent Area Ventilation Subsystem. A review of historical plant data identified five occurrences where the non-functional 66UC-22H resulted in the East Crescent Area Ventilation Subsystem being incapable of performing its specified function, and therefore non-functional. The East Crescent Area Ventilation Subsystem is required to support operability of the ECCS equipment located in the East Crescent. This ECCS equipment was therefore inoperable during the five time periods that were identified. This condition is prohibited by plant Technical Specifications, and resulted in the loss of safety function for the single train HPCI System.<br /><br /> Revision 1 is submitted as clarification, and to correct inaccuracies in the original report relative to how the reporting requirements of 10 CFR 50.73(a)(2)(i)(B) are met by this condition.
3332012002 | FitzPatrick | 08/30/2012 | 02/14/2014 | ML14045A27 | <strong>High Pressure Coolant Injection Pressure Control Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2012, while testing the High Pressure Coolant Injection System (HPCI), it was discovered that water was leaking into the reactor building sump (20TK-69A). This leakage was due to the lifting of HPCI booster pump recirculation safety valve (23SV-66) caused by a failure of HPCI booster pump P-1B recirculation pressure control valve (23PCV-50).<br /><br /> Due to the amount of leakage, the HPCI system may not have been able to meet its mission time without realigning its suction source to the torus. As a result, HPCI was declared inoperable. The most probable cause of the 23PCV-50 failure was material introduced into the sensing line and sensing line filter when the system was filled using torus water during a maintenance activity on June 8, 2012. Immediate corrective actions included replacing the snubber and filter, refilling the sensing line with condensate storage tank water, and then venting the system. Future corrective actions will include revising the procedure used to fill the HPCI system such that it contains additional guidance when filling the HPCI suction piping.<br /><br /> This event is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D) as an event or condition that could have prevented the fulfillment of a safety function of a system required to mitigate the consequences of an accident, and 10 CFR 50.73(a)(2)(i)(B), any operation or condition which was prohibited by the plant’s Technical Specifications.
3332012003 | FitzPatrick | 09/02/2012 | 11/01/2012 | ML12307A07 | <strong>High Pressure Coolant Injection System Inoperable due to Air in Flow Element Sensing Line</strong><br /><i>Abstract:&nbsp;</i>On September 2, 2012, with the James A. FitzPatrick Nuclear Power Plant (JAF) running at 100% power, the High Pressure Coolant Injection (HPCI) System was declared inoperable. This condition was caused by air in the instrument sensing line for the HPCI main pump discharge flow element (23FE-80) causing a false flow indication while HPCI was in standby. An apparent cause evaluation determined that a portion of the sensing line was improperly sloped preventing the line from self venting. This configuration is contrary to design requirements. During a HPCI maintenance activity, the main suction piping was drained in the vicinity of the flow element. Due to the improper slope of the sensing line, a portion of the instrument line was also drained creating an air void. This air void remained in the sensing line during the filling and venting of the suction piping post maintenance. This condition is reportable in accordance with 10 CFR 50.73(a)(2)(v)(D), as any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to mitigate the consequences of an accident. Immediate corrective actions were to fill and vent the instrument lines using a revised procedure that provided instructions to perform a pressurized back flush.
3332012004 | FitzPatrick | 09/16/2012 | 01/24/2013 | ML13025A16 | <strong>Control Rods Inoperable While Entering Plant Outage</strong><br /><i>Abstract:&nbsp;</i>On September 16, 2012, James A. FitzPatrick Nuclear Power Plant (JAF) was reducing power for its scheduled Refuel Outage 20. During the power reduction, reactor pressure lowered below 800 psig prior to the full insertion of 52 control rods which were within the population for friction test control. These 52 control rods were conservatively declared Inoperable because friction testing was not performed within 14 days. This requirement is in accordance with the General Electric Part 21 notification, SC11-05 Revision 1, for Seismic Input in Channel-Control Blade Interference. TS LCO 3.1.3 Condition E was entered for greater than 9 control rods declared Inoperable. This requires the plant to be placed in Mode 3 within 12 hours. Mode 3 was entered 2.5 hours later in accordance with the plan to shutdown for the Outage. The control rods remained fully functional and no control rod movement issues were experienced during the shutdown. An NRC notification was made per 10 CFR 50.72(b)(2)(i), initiation of any nuclear plant shutdown required by the plant’s Technical Specification. This report is being made per 10 CFR 50.73(a)(2)(i)(A), completion of any nuclear plant shutdown required by the Technical Specifications. The SC11-05 compensatory actions will remain active. New fuel channels will be installed in future refueling outages to reduce the channel to control rod blade friction.
3332012005 | FitzPatrick | 10/05/2012 | 12/04/2012 | ML12340A17 | <strong>Transformer Installation Error Causes Loss of Off-Site Power</strong><br /><i>Abstract:&nbsp;</i>On 10/5/12 at 1301, the James A. FitzPatrick Nuclear Power Plant experienced a loss of off-site power. This event occurred after both Reserve Station Service Transformers, 71T-2 and 71T-3, were replaced during Refueling Outage 20. Several hours after installation a maintenance activity which applied a load to the transformer caused a trip of 71T-3 resulting in the loss of off-site power. Investigation identified that the phase A differential protection relay, 71-87-A-1RSSA01, for 71T-3 tripped because the shorting bars (a factory setting) were not removed during installation. The loss of off-site power resulted in a loss of Reactor Protection System power which caused an automatic Primary Containment Isolation System isolation of Reactor Water Clean-Up and Drywell floor and equipment drains. The Emergency Diesel Generators started but one EDG output breaker did not close. In addition, the loss of power caused a loss of Emergency Response communications response capability. This event was reported to the NRC by ENS 48386. The root cause was determined to be not following the work order instructions as written. A contributing cause was an incorrect design drawing.
3332012006 | FitzPatrick | 10/16/2012 | 12/17/2012 | ML12353A31 | <strong>Loss of Safety Function for RHR Shutdown Cooling Isolation Function Due to Reference Leg Leakage During Maintenance</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2012, at 0529, with the reactor in mode 4 and one channel for the Residual Heat Removal(RHR) shutdown cooling isolation function Operable, as permitted by TS 3.3.6.1, Operators identified a rising reactor water level indication on instruments associated with the 3A reactor water level reference leg while actual level remained constant. At 0700, Operators determined this condition rendered the automatic RHRshutdown cooling isolation function on low reactor water level Inoperable. Operators continued to monitor water level and were capable of performing manual isolation. In accordance with Tech Spec 3.3.6.1 Required Action J.1, immediate action was initiated to restore isolation capability. Automatic RHR shutdown cooling isolation capability on low reactor water level was restored at 1040. The cause was leakage past Reference Leg 3A Backfill System injection isolation valves, 02-3NBI-371 and02-3NBI-372 after they were isolated for maintenance. This drained the reference leg and caused aninaccurate water level signal.
3332012007 | FitzPatrick | 11/04/2012 | 01/03/2013 | ML13003A14 | <strong>Reactor Scram Caused by Main Turbine Emergency Trip Lockout Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On November 4, 2012, at 9:53 pm, with the plant operating at 100% power in Mode 1, the James A. FitzPatrick Nuclear Power Plant experienced a reactor scram. The scram was due to a failure of the main turbine emergency lockout valve (94SOV-LV) which caused the main turbine stop valves to begin to close. Once the main turbine stop valves reached 85% open, a reactor scram signal was generated. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A), any event or condition that resulted in manual or automatic actuation of the reactor protection system. Corrective actions included replacing the failed valve, testing the lockout circuit electrically, and shipping the failed valve offsite to have an equipment failure evaluation performed. There was no industrial or radiological safety significance associated with this event. The nuclear safety significance was minimal because all safety systems responded as designed when the scram signal was received.
3332012008 | FitzPatrick | 11/11/2012 | 01/10/2013 | ML13011A13 | <strong>Automatic Reactor Shutdown Caused by a Fault in Main Transformer</strong><br /><i>Abstract:&nbsp;</i>An unplanned, automatic reactor scram occurred at 0355 on November 11, 2012, caused by a fire in the main transformer 71T-1A. All Reactor Protection Systems operated to shutdown the reactor without any complications. Offsite power transmission lines were Operable and onsite emergency power remained available during this event. At 0545 the emergency plan was entered by declaring a Notification of Unusual Event (HU 6.1). The fire was declared extinguished at 0632 and at 0801 the Notification of Unusual Event was exited. There was no release of radioactivity or personal injury. This event was caused by arcing; possibly originating by either a connection or coil failure internal to the transformer or by internal insulation breakdown or both. 71T-1A was replaced, tested, and returned to service.
3332012009 | FitzPatrick | 11/24/2012 | 06/20/2013 | ML13172A35 | <strong>Containment Atmosphere Dilution (CAD) System Valves Misaligned for Ascension into Mode 2</strong><br /><i>Abstract:&nbsp;</i>At 1135 hours on November 24, 2012 the James A. FitzPatrick Nuclear Power Plant (JAFNPP) entered into Mode 2 from Mode 4. At that time, the penetration flow paths for the Containment Atmosphere Dilution (CAD) System became inoperable. More specifically, the 20 inch diameter Primary Containment Isolation Valves (PCIVs) and 24 inch diameter PCIVs became “inoperable” in accordance with Technical Specifications (T/S) 3.6.1.3 Action B.1 due to the vent and purge of the Torus and Drywell evolution not being secured prior to the mode change which left the valves in their open position thus invalidating the recently performed T/S Surveillance (SR) 3.6.1.3.1. Concurrently T/S 3.6.4.3 one train of the Stand By Gas Treatment (SGT) System and T/S 3.6.1.1 Primary Containment (a suppression function bypass condition was created by the open valves) also became inoperable because of this valve lineup. Therefore, the PCIV’s, Primary Containment, and one train of the Stand-by Gas Treatment System were inoperable when Mode 2 was entered which is a condition prohibited by T/S LCO 3.0.4. At 1838 hours on November 24, 2012, with the Reactor Pressure Vessel (RPV) at approximately 108 psig, the affected flow path penetrations were isolated and restored to operable status by closure of SGT Isolation (ISOL) valve. With the SGT ISOL valve closed T/S SR 3.6.1.3.1 was no longer required to be met. Additionally at the same time, the 20 inch diameter PCIVs and 24 inch diameter PCIVs were also secured closed thus restoring the Stand By Gas Treatment (SGT) System and the pressure suppression function of the Primary Containment to operable.
3332012010 | FitzPatrick | 06/07/2012 | 07/10/2013 | ML13192A08 | <strong>High Pressure Coolant Injection (HPCI) System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2012, while the plant was in LCO 3.5.1 Action C.1, High Pressure Coolant Injection (HPCI) inoperable for planned maintenance, during the performance of Motor Operated Valve (MOV) limitorque and as found/as left viper diagnostic testing (for trending, data gathering, preventive maintenance, and corrective maintenance purposes), HPCI Suppression Pool Pump Suction Isolation MOV Valve (23MOV-57) failed to go completely open (it only opened 38%) after being manually closed. Upon discussions with the NRC Resident Inspector, the potential failure of this component of the High Pressure Coolant Injection (HPCI) system (a single train system) to completely open was subsequently determined to be a condition that would have prevented the fulfillment of the safety function of an SSC that mitigates the consequences of an accident and is therefore being reported under 10 CFR 50.73(a)(2)(v)(D). The level of judgment for reporting an event or condition under this criterion is a reasonable expectation of preventing fulfillment of a safety function. <br><br> The most probable cause was determined to be high contact resistance on open the limit torque switch most likely due to corrosion on the MOV contacts. Corrective actions included verifying the spring tension and cleaning the torque and limit switch contacts. The valve was then tested and determined to be operating properly.
3352012001 | St. Lucie 1 | 02/10/2012 | 04/10/2012 | ML12109A04 | <strong>Unit 1 Inadvertent Start of EDG upon Unexpected Under Voltage Condition</strong><br /><i>Abstract:&nbsp;</i>On February 10, 2012, St. Lucie Unit 1 was in Mode 5 at 0% power. An electrical maintenance worker inadvertently made contact with an unprotected safety-related relay during maintenance in the immediate work area. The physical contact of the relay caused an under voltage condition on an essential bus resulting in the automatic start and loading of the 1B emergency diesel generator (EDG). Prior to the event, the 1B EDG was inoperable but available and not required by Technical Specifications. All equipment responded as expected. The plant remained in Mode 5 with decay heat removal being supplied by the 1A shutdown cooling train without any interruptions. There was no impact on the Shutdown Safety Assessment. Unit 2 was unaffected and remained in Mode 1 at 100% power. A root cause evaluation (RCE) concluded that plant personnel did not fully understand or question the risk significance associated with unprotected relays in the immediate work environment. Corrective actions include procedure revisions and installation of relay covers, extent of condition for safety related relays for Unit 2, review of lessons learned and training.
3352012002 | St. Lucie 1 | 03/18/2012 | 11/26/2012 | ML12341A23 | <strong>Manual Trip During Physics Testing Due to Unexpected Movement of Control Element Assemblies (CEAS)</strong><br /><i>Abstract:&nbsp;</i>On March 18, 2012 at 2336 EDT, while St. Lucie Unit 1 was performing low power testing while in Mode 2 and subcritical at less than 1% power, the reactor was manually tripped due to a control element assembly (CEA) exhibiting unexpected movement. The reactor trip was uncomplicated and all CEAs fully inserted. No automatic safety system actuations were required and none occurred. Reactor coolant system (RCS) heat removal was maintained with auxiliary feedwater and atmospheric dump valves. The Offsite power grid was available and stable. The root cause for the unexpected CEA movement was determined to be inadequate design control of a modification which installed new automatic control timing modules (ACTM) with deficient 10 volt regulators that introduced signal noise that resulted in system malfunction. Corrective actions include strengthening the design control process to require a risk based review for the proper sequencing of post modification testing (PMT) for modifications that are risk significant and design improvements to the voltage regulators on the ACTMs to reduce noise. This event had no effect on the health and safety of the public.
3352012003 | St. Lucie 1 | 03/31/2012 | 09/07/2012 | ML12263A42 | <strong>Manual Trip During Steam Bypass Control System Post-Modification Testing</strong><br /><i>Abstract:&nbsp;</i>On March 31, 2012 at 0022 EDT, St. Lucie Unit 1 was in Mode 1 at 10% reactor power and performing post modification testing (PMT) of the steam bypass control system (SBCS) when the reactor was manually scrammed after a steam bypass control valve opened unexpectedly at 0019 EDT. Immediately following the reactor scram the steam bypass control valve closed, terminating the cooldown. Additionally, Operators closed the main steam isolation valves in accordance with Emergency Operating Procedure (EOP-01), "Standard Post Trip Actions" due to steam generator pressure decreasing to less than 750 psia. All control element assemblies (CEAs) fully inserted. No automatic safety system actuations were required and none occurred. RCS heat removal was maintained with auxiliary feedwater and atmospheric dump valves. The offsite power grid was available and stable. The root cause for failure of the control valve was less than adequate analyses supporting a recently implemented design change and less than adequate post modification testing that failed to provide appropriate contingency actions to mitigate potentially unfavorable SBCS test responses. Corrective actions include isolating the malfunctioning SBCS valve until it can be redesigned and replaced. SBCS capability is provided by the remaining four SBCS valves.
3352012004 | St. Lucie 1, St. Lucie 2 | 08/01/2012 | 08/20/2012 | ML12242A34 | <strong>Seismically Qualified Refueling Water Tank Aligned to Non-seismic Piping</strong><br /><i>Abstract:&nbsp;</i>On August 1, 2012, with Unit 1 operating at 100 percent power and Unit 2 reducing power from approximately 70 percent power to approximately 68 percent power as part of a coastdown for the upcoming refueling outage, it was determined that opening the boundary valve between the safety related and seismically qualified Refueling Water Tank (RWT) and the non-safety related and non-seismically qualified Spent Fuel Purification (SFP) system in Modes 1-4 renders the RWT inoperable. The isolation between the seismic and non-seismic piping is accomplished via a normally locked closed, manually operated, seismically qualified isolation valve (V07104). The piping on the discharge of the fuel pool purification pump is not seismically qualified and could fail during a seismic event. As a result, with V07104 open and aligned for fuel pool purification, this alignment could result in a loss of inventory from the RWT during a seismic event rendering the RWT inoperable. Consistent with NRC Information Notice 2012-01, it has been determined that opening the boundary valve for planned maintenance activities while the plant was operating in Modes 1 through 4 would render the RWT inoperable regardless of the administrative controls that were in place. Since the boundary valve had been opened under administrative controls in Modes 1 through 4 and the one hour completion time of the Action Statement for Technical Specification 3.5.4 was not satisfied, this represents a condition prohibited by Technical Specifications and is reportable pursuant to 10 CFR 50.73 (a) (2) (i) (B). This event had no significant safety consequence since a seismic event had not occurred while the SFP system was aligned to the RWT.
3352012005 | St. Lucie 1 | 06/02/2012 | 11/26/2012 | ML12341A23 | <strong>Unit 1 Reactor Trip on Turbine Trip</strong><br /><i>Abstract:&nbsp;</i>On June 2, 2012 at 1935 with St. Lucie Unit 1 in Mode 1 at 100% power the reactor automatically tripped from normal full power operation due to a loss of load following a failure of the turbine control system (TCS). The reactor trip was uncomplicated and all control rod assemblies (CEAs) fully inserted. No automatic safety system actuations were required and none occurred. The reactor coolant system (RCS) heat removal was maintained with main feedwater (MFW) and steam bypass to the condenser. The Offsite power grid was available and stable.<br /><br /> The reactor trip on turbine trip was caused by loss of communications of the Drop 3 and Drop 53 controllers in the recently installed Ovation turbine control system (TCS). The direct cause for the failure of the primary controller (Drop 53) was an intermittent fault in the Remote Node Controller (RNC) or the Media Attachment Unit (MAU). The back up controller (Drop 3) failed due to a failed fiber optic (FO) cable field connector. The root cause of this event was ineffective design control for the TCS upgrade.<br /><br /> Immediate corrective actions taken included removing all questionable control modules and controllers. Corrective actions to prevent reoccurrence included providing additional guidance to operators in the annunciator response procedure and implementing a new normal operating procedure for the TCS.<br /><br /> This event had no effect on the health and safety of the public.
3352012006 | St. Lucie 1 | 06/05/2012 | 08/02/2012 | ML12220A00 | <strong>Installation Wiring Error in the 1A Auxiliary Feedwater Flow Transmitter</strong><br /><i>Abstract:&nbsp;</i>On June 5, 2012 at 1314 EDT, St. Lucie Unit 1 was in Mode 1 at 100% reactor power and performing monthly flow testing of 1A auxiliary feed pump when the 1A auxiliary feed pump flow transmitter, FT-09-2A, was discovered to be inoperable. Upon troubleshooting, it was discovered that the leads were wired incorrectly on the square root extractor, and the indication was non-functional. The square root extractor had been replaced with a different design on May 9, 2012, and declared operable on May 10, 2012, while the flow transmitter was actually inoperable. This condition unknowingly existed for greater than the allowable Technical Specification action time of 72 hours per Technical Specification 3.3.3.8 and is reportable pursuant to 10 CFR 50.73(a) (2) (i) (B). This event had no significant safety consequence since an auxiliary feedwater actuation had not occurred while the flow transmitter leads were wired incorrectly. The wiring was corrected and tested to return the flow transmitter to operable status on June 5, 2012 at 2100 EDT.
3352012007 | St. Lucie 1 | 04/02/2012 | 08/03/2013 | ML12228A29 | <strong>1A2 EDG Coolant Leakage Rendered EDG Inoperable</strong><br /><i>Abstract:&nbsp;</i>On June 7, 2012 , FPL determined that the April 2, 2012 , failure of the St. Lucie 1A2 emergency diesel generator (EDG) immersion heater pressure boundary was reportable. The most likely failure mode would have rendered the EDG inoperable for longer than its allowed outage time. The failure was attributed to procedural inadequacies during the fill and vent of the EDG following maintenance performed during the SL1-24 refueling outage. A contributing factor included inadequate chemistry procedures.<br /><br /> Immediate corrective actions included replacement of the failed immersion heater, extent of condition electrical checks on all St. Lucie EDG immersion heaters. Other corrective actions included EDG chemistry, maintenance, and startup procedure changes. Additionally, the immersion heaters will be replaced with a design not susceptible to the same failure mechanism.<br /><br /> This event did not have a significant impact on the health and safety of the public.
3352012008 | St. Lucie 1, St. Lucie 2 | 08/23/2012 | 10/22/2012 | ML12310A06 | <strong>Control Room AC Single Failure Vulnerability</strong><br /><i>Abstract:&nbsp;</i>On August 2 3 , 2 0 1 2 , St. Lucie Unit 1 was in Mode 1 at 1 0 0% reactor power and Unit 2 was defueled in refueling outage SL2 -2 0 . During implementation of a design modification to the U2 control room air conditioning system (CRACS) , FPL discovered an original design error ( legacy issue) with both unit's swing CRACS unit control circuitry. The condition would have prevented these units from automatically starting after a loss of offsite power (LOOP) affects the system' s single failure criteria such that the design bases accident General Design Criteria (GDC) 19 control room dose may be affected. This condition Design modifications were developed to eliminate the original design error ( legacy issue) Procedure changes were developed to ensure that if the swing CRACS unit is credited for Operability then it must be in operation. The Design modifications and procedure changes were implemented for the Unit 1 CRACS, will be implemented on Unit 2 during the Unit 2 SL2 - 2 0 refueling outage. and This condition had no significant effect on the health and safety of the public.
3352012010 | St. Lucie 1, St. Lucie 2 | 11/02/2012 | 09/22/2014 | ML14280A43 | <strong>Degraded Manhole Conduit Seals Bypassed External Flood Protection</strong><br /><i>Abstract:&nbsp;</i>On November 1, 2012, St. Lucie Unit 1 was in Mode 1 at 100 percent reactor power when Engineering completed their review of the cumulative effects of the degraded and missing conduit seals in electrical manholes that provided a leakage path into the reactor auxiliary building (RAB). The evaluation concluded that the as-found condition was a reportable event because the postulated storm surge associated with a probable maximum hurricane (PMH) results in RAB flooding greater than the internal flooding analysis of record.<br /><br /> The flooding analyses used in revision 0 of this LER were non-conservative with respect to site water hold up volumes that changed the units' response to flooding. Based on the latest flooding analyses, St. Lucie Unit 2 is also reportable as the resultant RAB flooding is greater than the internal flooding analysis of record.<br /><br /> The reportability of Unit 2 was discovered during flooding design bases reconstitution efforts and was caused by legacy conduit seal installation deficiencies during original construction. Revision 2 adds additional reporting requirements.<br /><br /> All degraded conduit seals were repaired per design requirements.
3362012001 | Millstone 2 | 06/07/2012 | 12/19/2013 | ML14002A26 | <strong>Historical Gaps in High Energy Line Break Barrier</strong><br /><i>Abstract:&nbsp;</i>At 19:30 on June 7, 2012, with Millstone Power Station Unit 2 (MPS2) operating at 100 percent power in Mode 1, it was determined that a series of gaps in a high energy line break (HELB) barrier rendered equipment in the west 480VAC switchgear room inoperable. The Shift Manager entered Technical Specification (TS) 3.8.2.1 Action, TS 3.8.2.1A Action "c" and TS 3.3.3.5 Action "a". The openings were sealed and the equipment restored to operable status at 16:05 on June 8, 2012. At the time of discovery, appropriate and timely actions were taken that met the TS action requirements. There is evidence that this condition has existed since initial construction. Since the HELB barrier required to maintain operability of bus 22E, Inverters 5 and 6, and remote shutdown panel C-21 was non-functional for an extended period of time, the Actions for TS 3.8.2.1, TS 3.8.2.1A and TS 3.3.3.5 were historically not met. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(B) any operation or condition prohibited by the plants technical specifications".<br /><br /> The apparent cause, dating back to original construction, is that no construction details were developed for sealing Q-decking when the ribbing is perpendicular to the top of the wall. As noted above, the gaps were subsequently sealed and an extent of condition inspection was conducted. Additional gaps in the same wall did not affect safety related equipment. No other gaps were identified. This report assumes the steam from a HELB in the turbine building would have affected the operability of safety related equipment in the west 480VAC switchgear room. Upon further engineering analysis, it was determined that for limited exposure times safety functions could have been prevented for certain postulated high energy line breaks. Therefore, this condition is also being reported pursuant to 10 CFR 50.73(a)(2)(v)(A),(D).
3362012002 | Millstone 2 | 08/12/2012 | 10/02/2012 | ML12285A22 | <strong>Completion of Plant Shutdown Required by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>At 13:46 on August 12, 2012, Millstone Power Station Unit 2 (MPS2) completed a controlled plant shutdown from Mode 1 to Mode 3 (Hot Standby) as required by plant Technical Specification (TS) 3.7.11 Ultimate Heat Sink. TS 3.7.11 stipulates the ultimate heat sink shall be operable with a water temperature of less than or equal to 75 degrees F. TS 3.7.11 Action a. allows continued plant operation when ultimate heat sink (UHS) temperature is between 75 degrees F and 77 degrees F, provided UHS temperature averaged over the previous 24 hours is verified to be less than 75 degrees F once per hour. Otherwise, be in Hot Standby within the next 6 hours and in Cold Shutdown within the following 30 hours. The UHS for MPS2 is Long Island Sound. The UHS temperature had initially gone above the temperature limit at 16:30 on August 11, 2012, but had cooled below the limit based on environmental factors. At 00:44 on August 12, 2012 the UHS temperature again rose above the TS limit and operators initiated a plant shutdown as required by plant TS 3.7.11. At 02:55 the Shift Manager directed that power be stabilized at 65% power since UHS temperatures had cooled below the TS limit. Plant power was held at approximately 65% power until 08:35 on August 12, 2012 when temperature again rose above the UHS limit. The Shift Manager directed completion of the plant shutdown from Mode 1 to Mode 3, completed at 13:46 on August 12, 2012. The UHS temperature continued to cycle above and below the TS limit. The plant entered Mode 5 Cold Shutdown at 22:31 on August 13, 2012. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(i)(A) "the completion of any nuclear plant shutdown required by the plant's technical specifications".
3362012003 | Millstone 2 | 10/15/2012 | 12/19/2013 | ML14002A31 | <strong>Potential for a Loss of Safety Function due to Postulated Flood Conditions</strong><br /><i>Abstract:&nbsp;</i>On October 15, 2012 during a Millstone Power Station Unit 2 beyond design basis flooding walkdown, with the unit shutdown in MODE 5 (cold shutdown), a total of 20 four (4) inch and 2 two (2) inch unsealed electrical conduits, connecting the service water pump room of the intake structure and the turbine building, were identified. These conduits penetrated the wall above the design basis flood height of 22 feet mean sea level (MSL), but below the maximum standing wave height of 26.5 feet MSL inside the intake structure service water pump room. Because these conduits were unsealed at both ends, this condition could have resulted in flooding of the turbine building such that it could have rendered the turbine-driven auxiliary feedwater (AFW) pump inoperable. Additionally, several other unsealed conduit penetrations, conduit penetrations with damaged seals, or wall cracks were identified within the design basis flood zone during these walkdowns. Engineering analysis concluded these additional leak paths would have no impact to equipment needed to perform during the design basis flood without the concurrent intake structure standing wave. However, there was a potential to affect the functionality of the AFW pumps, the power operated relief valves and the high pressure injection system if the standing wave condition occurred, as assumed, for a duration of one hour at 26.5 ft. MSL concurrent with the design basis maximum storm surge. Engineering concluded this event was of very low safety significance. These deficiencies were historical in nature and appear to be original construction deficiencies. Upon discovery the identified deficiencies were repaired to restore the design basis for flood protection. This condition is being reported under 10 CFR 50.73(a)(2)(v)(A) and (B). Any event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and maintain it in a safe shutdown condition, or remove decay heat."
3382012001 | North Anna 1 | 03/24/2012 | 05/18/2012 | ML12151A44 | <strong>Degraded Reactor Coolant System Piping due to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>On March 24, 2012, at 1855 hours, with Unit 1 in Mode 6, refueling, two through-wall cracks were identified after machining the Unit 1 'B' Steam Generator (SG) Hot Leg Nozzle. The defects were identified after machining approximately 0.7" to 1.1" of material from the Nozzle-to-Safe End weld in preparation of full structural weld overlays (FSWOL). Work was being performed to support Relief Request N1-14-CMP-001 which permitted the application of FSWOL to mitigate the potential for primary water stress corrosion cracking (PWSCC) susceptibility at North Anna Unit 1. The cracking was determined to be caused by PWSCC and confirmed to be fully contained within the Dissimilar Metal (DM) Alloy 600 weld and butter. Subsequently, the 'B' Steam Generator and associated Reactor Coolant System piping were drained and the throughwall cracks were seal welded under the provisions of Relief Request N1-14-CMP-001. This event is reportable per 10 CFR 50.73(a)(2)(ii)(A) for a condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded. On March 25, 2012, at 0144, a non-emergency 8-hour report was made to the NRC Operations Center, in accordance with 10CFR50.72(b)(3)(ii)(A) for the same condition. The health and safety of the public were not affected by the event.
3392012001 | North Anna 2 | 10/24/2012 | 12/12/2012 | ML12362A01 | <strong>Automatic Reactor Trip Due To Turbine Trip Resulting From A Card Failure</strong><br /><i>Abstract:&nbsp;</i>On October 24, 2012, at 0147 hours with Unit 2 in Mode 1, 100 percent power, an automatic reactor trip occurred due to a low-low level in the "C" steam generator (SG) resulting from closure of all four governor valves. The governor valves' closed due to a spurious error signal from Speed Error Amplifier Card "B" (1A08D). The card malfunction was the result of a failed capacitor. All systems responded as expected. All control rods inserted into the core at the time of the trip and decay heat was removed via the main condenser steam dumps. The auxiliary feedwater (AFW) pumps received an automatic start signal due to low-low level in "C" SG at the time of the trip. The SG levels were restored to normal operating level. At 0240 hours, a 1 hour report was made to the NRC as an After-The-Fact Unusual Event due to a pressurizer relief valve opening momentarily exceeding EAL SU6.1, Reactor Coolant System Leakage. The emergency notification was subsequently retracted. At 0318 hours, a 4 hour report was made in accordance with 10CFR50.72(b)(2)(iv)(B) for Reactor Protection System (RPS) actuation and 8 hour report in accordance with 10CFR50.72(b)(3)(iv)(A) for AFW pump automatic start. This event is reportable per 10 CFR 50.73(a)(2)(iv)(A) for a condition that resulted in automatic actuation of the RPS and AFW System. The health and safety of the public were not affected by the event.
3412012001 | Fermi 2 | 04/11/2012 | 06/08/2012 | ML12163A36 | <strong>Loss of Shutdown Cooling due to a Voltage Transient</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2012, at approximately 1807 EDT, with the plant in Mode 5 during Refueling Outage 15, a common suction shutdown cooling inboard containment isolation valve closed in response to a voltage transient. The 'A' Residual Heat Removal pump tripped as a result of the valve closure. The valve closure resulted in an interruption of shutdown cooling, the primary means of decay heat removal for approximately 11 minutes. During this period, there was no measurable increase in reactor temperature. The Fuel Pool Cooling system was in service at that time and was capable of removing decay heat. The event occurred during a restoration of power to Division 2 Bus 65E from the 64T cross tie breaker when a voltage transient occurred due to a fault on Bus 65E. The fault was the result of an improper safety tagging clearance that left a grounding truck in place during the power restoration. The fault caused a Group 4 isolation of the E1150E009 shutdown cooling common suction valve. Abnormal Operating Procedure 20.205.01, Loss of Shutdown Cooling, was entered, the Group 4 isolation was reset and Shutdown Cooling was restored at 1818 EDT. Related human performance issues were addressed through additional operator just in time training. There were no safety consequences to this event.
3412012002 | Fermi 2 | 04/26/2012 | 06/21/2012 | ML12174A15 | <strong>Reactor Scram During Reactor Pressure Vessel Hydrostatic Test</strong><br /><i>Abstract:&nbsp;</i>On April 26, 2012, at 10:12 am EDT, during Refueling Outage 15 with the Reactor Pressure Vessel Hydrostatic Pressure Test, in progress, a high pressure reactor scram occurred. The control room operator was monitoring reactor pressure using an indication that was invalid due to excess flow check valve testing that was in progress. This resulted in a lowering of indicated reactor pressure while actual pressure was rising. All control rods were already fully inserted in the reactor core at the time of the scram. The Reactor Protection System and other plant equipment responded as expected to the high pressure condition and reactor pressure was lowered to 600 prig. The operating staff identified all control room instruments affected by the excess flow check valve testing, ensured they were monitoring valid signals prior to restarting the hydrostatic test, provided a dedicated operator for monitoring pressure, and communicated reactor pressure conditions to the staff. Long term corrective actions include revisions to procedural requirements and inclusion of the event in operator requalification training as part of refuel outage preparation.
3412012003 | Fermi 2 | 06/25/2012 | 08/24/2012 | ML12240A02 | <strong>Reactor Scram due to Degrading Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On 6/25/2012 after completing repairs to the main unit transformer, reactor power was raised to approximately 22% and the unit was synchronized to the power grid at 1203 EDT. At 1234 EDT Operations began a power increase. At 1322 to 1325 EDT multiple vibration related alarms were received for the south reactor feed pump, and the pump tripped at 1325 EDT. Manual operation of the north reactor feed pump was used initially to recover reactor level. At 1330 hours a manual scram was performed by placing the reactor mode switch in shutdown in response to degrading condenser vacuum. All rods fully inserted and operators used the standby feedwater system to restore water level. Reactor water level reduced to below Level 3 as a result of the scram, and all isolations and actuations associated with that level occurred as expected. The south reactor feed pump turbine was damaged which resulted in main condenser vacuum leaks that were isolated following the event. Decay heat was removed using the main condenser via the turbine bypass valves.
3412012004 | Fermi 2 | 08/27/2012 | 10/19/2012 | ML12296A08 | <strong>Operation or Condition Prohibited by Technical Specification 3.3.3.1</strong><br /><i>Abstract:&nbsp;</i>During an engineering review of Environmental Qualification & Surveillance, it was discovered that the cable connector assemblies connected to position indication limit switches for 3/4 inch valve B3100-F019, Reactor Recirculation Sample Line Inboard Isolation Valve, had exceeded their Environmentally Qualified life. On August 27, 2012 at 11:45 hours position indication for the B3100-F019 was declared inoperable. Position indication of the B3100-F019 is required by TS 3.3.3.1, "Post Accident Monitoring (PAM) Instrumentation." EQ subject matter experts could not assure the limit switch cable connector assemblies could have endured the design basis accident, had it occurred prior to discovery. It was determined that this condition existed for greater than the allowed completion time for TS 3.3.3.1 and was therefore an operation or condition prohibited by the TS. This event posed no significant risk to the health and safety of the public. The apparent cause was a failure to require peer or subject matter expert review for translating EQ requirements into Preventative Maintenance requirements. It is planned to replace the cable connector assemblies during the next refueling outage.
3412012005 | Fermi 2 | 09/14/2012 | 11/05/2012 | ML12311A36 | <strong>Reactor Scram Due to Loss of 120 kV Power</strong><br /><i>Abstract:&nbsp;</i>At approximately 1603 EDT, a fault occurred on the 13.2 kV side of 120 kV Transformer 1. The fault caused the isolation of Bus 101, and a loss of power to Transformer 64, Division I emergency safety system busses 64B and 64C, balance of plant bus 64A, the center condenser pump, center heater feed pump and both north and center heater drains pumps. The loss of the pumps resulted in a trip of the operating north reactor feed pump. Reactor water level lowered as a result of the loss of feedwater, and the unit automatically scrammed on low reactor water level 3 as designed. All control rods fully inserted, and the lowest reactor water level reached was approximately 96 inches above top of active fuel. Division I Emergency Diesel Generators, EDG-11 and EDG-12, automatically started and loaded Division I buses. The High Pressure Coolant Injection and Reactor Core Isolation Cooling systems automatically started as designed on low reactor water level 2 and restored reactor water level which was then maintained using the Condensate/Feed and Control Rod Drive systems. All isolations and actuations occurred as expected. The cause of the trip was determined to be animal intrusion that initiated a phase to ground fault at the Z-phase surge arrestor on the secondary side of Transformer 1. The potentially affected equipment was inspected and tested and the surge arrestor and associated jumpers were replaced prior to restart.
3412012006 | Fermi 2 | 11/07/2012 | 12/21/2012 | ML13002A02 | <strong>Manual Reactor Scram Due to Hydrogen Leakage Into the Stator Water Cooling System</strong><br /><i>Abstract:&nbsp;</i>At 09:21 EST 11/7/12, the reactor mode switch was taken to shutdown and the main turbine generator was manually tripped in response to excessive hydrogen gas leakage into the stator water cooling system from the main turbine generator. Two control rods did not respond as expected; however, both rods exhibited normal scram times up to position 02, and the scram was uncomplicated. The lowest reactor vessel water level reached was 125 inches above top of active fuel which is below reactor water Level 3 and above Level 2. As expected, the High Pressure Coolant Injection and Reactor Core Isolation Cooling did not actuate. Reactor pressure did not increase above normal operating pressure during the transient. No safety relief valves actuated, and all isolations and actuations associated with reactor water Level 3 occurred as expected. Water level was restored during the transient and maintained at 196 inches by the post scram feedwater logic and the North Reactor Feed Pump. Decay heat was removed via steam to the main condenser using the turbine bypass valves. Two control rod drive mechanisms have been replaced for the control rods that did not respond as expected. A leak in the generator stator water cooling system was located and repaired.
3462012001 | Davis-Besse | 05/19/2012 | 07/23/2012 | ML12208A11 | <strong>Direct Current Source for Diesel Generator Transferred to Inoperable Source During Fuel Movement</strong><br /><i>Abstract:&nbsp;</i>On May 19, 2012, with the Davis-Besse Nuclear Power Station in Mode 6 and movement of irradiated fuel in progress, the Direct Current (DC) power source providing the loss of power start function for the one required Emergency Diesel Generator (EDG) was transferred from its alternate to normal source. While the normal source was functional and available, required surveillance testing had not shown the DC power source to be operable following replacement of a battery cell and completion of a performance discharge test. This deficiency was identified during preparations for reloading fuel into the reactor core on May 22, 2012. The cause of this event was determined to be less than adequate administrative controls for maintaining the DC System power source operability with the system cross-tied during shutdown conditions. Subsequent testing showed the equipment was operable, and procedures will be revised to add a prerequisite for ensuring operability of the motor control center being transferred to, or to ensure both EDGs are operable. This event is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B) as operation of the plant in a condition prohibited by the Technical Specifications and 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented fulfillment of a safety function for a system needed to mitigate the consequences of an accident.
3462012002 | Davis-Besse | 06/06/2012 | 08/06/2012 | ML12220A35 | <strong>Leak from Reactor Coolant Pump Seal Piping Socket Weld due to High Cycle Fatigue</strong><br /><i>Abstract:&nbsp;</i>On June 6, 2012, with the Davis-Besse Nuclear Power Station in Mode 3 and the Reactor Coolant System at normal operating temperature and pressure, a scheduled walkdown identified a leak from Reactor Coolant Pump (RCP) 1-2 first stage seal vent cavity line. The 0.1 gallon per minute leak was from a socket weld of the small bore ASME Section III Class 2 piping between the RCP seal and the first isolation valve. The station cooled down to Mode 5 and repaired the leaking socket weld. The most probable cause of this leak was determined to be high cycle fatigue of the seal cavity vent line at the elbow socket weld in combination with a discontinuity in the socket weld root. The high cycle fatigue was due to a less than adequate design modification to minimize vibration of the line. Planned corrective actions include replacement of this and similar seal piping for all four RCPs with flexible hoses, and review of other socket welded piping for similar potential failure modes. This event is being reported pursuant to 10 CFR 50.73(a)(2)(ii)(A) as degradation of a principal safety barrier based on existing NRC precedence.
3482012001 | Farley 1, Farley 2 | 02/15/2012 | 04/09/2012 | ML12101A28 | <strong>Seismically Qualified RWST Aligned to Non-Seismic Piping</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2012, with both Units 1 and 2 operating 100 percent power, it was determined that opening the boundary valve between the safety related and seismically qualified Refueling Water Storage Tank (RWST) and the non-safety related and non-seismically qualified Spent Fuel Pool Purification (SFPP) system in Modes 1-4, renders the RWST inoperable. Plant procedures had been revised in 2009 to allow opening this boundary valve in Modes 1-4 under administrative controls. The 10 CFR 50.59 safety evaluation that had been performed to support the procedure change had concluded that the administrative controls would allow the RWST to remain operable. However, in consideration of the new interpretation provided in NRC Information Notice 2012-01, it was judged that the RWST would be considered to be inoperable regardless of the administrative controls established when the RWST was aligned to non-seismic piping in Modes 1 - 4. Since the boundary valve had been opened in Mode 1 under administrative controls and the one hour completion time of Technical Specification 3.5.4 Condition B was not entered, under this recent interpretation, this represented a condition prohibited by Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). This event had no significant safety consequence since a seismic event had not occurred while the SFPP system was in service on the RWST.
3482012002 | Farley 1 | 02/15/2012 | 04/09/2012 | ML12101A27 | <strong>Breaker Failure Results in Containment Cooling Train Inoperability</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2012 at 0212, with Unit 1 operating at 100 percent power, 1B containment cooling fan (A Train) failed to start in slow speed during surveillance testing. Subsequent troubleshooting revealed that the failure of the fan to start was due to a malfunction of the 600 volt breaker that provides power to the fan motor slow speed winding. Based upon the investigation performed, it was determined the breaker had been rendered incapable of closing since January 18, 2012. This was the last time the breaker had been closed and the containment cooling fan had operated in slow speed satisfactorily. Although the 1B containment cooling fan was inoperable, the A Train of containment cooling was operable until the 1B containment cooling fan was selected for automatic start on January 23, 2012. Therefore, the A Train was inoperable for approximately 23 days until the failure was discovered on February 15, 2012. Since the seven day completion time of Technical Specification 3.6.6 Condition C was exceeded, this represents a condition prohibited by Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). The A Train operability was restored in approximately eight minutes when the 1A containment cooling fan was selected to automatically start on February 15, 2012 at 02:20. Investigation into the breaker failure determined that the cause was due to a failed charging motor cut-out switch.
3482012003 | Farley 1 | 04/05/2012 | 05/31/2012 | ML12152A37 | <strong>Unplanned A Train LOSP During SI with LOSP Testing</strong><br /><i>Abstract:&nbsp;</i>On April 5, 2012 at approximately 12:24, with Unit 1 in mode 6, an unplanned loss of power on A-train 4160 volt emergency bus 1F occurred during a scheduled outage test, Safety Injection (SI) with Loss of Off-Site Power (LOSP). Prior to the event, the 1-2A Emergency Diesel Generator (EDG) was solely aligned to the 1F bus and successfully carrying all the loads per the test sequence. During subsequent restoration steps the 1-2A EDG should have been paralleled to the grid, however, a human performance error was made and this procedure step was not correctly performed. When the BlF Sequencer Test Trip Override Switch (TTOS) was selected to the 'On' position, the EDG output breaker (DF08-1) opened to generate an LOSP signal on the 1F bus. As a result, the B1F Sequencer functioned to automatically re-close DF08-1, and automatically start all LOSP loads. All systems functioned as designed for this condition. Since core cooling was aligned to the A-train prior to the event, the A-train 1A Residual Heat Removal (RHR) pump was deenergized when the LOSP occurred. This pump is not an LOSP load and therefore did not automatically restart. The 1A RHR pump was manually restarted one minute after the LOSP to reestablish core cooling after an increase in reactor coolant system (RCS) temperature of approximately four degrees. Unit 2 was unaffected and remained at 100 percent power during the event. Once the error was recognized, the surveillance test procedure was properly executed to restore off-site power and shutdown the 1-2A EDG without further complications.
3482012004 | Farley 1 | 04/06/2012 | 05/31/2012 | ML12152A37 | <strong>Unplanned B Train LOSP During Switchyard Breaker Testing</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2012 at approximately 14:44, with Unit 1 in mode 6, an unplanned loss of power on B-train 4160 volt emergency bus 1G occurred during scheduled high voltage switchyard breaker testing activities. The 1G bus was powered from the 1B startup transformer (SUT) that lost power when power circuit breaker (PCB) 820 unexpectedly opened. A second PCB, 924, to the 1B SUT was out of service for breaker testing. During that fault circuitry testing, an unanticipated trip of the adjacent PCB 820 occurred due to an inadequate test procedure. When power was lost to the 1B SUT an undervoltage condition was sensed on the 1G bus and the B1G Sequencer caused the DG-15 feeder breaker to open and initiated a load shed on the 1G bus. Due to B-train outage conditions, the 1B Emergency Diesel Generator (EDG) was tagged out and did not automatically start and therefore no Loss of Offsite Power (LOSP) loads started. All systems functioned as designed for this condition. Since core cooling was aligned to the A-train prior to the event, the A-train, 1A Residual Heat Removal (RHR) pump remained in service for shutdown cooling. Unit 2 was unaffected and remained at 100 percent power during the event. The 1G bus was restored to service on April 6, 2012 at 15:42. Investigation revealed that the test procedure did not contain a step to isolate one of the fault protection relay schemes for PCB 820. The test procedure was corrected and the test was successfully completed on April 7, 2012.
3482012005 | Farley 1 | 07/26/2012 | 09/24/2012 | ML12269A16 | <strong>Unit Shutdown Required by Technical Specification 3.8.1</strong><br /><i>Abstract:&nbsp;</i>On July 26, 2012, at 2151 hours CDT with Unit 1 operating in Mode 1 at approximately 100 percent rated thermal power, a reactor shutdown was conducted in accordance with Condition H of Limiting Condition for Operation (LCO) 3.8.1 following expiration of the Completion Time allowed for compliance with Condition B.4 of that LCO. The Unit was stabilized in Mode 5 pending necessary repairs to EDG 1B and its return to operability. Previously, on July 16, 2012, LCO 3.8.1 was voluntarily entered and EDG 1B was removed from service for planned 24-month maintenance. Following completion of the maintenance on July 20, 2012, during the post-maintenance operation evaluation run, oscillations occurred in certain EDG parameters including power output. Subsequently, within minutes, EDG 1B unexpectedly shutdown. The initial investigation included an examination of all cylinders which led to the discovery of a damaged piston and cylinder liner on the #12 cylinder. Subsequent investigation determined the immediate cause of the EDG 1B shutdown was a high crankcase pressure trip; the underlying cause of the engine shutdown was the malfunction of the engine's intercooler thermostatic bypass valve (Q1R43V0561) due to the failure of one of three thermal actuating devices. There were no adverse effects on plant safety or on the health and safety of the public as a result of this event.
3522012001 | Limerick 1 | 02/20/2012 | 04/19/2012 | ML12111A01 | <strong>Three Main Steam Isolation Valves Failed Hot Closing Stroke Time Surveillance Test</strong><br /><i>Abstract:&nbsp;</i>Three of eight main steam isolation valves (MSIVs) exceeded the 5 second maximum closing time requirement during the Unit 1 MSIV cold shutdown valve test. The apparent cause of the test failure was that valve stroke times were not always optimized following prior test failures. A contributing cause was the inherent inaccuracies in valve stroke timing practices. An additional contributing cause is the HV-041-1F028B MSIV pneumatic manifold is causing an extended delay time prior to valve motion. The cold shutdown valve test was performed successfully prior to restart. The test will be revised to require valve stoke time adjustment if the as-found stroke time exceeds pre-established test limits. The HV-041-1F028B MSIV manifold has been scheduled for replacement in the next Unit 1 refueling outage (1R15) in spring 2014. MSIV stroke timing method improvements for timing accuracy will be investigated, benchmarked and incorporated as necessary.
3522012002 | Limerick 1 | 04/19/2012 | 09/18/2012 | ML12262A46 | <strong>Valid Manual Actuation of the Reactor Protection System due to Reactor Recirculation Pumps Tripping</strong><br /><i>Abstract:&nbsp;</i>A transformer failure and subsequent low voltage condition resulted in a loss of the main generator stator cooling water system. The loss of stator cooling water resulted in an automatic trip of both reactor recirculation pumps which required a valid manual actuation of the reactor protection system. The transformer failure was caused by partial current discharge (corona effect). The partial current discharge was caused by a manufacturing defect resulting in improper insulation of the High Voltage line rod where it passes through the polyester support board. The faulted transformer was replaced.
3522012003 | Limerick 1 | 05/02/2013 | 05/21/2013 | ML13142A44 | <strong>Valid Manual Actuation of the Primary Containment Isolation System due to Ventilation System Trip</strong><br /><i>Abstract:&nbsp;</i>A valid manual actuation of the primary containment isolation system was initiated in response to a low delta pressure condition in the reactor enclosure secondary containment. The manual actuation affected primary containment isolation valves in more than one system. The cause of the event was a trip of the reactor enclosure ventilation system. Operators initiated a "B" manual secondary containment isolation as directed by the low delta pressure alarm procedure. The cause of the ventilation system trip was due to degraded performance of the reactor enclosure equipment compartment exhaust (REECE) flow transmitter. The degraded REECE flow transmitter was replaced and the system was tested successfully. The reactor enclosure ventilation system was restored to service and continues to operate normally.
3522012004 | Limerick 1 | 07/11/2012 | 09/10/2012 | ML12255A02 | <strong>Common-cause Inoperability of Independent Channels due to Pipe Leak</strong><br /><i>Abstract:&nbsp;</i>An instrument pipe used to sense main turbine first stage pressure developed a leak that caused inoperability of two instruments in the reactor protection system. The Reactor Protection System Instrumentation Technical Specification one-hour action to place the affected trip systems in the tripped condition was not met. The instruments' reactor protection system function is to bypass the turbine stop valve closure and turbine control valve fast closure trip functions when turbine first stage pressure is equivalent to a thermal power of less than 29.5 percent. The instrument also bypasses the turbine stop valve closure and turbine control valve fast closure trip functions in the end-of-cycle recirculation pump trip logic. The cause of the event was vibration induced fatigue of the affected instrument pipe. The failed instrument pipe was repaired. The "turbine control valve/stop valve scram bypassed" alarm response procedure was revised to direct a power reduction if trip unit status can not be determined within 15 minutes. A modification will be installed to address vibration induced fatigue on the affected instrument piping.
3522012005 | Limerick 1 | 07/18/2012 | 09/17/2012 | ML12261A37 | <strong>Valid Actuation of the Reactor Protection System with the Reactor Critical and Unusual Event Declared</strong><br /><i>Abstract:&nbsp;</i>A valid manual actuation of the reactor protection system was initiated due to an automatic trip of both reactor recirculation pumps. The reactor recirculation pumps tripped due to a loss of stator cooling water following a failure of a connection in a 13 kV/480 VAC non-safeguard load center air termination cabinet. An Unusual Event was declared due to flash-over damage on the failed transformer air termination cabinet which was classified as an explosion within the protected area boundary. The cause of the failed transformer was a high voltage connection clamp that was larger than the 13 kV cable size and the cable was not installed properly. The cable in use was a solid conductor and the clamp used was designed for stranded cable. This resulted in overheating and subsequent failure of the connection which damaged the cable and the load center transformer. The investigation determined that this connection is not disturbed during routine maintenance. Therefore, this is believed to be a manufacturing issue. The 124A load center transformer supply cable was upgraded to a stranded cable with a crimped lug connection. The faulted 124A load center transformer was replaced and returned to service. Similar load center transformers will be upgraded to stranded cable with crimped lug connections.
3522012006 | Limerick 1 | 07/19/2012 | 09/17/2012 | ML12261A41 | <strong>Valid Manual Actuation of the Reactor Protection System due to a Personnel Error and Surveillance Test Weakness</strong><br /><i>Abstract:&nbsp;</i>A valid manual actuation of the reactor protection system was initiated during an outage with all control rods inserted. The reactor mode switch was repositioned from "Shutdown" to "Refuel" during preparation to perform control rod exercising. The mode switch was returned to "Shutdown" when it was identified that the required nuclear instrumentation surveillance tests were not in surveillance. The cause of the event was a personnel error caused by a test weakness. The "Pre-control Rod Withdrawal Check and CRD Exercise OPCONs 3,4 With No Core Alterations" surveillance test does not have verification steps to ensure that the Surveillance Test Coordinator (STC) input is accurate. The "Pre-control Rod Withdrawal Check and CRD Exercise OPCONs 3,4 With No Core Alterations" surveillance test Attachment 2 will be revised to add an additional Work Management signoff for a peer check of the STC input. The notes and body of Attachment 2 will be revised to improve human factoring.
3522012007 | Limerick 1, Limerick 2 | 08/20/2012 | 10/19/2012 | ML12293A10 | <strong>Condition Prohibited by Technical Specifications due to Inoperable Primary Containment Isolation Valves</strong><br /><i>Abstract:&nbsp;</i>Multiple primary containment isolation valves (PCIVs) were declared inoperable following identification of a closing circuit design deficiency. Overall, 15 Unit 1 PCIVs and 15 Unit 2 PCIVs were affected. The deficiency resulted in a potential failure of affected PCIVs to fully close during a loss of coolant accident (LOCA) with offsite power available. The original design for certain PCIVs contained a design flaw that could potentially prevent the equipment from performing the intended safety function. Following the identification of the design deficiency a design change was implemented on 24 affected PCIVs (12 per unit). The design change installed a jumper which removed the LS-8 contact feature. Three Unit 1 affected Containment Atmospheric Control (CAC) system drywell purge PCIVs' stroke times were reduced to remove the vulnerability. Three inoperable Unit 2 affected CAC drywell purge PCIVs' stroke times will be reduced to remove the vulnerability.
3522012008 | Limerick 1 | 09/13/2012 | 11/12/2012 | ML12318A12 | <strong>Condition Prohibited by Technical Specifications due to Inoperable Isolation Instrumentation</strong><br /><i>Abstract:&nbsp;</i>During planned surveillance testing three of four isolation instrumentation channel response times exceeded the Technical Specification (TS) maximum limit of less than or equal to 0.5 seconds for main steam line (MSL) high flow. The response time test failures were caused by a failure to proceduralize the method of replacement relay selection to ensure the fastest contact release times. This caused the overall as-left logic response time to lose margin to the TS limit. The affected relays in the 1A, 1C and 1D MSL flow channels were replaced. The relay testing and/or replacement procedure will be revised to include a step-by-step method of selecting relays with the shortest contact release times upon de-energization of the relay. A new stock code will be created for new relays that have been response time tested and found to be acceptable for this application.
3522012009 | Limerick 1, Limerick 2 | 10/03/2012 | 12/03/2012 | ML12339A00 | <strong>Unanalyzed Condition Due to a Fire Safe Shutdown Analysis Error</strong><br /><i>Abstract:&nbsp;</i>An unprotected control cable was identified during a detailed logic and cable routing review for the Multiple Spurious Operations (MSO) 5f scenario. The review identified that a D22 Emergency Diesel Generator (EDG) output breaker control cable could fail due to postulated fire damage in fire area 067W. The event was caused by an error during the Fire Safe Shutdown (FSSD) analysis. The D22 EDG output breaker control logic was rewired to eliminate the deficiency.
3532012001 | Limerick 2 | 05/10/2012 | 07/09/2012 | ML12338A02 | <strong>Condition Prohibited by Technical Specifications Due to Redundant Reactivity Control System Setpoint Drift</strong><br /><i>Abstract:&nbsp;</i>The Unit 2 Division 2 redundant reactivity control system was determined to be inoperable due to instrument signal drift on a reactor pressure vessel pressure channel. An investigation determined that the channel was inoperable for a time longer than permitted by the Technical Specifications. The apparent cause of the unplanned inoperability of the affected channel was a premature failure of the reactor pressure analog trip module (ATM) card. The ATM card failure was most likely due to a failure of the U1-amplifier sub-component on the card. The degraded card was replaced, calibrated and tested successfully. The Daily Surveillance Log/OPCONS 1,2,3 RRCS channel check has been revised to ensure unacceptable RRCS channel signal drift will be identified and evaluated as required.
3542012001 | Hope Creek | 03/06/2012 | 05/04/2012 | ML12138A13 | <strong>Average Power Range Monitor Flow Unit Summers Out of Tech Spec Tolerance</strong><br /><i>Abstract:&nbsp;</i>On 3/1/2012, the "B" Reactor Recirculation pump tripped causing entry into single loop operation (SLO). During SLO the Average Power Range Monitor (APRM) Flow Unit Summers were adjusted via a weekly channel calibration. After restoring the "B" pump to service and power ascension, several alarms were received indicating that the 'D' APRM Flow Unit was UPSCALE. Investigation discovered that all four APRM Flow Units were out of tolerance. All of the APRMs were declared INOPERABLE and (TS) 3.3.1 (action b) was entered for the number of OPERABLE channels being less than the required minimum OPERABLE channels for both trip systems. The channel calibration (HC.IC-CC.SE-0032) was completed satisfactorily and the APRM Flow Units were declared OPERABLE. The cause of the event was inadequate procedural guidance or instructions. Corrective actions include revision of the appropriate procedures and development of a schedule template (including required surveillances) for entry into and return from SLO. This condition is reportable under 10 CFR 50.36(c)(1)(ii)(A) for exceeding the allowable value for a Limiting Safety System Setpoint, 50.73(a)(2)(i)(B) for a condition prohibited by TS, and 50.73(a)(2)(vii) for a common-cause inoperability of independent trains or channels. No similar events were identified.
3542012002 | Hope Creek | 03/14/2012 | 05/14/2012 | ML12144A09 | <strong>High Pressure Coolant Injection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>On March 14, 2012, the High Pressure Coolant Injection (HPCI) system was declared INOPERABLE when the turbine governor control valve failed to respond as operators expected during a planned maintenance evolution. The system was aligned for obtaining an oil sample and the reactor operator (RO) started the auxiliary oil pump (AOP). The control valve moved to mid position, but did not immediately return to the closed position as expected. When the AOP was secured, the control valve went fully closed. The cause of the event was an unexpected response of the HPCI turbine governor control valve. As part of the troubleshooting the EGR was replaced and sent to the manufacturer for failure analysis. This LER is being submitted because the as found condition of the EGR will not be confirmed until the manufacturer's failure analysis is complete and reviewed. This condition is reportable under 10 CFR 50.73(a)(2)(v)(D) for a condition that would have prevented fulfillment of a safety function.
3542012003 | Hope Creek | 04/22/2012 | 05/14/2012 | ML12151A40 | <strong>Operation with the Potential to Drain the Reactor Vessel</strong><br /><i>Abstract:&nbsp;</i>On April 22, 2012, at 5:30 pm, Hope Creek commenced Operations with the Potential to Drain the Reactor Vessel (OPDRV) for the replacement of Local Power Range Monitor (LPRM) strings without setting secondary containment. This activity is a condition prohibited by Technical Specifications (TS) as defined by 10 CFR 50.73(a)(2)(i)(B). Secondary containment is required by TS 3/4.6.5.1 in Operational Condition *, which is a condition during operations with the potential to drain the reactor vessel. The Required Action for this specification is to suspend OPDRV operations. The NRC issued Enforcement Guidance Memorandum (EGM) 11-003 on October 4, 2011, to provide guidance on how to disposition boiling water reactor (BWR) licensee noncompliance with TS containment requirements during OPDRV operations. To be eligible for enforcement discretion, Hope Creek was in compliance with the minimum criteria established in the EGM during the replacement of the LPRM strings. This condition is reportable under 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by TS. No similar events were identified.
3542012004 | Hope Creek | 05/10/2012 | 12/10/2012 | ML13004A09 | <strong>As-found Values for Safety Relief Valve Lift Setpoints Exceed Technical Specification Allowable</strong><br /><i>Abstract:&nbsp;</i>On May 10, 2012, PSEG received the initial results for the safety relief valve (SRV) pilot valve 'as-found' setpoint testing. The results indicated that two SRV pilot valve setpoints exceeded Technical Specification (TS) allowable tolerance specified in TS 3.4.2.1. This specification requires SRV setpoint limits to be within +/- 3% of the specified value. The valves failing to meet limits were Target Rock Model 7567F two-stage SRVs. As planned all 14 SRV pilot valves were removed and replaced with pre-tested, certified spare pilot valves during refueling outage H1R17. All 14 SRV pilot valves were 'as-found' tested at an offsite test facility. A total of six of the 14 SRV pilot valves experienced setpoint drift outside of the TS 3.4.2.1 limits. Five of the six SRVs were within the maximum allowable percent increase (MAPI) value. The SRV-F was the only SRV that did not meet the MAPI value. A Technical Evaluation assessed whether the stresses imposed by the increased lift setpoint would have been below the ASME Section III, Appendix F value for failure. The results of the Technical Evaluation are being communicated in this supplemental LER. The cause of the setpoint drift for all six SRVs is corrosion bonding, which is consistent with industry experience. The materials combination for the pilot disc and the pilot seat has been a known industry issue because of the design of the Target Rock 2 stage SRV. This condition is reportable under 10CFR50.73(a)(2)(i)(B) as any operation or condition prohibited by the plant Technical Specifications.
3542012005 | Hope Creek | 07/15/2012 | 08/23/2012 | ML12263A42 | <strong>RCIC Bearing Low Oil Pressure Indication on Remote Shutdown Panel Inoperable</strong><br /><i>Abstract:&nbsp;</i>On July 15, 2012, the performance of monthly surveillance HC.OP-ST.SV-0001, "Remote Shutdown Monitoring Instrumentation Channel Check - Monthly," identified that the remote indication for the Reactor Core Isolation Cooling (RCIC) Bearing Oil Low Pressure Alarm was INOPERABLE. The Shift Manager entered the action statement for Technical Specification (TS) 3.3.7.4. Preliminary investigation showed that normally energized relay E51-K58 had malfunctioned. The relay was replaced and OPERABILITY restored on July 16, 2012. During the investigation into the cause of the failed indication, the Work Control Senior Reactor Operator reviewed the surveillance performed in June 2012 and found that the alarm was extinguished and incorrectly documented in the test as satisfactory. The Control Room Supervisor (CRS) who reviewed and approved the June surveillance also missed the error and subsequently signed off the completed test as satisfactory. Therefore, the RCIC Bearing Oil Low Pressure Alarm Indication on the Remote Shutdown Panel had been INOPERABLE since June 16, 2012. The cause of the event was inattention to detail by the Operator performing the surveillance in June and inattention by the CRS reviewing the surveillance. Both operators were delimited and remedial training was completed prior to resuming licensed operator duties. This condition is reportable under 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by Tech Specs.
3542012006 | Hope Creek | 09/04/2012 | 11/03/2012 | ML12319A41 | <strong>High Pressure Coolant Injection System Inoperable</strong><br /><i>Abstract:&nbsp;</i>At 1:20 p.m., on September 4, 2012, the high pressure coolant injection (HPCI) system was being run to perform the quarterly in service test (1ST) - HC.OP-IS.BJ-0001 "HPCI Main And Booster Pump Set - 0P204 and 0P217 - In Service Test." The operator started in parallel the HPCI Auxiliary Oil Pump and opened the HPCI steam admission valve 1FD-HV-F001; however, the HPCI steam admission valve did not stroke open as indicated by observation of control room position indication, zero turbine speed indicated on the HPCI speed controller, and local position. The HPCI IST was aborted and the Shift Manager declared the HPCI system INOPERABLE. Troubleshooting performed on the valve identified that there was no continuity through a normally closed contact on the motor-operator (Limitorque) LS-11 limit switch. The contacts were cleaned and continuity was subsequently checked satisfactorily. The cause of the failure of 1FD-HV-F001 to open was dirty contacts on the motor operator LS-11 limit switch that prevented continuity through the contactors. The contacts were cleaned and continuity restored. The HPCI F001 valve was retested satisfactory. This condition is reportable under 10 CFR 50.73(a)(2)(v)(D) for a condition that would have prevented fulfillment of a safety function.
3612012001 | San Onofre 2, San Onofre 3 | 02/09/2012 | 04/03/2012 | ML12096A29 | <strong>AFW Pump Inoperable due to Postulated Flooding Event Results in Condition Prohibited by TS</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2012, an engineering evaluation determined that during a postulated Probable Maximum Precipitation (PMP) event, the Turbine Driven Auxiliary Feedwater Pump (TDAFWP) turbine could potentially trip on overspeed due to excessive condensation in the steam supply line, rendering the TDAFWP inoperable. The portion of the TDAFWP turbine steam supply piping located in an external trench is susceptible to flooding during a PMP event. Excessive steam line condensation was possible due to the as-found incorrect piping insulation. As a result, water slugging and turbine overspeed could occur if the TDAFWP is started by an Emergency Feedwater Actuation Signal. Technical Specification (TS) Limiting Condition for Operation 3.7.5 requires all three AFW trains to be operable in Modes 1, 2, and 3, and Mode 4 when the Steam Generator is relied upon for heat removal. TS 3.7.5 Condition B for one AFW train inoperable requires restoration of the AFW train to Operable status within 72 hours. The identified condition existed on both Units 2 and 3 since 1993; therefore, one AFW train was inoperable for longer than allowed by TS. Based on the risk assessment and AFW system redundancy, the safety significance of this event is considered minimal.
3612012002 | San Onofre 2, San Onofre 3 | 03/17/2012 | 09/24/2012 | ML12269A16 | <strong>Emergency Diesel Generator Vibration Trip Not Bypassed For Non-Accident Condition</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2012, the analysis for the SONGS Emergency Diesel Generators (EDGs) high vibration trip was completed, concluding the EDGs would have remained operable as designed during seismic events. LER 2012-02-00 conservatively reported the potential for spurious actuation of the high vibration trip under 10 CFR 50.73(a)(2)(ii)(B), “Any event or condition that resulted in the nuclear power plant being in an unanalyzed condition that significantly degraded plant safety.” This supplemental report documents the previously unanalyzed condition did not degrade plant safety and changes the reporting criteria to voluntary. The high vibration trip was part of the 1981 EDG installation, and was bypassed during EDG operation for accident mitigation. The original design documentation did not demonstrate the EDGs would respond to a loss of offsite power as described in the Technical Specifications (TS) and the Updated Final Safety Analysis Report (UFSAR) under conditions that did not bypass the high vibration trip. Following submittal of the initial event report, an independent expert developed analytical models based on manufacturer's data, direct measurements, circuit analysis, and shake table testing to further evaluate the response of the circuit. The results confirmed a Design Basis Event would not have caused a spurious high vibration trip of the EDGs.
3622012001 | San Onofre 3 | 01/31/2012 | 03/29/2012 | ML12090A15 | <strong>Unit 3 Manual Reactor Trip due to Steam Generator Tube Leak</strong><br /><i>Abstract:&nbsp;</i>On 01/31/2012 at 1505 PST, SONGS Unit 3 was in Mode 1 operating at 100 percent power, when a high radiation alarm from the condenser air ejector monitor indicated a tube leak in one of the two steam generators (SGs). A rapid power reduction was commenced in accordance with plant procedures when the primary to secondary leak rate was determined to be greater than 75 gallons per day (gpd) with an increasing rate of leakage exceeding 30 gpd per hour. At 1731 PST, the operators manually tripped the reactor at 35 percent power as directed by procedure, resulting in actuation of the Reactor Protection System which is reportable. All control rods inserted to shutdown the reactor. Safety systems responded as designed. SG level was maintained using the main feedwater system. Decay heat was removed through the main steam bypass valves to the condenser; no atmospheric relief valves lifted during the trip. The affected SG was isolated. The reactor was placed in a stable cold shutdown condition in Mode 5. Small, monitored radioactive releases to the environment occurred, well below allowable limits. Inspection, testing, and analysis of SG tube integrity in both Unit 3 SGs is ongoing. Defective tubes will be removed from service prior to plant startup. Any subsequent required reporting associated with tube degradation will be addressed in a separate report.
3622012002 | San Onofre 3 | 03/14/2012 | 05/14/2012 | ML12136A06 | <strong>Unit 3 Steam Generator Tube Degradation Indicated by Failed In-Situ Pressure Testing</strong><br /><i>Abstract:&nbsp;</i>On 03/14/2012 at 1120 PDT, SONGS Unit 3 was in Mode 5 (cold shutdown), when the first of eight Steam Generator (SG) tubes failed in-situ pressure testing. A SG tube is considered degraded and is reportable if it does not meet the tube integrity performance criteria stated in the SG Program (Technical Specification 5.5.2.11), as indicated by a failed in-situ test. In addition, the degraded condition was considered a safety system functional failure; i.e., potential failure to isolate radioactive fission products in the primary coolant from the secondary system as part of the reactor coolant pressure boundary. The first tube that failed was the tube with a through-wall leak that resulted in the Unit 3 shutdown from full power on 01/31/2012. Following the shutdown, extensive inspection, testing, and analysis of SG tube integrity in both Unit 3 SGs commenced, with a total of eight tubes failing in-situ testing in SG 3E088 as follows: on 03/14/12, three tubes did not meet the accident induced leakage performance criteria (exceeded 0.5 gpm at maximum pressure achieved during test); and on 03/15/12 and 03/16/12, a total of five tubes did not meet the structural integrity performance criteria (failed three-times normal pressure conditions). The postulated post-accident onsite and offsite doses were well below allowable limits. At the time of this event, Unit 2 was in a refueling outage. Planned inspection of 100 percent of the Unit 2 SG tubes was performed, with one tube requiring in-situ testing. This tube met the performance criteria.
3642012001 | Farley 2 | 09/12/2012 | 08/14/2013 | ML13227A03 | <strong>TDAFW Pump Orifice Plate Thickness Results in Condition Prohibited by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On September 12, 2012, while Unit 2 was in Mode 1 at approximately 100% power, an external inspection of the Unit 2 Turbine Driven Auxiliary Feedwater (TDAFW) Pump flow orifice plates [OR] identified the thickness to be 1/8 inch versus 1/2 inch as specified in design drawings. An evaluation of this condition was unable to provide assurance of orifice plate geometry and integrity under design maximum flow conditions. As a result, the Unit 2 TDAFW Pump [P] was declared INOPERABLE and Technical Specification 3.7.5 condition B was entered. Temporary Modification SNC429958 was subsequently implemented to limit the maximum pressure drop across the orifice plates to an acceptable level by restricting the open movement of the TDAFW flow control valves. This allowed the restoration of the TDAFW Pump to OPERABLE status within the time limit of Technical Specification 3.7.5 condition B. A review of maintenance history has determined that prior to initial plant operation, design changes were issued in 1977 and 1978 to replace originally installed 1/8 inch orifice plates with 1/2 inch orifice plates. For unknown reasons these design changes for orifice plate replacement were not implemented. Since the 1/8 inch orifice plates have been in place for the life of the plant, this represents a condition prohibited by Technical Specifications and is reportable under 10CFR50.73(a)(2)(i)(B). This condition is additionally reportable under 10CFR50.73(a)(2)(ii)(B) and 10CFR50.73(a)(2)(v)(D).
3662012001 | Hatch 2 | 11/15/2012 | 01/31/2013 | ML13038A60 | <strong>"2B" Standby Gas Treatment Filter Train Found Operating at Higher Flow than Allowed by Technical Specification</strong><br /><i>Abstract:&nbsp;</i>On December 10, 2012, at 14:31 EST, with Unit 2 operating near 100 percent rated thermal power (RTP), HNP Engineering reported that removal of the Unit 2 refueling floor Hatch resulted in a flow increase of approximately 60 cfm for the Unit 2 'B' Standby Gas Treatment (SGT) filter train. The 2B SGT train had recently been operating near its upper limit of 4000 cfm due to slight incremental increases in flow rate induced by normal wear and tear of door seals and other mechanical seals in the reactor building. The combination of operating so close to its upper flow limit and the increase in flow due to the removal of the refueling floor hatch caused the 2B SGT train to exceed its upper flow limit by approximately 30-50 cfm during the performance of the secondary containment test on November 15, 2012. Records were reviewed and it was determined that the refueling floor hatch had been removed November 6, 2012. Engineering determined that the 2B SGT train would have exceeded its technical specifications flow rate during any surveillance performed since that time. The 2B SGT train was thoroughly checked and adjusted back within its flow rate limits by adjusting a flow damper on November 17, 2012.
3682012001 | Arkansas 2 | 08/08/2012 | 09/27/2012 | ML12271A31 | <strong>Degraded Condenser Vacuum Due to the Failure of Condenser Vacuum Pump Solenoid Valves Results in a Main Turbine Trip and Subsequent Automatic Reactor Trip</strong><br /><i>Abstract:&nbsp;</i>On August 08, 2012 at 0823 CDT, Arkansas Nuclear One Unit-2 (ANO-2) tripped from approximately one hundred percent power due to degraded main condenser vacuum. The 2C-5B Condenser Vacuum Pump (one of two condenser vacuum pumps) had been secured by taking the control handswitch to pull-to-lock by Operations personnel to perform routine oil level checks. Ambient temperatures were low enough to maintain condenser vacuum with one condenser vacuum pump (2C-5A) in service. When 2C-5B was secured, two solenoid valves failed to reposition the isolation valves on 2C-5B, which resulted in a significant air flow path from atmosphere through the vacuum pump, causing condenser pressure to increase to the main turbine trip setpoint. The main turbine tripped on high turbine exhaust pressure which resulted in an automatic reactor scram due to high reactor coolant system pressurizer pressure. The Emergency Feedwater Actuation System actuated for the “A” Steam Generator due to steam generator water level trending slightly below setpoint. After investigation and corrective maintenance, ANO-2 was reconnected to the electrical grid on August 09, 2012. The root cause investigation determined that the subject solenoid valves were installed in an environment with temperatures in excess of designed temperature ratings. This condition resulted in heat related binding of the solenoid valves and failure to reposition when de-energized. The planned corrective action to preclude recurrence of this root cause will implement a modification to change the solenoid valve location to allow proper heat dissipation.
3692012001 | McGuire 1, McGuire 2 | 03/22/2012 | 05/17/2012 | ML12151A41 | <strong>Appendix R Non-Compliance Could Have Potentially Affected Cold Shutdown</strong><br /><i>Abstract:&nbsp;</i>McGuire Nuclear Station (MNS) has identified 10 CFR 50 Appendix R related non-compliances which could have resulted in fire-induced multiple spurious operation of the block valves for the Unit 1 or Unit 2 Steam Generator (SG) Power Operated Relief Valves (PORVs). This spurious operation could have potentially damaged these valves and rendered them inoperable. Since these valves are unisolable, they could not have been repaired to allow the SGs to be used for Unit cool down if needed. This potential condition could have adversely affected the ability to achieve a cold shutdown of the affected Unit following an Appendix R fire event. This event was not safety significant since the Appendix R non-compliances have low risk significance with respect to cold shutdown and they are mitigated by existing compensatory measures (i.e. fire watches) which have been in place as part of the MNS NFPA 805 transition. The cause of this event is a latent Appendix R design deficiency in the electrical circuits for the Unit 1 and Unit 2 SG PORV block valves. As part of the transition to NFPA 805, compensatory measures in the form of fire watches have been established in the Fire Areas associated with Appendix R non-compliances to mitigate the latent Appendix R design deficiency. PRA risk significance of this event determined it is not "High Risk" for purposes of ensuring NFPA 805 enforcement discretion criteria are satisfied. The MNS current licensing basis will be revised to maintain a Fire Protection Program that complies with NFPA 805 as an alternative to 10 CFR 50 Appendix R.
3692012002 | McGuire 1, McGuire 2 | 09/26/2012 | 12/18/2012 | ML12363A03 | <strong>Discovery of Inadequacy in Surveillance Testing of Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>At the time of the event, September 26, 2012, Unit 1 was in Mode 1 at 100% power and Unit 2 was in Mode 6. It was discovered that the existing Solid State Protection System (SSPS) logic test (semi- automatic test) and Westinghouse "7300" series channel operational test (COT) surveillance procedures for the "Safety Injection on 2/4 Low-Low Pressurizer Pressure" function may not provide sufficient overlap to confirm continuity for some of the SSPS jumpers used for channel multiplication. The inadequate surveillance testing constitutes a failure to meet the Limiting Condition for Operation, resulting in past operation prohibited by Technical Specifications, and common cause inoperability of an independent train or channel. The cause of this event was a design deficiency by the vendor in the specific test circuitry used to verify the SSPS logic. Testing was conducted to verify continuity of the affected SSPS jumpers which provide overlap. As corrective actions, the appropriate procedure changes were made and design changes will be implemented.
3702012001 | McGuire 2 | 11/02/2012 | 12/27/2012 | ML13009A08 | <strong>Manual Containment Isolation Valve inoperable longer than allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>During the Fall 2012 Unit 2 refueling outage, while in Mode 4, the primary means of providing Reactor Coolant system pressurizer spray, the 2A and 2B reactor coolant pumps (RCP), became unavailable. After a review of relevant documents, Operations determined that the Residual Heat Removal (ND) system auxiliary pressurizer spray feature could be placed in service. Manual containment isolation valve 2NV-1053 was opened to align ND auxiliary pressurizer spray. Two days later, it was determined that this action violated Technical Specification (TS) 3.6.3, Containment Isolation Valves (CIV), since valve 2NV-1053 was made inoperable when opened in Mode 4. The cause of this event was incorrect design basis operability and procedure guidance which allowed Operations to wrongly interpret that they could open a manual CIV in a Mode prohibited by Technical Specifications. Immediate actions taken were to declare CIV 2NV-1053 inoperable, enter TS 3.6.3, re-establish pressurizer spray using the 2B RCP, then close CIV 2NV-1053. Planned corrective actions are to correct the design basis operability guidance document for CIV 2NV-1053 and revise applicable procedures to remove the option to use the ND auxiliary pressurizer spray feature in Mode 4.
3702012002 | McGuire 2 | 12/01/2012 | 01/30/2013 | ML13042A22 | <strong>Automatic Actuation of the Auxiliary Feedwater and Nuclear Service Water Systems</strong><br /><i>Abstract:&nbsp;</i>At approximately 23:17 on December 1, 2012, Unit 2 experienced an actuation of the Anticipated Transient Without Scram Mitigation System Actuation Circuitry (AMSAC), which initiated an automatic turbine trip and automatic start of the 2A and 2B motor driven Auxiliary Feedwater (CA) pumps. The 2A Nuclear Service Water (RN) pump was operating at the time. The 2B RN pump automatically started due to start of the 2B CA pump. The actuation occurred at approximately 290 psig turbine inlet pressure when AMSAC unexpectedly armed with low feedwater flow conditions. It was subsequently determined that the setpoint in the AMSAC setpoint calibration procedure had not been changed to reflect the new setpoint of approximately 359 psig associated with the replacement high pressure turbine. The cause of this event was the lack of a formal method for notifying the McGuire Major Projects (MMP) procedure team when Engineering Changes (ECs) that are owned by MMP are approved. Corrective actions include modifying the computer application Nuclear Asset Suite used for ECs to correct this deficiency.
3732012001 | LaSalle 1, LaSalle 2 | 09/18/2012 | 11/09/2012 | ML12340A44 | <strong>Secondary Containment Inoperable Due to Interlock Doors Open</strong><br /><i>Abstract:&nbsp;</i>On September 18, 2012, Units 1 and 2 were in Mode 1 at 100% power. At 0115 hours CDT, an Equipment Operator (EO) reported the Unit 2 Reactor Building 761'elevation Interlock Doors 424/314 were both open at the same time for approximately 10 seconds. The control room supervisor instructed the EO to remain in the interlock to ensure one door remained closed at all times. During the time period that both interlock doors were open, Technical Specification (TS) Surveillance Requirement (SR) 3.6.4.1.2 ("Verify one secondary containment access door in each access opening is closed") was not met. The Secondary Containment was declared INOPERABLE for the period of time that both interlock doors were open and until administrative controls (posting the operator at the door) were established to verify one door remained closed at all times. LaSalle Station entered and exited TS 3.6.4.1 Required Action A.1 for both Units 1 and 2 to restore Secondary Containment to OPERABLE status within 4 hours. TS 3.6.4.1 Required Action A.1 was entered and exited at 0115 CDT on September 18, 2012. The cause of the event was determined to be the solenoid bracket being loose on Unit 2 Reactor Building 761'interlock door 424. Two screws that hold the locking solenoid bracket in place were found loose. The two loose screws on the locking solenoid mounting bracket caused the electric lock assembly to become misaligned. The misalignment of the electric lock assembly prohibited the locking solenoid plunger from being fully engaged with the door catch and damaged the limit switch, which resulted in the capability to open both interlock doors at the same time. The corrective actions were to replace the damaged limit switch and removing, tightening, and re-installing the solenoid mounting bracket. Operations verified the proper operation of the door interlock prior to returning the door to service.
3742012001 | LaSalle 2 | 08/31/2012 | 10/30/2012 | ML12318A18 | <strong>2B Diesel Generator Declared Inoperable due to Excessive Air Start Receiver Blowdown Caused by a Degraded Drain Valve</strong><br /><i>Abstract:&nbsp;</i>On August 31, 2012, at 09:40 CDT, while blowing down the 2B Diesel Generator (DG) A train Starting Air receiver for preventative maintenance, the receiver pressure decreased below the minimum 165 psig required for DG operability per Technical Specification (TS) 3.8.3, Condition D. The 2B DG provides emergency AC power to Division 3, which supplies the High Pressure Core Spray System (HPCS). The 2B DG was declared inoperable in accordance with TS 3.8.3 Required Action E.1. At 10:22 CDT, the A air start train was re-pressurized to greater than 165 psig, and the 2B DG was declared operable. The 2B DG was inoperable for approximately 42 minutes. The cause of the event was determined to be a degraded drain valve on the A train starting air receiver. The corrective actions included replacement of the drain valve.
3822012001 | Waterford 3 | 01/05/2012 | 03/05/2012 | ML12066A05 | <strong>Technical Specification for Containment Fan Cooler Minimum Cooling Flow Not Met</strong><br /><i>Abstract:&nbsp;</i>During the recent NRC Triennial Heat Sink Performance Inspection, it was identified that Component Cooling Water flows to the B and D Containment Fan Coolers during normal operating conditions were below the Technical Specification (TS) Surveillance Requirement (SR) for minimum flow from approximately July 8, 2009 through July 19, 2009. The duration of this condition exceeded the TS 3.6.2.2 Limiting Condition for Operation Allowable Outage Time of 72 hours. TS SR 4.6.2.2.a requires that each train of containment cooling shall be demonstrated operable at least once per 31 days by verifying a cooling water flow rate of greater than or equal to 625 GPM to each cooler. The original condition that caused the flows to be less than 625 GPM during normal operating conditions has since been corrected and subsequently meets or exceeds the flow-rate listed in the surveillance requirement. No plant transient or safety system actuations occurred. Stable plant operation continued at 100 percent power.
3822012002 | Waterford 3 | 02/16/2012 | 04/13/2012 | ML12109A08 | <strong>Failed Valve Actuator Diaphragm Causes Inoperability Greater Than Allowed by TS LCO Action</strong><br /><i>Abstract:&nbsp;</i>During a scheduled surveillance per procedure STA-001-005 (Leakage Testing of Air and Nitrogen Accumulators for Safety Related Valves) for the nitrogen accumulator system, an accumulator as-found leak rate exceeded the acceptance criteria. Subsequent investigation determined that the cause of the leakage was an emergency feedwater valve failed actuator diaphragm. This failure could have existed prior to discovery for a duration longer than the Technical Specification Limiting Condition for Operation action statement allows. The applicable Technical Specifications are 3.6.3 (Containment Isolation), 3.7.1.2 (Emergency Feedwater), and 3.7.1.7 (Atmospheric Dump Valves). The failed diaphragm was replaced and system operability restored within 72 hours after discovery. This identified condition is being reported as a Licensee Event Report (LER) under reporting criteria 10CFR50.73(a)(2)(i)(B): Any operation or condition which was prohibited by the plant's Technical Specifications.
3822012003 | Waterford 3 | 04/04/2012 | 06/04/2012 | ML12157A32 | <strong>Cracked Instrument Line Affects Fire Protection Safe Shutdown Analysis</strong><br /><i>Abstract:&nbsp;</i>On 04/04/2012, during the conduct of a scheduled surveillance, steam leakage was observed from an instrument line associated with the steam supply to Emergency Feedwater (EFW) Pump AB. Investigation determined the leakage source as a crack in the instrument line downstream of the normally open instrument root valve. The leakage was isolated by closing the instrument root valve. Engineering evaluation has determined that EFW Pump AB remained capable of performing its safety function. Due to the steam leak in the EFW Pump AB area, the fire protection safe shutdown manual actions could be affected which requires this to be reported under 10CFR50.73(a)(2)(ii).
3822012004 | Waterford 3 | 04/22/2012 | 06/21/2012 | ML12174A16 | <strong>Essential Chiller Oil Leak Creates Unanalyzed Past Operability Condition</strong><br /><i>Abstract:&nbsp;</i>At 14:43 CDT on 04/22/2012, a 22 drop per minute oil leak was discovered on instrument tubing for Essential Chiller A Compressor Low Oil Pressure Switch. Due to the noted oil leakage and loss of compressor oil inventory, the Essential Chiller Technical Specification (TS) 72 hour shutdown action was entered. Plant personnel aligned Essential Chiller AB (swing chiller) to replace A. Essential Chiller Train A was declared operable at 00:44 on 4/23/2012. Examination of the leak revealed that the tubing had been tie-wrapped to adjacent piping. Friction from normal system vibration had worn through the tubing. The instrument tubing was subsequently replaced. In evaluating the past operability of the Essential Chillers within the 30 day mission time, several occasions were discovered where opposite train equipment had been declared inoperable. This created a condition where both trains of Essential Chillers were inoperable, which is not covered by actions in the Essential Chiller TS. As none of the individual periods where both trains were inoperable exceeded 24 hours, consistent with the mission time assumed in quantitative risk analysis, the safety significance of the condition is negligible. This condition is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(ii)(B), and 10 CFR 50.73(a)(2)(v)(D).
3822012005 | Waterford 3 | 06/01/2012 | 01/05/2013 | ML13025A16 | <strong>Valve Degradation Causes Inoperability of Safety Related System</strong><br /><i>Abstract:&nbsp;</i>On 6/1/2012 at 04:26 CDT, Operations declared Auxiliary Component Cooling Water (ACCW) Train A inoperable due to excessive seat leakage through air operated temperature control valve ACC-126A. The Component Cooling Water Technical Specification 72 hour shutdown action was entered. The valve was unable to meet its low leakage safety function when closed by flow demand. Following maintenance, ACCW Train A was declared operable on 6/2/2012 at 14:30 CDT. Similar conditions have occurred since October of 2011. Engineering evaluation has determined the cause to be wearing of the valve stem bushings for ACC-126A. Since the condition is only recognized when placing the system in standby, the recurring condition created several occasions where past operability of ACCW Train A was not assured. Train B has not exhibited this problem. Analysis of past operability has determined that the impact on safety significance of ACC-126A failing to fully close is minimal. This condition is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(ii)(B), 10 CFR 50.73(a)(2)(v)(D), and 10 CFR 21.
3822012007 | Waterford 3 | 10/31/2012 | 12/31/2012 | ML13002A23 | <strong>Inoperability of a Safety Related Valve Due To Backup Air Accumulator Leakage</strong><br /><i>Abstract:&nbsp;</i>On 10/31/2012 during refueling outage RF-18, a post-maintenance leak test was performed on the actuator for air operated valve CC MVAAA134B (CC-134B), Dry Cooling Tower B Component Cooling Water (CCW) Bypass Valve. Although not part of the leak test, associated dual solenoid valve CC ISV0134B1/B2 was found to be leaking air through the solenoid valve exhaust vent port. Following replacement, the leaking solenoid valve was discarded prior to determining the cause or rate of leakage. Valve CC-134B is provided with a backup Instrument Air accumulator which is credited for operation to ensure meeting post tornado event functions on loss of the non-safety related Instrument Air system. On further evaluation, it was determined that the solenoid valve leakage could adversely affect the backup air accumulator inventory. As the leakage rate was never established prior to discarding the old solenoid valve, the backup accumulator could not be assumed to be capable of meeting the safety functions of valve CC-134B. This condition was discovered during RF-18 with the plant in a mode which did not require operability of the CCW system. CC-134B operability was restored. However, past operability was potentially affected back to RF-17 when the last accumulator leak test was conducted, a period of approximately 18 months. This condition is being reported pursuant to the requirements of 10 CFR 50.73(a)(2)(i)(B), 10 CFR 50.73(a)(2)(ii)(B), and 10 CFR 50.73(a)(2)(v)(D).
3872012001 | Susquehanna 1, Susquehanna 2 | 02/16/2012 | 05/23/2012 | ML12145A06 | <strong>Both Control Structure Chillers Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 22, 2012 at approximately 1500, a linkage connector on the "B" Control Structure (CS) chiller that connects the compressor guide vanes to the guide vane motor was found broken. As a result, Operations declared "B" CS chiller inoperable and entered the appropriate Technical Specifications. On March 27, follow-up investigation into the guide vane failure determined that "B" CS chiller failed while the "A" CS chiller was out-of-service for maintenance. Consequently, both CS chillers were inoperable simultaneously. The direct cause of the connector failure was cyclic fatigue. The apparent cause was cyclic fatigue failure initiated / accelerated by corrosion of the ball-joint connector. The broken ball-joint connectors on the "B" CS chiller were replaced. Other key corrective actions that will be completed include: replacing the mechanical ball-joint connectors on the guide vane linkage on other applicable chillers, including replacement of the ball-joint connectors on the chiller guide vane linkage as a preventive maintenance activity for the "B" CS chiller and other applicable chillers, and completing a root cause analysis on chiller reliability. There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(v) as a condition that could have prevented the fulfillment of a safety function and 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3872012002 | Susquehanna 1, Susquehanna 2 | 04/04/2012 | 06/04/2012 | ML12156A22 | <strong>"B" Control Structure Chiller Inoperable Concurrent with "A" Emergency Diesel Generator Out of Service</strong><br /><i>Abstract:&nbsp;</i>On April 4, 2012 at 1517, the "A" Emergency Diesel Generator (EDG) was declared inoperable for performance of a surveillance. At 1835 on April 4, 2012, the "B" Control Structure (CS) chiller was declared inoperable due to an unrelated problem (degradation of refrigerant piping associated with the chiller). With the "B" CS chiller inoperable coincident with the "A" EDG inoperable, the "A" CS chiller would not be available to perform its design function on a loss of offsite power. The direct cause of the refrigerant line degradation was corrosion. Causes of the event included: 1) a lack of an agreed upon documented system recovery plan fix for chiller leaks because the station failed to identify the complexity and need for a plan and 2) the corrective action program (CAP), System Health, and Work Management processes are not linked so that they work together to produce reliable, failure free operation of station chillers. The degraded piping on the "B" CS chiller that resulted in the chiller inoperability was replaced. Key corrective actions that are planned include developing a long-term chiller reliability project plan, replacing the refrigerant lines on the CS chillers and other applicable chillers, changes to the Equipment Reliability and Station Health Process procedure to include a template that directs that a project plan be developed that includes a systematic and thorough analysis for a system or component recovery, and changes to the station work management process procedure and the station CAP procedure to ensure the processes are properly linked. This will ensure that work orders that are CAP corrective actions are given sufficient priority. There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(v) as a condition that could have prevented the fulfillment of a safety function.
3872012003 | Susquehanna 1 | 04/06/2012 | 08/08/2013 | ML13221A52 | <strong>Unit 1 Secondary Containment Bypass Leakage Exceeded</strong><br /><i>Abstract:&nbsp;</i>On April 6, 2012, during the Susquehanna Unit 1 17th Refueling and Inspection Outage, it was determined that the as-found minimum pathway Secondary Containment Bypass Leakage (SCBL) Technical Specification (TS) limit was exceeded during the regularly scheduled Local Leak Rate Testing (LLRT). At the time the limit was exceeded, a LLRT was being performed on the Unit 1 'A' Feedwater (FW) Line Penetration X-9A. Of the three containment isolation valves in this FW line, two of the valves (141F010A and HV141F032A) failed to pressurize during testing. This required the leakage from valve 141818A, the remaining valve in the Unit 1 'A' RN line, to be used as the as-found minimum pathway leakage SCBL result. The leakage from the tested containment isolation valve 141818A was determined to be 2,855 standard cubic centimeters per minute (sccm). When the 2,855 sccm leakage was added to the combined as-found minimum pathway SCBL calculation (which included 3,893 sccm carryover from the Containment Spray penetration X-39B valves), it contributed to the total exceeding the TS limit of 7,079 sccm (15 scfh). In accordance with 10 CFR 50.72(b)(3)(ii)(A), on April 6, 2012, ENS notification (# 47812) was made to the NRC for a degraded or unanalyzed condition, and 10 CFR 50.73(a)(2)(i)(B) for a condition prohibited by TS. <br><br> The direct cause of the excessive leakage through the 141818A valve was due to a galled disc stud and minor seat wear. The root causes of the event were 1) Station Engineering management and supervision had not exercised technical authority over the Appendix J Program to prevent SCBL LLRT failures, and 2) The Leak Rate Test Program procedure did not establish "maintenance limits" for as-found and as-left SCBL LLRT test results for each valve. <br><br> The 141818A valve's disc stud was repaired and the soft seat was replaced. The Conduct of Station Engineering procedure was revised to include the Technical Conscience obligation statement from INPO 10-005, Principles for Maintaining an Effective Technical Conscience. The Leakage Rate Testing Program procedure has been revised to establish administrative maintenance limits for as-found and as-left SCBL LLRT results for each valve. These administrative maintenance limits identify when as-found corrective maintenance needs to be performed as well as what as-left limit must be achieved prior to returning the valve back to service after maintenance. There were no actual adverse consequences to the health and safety of the public since the dose consequences from the additional leakage would not have exceeded regulatory limits.
3872012004 | Susquehanna 1 | 01/28/2011 | 06/26/2012 | ML12179A27 | <strong>Unit 1 Secondary Containment TS 3.6.4.2 Combined LCO Time Exceeded on Two Occasions when the Primary Containment N2 Spectacle Flange was Rotated in the Open Position</strong><br /><i>Abstract:&nbsp;</i>On April 27, 2012, it was determined that PPL Susquehanna, LLC (PPL) failed to enter Unit 1 Technical Specification (TS) 3.6.4.2, "Secondary Containment Isolation Valves" Limiting Condition for Operation (LCO) when the primary containment nitrogen makeup line spectacle flange (1S2104) was rotated in the open position in Modes 1, 2 and 3. This condition was identified as a result of questions raised regarding the need to enter TS LCO 3.6.4.2, in addition to TS LCO 3.6.1.3, "Containment Systems Primary Containment Isolation Valves," when the Unit 1 and Unit 2 spectacle flanges were rotated to the open position. A review of the Unit 1 and Unit 2 control room logs for the past three years identified that on two occasions in 2011 (January 28, 2011 and June 25, 2011), the Unit 1 spectacle flange was open for greater than the combined completion times for TS 3.6.4.2, Condition C.1 and D.1 (4 hours and 12 hours, respectively) of 16 hours. As a result, these events are reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), as a condition prohibited by Technical Specifications. The cause of the event was less than adequate guidance specified in Operations procedures and status control mechanisms for controlling Secondary Containment. This event had no impact on the health and safety of the public. The Unit 1 and Unit 2 primary containment nitrogen makeup supply line spectacle flanges have been deleted from the Unit 1 and 2 TS Bases Table B3.6.4.2-2, "Secondary Containment Ventilation System Passive Isolation Valves or Devices."
3872012005 | Susquehanna 1 | 06/12/2012 | 08/02/2012 | ML12216A02 | <strong>Valve Internal Misalignment Resulting in Multiple Inoperable Main Steam Safety Relief Valves</strong><br /><i>Abstract:&nbsp;</i>During the Susquehanna Unit 1 17th Refueling and Inspection Outage, two (2) Main Steam Safety Relief Valves (SRVs) failed to meet the setpoint criteria of +3/-5% set forth in Technical Specification 3.4.3. The two SRVs actuated at a setpoint less than the -5% criteria during off-site testing on April 24 and April 25, 2012. The cause of the lower setpoint actuation is attributed to possible misalignment of the valve internals due to post-installation valve actuation using the actuator assembly. This event was determined to be a Common-Cause Inoperability of Independent Trains or Channels and reportable under 10 CFR 50.73(a)(2)(vii) due to having more than one failure caused by misalignment of the valve internals. The SRVs remained functional and would have relieved pressure. There were no actual adverse consequences to the fuel, any plant equipment, or to the health and safety of the public as a result of this event. To correct the condition, the SRVs were replaced with SRVs having a setpoint tolerance of +/- 1% of nameplate setpoint pressure. The SRVs that failed their setpoint tolerance will be refurbished to have an actuation pressure within +/- 1% of nameplate pressure. Pending a license amendment and In-Service Testing (IST) Relief Request, the procedures for post-installation testing of SRVs will be modified to test the SRVs using alternative methods.
3872012006 | Susquehanna 1 | 04/09/2012 | 08/08/2013 | ML13221A52 | <strong>"D" Outboard Main Steam Isolation Valve Leakage - 2012</strong><br /><i>Abstract:&nbsp;</i>On April 9, 2012, during local leak rate testing (LLRT) of Main Steam Line Isolation Valve (MSIV) Penetration Number X-7D, the Unit 1 "D" Main Steam Line Boundary would not pressurize to 25 psig due to excessive leakage. As a result of the testing and subsequent troubleshooting, Susquehanna discovered that the leak rate for the Unit 1 "D" Outboard Isolation Valve exceeded 150 standard liters per minute. This condition, which was considered to have existed during the previous operating cycle, was a failure to meet Technical Specification (TS) 3.6.1.3.<br><br> The causes of the event were imperfections in the seating surface and a less than adequate rework procedure. Root causes included: 1) Station Engineering management and supervision not exercising Technical Authority over the Appendix J Program, 2) the Leak Rate Test Program procedure not establishing "maintenance limits" for As-Found and As-Left MSIV LLRT test results, and 3) the station reportability procedure inappropriately stating that exceeding the MSIV 100 scfh leak rate limit is not reportable.<br><br> Key corrective actions taken include: 1) benchmarking industry MSIV rework procedures 2) revising the Susquehanna MSIV rework procedure, the conduct of station engineering procedure, the leak rate testing program procedure, and the station reportability procedure, and 3) evaluating replacing, instead of reworking, the poppet assembly for MSIVs that have failed their as-found LLRT.<br><br> There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(i)(B) as a condition prohibited by Technical Specifications.
3872012007 | Susquehanna 1 | 06/19/2012 | 08/17/2012 | ML12230A16 | <strong>Unplanned Shutdown due to Unidentified Drywell Leakage</strong><br /><i>Abstract:&nbsp;</i>On 6/15/2012, an increasing trend on the Unit 1 Containment Radiation Monitor (CRM) particulate channels was identified. Over the next 3 days Unit 1 unidentified drywell leakage continued to slowly rise. On 6/18/2012 a controlled shutdown was initiated and completed because of the unidentified drywell leakage. This event is reportable under 10CFR50.73(a)(2)(i)(A) as "the completion of any nuclear plant shutdown required by the plant's Technical Specifications" and 10CFR50.73(a)(2)(ii)(A) as "Any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded." On 6/19/2012 primary containment was entered to identify the source of the leak. The direct cause of the leak was a crack in the heat affected weld area of the weldolet joining the 4 inch diameter chemical decontamination pipe to the "1A" reactor recirculation pump suction line. Metallurgical examinations determined that the crack occurred due to cyclic fatigue. The preliminary cause of this through wall crack was fatigue failure due to cyclic vibration. The cyclic vibration was caused by operating the reactor recirculation pumps near the natural frequency of the decontamination flange assembly. The extent of this condition included all welds in the "1A" and "1B" reactor recirculation systems and connected system pipe welds. The immediate corrective action taken was to modify the chemical decontamination assembly connected to the reactor recirculation piping. This consisted of a redesigned 4 inch diameter chemical decontamination flange connection on both the "1A" and "1B" reactor recirculation pump suction lines. The length of the 4 inch diameter pipe was reduced from 6 inches to approximately 3.5 inches to produce a new configuration that is not susceptible to the cyclic fatigue caused by reactor recirculation pump vane passing frequency that is very close to the natural frequency of the assembly. There were no actual consequences to the health and safety of the public due to this event. At the time of the event, the Susquehanna Unit 2 reactor recirculation system piping and connected piping was determined to be capable of performing the required design function as part of the Reactor Coolant Pressure Boundary (RCPB). However, as a compensatory action, the Unit 2 reactor recirculation pump speed is limited to 1600 rpm to provide margin to the resonant frequency of the recirculation decontamination connection assemblies. There is no evidence of a leak from the Unit 2 RCPB and if a leak did occur it would be detected by the various drywell leakage monitoring systems prior to gross pipe failure,( i.e. leak before break. ) The root cause, safety significance, and corrective actions will be provided in a supplement to this LER upon completion of the Root Cause Evaluation.
3872012008 | Susquehanna 1, Susquehanna 2 | 06/28/2012 | 08/24/2012 | ML12241A13 | <strong>Loss of One of Two Offsite Power Sources</strong><br /><i>Abstract:&nbsp;</i>On June 28, 2012, at 1353, Susquehanna Steam Electric Station experienced a loss of power from one of two offsite power sources when Startup Transformer 20 (T-20) shutdown automatically. All Engineered Safeguards System (ESS) electrical busses fed by T-20 automatically transferred to the other offsite power source, Startup Transformer 10 (T-10). Additionally, Startup Bus 20, which is normally fed from T-20, automatically transferred to T-10. Multiple system containment isolation valves on both Units 1 and 2 closed as a result of the electrical transient. Operators were able to reset and restore each system. On Unit 1, Residual Heat Removal (RHR) shutdown cooling ceased operation during the transient. Shutdown cooling was restored within one hour by control room operators in accordance with off-normal procedures. Unit 2 remained at 100% power throughout the event. At the time of the event, Unit 1 was in Mode 4, Cold Shutdown and Unit 2 was operating in Mode 1 at approximately 100% power. This event was an unplanned actuation of systems that mitigate the consequences of significant events and was reported as an 8 hour report in EN 48055 in accordance with 10 CFR 50.72(b)(3)(iv)(A). The event is also reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv)(A). The direct cause of the event was an open ammeter switch contact causing a phase current imbalance that was detected by the protective relaying and initiated transformer lockout. The root causes of the event included: 1) foreign material from the manufacturing process that prevented the ammeter switch contact from closing and 2) design of the protective relay scheme that included a shared metering function. Key corrective actions that are planned include: 1) an interim compensatory action to ensure that switches within the extent of condition are not operated, 2) completing an engineering evaluation to select the best approach to correcting the condition, and 3) implementing the approach selected based on the engineering evaluation. There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(iv)(A) as an unplanned actuation of systems that mitigate the consequences of significant events.
3872012009 | Susquehanna 1, Susquehanna 2 | 05/08/2012 | 07/03/2013 | ML13186A13 | <strong>Multiple Test Failures of Reactor Protection System Electrical Protection Assembly Breakers</strong><br /><i>Abstract:&nbsp;</i>During the Susquehanna Unit 1- 17Th Refueling and Inspection Outage in May 2012, three (3) Reactor Protection System (RPS) Electrical Protection Assembly (EPA) breakers failed to trip during channel functional testing, thus failing to meet Technical Specification (TS) Surveillance Requirement (SR) 3.3.8.2.1. General Electric Hitachi Nuclear Energy (GEH), manufacturer of the EPA breakers, determined that the cause of these breaker failures to trip was a random calibration issue in that the undervoltage release mechanisms (UVR) drifted out of calibration. GEH also completed a 10 CFR Part 21 Evaluation which concluded that a postulated EPA undervoltage device common mode failure was not reportable under Part 21 because it does not represent a substantial safety hazard in the RPS EPA application. <br><br> A subsequent EPA breaker failure to trip was experienced during testing on Unit 2 in January 2013. <br><br> NRC determined these failures to be reportable as a common cause inoperability of two independent trains of RPS electrical power monitoring associated with several Unit 1 RPS breakers, (i.e., EPA Breaker calibration drift), in a single system, designed to shutdown the reactor. Accordingly, a Severity Level IV Traditional Enforcement violation of 10 CFR 50.73(a)(2)(vii) was issued to PPL on February 13, 2013 for failure to report this common cause inoperability. <br><br> The individual RPS power supply circuits containing the EPA breakers that failed to trip remained operable at all times. Testing of the redundant series connected EPA breakers demonstrated that they successfully tripped and would have performed the safety function of the circuits. There were no actual safety consequences to any plant equipment or to the health and safety of the public as a result of this event. All of the Unit 1 and Unit 2 Normal Supply EPA breakers have been replaced and the Alternate Supply EPA breakers are planned for replacement in accordance with the Work Management process.
3872012010 | Susquehanna 1, Susquehanna 2 | 12/14/2012 | 07/03/2013 | ML13186A13 | <strong>Both Trains of Control Structure HVAC at Susquehanna Were Rendered Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2012 at 1350 while Susquehanna Unit 1 was operating in Mode 1, 99% Rated Thermal Power (RTP) and Susquehanna Unit 2 was also operating in Mode 1, 99% RTP, the 'A' Control Structure (CS) HVAC was inoperable during routine maintenance. Subsequently, Operations declared the 'B' CS HVAC inoperable when the 'B' loop chilled water circulating pump tripped during a swap from the 'A' to the 'B' train. Consequently, both trains of CS HVAC were inoperable simultaneously, although at least one train of CS HVAC was in operation during the event. This event required entry into Technical Specification (TS) Limiting Condition for Operation (LCO) 3.0.3 for both Units and a power reduction commenced at 1453 for Unit 1 and at 1459 for Unit 2. There were no SSC's out of service at the time of the event that could have complicated the plant's ability to mitigate the event. This event was reported on Event Notification #48595. <br><br> The direct cause of the event was a failure of the IV CS HVAC system to start when the 'B' loop chilled water circulating pump tripped during starting. The apparent cause is electrical breakdown of the 'B' CS Chilled Water Circulating Pump motor such that the motor no longer operates within the manufacturers nameplate rating under startup conditions. <br><br> An immediate corrective action was to restore the 'A' CS HVAC system to OPERABLE and suspend the power reductions on both units followed by restoration to the pre-event power levels. An interim corrective action taken was to temporarily raise the breaker setting for the 'B' CS Chilled Water Circulating Pump by replacing the breaker with a higher trip setpoint. A long term corrective action to replace the 'B' CS Chilled Water Circulating Pump motor is planned for the 4th quarter 2013. <br><br> There were no adverse consequences to the health and safety of the public as a result of this event. This event is being reported under 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of a safety function and 10 CFR 50.73(a)(2)(1)(B) as operation prohibited by Technical Specifications.
3882012001 | Susquehanna 2 | 05/11/2012 | 11/20/2012 | ML12325A69 | <strong>Two Control Room Floor Cooling Systems Inoperable</strong><br /><i>Abstract:&nbsp;</i>On 5/11/12 at 1603 hours, while operating at 100% power, Unit 2 entered LCO 3.0.3 due to two control room floor cooling systems being inoperable. 0V117A Control Room Floor Cooling Unit fan's discharge damper failed earlier during the same day at 0523 hours, rendering the associated 0V117A fan inoperable. The redundant 'B' train fans and associated Control Structure Chiller automatically started as a result of a fan low flow interlock. The control switch for the 'A' train logic was left in 'Start' and the control switch for the 'B' train logic was left in 'Auto' as directed by the alarm response procedure. During application of a clearance order for repair of the failed 0V117A fan damper, the 'A' control room cooling fan switch was placed in 'Stop' position. This resulted in an automatic start of the 'A' Control Structure Chiller and all the associated 'A' fans except for the control room cooling fan, and a shutdown of the 'B' train fans and chiller. This condition caused the loss of both control room cooling fans and LCO 3.7.3, "Control Room Emergency Outside Air Supply (CREOAS) System," Condition E; LCO 3.7.4, "Control Room Floor Cooling System," Condition D; LCO 3.0.3; TRO 3.7.9, "Control Structure HVAC," and TRO 3.8.6, "Emergency Switchgear Room Cooling," were entered at 1603 hours. The control room operators immediately recognized the loss of cooling and took manual action to restart the 'B' train. LCO 3.0.3 was exited at 1618 hours without a reactor power reduction. This event is reportable as a loss of entire safety function under 10CFR50.73(a)(2)(v)(D). The causes of the event included a control switch design deficiency and less than adequate clearance order preparation, review and application authorization. Immediate corrective actions were taken to modify alarm response procedures. Key corrective actions that are planned include replacing control switches to correct the design deficiency and revising the Susquehanna clearance order procedure to provide better guidance for developing clearance orders for equipment that is in an a typical configuration due to system transient. Susquehanna Unit 1 was in Mode 5 at the time of the event and therefore was unaffected because the associated Unit 1 Technical Specifications were not applicable. There were no adverse consequences to the health and safety of the public as a result of this event.
3882012002 | Susquehanna 2 | 11/09/2012 | 11/04/2013 | ML13309A63 | <strong>Unit 2 Manual Scram due to Loss of the Integrated Control System</strong><br /><i>Abstract:&nbsp;</i>At approximately 0117 hours on November 9, 2012, with power at approximately 90%, plant operators scrammed Susquehanna Unit 2 and tripped Reactor Feed Pump Turbines A, B, and C due to a loss of the Integrated Control System (ICS). All control rods inserted and both reactor recirculation pumps tripped at -38 inches. Reactor water level lowered to -52 inches causing Level 3 (+13 inches) and Level 2 (-38 inches) isolations. High Pressure Coolant Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) both automatically initiated. HPCI was overridden prior to injection and RCIC was utilized to restore reactor water level to the normal band. All isolations and initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected.<br /><br /> Following the manual scram due to the ICS failure, a second scram signal was received at approximately 0420 hours on November 9, 2012 due to low water level during recovery from the initial scram. Reactor water level was +15 inches at the time of the trip. All initiations at this level occurred as expected. No steam relief valves opened. Pressure was controlled via turbine bypass valve operation. All safety systems operated as expected.<br /><br /> The initial scram and other associated system actuations were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B), 10 CFR 50.72(b)(3)(iv)(A), and 10 CFR 50.72(b)(2)(iv)(A) in EN 48496. The second scram signal was reported in accordance with 10 CFR 50.72(b)(3)(iv)(A) in EN 48500. These events are also reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv)(A).<br /><br /> The root cause of the initial scram was less than adequate evaluation of deficiencies associated with ICS core switch design, testing, and mitigating strategies that resulted in delayed resolution without understanding risk implications. The root cause of the second scram was Operations and Engineering did not emphasize the avoidance of a second scram on RPV Level 3 through standards, policies, administrative controls, procedures, and associated training. Key corrective actions included: 1) replacing the core switches with a newer version of the switches and enabling loop protection algorithms on Unit 1 and Unit 2, 2) various procedure changes to provide margin to a secondary scram including changes to the scram off-normal procedures, and training.<br /><br /> There were no adverse consequences to the health and safety of the public as a result of this event.
3882012003 | Susquehanna 2 | 12/16/2012 | 10/04/2013 | ML13277A60 | <strong>Unit 2 Automatic Reactor Scram While Performing Turbine Control Valve Surveillance Testing</strong><br /><i>Abstract:&nbsp;</i>On December 16, 2012, at approximately 0156 hours, the Susquehanna Steam Electric Station (SSES) Unit 2 reactor automatically scrammed during the performance of quarterly channel functional test of the turbine control valve (CV) fast closure channels of the Reactor Protection System (RPS). Both the High Pressure Cooling Injection (HPCI) and Reactor Core Isolation Cooling (RCIC) systems automatically initiated and injected water into the reactor vessel. At approximately 0210 hours on December 16, 2012, a second reactor scram signal was received due to reactor water level lowering to +13 inches. This LER is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A) for an event or condition that resulted in the automatic actuation of the RPS, and the HPCI and RCIC systems. <br /><br /> 0156 hours Scram - No direct cause of the unexpected Division 1 scram signal was identified. This conclusion is based on laboratory results from the disassembly and inspection of the #1 Turbine CV. The root cause of the scram was SSES failed to incorporate industry best practices with other impacted work groups for half scram reduction. 0210 hours Scram - The root causes are: The ICS design control value of +18 inches for setpoint setdown did not provide adequate margin to prevent operational overlap with the RPS low level scram setpoint of +15 inches; and the ICS reactor water level setpoint setdown was not reset prior to raising the ICS reactor water level <br /><br /> .Key completed corrective actions include: replaced the Unit 1 CV #1 Fast Acting Solenoid Valve and Shutoff Valve; revised the Unit 1 and 2 quarterly turbine valve cycling surveillance procedure to require the use of an RPS test box; inspected all four Unit 1 Fast Acting Solenoid Valves for secure butt splice connections; revised ON-100(200)-101 to specify reactor water level band that would not create a reactor low water level scram; revised OP-245-001 and hard card OP-245-001-01 to provide direction for resetting the ICS setpoint setdown. Key planned corrective action: provide training to all operators on specific lessons learned as they pertain to reactor level control. Include this training in initial license and licensed operator requal training. There were no actual consequences to the health and safety of the public as a result of this event.
3882012004 | Susquehanna 2 | 12/19/2012 | 02/19/2013 | ML13051A45 | <strong>Unit 2 Automatic Scram due to Low Reactor Pressure Vessel Level</strong><br /><i>Abstract:&nbsp;</i>At approximately 1731 hours on December 19, 2012, with the unit operating at approximately 18% power, Susquehanna Steam Electric Station Unit 2 automatically scrammed on low reactor pressure vessel (RPV) level (Level 3, +13 inches) while transitioning the 'A' reactor feed pump from discharge pressure mode to flow control mode. All control rods inserted and both reactor recirculation pumps tripped. Reactor water level lowered to approximately -29 inches causing Level 3 (+13 inches) isolations. There were no automatic Emergency Core Cooling System initiations. No steam relief valves opened during the event. All safety systems operated as expected. The scram and associated actuations were reported in accordance with 10 CFR 50.72(b)(2)(iv)(B) and 10 CFR 50.72(b)(3)(iv)(A) in EN 48607 at 2029 on December 19, 2012. These events are also reportable as an LER in accordance with 10 CFR 50.73(a)(2)(iv)(A). The root causes of the event were: 1) decision making without a formal evaluation of impacts that reflected a conditioned operator response and inadequate risk evaluation of activities and 2) missed opportunities to identify and provide compensation for the design of the integrated control system logic interface with the valve breaker power. Key corrective actions included: 1) providing operator training, 2) providing an equipment reliability update to crews, 3) issuing an Operations directive to minimize the knowledge based decisions, 4) revising the Units 1 and 2 reactor feed pump operating procedures, and 5) placing caution signs on the applicable valve breakers indicating that opening the breakers impacts Integrated Control System (ICS) logic. Key corrective actions planned include: 1) defining operator specific skill of the craft work activity actions in an Operations administrative procedure, 2) implementing changes to the station procedure use and adherence procedure, and 3) creating new or revised guidance on the need to identify actions to respond to or compensate for single point vulnerabilities. There were no adverse consequences to the health and safety of the public as a result of this event.
3892012001 | St. Lucie 2 | 05/11/2012 | 07/10/2012 | ML12202A08 | <strong>Unit 2 Trip due to Erratic Main Feedwater Regulating Valve Behavior</strong><br /><i>Abstract:&nbsp;</i>On May 11, 2012 at 0355 EDT St. Lucie Unit 2 was at 99% power when an unplanned reactor scram occurred. Operators manually scrammed the reactor and turbine due to lowering of the 2A steam generator (SG) level caused by erratic behavior of the 2A SG main feedwater regulating valve (MFRV) FCV-9011. Unit 1 was operating at reduced power (29%) due to power ascension from the Extended Power Up-rate (EPU) refueling outage. The Unit 2 reactor trip was uncomplicated and all control rod assemblies (CEAs) fully inserted. In accordance with plant design, all three auxiliary feedwater (AFW) pumps started in response to an auxiliary feedwater actuation signal (AFAS) due to low SG level. No other automatic safety system actuations were required and none occurred. Reactor coolant system (RCS) heat removal was maintained with AFW and atmospheric dump valves (ADV). The Offsite power grid was available and stable. The root cause for failure of the 2A SG MFRV was determined to be untimely corrective actions and sub-quality parts for the travel sensor (Xact) on the position feedback mechanism provided by the Vendor. Corrective actions included procedure revisions and replacement of travel feedback sensors.
3892012002 | St. Lucie 2 | 10/03/2012 | 11/27/2012 | ML12341A23 | <strong>Non-Segregated Phase Bus Fault Resulting in Partial Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On October 3, 2012 at 0843 with St. Lucie Unit 2 in a defueled condition, the collapse of a corroded non-segregated phase bus vent assembly resulted in a fault on the 6.9kV non-segregated phase bus for the 2B Startup Transformer. The 2B Startup Transformer locked out resulting in a partial loss of offsite power to Unit 2. The lockout caused a loss of voltage condition on essential 4.16kV Bus 2B3, and the automatic start and loading of the 2B Emergency Diesel Generator (EDG) equipment responded as expected. All euipment responded as expected. Risk associated with susceptibility of the perforated metal screen to corrosion was not recognized with respect to the collapse on to the phase bus duct bars. Immediate corrective actions included repairs to the degraded vents on the affected non-segregated phase bus run. An additional corrective action includes updates to the preventive maintenance bases for startup and auxiliary transformers to improve periodic maintenance of non-segregated phase bus run vent assemblies. This event had no effect on the health and safety of the public.
3892012003 | St. Lucie 2 | 10/07/2012 | 12/06/2012 | ML12355002 | <strong>Inadvertent Trip of 2B3 4.16kv Switchgear</strong><br /><i>Abstract:&nbsp;</i>On October 7, 2012, while in a defueled condition, a differential current lockout occurred on the St Lucie Unit 2 2B3 4.16kV essential bus, causing the bus to deenergize. At the time of the event, the 2B emergency diesel generator (EDG) was loaded to the essential bus. Due to the differential current lockout, all bus loads were lost and the 2B EDG output breaker feeding the essential bus opened. The 2B EDG transferred to emergency mode and the 2A EDG remained operable and in standby. This event is reportable pursuant to 10CFR5O . 73 (a) 2) (iv) (A) An investigation concluded the apparent cause was accidental shorting of the differential relay terminals while attempting to rack in the 2B component cooling water (CCW) breaker. Immediate corrective actions included systems checks and restoring the power to the 2B3 4.16kV essential bus. The 2B3 bus differential and lockout relays were tested satisfactory and no indications of equipment failure were identified. Corrective actions included a needs analysis to incorporate changes to training based on the lessons learned. This event had no effect on the health and safety of the public.
3902012001 | Watts Bar 1 | 02/13/2011 | 06/28/2013 | ML13182A69 | <strong>Failure to Meet Technical Specifications due to Issues Associated with Vital Battery Surveillance Program</strong><br /><i>Abstract:&nbsp;</i>On 01/17/2012, TVA determined that Vital Battery IV (VB4) was inoperable between 02/13/11 and 12/03/2011. This was based on an independent analysis of test data from the performance of Surveillance Requirement (SR) 3.8.4.14 for VB4 conducted on 02/10/2011 that indicated the actual battery capacity did not meet the SR 3.8.4.14 acceptance criterion. On 11/21/2011, VB3 did not meet the SR 3.8.4.14 acceptance criterion. On 03/14/2012, WA concluded that VB3 and VB4 may have been inoperable for unknown periods of time prior to the failed capacity tests. As a result, there were times when VB3 and VB4 were required to be operable to comply with Technical Specification (TS) 3.8.4 and TS 3.8.5, and WBN, Unit 1 failed to meet the applicable requirements of TS 3.8.4, TS 3.8.5 and LCO 3.0.4. Also, VB3 and VB4 may have been inoperable concurrently; thus, the requirements of LCO 3.0.3 may not have been met. <br><br> During the time periods discussed above, VB3 and VB4 were capable of performing their safety function. <br><br> The direct causes were due to the aggregate effects of lower battery temperatures, high electrolyte specific gravities, and marginal float voltages which over time caused the loss of battery capacity.
3902012002 | Watts Bar 1 | 06/29/2012 | 01/28/2013 | ML13029A62 | <strong>Unanalyzed Condition Affecting Probable Maximum Flood (PMF) Level</strong><br /><i>Abstract:&nbsp;</i>On June 29, 2012, Tennessee Valley Authority (TVA) approved an updated calculation titled "PMF Determination for Tennessee Valley Watershed" that increased the WBN probable maximum flood (PMF) level to Elevation 739.2 feet (ft) mean sea level (MSL). The current Updated Final Safety Analysis Report (UFSAR) PMF elevation is 734.9 ft MSL. WBN reviewed flood sensitive safety-related systems, structures, and components. Essential Raw Cooling Water and High Pressure Fire Protection equipment required for flood mode operation located on Elevation 722 ft of the Intake Pumping Station (IPS) and the Thermal Barrier Booster Pump (TBBP) motors are affected by the revised PMF level. The increase in calculated PMF elevation resulted from new rim leakage paths (i.e., leakage that occurs when water contained in a reservoir finds an alternate path around the dam) identified during aerial surveys for the proposed TVA Clinch River Site. No actual flooding has occurred. However, because of the unanalyzed condition, the potential existed for WBN to exceed its design basis PMF and adversely affect plant safety. Contingency measures have been put into place to protect the TBBPs and equipment located on Elevation 722 ft of the IPS. Permanent plant modifications will be made to protect affected equipment during a PMF event.
3902012003 | Watts Bar 1 | 09/21/2009 | 01/08/2014 | ML14008A29 | <strong>Entry into Mode 4 Without Meeting LCO 3.4.12, "Cold Overpressure Mitigation System (COMS)"</strong><br /><i>Abstract:&nbsp;</i>On September 21, 2009, Watts Bar Nuclear Plant Unit 1 (WBN) entered Mode 4 as part of the Cycle 9 refueling outage (RFO). When Mode 4 was entered, two Safety Injection (SI) pumps and more than one Centrifugal Charging Pump (CCP) were capable of injecting into the Reactor Coolant System (RCS). Technical Specification (TS) 3.4.12, "Cold Overpressure Mitigation System (COMS)," requires that a maximum of one CCP and no SI pumps be capable of injecting into the RCS when in Modes 4, 5, or 6 (with the reactor head on). As a result, Limiting Condition for Operation (LCO) 3.4.12 was not met and the applicable Required Actions were not taken within their associated Completion Times. Therefore, WBN was in a condition prohibited by the TSs. <br /><br /> A review of previous operating data revealed this condition also existed on April 4, 2011, when WBN entered Mode 4 as a part of the Cycle 10 RFO. <br /><br /> The cause of this event was that personnel were ineffective at the use of human performance tools. Specifically, personnel were ineffective at self checking to ensure all required procedures were identified during an impact review for a License Amendment request.
3902012004 | Watts Bar 1 | 08/28/2012 | 10/26/2012 | ML12299A39 | <strong>Automatic Reactor Trip due to Low-Low Steam Generator Level</strong><br /><i>Abstract:&nbsp;</i>On August 28, 2012, at 0332 hours with Watts Bar Nuclear Plant (WBN) Unit 1 at 100 percent rated thermal power, the reactor tripped automatically on low-low steam generator (SG) #2 level. Incorrect configuration of test equipment during testing of a Pressurizer Pressure channel induced a fault into the channel, and the channel fuse and upstream circuit breaker cleared on this fault. Loss of the upstream circuit removed power from the #2 main feedwater regulating valve circuitry, causing the valve to fail closed and resulting in loss of main feedwater to SG #2. Low-low level in SG #2 resulted in an automatic reactor trip and initiation of the auxiliary feedwater system. Plant personnel immediately entered appropriate trip response procedures and stabilized the plant in Mode 3. All safety systems functioned as designed. The root cause of this event is that procedure detail was inadequate to ensure correct configuration of the test equipment by inexperienced technicians. Procedures for circuit-intrusive activities with similar consequences were identified, placed on administrative hold, and will be updated to ensure procedural guidance meets procedure writing requirements. This event is reported as an LER in accordance with 10 CFR 50.73(a)(2)(iv)(A) for the automatic actuation of the reactor protection system and the auxiliary feedwater system.
3902012005 | Watts Bar 1 | 10/16/2012 | 12/15/2012 | ML12349A31 | <strong>Automatic Start of Emergency Diesel Generators due to Failed Transfer of Power to 6.9kV Shutdown Board</strong><br /><i>Abstract:&nbsp;</i>On October 16, 2012, at 2330 EDT, Watts Bar Nuclear Plant (WBN-1) licensed operators attempted a manual fast transfer of the 1B-B 6.9kV Shutdown Board (SDBD) from the normal feeder breaker to the alternate feeder breaker. The transfer was not successful, resulting in the automatic start of the four Emergency Diesel Generators (EDGs). After the 1B-B 6.9kV SDBD de-energized and the loads were shed, the alternate feeder breaker closed and re-energized the 1B-B 6.9kV SDBD. The loads supplied by the 1B-B 6.9kV SDBD were subsequently reconnected, and required tests were successfully completed to ensure operability of the 1B-B 6.9kV SDBD. At the time of the event, WBN-1 was in MODE 5 following a refueling outage. Operations personnel promptly entered the appropriate response procedure and re-established power to required loads. Required safety systems functioned as designed. This condition did not adversely affect the safe operation of the plant or the health and safety of the public. The cause of this event was that plant operators did not ensure the alternate feeder breaker hand-switch was held firmly in the "closed" position while initiating the fast board transfer. This report is being submitted in accordance with 10 CFR 50.73(a)(2)(iv)(A), a condition that resulted in automatic actuation of the EDGs.
3952012001 | Summer 1 | 01/17/2012 | 08/03/2012 | ML12220A20 | <strong>Core Exit Thermocouples & Reactor Water Level Indication System Inoperable due to Inadequate Maintenance Procedure</strong><br /><i>Abstract:&nbsp;</i>On January 17, 2012, a past operability analysis determined that Core Exit Thermocouples (CETCs), which are required by Technical Specification 3.3.3.6 for accident monitoring, were inoperable. Additional engineering analysis completed on June 6, 2012, determined that the Reactor Water Level Indication System (RVLIS) (required by Technical Specification 3.3.3.6) was also inoperable. At the end of Refuel (RF) 18, Control Rod Drive Mechanism (CRDM) Cable Bridge hold-down bolts were not installed following reactor reassembly. Had there been a Loss of Coolant Accident (LOCA) during the subsequent cycle, movement of the bridge could have resulted in damage to the Core Exit Thermocouple (CETC) cables and tubing for the Reactor Water Level Indication System (RVLIS) which would have resulted in loss of monitoring capability. This condition was not discovered until the beginning of RF-19. An Apparent Cause Evaluation (ACE) determined the cause of the missing hold-down bolts was an inadequate station procedure for Reactor Vessel reassembly.
3952012002 | Summer 1 | 06/14/2012 | 07/31/2013 | ML13214A37 | <strong>Seismically Qualified Refueling Water Storage Tank Aligned to Non-Seismic Piping</strong><br /><i>Abstract:&nbsp;</i>On 06/14/2012, with the plant in Mode 1 at 100% power, it was determined that opening the code boundary valve between the safety related and seismically qualified Refueling Water Storage Tank (RWST) and the non-safety related and non-seismically qualified Spent Fuel Pool (SFP) Purification Loop in Modes 1-4 renders the RWST inoperable. This alignment was utilized for RWST water mixing in support of weekly surveillance sampling and for filtration of the RWST water prior to refueling outages. As a result, on multiple occasions the RWST was inoperable for a period longer than allowed by Technical Specifications (TS) 3.5.4, Emergency Core Cooling Systems - Refueling Water Storage Tank, Limiting Conditions for Operation (LCO).<br><br> The cause of this event is a result of regulatory requirements for the separation of seismically qualified and non-qualified systems, structures and components not being adequately incorporated into the Design Basis Document (DBD) and Updated Final Safety Analysis Report (UFSAR).<br><br> Immediate actions consisted of implementation of a Station Order (11-22), which indefinitely suspended this alignment, and submittal of a license amendment request (LAR) to revise TS 3.5.4 such that the non-seismically qualified piping of the SFP Purification System may be aligned to the RWST by operation of a seismically qualified manual ASME code boundary valve under administrative controls for performance of RWST surveillance requirements and pre-outage filtration. This change will only be applicable through the next two fuel cycles.
3952012003 | Summer 1 | 10/23/2012 | 12/12/2012 | ML12348A05 | <strong>Reactor Vessel Head Penetrations Not Meeting Requirments of 10CFR50.55a(g)(6)(ii)(D)</strong><br /><i>Abstract:&nbsp;</i>On October 23, 2012 V. C. Summer Station Unit 1 (VCSNS) identified its first of four reactor vessel head penetrations that did not meet the requirements of 10CFR50.55a(g)(6)(ii)(D) and ASME Code Case N-729-1. The station was in a refueling outage (RF20) and commenced volumetric testing of the reactor vessel head penetrations as a result of recent industry experience on other cold head plants. Even though the volumetric and visual inspections determined that four penetrations were not through wall, this event is reportable because of a material defect in the primary coolant system which cannot be found acceptable under ASME Section XI. Therefore, these inspection results are reportable pursuant to 10CFR50.73(a)(2)(ii)(A). The flaws were subsequently repaired utilizing the embedded flaw repair process in accordance with NRC approved WCAP15987, Revision 2-P-A. The apparent cause of the flaws is attributed to primary water stress corrosion cracking. Corrective actions included repairing the penetrations and revising the frequency of the Bare Metal Visual Exam and the Volumetric Exam to every refueling outage.
3972012001 | Columbia | 02/28/2010 | 03/13/2012 | ML12083A29 | <strong>DG-3 Inoperable for Longer than Allowed by TS due to Failed Governor</strong><br /><i>Abstract:&nbsp;</i>On February 28, 2010, following investigations of a small amount of oil found in the vicinity of the division 3 emergency diesel generator (DG-3) electro-hydraulic type governor (governor), DG-3 was being operated to validate no oil leakage from the governor. DG-3 started experiencing load oscillations of approximately 300 kW after 45 minutes of full load operation. Subsequent investigative actions revealed the load instabilities were present in all modes of operation (idle, rated speed, and fully loaded) which indicated a governor control problem. Following troubleshooting, the DG-3 governor was replaced. DG-3 testing was completed and was returned to service on March 4, 2010. The direct cause of the event was determined to be the result of foreign material left in the governor as early as 2005. The root cause of the event was organizational decision making did not adequately consider long term risks and consequences associated with operating the governor with known foreign material intrusion. Contributing factors included wear due to aging, flushing the governor with fuel oil, and overfilling the governor.
3972012002 | Columbia | 01/17/2012 | 03/15/2012 | ML12088A03 | <strong>Technical Specification Non-Compliance due to Inadequate Procedure Guidance</strong><br /><i>Abstract:&nbsp;</i>On January 16, 2012, at 0505 hours, the Division 1 Control Room Emergency Filtration filter unit was declared inoperable in preparation for performing a number of maintenance activities. Technical Specification (TS) Action Statement 3.7.3.B was entered for one or more subsystems inoperable due to an inoperable control room envelope (CRE). TS 3.7.3.B.2 requires an evaluation be performed within 24 hours to verify that the mitigating actions ensure CRE occupant exposures to radiological hazards will not exceed limits. The plant procedure for control of breaches to the CRE specified the required mitigating actions. It was subsequently determined that the mitigating actions specified by the procedure were not adequate to ensure the dose to control room occupants would remain below design basis accident consequences. Thus, TS 3.7.3.0 should have been entered on January 17, 2012, for the Required Action and Associated Completion Time of Condition B not met. This TS Action Statement was not entered and the Required Action was not completed. The cause of the event was determined to be inadequate procedure guidance for implementing the revised TS Bases requirements. A stop work order was issued on all planned CRE breaches until planned corrective actions are completed. Planned corrective actions will revise guidance for performing maintenance on the CRE.
3972012003 | Columbia | 07/24/2012 | 09/20/2012 | ML12277A38 | <strong>Secondary Containment Pressure Exceeded During Plant Maintenance</strong><br /><i>Abstract:&nbsp;</i>On July 24, 2012, secondary containment pressure exceeded technical specification allowable limits for a period of approximately four and a half minutes. The pressure excursion was due to an inadvertent trip of reactor building fans ROA-FN-1B and REA-FN-1B. The trip occurred during ongoing maintenance on the Standby Gas Treatment (SGT) system. While technical specification limits were exceeded, the resulting pressure excursion was bounded by analytical results, and thus there were no safety consequences for this event. The investigation concluded that there was no direct evidence that a human performance error caused this event. The cause for the event was determined to be that operations does not have guidance on swapping to redundant lineups when work is to be performed on the SGT or reactor building HVAC Corrective actions will revise standard operating procedures and Instrument Master Data Sheets by adding a note about reactor building fan trip risk.
3972012005 | Columbia | 10/03/2012 | 11/01/2012 | ML12321A00 | <strong>Violation of Technical Specifications due to the Failure to Enter the Appropriate Technical Specification</strong><br /><i>Abstract:&nbsp;</i>In July 2012, the Nuclear Regulatory Commission (NRC) questioned Columbia Generating Station's (Columbia) practice of applying the Service Water (SW) Technical Specification. (TS) 3.7.1, as called out in procedures and work instructions, when taking safety related room coolers or fans out of service. This question was entered into Columbia's corrective action process and on October 3, 2012, it was determined that this practice had resulted in instances in which Columbia had been in a condition prohibited by TS. Specifically, Columbia did not enter the appropriate TS for an inoperable system, subsystem, train or component when the necessary attendant non-technical specification support equipment was not capable of performing its support function. Columbia entered the TS Limiting Condition for Operation (LCO) Action for one SW subsystem inoperable rather than entering the appropriate TS Action for the equipment supported by the room coolers. Columbia's procedures and work instructions were based on an inappropriate example provided in TS Bases 3.7.1. This information was added to the TS Bases in 1999. A review identified multiple occurrences over the past three years in which Columbia had not entered the appropriate TS, and on five occurrences, Columbia was in a condition prohibited by TS. The cause is due to human error in failing to recognize that the change to the TS Bases in 1999 required NRC review and approval. Corrective actions consist of revising the affected procedures and work instructions and correcting the TS Bases language. There were no actual safety consequences associated with this event.
3972012006 | Columbia | 09/19/2012 | 03/08/2013 | ML13079A26 | <strong>Both Divisions of SDC Isolation Valves Made Inoperable</strong><br /><i>Abstract:&nbsp;</i>On September 19, 2012, Energy Northwest (EN) identified that both divisions of Residual Heat Removal (RHR) Shutdown Cooling (SDC) Reactor Vessel isolation valves were inappropriately made inoperable at the same time on multiple occasions in support of maintenance and surveillance testing during the 2011 refueling outage (R-20). This planned inoperability of the SDC isolation valves was performed using procedure SOP-RHR-SDC-BYPASS. SOP-RHR-SDC-BYPASS contains the specific steps for preventing the closure of each of the SDC isolation valves and the subsequent restoration steps. SOP-RHR-SDC-BYPASS did not contain guidance to allow both divisions SDC isolation valves to be inoperable at the same time. Since both divisions of SDC isolation valves were made inoperable without procedural guidance, this is being reported as a condition that could have prevented the fulfillment of the safety function of systems that are needed to remove residual heat and to mitigate the consequences of an accident.
3972012007 | Columbia | 12/30/2012 | 02/28/2013 | ML13070A00 | <strong>Secondary Containment Inoperable due to Both Airlock Doors Being Open</strong><br /><i>Abstract:&nbsp;</i>On December 30, 2012, Columbia was operating at 100% power with all safety systems operable. At 0530 PST both doors of the 471 elevation airlock entrance of the Reactor Building were simultaneously opened for a short period of time. This was the result of the failure of the interlock between the outer security door R-204, and the inner door R-205. Having a condition where both doors in a Reactor Building airlock were opened simultaneously while not undergoing a planned evolution for maintenance or surveillance testing, results in an unintended entry into Technical Specification (TS) 3.6.4.1 Secondary Containment due to a failure to satisfy Surveillance Requirement (SR) 3.6.4.1.3. It was determined that this condition resulted in a loss of safety function (Secondary Containment) and was reported to the NRC (Event Notification 48639) at 1245 PST on December 30, 2012.
4002012001 | Harris | 04/21/2012 | 06/20/2012 | ML12172A38 | <strong>Delayed Closure of Main Steam Isolation Valves due to Corrosion</strong><br /><i>Abstract:&nbsp;</i>At 5:00 AM on April 21, 2012, Harris Nuclear Plant (HNP) was in a refueling outage, in Mode 4 (Hot Shutdown), cooling down to cold shutdown. During a surveillance test, two Main Steam Isolation Valves (MSIVs) did not close with acceptable stroke times. The two valves were declared INOPERABLE resulting in entry into Technical Specification (TS) 3.0.3. The plant continued to cool down as planned, entered Mode 5 (Cold Shutdown) at 11:27 AM, and exited TS 3.0.3. Troubleshooting revealed high friction within all three MSIVs with the root cause being unexpected long-term corrosion of the valve piston rings. Primary contributing causes were that the MSIVs were not properly categorized in the Air Operated Valve Program, and opportunities to identify potential valve degradation were not recognized. Corrective actions to prevent recurrence include replacing the valve piston rings with upgraded rings made of a material less susceptible to corrosion and implementing a diagnostic testing program on the MSIVs.
4002012002 | Harris | 05/31/2012 | 07/30/2012 | ML12213A25 | <strong>Missed Surveillance Resulting in Inoperable Containment Penetration Overcurrent Protection Devices</strong><br /><i>Abstract:&nbsp;</i>An investigation in May 2012 revealed that surveillance tests for containment penetration overcurrent protection devices had not been properly scheduled. Testing was performed on the components with missed surveillances over the next several weeks. On May 31, 2012, the breaker for Pressurizer Heater Bank C could not be tested due to a broken handle, which precluded demonstration of acceptable performance. Subsequently, on June 2, the B Reactor Coolant Pump overcurrent protection timing relay did not meet acceptance criteria for its surveillance test. Missed surveillances are required to be reported if subsequent testing does not demonstrate acceptable results. Root and Contributing Causes to the missed surveillances are historical in nature resulting from activities in the 1980s and 1990s. An extent of condition evaluation resulted in the testing of 30 breakers and six timing relays, with all but the subject two components described above passing the subsequent surveillance testing. The two components that did not pass subsequent testing were replaced and tested satisfactorily. Completed corrective actions include replacement and satisfactory testing of the breaker and relay. Planned corrective actions include revising impacted plant procedures and design documents.
4002012003 | Harris | 10/26/2012 | 05/09/2013 | ML13130A05 | <strong>Primary Shield Cooling Fan Fails to Secure as Required</strong><br /><i>Abstract:&nbsp;</i>At 10:18 EDT on October 26, 2012, at 100% power in Mode 1, during the monthly equipment swaps, primary shield fan S-2B-SB failed to remain secured after engaging the main control board (MCB) hand switch. The condition caused the “B” emergency diesel generator (EDG) to be inoperable, but licensed operators and other station personnel did not recognize the impact on EDG operability. On October 31, 2012 at 15:26, “B” EDG was returned to operable status.<br><br> The primary shield fan starting upon closure of the EDG output breaker had no significant adverse impact on the ability of the EDG to perform its safety function. The primary shield fan is a small load, and the EDG loading capability had sufficient margin to accept the small load upon closure of the output breaker.<br><br> The cause of the failure of the fan to remain secured was age-related failure of the 42 seal in contact. The root cause of the failure to recognize the impact of the contact failure on the “B” EDG operability was that the Technical Specifications Bases do not provide adequate clarity regarding Surveillance Requirement applicability and the specific requirements associated with EDG Operability. Corrective actions include revising the Technical Specification Bases, procedure changes, and additional training.
4102012001 | Nine Mile Point 2 | 12/09/2011 | 03/16/2012 | ML12080A14 | <strong>Forced Shutdown due to an Increase in Drywell Leakage in Excess of Technical Specifications Limit</strong><br /><i>Abstract:&nbsp;</i>On December 9, 2011, at 0908, Nine Mile Point Unit 2 (NMP2) was operating at 100 percent of rated thermal power when alert alarms were received for containment monitoring particulate channels. These alarms were accompanied by a rise in unidentified drywell leakage and drywell pressure. At 1046, a manual shutdown of Unit 2 was initiated due to exceeding the Technical Specification (TS) Limiting Condition for Operation for unidentified leakage in the drywell. TS 3.4.5 requires action to be taken if unidentified leakage increases > 2 gpm within a 24 hour period while in Mode 1. Peak drywell floor drain leakage was 3.7 gpm. Entry into the drywell revealed a packing leak from the Reactor Coolant System (RCS) "A" blocking valve 2RCS*MOV18A. The valve stem packing leak occurred due to a score in the packing material created by a burr on the valve stem. The burr was created during packing replacement in August 2011 when the plant was shutdown due to high unidentified drywell leakage from the packing of this same valve. The root cause of this event was that Nine Mile Point leadership did not exhibit a questioning attitude toward potential error likely situations. Leadership did not appropriately identify situations where precursors, such as lack of adequate procedure details and environmental conditions, were challenges to workmanship.
4102012002 | Nine Mile Point 2 | 05/25/2012 | 07/23/2012 | ML12214A39 | <strong>Loss of Isolation Function on RHR Shutdown Cooling Suction Line due to Breaker Trip</strong><br /><i>Abstract:&nbsp;</i>On Friday, May 25, 2012, at 1322 EDT, Nine Mile Point Unit 2 (NMP2) was in Mode 4, Cold Shutdown, and experienced a loss of power to 600V emergency load center 2EJS*US1 while performing scheduled preventative maintenance of the Division I Remote Shutdown System disconnect switches. Disconnect switch SW1-2CESA20 was taken to the actuate position which isolated main control room control, bypassed the housing limit switches, and aligned the trip test switch for local breaker control of 2EJS*US1 supply breaker 1-3B. Contacts in the trip test switch for EJS*US1 supply breaker 1-3B were found to be closed which energized its trip coil. This resulted in a loss of motive power to Division I Residual Heat Removal (RHR) system primary containment isolation valve 2RHS*MOV113 on the shutdown cooling suction line from the reactor vessel. At the time of the event, the Division I RHR shutdown cooling system was in-service with the Division II shutdown cooling suction line primary containment isolation valve 2RHS*MOV112 de-energized open to prevent inadvertent or spurious closure, which would interrupt the shutdown cooling decay heat removal function. The result of the event was that both the Division I and Division II isolation valves on the common RHR shutdown cooling suction line (2RHS*MOV112 and 2RHS*MOV113) were open with no motive power. Thus, neither valve was capable of automatically closing in the event of a reactor level low (level 3) signal due to a leak in the RHR shutdown cooling system. This report constitutes a 10 CFR 21 (Part 21) notification because the breaker failure that initiated the event is attributed to a breaker assembly deficiency.
4102012003 | Nine Mile Point 2 | 06/04/2012 | 08/02/2012 | ML12227A35 | <strong>Suppression Pool Level Below Technical Specification Limit During Mode Change</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2012, at 0517, Nine Mile Point Unit 2 (NMP 2) entered Mode 2 (startup) with suppression pool water level at 199.44 feet, below the minimum required level of 199.5 feet, per Technical Specification (TS) Limiting Condition for Operation (LCO) 3.6.2.2. Contrary to the requirements of LCO 3.0.1, the conditions for changing modes from Mode 4 (cold shutdown) to Mode 2 were not met when Mode 2 was entered. The low suppression pool level of 199.4 feet was discovered during shift checks on June 4, 2012 at 0846, when TS 3.6.2.2, Condition A was entered. Suppression pool water level was restored at 0926 and TS 3.6.2.2 Condition A was exited at 0933. The cause of this event is a failure to recognize abnormalities. The operators performing and verifying the Surveillance Requirements (SRs) and control room supervision reviewing the SRs did not recognize that little margin remained to the TS required lower level for suppression pool water level. Actions are being taken to communicate lessons learned from this event with operating crews for both units at Nine Mile Point Nuclear Station (NMPNS) with an emphasis on operator fundamentals of plant parameter monitoring and control. This event was entered into the NMPNS corrective action program (Condition Report CR-2012-005507).
4102012004 | Nine Mile Point 2 | 07/12/2012 | 09/10/2012 | ML12263A35 | <strong>Manual Reactor Scram due to a Loss of Main Turbine Gland Sealing Steam Resulting in Lowering Condenser Vacuum</strong><br /><i>Abstract:&nbsp;</i>On July 12, 2012, at 02:20, Nine Mile Point Unit 2 was manually scrammed from approximately 85 percent of rated power due to indications of rising offgas system inlet pressure and lowering main condenser vacuum. These conditions occurred due to a loss of the in-service 'B' clean steam reboiler and a low backup sealing steam supply initiation setpoint that resulted in an inadequate sealing steam supply pressure. The reboiler tripped on a low water level condition due to excess steam demand caused by an incorrectly installed gag on relief valve 2TME-RV135. The relief valve gag implementation plan did not contain an adequate level of detail for installation and testing. This event is reportable in accordance with 10 CFR 50.73(a)(2)(iv)(A) as a valid actuation of the reactor protection system. The root cause of this event is attributed to inadequate management guidance to ensure that changes in scope during engineering change package development are adequately reviewed and assessed. Corrective actions include adjusting the gag installed on relief valve 2TME-RV135, changing the initiation setpoint for the backup sealing steam supply, revising the turbine gland sealing system operating procedure, and revising the engineering change management procedure.
4102012005 | Nine Mile Point 2, Nine Mile Point 1 | 10/29/2012 | 12/21/2012 | ML13007A08 | <strong>Automatic Diesel Actuation Due to the Loss of a 115 kV Offsite Power Source</strong><br /><i>Abstract:&nbsp;</i>On October 29, 2012 at 21:00, Nine Mile Point Unit 2 (NMP2) was operating at 100 percent power when an automatic actuation of the Division I Emergency Diesel Generator (EDG) 2EGS*EG1 occurred due to the loss of a 115 kV off-site power source (Line 5). High winds from the remnants of Hurricane Sandy caused a lightning mast maintained by grid operator National Grid to fall in the Scriba substation in close proximity to the 'A' bus, causing a fault which actuated protective relaying and isolated the 'A' bus. Line 5, the 115 kV offsite power source for Division I, was de-energized when the breaker opened to isolate the fault on the 'A' bus, leading to the automatic actuation of the Division I EDG. Following the event, the unit continued to operate at 100 percent power and Line 5 was restored at 03:26 on October 30, 2012. The EDG was secured and placed in standby at 04:47 on October 30, 2012. This event is reportable in accordance with 10 CFR 50.73 (a)(2)(iv)(A), as an automatic actuation of an Emergency Diesel Generator (EDG). The cause of the lightning mast failure was a horizontal crack above the weld between the base plate and the bottom of the pole. Corrective actions taken include removal of the failed lightning mast and external and internal visual inspections of the remaining lightning masts in the Scriba substation.
4122012001 | Beaver Valley 2 | 09/24/2012 | 11/20/2012 | ML12331A12 | <strong>Automatic Actuation of Standby Service Water Pump During Emergency Diesel Generator Test</strong><br /><i>Abstract:&nbsp;</i>On September 24, 2012 at 1225 hours, Beaver Valley Power Station (BVPS) Unit 2 experienced an automatic start of "B" Standby Service Water Pump (2SWE-P21B) during the "A" Emergency Diesel Generator (EDG) Automatic Test. As part of the test, the "A" Service Water Pump (2SWS-P21A) tripped as expected on a simulated loss of offsite power. This resulted in a low pressure condition on the Service Water headers which caused an automatic start of 2SWE-P21B. 2SWS-P21A re-started about 13 seconds after tripping as expected by the test sequence. The "B" Service Water Pump (2SWS-P21B) continued to operate normally during this event. Prior to testing, operators had briefed on the possibility of a Standby Service Water Pump starting as a result of the EDG test. However, an expected actuation was not documented in the test procedure or operator logs (i.e., not a preplanned actuation). This event is reportable pursuant to 10 CFR 50.73(a)(2)(iv)(A) as a condition that resulted in an actuation of an emergency service water system that does not normally run and that serves as an ultimate heat sink. The expected trip of 2SWS-P21A was the direct cause for the automatic actuation of the Standby Service Water System. The safety significance associated with the automatic start of "B" Standby Service Water Pump that occurred at BVPS Unit 2 on September 24, 2012 is considered to be very low.
4122012002 | Beaver Valley 2 | 10/06/2012 | 12/04/2012 | ML12341A27 | <strong>Unacceptable Indication Identified During Reactor Vessel Head Inspection</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2012, during the Beaver Valley Power Station, Unit No. 2 (BVPS-2) refueling outage (2R16), the results of planned ultrasonic examinations performed on Penetration No. 44 of the reactor vessel head did not meet the applicable acceptance criteria. The indication was not through wall as there was no evidence of leakage at this penetration based on inspections performed on top of the reactor vessel head. The reactor vessel head examinations were being performed to meet the requirements of 10 CFR 50.55a(g)(6)(ii)(D) for reactor vessel head inspections to find potential flaws/indications well before the structural integrity of the reactor vessel head pressure boundary is significantly challenged. Indications that cannot be dispositioned as acceptable per ASME Code Section XI in a Reactor Coolant System pressure boundary are reportable under 10 CFR 50.72(b)(3)(ii)(A) / 50.73(a)(2)(ii)(A) as a condition of the nuclear power plant, including its principal safety barriers, being degraded. Primary Water Stress Corrosion Cracking (PWSCC) of the Alloy 600 J groove weld was determined to be the apparent cause of the identified flaw. Reactor head Penetration No. 44 was repaired in accordance with the applicable embedded flaw repair methodology which was approved by the Nuclear Regulatory Commission for use at BVPS-2. The safety significance of this indication was very low.
4122012003 | Beaver Valley 2, Beaver Valley 1 | 10/30/2012 | 12/21/2012 | ML12361A41 | <strong>Mode 3 Entered with Both Trains of Turbine Trip Circuitry Inoperable</strong><br /><i>Abstract:&nbsp;</i>On October 30, 2012 at approximately 1027 hours, Operations personnel identified that Beaver Valley Power Station Unit 2 (BVPS-2) was operating in Mode 3 with both trains of turbine trip actuation relays inoperable. The DC breakers that power the turbine trip actuation relays were open for turbine trip circuitry testing during plant start-up from a refueling outage. Technical Specification (TS) Table 3.3.2-1, Engineered Safety Feature Actuation System Instrumentation, Function 5.a requires two trains of turbine trip actuation relays in Mode 3 unless the main feedwater lines are isolated and the valves deactivated. The main feedwater lines were isolated, but the valves were not deactivated. TS 3.0.3 was entered as this condition did not meet the requirements of TS Table 3.3.2-1 Function 5.a and no associated action exists for this condition. Also, the requirements of TS 3.0.4 were not met since the plant transitioned from Mode 4 to Mode 3 without meeting the stated exceptions of TS 3.0.4. At approximately 1045 hours,TS 3.3.2 was met and TS 3.0.3 was exited when the main feedwater isolation valves were deactivated in the closed position. It was also identified that two similar events occurred at Beaver Valley Power Station Unit 1 (BVPS-1). On May 9, 2012, and October 31, 2010, BVPS-1 entered Mode 3 with the DC breakers that power the turbine trip actuation relays open for turbine trip circuitry testing. The root cause was determined to be an inaccurate perception of the applicability of the turbine trip TS in combination with less than adequate information in plant documents. Corrective actions planned include additional training, revisions to procedures, and enhancing plant documents and processes.
4132012001 | Catawba 1, Catawba 2 | 04/04/2012 | 12/10/2012 | ML12348A05 | <strong>Unit 1 Automatic Reactor Trip due to Faulted Reactor Coolant Pump Motor Cable Resulted in Zone G Relay Lockout and Subsequent Loss of Offsite Power and Emergency Diesel Generator Automatic Start for Both Units</strong><br /><i>Abstract:&nbsp;</i>On 04/04/12 at 2003 hours, Unit 1 tripped from 100% power following a trip of reactor coolant pump 1D. Shortly after the Unit 1 generator power circuit breakers opened, the Zone G protective relaying system unexpectedly actuated on an instantaneous underfrequency condition as a result of an error in the relay logic. This opened the switchyard breakers thereby isolating Unit 1 from the grid and resulting in a Loss of Offsite Power (LOOP). At the time of the trip, Unit 2 was in Mode 5 during its End-of-Cycle 18 Refueling Outage with both of its essential busses aligned to Unit 1 offsite power. Therefore, Unit 2's essential busses lost power as a result of the LOOP. Both emergency diesel generators (EDGs) on each unit automatically started and powered their respective essential busses as designed. A Notification of Unusual Event (NOUE) was declared as a result of the LOOP and the Catawba Emergency Response Organization was activated. Approximately five and one-half hours later, after confirming that the sources of the fault were cleared, offsite power was restored to one essential bus on each unit and the NOUE was terminated. The root causes of this event and the planned corrective actions in response to this event are described in detail in the respective sections of this LER. All plant safety related systems required to mitigate the event were operable and capable of performing their required safety related functions. These systems functioned as designed in response to this event. Therefore, the health and safety of the public were not adversely affected by this event.
4132012002 | Catawba 1, Catawba 2 | 09/26/2012 | 12/17/2012 | ML12355004 | <strong>Discovery of Inadequacy in Surveillance Testing of Solid State Protection System</strong><br /><i>Abstract:&nbsp;</i>Unit Status: At the time of the condition, September 26, 2012, Units 1and 2 were both in Mode 1 at 100% power. Event Description: It was discovered that the existing Solid State Protection System (SSPS) logic test (semi-automatic test) and Westinghouse "7300" series channel operational test (COT) surveillance procedures for the "Safety Injection on 2/4 Low Pressurizer Pressure" function do not provide sufficient overlap to functionally test some of the SSPS wiring used for channel combination logic. The inadequate surveillance testing constitutes a failure to meet the Limiting Condition for Operation, resulting in past operation prohibited by Technical Specifications, and common cause inoperability of an independent train or channel. Event Cause:The apparent cause was a functional design deficiency by the vendor in the specific test circuitry used to verify the SSPS logic. Corrective Actions:Testing was conducted to verify the function of the affected SSPS wiring.
4132012003 | Catawba 1 | 12/22/2012 | 03/22/2013 | ML13085A02 | <strong>Technical Specification (TS) Limiting Conditions for Operation (LCOs) 3.0.4 and 3.7.5 Were Violated due to Unit 1 Entering Mode 3 with Turbine Driven Auxiliary Feedwater (AFW) Pump Unknowingly Inoperable</strong><br /><i>Abstract:&nbsp;</i>On December 22, 2012, Unit 1 entered Mode 3 during startup from the End of Cycle (EOC) 20 Refueling Outage (RFO) with the turbine driven AFW pump unknowingly inoperable, in violation of LCO 3.0.4. It was also determined during a reportability review that the Completion Time requirement of LCO 3.7.5 for re-entering Mode 4 was retroactively violated by 44 minutes. Maintenance work had been performed on the pump during the RFO. Although the pump was believed to be operable following the completion of the maintenance, it failed its TS required surveillance test (the test can only be performed in Mode 3 when sufficient steam pressure exists to operate the pump). The cause of this event was determined to be human performance error by the maintenance technician during the assembly of the turbine and pump. In addition, the governing maintenance procedure was deficient in that it lacked detail concerning the required orientation of a turbine component during the assembly process. Planned corrective actions in response to this event include providing remedial actions to ensure maintenance technicians understand the requirements of human performance tool use and enhancing the maintenance procedure to include additional detail governing the assembly process. There was no safety significance to this event. During the time that the turbine driven AFW pump was inoperable while Unit 1 was in Mode 3, both motor driven AFW pumps were operable and remained capable of automatically starting and providing the required flow to the steam generators. Throughout this event, no situation existed that would have resulted in a demand for an AFW System automatic start. Therefore, this event did not affect the health and safety of the public.
4142012001 | Catawba 2, Catawba 1 | 10/23/2012 | 12/20/2012 | ML12363A01 | <strong>Diesel Generator (DG) 2B Was Unknowingly Inoperable from 09/28/12 to 10/23/12 Due to Failed Tachometer Relay Power Supply</strong><br /><i>Abstract:&nbsp;</i>On 10/23/12, during planned maintenance on DG 2B, it was determined that the DG had been retroactively inoperable since its last monthlytest which was conducted on 09/28/12. During this test, it was noted that an engine, tachometer malfunction had occurred; however, at thetime, the malfunction was not recognized as adversely affecting DG operability. On 10/23/12, the cause of the DG inoperability wasdetermined to be a failed tachometer relay power supply. It was determined that the failed power supply would have prevented the DG'soutput breaker from automatically closing in response to a Design Basis Accident (DBA). The root cause of this event was determined to be an inadequate technical evaluation following the tachometer malfunction on 09/28/12.Planned corrective actions in response to this event include: 1) Revising the DG operating and test procedures to ensure that thetachometer relay is operating properly; 2) Revising the DG Design Basis Document to describe the relationship between the tachometerrelated components; and 3) Developing a visible and/or an audible indication for verification of the status of the tachometer relay powersupply. There was minimal safety significance to this event. A Probabilistic Risk Analysis (PRA) evaluation was performed and the results of thisevaluation indicated that the Incremental Conditional Core Damage Probability (ICCDP) and the Incremental Conditional Large EarlyRelease Probability (ICLERP) associated with this event were less than 1.0E-06 and less than 1.0E-07, respectively. Therefore, this eventdid not affect the health and safety of the public.
4162012001 | Grand Gulf 1 | 11/19/2009 | 03/14/2012 | ML12074A08 | <strong>Surveillance Test Procedure Inadequate to Meet the Requirements of Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On November 19, 2009 Grand Gulf Nuclear Station (GGNS) failed to ensure that Technical Specification (TS) Surveillance Requirement (SR) 3.5.3.1 was met. The 2009 NRC Problem Identification and Resolution (Pl&R) Inspection identified a concern that there was no basis (calculation) for the two-minute venting criterion and that there was no visual means of confirming water flow through the vent line when performing venting of the Reactor Core Isolation Cooling (RCIC) system. In 2009, during review of the NRC concern, GGNS determined that the acceptance criteria of SR 3.5.3.1 was met, and that the RCIC system had successfully completed the required surveillance testing. However, as an enhancement, GGNS revised the verification procedures to require an ultrasonic test (UT) examination and commenced the engineering change process to install a permanent sightglass for the vent line. During the 2011 Pl&R Inspection, a review of a previous 2009 Pl&R Inspection violation determined that the acceptance criteria to satisfy TS (SR) 3.5.3.1 was inadequate which resulted in the RCIC system being inoperable for a period of time in excess of TS allowances which resulted in a condition prohibited by TS. GGNS confirmed full compliance with TS SR 3.5.3.1 by performing UT testing on February 5, 2010 which verified the piping was full of water. Because GGNS considered SR 3.5.3.1 to still be met in 2009, SR 3.0.3 was not applied at the time it was discovered that the surveillance procedure may not be adequate.
4162012002 | Grand Gulf 1 | 02/19/2012 | 04/19/2012 | ML12111A01 | <strong>Manual Reactor Scram due to a Steam Supply Motor Operated Valve Failure that Resulted in the Inability to Maintain Reactor Water Level</strong><br /><i>Abstract:&nbsp;</i>On February 19, 2012, at 1904 hours Central Standard Time (CST), Grand Gulf Nuclear Station (GGNS) was in Mode 1 operating at approximately 22 percent power during a planned plant shutdown with the Reactor Feed Pump A (RFP A) secured when a manual reactor scram was initiated due to decreasing reactor pressure vessel (RPV) water level. The cause of the event was a combination of the isolating steam valve to the Reactor Feed Pump B (RFP B) being out of position, ninety percent closed, which isolates the main steam header from RFP B and a planned power reduction. The power reduction resulted in the turbine bypass valves (TBPV) opening as designed, then when the TBPVs reached 16 percent open, RFP B began to decrease in speed. This resulted in a decreasing level in the RPV. As level decreased, the Control Room Supervisor directed a manual scram be inserted prior to reaching the low level scram set point (+11.4 inches narrow range). After the scram, Reactor Core Isolation Cooling (RCIC) was manually started to inject water into the RPV and RFP A was restarted to restore and maintain reactor water level. The appropriate off-normal event procedures were entered to mitigate the transient with all systems responding as designed. All control rods inserted to shut down the reactor. No emergency core cooling system (ECCS) initiation setpoint was reached and no safety relief valves (SRVs) lifted. The normal heat sink (main condenser) remained available during this event.
4162012003 | Grand Gulf 1 | 04/02/2012 | 06/01/2012 | ML12150A18 | <strong>ESF Actuation due to Division III Bus Undervoltage following a Lightning Strike</strong><br /><i>Abstract:&nbsp;</i>On 4/2/12 at 1511 hours Central Daylight Time (CDT), Grand Gulf Nuclear Generating Station (GGNS) was in Mode 5 when a valid Engineered Safety Feature (ESF) actuation for emergency Alternating Current (AC) power to Division Ill 4160 Volt bus occurred due to degraded voltage. One of the two 500 (kilovolt) kV offsite feeder breakers tripped causing a drop in grid voltage which resulted in a trip of the ESF feeder breaker for Division Ill 4160 V bus. The High Pressure Core Spray (HPCS) Diesel Generator automatically started and energized the bus. The HPCS system was not running and no Emergency Core Cooling System (ECCS) initiation occurred during this event. Divisions I and II ESF power monitoring instrumentation responded to the grid voltage transient but no actuation setpoints were reached. Division I and II ESF 4160 Volt buses remained energized and shutdown cooling remained in service. The Technical Specifications required offsite power sources remained operable and in service during this event. The 500kV feeder that tripped was restored by the dispatcher at approximately 1515 CDT. The Division Ill bus was subsequently transferred back to offsite power and the HPCS Diesel Generator was secured.
4162012004 | Grand Gulf 1 | 04/28/2012 | 06/27/2012 | ML12180A07 | <strong>Weld Defect Indication Found in Residual Heat Removal System to Reactor Pressure Vessel Boundary Nozzle</strong><br /><i>Abstract:&nbsp;</i>On 4/28/2012 with the plant in Mode 4 for refueling outage 18 (RF18) with the reactor shutdown, during In-Service Inspection (ISI) testing, the nozzle weld N6B-KB, Residual Heat Removal / Low Pressure Coolant Injection (RHR/LPCI) "C" Nozzle to Safe End Weld was ultrasonically (UT) tested. The UT examination revealed an indication indicative of intergranular stress corrosion cracking (IGSCC). The indication was evaluated by Entergy Engineering and Electric Power Research Institute (EPRI) personnel and confirmed to be a weld defect. Inservice Inspection (ISI) relief request (RR-ISI-17; ML12124A245) to repair the weld was submitted to, and approved by, the NRC (reference GTC 2012-00011). A full structural weld overlay repair to restore the weld to ASME Code requirements was completed on May 14, 2012. A post-weld UT test was completed satisfactorily on May 16, 2012. The event posed no threat to public health and safety.
4162012005 | Grand Gulf 1 | 06/13/2012 | 08/13/2012 | ML12227A71 | <strong>Average Power Range Monitors Inoperable in Excess of Technical Specification Allowances in Mode 2</strong><br /><i>Abstract:&nbsp;</i>On June 13, 2012, during startup activities for Unit 1 with the reactor in Mode 1 operating at approximately 12 -15 percent (%) power, it was identified that the Average Power Range Monitor (APRMs) were indicating reactor power level lower than expected for the plant condition. Investigation identified that during Refueling Outage 18 (RF18) the APRMs were set to indicate flux lower than the actual power level. This resulted in the system being inoperable during Mode 2 due to the APRM setdown high flux scram setpoint being outside of Technical Specification (TS) 3.3.1.1 Reactor Protection System (RPS) Instrumentation limits. This condition existed when Mode 2 was entered initially on June 6, 2012 until Mode 1 was entered on June 13, 2012. The apparent cause of this condition was differing operating characteristics between the old system and the new system that were not noted during the Engineering Change (EC) process, and therefore they were not adequately addressed by procedure revisions/work order instructions. This condition was limited to the Power Range Neutron Monitoring (PRNM) system. This issue was related to the installation of the new system, future outages will only involve detector replacements and will not involve transferring settings from an existing analog system to a replacement digital system. During startup in Mode 2, the intermediate range monitors (IRM) and the high reactor pressure trip functions were operable. Therefore reactor power transients would have been mitigated by these functions. The APRM Neutron Flux High (Setdown) function is not directly credited in any safety analyses, this event did not adversely affect plant safety or the health and safety of the public.
4162012006 | Grand Gulf 1 | 07/25/2012 | 08/23/2012 | ML12236A40 | <strong>Special Nuclear Material Inventory Discrepancy</strong><br /><i>Abstract:&nbsp;</i>On July 25, 2012, at 1534 hours Central Daylight Time (CDT), the determination was made that a Source Range Monitor (SRM) detector was not in its expected storage location, thus meeting the reporting criteria in 10 CFR 72.74 and 10 CFR 74.11 as a loss of special nuclear material. The SRM detector contained an estimated maximum activity of 0.187 microcuries (all isotopes, including U-235), thus meeting the reporting criteria in 10 CFR 20.2201 (a) (1) (ii) as a loss of licensed material of a quantity greater than ten times that specified in Appendix C to 10 CFR Part 20. According to special nuclear material (SNM) inventory sheets, the SRM detector was expected to be stored in an SNM Item Control Area (ICA) on the 208 foot elevation of the Auxiliary building. However, during performance of the annual physical inventory of SNM, the SRM detector could not be located. Subsequent investigation concluded that the SRM was removed from the 208 Auxiliary building SNM ICA during clean up at the end of Refueling Outage 18, along with other material that was stored in the area, and discarded as radioactive waste. The event posed no threat to public health and safety as the detector was not highly irradiated (not in the reactor core during reactor startup) and was controlled as radioactive waste.
4162012007 | Grand Gulf 1 | 07/19/2012 | 09/14/2012 | ML12261A12 | <strong>Standby Service Water System Administratively Inoperable for a Period Longer than Allowed By Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On August 18, 1987, a 10 CFR 50.59 safety evaluation was performed for a change to the Grand Gulf Nuclear Station (GGNS) Final Safety Analysis Report (FSAR) to relax methodology for single passive failures of Standby Service Water (SSW) components. On July 19, 2012, with the plant in Mode 1 at approximately 100% pre-extended power uprate power, during the 2012 Component Design Basis Inspection (CDBI), the Nuclear Regulatory Commission (NRC) reviewed FSAR change NPEFSAR 87/0067 and determined prior NRC approval of the change was required. SSW was administratively inoperable for a period longer than allowed by technical specifications due to relaxation of the passive failure methodology without prior NRC approval. The event posed no threat to public health and safety as there have been no passive failures which have challenged operability. Compensatory measures have been implemented and a request to revise the SSW passive failure methodology has been submitted to the NRC. Procedures are in place to prevent recurrence.
4162012008 | Grand Gulf 1 | 12/29/2012 | 02/27/2013 | ML13059A32 | <strong>Reactor Protection System Actuation due to a Main Turbine Generator Trip</strong><br /><i>Abstract:&nbsp;</i>On December 29, 2012, at 00:18 Central Standard Time, Grand Gulf Nuclear Station was operating in Mode 1 at 100 percent thermal power when an unexpected Reactor SCRAM occurred due to a Main Generator trip. All systems responded as expected with the exception of Safety Relief Valve (SRV) 1B21F047A, which was slow to close, and high pressure feedwater heater start-up outlet valve 1N21F010B, which did not open. The shift immediately entered the appropriate Off Normal Event Procedures. Reactor water level was controlled using the normal condensate/feedwater system throughout the event. All control rods inserted after Reactor Protection System signals were received. There were no Emergency Core Cooling System actuations. The plant was stabilized with pressure control on the main turbine bypass valves, and level controlled on the start-up level control valve. The plant responded to the trip as designed with the exception of the one SRV and one start-up outlet valve noted above. The cause of the SCRAM was not initially determined. Additional monitoring equipment was installed to detect a similar condition. Following a second SCRAM on January 4, 2013, the cause was determined to be grounding of the Main Generator 'A' Phase Neutral Current Transformer. There were no adverse effects on the health and safety of the public.
4232012001 | Millstone 3 | 02/09/2012 | 04/03/2012 | ML12107A02 | <strong>Main Steam Line Pressure Transmitters Declared Inoperable</strong><br /><i>Abstract:&nbsp;</i>On February 9, 2012, at 1655, while operating in MODE 1 at 100% power, Millstone Power Station Unit 3 (MPS3) discovered that all twelve main steam line steam generator (SG) pressure transmitter's Litton-Veam connectors had not been reconnected using new gaskets as required by the Equipment Qualification (EQ) Record after maintenance was performed from Jan. 17, 2012 to Feb. 2, 2012. Upon discovery, operators declared the main steam line SG pressure transmitters inoperable per Technical Specification (TS) 3.3.2 and entered TS Action Statement (TSAS) 3.0.3. By 2151 on Feb. 9, 2012, new gaskets were installed in all twelve main steam line SG pressure transmitters, operators declared the transmitters operable, and exited MPS3 TS 3.0.3. The cause was determined to be a failure to incorporate 1998 EQ program requirement changes into the affected surveillance procedures as required by station procedures. Surveillance Procedure SP3444-B01 has been revised to incorporate a step to require changing out gaskets. This condition is being reported pursuant to 10 CFR 50.73(a)(2)(v)(C) as an event or condition that could have prevented the fulfillment of the safety function of structures or systems that are needed to shutdown the reactor and mitigate the consequences of an accident, and 10 CFR 50.73 (a)(2)(i)(B) as a condition prohibited by TS.
4242012001 | Vogtle 1 | 02/15/2012 | 04/11/2012 | ML12103A27 | <strong>Seismically Qualified RWST Aligned to Non-Seismic Piping</strong><br /><i>Abstract:&nbsp;</i>On February 15, 2012, with the unit at 100 percent power, it was determined that opening the boundary valve between the safety related and seismically qualified Refueling Water Storage Tank (RWST) and the non safety related and non seismically qualified Spent Fuel Pool Purification (SFPP) system in Modes 1-4, renders the RWST inoperable. Plant procedures had been revised in 2009 to allow opening this boundary valve in Modes 1-4 under administrative controls. The 10 CFR 50.59 safety evaluation that had been performed to support the procedure change had concluded that the administrative controls would allow the RWST to remain operable. However, in consideration of the new interpretation provided in NRC Information Notice 2012-01, it was judged that the RWST would be considered to be inoperable regardless of the administrative controls established when the RWST was aligned to non-seismic piping in Modes 1-4. Since the boundary valve had been opened in Mode 1 under administrative controls and the one hour completion time of Technical Specification 3.5.4 Condition D was not entered, under this recent interpretation, this represented a condition prohibited by Technical Specifications and is reportable pursuant to 10 CFR 50.73(a)(2)(i)(B). This event had no significant safety consequence since a seismic event had not occurred while the SFPP system was in service on the RWST.
4242012002 | Vogtle 1 | 04/14/2012 | 06/13/2012 | ML12163A24 | <strong>Manual Reactor Trip due to Circuit Board Failure</strong><br /><i>Abstract:&nbsp;</i>On April 14, 2012, at approximately 1346 Eastern Daylight Time (EDT) time, with Unit 1 operating in Mode 1 at 100 percent rated thermal power, Unit 1 operators initiated a manual reactor trip due to the loss of flow from the 1B Main Feedwater Pump (MFP). The Reactor Trip System, the Engineered Safety Feature Actuation System, and other responding equipment performed as expected. The plant was stabilized in Mode 3. The cause of the loss of 1B MFP flow was the failure of a "Position 5" circuit board in the feed pump turbine speed control circuit. This board failure is preliminarily attributed to component aging. The failed board has been shipped to a vendor for a detailed failure analysis. Upon review of the detailed failure analysis, the conclusions, if different than component aging, will be provided in a Supplemental LER. The controller board is obsolete and no longer has original manufacturer support. The prompt corrective action was to replace the subject circuit board. The safety significance of this event is low. There were no adverse effects on the health and safety of the public.
4242012003 | Vogtle 1 | 08/19/2012 | 10/17/2012 | ML12291093 | <strong>Failure to Comply with Technical Specification LCOs 3.7.14 and 3.0.3</strong><br /><i>Abstract:&nbsp;</i>On August 17, 2012, 1A ESF Chiller condenser vacuum was noted to be 12 inches of mercury, with a vacuum of 15 inches of mercury specified as the low limit on operating logs. The Shift Supervisor mistakenly believed condenser pressure was one of the parameters in which engineering had evaluated and was continuing to monitor. This misinformation was carried forward through subsequent shifts via logs. During the next five days, 1A ESF Chiller condenser vacuum decreased to 4 inches of mercury and stabilized for an additional four days prior to initiation of a condition report (CR) on August 26, 2012. Subsequent investigation and consultation with the vendor determined the 1A ESF Chiller was inoperable and the technical specification LCO was entered at 1437 on August 26, 2012. As a result of the delay in recognition of the status of the subject chiller, appropriate entries into LCOs 3.7.14 and 3.0.3 were not taken. Neither the safety of the plant nor the public health and safety were affected in a significant way by these events.
4242012004 | Vogtle 1 | 10/05/2012 | 12/03/2012 | ML12339A01 | <strong>Unplanned Auxiliary Feedwater Actuation</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2012 with Unit 1 in Mode 5 and the residual heat removal (RHR) system in service for reactor coolant system temperature control, activities were in progress in preparation for Mode 4 entry. One of the activities involved restoration of the steam generator level RPS/ESFAS instrumentation from a bypassed condition to normal alignment. During the restoration a steam generator lo-lo level actuation was received and the motor-driven auxiliary feed water (AFW) pumps started and two turbine-driven AFW discharge valves stroked full open. The AFW system had previously been removed from service per the controlling unit operating procedure; however, following safety system testing during the outage the AFW system was not properly aligned to prevent inadvertent actuations. Neither the safety of the plant nor public health and safety were affected by this event.
4242012005 | Vogtle 1 | 10/08/2012 | 12/03/2012 | ML12339A19 | <strong>Main Steam Isolation Valve Failure</strong><br /><i>Abstract:&nbsp;</i>On October 5, 2012 with Unit 1 in Mode 5 and the residual heat removal (RHR) system in service for reactor coolant system temperature control, activities were in progress in preparation for Mode 4 entry. One of the activities involved restoration of the steam generator level RPS/ESFAS instrumentation from a bypassed condition to normal alignment. During the restoration a steam generator lo-lo level actuation was received and the motor-driven auxiliary feed water (AFW) pumps started and two turbine-driven AFW discharge valves stroked full open. The AFW system had previously been removed from service per the controlling unit operating procedure; however, following safety system testing during the outage the AFW system was not properly aligned to prevent inadvertent actuations. Neither the safety of the plant nor public health and safety were affected by this event.
4402012001 | Perry | 03/01/2012 | 04/27/2012 | ML12128A00 | <strong>Manual Reactor Protection System Actuation due to Automatic Turbine Generator Runback</strong><br /><i>Abstract:&nbsp;</i>On March 1, 2012, at 0224 hours, operators manually initiated a reactor protection system actuation in response to a turbine generator runback. At the time of the event, the plant was in Mode 1 with the reactor operating at 100 percent of rated thermal power. All control rods fully inserted into the core and no Emergency Core Cooling systems were required to maintain level. The turbine generator runback resulted from restoration of a generator stator water cooling system pressure gauge after calibration. A low pressure condition was created in a sensing line common to the gauge and associated pressure switch when a technician opened the gauge isolation valve. The low pressure condition resulted in pressure switch actuation on low pressure and was the direct cause of the turbine generator runback. Corrective actions include coding the pressure gauge calibration as an outage task, revising plant procedures, and training of plant personnel to the lessons learned from this event. The safety significance of this event is considered to be small. This event is being reported in accordance with 10 CFR 50.73(a)(2)(iv)(A) as any event or condition that resulted in a manual or automatic actuation of the reactor protection system.
4402012002 | Perry | 06/11/2012 | 08/02/2012 | ML12228A28 | <strong>Inoperable High Pressure Core Spray System Results in Loss of Safety Function</strong><br /><i>Abstract:&nbsp;</i>On June 11, 2012, at 0852 hours, with the plant in Mode 1 and the reactor operating at 73 percent of rated thermal power, plant operators determined that the High Pressure Core Spray (HPCS) system was inoperable. The HPCS system was inoperable due to the Division 3 DC Electrical Power Subsystem being declared inoperable at 0852 hours. The cause of the event was the failure of a High Voltage Shut Down (HVSD) board in the Unit 1 Division 3 Normal Battery Charger. The Division 3 DC Electrical Power Subsystem was declared inoperable as a result of this failure. The HPCS system was subsequently declared inoperable in accordance with Technical Specifications. The Division 3 Reserve Charger was placed in service. The Division 3 DC Electrical Power Subsystem and the HPCS system were declared operable at 1245 hours. The HVSD boards in the Unit 1 Division 3 and Unit 2 Division 3 Normal Battery Chargers will be replaced with boards that are not susceptible to the identified failure mode. The safety significance of this event is considered to be small. This event is reported in accordance with 10 CFR 50.73(a)(2)(v)(D) as a condition that could have prevented the fulfillment of the safety function of a system needed to mitigate the consequences of an accident.
4432012001 | Seabrook | 07/18/2012 | 09/13/2012 | ML12262A51 | <strong>Inadequate Testing of Certain Emergency Feedwater Actuation System Relays</strong><br /><i>Abstract:&nbsp;</i>On July 18, 2012, during operation at approximately 85% power, while performing an extent of condition review for a previously identified missed surveillance, station personnel identified that the response time for starting and loading of the motor-driven emergency feedwater pump (EFW) pump (FW-P-37-B) had not been adequately tested, resulting in a condition prohibited by the Technical Specifications (TS). The instrumentation that actuates the motor-driven EFW pump on steam generator (SG) low-low water level includes Solid State Protection System master relay K515 and slave relay K640. Surveillance testing has not verified the response times of these relays since initial testing in 1986. Therefore, the response time for EFW actuation on low-low SG level has not been adequately tested as required by TS 3.3.2, Engineered Safety Features Actuation System Instrumentation. The event resulted from ineffective methods utilized in the mid 1980's to verify that surveillance test procedures ensured compliance with the TS. The corrective actions for this condition will include development of a procedure that verifies response time for actuation of the motor-driven EFW pump following a low-low-SG water level and measurement of the response time during the refueling outage in the fall of 2012. No adverse consequences resulted from this event.
4432012002 | Seabrook | 09/25/2012 | 11/08/2012 | ML12319A07 | <strong>Inadequate Testing of Response Time for Reactor Trip Breakers</strong><br /><i>Abstract:&nbsp;</i>On September 25, 2012 with the unit in a refueling outage and defueled, station personnel, while reviewing a design change for installation of new circuit boards in the solid state protection system, identified a deficiency in the procedure that performs response time testing of the reactor trip breakers (RTB). The RTB have two diverse trip methods: the undervoltage circuit and the shunt trip circuit. When a RTB is opened through the shunt trip circuit, two coils (STA and SH TR) must function in order to open the breaker. A review of the existing test method found that the shunt trip circuits for both RTB had not been adequately tested. Further, a review of previous revisions of the surveillance procedures concluded that the response time of the shunt trip circuit had never been adequately tested. This event is similar to and has the same cause as the inadequate time response testing reported in LER 2012-001. The cause of both events was ineffective methods utilized in the mid 1980's to verify that surveillance test procedures ensured compliance with the TS. The corrective actions for this condition included revising the surveillance procedure and obtaining response times, which were found to be within acceptable limits. A review of the adequacy of time response testing is ongoing to address the extent of condition. No adverse consequences resulted from this event.
4432012003 | Seabrook | 09/14/2012 | 11/08/2012 | ML12319A07 | <strong>Reactor Trip due to Circuit Board Failure That Closes Feed Regulating Valve</strong><br /><i>Abstract:&nbsp;</i>On September 14, 2012 at 8:25 pm while operating at approximately 85% power, Seabrook Station experienced an automatic reactor trip on low steam generator (SG) water level. The failure of a printed circuit board in the 7300 process control system caused the feedwater regulating valve for SG-C to close. As a result, the water level in SG-C decreased to the low level trip setpoint and initiated an automatic reactor trip. The emergency feedwater system actuated on low SG level, and plant equipment functioned as expected. No adverse consequences resulted from this event. The root cause of the event was the failure of an internal component on a printed circuit board (manual nuclear tracking driver board) in the 7300 control system. The corrective actions included replacing the failed circuit card and three additional cards in the same instrument loop.
4432012004 | Seabrook | 10/31/2012 | 04/22/2013 | ML13115A26 | <strong>Manual Actuation of the Service Water Cooling Tower</strong><br /><i>Abstract:&nbsp;</i>On October 31, 2012, during operation at approximately 48% power, the operators manually initiated a tower actuation (TA), which transferred the cooling water source for the train-A service water (SW) loop from the ocean to the cooling tower. The Atlantic Ocean serves as the normal ultimate heat sink; however, if the normal supply of cooling water from the ocean is unavailable, a mechanical draft cooling tower serves as the ultimate heat sink. A strainer is provided in each SW train to prevent shells and mussels from fouling the heat exchangers. During this event, SW was operating on the ocean and differential pressure across the train-A SW strainer increased above the alarm setpoint of 10 psid. In response to the high differential pressure, the operators initiated a TA in accordance with station procedures to transfer train-A SW operation to the cooling tower. Train-A SW operated on the cooling tower until 0430 on November 1, 2012, when the SW train was transferred back to the ocean.<br><br> The root cause of the event is the lack of a structured process to ensure ongoing equipment monitoring following a storm for systems sensitive to changing environmental conditions. The corrective action for this event is creation of a procedure to address the affects of severe weather on the SW screens (both during the storm and after). No adverse consequences resulted from this event.
4432012005 | Seabrook | 12/07/2012 | 02/04/2013 | ML13042016 | <strong>Service Water Cooling Tower Low Water Level</strong><br /><i>Abstract:&nbsp;</i>On 12/7/12, with the plant in Mode 1 at 100% power, Service Water Cooling Tower level was discovered to be below the Technical Specification (TS) limit of 42.15 feet. Following discovery, a fast fill of the cooling tower was performed to restore water level above the TS limit. It was subsequently determined that cooling tower water level was below the TS limit for approximately 17 days. No adverse consequences resulted from this event and no safety system functional failure occurred since there was sufficient water in the cooling tower to maintain the cooling tower functional at all times. The cause of the event was failure to use diverse means to validate the accuracy of a potentially inaccurate cooling tower level indicator. Corrective actions included restoring level in the Service Water Cooling Tower and increasing the use of operator fundamentals.
4452012001 | Comanche Peak 1, Comanche Peak 2 | 03/01/2012 | 04/30/2012 | ML12128A42 | <strong>Unanalyzed Condition Discovered for the Normally Open Battery Room Fire and Cable Spread Room Doors Close on Momentary Loss of Power</strong><br /><i>Abstract:&nbsp;</i>On 3/1/2012, at 1353 hours, an issue was identified with the doors for the safety related battery rooms and their normal position. Several doors to the battery rooms are held open via electromagnetic door devices. At the time, it was thought that there was no uninterruptible power to the door mechanisms, and that all the doors are expected to close in the event of a loss of offsite power (LOOP). Inadvertent closure of the doors following a momentary loss of power prevents their design function of venting hydrogen from the battery rooms and providing tornado venting pathways in the building. Compensatory measures were taken to secure the doors open to maintain the hydrogen purging and tornado venting functions. A roving fire watch was implemented to comply with the fire protection function of the doors. As an extent of condition on 3/12/12, the cable spread room (CSR) doors were also identified to utilize the same design and electrical supply configuration as the battery room doors. The CSR is located above the battery rooms in the Electric and Control (E&C) Building. Contingency actions were put in place to secure the CSR doors open and implement a fire impairment in the event of a tornado risk. On 4/11/12, it was discovered that the battery room and CSR doors have small battery backup units which could sustain the doors with adequate power to maintain their position for 45 seconds sufficient to allow AC power to be restored through the Emergency Diesel Generators (EDGs) during a tornado. However, the backup units were found to be in a state of degradation, challenging the ability of the backup batteries to maintain their power supply to the door hold-open devices during a tornado event. No recent preventive maintenance work orders exist for the inspection or replacement of these units. There were no actual safety consequences impacting the plant or public safety as a result of these events. The cause was a design process legacy issue, and current design processes are significantly different from those in place during early operation of CPNPP. The specific conditions have been addressed in the corrective action program and, along with current programs and practices, are adequate to prevent future occurrences. All times in this report are approximate and Central Time unless noted otherwise.
4452012002 | Comanche Peak 1, Comanche Peak 2 | 06/20/2012 | 08/16/2012 | ML12240A05 | <strong>Failure of Safety Related Breaker Control Devices due to a Common Cause</strong><br /><i>Abstract:&nbsp;</i>Between October 2009 and March 2012, Comanche Peak Nuclear Power Plant (CPNPP) Units 1 and 2 experienced three failures of safety related breaker control devices that caused Technical Specification equipment to become inoperable. Two of the failures were on Unit 1 and one of the failures was on Unit 2. On June 14, 2012, a failure analysis concluded that these failures were caused by a material weakness of the control devices' contact carrier frames due to a manufacturing defect. Less than adequate control of the manufacturing process increased the susceptibility to shock loading of the cured phenolic material used to make the contact carrier frames. On June 20, 2012, CPNPP determined that this condition was reportable per 10CFR50.73(a)(2)(ix)(A) and 10CFR21. Corrective actions include replacement of the potentially affected safety related breaker control devices, development of receipt inspection testing criteria to be used for breaker control devices, issuing an Operating Experience Report on this event, and notification of the breaker vendor (ABB Inc.). All times in this report are approximate and Central Time unless noted otherwise.
4452012003 | Comanche Peak 1 | 11/02/2012 | 12/19/2012 | ML13009A10 | <strong>Unit 1 Manual Reactor Trip Due To Reactor Coolant Pump Low Oil Level</strong><br /><i>Abstract:&nbsp;</i>On November 2, 2012, Comanche Peak Nuclear Power Plant (CPNPP) Unit 1 was in Mode 1 operating at 100 percent power. At 0142 hours, the Unit 1 reactor was manually tripped due to rising Reactor Coolant Pump (RCP) 1-04 motor lower radial bearing temperature and a bearing oil level alarm. All control rods fully inserted, both Motor Driven Auxiliary Feedwater Pumps were manually started, and the Turbine Driven Auxiliary Feedwater Pump automatically started as a result of the reactor trip. The RCP 1-04 motor experienced a lower radial bearing failure which required a Unit 1 manual reactor trip. The lower radial bearing failure was caused by overheating due to loss of oil in the oil reservoir. The loss of oil was due to slow leakage from a degraded elastomeric coupling within the RCP internal oil supply system. The oil supply coupling connection degraded sufficiently to allow the reservoir level to decrease and prevent adequate lower radial bearing lubrication. The seal degraded because a preventative maintenance (PM) activity had not been created or implemented to periodically change these sub-components. Immediate corrective actions included replacement of the RCP 1-04 lower radial bearing and cooling line coupling, seals, and gaskets, and changing the setpoint on the oil level alarm to account for dynamic oil levels within the lower reservoir which will assure a more timely alarm. As a part of the CPNPP Corrective Action Program, PMs will be developed and implemented to evaluate and replace perishable "soft" subcomponents to ensure that those subcomponents will perform their design function throughout their service life and do not adversely affect equipment operation. All times in this report are approximate and Central Time unless noted otherwise.
4462012001 | Comanche Peak 2 | 02/21/2012 | 04/23/2012 | ML12124A27 | <strong>PORV Block Valve Inoperable for Longer than Allowed by Technical Specifications</strong><br /><i>Abstract:&nbsp;</i>On April 8, 2011, during the Unit 2 twelfth refueling outage, an in-service surveillance on the Pressurizer 2-01 Power Operated Relief Valve (PORV) 0456 Block Valve Motor Operator did not meet the minimum required stem thrust in the closed direction. The PORV block valve surveillance failure was caused by degraded valve stem lubrication at the stem/stem nut area. Immediate corrective actions included removing the degraded grease from the affected PORV Block valve, applying new grease, and successfully performing the surveillance test on the valve. Work order instructions and procedure MSE-P0-8349 will be revised to provide steps for properly lubricating the PORV Block Valve Motor Operators. On February 21, 2012, Comanche Peak Nuclear Power Plant conservatively determined that the affected block valve had likely been inoperable in the past for longer than allowed by Technical Specifications and that this event was reportable per 10CFR50.73(a)(2)(i)(B) "Any operation or condition which was prohibited by the plant's Technical Specifications." All times in this report are approximate and Central Time unless noted otherwise.
4462012002 | Comanche Peak 2 | 11/17/2012 | 01/16/2013 | ML13029A59 | <strong>Unit 2 Automatic Reactor Trip due to Low Steam Generator Water Level</strong><br /><i>Abstract:&nbsp;</i>On November 17, 2012, Comanche Peak Nuclear Power Plant (CPNPP) Unit 2 was in Mode 1 operating at 100% power. At 1023 hours, the Unit 2 reactor automatically tripped due to low steam generator water level. All control rods fully inserted and all three Auxiliary Feedwater pumps started as expected as a result of the reactor trip. All systems responded normally during and following the event. The cause of this event was the planning process did not provide instructions for mounting the air pressure regulator for the Heater Drain pump discharge valve. The valve was reassembled without properly supporting the pressure regulator which allowed vibration to occur in the tubing. This eventually caused a swage-lok fitting fatigue failure which resulted in the loss of air and closure of the Heater Drain pump discharge valve. This resulted in the loss of one main Feedwater pump and an automatic reactor trip on low steam generator water level. Immediate corrective actions included replacement of the broken fitting and mounting of the air pressure regulator to the actuator of the Heater Drain pump discharge valve. As a part of the CPNPP Corrective Action Program, procedures will be revised to ensure that the planning process contains specific instructions for installation of an alternate part if required. All times in this report are approximate and Central Time unless noted otherwise.
4542012001 | Byron 1, Byron 2 | 01/30/2012 | 09/28/2012 | ML12272A35 | <strong>Unit 2 Loss of Normal Offsite Power and Reactor Trip and Unit 1 Loss of Normal Offsite Power Due to Failure of System Auxiliary Transformer Inverted Insulators</strong><br /><i>Abstract:&nbsp;</i>Two events involving the loss of normal offsite power occurred on January 30, 2012 for Unit 2 and February 28, 2012 for Unit 1. The January 30, 2012, event was initiated by a mechanical failure of a 345 kilovolt (kV) Ohio Brass inverted porcelain insulator on the System Auxiliary Transformer (SAT) 242-1/2 A-Frame structure in the Switchyard resulting in an open phase non-faulted condition on phase C. The 4.16 kV Engineered Safety Feature (ESF) buses undervoltage protection scheme did not automatically switch over to the emergency Diesel Generators (DG). However, the 6.9 kV buses powering the Reactor Coolant Pumps did recognize the undervoltage condition and as designed generated a reactor trip signal. The 4.16 kV ESF buses remained energized with a voltage unbalance. Loads energized by SAT 242-1/2 tripped off due to a phase A overcurrent condition. Operators diagnosed the situation and manually isolated SAT 242-1/2 from the 4.16 kV ESF buses. The 2A and 2B Diesel Generators (DG) started and energized the 4.16 kV ESF buses. Loads sequenced onto the buses as designed. The February 28, 2012 event was also initiated by a failed inverted porcelain insulator. In this event, the 4.16 kV ESF buses did sense fault condition and separated SAT 242-1/2 from the 4.16 kV buses. The 1A and 1B DGs started and energized the 4.16 kV ESF buses. The insulator failures were caused by service propagation of a large manufacturing material defect. The defect was characterized as poorly vitrified porcelain, which contained a high density of porosity and micro-cracks. All Ohio Brass inverted insulators associated with both Unit's SATs and Main Power transformers have been replaced with insulators from a different manufacturer.
4542012002 | Byron 1 | 04/21/2011 | 06/28/2013 | ML13179A45 | <strong>One Train of Containment Cooling System Inoperable Longer Than Allowed by Technical Specifications due to Inadequate Work Instructions</strong><br /><i>Abstract:&nbsp;</i>On March 29, 2012, an inspection was in progress for a water leak inside containment that was causing elevated containment sump levels. The inspection involved looking for leaks within the Reactor Coolant Fan Coolers (RCFC) plenums. At 1217 hours, Technical Specifications (TS) 3.6.6, "Containment Spray and Cooling Systems," Condition C was entered for the 1A Containment Cooling (VP) train and mechanics proceeded to remove the 1A Reactor Containment Fan Cooler (RCFC) plenum access panel to inspect within plenum for leaks. During the inspection, an interior access panel (4 by 6 feet) was discovered not to be installed, as required. Shift supervisor was immediately notified and the 1A VP train remained in TS 3.6.6 Condition C pending resolution. The interior panel and plenum access panels were replaced and TS 3.6.6 Condition C exited at 1308 hours on March 29, 2012. The function of this interior panel is to ensure all containment air is directed across the Essential Service Water (SX) coils for cooling. During accident conditions, this opening would allow some of the air to bypass the cooling coils and consequently, not be cooled. An investigation revealed the interior panel was removed on March 15, 2011, during Unit 1's refueling outage for maintenance activities, and was inadvertently not re-installed on April 15, 2011, after maintenance completion. The cause of the event was inadequate level of details in the work package that removed and re-installed the RCFC access panels. Corrective actions include providing unique equipment identification number for each RCFC panel and to include this information on the model work package used for future RCFC panel/s removal.
4542012003 | Byron 1, Byron 2 | 06/04/2012 | 02/22/2013 | ML13053A37 | <strong>Containment Area Radiation Monitors Inoperable for Longer than Allowed by Technical Specifications due to Inadequate Procedure Controls</strong><br /><i>Abstract:&nbsp;</i>In accordance with Technical Specifications (TS) 3.3.6, "Containment Ventilation Isolation Instrumentation," the setpoints for the containment Area Radiation (AR) monitors 1/2AR011J and 1/2AR012J are required to be set less than or equal to 10 mR/hr above the background radiation level in containment. The procedural controls for installing these setpoints for these monitoring channels did not account for the lowering background radiation level that occurs while reactor power is being reduced. Consequently, during a power reduction, with the setpoint constant and background levels reducing, the TS setpoint limit of being less than or equal to 10 mR/hr above background would be exceeded and would make the channel inoperable. Once Mode 5 was reached the setpoints were adjusted to shutdown background levels. In addition, when returning to power from an outage, the setpoints for full power operations were installed while in Mode 5 based on anticipated full power background levels. TS required actions and completion times were inadvertently exceeded for both radiation monitors being inoperable during Unit startup and power ascension. The cause of the condition was inadequate procedural controls to ensure compliance with the TS setpoint requirements for 1/2AR011J and 1/2AR012J radiation monitors. Procedural controls were added to ensure 1/2AR011J and 1/2AR12J setpoints are adjusted as necessary to ensure compliance with TS during changing containment background radiation conditions.
4542012004 | Byron 1 | 09/14/2012 | 11/12/2012 | ML12318A11 | <strong>Reactor Pressure Vessel Head Control Rod Drive Mechanism Penetration Nozzle Weld Repair Surface Indications</strong><br /><i>Abstract:&nbsp;</i>During the Byron Station Unit 1 spring 2011 Refueling Outage, EGC performed volumetric and surface examinations of the reactor Vessel Head Penetration (VHP) nozzles in accordance with 10 CFR 50.55a(g)(6)(ii)(D). Examination results for the VHPs 31, 43, 64 and 76 did not meet the applicable acceptance criteria and therefore these nozzles required repair prior to return the reactor head to service. The flaws were repaired using the weld overlay method prior to returning the reactor head to service. During the examinations of the weld overlay repairs in the subsequent refueling outage, fall of 2012, multiple rounded indications were found on the weld material of VHP 31 and 43. One indication of each penetration exceeded acceptance criteria. These indications are the result of surface irregularities on the weld material from the initial installation of the repair in spring 2011. The indications were reduced to acceptable size by mechanical means. No additional welding was necessary.
4552012001 | Byron 2 | 02/06/2012 | 04/06/2012 | ML12090A49 | <strong>Manual Reactor Trip During Power Ascension due to Steam Generator Level Approaching Turbine Trip Setpoint Caused by an Overly Complex Startup Procedure</strong><br /><i>Abstract:&nbsp;</i>At approximately 1700 hours, on February 6, 2012, the Unit 2 Operating crew was in the process of conducting a unit startup in accordance with startup procedures. The reactor was at approximately 25% power. During the step that switched Feedwater (FW) flow from the upper nozzle of the 2C Steam Generator (SG) to its lower nozzle via the 2C FW Isolation Valve (FWIV), the Reactor Operator controlling the SG levelsmanually was also focused on maintaining subcooling in the tempering line and satisfying water hammer interlocks. Consequently, the RO was not closely monitoring the 2C SG level increase. Another assisting RO recognized the level increase was approaching the high level setpoint and informed the RO. Subsequently, the RO reduced FW flow; however, the level continued to increase and approach the high level setpoint of 80.8% (i.e., P-14), which causes an automatic turbine trip and FW isolation. In anticipation of reaching this setpoint, the Unit 2 Senior RO directed a manual reactor trip at 1719 hours. Almost simultaneous to the manual reactor trip the 2C SG level reached the P-14 setpoint. The reactor trip signal and P-14 both generate an automatic turbine trip and FW isolation. The turbine tripped and FW isolated, as designed. In accordance with reactor trip response procedures, the 2A and 2B Auxiliary Feedwater pumps were started. The cause of the event was determined to be an overly complex startup procedure and weak Operating crew performance. The startup procedure will be revised and personnel performance issues were remediated.
4562012001 | Braidwood 1 | 04/12/2012 | 06/11/2012 | ML12163A52 | <strong>Two Main Steam Safety Valves Failed Pre-outage Setpoint Testing due to Abnormal Spring Geometry</strong><br /><i>Abstract:&nbsp;</i>On April 11, 2012, pre-outage testing was initiated for the main steam safety valves for their setpoint verification per Technical Specification (TS) 3.7.1, Main Steam Safety Valves. During the testing, two of the valves (1MS015D on April 11, 2012 and 1MS014D on April 12, 2012) failed to meet the as-found set pressure acceptance criteria. When each valve (1MS015D and 1MS014D) was identified as outside the acceptance criteria, the appropriate Limiting Condition for Operation (LCO) was entered, the valve was returned to its operable status by returning the setpoints within the TS surveillance requirements, and the LCO was exited. The apparent cause of the 1MS015D and 1MS014D valves failing their performance tests was determined to be abnormal spring geometry. Contributing causes were determined to be spindle wear and steam leakage across the disc seat area. Corrective actions included refurbishing the 1MS015D and 1MS014D valves. This event is reportable in accordance with 10 CFR 50.73(a)(2)(i)(B), any operation or condition prohibited by the plant's Technical Specifications. This event is also being reported in accordance with 10 CFR 50.73(a)(2)(vii) for any event where a single cause or condition caused at least two independent trains or channels to become inoperable in a single system designed to mitigate the consequences of an accident.
4562012002 | Braidwood 1 | 04/23/2012 | 06/22/2012 | ML12174A22 | <strong>Reactor Pressure Vessel Head Control Rod Drive Mechanism Penetration Nozzle Weld Indication Attributed to Primary Water Stress Corrosion Cracking</strong><br /><i>Abstract:&nbsp;</i>During the Braidwood Unit 1 spring 2012 refueling outage, scheduled Volumetric Examination of the upper reactor pressure vessel (RPV) [AB] head penetrations was performed in accordance with the Electric Power Research Institute Performance Demonstration Program by the implementation of 10 CFR 50.55a and in accordance with American Society of Mechanical Engineers Section XI Code Case N-729-1 as amended by 10 CFR 50.55a(g)(6)(ii)(D). On April 23, 2012, at approximately 0100, an indication was discovered in Penetration 69. The flaw was located on the outside diameter of the penetration tube and was axially oriented with a linear extent of 0.600 inches and a through wall depth of 0.216 inches, approximately 33.5% through wall. The embedded flaw was subsequently repaired in accordance with NRC approved WCAP 15987, Revision 2-P-A, and WCAP 16401-P Revision 0. The apparent cause of the flaw is attributed to primary water stress corrosion cracking. Corrective actions included repairing the indication in Penetration 69 and revising the frequency of the Unit 1 Bare Metal Visual Exam and the Volumetric Exam to every refueling outage. This event is reportable in accordance with 10 CFR 50.73(a)(2)(ii)(A), any event or condition that resulted in the condition of the nuclear power plant, including its principal safety barriers, being seriously degraded.
4562012003 | Braidwood 1, Braidwood 2 | 06/03/2012 | 02/18/2013 | ML13051A00 | <strong>Fuel Handling Incident Area Radiation Monitors Inoperable due to Incorrect Alarm Setpoints</strong><br /><i>Abstract:&nbsp;</i>On May 30, 2012, and June 1, 2012, setpoint adjustments on fuel handling incident area radiation monitors 1AR011J and 1AR012J were performed. On June 3, 2012 at 1200, Operations declared 1AR011J Inoperable due to the detector drifting high, and the required compensatory actions were implemented. At 1230, during a review of 1AR011J and 1AR012J performance, Operations determined that the setpoint for 1AR012J was not set in accordance with Technical Requirements Manual 3.3.p and Technical Specification (TS) 3.3.6. 1AR012J was declared Inoperable, and compensatory actions were implemented. On June 3, 2012, at 1621, 1AR012J setpoints were restored and the monitor was declared Operable. On June 6, 2012 at 1540, 1AR011J was repaired and returned to Operable status. The root causes of this event were determined to be: 1) Operations used the incorrect procedure attachment and did not validate the need to adjust 1AR012J setpoint; and 2) a lack of procedural guidance or alarm response guidance that checks if the 1/2AR011J or 1/2AR012J monitors have operable setpoints. Corrective actions to prevent recurrence included addressing personal accountability for the isolated human performance error during setpoint adjustments of 1AR012J, and revising procedures to include guidance to trigger implementing setpoint changes for 1/2AR011J and 1/2AR012J (these actions are complete).
4562012004 | Braidwood 1, Braidwood 2 | 07/07/2012 | 12/13/2012 | ML12349A17 | <strong>Notice of Enforcement Discretion Received for Ultimate Heat Sink Temperature Exceeding Technical Specifications Requirements due to Prolonged Hot Weather</strong><br /><i>Abstract:&nbsp;</i>From July 4 through July 6, 2012, hot weather and drought conditions affected the northern Illinois area and resulted in elevated water temperatures in Braidwood Station's ultimate heat sink. At 1556 on July 7, 2012, the average discharge temperature of the running essential service water pumps exceeded 100 degrees F, and Technical Specification (TS) 3.7.9, "Ultimate Heat Sink (UHS)," Condition A was entered. Condition A requires that with the UHS inoperable, Units 1 and 2 be placed in Mode 3 in 6 hours and Mode 5 in 36 hours. Enforcement Discretion was requested to extend the Completion Time of Required Action A.1 by an additional 18 hours and to increase the limit of the average water temperature of the UHS in Surveillance Requirement 3.7.9.2 to 102 degrees F to allow continued operation of Braidwood Station, Units 1 and 2, with the average water temperature of the UHS > 100 degrees F but <\= 102 degrees F for 24 hours. At 1705 on July 7, 2012, approval of the request was verbally granted by the NRC. At 2018 on July 7, 2012, the UHS temperature was below 99.9 degrees F, and TS 3.7.9 Condition A was exited. There were no safety consequences impacting plant or public safety as a result of this event. This event is reportable under 10 CFR 50.73(a)(2)(v)(B), any event or condition that could have prevented the fullfillment of the safety function of structures or systems that are needed to remove heat.
4562012005 | Braidwood 1 | 12/13/2012 | 02/11/2013 | ML13042028 | <strong>Incorrect Procedure Guidance due to a Lack of Technical Rigor Resulted in Unplanned Inoperability of the 1A and 1B Emergency Diesel Generators</strong><br /><i>Abstract:&nbsp;</i>On December 13, 2012, it was questioned whether both emergency diesel generators (DGs) would be considered inoperable if one diesel oil storage tank (DOST) room water tight door was impaired because the door between the DOST rooms was not water tight. The Plant Barrier Impairment Program procedure contained a pre-evaluated compensatory action for impairment of one of the DOST room water tight doors, which required declaring only the affected emergency diesel generator (DG) inoperable. A subsequent technical review determined that the compensatory note was incorrect and that both DOST rooms would be vulnerable to flooding with the water tight door for one DOST room impaired. A review of prior plant barrier impairments identified one instance in the previous three years where only one DG was declared inoperable while the corresponding water tight door was impaired. The cause of the event was determined to be inadequate technical rigor, which led to improper compensatory measures being included in the Plant Barrier Impairment Program procedure. The corrective action was to revise the procedure to consider both trains of the affected unit's DGs inoperable when either DOST water tight door was impaired.
4582012001 | River Bend | 05/08/2012 | 11/14/2012 | ML12340A06 | <strong>Operations Prohibited by Technical Specifications Due to Inoperability of Division 3 Diesel Generator</strong><br /><i>Abstract:&nbsp;</i>On May 8, 2012, plant engineers confirmed that the lubricating oil in the Division 3 diesel generator (DG) was contaminated with fuel at a level that required its replacement. At the time of this discovery, a plant heat-up was in progress in preparation for return to service following a maintenance outage. The oil sample that yielded these results had been drawn on April 25, and shipped off-site for vendor analysis. Plant engineers evaluated the trends of prior lubricating oil samples taken prior to May 8, and determined that the DG had become incapable of performing its design safety function on approximately October 28, 2011. It was concluded that this date was the likely starting point of the internal fuel leak that contaminated the oil. That fuel leak likely resulted from gasket damage that occurred during work on the fuel injectors. On May 8, the DG was removed from service in order to change the lubricating oil and repair the fuel leak. It has been determined that, in the as-found condition, the DG remained capable of fulfilling the mission time assumed by the station's probabilistic risk analysis. Enhanced work instructions for fuel jumper installation have been added to the vendor manual and to model work orders. This condition is being reported in accordance with 10CFR50.73(a)(2)(i)(B) as operations prohibited by Technical Specifications.
4582012002 | River Bend | 05/21/2012 | 07/20/2012 | ML12209A09 | <strong>Automatic Reactor Scram due to Low Main Condenser Vacuum Resulting from Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>On May 21, 2012, at 2:52 p.m., while the plant was operating at 100% power, an automatic reactor scram occurred due to a partial loss of vacuum in the main condenser. This condition initially caused a trip of the main turbine, and the fast closure of the turbine control valves provided the actuation signal to the reactor protection system (RPS). Main condenser vacuum remained within the operating limits for use of the main turbine bypass valves, thus reactor pressure was automatically controlled following the initial transient. The reactor feedwater system remained inservice. The decrease in main condenser vacuum resulted from the loss of two of four circulating water pumps. This condition was caused by the failure of a splice in one of three 13.8kV cables providing power to half of the 4160V switchgear at the circulating water structure. The splice failure resulted in a small fire inside a manhole located outside the protected area. The plant fire brigade confirmed the fire was out within approximately 24 minutes of the onset of the event. Six reactor safety-relief valves actuated in response to the main turbine trip. The reactor core isolation cooling (RCIC) system steam supply valve automatically closed due to a false high-flow signal from the steam flow sensors. The system was restored to its standby configuration at 5:36 p.m. No plant parameters requiring the automatic actuation of the RCIC system were exceeded during the event. The failed splice was replaced, and the other cables in the circuit were tested for integrity, resulting in the replacement of one other splice. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an automatic actuation of the RPS system. There were no safety-related systems out of service at the time of the event.
4582012003 | River Bend | 05/24/2012 | 07/23/2012 | ML12209A09 | <strong>Reactor Scram following a Loss of Main Reactor Feedwater Pump due to Electrical Fault</strong><br /><i>Abstract:&nbsp;</i>On May 24, 2012, at 3:40 p.m. CDT, a manual reactor scram was initiated in response to the loss of the running reactor feedwater pump. The plant was operating at approximately 32% power. The reactor core isolation cooling system was manually started to provide high pressure makeup to the reactor. The high pressure core spray system was manually started during the recovery from the event, but was not aligned to the reactor vessel. An electrical transient caused by the failure of a lockout relay resulted in the main supply breaker to the "B" 13.8kv switchgear to trip. Reactor recirculation pump "B" tripped due to the loss of its power source; the "A" reactor recirculation pump continued to operate in slow speed. The electrical transient also caused a loss of power to all main condenser circulating water pumps and normal service water pumps, necessitating the manual closure of the main steam isolation valves. The standby service water system actuated as designed in response to low normal service water pressure. The operators manually operated selected SRVs for reactor pressure control and for reactor cooldown. Personnel in the turbine building reported the presence of smoke in the area of the feedwater pumps, but no actual fire was observed. There were no safety-related systems out of service at the time. This event is being reported in accordance with 10CFR50.73(a)(2)(iv)(A) as an actuation of the reactor protection system and the standby servicewater system. This event was of low safety significance to the health and safety of the public.
4582012004 | River Bend | 10/06/2012 | 11/29/2012 | ML12348A00 | <strong>Operations Prohibited by Technical Specifications due to Wiring Error in Safety-Related Circuit Breaker</strong><br /><i>Abstract:&nbsp;</i>On October 6, 2012, while the plant was operating at 100 percent power, it was discovered that one of the safety-related fans in the standby service water cooling tower would not start from the remote shutdown panel. The initial investigation determined that the failure was due to incorrect maintenance that had been performed on May 3, 2011, when a relay in the fan motor breaker was miswired during re-installation after bench testing. This condition caused the fan to have been inoperable since that time with respect to the function of the Remote Shutdown System, as governed by Technical Specification 3.3.3.2. The investigation of this event found that control of lifted leads and application of post-maintenance testing requirements were ineffective. Revisions to the applicable maintenance procedures have been planned / completed to address the causes of this event. This event is being reported in accordance with 10 CFR 50.73(a)(2)(i)(B) as operations prohibited by technical specifications.
4612012001 | Clinton 1 | 09/02/2012 | 10/26/2012 | ML12312A46 | <strong>Loss of Secondary Containment Differential Pressure Due to Transformer Trip</strong><br /><i>Abstract:&nbsp;</i>At 2204 on September 2, 2012, the Emergency Reserve Auxiliary Transformer (ERAT) transferred unexpectedly to the Reserve Auxiliary Transformer, causing a trip of the Fuel Pool Cooling and Cleanup system pump 'A' and trip of the Fuel Building Ventilation system. Secondary Containment differential pressure increased above the Technical Specification 0.25 inches vacuum and was restored at 2219 on September 2, 2012, when the Standby Gas Treatment System was manually started. This event is being reported as a condition that could have prevented the fulfillment of a safety function per 10 CFR 50.73(a)(2)(v)(C). The trip of the ERAT was caused by a spurious station ground on one of the ERAT sudden pressure seal-in relay cards (63SPX) caused by a latent design error. The ground revealed itself when Electrical Maintenance technicians were performing circuit checks to determine the source of a ground indicated on the 125 Volts Direct Current motor control center 1F. A temporary modification was implemented to disable the seal-in trip feature of the 63SPX relay card.
4612012002 | Clinton 1 | 03/01/2012 | 11/27/2012 | ML12341A23 | <strong>Division 1 Emergency Diesel Generator Supply Air Damper Failure</strong><br /><i>Abstract:&nbsp;</i>At 1212 on March 1, 2012, the Division 1 Emergency Diesel Generator (EDG) was started for monthly surveillance testing. At 1215, Operators in the EDG room reported a lack of expected air flow in the room. The EDG Room supply air fan automatically started as expected, as evidenced by Main Control Room (MCR) and field indications. Investigation found the supply damper-to-hydramotor coupling disconnected, resulting in the supply damper remaining in the closed position. The cause of the event was a failure to ensure the lock nut on the coupling was sufficiently tightened during the previous hydramotor replacement. Corrective action taken was to revise a site procedure to include supervisory oversight on the assembly of the coupling and allow the use of an engineered adhesive (i.e., Loctite®) for coupling lock nuts. The Division 1 EDG was previously run for a monthly surveillance test on January 25, 2012 with no problems noted. This date is the last date for which there is firm evidence that the supply air damper coupling was connected, had a demand occurred. Therefore, this event is being reported as a condition prohibited by Technical Specifications (TS) due to the EDG being inoperable for a period of time that greater than allowed by TS per 10 CFR 50.73(a)(2)(i)(B). This event is also being reported as a condition that could have prevented the fulfillment of a safety function per 10CFR 50.73(a)(2)(v)(B) due to the Division 2 EDG being inoperable for a period of the time the Division 1 EDG was inoperable.
4612012003 | Clinton 1 | 11/23/2012 | 01/17/2013 | ML13031A00 | <strong>Breaker Failure Leads to Loss of Safety Function and System Start</strong><br /><i>Abstract:&nbsp;</i>On 11/23/12 an operator reported to the Main Control Room that the Control Room (VC) B Chiller Breaker was cycling with no demand signal and attempted numerous times to open the breaker with no success. In response, the Control Building Unit Sub B Cubicle was manually tripped causing the following isolations/actuations: a loss of power to Division 2 Instrument Air System and Service Air System containment isolation valves causing the valves to isolate; and a loss of power to Fuel Building (VF) system ventilation Division 2 isolation dampers resulting in a trip of the VF system. High Pressure Core Spray (HPCS) became inoperable based on inoperability of the room cooler for the associated Division 4 inverter and battery charger. Following the loss of power to the VF isolation dampers, secondary containment differential pressure became positive. Subsequently, power was restored to Control Building Unit Sub B and HPCS was restored to operable. The Standby Gas Treatment System was manually started and secondary containment differential pressure was restored. An automatic start of Division 2 Shutdown Service Water (SX) system also occurred during this event. The cause of this event was the failure of the VC B Chiller Breaker closing spring charging mechanism. The breaker that failed has been replaced and the failed breaker has been sent to an offsite laboratory for failure analysis.
4822012001 | Wolf Creek | 01/13/2012 | 04/09/2012 | ML12109A04 | <strong>Failure of 345 kV Switchyard Breaker due to Internal Fault Resulting in Reactor Trip and Coincident Loss of Offsite Power</strong><br /><i>Abstract:&nbsp;</i>On January 13, 2012, at approximately 1403 Central Standard Time (CST), the unit experienced an unplanned automatic shutdown from full power operations and a coincidental loss of offsite power. The 345-60 generator output breaker in the switchyard catastrophically failed (fault on 'C' phase) resulting in breaker operations and subsequent loss of the East 345 kV bus and a trip of the main turbine. Coincident with the loss of the East 345 kV bus, a rapid transfer of the non-safety buses from the Unit Auxiliary Transformer to the Startup Transformer occurred. After the rapid transfer, a 'B' phase differential relay trip on the Startup Transformer resulted in a loss of the West 345 kV bus and loss of offsite power. The turbine trip initiated a reactor trip. All control rods inserted into the core. All reactor coolant pumps tripped. Both diesel generators started and supplied power to the 4.16 kV engineered safety features buses. Control room operators initiated action per procedure EMG E-0, "Reactor Trip or Safety Injection," and transitioned into EMG ES-02, "Reactor Trip Response." Subsequently, a natural circulation cooldown was performed to place the unit in Mode 5.
4822012002 | Wolf Creek | 03/19/2012 | 05/17/2012 | ML12152A15 | <strong>One Train of Automatic Safety Injection Blocked During Entry into Mode 3 due to Procedural Weakness</strong><br /><i>Abstract:&nbsp;</i>On March 19, 2012, the unit was in the process of starting up from a forced outage. Procedure STS KJ-001A, "Integrated D/G and Safeguards Actuation Test - Train A," had been performed which actuated the 'A' safety injection (SI) signal. The actuation signal was subsequently reset, but the reactor trip breakers were not closed to allow permissive P-4 to be cleared allowing the 'A' train automatic SI actuation to be operable. On March 19, 2012, at 0327 Central Daylight Time (CDT), entry was made into Mode 3 with the train 'A' automatic SI actuation signal blocked. Changing from Mode 4 to 3 with an inoperable automatic SI actuation signal is prohibited by Technical Specifications. On March 20, 2012, at 0945 CDT, the reactor trip breakers were closed which enabled the train 'A' automatic SI actuation signal. The cause of the event was inadequate procedural guidance prior to making Mode changes. Procedure GEN 00-002, "Cold Shutdown to Hot Standby," was revised to ensure automatic SI actuation is operable prior to entry into Mode 4.
4822012003 | Wolf Creek | 01/14/2012 | 06/18/2012 | ML12179A21 | <strong>B Train ECCS and Containment Spray System Inoperable due to Damaged Watertight Containment Spray Pump Door Seal</strong><br /><i>Abstract:&nbsp;</i>On April 17, 2012, at 1453 Central Daylight Time, the watertight door seal for the B train Containment Spray (CS) Pump room was determined to be nonfunctional and the equipment supported by the door was inoperable. The equipment supported by the door is the B train Emergency Core Cooling System and the B train CS System. The door was repaired on April 18, 2012 at 1448 CDT. The watertight seal was replaced, welding was performed on the knife-edge of the door and the door lugs were tightened. The direct cause of this condition was due to door knife-edge damage and age degradation and hardening of the door seal. The apparent cause of this condition was a less than adequate preventative maintenance to identify potentially deficient door seals.
4822012004 | Wolf Creek | 05/09/2012 | 07/03/2012 | ML12192A54 | <strong>Two Charging Pumps Capable of Injecting into the RCS due to Inadequate Definition of Centrifugal Charging Pump in LCO 3.4.12</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2012, a Nuclear Regulatory Commission (NRC) regional inspector identified that a potential violation of Technical Specification (TS) 3.4.12, "Low Temperature Overpressure Protection (LTOP) System," occurred during the recent forced outage and in prior refueling outages. Limiting Condition for Operation (LCO) 3.4.12 requires an LTOP System shall be operable with a maximum of zero safety injection pumps and one centrifugal charging pump capable of injecting into the Reactor Coolant System (RCS). During the recent forced outage and during refueling outages, one safety related centrifugal charging pump and the non-safety related normal charging pump were capable of injecting into the RCS. The apparent cause for this potential violation is the failure to specifically define in the TS LCO that the centrifugal charging pump is an Emergency Core Cooling System (ECCS) centrifugal charging pump. A request for interpretation of TS 3.4.12 was submitted to the NRC on May 31, 2012.
4822012005 | Wolf Creek | 05/23/2012 | 07/23/2012 | ML12214A43 | <strong>Calculation Assumptions Lead to Inadequate Procedure, Resulting in LCO 3.0.3 Entry due to Non-Functional Class 1E Electrical Equipment Air Conditioning Unit</strong><br /><i>Abstract:&nbsp;</i>On June 4, 2012 at 0325 CDT, a Class 1E electrical equipment air conditioning (A/C) train was declared nonfunctional. Technical Requirement (TR) 3.7.23 allows a train to be nonfunctional if compensatory measures are established for the affected unit. During the operability determination and functionality assessment process it was determined that the operability of the associated train Class 1E electrical equipment could not be maintained without additional compensatory measures and for a limited period of time. Technical Specification (TS) Limiting Condition for Operation 3.0.3 was entered and a plant shutdown was commenced on June 6, 2012 at 0327 CDT. On June 6, 2012 at 0505, the Class 1E electrical equipment A/C train was restored to functional status and the plant returned to 100 percent power. The cause of the event was a calculation that concluded one train of air conditioning was not capable of supporting both trains of Class 1E equipment while maintaining room ambient temperatures below the maximum specified operating temperature. Control room operators have been directed to enter the applicable TS on a loss of a Class 1 E electrical equipment A/C train.
4832012001 | Callaway | 03/28/2012 | 05/23/2012 | ML12144A19 | <strong>Modification Implementation Error Adversely Impacted the Containment Cooling System</strong><br /><i>Abstract:&nbsp;</i>On March 28, 2012, Callaway Plant personnel discovered a condition in which one train of the containment cooling system operating in 'fast speed' could be tripped by thermal overload protection under certain accident conditions. In this condition, the tripped containment cooling fans could not be automatically restarted by the Load Shedding and Emergency Load Sequencing system. This condition was previously discovered and reported as Callaway Plant LER 2008-001. After that discovery, Modification MP 08-0013 was implemented to correct this condition. However, on March 16, 2012, MP 08-0013 was inadvertently uninstalled on the 'B' train containment coolers during implementation of a different modification on the same control circuit. Causes of this event are associated with ineffective communication between the job planner and design engineer, modification implementation work planned beyond the approved scope of the modification, inadequate evaluation of interaction between plant modifications, and inadequate review of the work instructions. Corrective actions for this event include requiring Field Change Notice initiation when design-related issues are identified, providing training to Callaway Plant staff, and implementing procedure revisions and new checklists to add and strengthen reviews of modifications and work instructions.
4832012002 | Callaway | 08/19/2012 | 10/15/2012 | ML12290A16 | <strong>Failure of 120-V Vital Instrument System Power Inverter NN14</strong><br /><i>Abstract:&nbsp;</i>At 1521 on August 19, 2012, a failure of the NN14 inverter occurred. This inverter provides power to the NN04 instrument bus which is one of the four vital 120-volt, alternating current (AC), instrument buses at Callaway Plant. The NN04 bus remained energized throughout the event. The cause was failure of the output constant-voltage transformer (CVT) within the inverter. Specifically, internal windings in the transformer shorted to ground as a result of less robust varnish used by the manufacturer (prior to 1998) for insulation and controlling vibration. After the cause of failure was identified and work to replace the CVT was progressing, enforcement discretion (ED) was verbally requested of the NRC to allow continued plant operation beyond the Technical Specification time limit for restoration of the inverter to operable status. The ED request was verbally approved at 1455 on August 20. Following replacement of the CVT, NN14 was declared operable at 1205 on August 21, 2012. Corrective actions include periodic replacements of the CVTs on all four similar inverters, as well as enhanced periodic inspections and monitoring of the subject inverters, including the transformers.
4982012001 | South Texas 1 | 03/27/2012 | 08/01/2012 | ML12222A01 | <strong>Unit 1 Nuclear Instrumentation Channel NI-45A Failed Channel Check</strong><br /><i>Abstract:&nbsp;</i>On March 27, 2012, Operations declared the Extended Range (E/R) Flux Lower Range Nuclear Instrument (NI-45A) inoperable based on failure to meet channel check acceptance criteria per the "Remote Shutdown Monitoring AND Accident Monitoring Instrumentation Channel Checks" Procedure. Subsequent troubleshooting discovered an issue with the channel's isolation circuit card, AT1. The AT1 card was found with a degraded condition which affected the output range of NI-45A. With this degraded condition, Extended Range (E/R) Flux Lower Range Nuclear Instrument (NI-45A) would not have been able to perform its design function. Subsequent review determined that NI 45A had been inoperable since February 29, 2012. After replacement of the AT1 card, the surveillance procedure was completed satisfactory on March 30, 2012 and the instrument was restored to operable. Since NI-45 had been inoperable for longer than the applicable Technical Specification 7 day Allowed Outage Time, this event is reportable under 10CFR50.73(a)(2)(i)(B), as an Operation or Condition Prohibited by Technical Specifications. There were no personnel injuries, no offsite radiological releases, and no damage to safety-related equipment associated with this condition. This condition did not have an adverse effect on the health and safety of the public. This LER revision provides the results of the associated Root Cause Evaluation. The root cause of this event is the lack of timely and dependable testing to identify a failure prior to exceeding the Limiting Condition for Operation (LCO). The corrective action identified to prevent recurrence is to initiate periodic Preventive Maintenance activities to press test switches 1 and 2 to test E/R Low Range indication twice weekly and verify startup rate indication on the Integrated Computer System (ICS).
5282012001 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 04/19/2005 | 05/07/2012 | ML12139A13 | <strong>Technical Specification LCO 3.1.7 Incorrect PDIL Setpoint Values</strong><br /><i>Abstract:&nbsp;</i>On March 8, 2012, at approximately 1752 Mountain Standard Time, all Palo Verde units entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.1.7 Regulating Control Element Assembly (CEA) Insertion Limits, Condition D, when the power dependent insertion limit (PDIL) alarm setpoint was determinedto be non-conservative. The value for the PDIL alarm setpoint had been incorrect since April 19, 2005, when the specified regulating group CEAs fully withdrawn position was raised from greater than or equal to (>/=) 144.47 inches to >/=147.75 inches, and the PDIL alarm setpoint remained at 144 inches. As an immediate corrective action, the PDIL alarm setpoint for all three units was changed to 147 inches. This corrective action allowed each unit to exit TS LCO 3.1.7 on March 11, 2012. The cause of this event was determined to be the implementation of a change that was made to the specified CEA fully withdrawn position in the Core Operating Limits Report (COLR) without making the corresponding change to the PDIL alarm setpoint. No similar events have been reported to the NRC in the prior three years.
5282012002 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 01/22/2012 | 07/09/2012 | ML12202A09 | <strong>Supported Systems Not Considered Inoperable with Support Equipment Inoperable</strong><br /><i>Abstract:&nbsp;</i>On May 9, 2012, a review of the procedural guidance for inoperable essential ventilation equipment by an investigation team concluded that a condition prohibited by Technical Specifications (TS) had occurred in unit 2 on January 22, 2012, when the TS requirements for electrical distribution equipment were not met. On January 22, 2012, during surveillance testing in unit 2, a control relay did not change state as expected and the essential ventilation dampers controlled by this relay did not change position. Operations declared the affected essential air handling units inoperable. The TSs do not contain specific Limiting Conditions for Operation (LCO) requirements for the affected essential ventilation equipment and no TS LCO Conditions were entered. Operations followed existing procedural guidance for inoperable ventilation equipment. The procedural guidance required operations to verify that there was no loss of safety function and that normal room cooling was available. The cause of the event was an inadequate procedure that was based on an incorrect understanding of the relationship between essential ventilation equipment that provides a support function to electrical distribution equipment and operability of the electrical distribution equipment. As corrective action, the affected procedure was revised. Similar reportable events have not occurred in the past three years.
5282012003 | Palo Verde 1 | 07/13/2012 | 09/11/2012 | ML12258A37 | <strong>Main Steam Isolation Valve Actuator Train Inoperable due to Low Nitrogen Pre-Charge Pressure</strong><br /><i>Abstract:&nbsp;</i>On July 13, 2012, an engineering evaluation determined that the Unit 1 Main Steam Isolation Valve (MSIV) SGE-UV-180 'A' actuator train was inoperable for approximately 23 days (June 2 to June 25). The evaluation concluded that, due to a nitrogen leak on the accumulator, low nitrogen pre-charge pressure on the 'A' actuator train could have prevented the fast close feature on MSIV 180 using the 'A' actuator train. Technical Specification (TS) Limiting Condition of Operation (LCO.) 3.7.2 Condition A allows one actuator train to be inoperable for up to 7 days; therefore, the duration of the condition was greater than allowed by Technical Specifications. The leak was discovered and corrected during a maintenance activity on June 25, 2012, and the accumulator nitrogen pre-charge pressure was restored to within specifications. The root cause investigation determined that less than adequate monitoring of various alarm system features placed the Unit 1 MSIV 180 hydraulic fluid reservoir low level alarm in a condition where it could not alert plant operators to the degrading nitrogen pre-charge pressure condition. To prevent recurrence, actions will be implemented to record and trend levels in the MSIV and FWIV fluid reservoirs and to monitor accumulator pre-charge pressure to ensure timely discovery of a loss of pre-charge pressure affecting operability of the valves. In the past three years, PVNGS has not reported a similar event to the NRC.
5282012004 | Palo Verde 1 | 08/29/2012 | 10/29/2012 | ML12310A36 | <strong>Essential Spray Pond Pump Actuation Due to a Control Room Essential Filtration Actuation Signal</strong><br /><i>Abstract:&nbsp;</i>On August 29, 2012, the Unit 1 control room received a fuel building ventilation exhaust radiation monitor 1JSOBRU0145 (RU-145) high radioactivity alarm. This resulted in actuation of the train A and B fuel building essential ventilation actuation signals (FBEVAS) and control room essential filtration actuation signals (CREFAS). The CREFAS started the train A and B control room essential air filtration units, essential chilled water systems, essential cooling water systems and essential spray pond systems. Alternate sampling and radiation monitor comparisons determined the RU-145 high radioactivity alarm to be invalid. An investigation determined the RU-145 high radioactivity alarm was caused by failure of a power supply zener diode and resultant loss of the 24 VDC low voltage power supply. Loss of the 24 VDC supply activated the check source feature which raised the radiation monitor output to above the high alarm set-point value.The faulty power supply was replaced. No additional actions were determined to be necessary because existing preventive maintenance requirements replace the power supply board every 7.5 years and zener diodes are reliable in voltage regulation applications for the radiation monitoring system at PVNGS. This was the first failure of this type at PVNGS with greater than 25 years of operation. In the past three years, PVNGS has not reported a similar event to the NRC.
5282012005 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 12/14/2012 | 10/07/2013 | ML13283A08 | <strong>Condition Prohibited by Technical Specifications due to Remote Shutdown System Control Circuit Deficiencies</strong><br /><i>Abstract:&nbsp;</i>On December 14, 2012, during a review of remote shutdown system (RSS) control circuits, a deficiency was identified which could prevent proper isolation of the train B pressurizer (PZR) backup heater controls during a control room (CR) fire event. On January 29, 2013, further review of RSS control circuits identified similar deficiencies for two chemical and volume control system isolation valves. On August 7, 2013, five additional RSS control circuits with similar deficiencies were identified during extent of condition reviews to confirm circuit isolation design features are adequate. <br /><br /> In each of the cases, Technical Specification Limiting Condition for Operation 3.3.11 Condition B was entered and within 30 days, exited when alternative measures to address the RSS control circuit functions were provided in corresponding revisions to the CR fire procedure. The cause of the event was original latent design deficiencies. Additionally, RSS control circuit reviews performed during a 2007 cause evaluation, for a similar event, were conducted without adequate comprehensive review and independent verification. In the past three years, PVNGS reported one event involving an inoperable RSS component which was caused by inadequate post maintenance testing. (LER 50- 530/2010-001-00).
5282012006 | Palo Verde 1, Palo Verde 2, Palo Verde 3 | 12/21/2012 | 02/19/2013 | ML13056A00 | <strong>Safety Injection System Check Valve Testing Could Have Resulted in Less than Required Injection Flow</strong><br /><i>Abstract:&nbsp;</i>On December 21, 2012, PVNGS discovered that previous revisions of surveillance test (ST) procedures to conduct safety injection system (SI) injection line check valve testing allowed system alignments that could have resulted in less than the minimum required emergency core cooling system (ECCS) flow described in the safety analysis and licensing bases. The ST procedures directed closure of the manual discharge isolation valve for the train B high pressure safety injection (HPSI) pump and directed opening of a manual drain valve on one of the four SI injection headers which created a potential for diversion of a portion of the ECCS flow provided by the train A HPSI pump. The latent procedure deficiencies existed since 1983. The root cause was the procedure review process failed to identify the latent procedure deficiencies affecting both ECCS trains. The ST procedures were revised so that system alignments for SI injection line check valve testing ensure availability of at least 100 percent of ECCS flow equivalent to a single operable ECCS train. To prevent recurrence, the procedure process will be revised to identify and resolve common train impacts on design and licensing bases involving safety systems during procedure reviews. A similar event has not occurred in the prior three years that required reporting.
5292012001 | Palo Verde 2 | 01/25/2012 | 03/26/2012 | ML12101A10 | <strong>Technical Specification LCO 3.1.7 Completion Time Exceeded</strong><br /><i>Abstract:&nbsp;</i>On January 25, 2012, at approximately 1005 Mountain Standard Time, a reactor power cutback occurred in Unit 2 due to the loss of one main feedwater pump. Main turbine load was automatically reduced and all regulating group 4 and group 5 control element assemblies (CEAs) were automatically fully inserted to lower reactor power to approximately 50 percent. The Reactor Regulating System then automatically inserted regulating group 3 CEAs below the Technical Specification (TS) Transient Insertion Limits to maintain Reactor Coolant System temperature within limits. TS LCO 3.1.7 Regulating CEA Insertion Limits are not applicable for two hours after a reactor power cutback and then require CEA positions to be restored to within limits in the next two hours or be in Mode 3 within the following six hours. Group 4 and 5 CEAs were restored to within TS LCO 3.1.7 transient insertion limits at 1144. The regulating group 3 CEAs were withdrawn to the upper group stop position of 145.5 inches at 1124 but were not fully withdrawn to within limits (greater than or equal to [>/=] 147.75 inches) until 2030, which exceeded the TS LCO 3.1.7 Completion Time by 25 minutes. The root cause was determined to be inadequate procedural guidance necessary to ensure regulating CEA group 3 was fully withdrawn to comply with the requirements of TS LCO 3.1.7 insertion limits. Corrective actions to prevent recurrence include procedure revisions to provide the needed guidance to ensure CEA insertion limits are met following a reactor power cutback. No similar events have been reported to the NRC in the prior three years.
5292012002 | Palo Verde 2 | 10/07/2012 | 10/25/2013 | ML13304A50 | <strong>Condition Prohibited by Technical Specification due to Low Pressure Safety Injection System Drain Pipe Leak</strong><br /><i>Abstract:&nbsp;</i>On October 8, 2012, at 13:30, when Unit 2 was in Mode 5 during refueling outage 2R17, Shutdown Cooling System (SDC) Train A was declared inoperable in accordance with Technical Specification 3.4.7 due to a leak on a Low Pressure Safety Injection (LPSI) system Train A drain pipe during SDC operation. The leakage source was a weld defect on the LPSI cold leg 1A injection pipe drain connection upstream of drain valve SIA-V908. The leakage was first discovered on October 7, 2012, at 22:00 when water on the floor adjacent to the LPSI cold leg 1A injection pipe was first found, but not identified as leakage through the drain pipe weld until insulation was removed on October 8, 2012.<br /><br /> A configuration control problem in the early 1990s allowed contact between the drain pipe and a pipe hanger when the SDC system was in operation. This resulted in a weld defect being introduced due to the high cyclic stresses from the pipe/hanger contact. The configuration control problem was corrected in May 1993; but, the weld defect propagated slowly during periods of SDC operations until the leak occurred in the 2R17 outage. The cause was determined to be inadequate guidance to ensure temporary fittings on safety-related fluid systems were removed prior to placing the system in service. To prevent recurrence, procedures were revised to require that systems with capped pipe ends be returned to their design configuration following maintenance.
5292012003 | Palo Verde 2 | 11/02/2012 | 12/28/2012 | ML13004A09 | <strong>Entry into Mode 3 with one Auxiliary Feedwater Train Inoperable</strong><br /><i>Abstract:&nbsp;</i>On November 02, 2012, with Unit 2 in Mode 3 following refueling activities, Operations personnel entered Technical Specification (TS) Limiting Condition for Operation (LCO) 3.7.5, Condition A, when the turbine driven Auxiliary Feedwater (AF) pump (AFA-P01) was declared inoperable to support surveillance testing per procedure 73ST-9AF04, AFA-P01 Full Flow-In service Test. During the test, a steam leak was identified on AFA-P01 steam supply valve SGA-UV-138. The valve had been disassembled and reassembled during their fueling outage to correct seat leakage. Testing was secured and Operations personnel declared valve SGA-UV-138 inoperable. Since TS LCO 3.7.5 requires three AF trains to be operable in Modes 1, 2, and 3, and one of the steam supply valves for AFA-P01 was inoperable, TS LCO 3.0.4 was not met when Unit 2 entered Mode 3 at 00:07 on November 2, 2012. As an immediate corrective action, Operations personnel closed valve SGA-UV-138 to stop the leak and placed Unit 2 in Mode 5 to allow the valve repairs. The cause was determined to be inadequate work instructions for valve re-assembly. To prevent recurrence, work instructions will be revised to provide detailed guidance for valve re-assembly and to require verifications of proper re-assembly. In the past three years, PVNGS has not reported a similar event to the NRC.
5302012001 | Palo Verde 3 | 04/15/2012 | 10/23/2012 | ML12299A28 | <strong>Unit 3 Manual Reactor Trip During Low Power Physics Testing</strong><br /><i>Abstract:&nbsp;</i>On April 15, 2012, at approximately 12:16 Mountain Standard Time, Unit 3 was manually tripped during low power physics testing (LPPT) following completion of its 16th refueling outage. An automatic control element drive mechanism timer module (ACTM) was installed on each control element drive mechanism (CEDM) during the refueling outage to minimize the occurrence of slipped or dropped control element assemblies (CEAs) resulting from CEDM or control system (CEDMCS) abnormalities. Regulating CEA group 1 was being inserted during a reactor coolant system (RCS) boron dilution test directed by the LPPT procedure. During the insertion, the ACTM for CEA 57 stopped movement of the CEA and actuated related alarms. Control room staff stopped insertion of regulating CEA group 1 and RCS dilution. Power increased, approaching the LPPT procedural limit of 0.5% power because of the residual RCS dilution effect. The control room staff manually tripped the reactor to comply with the procedural power limit. The root cause of the manual reactor trip was the LPPT procedure did not provide contingency direction to insert other CEA groups to compensate for the RCS dilution. To prevent recurrence, the station will incorporate appropriate contingencies in the LPPT procedure to stabilize reactor power during reactivity manipulations if abnormal conditions with CEAs are encountered.